## CO2
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 10.0385 | [19 empty] | 100 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 9.9114 | [19 empty] | 133.3521 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.5455 | [19 empty] | 177.8279 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 10.8666 | [19 empty] | 237.1374 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.8594 | [19 empty] | 316.2278 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.3314 | [19 empty] | 421.6965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1262 | [19 empty] | 562.3413 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9332 | [19 empty] | 749.8942 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.6782 | [19 empty] | 1000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.0502 | [19 empty] | 1333.5214 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.585 | [19 empty] | 1778.2794 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1885 | [19 empty] | 2371.3737 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.6695 | [19 empty] | 3162.2777 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.8876 | [19 empty] | 4216.965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.6441 | [19 empty] | 5623.4133 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.5892 | [19 empty] | 7498.9421 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.838 | [19 empty] | 10000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.6531 | [19 empty] | 13335.2143 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.9619 | [19 empty] | 17782.7941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.0327 | [19 empty] | 23713.7371 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0042 | [19 empty] | 31622.7766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1794 | [19 empty] | 42169.6503 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7916 | [19 empty] | 56234.1325 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9588 | [19 empty] | 74989.4209 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0754 | [19 empty] | 100000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0041 | [19 empty] | 133352.1432 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.5009 | [19 empty] | 177827.941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.8508 | [19 empty] | 237137.3706 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.8335 | [19 empty] | 316227.766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0139 | [19 empty] | 421696.5034 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.485 | [19 empty] | 562341.3252 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.7734 | [19 empty] | 749894.2093 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.6644 | [19 empty] | 1000000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.4238 | [19 empty] | 1333521.4322 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.2311 | [19 empty] | 1778279.41 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9565 | [19 empty] | 2371373.7057 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.947 | [19 empty] | 3162277.6602 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9126 | [19 empty] | 4216965.0343 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1413 | [19 empty] | 5623413.2519 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1999 | [19 empty] | 7498942.0933 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.5432 | [19 empty] | 10000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.5706 | [19 empty] | 100 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.1505 | [19 empty] | 133.3521 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.2889 | [19 empty] | 177.8279 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.925 | [19 empty] | 237.1374 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.3473 | [19 empty] | 316.2278 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6368 | [19 empty] | 421.6965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2549 | [19 empty] | 562.3413 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3777 | [19 empty] | 749.8942 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7286 | [19 empty] | 1000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1624 | [19 empty] | 1333.5214 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9061 | [19 empty] | 1778.2794 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2441 | [19 empty] | 2371.3737 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5649 | [19 empty] | 3162.2777 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0565 | [19 empty] | 4216.965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1934 | [19 empty] | 5623.4133 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7444 | [19 empty] | 7498.9421 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3828 | [19 empty] | 10000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.757 | [19 empty] | 13335.2143 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.513 | [19 empty] | 17782.7941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9897 | [19 empty] | 23713.7371 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.744 | [19 empty] | 31622.7766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9953 | [19 empty] | 42169.6503 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.7486 | [19 empty] | 56234.1325 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.286 | [19 empty] | 74989.4209 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5761 | [19 empty] | 100000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.845 | [19 empty] | 133352.1432 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1329 | [19 empty] | 177827.941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8307 | [19 empty] | 237137.3706 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.067 | [19 empty] | 316227.766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.5192 | [19 empty] | 421696.5034 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1234 | [19 empty] | 562341.3252 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.4332 | [19 empty] | 749894.2093 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.789 | [19 empty] | 1000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2488 | [19 empty] | 1333521.4322 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.6276 | [19 empty] | 1778279.41 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7433 | [19 empty] | 2371373.7057 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.8025 | [19 empty] | 3162277.6602 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5855 | [19 empty] | 4216965.0343 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7944 | [19 empty] | 5623413.2519 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.1602 | [19 empty] | 7498942.0933 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0623 | [19 empty] | 10000000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.1683 | [19 empty] | 100 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 10.2191 | [19 empty] | 133.3521 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.1569 | [19 empty] | 177.8279 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.4592 | [19 empty] | 237.1374 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.369 | [19 empty] | 316.2278 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.401 | [19 empty] | 421.6965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0652 | [19 empty] | 562.3413 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0068 | [19 empty] | 749.8942 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2085 | [19 empty] | 1000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3815 | [19 empty] | 1333.5214 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2173 | [19 empty] | 1778.2794 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1768 | [19 empty] | 2371.3737 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3664 | [19 empty] | 3162.2777 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3393 | [19 empty] | 4216.965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2258 | [19 empty] | 5623.4133 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0429 | [19 empty] | 7498.9421 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8629 | [19 empty] | 10000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1274 | [19 empty] | 13335.2143 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0866 | [19 empty] | 17782.7941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5154 | [19 empty] | 23713.7371 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.009 | [19 empty] | 31622.7766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.607 | [19 empty] | 42169.6503 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2642 | [19 empty] | 56234.1325 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1097 | [19 empty] | 74989.4209 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5467 | [19 empty] | 100000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3906 | [19 empty] | 133352.1432 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4764 | [19 empty] | 177827.941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9546 | [19 empty] | 237137.3706 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0593 | [19 empty] | 316227.766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7303 | [19 empty] | 421696.5034 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0966 | [19 empty] | 562341.3252 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.5032 | [19 empty] | 749894.2093 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3634 | [19 empty] | 1000000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4502 | [19 empty] | 1333521.4322 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3641 | [19 empty] | 1778279.41 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7622 | [19 empty] | 2371373.7057 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8813 | [19 empty] | 3162277.6602 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1299 | [19 empty] | 4216965.0343 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8245 | [19 empty] | 5623413.2519 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5992 | [19 empty] | 7498942.0933 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1652 | [19 empty] | 10000000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 10.9154 | [19 empty] | 100 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 10.928 | [19 empty] | 133.3521 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.6677 | [19 empty] | 177.8279 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.2818 | [19 empty] | 237.1374 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0511 | [19 empty] | 316.2278 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.21 | [19 empty] | 421.6965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.1358 | [19 empty] | 562.3413 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7833 | [19 empty] | 749.8942 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2505 | [19 empty] | 1000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.1568 | [19 empty] | 1333.5214 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2238 | [19 empty] | 1778.2794 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8547 | [19 empty] | 2371.3737 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5759 | [19 empty] | 3162.2777 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9384 | [19 empty] | 4216.965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.522 | [19 empty] | 5623.4133 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6383 | [19 empty] | 7498.9421 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.872 | [19 empty] | 10000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3407 | [19 empty] | 13335.2143 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7194 | [19 empty] | 17782.7941 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8894 | [19 empty] | 23713.7371 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3938 | [19 empty] | 31622.7766 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9028 | [19 empty] | 42169.6503 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4062 | [19 empty] | 56234.1325 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9065 | [19 empty] | 74989.4209 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3399 | [19 empty] | 100000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9435 | [19 empty] | 133352.1432 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9983 | [19 empty] | 177827.941 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8781 | [19 empty] | 237137.3706 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2778 | [19 empty] | 316227.766 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4294 | [19 empty] | 421696.5034 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8143 | [19 empty] | 562341.3252 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4023 | [19 empty] | 749894.2093 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5197 | [19 empty] | 1000000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7314 | [19 empty] | 1333521.4322 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3895 | [19 empty] | 1778279.41 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0263 | [19 empty] | 2371373.7057 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9605 | [19 empty] | 3162277.6602 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0472 | [19 empty] | 4216965.0343 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0835 | [19 empty] | 5623413.2519 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3784 | [19 empty] | 7498942.0933 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8234 | [19 empty] | 10000000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.1617 | [19 empty] | 100 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.3675 | [19 empty] | 133.3521 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.4799 | [19 empty] | 177.8279 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2763 | [19 empty] | 237.1374 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7918 | [19 empty] | 316.2278 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.8326 | [19 empty] | 421.6965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.9877 | [19 empty] | 562.3413 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.1939 | [19 empty] | 749.8942 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.1978 | [19 empty] | 1000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8912 | [19 empty] | 1333.5214 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5634 | [19 empty] | 1778.2794 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8125 | [19 empty] | 2371.3737 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9083 | [19 empty] | 3162.2777 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4347 | [19 empty] | 4216.965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7595 | [19 empty] | 5623.4133 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.669 | [19 empty] | 7498.9421 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3854 | [19 empty] | 10000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0819 | [19 empty] | 13335.2143 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5838 | [19 empty] | 17782.7941 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9789 | [19 empty] | 23713.7371 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7176 | [19 empty] | 31622.7766 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1269 | [19 empty] | 42169.6503 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8694 | [19 empty] | 56234.1325 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6411 | [19 empty] | 74989.4209 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8822 | [19 empty] | 100000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9325 | [19 empty] | 133352.1432 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2436 | [19 empty] | 177827.941 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5771 | [19 empty] | 237137.3706 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2214 | [19 empty] | 316227.766 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0276 | [19 empty] | 421696.5034 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.7148 | [19 empty] | 562341.3252 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9574 | [19 empty] | 749894.2093 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2855 | [19 empty] | 1000000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.3604 | [19 empty] | 1333521.4322 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0245 | [19 empty] | 1778279.41 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6457 | [19 empty] | 2371373.7057 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2452 | [19 empty] | 3162277.6602 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1302 | [19 empty] | 4216965.0343 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.2254 | [19 empty] | 5623413.2519 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4 | [19 empty] | 7498942.0933 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9085 | [19 empty] | 10000000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.8783 | [19 empty] | 100 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.4443 | [19 empty] | 133.3521 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.8671 | [19 empty] | 177.8279 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7647 | [19 empty] | 237.1374 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1991 | [19 empty] | 316.2278 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.6338 | [19 empty] | 421.6965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8778 | [19 empty] | 562.3413 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2737 | [19 empty] | 749.8942 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4992 | [19 empty] | 1000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7792 | [19 empty] | 1333.5214 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1874 | [19 empty] | 1778.2794 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.637 | [19 empty] | 2371.3737 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0087 | [19 empty] | 3162.2777 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9992 | [19 empty] | 4216.965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9402 | [19 empty] | 5623.4133 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3878 | [19 empty] | 7498.9421 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3755 | [19 empty] | 10000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.908 | [19 empty] | 13335.2143 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1201 | [19 empty] | 17782.7941 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.51 | [19 empty] | 23713.7371 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6405 | [19 empty] | 31622.7766 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0329 | [19 empty] | 42169.6503 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3645 | [19 empty] | 56234.1325 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.635 | [19 empty] | 74989.4209 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5299 | [19 empty] | 100000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2749 | [19 empty] | 133352.1432 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.0369 | [19 empty] | 177827.941 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.7131 | [19 empty] | 237137.3706 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3794 | [19 empty] | 316227.766 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9177 | [19 empty] | 421696.5034 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1081 | [19 empty] | 562341.3252 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0728 | [19 empty] | 749894.2093 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.96 | [19 empty] | 1000000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1138 | [19 empty] | 1333521.4322 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9216 | [19 empty] | 1778279.41 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9024 | [19 empty] | 2371373.7057 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4386 | [19 empty] | 3162277.6602 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7174 | [19 empty] | 4216965.0343 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.6492 | [19 empty] | 5623413.2519 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6874 | [19 empty] | 7498942.0933 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4367 | [19 empty] | 10000000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.4184 | [19 empty] | 100 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.6952 | [19 empty] | 133.3521 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.5538 | [19 empty] | 177.8279 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8886 | [19 empty] | 237.1374 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.2195 | [19 empty] | 316.2278 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.9395 | [19 empty] | 421.6965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.2621 | [19 empty] | 562.3413 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7605 | [19 empty] | 749.8942 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9889 | [19 empty] | 1000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.7526 | [19 empty] | 1333.5214 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0034 | [19 empty] | 1778.2794 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2233 | [19 empty] | 2371.3737 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.5076 | [19 empty] | 3162.2777 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1545 | [19 empty] | 4216.965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4012 | [19 empty] | 5623.4133 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5634 | [19 empty] | 7498.9421 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8805 | [19 empty] | 10000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9789 | [19 empty] | 13335.2143 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.2059 | [19 empty] | 17782.7941 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.669 | [19 empty] | 23713.7371 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.3841 | [19 empty] | 31622.7766 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7506 | [19 empty] | 42169.6503 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.6172 | [19 empty] | 56234.1325 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7337 | [19 empty] | 74989.4209 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5159 | [19 empty] | 100000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6876 | [19 empty] | 133352.1432 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.3327 | [19 empty] | 177827.941 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2149 | [19 empty] | 237137.3706 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5294 | [19 empty] | 316227.766 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4218 | [19 empty] | 421696.5034 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1448 | [19 empty] | 562341.3252 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7037 | [19 empty] | 749894.2093 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2039 | [19 empty] | 1000000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5601 | [19 empty] | 1333521.4322 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4371 | [19 empty] | 1778279.41 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.5483 | [19 empty] | 2371373.7057 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2076 | [19 empty] | 3162277.6602 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0975 | [19 empty] | 4216965.0343 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.7193 | [19 empty] | 5623413.2519 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4887 | [19 empty] | 7498942.0933 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.1782 | [19 empty] | 10000000 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.0063 | [19 empty] | 100 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6713 | [19 empty] | 133.3521 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.5981 | [19 empty] | 177.8279 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.785 | [19 empty] | 237.1374 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0361 | [19 empty] | 316.2278 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055897 | 1.9124e-05 | 4 | 93998332.9549 | 312153337.3225 | 1916283.1594 | 6363668 | 22.5612 | 0.029797 | 18.7587 | 2255.7085 | 0 | 1984.8925 | 0 | 0 | 0 | 0 | 1653.8344 | 4302.9378 | 2936.8435 | 13134.2167 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7190373.4307 | 23878073.0724 | 421.6965 | 7.6495e-05 | 93998332.9549 | 312153337.3225 | 1916283.1594 | 6363668
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055897 | 1.9131e-05 | 4 | 93963286.1612 | 312036832.7527 | 1915568.6831 | 6361292.8967 | 22.5613 | 0.029809 | 18.0836 | 2256.3178 | 0 | 1985.5587 | 0 | 0 | 0 | 0 | 1654.3318 | 4304.232 | 2937.7268 | 13138.167 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7190377.381 | 23878077.0227 | 562.3413 | 7.6523e-05 | 93963286.1612 | 312036832.7527 | 1915568.6831 | 6361292.8967
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055897 | 1.9138e-05 | 4 | 93926690.1724 | 311915178.2743 | 1914822.6244 | 6358812.8056 | 22.5613 | 0.029821 | 19.2728 | 2256.9544 | 0 | 1986.2547 | 0 | 0 | 0 | 0 | 1654.8515 | 4305.5843 | 2938.6497 | 13142.2946 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7190381.5086 | 23878081.1503 | 749.8942 | 7.6553e-05 | 93926690.1724 | 311915178.2743 | 1914822.6244 | 6358812.8056
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055897 | 1.9142e-05 | 4 | 93907497.844 | 311851378.0446 | 1914431.3628 | 6357512.1516 | 22.5614 | 0.029828 | 17.8426 | 2257.2884 | 0 | 1986.62 | 0 | 0 | 0 | 0 | 1655.1243 | 4306.2938 | 2939.134 | 13144.4604 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7190383.6744 | 23878083.3161 | 1000 | 7.6569e-05 | 93907497.844 | 311851378.0446 | 1914431.3628 | 6357512.1516
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055897 | 1.9143e-05 | 4 | 93904230.5581 | 311840516.7475 | 1914364.7548 | 6357290.7294 | 22.5614 | 0.029829 | 17.4449 | 2257.3453 | 0 | 1986.6821 | 0 | 0 | 0 | 0 | 1655.1707 | 4306.4146 | 2939.2165 | 13144.8292 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7190384.0431 | 23878083.6849 | 1333.5214 | 7.6571e-05 | 93904230.5581 | 311840516.7475 | 1914364.7548 | 6357290.7294
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8 | 0.26352 | 0.00043606 | 4 | 4193552.8199 | 13760847.8917 | 85491.2464 | 280533.4972 | 23.6529 | 0.18471 | 17.6431 | 19192.7577 | 0 | 25150.1652 | 0 | 0 | 0 | 0 | 17293.74 | 44994.7639 | 30709.8509 | 137341.2778 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7314580.4917 | 24002280.1334 | 1778.2794 | 0.0017442 | 4193552.8199 | 13760847.8917 | 85491.2464 | 280533.4972
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4421 | 0.44469 | 0.00076117 | 4 | 2425752.0307 | 7906710.2899 | 49452.2362 | 161188.9839 | 23.7393 | 0.197 | 37.8665 | 28090.6439 | 0 | 39185.4095 | 0 | 0 | 0 | 0 | 26237.6608 | 68265.0114 | 46592.273 | 208370.9987 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7385610.2126 | 24073309.8543 | 2371.3737 | 0.0030447 | 2425752.0307 | 7906710.2899 | 49452.2362 | 161188.9839
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086552 | 4 | 2139399.0296 | 6959512.3307 | 43614.543 | 141879.0723 | 23.7472 | 0.19811 | 42.8179 | 30686.3416 | 0 | 43433.4136 | 0 | 0 | 0 | 0 | 28906.7045 | 75209.3155 | 51331.9033 | 229567.6784 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406806.8924 | 24094506.5341 | 3162.2777 | 0.0034621 | 2139399.0296 | 6959512.3307 | 43614.543 | 141879.0723
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086558 | 4 | 2139258.6187 | 6959048.5623 | 43611.6805 | 141869.6178 | 23.7473 | 0.19812 | 40.8324 | 30687.6826 | 0 | 43435.5499 | 0 | 0 | 0 | 0 | 28908.0607 | 75212.844 | 51334.3115 | 229578.4486 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406817.6626 | 24094517.3043 | 4216.965 | 0.0034623 | 2139258.6187 | 6959048.5623 | 43611.6805 | 141869.6178
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086563 | 4 | 2139152.3103 | 6958697.4326 | 43609.5133 | 141862.4595 | 23.7474 | 0.19813 | 42.7217 | 30688.698 | 0 | 43437.1675 | 0 | 0 | 0 | 0 | 28909.0875 | 75215.5157 | 51336.135 | 229586.6038 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406825.8177 | 24094525.4595 | 5623.4133 | 0.0034625 | 2139152.3103 | 6958697.4326 | 43609.5133 | 141862.4595
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50606 | 0.00086564 | 4 | 2139108.8692 | 6958553.9495 | 43608.6277 | 141859.5344 | 23.7474 | 0.19814 | 42.4051 | 30689.113 | 0 | 43437.8286 | 0 | 0 | 0 | 0 | 28909.5072 | 75216.6075 | 51336.8802 | 229589.9364 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406829.1504 | 24094528.7921 | 7498.9421 | 0.0034626 | 2139108.8692 | 6958553.9495 | 43608.6277 | 141859.5344
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50606 | 0.00086564 | 4 | 2139113.306 | 6958568.604 | 43608.7181 | 141859.8332 | 23.7474 | 0.19814 | 38.1575 | 30689.0706 | 0 | 43437.761 | 0 | 0 | 0 | 0 | 28909.4643 | 75216.496 | 51336.8041 | 229589.5961 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406828.81 | 24094528.4517 | 10000 | 0.0034626 | 2139113.306 | 6958568.604 | 43608.7181 | 141859.8332
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086563 | 4 | 2139144.9819 | 6958673.2273 | 43609.3639 | 141861.966 | 23.7474 | 0.19813 | 41.0255 | 30688.768 | 0 | 43437.279 | 0 | 0 | 0 | 0 | 28909.1583 | 75215.6999 | 51336.2607 | 229587.166 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406826.38 | 24094526.0217 | 13335.2143 | 0.0034625 | 2139144.9819 | 6958673.2273 | 43609.3639 | 141861.966
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086561 | 4 | 2139187.9898 | 6958815.2798 | 43610.2406 | 141864.862 | 23.7474 | 0.19813 | 40.1933 | 30688.3572 | 0 | 43436.6246 | 0 | 0 | 0 | 0 | 28908.7429 | 75214.619 | 51335.523 | 229583.8666 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406823.0806 | 24094522.7223 | 17782.7941 | 0.0034624 | 2139187.9898 | 6958815.2798 | 43610.2406 | 141864.862
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086559 | 4 | 2139232.8583 | 6958963.4775 | 43611.1553 | 141867.8832 | 23.7473 | 0.19813 | 39.9719 | 30687.9286 | 0 | 43435.9418 | 0 | 0 | 0 | 0 | 28908.3095 | 75213.4914 | 51334.7533 | 229580.4247 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406819.6387 | 24094519.2804 | 23713.7371 | 0.0034624 | 2139232.8583 | 6958963.4775 | 43611.1553 | 141867.8832
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086558 | 4 | 2139273.8725 | 6959098.9447 | 43611.9915 | 141870.6449 | 23.7473 | 0.19812 | 40.0654 | 30687.5369 | 0 | 43435.3178 | 0 | 0 | 0 | 0 | 28907.9133 | 75212.4607 | 51334.0499 | 229577.2785 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406816.4925 | 24094516.1342 | 31622.7766 | 0.0034623 | 2139273.8725 | 6959098.9447 | 43611.9915 | 141870.6449
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086556 | 4 | 2139309.1498 | 6959215.4633 | 43612.7106 | 141873.0203 | 23.7473 | 0.19812 | 39.4157 | 30687.2 | 0 | 43434.781 | 0 | 0 | 0 | 0 | 28907.5726 | 75211.5741 | 51333.4448 | 229574.5725 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406813.7865 | 24094513.4282 | 42169.6503 | 0.0034622 | 2139309.1498 | 6959215.4633 | 43612.7106 | 141873.0203
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086555 | 4 | 2139338.4089 | 6959312.1042 | 43613.3071 | 141874.9904 | 23.7473 | 0.19812 | 42.6314 | 30686.9205 | 0 | 43434.3359 | 0 | 0 | 0 | 0 | 28907.29 | 75210.8389 | 51332.9429 | 229572.3282 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406811.5421 | 24094511.1839 | 56234.1325 | 0.0034622 | 2139338.4089 | 6959312.1042 | 43613.3071 | 141874.9904
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086554 | 4 | 2139361.6393 | 6959388.8327 | 43613.7807 | 141876.5546 | 23.7473 | 0.19811 | 40.7375 | 30686.6987 | 0 | 43433.9824 | 0 | 0 | 0 | 0 | 28907.0656 | 75210.2551 | 51332.5445 | 229570.5463 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406809.7603 | 24094509.402 | 74989.4209 | 0.0034622 | 2139361.6393 | 6959388.8327 | 43613.7807 | 141876.5546
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086553 | 4 | 2139380.0588 | 6959449.6712 | 43614.1562 | 141877.7949 | 23.7472 | 0.19811 | 41.8262 | 30686.5227 | 0 | 43433.7022 | 0 | 0 | 0 | 0 | 28906.8877 | 75209.7922 | 51332.2286 | 229569.1335 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406808.3475 | 24094507.9892 | 100000 | 0.0034621 | 2139380.0588 | 6959449.6712 | 43614.1562 | 141877.7949
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086553 | 4 | 2139394.391 | 6959497.0094 | 43614.4484 | 141878.76 | 23.7472 | 0.19811 | 39.8589 | 30686.3859 | 0 | 43433.4841 | 0 | 0 | 0 | 0 | 28906.7493 | 75209.4321 | 51331.9828 | 229568.0342 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406807.2482 | 24094506.8899 | 133352.1432 | 0.0034621 | 2139394.391 | 6959497.0094 | 43614.4484 | 141878.76
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086552 | 4 | 2139405.4117 | 6959533.4103 | 43614.6731 | 141879.502 | 23.7472 | 0.19811 | 40.9965 | 30686.2806 | 0 | 43433.3165 | 0 | 0 | 0 | 0 | 28906.6429 | 75209.1552 | 51331.7938 | 229567.1889 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406806.4029 | 24094506.0446 | 177827.941 | 0.0034621 | 2139405.4117 | 6959533.4103 | 43614.6731 | 141879.502
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086552 | 4 | 2139413.8482 | 6959561.2755 | 43614.8451 | 141880.0701 | 23.7472 | 0.19811 | 40.6376 | 30686.2001 | 0 | 43433.1881 | 0 | 0 | 0 | 0 | 28906.5614 | 75208.9432 | 51331.6491 | 229566.5418 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406805.7558 | 24094505.3975 | 237137.3706 | 0.0034621 | 2139413.8482 | 6959561.2755 | 43614.8451 | 141880.0701
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086552 | 4 | 2139420.268 | 6959582.4797 | 43614.9759 | 141880.5024 | 23.7472 | 0.19811 | 41.262 | 30686.1387 | 0 | 43433.0904 | 0 | 0 | 0 | 0 | 28906.4994 | 75208.7819 | 51331.539 | 229566.0494 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406805.2634 | 24094504.9051 | 316227.766 | 0.0034621 | 2139420.268 | 6959582.4797 | 43614.9759 | 141880.5024
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139425.135 | 6959598.555 | 43615.0752 | 141880.8301 | 23.7472 | 0.19811 | 38.611 | 30686.0923 | 0 | 43433.0164 | 0 | 0 | 0 | 0 | 28906.4524 | 75208.6596 | 51331.4555 | 229565.6761 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.8901 | 24094504.5318 | 421696.5034 | 0.0034621 | 2139425.135 | 6959598.555 | 43615.0752 | 141880.8301
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139428.8145 | 6959610.7083 | 43615.1502 | 141881.0779 | 23.7472 | 0.19811 | 41.7898 | 30686.0571 | 0 | 43432.9604 | 0 | 0 | 0 | 0 | 28906.4168 | 75208.5671 | 51331.3924 | 229565.3939 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.6079 | 24094504.2496 | 562341.3252 | 0.003462 | 2139428.8145 | 6959610.7083 | 43615.1502 | 141881.0779
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139431.5904 | 6959619.8768 | 43615.2068 | 141881.2648 | 23.7472 | 0.19811 | 41.1228 | 30686.0306 | 0 | 43432.9182 | 0 | 0 | 0 | 0 | 28906.39 | 75208.4974 | 51331.3448 | 229565.181 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.395 | 24094504.0367 | 749894.2093 | 0.003462 | 2139431.5904 | 6959619.8768 | 43615.2068 | 141881.2648
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139433.6817 | 6959626.7844 | 43615.2494 | 141881.4056 | 23.7472 | 0.19811 | 40.8097 | 30686.0106 | 0 | 43432.8864 | 0 | 0 | 0 | 0 | 28906.3698 | 75208.4448 | 51331.309 | 229565.0206 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.2346 | 24094503.8763 | 1000000 | 0.003462 | 2139433.6817 | 6959626.7844 | 43615.2494 | 141881.4056
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139435.2555 | 6959631.9825 | 43615.2815 | 141881.5116 | 23.7472 | 0.19811 | 40.5335 | 30685.9956 | 0 | 43432.8624 | 0 | 0 | 0 | 0 | 28906.3546 | 75208.4053 | 51331.282 | 229564.8999 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.1139 | 24094503.7556 | 1333521.4322 | 0.003462 | 2139435.2555 | 6959631.9825 | 43615.2815 | 141881.5116
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139436.4385 | 6959635.8898 | 43615.3056 | 141881.5912 | 23.7472 | 0.19811 | 41.4056 | 30685.9843 | 0 | 43432.8444 | 0 | 0 | 0 | 0 | 28906.3432 | 75208.3755 | 51331.2617 | 229564.8092 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406804.0232 | 24094503.6649 | 1778279.41 | 0.003462 | 2139436.4385 | 6959635.8898 | 43615.3056 | 141881.5912
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139437.3297 | 6959638.8334 | 43615.3238 | 141881.6512 | 23.7472 | 0.19811 | 40.3331 | 30685.9758 | 0 | 43432.8309 | 0 | 0 | 0 | 0 | 28906.3346 | 75208.3531 | 51331.2464 | 229564.7408 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.9548 | 24094503.5965 | 2371373.7057 | 0.003462 | 2139437.3297 | 6959638.8334 | 43615.3238 | 141881.6512
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139437.9948 | 6959641.0303 | 43615.3373 | 141881.696 | 23.7472 | 0.19811 | 41.1076 | 30685.9695 | 0 | 43432.8208 | 0 | 0 | 0 | 0 | 28906.3282 | 75208.3364 | 51331.235 | 229564.6898 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.9038 | 24094503.5455 | 3162277.6602 | 0.003462 | 2139437.9948 | 6959641.0303 | 43615.3373 | 141881.696
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139438.4958 | 6959642.6849 | 43615.3475 | 141881.7297 | 23.7472 | 0.19811 | 39.3623 | 30685.9647 | 0 | 43432.8131 | 0 | 0 | 0 | 0 | 28906.3233 | 75208.3238 | 51331.2264 | 229564.6514 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.8654 | 24094503.5071 | 4216965.0343 | 0.003462 | 2139438.4958 | 6959642.6849 | 43615.3475 | 141881.7297
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139438.887 | 6959643.9771 | 43615.3555 | 141881.7561 | 23.7472 | 0.19811 | 40.3528 | 30685.9609 | 0 | 43432.8072 | 0 | 0 | 0 | 0 | 28906.3196 | 75208.314 | 51331.2197 | 229564.6214 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.8354 | 24094503.4771 | 5623413.2519 | 0.003462 | 2139438.887 | 6959643.9771 | 43615.3555 | 141881.7561
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139439.154 | 6959644.8588 | 43615.361 | 141881.7741 | 23.7472 | 0.19811 | 39.916 | 30685.9584 | 0 | 43432.8031 | 0 | 0 | 0 | 0 | 28906.317 | 75208.3073 | 51331.2151 | 229564.6009 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.8149 | 24094503.4566 | 7498942.0933 | 0.003462 | 2139439.154 | 6959644.8588 | 43615.361 | 141881.7741
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6742 | 0.50607 | 0.00086551 | 4 | 2139439.3658 | 6959645.5585 | 43615.3653 | 141881.7883 | 23.7472 | 0.19811 | 39.5458 | 30685.9564 | 0 | 43432.7999 | 0 | 0 | 0 | 0 | 28906.3149 | 75208.302 | 51331.2115 | 229564.5847 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7406803.7986 | 24094503.4403 | 10000000 | 0.003462 | 2139439.3658 | 6959645.5585 | 43615.3653 | 141881.7883
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.0655 | [19 empty] | 100 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.4924 | [19 empty] | 133.3521 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.8729 | [19 empty] | 177.8279 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.996 | [19 empty] | 237.1374 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1303 | [19 empty] | 316.2278 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055274 | 0.00022484 | 4 | 8517413.4258 | 27844617.6369 | 173638.9933 | 567650.1932 | 25.2354 | 0.41701 | 18.4216 | 14515.0377 | 0 | 17584.9138 | 0 | 0 | 0 | 3377.7428 | 13836.3007 | 35999.2163 | 24570.2049 | 109883.4162 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7660301.5878 | 25042598.9714 | 421.6965 | 0.00089937 | 8517413.4258 | 27844617.6369 | 173638.9933 | 567650.1932
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055573 | 0.00030867 | 4 | 6195788.6153 | 20274124.9813 | 126309.5313 | 413315.4605 | 25.2355 | 0.41702 | 18.6668 | 14515.2479 | 0 | 17585.197 | 0 | 0 | 0 | 0 | 12519.1735 | 32572.3214 | 22231.2787 | 99423.2186 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7649841.3902 | 25032138.7738 | 562.3413 | 0.0012347 | 6195788.6153 | 20274124.9813 | 126309.5313 | 413315.4605
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055572 | 0.00030868 | 4 | 6195634.2713 | 20273616.8369 | 126306.3848 | 413305.1013 | 25.2355 | 0.41703 | 17.8292 | 14515.4791 | 0 | 17585.5085 | 0 | 0 | 0 | 0 | 12519.3852 | 32572.8721 | 22231.6545 | 99424.8994 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7649843.071 | 25032140.4547 | 749.8942 | 0.0012347 | 6195634.2713 | 20273616.8369 | 126306.3848 | 413305.1013
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055572 | 0.00030868 | 4 | 6195541.5645 | 20273311.6199 | 126304.4949 | 413298.8791 | 25.2355 | 0.41703 | 17.6775 | 14515.618 | 0 | 17585.6956 | 0 | 0 | 0 | 0 | 12519.5123 | 32573.2029 | 22231.8803 | 99425.9091 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7649844.0807 | 25032141.4643 | 1000 | 0.0012347 | 6195541.5645 | 20273311.6199 | 126304.4949 | 413298.8791
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.055572 | 0.00030868 | 4 | 6195515.6053 | 20273226.1548 | 126303.9657 | 413297.1367 | 25.2356 | 0.41703 | 17.6644 | 14515.6569 | 0 | 17585.748 | 0 | 0 | 0 | 0 | 12519.5479 | 32573.2955 | 22231.9435 | 99426.1918 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7649844.3634 | 25032141.747 | 1333.5214 | 0.0012347 | 6195515.6053 | 20273226.1548 | 126303.9657 | 413297.1367
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8 | 0.27173 | 0.0017576 | 4 | 1124498.1527 | 3596990.8788 | 22924.4158 | 73329.5244 | 26.4642 | 0.60116 | 18.1375 | 46881.012 | 0 | 67772.2281 | 0 | 0 | 0 | 0 | 44714.7636 | 116338.6427 | 79403.5141 | 355110.1604 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7905528.3321 | 25287825.7157 | 1778.2794 | 0.0070303 | 1124498.1527 | 3596990.8788 | 22924.4158 | 73329.5244
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8185 | 0.42812 | 0.0027511 | 4 | 731323.0149 | 2310920.9929 | 14909.0088 | 47111.2502 | 26.5564 | 0.61509 | 27.04 | 63806.8498 | 0 | 96737.3327 | 0 | 0 | 0 | 0 | 62612.2312 | 162904.182 | 111185.4516 | 497246.0474 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8047664.219 | 25429961.6027 | 2371.3737 | 0.011004 | 731323.0149 | 2310920.9929 | 14909.0088 | 47111.2502
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694923.2773 | 2192087.6072 | 14166.951 | 44688.6709 | 26.5651 | 0.6164 | 31.1814 | 66209.7852 | 0 | 100952.1699 | 0 | 0 | 0 | 0 | 65193.1625 | 169619.2358 | 115768.6138 | 517742.9672 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068161.1389 | 25450458.5225 | 3162.2777 | 0.01161 | 694923.2773 | 2192087.6072 | 14166.951 | 44688.6709
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694912.4962 | 2192052.5502 | 14166.7312 | 44687.9562 | 26.5651 | 0.61641 | 32.133 | 66210.4708 | 0 | 100953.309 | 0 | 0 | 0 | 0 | 65193.8741 | 169621.0873 | 115769.8775 | 517748.6187 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068166.7903 | 25450464.174 | 4216.965 | 0.01161 | 694912.4962 | 2192052.5502 | 14166.7312 | 44687.9562
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694905.5411 | 2192029.9344 | 14166.5894 | 44687.4952 | 26.5651 | 0.61641 | 32.0998 | 66210.9131 | 0 | 100954.0438 | 0 | 0 | 0 | 0 | 65194.3332 | 169622.2818 | 115770.6927 | 517752.2646 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068170.4363 | 25450467.8199 | 5623.4133 | 0.01161 | 694905.5411 | 2192029.9344 | 14166.5894 | 44687.4952
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694903.2839 | 2192022.5946 | 14166.5434 | 44687.3455 | 26.5651 | 0.61641 | 30.9922 | 66211.0567 | 0 | 100954.2823 | 0 | 0 | 0 | 0 | 65194.4822 | 169622.6694 | 115770.9573 | 517753.4479 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068171.6195 | 25450469.0032 | 7498.9421 | 0.01161 | 694903.2839 | 2192022.5946 | 14166.5434 | 44687.3455
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694904.31 | 2192025.9313 | 14166.5643 | 44687.4135 | 26.5651 | 0.61641 | 31.7546 | 66210.9914 | 0 | 100954.1739 | 0 | 0 | 0 | 0 | 65194.4145 | 169622.4932 | 115770.837 | 517752.91 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068171.0816 | 25450468.4653 | 10000 | 0.01161 | 694904.31 | 2192025.9313 | 14166.5643 | 44687.4135
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694907.0786 | 2192034.9337 | 14166.6207 | 44687.5971 | 26.5651 | 0.61641 | 31.8405 | 66210.8154 | 0 | 100953.8814 | 0 | 0 | 0 | 0 | 65194.2317 | 169622.0178 | 115770.5125 | 517751.4587 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068169.6303 | 25450467.014 | 13335.2143 | 0.01161 | 694907.0786 | 2192034.9337 | 14166.6207 | 44687.5971
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694910.4853 | 2192046.0115 | 14166.6902 | 44687.8229 | 26.5651 | 0.61641 | 30.9332 | 66210.5987 | 0 | 100953.5214 | 0 | 0 | 0 | 0 | 65194.0068 | 169621.4327 | 115770.1132 | 517749.6728 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068167.8445 | 25450465.2281 | 17782.7941 | 0.01161 | 694910.4853 | 2192046.0115 | 14166.6902 | 44687.8229
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694913.8781 | 2192057.0439 | 14166.7593 | 44688.0478 | 26.5651 | 0.6164 | 30.3438 | 66210.3829 | 0 | 100953.163 | 0 | 0 | 0 | 0 | 65193.7829 | 169620.85 | 115769.7155 | 517747.8943 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068166.0659 | 25450463.4496 | 23713.7371 | 0.01161 | 694913.8781 | 2192057.0439 | 14166.7593 | 44688.0478
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694916.9324 | 2192066.9756 | 14166.8216 | 44688.2503 | 26.5651 | 0.6164 | 32.1568 | 66210.1887 | 0 | 100952.8403 | 0 | 0 | 0 | 0 | 65193.5813 | 169620.3255 | 115769.3575 | 517746.2932 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068164.4648 | 25450461.8485 | 31622.7766 | 0.01161 | 694916.9324 | 2192066.9756 | 14166.8216 | 44688.2503
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029026 | 4 | 694919.5263 | 2192075.4102 | 14166.8745 | 44688.4222 | 26.5651 | 0.6164 | 32.6998 | 66210.0237 | 0 | 100952.5662 | 0 | 0 | 0 | 0 | 65193.4101 | 169619.88 | 115769.0535 | 517744.9335 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068163.1051 | 25450460.4888 | 42169.6503 | 0.01161 | 694919.5263 | 2192075.4102 | 14166.8745 | 44688.4222
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694921.6492 | 2192082.313 | 14166.9178 | 44688.563 | 26.5651 | 0.6164 | 30.8163 | 66209.8887 | 0 | 100952.3419 | 0 | 0 | 0 | 0 | 65193.27 | 169619.5154 | 115768.8046 | 517743.8207 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068161.9923 | 25450459.376 | 56234.1325 | 0.01161 | 694921.6492 | 2192082.313 | 14166.9178 | 44688.563
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694923.3441 | 2192087.8244 | 14166.9523 | 44688.6753 | 26.5651 | 0.6164 | 32.6774 | 66209.7809 | 0 | 100952.1629 | 0 | 0 | 0 | 0 | 65193.1581 | 169619.2244 | 115768.606 | 517742.9322 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068161.1039 | 25450458.4875 | 74989.4209 | 0.01161 | 694923.3441 | 2192087.8244 | 14166.9523 | 44688.6753
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694924.6743 | 2192092.1498 | 14166.9794 | 44688.7635 | 26.565 | 0.6164 | 32.625 | 66209.6963 | 0 | 100952.0223 | 0 | 0 | 0 | 0 | 65193.0703 | 169618.9959 | 115768.4501 | 517742.235 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068160.4066 | 25450457.7902 | 100000 | 0.01161 | 694924.6743 | 2192092.1498 | 14166.9794 | 44688.7635
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694925.7056 | 2192095.5033 | 14167.0005 | 44688.8319 | 26.565 | 0.6164 | 31.3698 | 66209.6308 | 0 | 100951.9134 | 0 | 0 | 0 | 0 | 65193.0022 | 169618.8188 | 115768.3292 | 517741.6943 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068159.866 | 25450457.2496 | 133352.1432 | 0.01161 | 694925.7056 | 2192095.5033 | 14167.0005 | 44688.8319
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694926.4983 | 2192098.0809 | 14167.0166 | 44688.8844 | 26.565 | 0.6164 | 31.6793 | 66209.5803 | 0 | 100951.8296 | 0 | 0 | 0 | 0 | 65192.9499 | 169618.6827 | 115768.2363 | 517741.2788 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068159.4505 | 25450456.8341 | 177827.941 | 0.01161 | 694926.4983 | 2192098.0809 | 14167.0166 | 44688.8844
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694927.1036 | 2192100.0491 | 14167.029 | 44688.9245 | 26.565 | 0.6164 | 31.6989 | 66209.5418 | 0 | 100951.7657 | 0 | 0 | 0 | 0 | 65192.9099 | 169618.5788 | 115768.1653 | 517740.9615 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068159.1332 | 25450456.5168 | 237137.3706 | 0.01161 | 694927.1036 | 2192100.0491 | 14167.029 | 44688.9245
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694927.5637 | 2192101.5452 | 14167.0383 | 44688.955 | 26.565 | 0.61639 | 31.6109 | 66209.5126 | 0 | 100951.7171 | 0 | 0 | 0 | 0 | 65192.8796 | 169618.4997 | 115768.1114 | 517740.7204 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.892 | 25450456.2756 | 316227.766 | 0.01161 | 694927.5637 | 2192101.5452 | 14167.0383 | 44688.955
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694927.9122 | 2192102.6786 | 14167.0455 | 44688.9781 | 26.565 | 0.61639 | 31.9912 | 66209.4904 | 0 | 100951.6803 | 0 | 0 | 0 | 0 | 65192.8566 | 169618.4399 | 115768.0705 | 517740.5377 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.7093 | 25450456.0929 | 421696.5034 | 0.01161 | 694927.9122 | 2192102.6786 | 14167.0455 | 44688.9781
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.1756 | 2192103.5349 | 14167.0508 | 44688.9956 | 26.565 | 0.61639 | 31.5981 | 66209.4737 | 0 | 100951.6524 | 0 | 0 | 0 | 0 | 65192.8392 | 169618.3947 | 115768.0397 | 517740.3996 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.5713 | 25450455.9549 | 562341.3252 | 0.01161 | 694928.1756 | 2192103.5349 | 14167.0508 | 44688.9956
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.3742 | 2192104.1807 | 14167.0549 | 44689.0088 | 26.565 | 0.61639 | 31.6086 | 66209.461 | 0 | 100951.6315 | 0 | 0 | 0 | 0 | 65192.8261 | 169618.3606 | 115768.0164 | 517740.2955 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.4672 | 25450455.8508 | 749894.2093 | 0.01161 | 694928.3742 | 2192104.1807 | 14167.0549 | 44689.0088
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.5237 | 2192104.667 | 14167.0579 | 44689.0187 | 26.565 | 0.61639 | 31.6938 | 66209.4515 | 0 | 100951.6157 | 0 | 0 | 0 | 0 | 65192.8162 | 169618.3349 | 115767.9989 | 517740.2171 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.3888 | 25450455.7724 | 1000000 | 0.01161 | 694928.5237 | 2192104.667 | 14167.0579 | 44689.0187
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.6362 | 2192105.0328 | 14167.0602 | 44689.0261 | 26.565 | 0.61639 | 33.1046 | 66209.4444 | 0 | 100951.6038 | 0 | 0 | 0 | 0 | 65192.8088 | 169618.3156 | 115767.9857 | 517740.1582 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.3298 | 25450455.7134 | 1333521.4322 | 0.01161 | 694928.6362 | 2192105.0328 | 14167.0602 | 44689.0261
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.7208 | 2192105.3078 | 14167.0619 | 44689.0317 | 26.565 | 0.61639 | 30.4901 | 66209.439 | 0 | 100951.5948 | 0 | 0 | 0 | 0 | 65192.8032 | 169618.301 | 115767.9758 | 517740.1138 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.2855 | 25450455.6691 | 1778279.41 | 0.01161 | 694928.7208 | 2192105.3078 | 14167.0619 | 44689.0317
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.7843 | 2192105.5143 | 14167.0632 | 44689.036 | 26.565 | 0.61639 | 29.7568 | 66209.435 | 0 | 100951.5881 | 0 | 0 | 0 | 0 | 65192.799 | 169618.2901 | 115767.9683 | 517740.0805 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.2522 | 25450455.6358 | 2371373.7057 | 0.01161 | 694928.7843 | 2192105.5143 | 14167.0632 | 44689.036
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.832 | 2192105.6693 | 14167.0642 | 44689.0391 | 26.565 | 0.61639 | 31.9551 | 66209.4319 | 0 | 100951.5831 | 0 | 0 | 0 | 0 | 65192.7959 | 169618.2819 | 115767.9627 | 517740.0555 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.2272 | 25450455.6108 | 3162277.6602 | 0.01161 | 694928.832 | 2192105.6693 | 14167.0642 | 44689.0391
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.8678 | 2192105.7858 | 14167.0649 | 44689.0415 | 26.565 | 0.61639 | 31.8655 | 66209.4297 | 0 | 100951.5793 | 0 | 0 | 0 | 0 | 65192.7935 | 169618.2758 | 115767.9585 | 517740.0368 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.2084 | 25450455.592 | 4216965.0343 | 0.01161 | 694928.8678 | 2192105.7858 | 14167.0649 | 44689.0415
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.8947 | 2192105.8732 | 14167.0655 | 44689.0433 | 26.565 | 0.61639 | 30.4749 | 66209.4279 | 0 | 100951.5765 | 0 | 0 | 0 | 0 | 65192.7917 | 169618.2712 | 115767.9554 | 517740.0227 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.1943 | 25450455.578 | 5623413.2519 | 0.01161 | 694928.8947 | 2192105.8732 | 14167.0655 | 44689.0433
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.9148 | 2192105.9388 | 14167.0659 | 44689.0446 | 26.565 | 0.61639 | 31.7812 | 66209.4267 | 0 | 100951.5743 | 0 | 0 | 0 | 0 | 65192.7904 | 169618.2677 | 115767.953 | 517740.0121 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.1838 | 25450455.5674 | 7498942.0933 | 0.01161 | 694928.9148 | 2192105.9388 | 14167.0659 | 44689.0446
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 0.45198 | 0.0029025 | 4 | 694928.93 | 2192105.9879 | 14167.0662 | 44689.0456 | 26.565 | 0.61639 | 31.757 | 66209.4257 | 0 | 100951.5727 | 0 | 0 | 0 | 0 | 65192.7894 | 169618.2651 | 115767.9512 | 517740.0042 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8068158.1758 | 25450455.5595 | 10000000 | 0.01161 | 694928.93 | 2192105.9879 | 14167.0662 | 44689.0456
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.1925 | [19 empty] | 100 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.44303 | -0.0013461 | 5.275e-05 | 4 | 37708637.1587 | 123446261.945 | 768741.5732 | 2516619.0232 | 24.2286 | 0.27159 | 28.9529 | 4402.0143 | 0 | 4340.3499 | 0 | 0 | 0 | 0 | 3409.5221 | 8870.877 | 6054.5559 | 27077.3192 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 7956534.5394 | 26047200.8785 | 133.3521 | 0.000211 | 37708637.1587 | 123446261.945 | 768741.5732 | 2516619.0232
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6088 | 0.0057254 | 0.00011908 | 4 | 16749626.7411 | 54730670.4899 | 341463.7967 | 1115758.7466 | 25.2423 | 0.41953 | 24.8789 | 7545.1871 | 0 | 8120.3627 | 0 | 0 | 0 | 0 | 6109.5644 | 15895.8333 | 10849.2329 | 48520.1804 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 7977977.4005 | 26068643.7396 | 177.8279 | 0.00047631 | 16749626.7411 | 54730670.4899 | 341463.7967 | 1115758.7466
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81347 | 0.015389 | 0.00021226 | 4 | 9425713.2351 | 30733148.8496 | 192155.9135 | 626536.809 | 26.0008 | 0.53229 | 23.2108 | 11050.8391 | 0 | 12603.1505 | 0 | 0 | 0 | 0 | 9225.0559 | 24001.7033 | 16381.6557 | 73262.4045 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8002719.6246 | 26093385.9637 | 237.1374 | 0.00084903 | 9425713.2351 | 30733148.8496 | 192155.9135 | 626536.809
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0887 | 0.029047 | 0.00039352 | 4 | 5109674.6714 | 16602644.3665 | 104167.6295 | 338467.3622 | 27.0281 | 0.68822 | 31.3078 | 16593.7154 | 0 | 20050.4169 | 0 | 0 | 0 | 0 | 14291.2116 | 37182.8011 | 25378.0258 | 113496.1708 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8042953.3909 | 26133619.73 | 316.2278 | 0.0015741 | 5109674.6714 | 16602644.3665 | 104167.6295 | 338467.3622
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4569 | 0.048051 | 0.00059781 | 4 | 3380399.9947 | 10945735.5731 | 68914.0262 | 223143.6249 | 27.4828 | 0.75828 | 96.9678 | 21979.9415 | 0 | 27725.3914 | 0 | 0 | 0 | 0 | 19385.0798 | 50436.0012 | 34423.6072 | 153950.0211 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8083407.2413 | 26174073.5804 | 421.6965 | 0.0023913 | 3380399.9947 | 10945735.5731 | 68914.0262 | 223143.6249
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.073628 | 0.00087472 | 4 | 2324513.1905 | 7494932.5172 | 47388.3455 | 152794.337 | 27.8345 | 0.81299 | 131.8779 | 28443.1693 | 0 | 37334.7187 | 0 | 0 | 0 | 0 | 25653.3763 | 66744.8229 | 45554.7131 | 203730.8004 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8133188.0205 | 26223854.3596 | 562.3413 | 0.0034989 | 2324513.1905 | 7494932.5172 | 47388.3455 | 152794.337
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.076719 | 0.0009082 | 4 | 2240396.7828 | 7220201.2508 | 45673.5188 | 147193.5685 | 27.8656 | 0.81784 | 136.1786 | 29178.8396 | 0 | 38452.3384 | 0 | 0 | 0 | 0 | 26376.1594 | 68625.3563 | 46838.2158 | 209470.9095 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8138928.1296 | 26229594.4687 | 749.8942 | 0.0036328 | 2240396.7828 | 7220201.2508 | 45673.5188 | 147193.5685
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.16571 | 0.0012843 | 4 | 1628233.3136 | 5149795.329 | 33193.7384 | 104985.5434 | 28.7081 | 0.95137 | 27.374 | 51063.0912 | 0 | 73275.6066 | 0 | 0 | 0 | 16096.4618 | 54769.7123 | 142499.5565 | 97258.8754 | 434963.3038 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8364420.524 | 26455086.8631 | 1000 | 0.0051371 | 1628233.3136 | 5149795.329 | 33193.7384 | 104985.5434
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.1675 | 0.0020643 | 4 | 1006938.7843 | 3197813.3898 | 20527.8091 | 65191.7513 | 28.7083 | 0.9514 | 27.8338 | 51064.3592 | 0 | 73277.6873 | 0 | 0 | 0 | 0 | 48493.3981 | 126169.8745 | 86113.5319 | 385118.8509 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8314576.0711 | 26405242.4102 | 1333.5214 | 0.0082573 | 1006938.7843 | 3197813.3898 | 20527.8091 | 65191.7513
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622074.0458 | 1947186.0441 | 12681.8208 | 39696.0213 | 28.9009 | 0.98205 | 30.3745 | 72293.226 | 0 | 109548.2193 | 0 | 0 | 0 | 0 | 70918.1637 | 184514.5146 | 125934.9476 | 563209.0711 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492666.2913 | 26583332.6304 | 1778.2794 | 0.013652 | 622074.0458 | 1947186.0441 | 12681.8208 | 39696.0213
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622071.1469 | 1947176.6461 | 12681.7617 | 39695.8297 | 28.9009 | 0.98206 | 30.5706 | 72293.4703 | 0 | 109548.6454 | 0 | 0 | 0 | 0 | 70918.4251 | 184515.1948 | 125935.4118 | 563211.1474 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492668.3676 | 26583334.7067 | 2371.3737 | 0.013652 | 622071.1469 | 1947176.6461 | 12681.7617 | 39695.8297
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622067.9007 | 1947166.1223 | 12681.6956 | 39695.6151 | 28.9009 | 0.98206 | 28.8731 | 72293.7439 | 0 | 109549.1225 | 0 | 0 | 0 | 0 | 70918.7179 | 184515.9565 | 125935.9317 | 563213.4724 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492670.6926 | 26583337.0317 | 3162.2777 | 0.013652 | 622067.9007 | 1947166.1223 | 12681.6956 | 39695.6151
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622066.6528 | 1947162.0769 | 12681.6701 | 39695.5327 | 28.9009 | 0.98206 | 27.9711 | 72293.849 | 0 | 109549.3059 | 0 | 0 | 0 | 0 | 70918.8304 | 184516.2493 | 125936.1316 | 563214.3662 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492671.5864 | 26583337.9255 | 4216.965 | 0.013652 | 622066.6528 | 1947162.0769 | 12681.6701 | 39695.5327
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622067.2074 | 1947163.8748 | 12681.6814 | 39695.5693 | 28.9009 | 0.98206 | 29.571 | 72293.8023 | 0 | 109549.2244 | 0 | 0 | 0 | 0 | 70918.7804 | 184516.1192 | 125936.0428 | 563213.969 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492671.1892 | 26583337.5283 | 5623.4133 | 0.013652 | 622067.2074 | 1947163.8748 | 12681.6814 | 39695.5693
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622068.8314 | 1947169.1397 | 12681.7145 | 39695.6767 | 28.9009 | 0.98206 | 29.5833 | 72293.6654 | 0 | 109548.9857 | 0 | 0 | 0 | 0 | 70918.6339 | 184515.7381 | 125935.7827 | 563212.8058 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492670.026 | 26583336.3651 | 7498.9421 | 0.013652 | 622068.8314 | 1947169.1397 | 12681.7145 | 39695.6767
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622070.8925 | 1947175.8213 | 12681.7566 | 39695.8129 | 28.9009 | 0.98206 | 30.5597 | 72293.4917 | 0 | 109548.6828 | 0 | 0 | 0 | 0 | 70918.4481 | 184515.2545 | 125935.4526 | 563211.3296 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492668.5498 | 26583334.8889 | 10000 | 0.013652 | 622070.8925 | 1947175.8213 | 12681.7566 | 39695.8129
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.0034131 | 4 | 622072.9837 | 1947182.6008 | 12681.7992 | 39695.9511 | 28.9009 | 0.98206 | 27.5183 | 72293.3155 | 0 | 109548.3754 | 0 | 0 | 0 | 0 | 70918.2595 | 184514.7638 | 125935.1177 | 563209.8319 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492667.052 | 26583333.3911 | 13335.2143 | 0.013652 | 622072.9837 | 1947182.6008 | 12681.7992 | 39695.9511
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622074.8897 | 1947188.78 | 12681.838 | 39696.077 | 28.9009 | 0.98205 | 30.1559 | 72293.1549 | 0 | 109548.0953 | 0 | 0 | 0 | 0 | 70918.0876 | 184514.3165 | 125934.8124 | 563208.4667 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492665.6869 | 26583332.026 | 17782.7941 | 0.013652 | 622074.8897 | 1947188.78 | 12681.838 | 39696.077
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622076.5223 | 1947194.0727 | 12681.8713 | 39696.1849 | 28.9009 | 0.98205 | 28.6395 | 72293.0173 | 0 | 109547.8554 | 0 | 0 | 0 | 0 | 70917.9403 | 184513.9335 | 125934.551 | 563207.2974 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492664.5176 | 26583330.8567 | 23713.7371 | 0.013652 | 622076.5223 | 1947194.0727 | 12681.8713 | 39696.1849
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622077.8666 | 1947198.4308 | 12681.8987 | 39696.2738 | 28.9009 | 0.98205 | 29.0264 | 72292.904 | 0 | 109547.6578 | 0 | 0 | 0 | 0 | 70917.8191 | 184513.6181 | 125934.3357 | 563206.3346 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492663.5548 | 26583329.8939 | 31622.7766 | 0.013652 | 622077.8666 | 1947198.4308 | 12681.8987 | 39696.2738
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622078.9447 | 1947201.926 | 12681.9207 | 39696.345 | 28.9009 | 0.98205 | 28.951 | 72292.8131 | 0 | 109547.4994 | 0 | 0 | 0 | 0 | 70917.7219 | 184513.3651 | 125934.163 | 563205.5625 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492662.7826 | 26583329.1217 | 42169.6503 | 0.013652 | 622078.9447 | 1947201.926 | 12681.9207 | 39696.345
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622079.7933 | 1947204.6771 | 12681.938 | 39696.4011 | 28.9008 | 0.98205 | 29.3548 | 72292.7416 | 0 | 109547.3746 | 0 | 0 | 0 | 0 | 70917.6453 | 184513.166 | 125934.0271 | 563204.9547 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492662.1748 | 26583328.5139 | 56234.1325 | 0.013652 | 622079.7933 | 1947204.6771 | 12681.938 | 39696.4011
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622080.453 | 1947206.8156 | 12681.9515 | 39696.4447 | 28.9008 | 0.98205 | 28.739 | 72292.686 | 0 | 109547.2777 | 0 | 0 | 0 | 0 | 70917.5859 | 184513.0112 | 125933.9215 | 563204.4823 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492661.7024 | 26583328.0415 | 74989.4209 | 0.013652 | 622080.453 | 1947206.8156 | 12681.9515 | 39696.4447
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622080.9608 | 1947208.4618 | 12681.9618 | 39696.4783 | 28.9008 | 0.98205 | 28.2517 | 72292.6432 | 0 | 109547.2031 | 0 | 0 | 0 | 0 | 70917.5401 | 184512.892 | 125933.8402 | 563204.1185 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492661.3387 | 26583327.6778 | 100000 | 0.013652 | 622080.9608 | 1947208.4618 | 12681.9618 | 39696.4783
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622081.3492 | 1947209.721 | 12681.9697 | 39696.504 | 28.9008 | 0.98205 | 28.792 | 72292.6105 | 0 | 109547.146 | 0 | 0 | 0 | 0 | 70917.505 | 184512.8009 | 125933.778 | 563203.8404 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492661.0605 | 26583327.3996 | 133352.1432 | 0.013652 | 622081.3492 | 1947209.721 | 12681.9697 | 39696.504
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622081.6445 | 1947210.6785 | 12681.9758 | 39696.5235 | 28.9008 | 0.98204 | 30.1824 | 72292.5856 | 0 | 109547.1026 | 0 | 0 | 0 | 0 | 70917.4784 | 184512.7316 | 125933.7307 | 563203.6288 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.849 | 26583327.1881 | 177827.941 | 0.013652 | 622081.6445 | 1947210.6785 | 12681.9758 | 39696.5235
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622081.8685 | 1947211.4046 | 12681.9803 | 39696.5383 | 28.9008 | 0.98204 | 29.5029 | 72292.5667 | 0 | 109547.0697 | 0 | 0 | 0 | 0 | 70917.4582 | 184512.679 | 125933.6948 | 563203.4684 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.6886 | 26583327.0277 | 237137.3706 | 0.013652 | 622081.8685 | 1947211.4046 | 12681.9803 | 39696.5383
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.0371 | 1947211.9514 | 12681.9838 | 39696.5494 | 28.9008 | 0.98204 | 28.6302 | 72292.5525 | 0 | 109547.0449 | 0 | 0 | 0 | 0 | 70917.443 | 184512.6395 | 125933.6678 | 563203.3477 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.5678 | 26583326.9069 | 316227.766 | 0.013652 | 622082.0371 | 1947211.9514 | 12681.9838 | 39696.5494
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.1655 | 1947212.3675 | 12681.9864 | 39696.5579 | 28.9008 | 0.98204 | 28.6082 | 72292.5417 | 0 | 109547.026 | 0 | 0 | 0 | 0 | 70917.4314 | 184512.6094 | 125933.6472 | 563203.2557 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.4759 | 26583326.815 | 421696.5034 | 0.013652 | 622082.1655 | 1947212.3675 | 12681.9864 | 39696.5579
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.2618 | 1947212.6798 | 12681.9883 | 39696.5643 | 28.9008 | 0.98204 | 29.1991 | 72292.5336 | 0 | 109547.0119 | 0 | 0 | 0 | 0 | 70917.4227 | 184512.5868 | 125933.6318 | 563203.1867 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.4069 | 26583326.746 | 562341.3252 | 0.013652 | 622082.2618 | 1947212.6798 | 12681.9883 | 39696.5643
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.3336 | 1947212.9123 | 12681.9898 | 39696.569 | 28.9008 | 0.98204 | 27.9951 | 72292.5275 | 0 | 109547.0013 | 0 | 0 | 0 | 0 | 70917.4163 | 184512.5699 | 125933.6203 | 563203.1354 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.3555 | 26583326.6946 | 749894.2093 | 0.013652 | 622082.3336 | 1947212.9123 | 12681.9898 | 39696.569
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.3886 | 1947213.0907 | 12681.9909 | 39696.5727 | 28.9008 | 0.98204 | 27.8392 | 72292.5229 | 0 | 109546.9932 | 0 | 0 | 0 | 0 | 70917.4113 | 184512.557 | 125933.6115 | 563203.096 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.3161 | 26583326.6552 | 1000000 | 0.013652 | 622082.3886 | 1947213.0907 | 12681.9909 | 39696.5727
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.4294 | 1947213.2231 | 12681.9918 | 39696.5754 | 28.9008 | 0.98204 | 28.6951 | 72292.5195 | 0 | 109546.9872 | 0 | 0 | 0 | 0 | 70917.4076 | 184512.5474 | 125933.605 | 563203.0667 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2869 | 26583326.626 | 1333521.4322 | 0.013652 | 622082.4294 | 1947213.2231 | 12681.9918 | 39696.5754
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.4602 | 1947213.3227 | 12681.9924 | 39696.5774 | 28.9008 | 0.98204 | 29.3568 | 72292.5169 | 0 | 109546.9827 | 0 | 0 | 0 | 0 | 70917.4048 | 184512.5402 | 125933.6001 | 563203.0447 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2649 | 26583326.604 | 1778279.41 | 0.013652 | 622082.4602 | 1947213.3227 | 12681.9924 | 39696.5774
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.4832 | 1947213.3974 | 12681.9928 | 39696.5789 | 28.9008 | 0.98204 | 29.1891 | 72292.5149 | 0 | 109546.9793 | 0 | 0 | 0 | 0 | 70917.4028 | 184512.5348 | 125933.5964 | 563203.0282 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2484 | 26583326.5875 | 2371373.7057 | 0.013652 | 622082.4832 | 1947213.3974 | 12681.9928 | 39696.5789
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.5005 | 1947213.4536 | 12681.9932 | 39696.5801 | 28.9008 | 0.98204 | 28.9191 | 72292.5135 | 0 | 109546.9768 | 0 | 0 | 0 | 0 | 70917.4012 | 184512.5308 | 125933.5936 | 563203.0158 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.236 | 26583326.5751 | 3162277.6602 | 0.013652 | 622082.5005 | 1947213.4536 | 12681.9932 | 39696.5801
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.5135 | 1947213.4955 | 12681.9935 | 39696.5809 | 28.9008 | 0.98204 | 28.3264 | 72292.5124 | 0 | 109546.9749 | 0 | 0 | 0 | 0 | 70917.4 | 184512.5277 | 125933.5915 | 563203.0065 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2267 | 26583326.5658 | 4216965.0343 | 0.013652 | 622082.5135 | 1947213.4955 | 12681.9935 | 39696.5809
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.5235 | 1947213.5282 | 12681.9937 | 39696.5816 | 28.9008 | 0.98204 | 27.0544 | 72292.5115 | 0 | 109546.9734 | 0 | 0 | 0 | 0 | 70917.3991 | 184512.5254 | 125933.5899 | 563202.9993 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2195 | 26583326.5586 | 5623413.2519 | 0.013652 | 622082.5235 | 1947213.5282 | 12681.9937 | 39696.5816
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.5305 | 1947213.5508 | 12681.9938 | 39696.582 | 28.9008 | 0.98204 | 29.1605 | 72292.5109 | 0 | 109546.9724 | 0 | 0 | 0 | 0 | 70917.3985 | 184512.5237 | 125933.5888 | 563202.9943 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2145 | 26583326.5536 | 7498942.0933 | 0.013652 | 622082.5305 | 1947213.5508 | 12681.9938 | 39696.582
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 0.28355 | 0.003413 | 4 | 622082.536 | 1947213.5686 | 12681.9939 | 39696.5824 | 28.9008 | 0.98204 | 28.878 | 72292.5105 | 0 | 109546.9716 | 0 | 0 | 0 | 0 | 70917.398 | 184512.5224 | 125933.5879 | 563202.9904 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8492660.2105 | 26583326.5496 | 10000000 | 0.013652 | 622082.536 | 1947213.5686 | 12681.9939 | 39696.5824
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.0084204 | 2.2224e-05 | 4 | 93684669.4402 | 305308140.2861 | 1909888.7044 | 6224119.3996 | 23.6956 | 0.19748 | 11.736 | 2414.6708 | 0 | 2099.1765 | 0 | 0 | 0 | 0 | 1760.4005 | 4580.2009 | 3126.0812 | 13980.53 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8328336.8896 | 27141143.3977 | 100 | 8.8898e-05 | 93684669.4402 | 305308140.2861 | 1909888.7044 | 6224119.3996
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.40413 | -0.0042757 | 9.4671e-05 | 4 | 22062391.3555 | 71742081.3497 | 449771.6894 | 1462559.3667 | 25.6785 | 0.48551 | 25.3131 | 6387.5668 | 0 | 6615.913 | 0 | 0 | 0 | 0 | 5071.3571 | 13194.631 | 9005.6068 | 40275.0748 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8354631.4344 | 27167437.9425 | 133.3521 | 0.00037868 | 22062391.3555 | 71742081.3497 | 449771.6894 | 1462559.3667
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.55509 | 0.0018606 | 0.00019081 | 4 | 10980219.0443 | 35628619.2348 | 223846.6171 | 726337.5944 | 26.8478 | 0.66123 | 27.3401 | 10134.9247 | 0 | 11257.5724 | 0 | 0 | 0 | 0 | 8343.0739 | 21706.9668 | 14815.4509 | 66257.9887 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8380614.3482 | 27193420.8563 | 177.8279 | 0.00076325 | 10980219.0443 | 35628619.2348 | 223846.6171 | 726337.5944
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75512 | 0.011143 | 0.00036052 | 4 | 5841820.8915 | 18887308.7694 | 119093.4205 | 385043.3362 | 28.2013 | 0.87288 | 20.3406 | 15819.1919 | 0 | 18705.4659 | 0 | 0 | 0 | 1020.5578 | 13862.6341 | 36067.7303 | 24616.967 | 110092.5469 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8424448.9065 | 27237255.4146 | 237.1374 | 0.0014421 | 5841820.8915 | 18887308.7694 | 119093.4205 | 385043.3362
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.99609 | 0.02344 | 0.00057543 | 4 | 3676060.658 | 11849498.8902 | 74941.4688 | 241568.0625 | 28.8461 | 0.97446 | 33.9778 | 21157.0365 | 0 | 26250.8135 | 0 | 0 | 0 | 0 | 18489.0615 | 48104.7454 | 32832.4772 | 146834.1342 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8461190.4937 | 27273997.0018 | 316.2278 | 0.0023017 | 3676060.658 | 11849498.8902 | 74941.4688 | 241568.0625
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.040836 | 0.00085727 | 4 | 2482585.9874 | 7968821.2859 | 50610.8733 | 162455.2005 | 29.3656 | 1.0576 | 33.4454 | 27872.832 | 0 | 36267.8029 | 0 | 0 | 0 | 0 | 25014.8476 | 65083.5023 | 44420.8277 | 198659.8126 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8513016.1721 | 27325822.6802 | 421.6965 | 0.0034291 | 2482585.9874 | 7968821.2859 | 50610.8733 | 162455.2005
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.323 | 0.040727 | 0.00085552 | 4 | 2487588.2731 | 7985079.1804 | 50712.8517 | 162786.6397 | 29.3632 | 1.0572 | 26.4924 | 27833.0845 | 0 | 36206.9964 | 0 | 0 | 0 | 0 | 24975.6316 | 64981.4701 | 44351.1886 | 198348.3711 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8512704.7307 | 27325511.2388 | 562.3413 | 0.0034221 | 2487588.2731 | 7985079.1804 | 50712.8517 | 162786.6397
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.323 | 0.040727 | 0.00085552 | 4 | 2487577.5395 | 7985044.2742 | 50712.6328 | 162785.9281 | 29.3632 | 1.0572 | 72.1315 | 27833.1725 | 0 | 36207.1342 | 0 | 0 | 0 | 0 | 24975.7196 | 64981.6993 | 44351.345 | 198349.0707 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8512705.4303 | 27325511.9383 | 749.8942 | 0.0034221 | 2487577.5395 | 7985044.2742 | 50712.6328 | 162785.9281
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1883 | 0.14354 | 0.001235 | 4 | 1841878.2927 | 5650072.9353 | 37549.1803 | 115184.3791 | 30.1204 | 1.1804 | 130.6481 | 80748.7055 | 0 | 172598.1898 | 0 | 0 | 0 | 0 | 98805.2892 | 257071.0947 | 175456.3044 | 784679.5835 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9099035.9431 | 27911842.4512 | 1000 | 0.0049401 | 1841878.2927 | 5650072.9353 | 37549.1803 | 115184.3791
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.20384 | 0.0020312 | 4 | 1142222.5853 | 3457693.6382 | 23285.7524 | 70489.7617 | 30.3162 | 1.2129 | 40.9951 | 99127.1366 | 0 | 212764.3079 | 0 | 0 | 0 | 0 | 121637.6634 | 316476.2488 | 216001.5427 | 966006.8994 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9280363.259 | 28093169.767 | 1333.5214 | 0.0081248 | 1142222.5853 | 3457693.6382 | 23285.7524 | 70489.7617
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773888.4645 | 2306322.9407 | 15776.7631 | 47017.5127 | 30.4578 | 1.2365 | 41.5184 | 120945.9706 | 0 | 262045.6185 | 0 | 0 | 0 | 0 | 149366.7198 | 388621.5655 | 265242.2038 | 1186222.0781 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500578.4377 | 28313384.9458 | 1778.2794 | 0.012276 | 773888.4645 | 2306322.9407 | 15776.7631 | 47017.5127
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773880.9521 | 2306300.7974 | 15776.61 | 47017.0613 | 30.4578 | 1.2365 | 41.4656 | 120945.9585 | 0 | 262045.1401 | 0 | 0 | 0 | 0 | 149366.5284 | 388621.0677 | 265241.8641 | 1186220.5588 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500576.9184 | 28313383.4265 | 2371.3737 | 0.012277 | 773880.9521 | 2306300.7974 | 15776.61 | 47017.0613
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030692 | 4 | 773869.7847 | 2306267.8809 | 15776.3823 | 47016.3902 | 30.4578 | 1.2365 | 40.9411 | 120945.9405 | 0 | 262044.4288 | 0 | 0 | 0 | 0 | 149366.244 | 388620.3277 | 265241.359 | 1186218.3 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500574.6595 | 28313381.1676 | 3162.2777 | 0.012277 | 773869.7847 | 2306267.8809 | 15776.3823 | 47016.3902
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030692 | 4 | 773864.2239 | 2306251.4901 | 15776.2689 | 47016.0561 | 30.4578 | 1.2365 | 39.4839 | 120945.9315 | 0 | 262044.0747 | 0 | 0 | 0 | 0 | 149366.1024 | 388619.9592 | 265241.1075 | 1186217.1753 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500573.5349 | 28313380.0429 | 4216.965 | 0.012277 | 773864.2239 | 2306251.4901 | 15776.2689 | 47016.0561
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030692 | 4 | 773864.3542 | 2306251.8744 | 15776.2716 | 47016.0639 | 30.4578 | 1.2365 | 42.0013 | 120945.9317 | 0 | 262044.0831 | 0 | 0 | 0 | 0 | 149366.1058 | 388619.968 | 265241.1135 | 1186217.2021 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500573.5616 | 28313380.0697 | 5623.4133 | 0.012277 | 773864.3542 | 2306251.8744 | 15776.2716 | 47016.0639
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030692 | 4 | 773868.09 | 2306262.8856 | 15776.3477 | 47016.2884 | 30.4578 | 1.2365 | 42.8512 | 120945.9378 | 0 | 262044.3211 | 0 | 0 | 0 | 0 | 149366.201 | 388620.2157 | 265241.2826 | 1186217.9583 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500574.3178 | 28313380.8259 | 7498.9421 | 0.012277 | 773868.09 | 2306262.8856 | 15776.3477 | 47016.2884
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030692 | 4 | 773873.4758 | 2306278.7604 | 15776.4575 | 47016.612 | 30.4578 | 1.2365 | 40.7822 | 120945.9465 | 0 | 262044.6643 | 0 | 0 | 0 | 0 | 149366.3382 | 388620.5728 | 265241.5263 | 1186219.0482 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500575.4078 | 28313381.9159 | 10000 | 0.012277 | 773873.4758 | 2306278.7604 | 15776.4575 | 47016.612
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773879.2029 | 2306295.6413 | 15776.5743 | 47016.9561 | 30.4578 | 1.2365 | 42.7006 | 120945.9558 | 0 | 262045.0292 | 0 | 0 | 0 | 0 | 149366.4842 | 388620.9525 | 265241.7855 | 1186220.2072 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500576.5667 | 28313383.0748 | 13335.2143 | 0.012277 | 773879.2029 | 2306295.6413 | 15776.5743 | 47016.9561
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773884.5488 | 2306311.3985 | 15776.6833 | 47017.2774 | 30.4578 | 1.2365 | 42.6095 | 120945.9645 | 0 | 262045.3698 | 0 | 0 | 0 | 0 | 149366.6204 | 388621.3069 | 265242.0273 | 1186221.2889 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500577.6484 | 28313384.1565 | 17782.7941 | 0.012276 | 773884.5488 | 2306311.3985 | 15776.6833 | 47017.2774
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773889.1925 | 2306325.0859 | 15776.778 | 47017.5564 | 30.4578 | 1.2365 | 41.4706 | 120945.972 | 0 | 262045.6656 | 0 | 0 | 0 | 0 | 149366.7387 | 388621.6147 | 265242.2374 | 1186222.2285 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500578.588 | 28313385.0961 | 23713.7371 | 0.012276 | 773889.1925 | 2306325.0859 | 15776.778 | 47017.5564
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773893.0504 | 2306336.4573 | 15776.8566 | 47017.7882 | 30.4578 | 1.2365 | 42.4135 | 120945.9783 | 0 | 262045.9114 | 0 | 0 | 0 | 0 | 149366.837 | 388621.8704 | 265242.412 | 1186223.0091 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500579.3686 | 28313385.8767 | 31622.7766 | 0.012276 | 773893.0504 | 2306336.4573 | 15776.8566 | 47017.7882
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773896.1627 | 2306345.6309 | 15776.92 | 47017.9752 | 30.4578 | 1.2365 | 43.0298 | 120945.9833 | 0 | 262046.1097 | 0 | 0 | 0 | 0 | 149366.9163 | 388622.0767 | 265242.5528 | 1186223.6388 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500579.9983 | 28313386.5064 | 42169.6503 | 0.012276 | 773896.1627 | 2306345.6309 | 15776.92 | 47017.9752
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773898.6232 | 2306352.8835 | 15776.9702 | 47018.1231 | 30.4578 | 1.2365 | 44.4442 | 120945.9873 | 0 | 262046.2664 | 0 | 0 | 0 | 0 | 149366.9789 | 388622.2398 | 265242.6641 | 1186224.1366 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500580.4961 | 28313387.0042 | 56234.1325 | 0.012276 | 773898.6232 | 2306352.8835 | 15776.9702 | 47018.1231
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773900.5411 | 2306358.5364 | 15777.0093 | 47018.2383 | 30.4578 | 1.2365 | 42.8418 | 120945.9904 | 0 | 262046.3886 | 0 | 0 | 0 | 0 | 149367.0278 | 388622.367 | 265242.7508 | 1186224.5246 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500580.8842 | 28313387.3922 | 74989.4209 | 0.012276 | 773900.5411 | 2306358.5364 | 15777.0093 | 47018.2383
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.0030691 | 4 | 773902.0207 | 2306362.8977 | 15777.0395 | 47018.3273 | 30.4578 | 1.2365 | 43.2261 | 120945.9928 | 0 | 262046.4828 | 0 | 0 | 0 | 0 | 149367.0655 | 388622.465 | 265242.8178 | 1186224.824 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.1835 | 28313387.6916 | 100000 | 0.012276 | 773902.0207 | 2306362.8977 | 15777.0395 | 47018.3273
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773903.1539 | 2306366.2377 | 15777.0626 | 47018.3953 | 30.4578 | 1.2365 | 42.4428 | 120945.9946 | 0 | 262046.555 | 0 | 0 | 0 | 0 | 149367.0944 | 388622.5401 | 265242.869 | 1186225.0532 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.4128 | 28313387.9209 | 133352.1432 | 0.012276 | 773903.1539 | 2306366.2377 | 15777.0626 | 47018.3953
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773904.017 | 2306368.7818 | 15777.0802 | 47018.4472 | 30.4578 | 1.2365 | 45.587 | 120945.996 | 0 | 262046.61 | 0 | 0 | 0 | 0 | 149367.1164 | 388622.5974 | 265242.9081 | 1186225.2278 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.5874 | 28313388.0955 | 177827.941 | 0.012276 | 773904.017 | 2306368.7818 | 15777.0802 | 47018.4472
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773904.6718 | 2306370.7119 | 15777.0935 | 47018.4866 | 30.4578 | 1.2365 | 42.8957 | 120945.9971 | 0 | 262046.6517 | 0 | 0 | 0 | 0 | 149367.133 | 388622.6408 | 265242.9377 | 1186225.3603 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.7199 | 28313388.228 | 237137.3706 | 0.012276 | 773904.6718 | 2306370.7119 | 15777.0935 | 47018.4866
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773905.1671 | 2306372.1719 | 15777.1036 | 47018.5163 | 30.4578 | 1.2365 | 43.6828 | 120945.9979 | 0 | 262046.6833 | 0 | 0 | 0 | 0 | 149367.1457 | 388622.6736 | 265242.9601 | 1186225.4605 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.8201 | 28313388.3282 | 316227.766 | 0.012276 | 773905.1671 | 2306372.1719 | 15777.1036 | 47018.5163
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773905.541 | 2306373.2738 | 15777.1112 | 47018.5388 | 30.4578 | 1.2365 | 41.9739 | 120945.9985 | 0 | 262046.7071 | 0 | 0 | 0 | 0 | 149367.1552 | 388622.6984 | 265242.977 | 1186225.5362 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.8957 | 28313388.4038 | 421696.5034 | 0.012276 | 773905.541 | 2306373.2738 | 15777.1112 | 47018.5388
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773905.8227 | 2306374.1042 | 15777.117 | 47018.5557 | 30.4578 | 1.2365 | 41.0453 | 120945.999 | 0 | 262046.725 | 0 | 0 | 0 | 0 | 149367.1624 | 388622.717 | 265242.9898 | 1186225.5932 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.9527 | 28313388.4608 | 562341.3252 | 0.012276 | 773905.8227 | 2306374.1042 | 15777.117 | 47018.5557
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.0347 | 2306374.7291 | 15777.1213 | 47018.5685 | 30.4578 | 1.2365 | 43.7519 | 120945.9993 | 0 | 262046.7385 | 0 | 0 | 0 | 0 | 149367.1678 | 388622.7311 | 265242.9994 | 1186225.6361 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500581.9956 | 28313388.5037 | 749894.2093 | 0.012276 | 773906.0347 | 2306374.7291 | 15777.1213 | 47018.5685
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.1941 | 2306375.1989 | 15777.1246 | 47018.578 | 30.4578 | 1.2365 | 44.2535 | 120945.9996 | 0 | 262046.7487 | 0 | 0 | 0 | 0 | 149367.1718 | 388622.7417 | 265243.0066 | 1186225.6683 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.0279 | 28313388.536 | 1000000 | 0.012276 | 773906.1941 | 2306375.1989 | 15777.1246 | 47018.578
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.3139 | 2306375.552 | 15777.127 | 47018.5852 | 30.4578 | 1.2365 | 44.2926 | 120945.9998 | 0 | 262046.7563 | 0 | 0 | 0 | 0 | 149367.1749 | 388622.7496 | 265243.012 | 1186225.6925 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.0521 | 28313388.5602 | 1333521.4322 | 0.012276 | 773906.3139 | 2306375.552 | 15777.127 | 47018.5852
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.4039 | 2306375.8172 | 15777.1288 | 47018.5906 | 30.4578 | 1.2365 | 44.3975 | 120945.9999 | 0 | 262046.762 | 0 | 0 | 0 | 0 | 149367.1772 | 388622.7556 | 265243.0161 | 1186225.7107 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.0703 | 28313388.5784 | 1778279.41 | 0.012276 | 773906.4039 | 2306375.8172 | 15777.1288 | 47018.5906
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.4714 | 2306376.0163 | 15777.1302 | 47018.5947 | 30.4578 | 1.2365 | 46.2014 | 120946 | 0 | 262046.7664 | 0 | 0 | 0 | 0 | 149367.1789 | 388622.76 | 265243.0191 | 1186225.7244 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.084 | 28313388.5921 | 2371373.7057 | 0.012276 | 773906.4714 | 2306376.0163 | 15777.1302 | 47018.5947
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.5221 | 2306376.1657 | 15777.1312 | 47018.5977 | 30.4578 | 1.2365 | 40.9935 | 120946.0001 | 0 | 262046.7696 | 0 | 0 | 0 | 0 | 149367.1802 | 388622.7634 | 265243.0214 | 1186225.7347 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.0942 | 28313388.6023 | 3162277.6602 | 0.012276 | 773906.5221 | 2306376.1657 | 15777.1312 | 47018.5977
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.5601 | 2306376.2778 | 15777.132 | 47018.6 | 30.4578 | 1.2365 | 43.7573 | 120946.0002 | 0 | 262046.772 | 0 | 0 | 0 | 0 | 149367.1811 | 388622.7659 | 265243.0231 | 1186225.7424 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.1019 | 28313388.61 | 4216965.0343 | 0.012276 | 773906.5601 | 2306376.2778 | 15777.132 | 47018.6
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.5887 | 2306376.3619 | 15777.1326 | 47018.6017 | 30.4578 | 1.2365 | 42.9161 | 120946.0002 | 0 | 262046.7738 | 0 | 0 | 0 | 0 | 149367.1819 | 388622.7678 | 265243.0244 | 1186225.7481 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.1077 | 28313388.6158 | 5623413.2519 | 0.012276 | 773906.5887 | 2306376.3619 | 15777.1326 | 47018.6017
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.6101 | 2306376.425 | 15777.133 | 47018.603 | 30.4578 | 1.2365 | 44.1029 | 120946.0002 | 0 | 262046.7752 | 0 | 0 | 0 | 0 | 149367.1824 | 388622.7692 | 265243.0254 | 1186225.7525 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.112 | 28313388.6201 | 7498942.0933 | 0.012276 | 773906.6101 | 2306376.425 | 15777.133 | 47018.603
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 0.28317 | 0.003069 | 4 | 773906.6262 | 2306376.4724 | 15777.1334 | 47018.604 | 30.4578 | 1.2365 | 43.2556 | 120946.0003 | 0 | 262046.7762 | 0 | 0 | 0 | 0 | 149367.1828 | 388622.7703 | 265243.0261 | 1186225.7557 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9500582.1153 | 28313388.6234 | 10000000 | 0.012276 | 773906.6262 | 2306376.4724 | 15777.1334 | 47018.604
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.0092573 | 6.0854e-05 | 4 | 35856360.4697 | 116166290.1654 | 730980.4075 | 2368206.9516 | 24.8439 | 0.41445 | 12.353 | 4061.7309 | 0 | 3330.1353 | 0 | 0 | 0 | 0 | 2882.8278 | 7500.5265 | 5119.2635 | 22894.4839 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8728010.0737 | 28276727.9643 | 100 | 0.00024342 | 35856360.4697 | 116166290.1654 | 730980.4075 | 2368206.9516
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.36987 | -0.0066393 | 0.00012855 | 4 | 17026248.9983 | 55043794.7675 | 347103.1155 | 1122142.2086 | 26.7774 | 0.66879 | 31.8671 | 7687.487 | 0 | 7861.4443 | 0 | 0 | 0 | 537.7639 | 6273.8111 | 16323.1696 | 11140.8986 | 49824.5745 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8754940.1643 | 28303658.0549 | 133.3521 | 0.0005142 | 17026248.9983 | 55043794.7675 | 347103.1155 | 1122142.2086
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.49674 | -0.0018937 | 0.00024373 | 4 | 9007074.6597 | 29058821.9536 | 183621.3999 | 592403.3905 | 28.0507 | 0.85617 | 26.5655 | 11630.9051 | 0 | 12907.7805 | 0 | 0 | 0 | 0 | 9570.0874 | 24899.4042 | 16994.355 | 76002.5322 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8781118.122 | 28329836.0126 | 177.8279 | 0.00097491 | 9007074.6597 | 29058821.9536 | 183621.3999 | 592403.3905
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.68196 | 0.0064719 | 0.00042378 | 4 | 5204699.5083 | 16737144.0667 | 106104.8394 | 341209.3205 | 29.1354 | 1.0319 | 24.5485 | 17076.8011 | 0 | 20068.657 | 0 | 0 | 0 | 759.9442 | 14783.1069 | 38462.6117 | 26251.5228 | 117402.6437 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8822518.2335 | 28371236.1241 | 237.1374 | 0.0016951 | 5204699.5083 | 16737144.0667 | 106104.8394 | 341209.3205
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.018484 | 0.00069397 | 4 | 3195219.143 | 10237521.1224 | 65138.8641 | 208705.7154 | 29.9297 | 1.1693 | 30.3985 | 23503.8008 | 0 | 28787.4653 | 0 | 0 | 0 | 816.92 | 20712.1926 | 53888.8764 | 36780.2654 | 164489.5204 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8869605.1102 | 28418323.0008 | 316.2278 | 0.0027759 | 3195219.143 | 10237521.1224 | 65138.8641 | 208705.7154
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2236 | 0.035 | 0.0010796 | 4 | 2066449.478 | 6593335.1556 | 42127.3677 | 134414.0553 | 30.5349 | 1.2772 | 79.9156 | 31113.2066 | 0 | 39451.014 | 0 | 0 | 0 | 0 | 27520.046 | 71601.5147 | 48869.505 | 218555.2864 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 8923670.8762 | 28472388.7668 | 421.6965 | 0.0043184 | 2066449.478 | 6593335.1556 | 42127.3677 | 134414.0553
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.058831 | 0.0016136 | 4 | 1394426.9691 | 4423168.2249 | 28427.2799 | 90172.267 | 31.0331 | 1.3667 | 113.9366 | 40820.7825 | 0 | 53526.9517 | 0 | 0 | 0 | 923.3133 | 37155.7086 | 96671.532 | 65980.307 | 295078.5951 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9000194.1849 | 28548912.0755 | 562.3413 | 0.0064544 | 1394426.9691 | 4423168.2249 | 28427.2799 | 90172.267
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.089889 | 0.0023406 | 4 | 970299.7484 | 3058319.2661 | 19780.8728 | 62347.9749 | 31.4036 | 1.4331 | 156.9559 | 52044.6491 | 0 | 70369.0474 | 0 | 0 | 0 | 0 | 47741.3416 | 124213.1778 | 84778.0462 | 379146.2621 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9084261.8519 | 28632979.7425 | 749.8942 | 0.0093623 | 970299.7484 | 3058319.2661 | 19780.8728 | 62347.9749
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9445 | 0.133 | 0.0033372 | 4 | 688829.5717 | 2153278.3634 | 14042.7225 | 43897.492 | 31.7014 | 1.4862 | 34.7816 | 66070.5122 | 0 | 92125.1364 | 0 | 0 | 0 | 0 | 61696.3029 | 160521.1246 | 109558.9659 | 489972.0421 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9195087.6319 | 28743805.5225 | 1000 | 0.013349 | 688829.5717 | 2153278.3634 | 14042.7225 | 43897.492
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9339 | 0.19038 | 0.0046653 | 4 | 500021.0825 | 1547584.0356 | 10193.6061 | 31549.5938 | 31.9274 | 1.5262 | 29.2366 | 82917.0532 | 0 | 119148.202 | 0 | 0 | 0 | 0 | 78805.4495 | 205035.6144 | 139941.0199 | 625847.3391 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9330962.9289 | 28879680.8195 | 1333.5214 | 0.018661 | 500021.0825 | 1547584.0356 | 10193.6061 | 31549.5938
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2445 | 0.26671 | 0.0064266 | 4 | 369484.1547 | 1129942.1848 | 7532.4343 | 23035.3998 | 32.0953 | 1.5556 | 23.0441 | 103212.7718 | 0 | 152830.3734 | 0 | 0 | 0 | 0 | 99856.8266 | 259806.9794 | 177323.602 | 793030.5532 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9498146.143 | 29046864.0336 | 1778.2794 | 0.025707 | 369484.1547 | 1129942.1848 | 7532.4343 | 23035.3998
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0077 | 0.36959 | 0.0088063 | 4 | 275579.1343 | 830542.3117 | 5618.0534 | 16931.7284 | 32.226 | 1.5784 | 36.4199 | 128130.6421 | 0 | 195455.6865 | 0 | 0 | 0 | 0 | 126198.6681 | 328343.0476 | 224100.8767 | 1002228.921 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9707344.5108 | 29256062.4014 | 2371.3737 | 0.035225 | 275579.1343 | 830542.3117 | 5618.0534 | 16931.7284
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3512 | 0.50658 | 0.011948 | 4 | 208536.8041 | 617588.8366 | 4251.3048 | 12590.3838 | 32.3154 | 1.5935 | 37.8588 | 158271.1768 | 0 | 248837.9139 | 0 | 0 | 0 | 0 | 158772.5454 | 413093.5944 | 281944.8664 | 1260920.0968 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9966035.6867 | 29514753.5773 | 3162.2777 | 0.04779 | 208536.8041 | 617588.8366 | 4251.3048 | 12590.3838
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4575 | 0.68824 | 0.0161 | 4 | 159714.9693 | 463270.5066 | 3256.0057 | 9444.3959 | 32.3789 | 1.6041 | 41.3081 | 194762.2089 | 0 | 315493.8171 | 0 | 0 | 0 | 0 | 198999.8502 | 517756.7896 | 353379.6478 | 1580392.3136 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 10285507.9034 | 29834225.794 | 4216.965 | 0.064399 | 159714.9693 | 463270.5066 | 3256.0057 | 9444.3959
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5837 | 0.9297 | 0.02154 | 4 | 123966.7746 | 350855.8462 | 2527.2304 | 7152.671 | 32.4116 | 1.6087 | 54.4968 | 238905.8214 | 0 | 399026.2449 | 0 | 0 | 0 | 0 | 248793.5058 | 647309.6677 | 441802.1491 | 1975837.3888 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 10680952.9787 | 30229670.8693 | 5623.4133 | 0.08616 | 123966.7746 | 350855.8462 | 2527.2304 | 7152.671
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.0165 | 1.2476 | 0.028573 | 4 | 97699.5728 | 268741.078 | 1991.7379 | 5478.6504 | 32.4167 | 1.6081 | 38.7203 | 291820.0874 | 0 | 502815.5457 | 0 | 0 | 0 | 0 | 309907.8969 | 806316.777 | 550327.7684 | 2461188.0754 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 11166303.6653 | 30715021.5559 | 7498.9421 | 0.11429 | 97699.5728 | 268741.078 | 1991.7379 | 5478.6504
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.1419 | 1.6647 | 0.037436 | 4 | 78528.0843 | 209075.1425 | 1600.9012 | 4262.2796 | 32.3802 | 1.5991 | 37.1012 | 354555.8378 | 0 | 631492.4209 | 0 | 0 | 0 | 0 | 384558.8209 | 1000543.1681 | 682891.2714 | 3054041.5191 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 11759157.109 | 31307874.9995 | 10000 | 0.14974 | 78528.0843 | 209075.1425 | 1600.9012 | 4262.2796
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.365 | 2.2047 | 0.048115 | 4 | 64806.6827 | 166380.4243 | 1321.1719 | 3391.89 | 32.2853 | 1.5781 | 44.5996 | 427215.2612 | 0 | 789176.4711 | 0 | 0 | 0 | 0 | 474392.7756 | 1234272.6907 | 842416.4732 | 3767473.6718 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 12472589.2616 | 32021307.1522 | 13335.2143 | 0.19246 | 64806.6827 | 166380.4243 | 1321.1719 | 3391.89
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.0675 | 2.8897 | 0.059927 | 4 | 55529.3162 | 137081.3699 | 1132.0402 | 2794.5891 | 32.1004 | 1.5389 | 44.6738 | 508018.6023 | 0 | 979018.7379 | 0 | 0 | 0 | 0 | 579944.5627 | 1508896.7891 | 1029853.0633 | 4605731.7553 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 13310847.3451 | 32859565.2357 | 17782.7941 | 0.23971 | 55529.3162 | 137081.3699 | 1132.0402 | 2794.5891
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.4527 | 3.7302 | 0.070862 | 4 | 50298.9638 | 119266.3702 | 1025.4124 | 2431.4063 | 31.7775 | 1.4724 | 41.7333 | 591623.8208 | 0 | 1200950.5876 | 0 | 0 | 0 | 0 | 699104.0192 | 1818925.2521 | 1241453.8598 | 5552057.5395 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14257173.1293 | 33805891.0199 | 23713.7371 | 0.28345 | 50298.9638 | 119266.3702 | 1025.4124 | 2431.4063
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.3876 | 4.3664 | 0.075746 | 4 | 49245.6952 | 113766.6361 | 1003.9401 | 2319.2868 | 31.4568 | 1.4082 | 53.9009 | 643678.1507 | 0 | 1363089.9569 | 0 | 0 | 0 | 0 | 782639.562 | 2036267.5989 | 1389794.4773 | 6215469.7459 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14920585.3357 | 34469303.2263 | 31622.7766 | 0.30298 | 49245.6952 | 113766.6361 | 1003.9401 | 2319.2868
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.3487 | 4.364 | 0.075716 | 4 | 49256.3763 | 113802.7416 | 1004.1579 | 2320.0228 | 31.4572 | 1.4083 | 49.2364 | 643451.2601 | 0 | 1362463.7454 | 0 | 0 | 0 | 0 | 782306.8521 | 2035401.9561 | 1389203.6583 | 6212827.472 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14917943.0618 | 34466660.9524 | 42169.6503 | 0.30286 | 49256.3763 | 113802.7416 | 1004.1579 | 2320.0228
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.3144 | 4.3618 | 0.075691 | 4 | 49264.6987 | 113831.8845 | 1004.3275 | 2320.6169 | 31.4575 | 1.4084 | 56.6801 | 643257.4033 | 0 | 1361918.0109 | 0 | 0 | 0 | 0 | 782018.4115 | 2034651.4927 | 1388691.4517 | 6210536.7701 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14915652.3599 | 34464370.2505 | 56234.1325 | 0.30277 | 49264.6987 | 113831.8845 | 1004.3275 | 2320.6169
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2903 | 4.3602 | 0.075673 | 4 | 49271.1672 | 113853.8862 | 1004.4594 | 2321.0655 | 31.4578 | 1.4084 | 56.2393 | 643117.8491 | 0 | 1361531.4495 | 0 | 0 | 0 | 0 | 781813.2264 | 2034117.6433 | 1388327.0885 | 6208907.2567 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14914022.8465 | 34462740.7371 | 74989.4209 | 0.30269 | 49271.1672 | 113853.8862 | 1004.4594 | 2321.0655
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2755 | 4.3593 | 0.07566 | 4 | 49276.1699 | 113869.9333 | 1004.5614 | 2321.3926 | 31.4578 | 1.4084 | 53.4039 | 643026.4355 | 0 | 1361288.3675 | 0 | 0 | 0 | 0 | 781682.7732 | 2033778.2306 | 1388095.4324 | 6207871.2392 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14912986.829 | 34461704.7196 | 100000 | 0.30264 | 49276.1699 | 113869.9333 | 1004.5614 | 2321.3926
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2561 | 4.3581 | 0.075648 | 4 | 49280.0144 | 113884.3085 | 1004.6397 | 2321.6857 | 31.4581 | 1.4085 | 52.2292 | 642921.4747 | 0 | 1360984.0858 | 0 | 0 | 0 | 0 | 781523.1686 | 2033362.9723 | 1387812.01 | 6206603.7115 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14911719.3013 | 34460437.1919 | 133352.1432 | 0.30259 | 49280.0144 | 113884.3085 | 1004.6397 | 2321.6857
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2413 | 4.3571 | 0.075638 | 4 | 49282.9573 | 113895.2913 | 1004.6997 | 2321.9096 | 31.4583 | 1.4085 | 57.785 | 642841.5101 | 0 | 1360752.4482 | 0 | 0 | 0 | 0 | 781401.6437 | 2033046.7895 | 1387596.2088 | 6205638.6003 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14910754.1901 | 34459472.0807 | 177827.941 | 0.30255 | 49282.9573 | 113895.2913 | 1004.6997 | 2321.9096
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.356 | 0.075629 | 4 | 49285.1973 | 113905.7251 | 1004.7454 | 2322.1223 | 31.4588 | 1.4086 | 58.7352 | 642745.4104 | 0 | 1360456.8947 | 0 | 0 | 0 | 0 | 781248.899 | 2032649.379 | 1387324.968 | 6204425.5512 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909541.141 | 34458259.0316 | 237137.3706 | 0.30252 | 49285.1973 | 113905.7251 | 1004.7454 | 2322.1223
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.3559 | 0.075626 | 4 | 49286.8965 | 113909.8948 | 1004.7801 | 2322.2073 | 31.4586 | 1.4086 | 60.261 | 642736.1579 | 0 | 1360448.0839 | 0 | 0 | 0 | 0 | 781241.8543 | 2032631.0501 | 1387312.4581 | 6204369.6044 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909485.1942 | 34458203.0848 | 316227.766 | 0.3025 | 49286.8965 | 113909.8948 | 1004.7801 | 2322.2073
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.3559 | 0.075624 | 4 | 49288.183 | 113913.0511 | 1004.8063 | 2322.2716 | 31.4585 | 1.4086 | 57.8849 | 642729.1633 | 0 | 1360441.4476 | 0 | 0 | 0 | 0 | 781236.5382 | 2032617.2189 | 1387303.018 | 6204327.3859 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909442.9758 | 34458160.8664 | 421696.5034 | 0.3025 | 49288.183 | 113913.0511 | 1004.8063 | 2322.2716
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.3559 | 0.075622 | 4 | 49289.155 | 113915.4352 | 1004.8261 | 2322.3202 | 31.4584 | 1.4086 | 55.3651 | 642723.888 | 0 | 1360436.4647 | 0 | 0 | 0 | 0 | 781232.5375 | 2032606.8099 | 1387295.9136 | 6204295.6137 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909411.2035 | 34458129.0941 | 562341.3252 | 0.30249 | 49289.155 | 113915.4352 | 1004.8261 | 2322.3202
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.3559 | 0.075621 | 4 | 49289.8875 | 113917.2322 | 1004.841 | 2322.3569 | 31.4584 | 1.4086 | 55.992 | 642719.9097 | 0 | 1360432.7004 | 0 | 0 | 0 | 0 | 781229.518 | 2032598.9536 | 1387290.5515 | 6204271.6332 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909387.2231 | 34458105.1137 | 749894.2093 | 0.30248 | 49289.8875 | 113917.2322 | 1004.841 | 2322.3569
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2218 | 4.3559 | 0.07562 | 4 | 49290.4393 | 113918.5854 | 1004.8523 | 2322.3845 | 31.4583 | 1.4085 | 55.9542 | 642716.9177 | 0 | 1360429.8802 | 0 | 0 | 0 | 0 | 781227.2512 | 2032593.0558 | 1387286.5262 | 6204253.6311 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14909369.2209 | 34458087.1115 | 1000000 | 0.30248 | 49290.4393 | 113918.5854 | 1004.8523 | 2322.3845
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075614 | 4 | 49290.8537 | 113924.5377 | 1004.8607 | 2322.5058 | 31.4589 | 1.4087 | 56.109 | 642630.82 | 0 | 1360143.9989 | 0 | 0 | 0 | 0 | 781082.1794 | 2032215.6087 | 1387028.9108 | 6203101.5177 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908217.1075 | 34456934.9981 | 1333521.4322 | 0.30245 | 49290.8537 | 113924.5377 | 1004.8607 | 2322.5058
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075613 | 4 | 49291.1652 | 113925.3017 | 1004.8671 | 2322.5214 | 31.4589 | 1.4087 | 56.6822 | 642629.132 | 0 | 1360142.4111 | 0 | 0 | 0 | 0 | 781080.9018 | 2032212.2849 | 1387026.6422 | 6203091.3721 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908206.962 | 34456924.8526 | 1778279.41 | 0.30245 | 49291.1652 | 113925.3017 | 1004.8671 | 2322.5214
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075613 | 4 | 49291.3998 | 113925.8765 | 1004.8719 | 2322.5331 | 31.4589 | 1.4087 | 55.0225 | 642627.8699 | 0 | 1360141.2452 | 0 | 0 | 0 | 0 | 781079.9549 | 2032209.8211 | 1387024.9606 | 6203083.8517 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908199.4416 | 34456917.3321 | 2371373.7057 | 0.30245 | 49291.3998 | 113925.8765 | 1004.8719 | 2322.5331
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075612 | 4 | 49291.575 | 113926.3067 | 1004.8754 | 2322.5419 | 31.4589 | 1.4087 | 55.1448 | 642626.9127 | 0 | 1360140.3259 | 0 | 0 | 0 | 0 | 781079.223 | 2032207.917 | 1387023.661 | 6203078.0396 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908193.6294 | 34456911.52 | 3162277.6602 | 0.30245 | 49291.575 | 113926.3067 | 1004.8754 | 2322.5419
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075612 | 4 | 49291.7073 | 113926.6307 | 1004.8781 | 2322.5485 | 31.4589 | 1.4087 | 56.4852 | 642626.2024 | 0 | 1360139.6732 | 0 | 0 | 0 | 0 | 781078.6915 | 2032206.5339 | 1387022.7171 | 6203073.818 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908189.4079 | 34456907.2985 | 4216965.0343 | 0.30245 | 49291.7073 | 113926.6307 | 1004.8781 | 2322.5485
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075612 | 4 | 49291.806 | 113926.873 | 1004.8801 | 2322.5534 | 31.4588 | 1.4087 | 54.7397 | 642625.6625 | 0 | 1360139.1521 | 0 | 0 | 0 | 0 | 781078.2777 | 2032205.4574 | 1387021.9823 | 6203070.5321 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908186.122 | 34456904.0126 | 5623413.2519 | 0.30245 | 49291.806 | 113926.873 | 1004.8801 | 2322.5534
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075612 | 4 | 49291.8803 | 113927.0553 | 1004.8817 | 2322.5571 | 31.4588 | 1.4086 | 56.4606 | 642625.2613 | 0 | 1360138.7792 | 0 | 0 | 0 | 0 | 781077.9758 | 2032204.672 | 1387021.4463 | 6203068.1346 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908183.7245 | 34456901.6151 | 7498942.0933 | 0.30245 | 49291.8803 | 113927.0553 | 1004.8817 | 2322.5571
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2024 | 4.3547 | 0.075612 | 4 | 49291.936 | 113927.1918 | 1004.8828 | 2322.5599 | 31.4588 | 1.4086 | 54.6245 | 642624.9588 | 0 | 1360138.4918 | 0 | 0 | 0 | 0 | 781077.7457 | 2032204.0733 | 1387021.0376 | 6203066.3071 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14908181.897 | 34456899.7875 | 10000000 | 0.30245 | 49291.936 | 113927.1918 | 1004.8828 | 2322.5599
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.010328 | 7.8648e-05 | 4 | 29034477.1948 | 93557165.6415 | 591907.0897 | 1907289.367 | 25.0413 | 0.6288 | 13.4418 | 5267.7308 | 0 | 2829.2673 | 0 | 0 | 0 | 2336.3855 | 4069.0196 | 10586.7544 | 7225.6774 | 32314.8351 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9134049.746 | 29432450.2327 | 100 | 0.00031459 | 29034477.1948 | 93557165.6415 | 591907.0897 | 1907289.367
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.31152 | -0.0090244 | 0.00017799 | 4 | 12836975.5731 | 41347353.7907 | 261699.1104 | 842921.7335 | 26.2347 | 0.77482 | 28.8328 | 7155.6154 | 0 | 5031.466 | 0 | 0 | 0 | 0 | 4752.9618 | 12366.2315 | 8440.2071 | 37746.4818 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9139481.3927 | 29437881.8793 | 133.3521 | 0.00071197 | 12836975.5731 | 41347353.7907 | 261699.1104 | 842921.7335
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.441 | -0.0051682 | 0.00031768 | 4 | 7216922.0356 | 23190979.4803 | 147126.7173 | 472779.4848 | 28.1325 | 1.0232 | 29.7608 | 11587.0157 | 0 | 10231.9326 | 0 | 0 | 0 | 421.0056 | 8673.5821 | 22566.8813 | 15402.3602 | 68882.7775 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9170617.6885 | 29469018.1751 | 177.8279 | 0.0012707 | 7216922.0356 | 23190979.4803 | 147126.7173 | 472779.4848
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.60417 | 0.0017345 | 0.00053791 | 4 | 4279320.4928 | 13713283.8764 | 87239.7365 | 279563.8404 | 29.5427 | 1.2254 | 26.8629 | 17008.9592 | 0 | 16724.2249 | 0 | 0 | 0 | 419.7445 | 13319.6421 | 34654.9766 | 23652.7336 | 105780.2809 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9207515.1918 | 29505915.6784 | 237.1374 | 0.0021516 | 4279320.4928 | 13713283.8764 | 87239.7365 | 279563.8404
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.82568 | 0.012722 | 0.00086769 | 4 | 2667060.0409 | 8515428.7393 | 54371.6264 | 173598.5328 | 30.6551 | 1.3968 | 28.1182 | 23925.3951 | 0 | 25225.9918 | 0 | 0 | 0 | 906.9788 | 19522.7626 | 50794.2236 | 34668.1013 | 155043.4532 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9256778.3642 | 29555178.8508 | 316.2278 | 0.0034708 | 2667060.0409 | 8515428.7393 | 54371.6264 | 173598.5328
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.028061 | 0.0013443 | 4 | 1731591.4451 | 5506591.7368 | 35300.8338 | 112259.3208 | 31.4795 | 1.5294 | 73.11 | 32032.1529 | 0 | 35490.5712 | 0 | 0 | 0 | 0 | 26333.8624 | 68515.3082 | 46763.1057 | 209135.0004 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9310869.9113 | 29609270.3979 | 421.6965 | 0.0053771 | 1731591.4451 | 5506591.7368 | 35300.8338 | 112259.3208
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.050227 | 0.0020134 | 4 | 1165305.6762 | 3685685.6767 | 23756.3324 | 75137.6878 | 32.1456 | 1.6383 | 99.6327 | 42280.6101 | 0 | 48898.8039 | 0 | 0 | 0 | 287.0539 | 35671.9225 | 92811.0251 | 63345.4317 | 283294.8472 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9385029.7582 | 29683430.2448 | 562.3413 | 0.0080537 | 1165305.6762 | 3685685.6767 | 23756.3324 | 75137.6878
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.080899 | 0.0029199 | 4 | 811755.7611 | 2549670.9646 | 16548.7392 | 51978.4913 | 32.668 | 1.7244 | 141.4318 | 54865.8459 | 0 | 65897.0246 | 0 | 0 | 0 | 1720.679 | 47768.5843 | 124284.0577 | 84826.4232 | 379362.6147 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9481097.5256 | 29779498.0123 | 749.8942 | 0.01168 | 811755.7611 | 2549670.9646 | 16548.7392 | 51978.4913
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7009 | 0.12144 | 0.0041591 | 4 | 576451.9517 | 1796573.521 | 11751.7527 | 36625.5813 | 33.0579 | 1.7884 | 33.4642 | 69664.7917 | 0 | 86575.242 | 0 | 0 | 0 | 1427.4464 | 61490.3172 | 159985.192 | 109193.1809 | 488336.1703 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9590071.0812 | 29888471.5679 | 1000 | 0.016636 | 576451.9517 | 1796573.521 | 11751.7527 | 36625.5813
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6024 | 0.1757 | 0.0058305 | 4 | 416803.9629 | 1287153.117 | 8497.1126 | 26240.3573 | 33.356 | 1.8368 | 38.3033 | 87512.2749 | 0 | 112349.7542 | 0 | 0 | 0 | 0 | 77946.1913 | 202800.0009 | 138415.1677 | 619023.389 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9720758.3 | 30019158.7866 | 1333.5214 | 0.023322 | 416803.9629 | 1287153.117 | 8497.1126 | 26240.3573
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8157 | 0.24901 | 0.0080612 | 4 | 306701.4164 | 936208.4598 | 6252.5232 | 19085.8758 | 33.5876 | 1.8744 | 32.415 | 109399.1565 | 0 | 144963.5757 | 0 | 0 | 0 | 0 | 99201.4656 | 258101.8644 | 176159.8259 | 787825.8881 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9889560.799 | 30187961.2856 | 1778.2794 | 0.032245 | 306701.4164 | 936208.4598 | 6252.5232 | 19085.8758
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4398 | 0.34738 | 0.011033 | 4 | 228937.0154 | 688883.9455 | 4667.1907 | 14043.831 | 33.7633 | 1.9026 | 42.249 | 136094.5918 | 0 | 186015.5822 | 0 | 0 | 0 | 1313.3535 | 126135.1757 | 328177.8532 | 223988.1282 | 1001724.6845 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10103459.5955 | 30401860.0821 | 2371.3737 | 0.044132 | 228937.0154 | 688883.9455 | 4667.1907 | 14043.831
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5741 | 0.47697 | 0.01499 | 4 | 172707.6376 | 511229.7119 | 3520.8788 | 10422.1092 | 33.893 | 1.9232 | 36.4054 | 168115.1507 | 0 | 236801.572 | 0 | 0 | 0 | 0 | 157917.5219 | 410868.9985 | 280426.534 | 1254129.7771 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10355864.688 | 30654265.1747 | 3162.2777 | 0.059962 | 172707.6376 | 511229.7119 | 3520.8788 | 10422.1092
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4512 | 0.65187 | 0.020248 | 4 | 131871.5685 | 382498.6335 | 2688.3803 | 7797.752 | 33.9812 | 1.9364 | 35.0491 | 207447.7184 | 0 | 301338.6517 | 0 | 0 | 0 | 892.1618 | 198774.6275 | 517170.8063 | 352979.7021 | 1578603.6679 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10680338.5788 | 30978739.0654 | 4216.965 | 0.08099 | 131871.5685 | 382498.6335 | 2688.3803 | 7797.752
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2413 | 0.88239 | 0.027164 | 4 | 101902.3299 | 288716.4762 | 2077.4168 | 5885.8759 | 34.0387 | 1.9443 | 50.2313 | 254756.901 | 0 | 381459.1397 | 0 | 0 | 0 | 0 | 248124.2559 | 645568.4165 | 440613.7094 | 1970522.4224 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 11072257.3334 | 31370657.82 | 5623.4133 | 0.10866 | 101902.3299 | 288716.4762 | 2077.4168 | 5885.8759
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2527 | 1.1873 | 0.036172 | 4 | 79885.1837 | 220175.3812 | 1628.5675 | 4488.573 | 34.0631 | 1.946 | 41.2402 | 311765.5206 | 0 | 481435.6438 | 0 | 0 | 0 | 0 | 309348.4541 | 804861.2215 | 549334.3219 | 2456745.1619 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 11558480.0729 | 31856880.5595 | 7498.9421 | 0.14469 | 79885.1837 | 220175.3812 | 1628.5675 | 4488.573
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8102 | 1.5863 | 0.047697 | 4 | 63690.1316 | 170083.5567 | 1298.4095 | 3467.3834 | 34.0506 | 1.9404 | 40.4555 | 379563.8462 | 0 | 605006.8727 | 0 | 0 | 0 | 0 | 383982.5804 | 999043.9085 | 681867.9959 | 3049465.2037 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 12151200.1147 | 32449600.6013 | 10000 | 0.19079 | 63690.1316 | 170083.5567 | 1298.4095 | 3467.3834
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.3151 | 2.1039 | 0.061992 | 4 | 51887.7362 | 133746.3919 | 1057.8017 | 2726.6011 | 33.9839 | 1.9234 | 34.3327 | 458834.9356 | 0 | 756696.7108 | 0 | 0 | 0 | 0 | 474057.3421 | 1233399.9616 | 841820.8176 | 3764809.7677 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 12866544.6786 | 33164945.1652 | 13335.2143 | 0.24797 | 51887.7362 | 133746.3919 | 1057.8017 | 2726.6011
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.1453 | 2.7632 | 0.078762 | 4 | 43523.6608 | 107953.2173 | 887.2887 | 2200.7724 | 33.8368 | 1.8893 | 46.4722 | 548565.2162 | 0 | 939948.9094 | 0 | 0 | 0 | 0 | 580520.509 | 1510395.2833 | 1030875.8163 | 4610305.7342 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 13712040.6451 | 34010441.1318 | 17782.7941 | 0.31505 | 43523.6608 | 107953.2173 | 887.2887 | 2200.7724
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.4198 | 3.5701 | 0.096503 | 4 | 38002.2028 | 90587.3686 | 774.7263 | 1846.746 | 33.5789 | 1.8319 | 40.7238 | 644093.1812 | 0 | 1153465.7504 | 0 | 0 | 0 | 0 | 701047.9833 | 1823983.0478 | 1244905.9093 | 5567495.872 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 14669230.7829 | 34967631.2695 | 23713.7371 | 0.38601 | 38002.2028 | 90587.3686 | 774.7263 | 1846.746
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.13 | 4.5215 | 0.11203 | 4 | 35047.5513 | 80345.5988 | 714.4917 | 1637.9537 | 33.1554 | 1.7405 | 47.1553 | 737555.1674 | 0 | 1394443.3339 | 0 | 0 | 0 | 0 | 831479.4155 | 2163338.8792 | 1476523.2373 | 6603340.0333 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 15705074.9442 | 36003475.4309 | 31622.7766 | 0.44811 | 35047.5513 | 80345.5988 | 714.4917 | 1637.9537
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4413 | 5.1424 | 0.11813 | 4 | 34563.7032 | 77523.0711 | 704.6278 | 1580.4127 | 32.8035 | 1.6664 | 50.464 | 787127.6502 | 0 | 1547099.8887 | 0 | 0 | 0 | 0 | 910348.7402 | 2368540.6837 | 1616577.6853 | 7229694.648 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16331429.5589 | 36629830.0456 | 42169.6503 | 0.4725 | 34563.7032 | 77523.0711 | 704.6278 | 1580.4127
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.3823 | 5.1385 | 0.11807 | 4 | 34570.8388 | 77549.5373 | 704.7733 | 1580.9522 | 32.8045 | 1.6666 | 63.4141 | 786787.6546 | 0 | 1546156.3555 | 0 | 0 | 0 | 0 | 909848.164 | 2367238.2871 | 1615688.7728 | 7225719.2341 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16327454.145 | 36625854.6317 | 56234.1325 | 0.47229 | 34570.8388 | 77549.5373 | 704.7733 | 1580.9522
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.348 | 5.1362 | 0.11804 | 4 | 34576.3562 | 77568.2485 | 704.8858 | 1581.3337 | 32.8048 | 1.6667 | 68.5376 | 786574.4288 | 0 | 1545592.8718 | 0 | 0 | 0 | 0 | 909545.2472 | 2366450.16 | 1615150.8599 | 7223313.5677 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16325048.4786 | 36623448.9653 | 74989.4209 | 0.47214 | 34576.3562 | 77568.2485 | 704.8858 | 1581.3337
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.3286 | 5.1348 | 0.11801 | 4 | 34580.6024 | 77581.5766 | 704.9724 | 1581.6054 | 32.8048 | 1.6667 | 66.734 | 786440.6509 | 0 | 1545260.5998 | 0 | 0 | 0 | 0 | 909363.4878 | 2365977.259 | 1614828.0953 | 7221870.0927 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16323605.0037 | 36622005.4903 | 100000 | 0.47205 | 34580.6024 | 77581.5766 | 704.9724 | 1581.6054
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.3091 | 5.1335 | 0.11799 | 4 | 34583.855 | 77592.4896 | 705.0387 | 1581.8279 | 32.805 | 1.6668 | 64.8169 | 786318.3673 | 0 | 1544939.7963 | 0 | 0 | 0 | 0 | 909190.6838 | 2365527.6586 | 1614521.2337 | 7220497.7397 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16322232.6506 | 36620633.1372 | 133352.1432 | 0.47196 | 34583.855 | 77592.4896 | 705.0387 | 1581.8279
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2897 | 5.1322 | 0.11797 | 4 | 34586.3356 | 77601.5265 | 705.0892 | 1582.0121 | 32.8053 | 1.6668 | 64.6195 | 786204.999 | 0 | 1544627.862 | 0 | 0 | 0 | 0 | 909024.8158 | 2365096.1041 | 1614226.6889 | 7219180.4698 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16320915.3808 | 36619315.8674 | 177827.941 | 0.47189 | 34586.3356 | 77601.5265 | 705.0892 | 1582.0121
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2897 | 5.1321 | 0.11796 | 4 | 34588.2201 | 77606.1028 | 705.1277 | 1582.1054 | 32.805 | 1.6668 | 61.7362 | 786183.4271 | 0 | 1544606.8063 | 0 | 0 | 0 | 0 | 909008.191 | 2365052.8498 | 1614197.167 | 7219048.4413 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16320783.3522 | 36619183.8388 | 237137.3706 | 0.47186 | 34588.2201 | 77606.1028 | 705.1277 | 1582.1054
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2749 | 5.1312 | 0.11795 | 4 | 34589.6475 | 77611.8639 | 705.1568 | 1582.2228 | 32.8053 | 1.6669 | 71.6325 | 786102.3988 | 0 | 1544374.4767 | 0 | 0 | 0 | 0 | 908885.9814 | 2364734.8856 | 1613980.1498 | 7218077.8923 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16319812.8033 | 36618213.2899 | 316227.766 | 0.47181 | 34589.6475 | 77611.8639 | 705.1568 | 1582.2228
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2749 | 5.1311 | 0.11795 | 4 | 34590.7265 | 77614.4834 | 705.1787 | 1582.2762 | 32.8051 | 1.6668 | 71.072 | 786090.0725 | 0 | 1544362.4984 | 0 | 0 | 0 | 0 | 908876.5027 | 2364710.2238 | 1613963.3177 | 7218002.6151 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16319737.526 | 36618138.0127 | 421696.5034 | 0.4718 | 34590.7265 | 77614.4834 | 705.1787 | 1582.2762
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1299 | 0.11794 | 4 | 34591.5405 | 77619.4724 | 705.1953 | 1582.3779 | 32.8057 | 1.6669 | 68.0999 | 785995.8594 | 0 | 1544069.4333 | 0 | 0 | 0 | 0 | 908725.4641 | 2364317.2525 | 1613695.1067 | 7216803.116 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318538.0269 | 36616938.5136 | 562341.3252 | 0.47175 | 34591.5405 | 77619.4724 | 705.1953 | 1582.3779
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1299 | 0.11793 | 4 | 34592.1533 | 77620.9597 | 705.2078 | 1582.4083 | 32.8056 | 1.6669 | 69.1531 | 785988.8684 | 0 | 1544062.6585 | 0 | 0 | 0 | 0 | 908720.0955 | 2364303.2844 | 1613685.5732 | 7216760.4801 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318495.391 | 36616895.8776 | 749894.2093 | 0.47174 | 34592.1533 | 77620.9597 | 705.2078 | 1582.4083
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1299 | 0.11793 | 4 | 34592.6144 | 77622.079 | 705.2172 | 1582.4311 | 32.8055 | 1.6669 | 68.3575 | 785983.6094 | 0 | 1544057.567 | 0 | 0 | 0 | 0 | 908716.0588 | 2364292.7816 | 1613678.4048 | 7216728.4216 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318463.3326 | 36616863.8192 | 1000000 | 0.47173 | 34592.6144 | 77622.079 | 705.2172 | 1582.4311
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34592.9611 | 77622.9205 | 705.2243 | 1582.4482 | 32.8055 | 1.6669 | 68.22 | 785979.6563 | 0 | 1544053.7425 | 0 | 0 | 0 | 0 | 908713.0255 | 2364284.8898 | 1613673.0185 | 7216704.3325 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318439.2435 | 36616839.7301 | 1333521.4322 | 0.47173 | 34592.9611 | 77622.9205 | 705.2243 | 1582.4482
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.2216 | 77623.5528 | 705.2296 | 1582.4611 | 32.8054 | 1.6669 | 68.8108 | 785976.6867 | 0 | 1544050.8709 | 0 | 0 | 0 | 0 | 908710.7475 | 2364278.9627 | 1613668.9731 | 7216686.2409 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318421.1518 | 36616821.6384 | 1778279.41 | 0.47172 | 34593.2216 | 77623.5528 | 705.2296 | 1582.4611
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.4173 | 77624.0277 | 705.2336 | 1582.4708 | 32.8054 | 1.6669 | 67.7947 | 785974.4567 | 0 | 1544048.7156 | 0 | 0 | 0 | 0 | 908709.0372 | 2364274.513 | 1613665.9361 | 7216672.6586 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318407.5696 | 36616808.0562 | 2371373.7057 | 0.47172 | 34593.4173 | 77624.0277 | 705.2336 | 1582.4708
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.5642 | 77624.3842 | 705.2366 | 1582.4781 | 32.8054 | 1.6669 | 63.7989 | 785972.7828 | 0 | 1544047.0982 | 0 | 0 | 0 | 0 | 908707.7536 | 2364271.1733 | 1613663.6567 | 7216662.4646 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318397.3756 | 36616797.8622 | 3162277.6602 | 0.47172 | 34593.5642 | 77624.3842 | 705.2366 | 1582.4781
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.6744 | 77624.6517 | 705.2388 | 1582.4835 | 32.8053 | 1.6669 | 64.0823 | 785971.5267 | 0 | 1544045.8847 | 0 | 0 | 0 | 0 | 908706.7904 | 2364268.6673 | 1613661.9463 | 7216654.8154 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318389.7263 | 36616790.2129 | 4216965.0343 | 0.47172 | 34593.6744 | 77624.6517 | 705.2388 | 1582.4835
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.7572 | 77624.8525 | 705.2405 | 1582.4876 | 32.8053 | 1.6669 | 62.4416 | 785970.5841 | 0 | 1544044.9743 | 0 | 0 | 0 | 0 | 908706.0678 | 2364266.7871 | 1613660.663 | 7216649.0764 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318383.9874 | 36616784.474 | 5623413.2519 | 0.47171 | 34593.7572 | 77624.8525 | 705.2405 | 1582.4876
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.8192 | 77625.0031 | 705.2418 | 1582.4907 | 32.8053 | 1.6669 | 62.9787 | 785969.877 | 0 | 1544044.2914 | 0 | 0 | 0 | 0 | 908705.5257 | 2364265.3767 | 1613659.7004 | 7216644.7713 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318379.6822 | 36616780.1689 | 7498942.0933 | 0.47171 | 34593.8192 | 77625.0031 | 705.2418 | 1582.4907
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2554 | 5.1298 | 0.11793 | 4 | 34593.8658 | 77625.1161 | 705.2427 | 1582.493 | 32.8053 | 1.6669 | 62.5407 | 785969.3466 | 0 | 1544043.7792 | 0 | 0 | 0 | 0 | 908705.1191 | 2364264.3188 | 1613658.9783 | 7216641.542 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16318376.4529 | 36616776.9396 | 10000000 | 0.47171 | 34593.8658 | 77625.1161 | 705.2427 | 1582.493
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.011473 | 7.6127e-05 | 4 | 31343393.5106 | 100509996.3918 | 638977.4718 | 2049032.2263 | 25.1944 | 0.84216 | 12.7291 | 6336.8453 | 0 | 2337.3612 | 0 | 0 | 0 | 4282.9643 | 5053.2966 | 13147.6413 | 8973.5353 | 40131.6442 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9544345.9671 | 30606200.2633 | 100 | 0.00030451 | 31343393.5106 | 100509996.3918 | 638977.4718 | 2049032.2263
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27263 | -0.010484 | 0.00019571 | 4 | 12184292.8892 | 39088375.9959 | 248393.291 | 796869.4156 | 25.6177 | 0.89224 | 23.7577 | 6939.1669 | 0 | 3000.2271 | 0 | 0 | 0 | 1120.7661 | 4313.4625 | 11222.7445 | 7659.7538 | 34256.1209 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9538470.4439 | 30600324.7401 | 133.3521 | 0.00078285 | 12184292.8892 | 39088375.9959 | 248393.291 | 796869.4156
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.38468 | -0.0081006 | 0.00034115 | 4 | 7009759.5092 | 22444314.9421 | 142903.429 | 457557.7183 | 27.8189 | 1.1596 | 25.2565 | 11038.6825 | 0 | 7486.1612 | 0 | 0 | 0 | 1247.4796 | 7711.2061 | 20062.9764 | 13693.3937 | 61239.8994 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9565454.2224 | 30627308.5185 | 177.8279 | 0.0013646 | 7009759.5092 | 22444314.9421 | 142903.429 | 457557.7183
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.55046 | -0.0020186 | 0.0005834 | 4 | 4117350.9511 | 13142765.811 | 83937.7683 | 267933.058 | 29.7999 | 1.4193 | 22.7619 | 17097.3646 | 0 | 14198.6298 | 0 | 0 | 0 | 2315.2484 | 13108.3847 | 34105.3281 | 23277.5872 | 104102.5429 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9608316.8658 | 30670171.162 | 237.1374 | 0.0023336 | 4117350.9511 | 13142765.811 | 83937.7683 | 267933.058
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.77197 | 0.0085142 | 0.00095745 | 4 | 2523244.7497 | 8022723.0462 | 51439.7572 | 163554.0608 | 31.3022 | 1.6317 | 33.7547 | 24807.9685 | 0 | 22950.3071 | 0 | 0 | 0 | 3670.0419 | 20057.0438 | 52184.3138 | 35616.8664 | 159286.5415 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9663500.8645 | 30725355.1606 | 316.2278 | 0.0038298 | 2523244.7497 | 8022723.0462 | 51439.7572 | 163554.0608
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0485 | 0.023576 | 0.0015018 | 4 | 1618979.9011 | 5124993.9801 | 33005.0951 | 104479.9344 | 32.3777 | 1.7914 | 63.7692 | 33747.1067 | 0 | 33386.2109 | 0 | 0 | 0 | 4402.5979 | 27899.007 | 72587.4934 | 49542.4558 | 221564.8716 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9725779.1945 | 30787633.4907 | 421.6965 | 0.0060074 | 1618979.9011 | 5124993.9801 | 33005.0951 | 104479.9344
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.045009 | 0.0022685 | 4 | 1080410.8395 | 3401549.376 | 22025.6363 | 69345.185 | 33.2165 | 1.9187 | 92.1921 | 44711.3241 | 0 | 46578.9901 | 0 | 0 | 0 | 5363.2686 | 37694.8973 | 98074.3905 | 66937.7867 | 299360.6573 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9803574.9802 | 30865429.2764 | 562.3413 | 0.0090739 | 1080410.8395 | 3401549.376 | 22025.6363 | 69345.185
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.073246 | 0.0033229 | 4 | 744170.223 | 2328762.9738 | 15170.9166 | 47474.9831 | 33.8413 | 2.0142 | 122.8885 | 57370.3559 | 0 | 62289.7996 | 0 | 0 | 0 | 5301.129 | 48734.9009 | 126798.2153 | 86542.3874 | 387036.7881 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9891251.1111 | 30953105.4073 | 749.8942 | 0.013292 | 744170.223 | 2328762.9738 | 15170.9166 | 47474.9831
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.484 | 0.11032 | 0.0047533 | 4 | 525527.0536 | 1633267.8607 | 10713.5798 | 33296.3745 | 34.321 | 2.0873 | 32.7757 | 72234.5295 | 0 | 81307.0173 | 0 | 0 | 0 | 3956.3837 | 61424.1929 | 159813.1501 | 109075.7588 | 487811.0324 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9992025.3553 | 31053879.6515 | 1000 | 0.019013 | 525527.0536 | 1633267.8607 | 10713.5798 | 33296.3745
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2688 | 0.15942 | 0.0066795 | 4 | 378309.721 | 1166612.4786 | 7712.3554 | 23782.9733 | 34.6957 | 2.1441 | 26.1202 | 90041.1365 | 0 | 104794.6336 | 0 | 0 | 0 | 0 | 75985.9503 | 197699.8559 | 134934.214 | 603455.7903 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10107670.1132 | 31169524.4094 | 1333.5214 | 0.026718 | 378309.721 | 1166612.4786 | 7712.3554 | 23782.9733
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3794 | 0.22893 | 0.009276 | 4 | 276945.3843 | 844588.809 | 5645.9063 | 17218.0853 | 35.0061 | 2.191 | 29.3767 | 113044.3681 | 0 | 136070.9754 | 0 | 0 | 0 | 0 | 97154.984 | 252777.3391 | 172525.728 | 771573.3947 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10275787.7176 | 31337642.0138 | 1778.2794 | 0.037104 | 276945.3843 | 844588.809 | 5645.9063 | 17218.0853
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8673 | 0.32241 | 0.012748 | 4 | 205690.3077 | 618739.2641 | 4193.2751 | 12613.8368 | 35.242 | 2.2263 | 39.1174 | 141109.3209 | 0 | 175453.2183 | 0 | 0 | 0 | 1195.582 | 123925.6673 | 322429.1657 | 220064.5308 | 984177.4851 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10488391.808 | 31550246.1042 | 2371.3737 | 0.050991 | 205690.3077 | 618739.2641 | 4193.2751 | 12613.8368
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8313 | 0.44621 | 0.017374 | 4 | 154553.2893 | 457621.0768 | 3150.7779 | 9329.2246 | 35.4148 | 2.2516 | 41.0994 | 174873.3383 | 0 | 224366.5877 | 0 | 0 | 0 | 0 | 155703.5711 | 405108.7529 | 276495.048 | 1236547.2981 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10740761.6211 | 31802615.9173 | 3162.2777 | 0.069496 | 154553.2893 | 457621.0768 | 3150.7779 | 9329.2246
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4526 | 0.6116 | 0.023515 | 4 | 117569.2696 | 341488.6233 | 2396.8086 | 6961.7075 | 35.5415 | 2.2697 | 30.4838 | 216014.4792 | 0 | 285833.7101 | 0 | 0 | 0 | 0 | 195720.7938 | 509225.3577 | 347556.7701 | 1554351.1109 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 11058565.4339 | 32120419.73 | 4216.965 | 0.09406 | 117569.2696 | 341488.6233 | 2396.8086 | 6961.7075
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9136 | 0.83008 | 0.031608 | 4 | 90555.6492 | 257140.9168 | 1846.0994 | 5242.1654 | 35.6319 | 2.2821 | 35.4842 | 265682.2312 | 0 | 362292.4161 | 0 | 0 | 0 | 0 | 244910.1125 | 637205.8746 | 434906.1027 | 1944996.7371 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 11449211.0601 | 32511065.3563 | 5623.4133 | 0.12643 | 90555.6492 | 257140.9168 | 1846.0994 | 5242.1654
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5204 | 1.1212 | 0.042243 | 4 | 70622.116 | 195268.8736 | 1439.7274 | 3980.8201 | 35.6775 | 2.2861 | 35.6881 | 325875.1346 | 0 | 458358.3133 | 0 | 0 | 0 | 0 | 305851.0447 | 795761.6795 | 543123.6975 | 2428969.8696 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 11933184.1925 | 32995038.4887 | 7498.9421 | 0.16897 | 70622.116 | 195268.8736 | 1439.7274 | 3980.8201
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.5445 | 1.5019 | 0.055952 | 4 | 55952.1477 | 150058.1149 | 1140.6602 | 3059.1376 | 35.6871 | 2.2833 | 41.7441 | 397611.9046 | 0 | 576940.0441 | 0 | 0 | 0 | 0 | 380075.26 | 988877.8624 | 674929.4605 | 3018434.5316 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 12522648.8546 | 33584503.1508 | 10000 | 0.22381 | 55952.1477 | 150058.1149 | 1140.6602 | 3059.1376
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3721 | 1.9968 | 0.073239 | 4 | 45179.8276 | 117074.304 | 921.0519 | 2386.718 | 35.6451 | 2.2698 | 39.0168 | 482055.92 | 0 | 722704.022 | 0 | 0 | 0 | 0 | 469856.3774 | 1222469.9131 | 834360.8349 | 3731447.0673 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 13235661.3902 | 34297515.6864 | 13335.2143 | 0.29296 | 45179.8276 | 117074.304 | 921.0519 | 2386.718
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.3138 | 2.6253 | 0.094113 | 4 | 37395.9982 | 93344.4303 | 762.368 | 1902.9525 | 35.5368 | 2.2419 | 37.2926 | 578482.6327 | 0 | 898165.5909 | 0 | 0 | 0 | 0 | 575892.8072 | 1498354.9525 | 1022658.0432 | 4573554.0265 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 14077768.3494 | 35139622.6456 | 17782.7941 | 0.37645 | 37395.9982 | 93344.4303 | 762.368 | 1902.9525
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.5723 | 3.3997 | 0.1176 | 4 | 31974.4005 | 76749.6747 | 651.8414 | 1564.6459 | 35.3312 | 2.1929 | 42.26 | 683647.5441 | 0 | 1103817.7275 | 0 | 0 | 0 | 0 | 697111.4559 | 1813741.0111 | 1237915.5087 | 5536233.2474 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 15040447.5704 | 36102301.8666 | 23713.7371 | 0.47039 | 31974.4005 | 76749.6747 | 651.8414 | 1564.6459
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1077 | 4.3158 | 0.14102 | 4 | 28527.9387 | 65867.1617 | 581.5806 | 1342.7912 | 34.9831 | 2.1132 | 39.1362 | 790467.2937 | 0 | 1336409.8698 | 0 | 0 | 0 | 0 | 829482.0938 | 2158142.2578 | 1472976.4364 | 6587477.9515 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 16091692.2744 | 37153546.5706 | 31622.7766 | 0.56407 | 28527.9387 | 65867.1617 | 581.5806 | 1342.7912
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2764 | 5.3289 | 0.15982 | 4 | 26839.3724 | 59784.7805 | 547.1569 | 1218.7936 | 34.4662 | 1.9985 | 44.5831 | 887261.971 | 0 | 1583984.9 | 0 | 0 | 0 | 0 | 963786.2797 | 2507574.2 | 1711470.917 | 7654078.2677 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17158292.5907 | 38220146.8869 | 42169.6503 | 0.6393 | 26839.3724 | 59784.7805 | 547.1569 | 1218.7936
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8212 | 5.8607 | 0.16594 | 4 | 26635.6088 | 58366.5637 | 543.0029 | 1189.8813 | 34.1335 | 1.9264 | 53.9274 | 928655.8693 | 0 | 1710951.8319 | 0 | 0 | 0 | 0 | 1029447.0035 | 2678409.9344 | 1828069.816 | 8175534.455 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17679748.7779 | 38741603.0741 | 56234.1325 | 0.66376 | 26635.6088 | 58366.5637 | 543.0029 | 1189.8813
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7887 | 5.8583 | 0.16589 | 4 | 26640.2882 | 58381.3146 | 543.0983 | 1190.1821 | 34.1335 | 1.9265 | 59.6442 | 928417.3833 | 0 | 1710381.5952 | 0 | 0 | 0 | 0 | 1029131.6016 | 2677589.3234 | 1827509.7322 | 8173029.6356 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17677243.9585 | 38739098.2547 | 74989.4209 | 0.66355 | 26640.2882 | 58381.3146 | 543.0983 | 1190.1821
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7692 | 5.8568 | 0.16585 | 4 | 26643.8824 | 58392.0578 | 543.1716 | 1190.4011 | 34.1333 | 1.9265 | 56.6225 | 928258.856 | 0 | 1710024.7815 | 0 | 0 | 0 | 0 | 1028930.6186 | 2677066.407 | 1827152.831 | 8171433.4941 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17675647.8171 | 38737502.1132 | 100000 | 0.6634 | 26643.8824 | 58392.0578 | 543.1716 | 1190.4011
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7427 | 5.8549 | 0.16582 | 4 | 26646.6299 | 58401.5126 | 543.2276 | 1190.5938 | 34.1336 | 1.9266 | 63.3745 | 928085.7478 | 0 | 1709580.8757 | 0 | 0 | 0 | 0 | 1028689.9832 | 2676440.3229 | 1826725.5158 | 8169522.4454 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17673736.7684 | 38735591.0646 | 133352.1432 | 0.66326 | 26646.6299 | 58401.5126 | 543.2276 | 1190.5938
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7233 | 5.8535 | 0.16579 | 4 | 26648.7222 | 58408.6336 | 543.2702 | 1190.739 | 34.1338 | 1.9266 | 63.14 | 927957.2648 | 0 | 1709253.8216 | 0 | 0 | 0 | 0 | 1028512.3237 | 2675978.0894 | 1826410.0318 | 8168111.5313 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17672325.8542 | 38734180.1504 | 177827.941 | 0.66316 | 26648.7222 | 58408.6336 | 543.2702 | 1190.739
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7085 | 5.8525 | 0.16577 | 4 | 26650.3099 | 58414.0436 | 543.3026 | 1190.8493 | 34.134 | 1.9267 | 68.7845 | 927859.5316 | 0 | 1709004.8587 | 0 | 0 | 0 | 0 | 1028377.1122 | 2675626.2969 | 1826169.9263 | 8167037.7257 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17671252.0487 | 38733106.3449 | 237137.3706 | 0.66308 | 26650.3099 | 58414.0436 | 543.3026 | 1190.8493
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.689 | 5.8512 | 0.16575 | 4 | 26651.5118 | 58419.0175 | 543.3271 | 1190.9507 | 34.1345 | 1.9268 | 71.1587 | 927748.8274 | 0 | 1708695.3751 | 0 | 0 | 0 | 0 | 1028213.239 | 2675199.9322 | 1825878.9236 | 8165736.2972 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17669950.6202 | 38731804.9164 | 316227.766 | 0.663 | 26651.5118 | 58419.0175 | 543.3271 | 1190.9507
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.689 | 5.8511 | 0.16574 | 4 | 26652.419 | 58421.2047 | 543.3456 | 1190.9953 | 34.1342 | 1.9267 | 70.1883 | 927730.8059 | 0 | 1708677.7521 | 0 | 0 | 0 | 0 | 1028199.3376 | 2675163.7638 | 1825854.2379 | 8165625.8975 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17669840.2204 | 38731694.5166 | 421696.5034 | 0.66297 | 26652.419 | 58421.2047 | 543.3456 | 1190.9953
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.687 | 5.8509 | 0.16574 | 4 | 26653.1032 | 58423.0705 | 543.3596 | 1191.0333 | 34.1341 | 1.9267 | 70.3182 | 927708.167 | 0 | 1708634.6409 | 0 | 0 | 0 | 0 | 1028173.6951 | 2675097.0471 | 1825808.7024 | 8165422.2525 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17669636.5755 | 38731490.8716 | 562341.3252 | 0.66295 | 26653.1032 | 58423.0705 | 543.3596 | 1191.0333
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.687 | 5.8509 | 0.16573 | 4 | 26653.6184 | 58424.3124 | 543.3701 | 1191.0586 | 34.134 | 1.9267 | 69.0736 | 927697.9408 | 0 | 1708624.6576 | 0 | 0 | 0 | 0 | 1028165.8134 | 2675076.5406 | 1825794.7063 | 8165359.6587 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17669573.9816 | 38731428.2778 | 749894.2093 | 0.66293 | 26653.6184 | 58424.3124 | 543.3701 | 1191.0586
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8498 | 0.16572 | 4 | 26654.0059 | 58427.1064 | 543.378 | 1191.1156 | 34.1346 | 1.9268 | 70.8803 | 927612.5014 | 0 | 1708360.934 | 0 | 0 | 0 | 0 | 1028029.6398 | 2674722.2449 | 1825552.8922 | 8164278.2124 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668492.5354 | 38730346.8315 | 1000000 | 0.66288 | 26654.0059 | 58427.1064 | 543.378 | 1191.1156
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16572 | 4 | 26654.297 | 58427.8081 | 543.3839 | 1191.1299 | 34.1345 | 1.9268 | 71.5473 | 927606.7259 | 0 | 1708355.3016 | 0 | 0 | 0 | 0 | 1028025.1907 | 2674710.6693 | 1825544.9916 | 8164242.8792 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668457.2022 | 38730311.4983 | 1333521.4322 | 0.66287 | 26654.297 | 58427.8081 | 543.3839 | 1191.1299
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16572 | 4 | 26654.5158 | 58428.3353 | 543.3884 | 1191.1406 | 34.1344 | 1.9268 | 67.8313 | 927602.3877 | 0 | 1708351.0722 | 0 | 0 | 0 | 0 | 1028021.8493 | 2674701.9757 | 1825539.0581 | 8164216.343 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668430.6659 | 38730284.9621 | 1778279.41 | 0.66287 | 26654.5158 | 58428.3353 | 543.3884 | 1191.1406
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16572 | 4 | 26654.68 | 58428.7312 | 543.3917 | 1191.1487 | 34.1344 | 1.9268 | 67.3885 | 927599.1303 | 0 | 1708347.8974 | 0 | 0 | 0 | 0 | 1028019.3408 | 2674695.449 | 1825534.6035 | 8164196.421 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668410.744 | 38730265.0401 | 2371373.7057 | 0.66286 | 26654.68 | 58428.7312 | 543.3917 | 1191.1487
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16571 | 4 | 26654.8033 | 58429.0284 | 543.3942 | 1191.1548 | 34.1343 | 1.9268 | 65.5326 | 927596.6853 | 0 | 1708345.5149 | 0 | 0 | 0 | 0 | 1028017.4581 | 2674690.5505 | 1825531.2601 | 8164181.4689 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668395.7919 | 38730250.0881 | 3162277.6602 | 0.66286 | 26654.8033 | 58429.0284 | 543.3942 | 1191.1548
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16571 | 4 | 26654.8959 | 58429.2514 | 543.3961 | 1191.1593 | 34.1343 | 1.9268 | 67.33 | 927594.8505 | 0 | 1708343.7272 | 0 | 0 | 0 | 0 | 1028016.0453 | 2674686.8748 | 1825528.7514 | 8164170.2493 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668384.5722 | 38730238.8684 | 4216965.0343 | 0.66286 | 26654.8959 | 58429.2514 | 543.3961 | 1191.1593
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16571 | 4 | 26654.9653 | 58429.4187 | 543.3975 | 1191.1627 | 34.1343 | 1.9268 | 66.1848 | 927593.4739 | 0 | 1708342.3861 | 0 | 0 | 0 | 0 | 1028014.9854 | 2674684.1171 | 1825526.8692 | 8164161.8317 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668376.1547 | 38730230.4509 | 5623413.2519 | 0.66285 | 26654.9653 | 58429.4187 | 543.3975 | 1191.1627
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16571 | 4 | 26655.0174 | 58429.5443 | 543.3986 | 1191.1653 | 34.1343 | 1.9268 | 66.608 | 927592.4412 | 0 | 1708341.3801 | 0 | 0 | 0 | 0 | 1028014.1903 | 2674682.0484 | 1825525.4573 | 8164155.5172 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668369.8401 | 38730224.1363 | 7498942.0933 | 0.66285 | 26655.0174 | 58429.5443 | 543.3986 | 1191.1653
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6696 | 5.8497 | 0.16571 | 4 | 26655.0565 | 58429.6384 | 543.3994 | 1191.1672 | 34.1343 | 1.9268 | 66.3487 | 927591.6665 | 0 | 1708340.6255 | 0 | 0 | 0 | 0 | 1028013.5939 | 2674680.4967 | 1825524.3982 | 8164150.7807 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17668365.1036 | 38730219.3998 | 10000000 | 0.66285 | 26655.0565 | 58429.6384 | 543.3994 | 1191.1672
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.012549 | 7.2162e-05 | 4 | 34502879.382 | 110162586.5831 | 703387.8648 | 2245813.3334 | 25.3134 | 1.0554 | 13.4616 | 7316.0003 | 0 | 1845.6362 | 0 | 0 | 0 | 5902.9712 | 5875.197 | 15286.0574 | 10433.0483 | 46658.9103 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 9959212.7361 | 31798292.0554 | 100 | 0.00028865 | 34502879.382 | 110162586.5831 | 703387.8648 | 2245813.3334
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.23373 | -0.011383 | 0.00018783 | 4 | 13232615.8511 | 42300316.7177 | 269764.7726 | 862349.1717 | 24.681 | 0.98273 | 26.3741 | 6497.7815 | 0 | 945.5114 | 0 | 0 | 0 | 2031.2973 | 3695.0902 | 9613.8666 | 6561.6615 | 29345.2085 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 9941899.0343 | 31780978.3536 | 133.3521 | 0.00075132 | 13232615.8511 | 42300316.7177 | 269764.7726 | 862349.1717
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.40413 | -0.0093139 | 0.00034811 | 4 | 7176749.275 | 22860886.2658 | 146307.7412 | 466050.0882 | 28.4805 | 1.4295 | 28.6333 | 13075.6888 | 0 | 7808.2133 | 0 | 0 | 0 | 5130.9822 | 10145.8049 | 26397.3031 | 18016.7018 | 80574.6941 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 9993128.5199 | 31832207.8392 | 177.8279 | 0.0013924 | 7176749.275 | 22860886.2658 | 146307.7412 | 466050.0882
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.58935 | -0.0026337 | 0.00061625 | 4 | 4075633.6195 | 12935355.5626 | 83087.304 | 263704.7195 | 30.7528 | 1.718 | 25.2648 | 20311.7017 | 0 | 15375.1305 | 0 | 0 | 0 | 7519.4521 | 16850.4509 | 43841.4167 | 29922.6677 | 133820.8196 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10046374.6453 | 31885453.9646 | 237.1374 | 0.002465 | 4075633.6195 | 12935355.5626 | 83087.304 | 263704.7195
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.82568 | 0.0087748 | 0.0010354 | 4 | 2441337.532 | 7714626.9019 | 49769.9677 | 157273.1042 | 32.3985 | 1.9408 | 31.6489 | 29109.1571 | 0 | 24803.1649 | 0 | 0 | 0 | 10057.4051 | 24948.1936 | 64910.0821 | 44302.4648 | 198130.4676 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10110684.2934 | 31949763.6127 | 316.2278 | 0.0041415 | 2441337.532 | 7714626.9019 | 49769.9677 | 157273.1042
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.025456 | 0.0016504 | 4 | 1542981.3004 | 4851105.0191 | 31455.7608 | 98896.3374 | 33.607 | 2.111 | 72.9685 | 39509.8186 | 0 | 36261.3185 | 0 | 0 | 0 | 12588.0192 | 34460.071 | 89658.0359 | 61193.4518 | 273670.7149 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10186224.5407 | 32025303.86 | 421.6965 | 0.0066017 | 1542981.3004 | 4851105.0191 | 31455.7608 | 98896.3374
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.048651 | 0.0025192 | 4 | 1019773.9328 | 3187011.0372 | 20789.471 | 64971.5307 | 34.5261 | 2.2427 | 103.0569 | 51881.4834 | 0 | 50295.3541 | 0 | 0 | 0 | 15226.7172 | 45787.3863 | 119129.3868 | 81308.2544 | 363628.5821 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10276182.4079 | 32115261.7272 | 562.3413 | 0.010077 | 1019773.9328 | 3187011.0372 | 20789.471 | 64971.5307
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.080039 | 0.0037183 | 4 | 698137.2426 | 2166475.3585 | 14232.472 | 44166.5306 | 35.2342 | 2.3445 | 138.3968 | 66600.7102 | 0 | 67501.3545 | 0 | 0 | 0 | 17991.6181 | 59316.5363 | 154329.4599 | 105333.0275 | 471072.7065 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10383626.5323 | 32222705.8516 | 749.8942 | 0.014873 | 698137.2426 | 2166475.3585 | 14232.472 | 44166.5306
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6692 | 0.12129 | 0.0053481 | 4 | 491262.8034 | 1512143.5162 | 10015.0567 | 30827.0909 | 35.7753 | 2.422 | 30.3594 | 83862.0378 | 0 | 88292.0158 | 0 | 0 | 0 | 20510.8678 | 75139.3193 | 195497.0957 | 133430.7849 | 596732.1213 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10509285.947 | 32348365.2663 | 1000 | 0.021392 | 491262.8034 | 1512143.5162 | 10015.0567 | 30827.0909
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5318 | 0.17677 | 0.0075468 | 4 | 353282.5524 | 1076733.5491 | 7202.1427 | 21950.6698 | 36.2028 | 2.4829 | 32.8754 | 104864.8579 | 0 | 114355.5126 | 0 | 0 | 0 | 23612.6802 | 94704.8898 | 246402.6966 | 168174.9035 | 752115.5407 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10664669.3665 | 32503748.6858 | 1333.5214 | 0.030187 | 353282.5524 | 1076733.5491 | 7202.1427 | 21950.6698
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6526 | 0.24946 | 0.010491 | 4 | 258549.1094 | 778954.1132 | 5270.8733 | 15880.0332 | 36.5305 | 2.5293 | 27.8979 | 129834.8808 | 0 | 146273.7804 | 0 | 0 | 0 | 26611.2449 | 118060.7634 | 307169.8887 | 209649.7607 | 937600.3188 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10850154.1446 | 32689233.4639 | 1778.2794 | 0.041966 | 258549.1094 | 778954.1132 | 5270.8733 | 15880.0332
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1038 | 0.34408 | 0.014414 | 4 | 192008.4145 | 570778.5933 | 3914.3512 | 11636.0937 | 36.7803 | 2.5643 | 51.8132 | 159473.2557 | 0 | 185274.8918 | 0 | 0 | 0 | 29209.3341 | 145843.4178 | 379454.6566 | 258985.6001 | 1158241.1562 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11070794.982 | 32909874.3013 | 2371.3737 | 0.057658 | 192008.4145 | 570778.5933 | 3914.3512 | 11636.0937
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9823 | 0.46695 | 0.019619 | 4 | 144421.247 | 422712.2635 | 2944.2225 | 8617.5613 | 36.9695 | 2.5904 | 38.2432 | 194700.6877 | 0 | 232972.2463 | 0 | 0 | 0 | 31121.6148 | 178929.874 | 465538.8287 | 317739.8165 | 1421003.068 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11333556.8938 | 33172636.2131 | 3162.2777 | 0.078476 | 144421.247 | 422712.2635 | 2944.2225 | 8617.5613
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3964 | 0.62523 | 0.026486 | 4 | 109902.7259 | 316043.4674 | 2240.5157 | 6442.9736 | 37.1099 | 2.6092 | 45.2567 | 236335.147 | 0 | 290961.4926 | 0 | 0 | 0 | 31528.4671 | 217941.7916 | 567039.8357 | 387016.3394 | 1730823.0733 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11643376.8991 | 33482456.2183 | 4216.965 | 0.10594 | 109902.7259 | 316043.4674 | 2240.5157 | 6442.9736
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3802 | 0.82159 | 0.035429 | 4 | 84575.317 | 238680.2252 | 1724.1822 | 4865.8192 | 37.2073 | 2.6214 | 46.5878 | 283780.7888 | 0 | 358915.9547 | 0 | 0 | 0 | 26636.0277 | 261039.7808 | 679171.9629 | 463548.8203 | 2073093.3351 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11985647.1609 | 33824726.4801 | 5623.4133 | 0.14172 | 84575.317 | 238680.2252 | 1724.1822 | 4865.8192
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.8225 | 1.0496 | 0.046779 | 4 | 65688.5094 | 182402.5379 | 1339.1491 | 3718.5225 | 37.2654 | 2.6271 | 39.9245 | 334470.3142 | 0 | 433573.6542 | 0 | 0 | 0 | 0 | 299537.1477 | 779334.2148 | 531911.6153 | 2378826.9463 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 12291380.7721 | 34130460.0913 | 7498.9421 | 0.18712 | 65688.5094 | 182402.5379 | 1339.1491 | 3718.5225
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.313 | 1.4096 | 0.062187 | 4 | 51746.8539 | 139543.4869 | 1054.9296 | 2844.7827 | 37.3022 | 2.6281 | 43.598 | 408899.3138 | 0 | 546553.5211 | 0 | 0 | 0 | 0 | 372626.6056 | 969497.9916 | 661702.3004 | 2959279.7325 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 12871833.5583 | 34710912.8775 | 10000 | 0.24875 | 51746.8539 | 139543.4869 | 1054.9296 | 2844.7827
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.4561 | 1.8781 | 0.081822 | 4 | 41477.2364 | 108204.8092 | 845.5696 | 2205.9014 | 37.289 | 2.6189 | 36.9282 | 496943.0926 | 0 | 685528.3836 | 0 | 0 | 0 | 0 | 461163.8757 | 1199853.8068 | 818924.8777 | 3662414.0364 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 13574967.8621 | 35414047.1814 | 13335.2143 | 0.32729 | 41477.2364 | 108204.8092 | 845.5696 | 2205.9014
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5593 | 2.4753 | 0.10599 | 4 | 33987.6874 | 85501.2574 | 692.885 | 1743.0588 | 37.214 | 2.5964 | 42.061 | 598443.8111 | 0 | 853313.6829 | 0 | 0 | 0 | 0 | 566185.4227 | 1473098.3292 | 1005419.8788 | 4496461.1248 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 14409014.9506 | 36248094.2698 | 17782.7941 | 0.42395 | 33987.6874 | 85501.2574 | 692.885 | 1743.0588
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.846 | 3.2156 | 0.13414 | 4 | 28644.6604 | 69345.5587 | 583.9601 | 1413.703 | 37.052 | 2.5545 | 35.6531 | 711040.2583 | 0 | 1050988.9079 | 0 | 0 | 0 | 0 | 687191.3748 | 1787930.9949 | 1220299.6424 | 5457451.1783 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 15370005.0041 | 37209084.3234 | 23713.7371 | 0.53657 | 28644.6604 | 69345.5587 | 583.9601 | 1413.703
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.254 | 4.0938 | 0.16413 | 4 | 25020.5753 | 58284.6694 | 510.0783 | 1188.2118 | 36.771 | 2.4861 | 39.3783 | 828408.755 | 0 | 1274860.2994 | 0 | 0 | 0 | 0 | 820274.9312 | 2134187.1094 | 1456626.5553 | 6514357.6503 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 16426911.4761 | 38265990.7953 | 31622.7766 | 0.65654 | 25020.5753 | 58284.6694 | 510.0783 | 1188.2118
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.2407 | 5.0709 | 0.19191 | 4 | 22815.1518 | 51264.4096 | 465.1177 | 1045.0943 | 36.347 | 2.387 | 39.6845 | 940037.6914 | 0 | 1514234.3168 | 0 | 0 | 0 | 0 | 957166.0832 | 2490349.8068 | 1699714.9147 | 7601502.8129 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 17514056.6387 | 39353135.9579 | 42169.6503 | 0.76765 | 22815.1518 | 51264.4096 | 465.1177 | 1045.0943
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9682 | 6.0893 | 0.21263 | 4 | 21816.7501 | 47493.9082 | 444.764 | 968.2276 | 35.7686 | 2.256 | 42.2249 | 1034720.7345 | 0 | 1755864.3737 | 0 | 0 | 0 | 0 | 1088328.1922 | 2831606.7093 | 1932629.7628 | 8643149.7724 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18555703.5982 | 40394782.9174 | 56234.1325 | 0.85053 | 21816.7501 | 47493.9082 | 444.764 | 968.2276
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.095 | 6.5476 | 0.2186 | 4 | 21722.7598 | 46698.3701 | 442.8478 | 952.0094 | 35.4586 | 2.1873 | 61.1605 | 1069689.1093 | 0 | 1862644.2634 | 0 | 0 | 0 | 0 | 1143610.0154 | 2975438.6733 | 2030798.0337 | 9082180.095 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18994733.9208 | 40833813.2401 | 74989.4209 | 0.87442 | 21722.7598 | 46698.3701 | 442.8478 | 952.0094
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0561 | 6.5447 | 0.21854 | 4 | 21725.8286 | 46708.8155 | 442.9104 | 952.2224 | 35.4591 | 2.1875 | 59.4638 | 1069415.9458 | 0 | 1861972.8149 | 0 | 0 | 0 | 0 | 1143241.6167 | 2974480.1755 | 2030143.8393 | 9079254.3922 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18991808.218 | 40830887.5373 | 100000 | 0.87416 | 21725.8286 | 46708.8155 | 442.9104 | 952.2224
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0413 | 6.5434 | 0.2185 | 4 | 21728.1724 | 46715.6128 | 442.9582 | 952.361 | 35.4588 | 2.1874 | 69.0938 | 1069275.6652 | 0 | 1861681.5968 | 0 | 0 | 0 | 0 | 1143073.3322 | 2974042.3337 | 2029845.0032 | 9077917.9311 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18990471.7569 | 40829551.0761 | 133352.1432 | 0.874 | 21728.1724 | 46715.6128 | 442.9582 | 952.361
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0218 | 6.5419 | 0.21847 | 4 | 21729.9555 | 46721.4324 | 442.9945 | 952.4796 | 35.4589 | 2.1875 | 66.3349 | 1069131.4815 | 0 | 1861338.5258 | 0 | 0 | 0 | 0 | 1142883.3029 | 2973547.9164 | 2029507.5533 | 9076408.7799 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18988962.6056 | 40828041.9249 | 177827.941 | 0.87386 | 21729.9555 | 46721.4324 | 442.9945 | 952.4796
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0024 | 6.5405 | 0.21844 | 4 | 21731.3076 | 46726.2184 | 443.0221 | 952.5772 | 35.4592 | 2.1876 | 64.7442 | 1069000.6202 | 0 | 1861008.5481 | 0 | 0 | 0 | 0 | 1142703.5757 | 2973080.3031 | 2029188.3976 | 9074981.4447 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18987535.2704 | 40826614.5897 | 237137.3706 | 0.87374 | 21731.3076 | 46726.2184 | 443.0221 | 952.5772
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9977 | 6.5401 | 0.21842 | 4 | 21732.3304 | 46729.039 | 443.043 | 952.6347 | 35.459 | 2.1875 | 63.9387 | 1068947.8763 | 0 | 1860908.9067 | 0 | 0 | 0 | 0 | 1142644.1454 | 2972925.6778 | 2029082.8626 | 9074509.4688 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18987063.2946 | 40826142.6139 | 316227.766 | 0.87368 | 21732.3304 | 46729.039 | 443.043 | 952.6347
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9855 | 6.5392 | 0.2184 | 4 | 21733.1024 | 46731.8596 | 443.0587 | 952.6922 | 35.4592 | 2.1876 | 51.036 | 1068868.0918 | 0 | 1860704.0512 | 0 | 0 | 0 | 0 | 1142533.1357 | 2972636.8534 | 2028885.734 | 9073627.8662 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18986181.6919 | 40825261.0112 | 421696.5034 | 0.87361 | 21733.1024 | 46731.8596 | 443.0587 | 952.6922
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9855 | 6.5391 | 0.21839 | 4 | 21733.6843 | 46733.2553 | 443.0706 | 952.7206 | 35.459 | 2.1876 | 52.9735 | 1068850.1756 | 0 | 1860686.5717 | 0 | 0 | 0 | 0 | 1142519.3315 | 2972600.9375 | 2028861.2207 | 9073518.237 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18986072.0628 | 40825151.3821 | 562341.3252 | 0.87358 | 21733.6843 | 46733.2553 | 443.0706 | 952.7206
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.5381 | 0.21838 | 4 | 21734.1222 | 46735.4811 | 443.0795 | 952.766 | 35.4594 | 2.1877 | 59.3763 | 1068768.7636 | 0 | 1860453.1106 | 0 | 0 | 0 | 0 | 1142396.531 | 2972281.4358 | 2028643.1542 | 9072542.9953 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18985096.8211 | 40824176.1404 | 749894.2093 | 0.87352 | 21734.1222 | 46735.4811 | 443.0795 | 952.766
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.5381 | 0.21837 | 4 | 21734.4516 | 46736.2709 | 443.0862 | 952.7821 | 35.4593 | 2.1877 | 61.5387 | 1068758.6284 | 0 | 1860443.2306 | 0 | 0 | 0 | 0 | 1142388.725 | 2972261.1263 | 2028629.2926 | 9072481.003 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18985034.8287 | 40824114.148 | 1000000 | 0.8735 | 21734.4516 | 46736.2709 | 443.0862 | 952.7821
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21837 | 4 | 21734.6991 | 46736.8646 | 443.0912 | 952.7942 | 35.4592 | 2.1876 | 60.5906 | 1068751.0117 | 0 | 1860435.8078 | 0 | 0 | 0 | 0 | 1142382.8596 | 2972245.8658 | 2028618.877 | 9072434.422 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984988.2477 | 40824067.567 | 1333521.4322 | 0.87349 | 21734.6991 | 46736.8646 | 443.0912 | 952.7942
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21837 | 4 | 21734.8851 | 46737.3105 | 443.095 | 952.8033 | 35.4591 | 2.1876 | 61.3929 | 1068745.2908 | 0 | 1860430.2338 | 0 | 0 | 0 | 0 | 1142378.4546 | 2972234.4048 | 2028611.0546 | 9072399.4385 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984953.2643 | 40824032.5836 | 1778279.41 | 0.87348 | 21734.8851 | 46737.3105 | 443.095 | 952.8033
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21837 | 4 | 21735.0247 | 46737.6454 | 443.0979 | 952.8101 | 35.4591 | 2.1876 | 61.1918 | 1068740.9955 | 0 | 1860426.0494 | 0 | 0 | 0 | 0 | 1142375.1475 | 2972225.8005 | 2028605.182 | 9072373.1749 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984927.0007 | 40824006.32 | 2371373.7057 | 0.87347 | 21735.0247 | 46737.6454 | 443.0979 | 952.8101
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21837 | 4 | 21735.1295 | 46737.8967 | 443.1 | 952.8152 | 35.459 | 2.1876 | 57.5755 | 1068737.7716 | 0 | 1860422.9091 | 0 | 0 | 0 | 0 | 1142372.6655 | 2972219.3427 | 2028600.7744 | 9072353.4633 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984907.2891 | 40823986.6084 | 3162277.6602 | 0.87347 | 21735.1295 | 46737.8967 | 443.1 | 952.8152
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21837 | 4 | 21735.2082 | 46738.0853 | 443.1016 | 952.8191 | 35.459 | 2.1876 | 60.3683 | 1068735.3523 | 0 | 1860420.5529 | 0 | 0 | 0 | 0 | 1142370.803 | 2972214.497 | 2028597.4671 | 9072338.6723 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984892.4981 | 40823971.8174 | 4216965.0343 | 0.87346 | 21735.2082 | 46738.0853 | 443.1016 | 952.8191
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9707 | 6.538 | 0.21836 | 4 | 21735.2672 | 46738.2269 | 443.1028 | 952.822 | 35.459 | 2.1876 | 58.7569 | 1068733.5372 | 0 | 1860418.7851 | 0 | 0 | 0 | 0 | 1142369.4057 | 2972210.8615 | 2028594.9858 | 9072327.5753 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18984881.4011 | 40823960.7204 | 5623413.2519 | 0.87346 | 21735.2672 | 46738.2269 | 443.1028 | 952.822
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9512 | 6.5367 | 0.21835 | 4 | 21735.3115 | 46739.8762 | 443.1037 | 952.8556 | 35.4598 | 2.1878 | 57.2308 | 1068643.0217 | 0 | 1860128.3246 | 0 | 0 | 0 | 0 | 1142220.825 | 2971824.2851 | 2028331.1394 | 9071147.5958 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18983701.4216 | 40822780.7408 | 7498942.0933 | 0.8734 | 21735.3115 | 46739.8762 | 443.1037 | 952.8556
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9512 | 6.5367 | 0.21835 | 4 | 21735.3446 | 46739.9557 | 443.1044 | 952.8572 | 35.4598 | 2.1878 | 56.9615 | 1068642.0012 | 0 | 1860127.3308 | 0 | 0 | 0 | 0 | 1142220.0395 | 2971822.2412 | 2028329.7444 | 9071141.3571 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18983695.1828 | 40822774.5021 | 10000000 | 0.8734 | 21735.3446 | 46739.9557 | 443.1044 | 952.8572
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.013556 | 6.7103e-05 | 4 | 38668952.2708 | 122980467.2122 | 788318.8957 | 2507123.1675 | 25.4054 | 1.2673 | 16.5241 | 8223.3046 | 0 | 1348.8379 | 0 | 0 | 0 | 7342.8664 | 6596.8534 | 17163.6594 | 11714.5502 | 52390.0719 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10379143.4914 | 33009219.0473 | 100 | 0.00026841 | 38668952.2708 | 122980467.2122 | 788318.8957 | 2507123.1675
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.23373 | -0.012318 | 0.00018124 | 4 | 14294703.2451 | 45510926.0312 | 291416.8607 | 927801.7852 | 24.7439 | 1.1915 | 25.0199 | 7359.8709 | 0 | 378.0236 | 0 | 0 | 0 | 3928.6953 | 4549.97 | 11838.0887 | 8079.7388 | 36134.3874 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10362887.8069 | 32992963.3628 | 133.3521 | 0.00072495 | 14294703.2451 | 45510926.0312 | 291416.8607 | 927801.7852
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.42358 | -0.010529 | 0.00035487 | 4 | 7343667.0185 | 23286249.1715 | 149710.5852 | 474721.6863 | 29.1315 | 1.7008 | 32.3244 | 15126.1435 | 0 | 8145.4817 | 0 | 0 | 0 | 8171.8883 | 12262.9702 | 31905.7331 | 21776.3184 | 97388.5352 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10424141.9547 | 33054217.5106 | 177.8279 | 0.0014195 | 7343667.0185 | 23286249.1715 | 149710.5852 | 474721.6863
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.62825 | -0.003238 | 0.00065123 | 4 | 4026202.6889 | 12713616.6276 | 82079.5877 | 259184.2714 | 31.6976 | 2.0183 | 31.9776 | 23618.6714 | 0 | 16584.2076 | 0 | 0 | 0 | 11846.1415 | 20299.118 | 52814.1411 | 36046.7365 | 161209.0161 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10487962.4356 | 33118037.9915 | 237.1374 | 0.0026049 | 4026202.6889 | 12713616.6276 | 82079.5877 | 259184.2714
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.86458 | 0.0084615 | 0.0011201 | 4 | 2356086.5853 | 7407175.2441 | 48032.0119 | 151005.2863 | 33.4043 | 2.241 | 36.86 | 32980.6245 | 0 | 26118.2166 | 0 | 0 | 0 | 14861.3478 | 28844.4737 | 75047.4037 | 51221.3951 | 229073.4615 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10555826.881 | 33185902.4369 | 316.2278 | 0.0044802 | 2356086.5853 | 7407175.2441 | 48032.0119 | 151005.2863
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1847 | 0.026517 | 0.0018133 | 4 | 1467338.1566 | 4587391.8106 | 29913.673 | 93520.187 | 34.7654 | 2.4243 | 78.1931 | 44798.486 | 0 | 38477.9471 | 0 | 0 | 0 | 18750.6453 | 39790.5606 | 103526.8764 | 70659.2204 | 316003.7359 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10642757.1553 | 33272832.7112 | 421.6965 | 0.0072531 | 1467338.1566 | 4587391.8106 | 29913.673 | 93520.187
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.05186 | 0.0027972 | 4 | 960506.4959 | 2983103.0008 | 19581.2241 | 60814.5896 | 35.801 | 2.5652 | 106.149 | 58896.442 | 0 | 53664.6773 | 0 | 0 | 0 | 23041.0792 | 52884.8574 | 137595.5508 | 93911.7907 | 419994.3975 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10746747.817 | 33376823.3729 | 562.3413 | 0.011189 | 960506.4959 | 2983103.0008 | 19581.2241 | 60814.5896
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.086123 | 0.0041566 | 4 | 653810.4992 | 2014911.8013 | 13328.8114 | 41076.7024 | 36.5955 | 2.6736 | 151.5199 | 75608.2913 | 0 | 72196.3551 | 0 | 0 | 0 | 27736.2364 | 68460.9442 | 178121.3337 | 121571.4702 | 543694.6308 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10870448.0503 | 33500523.6062 | 749.8942 | 0.016626 | 653810.4992 | 2014911.8013 | 13328.8114 | 41076.7024
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8519 | 0.13269 | 0.0060101 | 4 | 458502.9538 | 1399831.3612 | 9347.2029 | 28537.4557 | 37.219 | 2.7583 | 41.2818 | 95891.8889 | 0 | 95373.2582 | 0 | 0 | 0 | 33424.5353 | 87628.9762 | 227992.6208 | 155609.6485 | 695920.9279 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11022674.3474 | 33652749.9032 | 1000 | 0.024041 | 458502.9538 | 1399831.3612 | 9347.2029 | 28537.4557
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7681 | 0.19343 | 0.0085083 | 4 | 329127.0581 | 994069.513 | 6709.7003 | 20265.4516 | 37.691 | 2.822 | 35.5122 | 119675.0545 | 0 | 123368.0264 | 0 | 0 | 0 | 39294.7277 | 110111.7454 | 286488.1744 | 195534.0658 | 874471.7941 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11201225.2136 | 33831300.7695 | 1333.5214 | 0.034033 | 329127.0581 | 994069.513 | 6709.7003 | 20265.4516
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.964 | 0.27337 | 0.011856 | 4 | 240731.7329 | 717927.3865 | 4907.642 | 14635.9208 | 38.0551 | 2.8708 | 46.3521 | 148097.1018 | 0 | 157810.8635 | 0 | 0 | 0 | 45849.0562 | 137185.2384 | 356927.8497 | 243610.5916 | 1089480.7012 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11416234.1206 | 34046309.6765 | 1778.2794 | 0.047423 | 240731.7329 | 717927.3865 | 4907.642 | 14635.9208
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5083 | 0.37719 | 0.016315 | 4 | 178852.3366 | 525623.8402 | 3646.1468 | 10715.5529 | 38.3323 | 2.9074 | 43.0953 | 181759.979 | 0 | 199787.8191 | 0 | 0 | 0 | 52717.5818 | 169363.4981 | 440649.0809 | 300752.0522 | 1345030.0111 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11671783.4306 | 34301858.9865 | 2371.3737 | 0.065259 | 178852.3366 | 525623.8402 | 3646.1468 | 10715.5529
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5204 | 0.51286 | 0.022234 | 4 | 134703.1603 | 389155.8048 | 2746.1061 | 7933.4675 | 38.5437 | 2.9349 | 41.4366 | 222041.6393 | 0 | 251457.2618 | 0 | 0 | 0 | 60279.3559 | 208173.5202 | 541624.7973 | 369670.0534 | 1653246.6278 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11980000.0473 | 34610075.6032 | 3162.2777 | 0.088936 | 134703.1603 | 389155.8048 | 2746.1061 | 7933.4675
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1003 | 0.68729 | 0.03004 | 4 | 102731.667 | 291066.0225 | 2094.324 | 5933.7746 | 38.6998 | 2.9544 | 43.3613 | 269545.5907 | 0 | 314126.8375 | 0 | 0 | 0 | 67674.036 | 254025.121 | 660921.2573 | 451092.3386 | 2017385.1812 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 12344138.6007 | 34974214.1566 | 4216.965 | 0.12016 | 102731.667 | 291066.0225 | 2094.324 | 5933.7746
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3741 | 0.90917 | 0.040252 | 4 | 79308.5831 | 219862.0706 | 1616.8127 | 4482.1857 | 38.8102 | 2.967 | 42.4086 | 325076.372 | 0 | 389476.1065 | 0 | 0 | 0 | 74040.5015 | 307551.2622 | 800185.2967 | 546142.9072 | 2442472.4461 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 12769225.8656 | 35399301.4214 | 5623.4133 | 0.16101 | 79308.5831 | 219862.0706 | 1616.8127 | 4482.1857
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.4692 | 1.1874 | 0.053459 | 4 | 61995.6174 | 167824.7424 | 1263.8645 | 3421.3344 | 38.8804 | 2.9732 | 35.859 | 389154.4535 | 0 | 478951.1514 | 0 | 0 | 0 | 77939.2127 | 368957.4789 | 959951.6764 | 655186.7442 | 2930140.7171 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 13256894.1366 | 35886969.6925 | 7498.9421 | 0.21384 | 61995.6174 | 167824.7424 | 1263.8645 | 3421.3344
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.4197 | 1.5248 | 0.070196 | 4 | 49114.7711 | 129711.2464 | 1001.271 | 2644.3392 | 38.9125 | 2.9727 | 34.7092 | 460727.6654 | 0 | 581904.3535 | 0 | 0 | 0 | 75717.5468 | 436156.3306 | 1134789.3043 | 774517.0178 | 3463812.2185 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 13790565.6379 | 36420641.1938 | 10000 | 0.28078 | 49114.7711 | 129711.2464 | 1001.271 | 2644.3392
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.1419 | 1.9165 | 0.090767 | 4 | 39483.4556 | 101813.3596 | 804.9236 | 2075.603 | 38.908 | 2.9652 | 42.7446 | 537345.3573 | 0 | 695603.2039 | 0 | 0 | 0 | 61255.3635 | 504739.5306 | 1313228.7224 | 896305.5872 | 4008477.7649 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 14335231.1844 | 36965306.7403 | 13335.2143 | 0.36307 | 39483.4556 | 101813.3596 | 804.9236 | 2075.603
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8734 | 2.3127 | 0.11437 | 4 | 32145.4675 | 81611.7311 | 655.3288 | 1663.7655 | 38.8723 | 2.952 | 43.181 | 608809.0921 | 0 | 805126.4873 | 0 | 0 | 0 | 0 | 551434.876 | 1434720.4324 | 979226.1757 | 4379317.0634 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 14706070.4828 | 37336146.0387 | 17782.7941 | 0.45749 | 32145.4675 | 81611.7311 | 655.3288 | 1663.7655
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.1829 | 3.0139 | 0.14614 | 4 | 26780.3931 | 65492.0949 | 545.9545 | 1335.1449 | 38.7537 | 2.9176 | 46.6716 | 726642.5777 | 0 | 993759.3688 | 0 | 0 | 0 | 0 | 670956.7591 | 1745691.8551 | 1191470.5615 | 5328521.1222 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 15655274.5417 | 38285350.0976 | 23713.7371 | 0.58458 | 26780.3931 | 65492.0949 | 545.9545 | 1335.1449
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4876 | 3.8501 | 0.1814 | 4 | 23026.7314 | 54215.1793 | 469.4311 | 1105.2498 | 38.5331 | 2.8601 | 40.8137 | 852007.0029 | 0 | 1208285.8011 | 0 | 0 | 0 | 0 | 803514.1936 | 2090579.1082 | 1426863.1985 | 6381249.3043 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 16708002.7238 | 39338078.2797 | 31622.7766 | 0.72559 | 23026.7314 | 54215.1793 | 469.4311 | 1105.2498
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.3781 | 4.7915 | 0.2166 | 4 | 20554.7796 | 46674.8464 | 419.037 | 951.5299 | 38.1858 | 2.7743 | 42.1407 | 975607.2068 | 0 | 1439962.5047 | 0 | 0 | 0 | 0 | 942072.1875 | 2451078.5862 | 1672911.4997 | 7481631.9848 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 17808385.4042 | 40438460.9601 | 42169.6503 | 0.86639 | 20554.7796 | 46674.8464 | 419.037 | 951.5299
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9944 | 5.7764 | 0.24699 | 4 | 19106.1579 | 42012.2907 | 389.5049 | 856.4774 | 37.7097 | 2.661 | 47.9712 | 1086014.8004 | 0 | 1674218.7853 | 0 | 0 | 0 | 0 | 1076491.0984 | 2800809.0194 | 1911609.7066 | 8549143.4101 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 18875896.8295 | 41505972.3854 | 56234.1325 | 0.98795 | 19106.1579 | 42012.2907 | 389.5049 | 856.4774
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.3918 | 6.7394 | 0.26859 | 4 | 18468.2849 | 39532.2373 | 376.501 | 805.9181 | 37.1224 | 2.5253 | 46.827 | 1174581.3545 | 0 | 1897386.8078 | 0 | 0 | 0 | 0 | 1198067.5833 | 3117126.0943 | 2127502.6099 | 9514664.4497 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 19841417.8692 | 42471493.4251 | 74989.4209 | 1.0744 | 18468.2849 | 39532.2373 | 376.501 | 805.9181
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5265 | 7.2135 | 0.27567 | 4 | 18399.1077 | 38921.8632 | 375.0907 | 793.4748 | 36.7848 | 2.4489 | 59.8389 | 1210645.3775 | 0 | 2005627.7954 | 0 | 0 | 0 | 0 | 1254346.5374 | 3263552.3886 | 2227441.5645 | 9961613.6634 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20288367.0829 | 42918442.6388 | 100000 | 1.1027 | 18399.1077 | 38921.8632 | 375.0907 | 793.4748
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5017 | 7.2115 | 0.27561 | 4 | 18401.1304 | 38928.2296 | 375.1319 | 793.6046 | 36.7848 | 2.449 | 64.6033 | 1210439.0266 | 0 | 2005168.0274 | 0 | 0 | 0 | 0 | 1254086.7511 | 3262876.4777 | 2226980.2415 | 9959550.5243 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20286303.9438 | 42916379.4997 | 133352.1432 | 1.1024 | 18401.1304 | 38928.2296 | 375.1319 | 793.6046
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4823 | 7.2099 | 0.27557 | 4 | 18402.6684 | 38933.1102 | 375.1633 | 793.7041 | 36.7849 | 2.449 | 62.4887 | 1210279.1318 | 0 | 2004808.8398 | 0 | 0 | 0 | 0 | 1253884.3089 | 3262349.7648 | 2226620.7491 | 9957942.7944 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20284696.2139 | 42914771.7698 | 177827.941 | 1.1023 | 18402.6684 | 38933.1102 | 375.1633 | 793.7041
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4675 | 7.2087 | 0.27553 | 4 | 18403.8341 | 38936.8145 | 375.1871 | 793.7796 | 36.7849 | 2.4491 | 68.0382 | 1210157.5995 | 0 | 2004535.4904 | 0 | 0 | 0 | 0 | 1253730.3051 | 3261949.0783 | 2226347.2723 | 9956719.7455 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20283473.165 | 42913548.7209 | 237137.3706 | 1.1021 | 18403.8341 | 38936.8145 | 375.1871 | 793.7796
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.448 | 7.2072 | 0.2755 | 4 | 18404.7154 | 38940.1266 | 375.205 | 793.8472 | 36.7853 | 2.4492 | 67.3119 | 1210026.807 | 0 | 2004204.6384 | 0 | 0 | 0 | 0 | 1253550.2637 | 3261480.6476 | 2226027.5587 | 9955289.9153 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20282043.3348 | 42912118.8907 | 316227.766 | 1.102 | 18404.7154 | 38940.1266 | 375.205 | 793.8472
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.446 | 7.2069 | 0.27549 | 4 | 18405.3805 | 38941.8415 | 375.2186 | 793.8821 | 36.785 | 2.4492 | 71.3698 | 1209987.8234 | 0 | 2004145.5483 | 0 | 0 | 0 | 0 | 1253512.015 | 3261381.1322 | 2225959.6374 | 9954986.1563 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20281739.5758 | 42911815.1317 | 421696.5034 | 1.1019 | 18405.3805 | 38941.8415 | 375.2186 | 793.8821
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4286 | 7.2057 | 0.27546 | 4 | 18405.8817 | 38944.1196 | 375.2288 | 793.9286 | 36.7856 | 2.4493 | 68.1829 | 1209883.4433 | 0 | 2003861.6408 | 0 | 0 | 0 | 0 | 1253360.5828 | 3260987.1369 | 2225690.7275 | 9953783.5313 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20280536.9508 | 42910612.5067 | 562341.3252 | 1.1019 | 18405.8817 | 38944.1196 | 375.2288 | 793.9286
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4286 | 7.2056 | 0.27546 | 4 | 18406.2588 | 38945.0205 | 375.2365 | 793.9469 | 36.7854 | 2.4493 | 64.2151 | 1209866.7772 | 0 | 2003845.4831 | 0 | 0 | 0 | 0 | 1253347.7815 | 3260953.8305 | 2225667.9952 | 9953681.8676 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20280435.287 | 42910510.8429 | 749894.2093 | 1.1018 | 18406.2588 | 38945.0205 | 375.2365 | 793.9469
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.424 | 7.2052 | 0.27545 | 4 | 18406.5424 | 38945.9853 | 375.2423 | 793.9666 | 36.7854 | 2.4493 | 66.2361 | 1209832.3888 | 0 | 2003763.5829 | 0 | 0 | 0 | 0 | 1253302.4289 | 3260835.8324 | 2225587.4591 | 9953321.6921 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20280075.1116 | 42910150.6675 | 1000000 | 1.1018 | 18406.5424 | 38945.9853 | 375.2423 | 793.9666
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.424 | 7.2052 | 0.27544 | 4 | 18406.7555 | 38946.4944 | 375.2466 | 793.977 | 36.7853 | 2.4492 | 66.7544 | 1209822.973 | 0 | 2003754.458 | 0 | 0 | 0 | 0 | 1253295.1981 | 3260817.0192 | 2225574.6187 | 9953264.2669 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20280017.6864 | 42910093.2423 | 1333521.4322 | 1.1018 | 18406.7555 | 38946.4944 | 375.2466 | 793.977
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.424 | 7.2052 | 0.27544 | 4 | 18406.9156 | 38946.8768 | 375.2499 | 793.9848 | 36.7852 | 2.4492 | 65.3561 | 1209815.9011 | 0 | 2003747.6054 | 0 | 0 | 0 | 0 | 1253289.7676 | 3260802.8901 | 2225564.9753 | 9953221.1395 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20279974.559 | 42910050.1149 | 1778279.41 | 1.1018 | 18406.9156 | 38946.8768 | 375.2499 | 793.9848
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.424 | 7.2052 | 0.27544 | 4 | 18407.0358 | 38947.1639 | 375.2523 | 793.9906 | 36.7851 | 2.4492 | 64.4974 | 1209810.5917 | 0 | 2003742.4613 | 0 | 0 | 0 | 0 | 1253285.6907 | 3260792.2829 | 2225557.7356 | 9953188.7622 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20279942.1817 | 42910017.7376 | 2371373.7057 | 1.1017 | 18407.0358 | 38947.1639 | 375.2523 | 793.9906
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.424 | 7.2051 | 0.27544 | 4 | 18407.126 | 38947.3794 | 375.2542 | 793.995 | 36.7851 | 2.4492 | 63.0043 | 1209806.6067 | 0 | 2003738.6006 | 0 | 0 | 0 | 0 | 1253282.6309 | 3260784.3219 | 2225552.3021 | 9953164.4622 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20279917.8816 | 42909993.4375 | 3162277.6602 | 1.1017 | 18407.126 | 38947.3794 | 375.2542 | 793.995
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4091 | 7.2041 | 0.27542 | 4 | 18407.1937 | 38948.4607 | 375.2555 | 794.0171 | 36.7858 | 2.4494 | 64.6492 | 1209733.6796 | 0 | 2003512.508 | 0 | 0 | 0 | 0 | 1253166.0132 | 3260480.9066 | 2225345.2149 | 9952238.3222 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20278991.7417 | 42909067.2976 | 4216965.0343 | 1.1017 | 18407.1937 | 38948.4607 | 375.2555 | 794.0171
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4091 | 7.2041 | 0.27542 | 4 | 18407.2444 | 38948.5819 | 375.2566 | 794.0195 | 36.7857 | 2.4494 | 64.3863 | 1209731.4374 | 0 | 2003510.336 | 0 | 0 | 0 | 0 | 1253164.2916 | 3260476.4275 | 2225342.1579 | 9952224.6505 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20278978.0699 | 42909053.6258 | 5623413.2519 | 1.1017 | 18407.2444 | 38948.5819 | 375.2566 | 794.0195
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4091 | 7.2041 | 0.27542 | 4 | 18407.2825 | 38948.6729 | 375.2574 | 794.0214 | 36.7857 | 2.4494 | 61.5633 | 1209729.7554 | 0 | 2003508.7067 | 0 | 0 | 0 | 0 | 1253163.0002 | 3260473.0675 | 2225339.8646 | 9952214.3944 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20278967.8139 | 42909043.3698 | 7498942.0933 | 1.1017 | 18407.2825 | 38948.6729 | 375.2574 | 794.0214
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4091 | 7.2041 | 0.27542 | 4 | 18407.3111 | 38948.7411 | 375.2579 | 794.0228 | 36.7857 | 2.4494 | 64.4012 | 1209728.4937 | 0 | 2003507.4846 | 0 | 0 | 0 | 0 | 1253162.0315 | 3260470.5472 | 2225338.1444 | 9952206.7014 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 20278960.1209 | 42909035.6768 | 10000000 | 1.1017 | 18407.3111 | 38948.7411 | 375.2579 | 794.0228
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.014505 | 6.0961e-05 | 4 | 44308573.7985 | 140414811.697 | 903290.2087 | 2862545.8615 | 25.4762 | 1.4782 | 17.0345 | 9075.397 | 0 | 829.882 | 0 | 0 | 0 | 8668.2405 | 7243.6726 | 18846.5503 | 12863.1578 | 57526.9003 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 10804340.0043 | 34239183.0104 | 100 | 0.00024384 | 44308573.7985 | 140414811.697 | 903290.2087 | 2862545.8615
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.014117 | 0.0001744 | 4 | 15516457.8794 | 49109324.4648 | 316323.9814 | 1001160.0045 | 27.3895 | 1.6962 | 27.5847 | 12070.3873 | 0 | 3720.655 | 0 | 0 | 0 | 9289.2582 | 9781.3172 | 25448.9809 | 17369.4524 | 77680.051 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 10824493.1551 | 34259336.1611 | 133.3521 | 0.00069761 | 15516457.8794 | 49109324.4648 | 316323.9814 | 1001160.0045
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.44303 | -0.011738 | 0.00036182 | 4 | 7504039.053 | 23696487.8154 | 152979.9861 | 483084.956 | 29.773 | 1.9727 | 35.0967 | 17195.0139 | 0 | 8499.1703 | 0 | 0 | 0 | 10969.4018 | 14298.7985 | 37202.5407 | 25391.4985 | 113556.4236 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 10860369.5277 | 34295212.5337 | 177.8279 | 0.0014473 | 7504039.053 | 23696487.8154 | 152979.9861 | 483084.956
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.66251 | -0.0039686 | 0.00068951 | 4 | 3964129.8507 | 12461073.8126 | 80814.1489 | 254035.8445 | 32.5906 | 2.3139 | 26.1073 | 26817.7184 | 0 | 17636.0822 | 0 | 0 | 0 | 15723.2919 | 23469.0661 | 61061.6958 | 41675.8621 | 186383.7165 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 10933196.8205 | 34368039.8266 | 237.1374 | 0.002758 | 3964129.8507 | 12461073.8126 | 80814.1489 | 254035.8445
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.0088376 | 0.0012144 | 4 | 2266939.4586 | 7091304.2537 | 46214.6271 | 144565.8289 | 34.4809 | 2.5533 | 33.2454 | 37523.3155 | 0 | 28063.9221 | 0 | 0 | 0 | 19996.9847 | 33377.8467 | 86842.3104 | 59271.6613 | 265076.0406 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11011889.1447 | 34446732.1507 | 316.2278 | 0.0048576 | 2266939.4586 | 7091304.2537 | 46214.6271 | 144565.8289
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2625 | 0.028656 | 0.0019952 | 4 | 1392328.0516 | 4328801.6562 | 28384.4906 | 88248.4769 | 35.977 | 2.7474 | 89.6604 | 50945.5002 | 0 | 41492.6661 | 0 | 0 | 0 | 25346.9775 | 45936.2061 | 119516.5854 | 81572.5253 | 364810.4606 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11111623.5646 | 34546466.5707 | 421.6965 | 0.0079806 | 1392328.0516 | 4328801.6562 | 28384.4906 | 88248.4769
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.0566 | 0.003106 | 4 | 904002.8485 | 2790267.0872 | 18429.3208 | 56883.3687 | 37.1184 | 2.8967 | 118.0971 | 66988.6539 | 0 | 58011.2256 | 0 | 0 | 0 | 31418.8566 | 61003.3071 | 158718.0915 | 108328.3588 | 484468.4934 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11231281.5975 | 34666124.6035 | 562.3413 | 0.012424 | 904002.8485 | 2790267.0872 | 18429.3208 | 56883.3687
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 0.093624 | 0.0046434 | 4 | 612090.486 | 1873809.7445 | 12478.2925 | 38200.1462 | 37.974 | 3.0083 | 161.6373 | 85525.807 | 0 | 77658.7936 | 0 | 0 | 0 | 37636.943 | 78320.402 | 203773.6203 | 139079.683 | 621995.249 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11368808.353 | 34803651.3591 | 749.8942 | 0.018574 | 612090.486 | 1873809.7445 | 12478.2925 | 38200.1462
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0176 | 0.14363 | 0.0067403 | 4 | 427900.0846 | 1297110.3817 | 8723.322 | 26443.3496 | 38.6479 | 3.0957 | 38.6179 | 107910.6881 | 0 | 102082.0599 | 0 | 0 | 0 | 45017.9086 | 99454.1561 | 258759.3133 | 176608.5483 | 789832.6744 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11536645.7785 | 34971488.7845 | 1000 | 0.026961 | 427900.0846 | 1297110.3817 | 8723.322 | 26443.3496
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 0.21013 | 0.0095707 | 4 | 306656.0179 | 918808.3158 | 6251.5977 | 18731.1503 | 39.1715 | 3.163 | 37.1631 | 134745.0931 | 0 | 132224.3706 | 0 | 0 | 0 | 53574.9526 | 125012.3224 | 325256.4193 | 221994.1895 | 992807.3477 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11739620.4517 | 35174463.4578 | 1333.5214 | 0.038283 | 306656.0179 | 918808.3158 | 6251.5977 | 18731.1503
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2561 | 0.29717 | 0.013362 | 4 | 224178.3955 | 662633.8454 | 4570.1798 | 13508.6872 | 39.5732 | 3.2141 | 47.9842 | 166617.8059 | 0 | 169070.3869 | 0 | 0 | 0 | 63121.5639 | 155535.8052 | 404672.2602 | 276197.1328 | 1235214.955 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11982028.059 | 35416871.0651 | 1778.2794 | 0.053449 | 224178.3955 | 662633.8454 | 4570.1798 | 13508.6872
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8808 | 0.40983 | 0.018413 | 4 | 166578.9144 | 484769.658 | 3395.9365 | 9882.6852 | 39.8767 | 3.2519 | 50.4529 | 204205.9403 | 0 | 213794.2442 | 0 | 0 | 0 | 73329.7927 | 191618.6911 | 498552.5279 | 340272.3445 | 1521773.5408 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 12268586.6449 | 35703429.6509 | 2371.3737 | 0.07365 | 166578.9144 | 484769.658 | 3395.9365 | 9882.6852
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0493 | 0.56036 | 0.025131 | 4 | 125600.9184 | 358723.6337 | 2560.5446 | 7313.0665 | 40.1147 | 3.2811 | 42.254 | 250290.8179 | 0 | 270160.4061 | 0 | 0 | 0 | 86317.7216 | 236639.8888 | 615688.4491 | 420220.0177 | 1879317.3012 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 12626130.4053 | 36060973.4113 | 3162.2777 | 0.10053 | 125600.9184 | 358723.6337 | 2560.5446 | 7313.0665
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7802 | 0.75072 | 0.033967 | 4 | 95966.3531 | 268450.0546 | 1956.4039 | 5472.7175 | 40.2868 | 3.3013 | 37.8955 | 303650.3452 | 0 | 337281.3255 | 0 | 0 | 0 | 99029.4829 | 288584.8499 | 750838.5827 | 512462.7609 | 2291847.3471 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 13038660.4512 | 36473503.4572 | 4216.965 | 0.13587 | 95966.3531 | 268450.0546 | 1956.4039 | 5472.7175
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2561 | 0.99356 | 0.04552 | 4 | 74272.3371 | 202977.7468 | 1514.1421 | 4137.9759 | 40.4087 | 3.3142 | 45.2372 | 366230.4914 | 0 | 418234.4363 | 0 | 0 | 0 | 112067.2525 | 349647.5503 | 909711.2032 | 620896.5889 | 2776787.5225 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 13523600.6266 | 36958443.6326 | 5623.4133 | 0.18208 | 74272.3371 | 202977.7468 | 1514.1421 | 4137.9759
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5876 | 1.297 | 0.06043 | 4 | 58246.2343 | 155195.8168 | 1187.4283 | 3163.8766 | 40.4858 | 3.32 | 42.1629 | 438182.7685 | 0 | 514011.341 | 0 | 0 | 0 | 123785.1904 | 419631.927 | 1091796.1957 | 745173.3377 | 3332580.7603 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 14079393.8643 | 37514236.8704 | 7498.9421 | 0.24172 | 58246.2343 | 155195.8168 | 1187.4283 | 3163.8766
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8734 | 1.6683 | 0.079327 | 4 | 46331.1001 | 120185.9927 | 944.5221 | 2450.154 | 40.5207 | 3.3183 | 47.2926 | 519297.8907 | 0 | 625258.2079 | 0 | 0 | 0 | 132212.1487 | 497939.6164 | 1295536.7405 | 884230.446 | 3954475.0502 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 14701288.1542 | 38136131.1603 | 10000 | 0.31731 | 46331.1001 | 120185.9927 | 944.5221 | 2450.154
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.0808 | 2.106 | 0.1026 | 4 | 37437.669 | 94539.8064 | 763.2175 | 1927.3218 | 40.5137 | 3.3085 | 42.8049 | 607408.6092 | 0 | 750017.6577 | 0 | 0 | 0 | 133471.5794 | 581450.1601 | 1512814.0447 | 1032526.6707 | 4617688.7217 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 15364501.8258 | 38799344.8318 | 13335.2143 | 0.4104 | 37437.669 | 94539.8064 | 763.2175 | 1927.3218
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.0017 | 2.5963 | 0.13012 | 4 | 30787.1938 | 75812.2481 | 627.6386 | 1545.5352 | 40.4653 | 3.2902 | 43.5684 | 698433.1945 | 0 | 883437.1368 | 0 | 0 | 0 | 122040.5667 | 664525.2502 | 1728958.3882 | 1180049.6265 | 5277444.163 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 16024257.2671 | 39459100.2731 | 17782.7941 | 0.52048 | 30787.1938 | 75812.2481 | 627.6386 | 1545.5352
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0781 | 3.1011 | 0.16076 | 4 | 25805.3078 | 62248.3682 | 526.0761 | 1269.0172 | 40.3818 | 3.2647 | 48.4892 | 784943.5097 | 0 | 1015020.2747 | 0 | 0 | 0 | 87961.7786 | 736290.9696 | 1915678.0687 | 1307489.6452 | 5847384.2464 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 16594197.3505 | 40029040.3565 | 23713.7371 | 0.64305 | 25805.3078 | 62248.3682 | 526.0761 | 1269.0172
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.7988 | 3.5845 | 0.19276 | 4 | 21964.1047 | 52358.0958 | 447.768 | 1067.3906 | 40.2729 | 3.2343 | 45.0345 | 861634.3164 | 0 | 1136358.0889 | 0 | 0 | 0 | 0 | 779217.038 | 2027362.8936 | 1383716.833 | 6188289.1699 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 16935102.274 | 40369945.28 | 31622.7766 | 0.77104 | 21964.1047 | 52358.0958 | 447.768 | 1067.3906
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5639 | 4.482 | 0.23384 | 4 | 19281.1072 | 44335.4181 | 393.0715 | 903.8375 | 39.9987 | 3.1622 | 45.6481 | 994244.1333 | 0 | 1358807.0674 | 0 | 0 | 0 | 0 | 917689.9683 | 2387641.0534 | 1629614.0801 | 7287996.3026 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 18034809.4066 | 41469652.4127 | 42169.6503 | 0.93536 | 19281.1072 | 44335.4181 | 393.0715 | 903.8375
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.1721 | 5.4351 | 0.27229 | 4 | 17557.4143 | 39073.753 | 357.9316 | 796.5713 | 39.6068 | 3.0639 | 45.8041 | 1117714.0212 | 0 | 1586652.1822 | 0 | 0 | 0 | 0 | 1054702.8193 | 2744120.3866 | 1872918.5499 | 8376107.9591 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 19122921.0632 | 42557764.0692 | 56234.1325 | 1.0892 | 17557.4143 | 39073.753 | 357.9316 | 796.5713
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.6 | 6.3697 | 0.30367 | 4 | 16562.7503 | 35855.8471 | 337.6541 | 730.9699 | 39.1226 | 2.9466 | 38.4672 | 1221985.5677 | 0 | 1803774.4936 | 0 | 0 | 0 | 0 | 1180046.4239 | 3070238.7342 | 2095501.0232 | 9371546.2427 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 20118359.3467 | 43553202.3528 | 74989.4209 | 1.2147 | 16562.7503 | 35855.8471 | 337.6541 | 730.9699
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1165 | 7.235 | 0.32571 | 4 | 16102.1317 | 34089.5661 | 328.2637 | 694.9619 | 38.5759 | 2.8176 | 47.3035 | 1302858.8899 | 0 | 2000639.5127 | 0 | 0 | 0 | 0 | 1288364.377 | 3352059.8292 | 2287849.7113 | 10231772.3201 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 20978585.4242 | 44413428.4302 | 100000 | 1.3028 | 16102.1317 | 34089.5661 | 328.2637 | 694.9619
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2929 | 7.8651 | 0.33681 | 4 | 16009.1637 | 33403.8924 | 326.3685 | 680.9835 | 38.115 | 2.7112 | 52.362 | 1351763.3158 | 0 | 2142088.0504 | 0 | 0 | 0 | 0 | 1362602.0328 | 3545210.9813 | 2419679.3415 | 10821343.7219 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21568156.8259 | 45002999.8319 | 133352.1432 | 1.3472 | 16009.1637 | 33403.8924 | 326.3685 | 680.9835
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2681 | 7.8631 | 0.33675 | 4 | 16010.5056 | 33408.3335 | 326.3958 | 681.0741 | 38.1153 | 2.7113 | 57.4481 | 1351562.2823 | 0 | 2141632.2679 | 0 | 0 | 0 | 0 | 1362345.8746 | 3544544.5101 | 2419224.4612 | 10819309.396 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21566122.5001 | 45000965.5061 | 177827.941 | 1.347 | 16010.5056 | 33408.3335 | 326.3958 | 681.0741
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2675 | 7.8628 | 0.33672 | 4 | 16011.5224 | 33410.7876 | 326.4165 | 681.1241 | 38.1145 | 2.7112 | 71.6002 | 1351498.0015 | 0 | 2141563.5016 | 0 | 0 | 0 | 0 | 1362293.9862 | 3544409.5073 | 2419132.319 | 10818897.3157 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21565710.4197 | 45000553.4258 | 237137.3706 | 1.3469 | 16011.5224 | 33410.7876 | 326.4165 | 681.1241
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.248 | 7.8612 | 0.33668 | 4 | 16012.2909 | 33413.5971 | 326.4322 | 681.1814 | 38.1149 | 2.7113 | 70.198 | 1351357.192 | 0 | 2141221.7605 | 0 | 0 | 0 | 0 | 1362105.7915 | 3543919.8631 | 2418798.1269 | 10817402.734 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21564215.8381 | 44999058.8441 | 316227.766 | 1.3467 | 16012.2909 | 33413.5971 | 326.4322 | 681.1814
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.246 | 7.8609 | 0.33666 | 4 | 16012.8708 | 33415.0802 | 326.444 | 681.2116 | 38.1146 | 2.7112 | 68.9962 | 1351312.492 | 0 | 2141157.2653 | 0 | 0 | 0 | 0 | 1362063.2054 | 3543809.0628 | 2418722.5033 | 10817064.5288 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21563877.6329 | 44998720.6389 | 421696.5034 | 1.3467 | 16012.8708 | 33415.0802 | 326.444 | 681.2116
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2286 | 7.8596 | 0.33664 | 4 | 16013.3076 | 33416.9977 | 326.4529 | 681.2507 | 38.1151 | 2.7114 | 68.5928 | 1351201.5025 | 0 | 2140865.7561 | 0 | 0 | 0 | 0 | 1361906.2308 | 3543400.6473 | 2418443.7514 | 10815817.888 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21562630.992 | 44997473.9981 | 562341.3252 | 1.3465 | 16013.3076 | 33416.9977 | 326.4529 | 681.2507
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2286 | 7.8595 | 0.33663 | 4 | 16013.6363 | 33417.7804 | 326.4596 | 681.2667 | 38.1149 | 2.7113 | 67.5857 | 1351181.7665 | 0 | 2140846.7894 | 0 | 0 | 0 | 0 | 1361891.1368 | 3543361.3756 | 2418416.9476 | 10815698.0158 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21562511.1198 | 44997354.1259 | 749894.2093 | 1.3465 | 16013.6363 | 33417.7804 | 326.4596 | 681.2667
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.224 | 7.8591 | 0.33662 | 4 | 16013.8834 | 33418.6022 | 326.4647 | 681.2834 | 38.1149 | 2.7113 | 67.5991 | 1351144.3991 | 0 | 2140761.7491 | 0 | 0 | 0 | 0 | 1361843.3978 | 3543237.1686 | 2418332.1738 | 10815318.8884 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21562131.9924 | 44996974.9985 | 1000000 | 1.3465 | 16013.8834 | 33418.6022 | 326.4647 | 681.2834
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.224 | 7.8591 | 0.33661 | 4 | 16014.0691 | 33419.0444 | 326.4685 | 681.2924 | 38.1148 | 2.7113 | 69.2421 | 1351133.2502 | 0 | 2140751.037 | 0 | 0 | 0 | 0 | 1361834.872 | 3543214.9862 | 2418317.0339 | 10815251.1793 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21562064.2833 | 44996907.2893 | 1333521.4322 | 1.3464 | 16014.0691 | 33419.0444 | 326.4685 | 681.2924
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.224 | 7.8591 | 0.33661 | 4 | 16014.2086 | 33419.3765 | 326.4713 | 681.2992 | 38.1147 | 2.7113 | 65.8311 | 1351124.8769 | 0 | 2140742.9925 | 0 | 0 | 0 | 0 | 1361828.469 | 3543198.327 | 2418305.6636 | 10815200.3291 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21562013.4331 | 44996856.4391 | 1778279.41 | 1.3464 | 16014.2086 | 33419.3765 | 326.4713 | 681.2992
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.224 | 7.859 | 0.3366 | 4 | 16014.3133 | 33419.6258 | 326.4734 | 681.3043 | 38.1146 | 2.7113 | 68.0749 | 1351118.5906 | 0 | 2140736.9534 | 0 | 0 | 0 | 0 | 1361823.6621 | 3543185.8205 | 2418297.1277 | 10815162.1542 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21561975.2583 | 44996818.2643 | 2371373.7057 | 1.3464 | 16014.3133 | 33419.6258 | 326.4734 | 681.3043
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2091 | 7.858 | 0.33659 | 4 | 16014.3919 | 33420.5594 | 326.475 | 681.3233 | 38.1153 | 2.7115 | 68.0942 | 1351041.786 | 0 | 2140505.936 | 0 | 0 | 0 | 0 | 1361703.6116 | 3542873.4735 | 2418083.9445 | 10814208.7516 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21561021.8557 | 44995864.8617 | 3162277.6602 | 1.3464 | 16014.3919 | 33420.5594 | 326.475 | 681.3233
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2091 | 7.858 | 0.33659 | 4 | 16014.4508 | 33420.6998 | 326.4762 | 681.3262 | 38.1153 | 2.7114 | 69.3127 | 1351038.2476 | 0 | 2140502.537 | 0 | 0 | 0 | 0 | 1361700.906 | 3542866.4342 | 2418079.14 | 10814187.2648 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21561000.3689 | 44995843.3749 | 4216965.0343 | 1.3463 | 16014.4508 | 33420.6998 | 326.4762 | 681.3262
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2091 | 7.858 | 0.33659 | 4 | 16014.4951 | 33420.8051 | 326.4771 | 681.3283 | 38.1152 | 2.7114 | 68.4461 | 1351035.5929 | 0 | 2140499.987 | 0 | 0 | 0 | 0 | 1361698.8762 | 3542861.1529 | 2418075.5354 | 10814171.1444 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21560984.2485 | 44995827.2545 | 5623413.2519 | 1.3463 | 16014.4951 | 33420.8051 | 326.4771 | 681.3283
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2091 | 7.858 | 0.33658 | 4 | 16014.5282 | 33420.8841 | 326.4778 | 681.3299 | 38.1152 | 2.7114 | 67.5353 | 1351033.6015 | 0 | 2140498.0741 | 0 | 0 | 0 | 0 | 1361697.3535 | 3542857.1912 | 2418072.8314 | 10814159.0516 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21560972.1556 | 44995815.1617 | 7498942.0933 | 1.3463 | 16014.5282 | 33420.8841 | 326.4778 | 681.3299
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2091 | 7.8579 | 0.33658 | 4 | 16014.5531 | 33420.9434 | 326.4783 | 681.3311 | 38.1152 | 2.7114 | 69.3345 | 1351032.1077 | 0 | 2140496.6392 | 0 | 0 | 0 | 0 | 1361696.2113 | 3542854.2195 | 2418070.8032 | 10814149.9808 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 21560963.0849 | 44995806.0909 | 10000000 | 1.3463 | 16014.5531 | 33420.9434 | 326.4783 | 681.3311
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.25578 | -0.015402 | 5.3823e-05 | 4 | 52183730.3973 | 164836924.7756 | 1063835.9279 | 3360423.67 | 25.5301 | 1.6882 | 18.0464 | 9882.3172 | 0 | 235.0209 | 0 | 0 | 0 | 9910.0933 | 7810.6982 | 20321.8346 | 13870.0697 | 62030.0339 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11234762.9134 | 35488144.5831 | 100 | 0.00021529 | 52183730.3973 | 164836924.7756 | 1063835.9279 | 3360423.67
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.015274 | 0.00017011 | 4 | 16542976.7184 | 52186559.0957 | 337250.9564 | 1063893.5947 | 27.5249 | 1.9146 | 28.4149 | 13013.4 | 0 | 3259.801 | 0 | 0 | 0 | 10782.7675 | 10551.8277 | 27453.6912 | 18737.7084 | 83799.1957 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11256532.0752 | 35509913.7449 | 133.3521 | 0.00068044 | 16542976.7184 | 52186559.0957 | 337250.9564 | 1063893.5947
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.46248 | -0.012944 | 0.00036901 | 4 | 7657194.283 | 24088694.0758 | 156102.2626 | 491080.6111 | 30.4068 | 2.2454 | 36.2395 | 19288.5518 | 0 | 8867.7725 | 0 | 0 | 0 | 13659.1998 | 16308.0544 | 42430.2122 | 28959.4917 | 129513.2823 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11302246.1618 | 35555627.8315 | 177.8279 | 0.001476 | 7657194.283 | 24088694.0758 | 156102.2626 | 491080.6111
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.69881 | -0.0046095 | 0.00073141 | 4 | 3891513.8273 | 12181469.9122 | 79333.773 | 248335.7408 | 33.4958 | 2.6129 | 42.1941 | 30182.5622 | 0 | 18801.5529 | 0 | 0 | 0 | 19597.3852 | 26746.7851 | 69589.6484 | 47496.3649 | 212414.2988 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11385147.1783 | 35638528.848 | 237.1374 | 0.0029256 | 3891513.8273 | 12181469.9122 | 79333.773 | 248335.7408
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.0094849 | 0.0013186 | 4 | 2175724.2138 | 6773935.8607 | 44355.081 | 138095.8449 | 35.5779 | 2.87 | 36.6836 | 42401.6608 | 0 | 30244.792 | 0 | 0 | 0 | 25239.8124 | 38175.6434 | 99325.1933 | 67791.4854 | 303178.5873 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11475911.4668 | 35729293.1365 | 316.2278 | 0.0052745 | 2175724.2138 | 6773935.8607 | 44355.081 | 138095.8449
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3402 | 0.030941 | 0.0021962 | 4 | 1318990.6452 | 4079875.2114 | 26889.4084 | 83173.7746 | 37.1832 | 3.0718 | 95.5822 | 57302.2316 | 0 | 44578.8124 | 0 | 0 | 0 | 31826.8755 | 52146.0886 | 135673.426 | 92599.9011 | 414127.3353 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11586860.2148 | 35840241.8845 | 421.6965 | 0.0087846 | 1318990.6452 | 4079875.2114 | 26889.4084 | 83173.7746
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.060922 | 0.0034475 | 4 | 849734.3636 | 2608475.7091 | 17322.9844 | 53177.3056 | 38.405 | 3.2259 | 128.6812 | 74919.655 | 0 | 62008.1561 | 0 | 0 | 0 | 39120.9144 | 68659.0029 | 178636.6418 | 121923.1786 | 545267.5488 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11718000.4283 | 35971382.098 | 562.3413 | 0.01379 | 849734.3636 | 2608475.7091 | 17322.9844 | 53177.3056
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4099 | 0.10153 | 0.0051834 | 4 | 572679.3648 | 1742435.4893 | 11674.8435 | 35521.9043 | 39.3473 | 3.3441 | 179.3828 | 95789.3097 | 0 | 83251.6896 | 0 | 0 | 0 | 47299.4356 | 88272.7696 | 229667.6393 | 156752.883 | 701033.7268 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11873766.6063 | 36127148.276 | 749.8942 | 0.020734 | 572679.3648 | 1742435.4893 | 11674.8435 | 35521.9043
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.15708 | 0.0075555 | 4 | 399272.501 | 1201783.5239 | 8139.71 | 24499.9827 | 40.0949 | 3.4371 | 40.2021 | 121288.5305 | 0 | 109971.0973 | 0 | 0 | 0 | 57392.1238 | 112574.1831 | 292894.9324 | 199906.8098 | 894027.677 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12066760.5565 | 36320142.2262 | 1000 | 0.030222 | 399272.501 | 1201783.5239 | 8139.71 | 24499.9827
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 0.2295 | 0.010755 | 4 | 285759.4774 | 849541.1634 | 5825.5935 | 17319.0457 | 40.6617 | 3.5069 | 42.2234 | 151160.326 | 0 | 142189.663 | 0 | 0 | 0 | 68384.3975 | 141076.4107 | 367051.882 | 250520.4516 | 1120383.1309 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12293116.0104 | 36546497.6801 | 1333.5214 | 0.043019 | 285759.4774 | 849541.1634 | 5825.5935 | 17319.0457
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5922 | 0.32495 | 0.015043 | 4 | 208832.7489 | 611890.8755 | 4257.3381 | 12474.2231 | 41.1006 | 3.5603 | 47.9647 | 186909.9179 | 0 | 181857.5808 | 0 | 0 | 0 | 81129.6698 | 175459.8957 | 456510.6569 | 311577.9037 | 1393445.6247 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12566178.5042 | 36819560.1739 | 1778.2794 | 0.060173 | 208832.7489 | 611890.8755 | 4257.3381 | 12474.2231
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3413 | 0.44967 | 0.020759 | 4 | 155280.3845 | 447362.6608 | 3165.6007 | 9120.0929 | 41.4369 | 3.6005 | 54.834 | 229526.0908 | 0 | 230491.1144 | 0 | 0 | 0 | 95684.5333 | 216723.678 | 563870.5541 | 384853.2396 | 1721149.2103 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12893882.0897 | 37147263.7595 | 2371.3737 | 0.083036 | 155280.3845 | 447362.6608 | 3165.6007 | 9120.0929
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5876 | 0.61056 | 0.028329 | 4 | 117212.7953 | 331245.5324 | 2389.5414 | 6752.8882 | 41.6902 | 3.63 | 45.4566 | 279834.2108 | 0 | 289516.0348 | 0 | 0 | 0 | 111697.81 | 265608.7416 | 691059.4619 | 471662.2826 | 2109378.5416 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 13282111.4211 | 37535493.0908 | 3162.2777 | 0.11332 | 117212.7953 | 331245.5324 | 2389.5414 | 6752.8882
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4723 | 0.81774 | 0.038299 | 4 | 89709.8404 | 248025.203 | 1828.8564 | 5056.3292 | 41.8782 | 3.6508 | 49.8621 | 339311.5943 | 0 | 361249.2041 | 0 | 0 | 0 | 129372.2994 | 323673.9082 | 842133.1144 | 574773.1547 | 2570513.275 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 13743246.1545 | 37996627.8242 | 4216.965 | 0.1532 | 89709.8404 | 248025.203 | 1828.8564 | 5056.3292
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1381 | 1.0816 | 0.051319 | 4 | 69589.0903 | 187739.7824 | 1418.6677 | 3827.3294 | 42.0111 | 3.6637 | 53.6891 | 408975.5884 | 0 | 447639.6142 | 0 | 0 | 0 | 148199.7286 | 391877.8232 | 1019585.7108 | 695888.198 | 3112166.6632 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 14284899.5427 | 38538281.2124 | 5623.4133 | 0.20527 | 69589.0903 | 187739.7824 | 1418.6677 | 3827.3294
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.382 | 1.3893 | 0.067827 | 4 | 54729.6956 | 144123.3585 | 1115.7389 | 2938.1496 | 42.089 | 3.6682 | 28.2178 | 483573.3277 | 0 | 542797.9109 | 0 | 0 | 0 | 160477.9287 | 462871.1752 | 1204295.8501 | 821956.6635 | 3675972.8561 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 14848705.7356 | 39102087.4053 | 7498.9421 | 0.27131 | 54729.6956 | 144123.3585 | 1115.7389 | 2938.1496
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2501 | 1.8129 | 0.089288 | 4 | 43679.8796 | 111587.6281 | 890.4734 | 2274.8647 | 42.1303 | 3.6653 | 48.9704 | 578904.337 | 0 | 668019.5093 | 0 | 0 | 0 | 182606.9145 | 557516.9967 | 1450544.8631 | 990026.6748 | 4427619.2954 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 15600352.1749 | 39853733.8446 | 10000 | 0.35715 | 43679.8796 | 111587.6281 | 890.4734 | 2274.8647
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.7398 | 2.2846 | 0.11526 | 4 | 35444.8028 | 88049.169 | 722.5902 | 1795.0014 | 42.1217 | 3.6534 | 39.963 | 676228.3757 | 0 | 800130.8578 | 0 | 0 | 0 | 192598.9824 | 650893.7042 | 1693491.9017 | 1155843.0207 | 5169186.8425 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 16341919.722 | 40595301.3917 | 13335.2143 | 0.46105 | 35444.8028 | 88049.169 | 722.5902 | 1795.0014
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.0091 | 2.8154 | 0.14588 | 4 | 29294.7708 | 70857.9759 | 597.2135 | 1444.5357 | 42.0673 | 3.632 | 44.2409 | 777240.0483 | 0 | 942117.5357 | 0 | 0 | 0 | 192545.2758 | 745642.1153 | 1940007.8318 | 1324095.2084 | 5921648.0152 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 17094380.8947 | 41347762.5644 | 17782.7941 | 0.58353 | 29294.7708 | 70857.9759 | 597.2135 | 1444.5357
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.6534 | 3.3766 | 0.1801 | 4 | 24705.1844 | 58370.9752 | 503.6486 | 1189.9713 | 41.9705 | 3.6015 | 41.4853 | 875829.9742 | 0 | 1086098.2549 | 0 | 0 | 0 | 177154.7897 | 834242.3773 | 2170527.5391 | 1481429.6453 | 6625282.5803 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 17798015.4598 | 42051397.1295 | 23713.7371 | 0.72042 | 24705.1844 | 58370.9752 | 503.6486 | 1189.9713
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.0197 | 3.9213 | 0.21584 | 4 | 21281.0393 | 49372.3536 | 433.8428 | 1006.5222 | 41.8433 | 3.5651 | 42.5331 | 964301.1137 | 0 | 1220663.3628 | 0 | 0 | 0 | 139939.455 | 906712.5333 | 2359080.0193 | 1610120.5874 | 7200817.0716 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 18373549.951 | 42626931.6207 | 31622.7766 | 0.86338 | 21281.0393 | 49372.3536 | 433.8428 | 1006.5222
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.8183 | 4.1443 | 0.24357 | 4 | 18675.3236 | 43569.3684 | 380.7217 | 888.2205 | 41.7852 | 3.549 | 39.4033 | 996279.2933 | 0 | 1270880.9111 | 0 | 0 | 0 | 0 | 884192.4797 | 2300487.4595 | 1570129.9614 | 7021970.1051 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 18194702.9846 | 42448084.6543 | 42169.6503 | 0.97426 | 18675.3236 | 43569.3684 | 380.7217 | 888.2205
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.3445 | 5.0544 | 0.28835 | 4 | 16721.6369 | 37749.4476 | 340.8932 | 769.5735 | 41.4763 | 3.4668 | 47.1927 | 1129585.2479 | 0 | 1490131.6024 | 0 | 0 | 0 | 0 | 1021689.5716 | 2658226.688 | 1814294.3357 | 8113927.4456 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 19286660.3251 | 43540041.9948 | 56234.1325 | 1.1534 | 16721.6369 | 37749.4476 | 340.8932 | 769.5735
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9392 | 5.9655 | 0.32801 | 4 | 15480.3739 | 33965.4015 | 315.5884 | 692.4307 | 41.0751 | 3.3646 | 43.776 | 1247486.4418 | 0 | 1702990.8465 | 0 | 0 | 0 | 0 | 1150686.1424 | 2993849.3044 | 2043363.6677 | 9138376.4028 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 20311109.2823 | 44564490.952 | 74989.4209 | 1.3121 | 15480.3739 | 33965.4015 | 315.5884 | 692.4307
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6519 | 6.8077 | 0.35927 | 4 | 14753.768 | 31630.799 | 300.7755 | 644.8366 | 40.6248 | 3.2533 | 42.6227 | 1342997.6869 | 0 | 1895155.9272 | 0 | 0 | 0 | 0 | 1262879.9095 | 3285754.4722 | 2242594.9428 | 10029382.9385 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 21202115.818 | 45455497.4877 | 100000 | 1.4371 | 14753.768 | 31630.799 | 300.7755 | 644.8366
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1124 | 7.5554 | 0.38165 | 4 | 14377.3461 | 30264.3273 | 293.1016 | 616.9792 | 40.1526 | 3.1392 | 46.1541 | 1416273.4862 | 0 | 2062941.078 | 0 | 0 | 0 | 0 | 1356893.68 | 3530359.0183 | 2409542.5716 | 10776009.8342 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 21948742.7137 | 46202124.3834 | 133352.1432 | 1.5266 | 14377.3461 | 30264.3273 | 293.1016 | 616.9792
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9682 | 8.1846 | 0.39612 | 4 | 14228.6996 | 29535.4747 | 290.0713 | 602.1206 | 39.7025 | 3.0326 | 38.3577 | 1469310.5238 | 0 | 2202475.5358 | 0 | 0 | 0 | 0 | 1431996.5632 | 3725761.3147 | 2542908.654 | 11372452.5915 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22545185.471 | 46798567.1407 | 177827.941 | 1.5845 | 14228.6996 | 29535.4747 | 290.0713 | 602.1206
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5204 | 8.5067 | 0.40173 | 4 | 14212.5954 | 29305.5417 | 289.743 | 597.4331 | 39.4506 | 2.9737 | 55.1403 | 1493122.9936 | 0 | 2273434.0234 | 0 | 0 | 0 | 0 | 1468957.2366 | 3821925.4052 | 2608542.6217 | 11665982.2806 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22838715.16 | 47092096.8298 | 237137.3706 | 1.6069 | 14212.5954 | 29305.5417 | 289.743 | 597.4331
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5157 | 8.5061 | 0.4017 | 4 | 14213.2727 | 29307.3447 | 289.7568 | 597.4699 | 39.4501 | 2.9737 | 55.8943 | 1493046.7343 | 0 | 2273311.693 | 0 | 0 | 0 | 0 | 1468879.7867 | 3821723.8962 | 2608405.0877 | 11665367.1979 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22838100.0774 | 47091481.7471 | 316227.766 | 1.6068 | 14213.2727 | 29307.3447 | 289.7568 | 597.4699
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5151 | 8.5059 | 0.40168 | 4 | 14213.7836 | 29308.5856 | 289.7672 | 597.4952 | 39.4496 | 2.9736 | 58.5513 | 1493003.4431 | 0 | 2273263.4747 | 0 | 0 | 0 | 0 | 1468844.0979 | 3821631.0414 | 2608341.7125 | 11665083.7696 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22837816.6491 | 47091198.3188 | 421696.5034 | 1.6067 | 14213.7836 | 29308.5856 | 289.7672 | 597.4952
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5003 | 8.5047 | 0.40165 | 4 | 14214.1684 | 29310.1226 | 289.775 | 597.5265 | 39.4501 | 2.9737 | 65.8199 | 1492898.9767 | 0 | 2273004.7353 | 0 | 0 | 0 | 0 | 1468702.4477 | 3821262.4965 | 2608090.173 | 11663958.8291 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22836691.7085 | 47090073.3782 | 562341.3252 | 1.6066 | 14214.1684 | 29310.1226 | 289.775 | 597.5265
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5003 | 8.5046 | 0.40164 | 4 | 14214.458 | 29310.8103 | 289.781 | 597.5405 | 39.4498 | 2.9737 | 65.27 | 1492876.3102 | 0 | 2272983.1845 | 0 | 0 | 0 | 0 | 1468685.2029 | 3821217.6292 | 2608059.5501 | 11663821.8769 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22836554.7564 | 47089936.4261 | 749894.2093 | 1.6066 | 14214.458 | 29310.8103 | 289.781 | 597.5405
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5003 | 8.5046 | 0.40164 | 4 | 14214.6758 | 29311.3273 | 289.7854 | 597.5511 | 39.4495 | 2.9736 | 65.4105 | 1492859.2679 | 0 | 2272966.9818 | 0 | 0 | 0 | 0 | 1468672.2374 | 3821183.8955 | 2608036.5262 | 11663718.9086 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22836451.7881 | 47089833.4578 | 1000000 | 1.6065 | 14214.6758 | 29311.3273 | 289.7854 | 597.5511
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.5031 | 0.40161 | 4 | 14214.8393 | 29312.5339 | 289.7887 | 597.5757 | 39.4505 | 2.9739 | 68.7677 | 1492748.9024 | 0 | 2272652.8474 | 0 | 0 | 0 | 0 | 1468506.6824 | 3820753.1555 | 2607742.5373 | 11662404.1251 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22835137.0046 | 47088518.6743 | 1333521.4322 | 1.6064 | 14214.8393 | 29312.5339 | 289.7887 | 597.5757
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.5031 | 0.4016 | 4 | 14214.9621 | 29312.8255 | 289.7912 | 597.5816 | 39.4503 | 2.9738 | 66.8698 | 1492739.2919 | 0 | 2272643.7113 | 0 | 0 | 0 | 0 | 1468499.3712 | 3820734.1333 | 2607729.5542 | 11662346.0619 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22835078.9414 | 47088460.6111 | 1778279.41 | 1.6064 | 14214.9621 | 29312.8255 | 289.7912 | 597.5816
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.4016 | 4 | 14215.0543 | 29313.0444 | 289.7931 | 597.5861 | 39.4503 | 2.9738 | 63.6139 | 1492732.077 | 0 | 2272636.8526 | 0 | 0 | 0 | 0 | 1468493.8825 | 3820719.8529 | 2607719.8075 | 11662302.4725 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22835035.352 | 47088417.0217 | 2371373.7057 | 1.6064 | 14215.0543 | 29313.0444 | 289.7931 | 597.5861
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.4016 | 4 | 14215.1235 | 29313.2087 | 289.7945 | 597.5894 | 39.4502 | 2.9738 | 64.6025 | 1492726.662 | 0 | 2272631.7051 | 0 | 0 | 0 | 0 | 1468489.7632 | 3820709.1352 | 2607712.4925 | 11662269.758 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22835002.6375 | 47088384.3072 | 3162277.6602 | 1.6064 | 14215.1235 | 29313.2087 | 289.7945 | 597.5894
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.4016 | 4 | 14215.1754 | 29313.332 | 289.7956 | 597.5919 | 39.4501 | 2.9738 | 63.7452 | 1492722.5988 | 0 | 2272627.8427 | 0 | 0 | 0 | 0 | 1468486.6722 | 3820701.093 | 2607707.0035 | 11662245.2103 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22834978.0898 | 47088359.7595 | 4216965.0343 | 1.6064 | 14215.1754 | 29313.332 | 289.7956 | 597.5919
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.40159 | 4 | 14215.2144 | 29313.4246 | 289.7964 | 597.5938 | 39.4501 | 2.9738 | 63.5639 | 1492719.5504 | 0 | 2272624.945 | 0 | 0 | 0 | 0 | 1468484.3532 | 3820695.0594 | 2607702.8855 | 11662226.7935 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22834959.673 | 47088341.3427 | 5623413.2519 | 1.6064 | 14215.2144 | 29313.4246 | 289.7964 | 597.5938
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.40159 | 4 | 14215.2436 | 29313.4939 | 289.797 | 597.5952 | 39.4501 | 2.9738 | 67.289 | 1492717.2636 | 0 | 2272622.7712 | 0 | 0 | 0 | 0 | 1468482.6136 | 3820690.5333 | 2607699.7963 | 11662212.978 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22834945.8575 | 47088327.5272 | 7498942.0933 | 1.6064 | 14215.2436 | 29313.4939 | 289.797 | 597.5952
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4808 | 8.503 | 0.40159 | 4 | 14215.2655 | 29313.546 | 289.7974 | 597.5963 | 39.45 | 2.9738 | 67.0069 | 1492715.5483 | 0 | 2272621.1407 | 0 | 0 | 0 | 0 | 1468481.3087 | 3820687.1383 | 2607697.4792 | 11662202.6151 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 22834935.4946 | 47088317.1643 | 10000000 | 1.6064 | 14215.2655 | 29313.546 | 289.7974 | 597.5963
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1726 | [19 empty] | 100 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.016376 | 0.00016448 | 4 | 17774484.152 | 55903766.1894 | 362356.9012 | 1139673.8892 | 27.6371 | 2.1316 | 28.3544 | 13912.8956 | 0 | 2800.7228 | 0 | 0 | 0 | 12190.7122 | 11272.689 | 29329.2243 | 20017.7982 | 89524.0422 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 11694036.7879 | 36779728.3348 | 133.3521 | 0.00065791 | 17774484.152 | 55903766.1894 | 362356.9012 | 1139673.8892
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.49674 | -0.013914 | 0.00037661 | 4 | 7804125.5269 | 24456573.6436 | 159097.6547 | 498580.3337 | 31.2909 | 2.5482 | 30.3895 | 22131.8247 | 0 | 9876.2485 | 0 | 0 | 0 | 17012.7396 | 19118.117 | 49741.4187 | 33949.5403 | 151829.8887 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 11756342.6345 | 36842034.1814 | 177.8279 | 0.0015064 | 7804125.5269 | 24456573.6436 | 159097.6547 | 498580.3337
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | -0.0052935 | 0.00077742 | 4 | 3808235.4724 | 11875239.8517 | 77636.0311 | 242092.8268 | 34.3749 | 2.9104 | 35.0901 | 33534.9474 | 0 | 19910.7582 | 0 | 0 | 0 | 23341.262 | 29946.9174 | 77915.736 | 53179.0908 | 237828.7118 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 11842341.4576 | 36928033.0045 | 237.1374 | 0.0031097 | 3808235.4724 | 11875239.8517 | 77636.0311 | 242092.8268
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.010004 | 0.0014332 | 4 | 2083468.2683 | 6459144.2839 | 42474.3187 | 131678.3929 | 36.6435 | 3.1844 | 30.76 | 47228.9693 | 0 | 32287.0511 | 0 | 0 | 0 | 30253.0731 | 42809.9464 | 111382.6991 | 76020.9808 | 339982.7199 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 11944495.4657 | 37030187.0126 | 316.2278 | 0.005733 | 2083468.2683 | 6459144.2839 | 42474.3187 | 131678.3929
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.033376 | 0.002418 | 4 | 1247778.5351 | 3841367.4819 | 25437.6532 | 78311.472 | 38.3857 | 3.3974 | 107.6958 | 63865.8997 | 0 | 47734.8497 | 0 | 0 | 0 | 38287.3441 | 58456.3565 | 152091.4485 | 103805.5388 | 464241.4372 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12068754.183 | 37154445.7299 | 421.6965 | 0.0096722 | 1247778.5351 | 3841367.4819 | 25437.6532 | 78311.472
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.066592 | 0.0038267 | 4 | 798238.5403 | 2437090.8543 | 16273.1723 | 49683.3935 | 39.7282 | 3.5613 | 144.5428 | 83837.7016 | 0 | 66808.3214 | 0 | 0 | 0 | 47599.6206 | 77315.801 | 201159.8546 | 137295.7342 | 614017.0336 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12218529.7794 | 37304221.3263 | 562.3413 | 0.015307 | 798238.5403 | 2437090.8543 | 16273.1723 | 49683.3935
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.111 | 0.0057827 | 4 | 535759.2403 | 1620283.1543 | 10922.1768 | 33031.6637 | 40.7429 | 3.6842 | 193.0734 | 107076.6693 | 0 | 89641.8197 | 0 | 0 | 0 | 57675.0393 | 99213.476 | 258133.1132 | 176181.1538 | 787921.2713 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12392434.0171 | 37478125.564 | 749.8942 | 0.023131 | 535759.2403 | 1620283.1543 | 10922.1768 | 33031.6637
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.17038 | 0.0084528 | 4 | 372681.5935 | 1114613.4656 | 7597.6184 | 22722.9031 | 41.5332 | 3.7789 | 33.0889 | 134773.3955 | 0 | 117636.5055 | 0 | 0 | 0 | 69275.6272 | 125457.356 | 326414.3055 | 222784.4706 | 996341.6603 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12600854.4061 | 37686545.953 | 1000 | 0.033811 | 372681.5935 | 1114613.4656 | 7597.6184 | 22722.9031
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5038 | 0.25003 | 0.012062 | 4 | 266448.9977 | 786369.3683 | 5431.9232 | 16031.2032 | 42.1548 | 3.8525 | 47.5862 | 168298.6993 | 0 | 152499.6937 | 0 | 0 | 0 | 83240.9803 | 157575.3556 | 409978.7522 | 279818.9226 | 1251412.4037 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12855925.1495 | 37941616.6964 | 1333.5214 | 0.048249 | 266448.9977 | 786369.3683 | 5431.9232 | 16031.2032
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9166 | 0.35318 | 0.016893 | 4 | 194689.3801 | 565925.8731 | 3969.0064 | 11537.1644 | 42.6271 | 3.9076 | 47.1906 | 207645.7927 | 0 | 194583.519 | 0 | 0 | 0 | 98633.7323 | 195336.5872 | 508225.7308 | 346874.5043 | 1551299.8663 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 13155812.6121 | 38241504.159 | 1778.2794 | 0.067573 | 194689.3801 | 565925.8731 | 3969.0064 | 11537.1644
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7628 | 0.48871 | 0.023333 | 4 | 144843.7243 | 413618.2222 | 2952.8352 | 8432.1669 | 42.9927 | 3.9495 | 51.8652 | 254861.494 | 0 | 246501.8224 | 0 | 0 | 0 | 116691.8289 | 241041.5066 | 627140.5559 | 428036.3158 | 1914273.5236 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 13518786.2694 | 38604477.8163 | 2371.3737 | 0.093334 | 144843.7243 | 413618.2222 | 2952.8352 | 8432.1669
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1406 | 0.66401 | 0.031862 | 4 | 109461.3182 | 306292.281 | 2231.517 | 6244.1824 | 43.2688 | 3.9801 | 48.5039 | 310767.9337 | 0 | 309692.3578 | 0 | 0 | 0 | 137017.7714 | 295416.4445 | 768612.9904 | 524594.1594 | 2346101.6571 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 13950614.4029 | 39036305.9498 | 3162.2777 | 0.12745 | 109461.3182 | 306292.281 | 2231.517 | 6244.1824
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1808 | 0.88884 | 0.043079 | 4 | 83919.6388 | 229497.559 | 1710.8153 | 4678.6182 | 43.4729 | 4.0014 | 46.3495 | 376588.2529 | 0 | 386156.6875 | 0 | 0 | 0 | 159474.9816 | 359665.7696 | 935776.5549 | 638686.727 | 2856348.9735 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 14460861.7192 | 39546553.2661 | 4216.965 | 0.17232 | 83919.6388 | 229497.559 | 1710.8153 | 4678.6182
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0271 | 1.1741 | 0.057698 | 4 | 65242.3514 | 173935.9422 | 1330.0536 | 3545.9194 | 43.6167 | 4.0142 | 45.9256 | 453379.8019 | 0 | 477869.1185 | 0 | 0 | 0 | 183593.0283 | 434788.36 | 1131230.1254 | 772087.805 | 3452948.2391 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 15057460.9849 | 40143152.5318 | 5623.4133 | 0.23079 | 65242.3514 | 173935.9422 | 1330.0536 | 3545.9194
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.8191 | 1.5303 | 0.076496 | 4 | 51453.2359 | 133436.8051 | 1048.9438 | 2720.2898 | 43.707 | 4.0187 | 45.6852 | 541710.1543 | 0 | 586408.1438 | 0 | 0 | 0 | 208347.5755 | 521221.6907 | 1356111.9219 | 925574.252 | 4139373.7381 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 15743886.4839 | 40829578.0308 | 7498.9421 | 0.30598 | 51453.2359 | 133436.8051 | 1048.9438 | 2720.2898
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.5996 | 1.9616 | 0.10014 | 4 | 41206.5672 | 103835.6721 | 840.0516 | 2116.8306 | 43.7464 | 4.0143 | 50.511 | 640217.2337 | 0 | 711122.5886 | 0 | 0 | 0 | 230873.8189 | 617063.3201 | 1605472.1817 | 1095767.7532 | 4900516.8962 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 16505029.642 | 41590721.1889 | 10000 | 0.40054 | 41206.5672 | 103835.6721 | 840.0516 | 2116.8306
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.3593 | 2.4678 | 0.12901 | 4 | 33565.4444 | 82177.4124 | 684.277 | 1675.2977 | 43.7356 | 4.0001 | 56.6177 | 746850.557 | 0 | 850526.0796 | 0 | 0 | 0 | 248316.4361 | 719820.2984 | 1872824.7609 | 1278241.382 | 5716579.514 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 17321092.2598 | 42406783.8067 | 13335.2143 | 0.51604 | 33565.4444 | 82177.4124 | 684.277 | 1675.2977
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.9038 | 3.0355 | 0.16287 | 4 | 27858.76 | 66363.307 | 567.9385 | 1352.9058 | 43.6734 | 3.9748 | 59.0688 | 857103.2222 | 0 | 999915.2863 | 0 | 0 | 0 | 256290.6166 | 824190.5588 | 2144374.7692 | 1463579.8425 | 6545454.2955 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 18149967.0413 | 43235658.5882 | 17782.7941 | 0.6515 | 27858.76 | 66363.307 | 567.9385 | 1352.9058
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.7682 | 3.6306 | 0.20038 | 4 | 23612.0115 | 54908.974 | 481.3628 | 1119.3937 | 43.568 | 3.9406 | 42.8078 | 963870.4306 | 0 | 1150130.3033 | 0 | 0 | 0 | 249835.9782 | 921896.3177 | 2398585.1118 | 1637083.6248 | 7321401.7666 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 18925914.5123 | 44011606.0592 | 23713.7371 | 0.80154 | 23612.0115 | 54908.974 | 481.3628 | 1119.3937
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4487 | 4.2154 | 0.23948 | 4 | 20454.0313 | 46641.8541 | 416.9831 | 950.8573 | 43.4277 | 3.8993 | 44.8998 | 1060954.202 | 0 | 1292456.542 | 0 | 0 | 0 | 225873.5403 | 1005920.8709 | 2617199.7633 | 1786292.6165 | 7988697.5349 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 19593210.2807 | 44678901.8276 | 31622.7766 | 0.95791 | 20454.0313 | 46641.8541 | 416.9831 | 950.8573
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.413 | 4.7492 | 0.27761 | 4 | 18105.4969 | 40696.4584 | 369.105 | 829.6524 | 43.2698 | 3.8551 | 48.4024 | 1143277.65 | 0 | 1418347.9839 | 0 | 0 | 0 | 182864.6193 | 1070351.1988 | 2784834.2599 | 1900706.605 | 8500382.3169 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 20104895.0627 | 45190586.6096 | 42169.6503 | 1.1104 | 18105.4969 | 40696.4584 | 369.105 | 829.6524
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.987 | 5.1809 | 0.31192 | 4 | 16347.7324 | 36453.3143 | 333.2706 | 743.1501 | 43.1228 | 3.8152 | 58.9467 | 1205407.2515 | 0 | 1517200.4421 | 0 | 0 | 0 | 116203.4609 | 1107136.3502 | 2880541.6784 | 1966028.8847 | 8792518.0678 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 20397030.8136 | 45482722.3605 | 56234.1325 | 1.2477 | 16347.7324 | 36453.3143 | 333.2706 | 743.1501
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.2102 | 5.5119 | 0.34122 | 4 | 14949.733 | 33328.9511 | 304.7705 | 679.4557 | 42.9973 | 3.7817 | 47.9205 | 1250204.8295 | 0 | 1591116.8849 | 0 | 0 | 0 | 0 | 1108115.4686 | 2883089.1436 | 1967767.5821 | 8800293.9087 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 20404806.6545 | 45490498.2014 | 74989.4209 | 1.3649 | 14949.733 | 33328.9511 | 304.7705 | 679.4557
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2439 | 6.3362 | 0.38037 | 4 | 14017.5335 | 30505.3299 | 285.7664 | 621.8924 | 42.6257 | 3.6851 | 41.687 | 1358754.8263 | 0 | 1780396.3712 | 0 | 0 | 0 | 0 | 1224268.967 | 3185296.7201 | 2174030.4628 | 9722747.3474 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 21327260.0932 | 46412951.6401 | 100000 | 1.5215 | 14017.5335 | 30505.3299 | 285.7664 | 621.8924
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1318 | 7.0712 | 0.41097 | 4 | 13448.6631 | 28708.6302 | 274.1692 | 585.2643 | 42.2317 | 3.5854 | 42.3714 | 1445280.4485 | 0 | 1945980.8442 | 0 | 0 | 0 | 0 | 1322591.9042 | 3441112.8337 | 2348630.2168 | 10503596.2474 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 22108108.9932 | 47193800.5401 | 133352.1432 | 1.6439 | 13448.6631 | 28708.6302 | 274.1692 | 585.2643
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4339 | 7.6849 | 0.43316 | 4 | 13119.639 | 27597.9575 | 267.4616 | 562.6217 | 41.8608 | 3.4935 | 45.1897 | 1510267.6287 | 0 | 2082295.3091 | 0 | 0 | 0 | 0 | 1401099.5457 | 3645373.6129 | 2488042.3958 | 11127078.4922 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 22731591.238 | 47817282.7849 | 177827.941 | 1.7326 | 13119.639 | 27597.9575 | 267.4616 | 562.6217
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.3601 | 8.1948 | 0.44875 | 4 | 12940.8931 | 26916.095 | 263.8176 | 548.721 | 41.5169 | 3.4095 | 42.959 | 1558686.8048 | 0 | 2194502.634 | 0 | 0 | 0 | 0 | 1463743.8811 | 3808361.3236 | 2599284.8573 | 11624579.5009 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 23229092.2467 | 48314783.7936 | 237137.3706 | 1.795 | 12940.8931 | 26916.095 | 263.8176 | 548.721
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9166 | 8.6023 | 0.45928 | 4 | 12853.6685 | 26508.6985 | 262.0394 | 540.4157 | 41.2199 | 3.3379 | 47.4997 | 1593745.0929 | 0 | 2283559.426 | 0 | 0 | 0 | 0 | 1512148.7624 | 3934300.8953 | 2685241.2029 | 12008995.3795 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 23613508.1253 | 48699199.6722 | 316227.766 | 1.8371 | 12853.6685 | 26508.6985 | 262.0394 | 540.4157
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.2092 | 8.916 | 0.46615 | 4 | 12818.6464 | 26272.3509 | 261.3254 | 535.5974 | 40.978 | 3.2802 | 49.4972 | 1618511.1329 | 0 | 2351797.7672 | 0 | 0 | 0 | 0 | 1548420.471 | 4028672.4409 | 2749651.7219 | 12297053.5339 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 23901566.2797 | 48987257.8266 | 421696.5034 | 1.8646 | 12818.6464 | 26272.3509 | 261.3254 | 535.5974
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.6198 | 9.1647 | 0.47075 | 4 | 12811.7694 | 26133.8411 | 261.1852 | 532.7737 | 40.777 | 3.2326 | 36.8453 | 1636659.8195 | 0 | 2405718.4962 | 0 | 0 | 0 | 0 | 1576527.5431 | 4101801.2769 | 2799563.6551 | 12520270.7908 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24124783.5366 | 49210475.0835 | 562341.3252 | 1.883 | 12811.7694 | 26133.8411 | 261.1852 | 532.7737
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3271 | 9.1434 | 0.47029 | 4 | 12814.105 | 26149.285 | 261.2329 | 533.0885 | 40.7922 | 3.2362 | 49.0821 | 1634999.7702 | 0 | 2401140.4967 | 0 | 0 | 0 | 0 | 1574094.7041 | 4095471.5288 | 2795243.4719 | 12500949.9716 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24105462.7174 | 49191154.2643 | 749894.2093 | 1.8812 | 12814.105 | 26149.285 | 261.2329 | 533.0885
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3265 | 9.1433 | 0.47028 | 4 | 12814.2986 | 26149.7672 | 261.2368 | 533.0984 | 40.792 | 3.2362 | 64.623 | 1634977.2497 | 0 | 2401112.1777 | 0 | 0 | 0 | 0 | 1574074.8767 | 4095419.942 | 2795208.2629 | 12500792.509 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24105305.2548 | 49190996.8017 | 1000000 | 1.8811 | 12814.2986 | 26149.7672 | 261.2368 | 533.0984
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3265 | 9.1432 | 0.47027 | 4 | 12814.4441 | 26150.1119 | 261.2398 | 533.1054 | 40.7918 | 3.2362 | 61.5774 | 1634962.8771 | 0 | 2401098.6757 | 0 | 0 | 0 | 0 | 1574064.0056 | 4095391.6576 | 2795188.9582 | 12500706.1743 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24105218.9201 | 49190910.467 | 1333521.4322 | 1.8811 | 12814.4441 | 26150.1119 | 261.2398 | 533.1054
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3265 | 9.1432 | 0.47027 | 4 | 12814.5533 | 26150.3707 | 261.242 | 533.1107 | 40.7917 | 3.2361 | 61.019 | 1634952.0834 | 0 | 2401088.5358 | 0 | 0 | 0 | 0 | 1574055.8415 | 4095370.4164 | 2795174.4606 | 12500641.3378 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24105154.0836 | 49190845.6305 | 1778279.41 | 1.8811 | 12814.5533 | 26150.3707 | 261.242 | 533.1107
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47024 | 4 | 12814.6353 | 26151.2632 | 261.2437 | 533.1289 | 40.7927 | 3.2364 | 59.9588 | 1634843.3984 | 0 | 2400774.0067 | 0 | 0 | 0 | 0 | 1573890.788 | 4094940.981 | 2794881.3621 | 12499330.5362 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103843.282 | 49189534.8289 | 2371373.7057 | 1.881 | 12814.6353 | 26151.2632 | 261.2437 | 533.1289
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47024 | 4 | 12814.6968 | 26151.409 | 261.2449 | 533.1318 | 40.7927 | 3.2364 | 60.4534 | 1634837.3208 | 0 | 2400768.2974 | 0 | 0 | 0 | 0 | 1573886.1911 | 4094929.0208 | 2794873.1991 | 12499294.0293 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103806.7751 | 49189498.322 | 3162277.6602 | 1.881 | 12814.6968 | 26151.409 | 261.2449 | 533.1318
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47024 | 4 | 12814.743 | 26151.5183 | 261.2459 | 533.1341 | 40.7926 | 3.2364 | 62.027 | 1634832.7604 | 0 | 2400764.0135 | 0 | 0 | 0 | 0 | 1573882.7418 | 4094920.0465 | 2794867.0739 | 12499266.6362 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103779.382 | 49189470.9289 | 4216965.0343 | 1.8809 | 12814.743 | 26151.5183 | 261.2459 | 533.1341
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47023 | 4 | 12814.7776 | 26151.6004 | 261.2466 | 533.1357 | 40.7926 | 3.2364 | 61.1013 | 1634829.3391 | 0 | 2400760.7995 | 0 | 0 | 0 | 0 | 1573880.154 | 4094913.3136 | 2794862.4786 | 12499246.0847 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103758.8305 | 49189450.3774 | 5623413.2519 | 1.8809 | 12814.7776 | 26151.6004 | 261.2466 | 533.1357
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47023 | 4 | 12814.8036 | 26151.6619 | 261.2471 | 533.137 | 40.7925 | 3.2364 | 63.1054 | 1634826.7725 | 0 | 2400758.3885 | 0 | 0 | 0 | 0 | 1573878.2128 | 4094908.2629 | 2794859.0313 | 12499230.668 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103743.4137 | 49189434.9607 | 7498942.0933 | 1.8809 | 12814.8036 | 26151.6619 | 261.2471 | 533.137
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.307 | 9.1417 | 0.47023 | 4 | 12814.8231 | 26151.7081 | 261.2475 | 533.1379 | 40.7925 | 3.2364 | 61.7586 | 1634824.8474 | 0 | 2400756.58 | 0 | 0 | 0 | 0 | 1573876.7567 | 4094904.4744 | 2794856.4456 | 12499219.104 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24103731.8498 | 49189423.3967 | 10000000 | 1.8809 | 12814.8231 | 26151.7081 | 261.2475 | 533.1379
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9033 | [19 empty] | 100 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.017427 | 0.0001576 | 4 | 19253153.5339 | 60388974.1425 | 392501.5766 | 1231110.92 | 27.73 | 2.3473 | 28.7582 | 14774.7955 | 0 | 2340.498 | 0 | 0 | 0 | 13530.8557 | 11951.9982 | 31096.6475 | 21224.1009 | 94918.8958 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12137071.5987 | 38068844.2363 | 133.3521 | 0.00063039 | 19253153.5339 | 60388974.1425 | 392501.5766 | 1231110.92
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.51156 | -0.015191 | 0.00038498 | 4 | 7927776.8096 | 24767525.1754 | 161618.4534 | 504919.5013 | 31.8352 | 2.8129 | 31.3871 | 24079.0844 | 0 | 10080.8627 | 0 | 0 | 0 | 19418.4026 | 20895.5564 | 54365.9515 | 37105.879 | 165945.7366 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12208098.4396 | 38139871.0772 | 177.8279 | 0.0015399 | 7927776.8096 | 24767525.1754 | 161618.4534 | 504919.5013
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.76734 | -0.0059522 | 0.00082791 | 4 | 3715882.1669 | 11546359.1041 | 75753.2841 | 235388.1479 | 35.2484 | 3.2086 | 39.806 | 36962.642 | 0 | 21046.9011 | 0 | 0 | 0 | 27077.4478 | 33183.9265 | 86337.7697 | 58927.3019 | 263535.9891 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12305688.692 | 38237461.3296 | 237.1374 | 0.0033116 | 3715882.1669 | 11546359.1041 | 75753.2841 | 235388.1479
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0874 | 0.010749 | 0.0015597 | 4 | 1990898.009 | 6147380.9965 | 40587.1488 | 125322.6766 | 37.7249 | 3.5021 | 85.7382 | 52347.8327 | 0 | 34513.3517 | 0 | 0 | 0 | 35443.5053 | 47698.829 | 124102.5686 | 84702.5531 | 378808.6405 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12420961.3434 | 38352733.981 | 316.2278 | 0.0062389 | 1990898.009 | 6147380.9965 | 40587.1488 | 125322.6766
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.035963 | 0.0026625 | 4 | 1179098.2387 | 3613998.672 | 24037.5124 | 73676.2512 | 39.5857 | 3.724 | 121.5333 | 70633.4934 | 0 | 50959.3096 | 0 | 0 | 0 | 44775.1506 | 64883.5019 | 168813.5625 | 115218.7252 | 515283.7431 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12557436.4461 | 38489209.0837 | 421.6965 | 0.01065 | 1179098.2387 | 3613998.672 | 24037.5124 | 73676.2512
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.071412 | 0.0042421 | 4 | 749577.1078 | 2277815.5147 | 15281.1432 | 46436.3502 | 41.0105 | 3.893 | 157.8928 | 92298.064 | 0 | 70989.966 | 0 | 0 | 0 | 55285.4202 | 85243.6456 | 221786.4799 | 151373.8298 | 676977.4054 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12719130.1084 | 38650902.746 | 562.3413 | 0.016968 | 749577.1078 | 2277815.5147 | 15281.1432 | 46436.3502
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7157 | 0.1206 | 0.0064416 | 4 | 501310.4481 | 1507725.2596 | 10219.8916 | 30737.0188 | 42.1328 | 4.0247 | 41.6826 | 118573.7367 | 0 | 95981.627 | 0 | 0 | 0 | 67906.3907 | 110160.0842 | 286613.9422 | 195619.9049 | 874855.6858 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12917008.3887 | 38848781.0263 | 749.8942 | 0.025766 | 501310.4481 | 1507725.2596 | 10219.8916 | 30737.0188
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6024 | 0.18538 | 0.009444 | 4 | 348057.088 | 1034517.596 | 7095.6145 | 21090.0405 | 42.9856 | 4.1235 | 45.0939 | 149270.5529 | 0 | 126019.4293 | 0 | 0 | 0 | 81823.941 | 139274.43 | 362363.4978 | 247320.5331 | 1106072.3841 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13148225.087 | 39079997.7246 | 1000 | 0.037776 | 348057.088 | 1034517.596 | 7095.6145 | 21090.0405
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.27068 | 0.013497 | 4 | 248645.9338 | 728975.2822 | 5068.9837 | 14861.1471 | 43.6457 | 4.1989 | 31.5487 | 185684.1616 | 0 | 162661.7081 | 0 | 0 | 0 | 97731.7379 | 173970.267 | 452634.9485 | 308932.6531 | 1381615.4763 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13423768.1792 | 39355540.8168 | 1333.5214 | 0.053987 | 248645.9338 | 728975.2822 | 5068.9837 | 14861.1471
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.265 | 0.38429 | 0.018935 | 4 | 181683.8727 | 524054.8143 | 3703.8715 | 10683.5662 | 44.1638 | 4.2571 | 52.5136 | 229775.0823 | 0 | 208284.2477 | 0 | 0 | 0 | 116916.5013 | 216440.5742 | 563133.976 | 384350.5098 | 1718900.8913 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13761053.5942 | 39692826.2318 | 1778.2794 | 0.075742 | 181683.8727 | 524054.8143 | 3703.8715 | 10683.5662
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2038 | 0.53077 | 0.026169 | 4 | 135255.7836 | 382985.8289 | 2757.3721 | 7807.6841 | 44.5559 | 4.3002 | 58.7294 | 281580.6807 | 0 | 263389.656 | 0 | 0 | 0 | 138244.784 | 266453.8971 | 693258.383 | 473163.0914 | 2116090.4922 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 14158243.1952 | 40090015.8328 | 2371.3737 | 0.10468 | 135255.7836 | 382985.8289 | 2757.3721 | 7807.6841
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.713 | 0.72107 | 0.035749 | 4 | 102337.5523 | 283681.1939 | 2086.2894 | 5783.2248 | 44.8542 | 4.3318 | 44.0942 | 343249.4627 | 0 | 330800.6538 | 0 | 0 | 0 | 162791.125 | 326368.0842 | 849142.8079 | 579557.4145 | 2591909.5482 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 14634062.2511 | 40565834.8888 | 3162.2777 | 0.143 | 102337.5523 | 283681.1939 | 2086.2894 | 5783.2248
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9191 | 0.96504 | 0.04834 | 4 | 78590.7061 | 212703.4506 | 1602.1778 | 4336.2475 | 45.0746 | 4.3535 | 46.6864 | 415826.0153 | 0 | 412330.9862 | 0 | 0 | 0 | 190161.096 | 397144.058 | 1033287.3736 | 705239.8644 | 3153989.3935 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 15196142.0965 | 41127914.7341 | 4216.965 | 0.19336 | 78590.7061 | 212703.4506 | 1602.1778 | 4336.2475
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.948 | 1.2726 | 0.064706 | 4 | 61231.78 | 161422.6376 | 1248.2927 | 3290.8188 | 45.2287 | 4.3662 | 53.6842 | 499963.1984 | 0 | 509487.9593 | 0 | 0 | 0 | 219407.1199 | 479254.7282 | 1246922.4942 | 851050.224 | 3806085.7241 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 15848238.427 | 41780011.0646 | 5623.4133 | 0.25882 | 61231.78 | 161422.6376 | 1248.2927 | 3290.8188
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9593 | 1.6561 | 0.085702 | 4 | 48418.0689 | 124063.4054 | 987.0678 | 2529.2003 | 45.3252 | 4.3698 | 36.9666 | 596633.8527 | 0 | 624330.1969 | 0 | 0 | 0 | 249988.8624 | 573671.6357 | 1492575.9198 | 1018713.7347 | 4555914.2022 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 16598066.9051 | 42529839.5428 | 7498.9421 | 0.34281 | 48418.0689 | 124063.4054 | 987.0678 | 2529.2003
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.9808 | 2.1187 | 0.11201 | 4 | 38897.5296 | 96777.4241 | 792.9788 | 1972.9387 | 45.3664 | 4.3638 | 52.7017 | 704070.7538 | 0 | 755833.2158 | 0 | 0 | 0 | 278733.8641 | 678068.7551 | 1764195.8098 | 1204099.8908 | 5385002.2895 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 17427154.9924 | 43358927.6301 | 10000 | 0.44803 | 38897.5296 | 96777.4241 | 792.9788 | 1972.9387
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9749 | 2.6581 | 0.14396 | 4 | 31799.8331 | 76834.0614 | 648.2826 | 1566.3663 | 45.3535 | 4.3472 | 51.6863 | 819653.179 | 0 | 901925.1568 | 0 | 0 | 0 | 302454.351 | 789372.7478 | 2053785.9673 | 1401751.1238 | 6268942.5257 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 18311095.2286 | 44242867.8662 | 13335.2143 | 0.57582 | 31799.8331 | 76834.0614 | 648.2826 | 1566.3663
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.7091 | 3.2576 | 0.18112 | 4 | 26506.3086 | 62300.3364 | 540.367 | 1270.0766 | 45.2875 | 4.3194 | 60.2387 | 938202.1273 | 0 | 1057126.3781 | 0 | 0 | 0 | 316696.2385 | 901689.6501 | 2346011.5076 | 1601201.0596 | 7160926.9611 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 19203079.6641 | 45134852.3017 | 17782.7941 | 0.72447 | 26506.3086 | 62300.3364 | 540.367 | 1270.0766
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.205 | 3.8442 | 0.22117 | 4 | 22563.9531 | 51876.2944 | 459.9967 | 1057.5684 | 45.1806 | 4.2835 | 62.1521 | 1045149.8066 | 0 | 1202557.3817 | 0 | 0 | 0 | 309241.3011 | 997209.9109 | 2594535.6322 | 1770823.8814 | 7919517.9138 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 19961670.6168 | 45893443.2544 | 23713.7371 | 0.88467 | 22563.9531 | 51876.2944 | 459.9967 | 1057.5684
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.6166 | 4.5013 | 0.26444 | 4 | 19638.5571 | 44153.9704 | 400.3585 | 900.1384 | 45.0204 | 4.235 | 54.8396 | 1157023.233 | 0 | 1360907.8611 | 0 | 0 | 0 | 301020.2169 | 1099391.0113 | 2860389.8952 | 1952274.8786 | 8731007.096 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 20773159.7989 | 46704932.4365 | 31622.7766 | 1.0578 | 19638.5571 | 44153.9704 | 400.3585 | 900.1384
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.7318 | 5.0627 | 0.3055 | 4 | 17471.0771 | 38691.7968 | 356.1715 | 788.7846 | 44.851 | 4.1864 | 53.5236 | 1245329.2092 | 0 | 1491489.9029 | 0 | 0 | 0 | 268277.8146 | 1171987.8014 | 3049271.8516 | 2081190.695 | 9307547.2747 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 21349699.9776 | 47281472.6152 | 42169.6503 | 1.222 | 17471.0771 | 38691.7968 | 356.1715 | 788.7846
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.842 | 5.5478 | 0.34309 | 4 | 15861.2143 | 34757.0879 | 323.3523 | 708.5702 | 44.681 | 4.1393 | 50.1417 | 1316710.5452 | 0 | 1601472.1577 | 0 | 0 | 0 | 221696.4051 | 1224552.8521 | 3186035.3309 | 2174534.5798 | 9725001.8707 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 21767154.5737 | 47698927.2113 | 56234.1325 | 1.3724 | 15861.2143 | 34757.0879 | 323.3523 | 708.5702
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.6797 | 5.935 | 0.37549 | 4 | 14658.2649 | 31923.5851 | 298.8286 | 650.8055 | 44.5304 | 4.0985 | 63.6502 | 1370363.2893 | 0 | 1687271.1961 | 0 | 0 | 0 | 162616.5831 | 1255897.9167 | 3267588.7591 | 2230196.4703 | 9973934.2144 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 22016086.9174 | 47947859.555 | 74989.4209 | 1.502 | 14658.2649 | 31923.5851 | 298.8286 | 650.8055
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.4519 | 6.1636 | 0.40025 | 4 | 13744.8343 | 29942.012 | 280.207 | 610.4084 | 44.4375 | 4.0737 | 48.4593 | 1399968.9222 | 0 | 1735953.3501 | 0 | 0 | 0 | 80929.0845 | 1254572.0291 | 3264139.0717 | 2227841.9878 | 9963404.4454 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 22005557.1484 | 47937329.786 | 100000 | 1.601 | 13744.8343 | 29942.012 | 280.207 | 610.4084
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.9654 | 6.5202 | 0.42584 | 4 | 12999.0455 | 28222.946 | 265.0031 | 575.3629 | 44.2749 | 4.0306 | 59.4117 | 1446332.1146 | 0 | 1814586.6553 | 0 | 0 | 0 | 0 | 1271758.3203 | 3308854.2758 | 2258361.0334 | 10099892.3994 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 22142045.1023 | 48073817.74 | 133352.1432 | 1.7034 | 12999.0455 | 28222.946 | 265.0031 | 575.3629
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.9392 | 7.133 | 0.45507 | 4 | 12527.7521 | 26773.851 | 255.3952 | 545.8212 | 43.9616 | 3.949 | 46.2644 | 1523129.6496 | 0 | 1951484.6781 | 0 | 0 | 0 | 0 | 1355099.5878 | 3525691.1583 | 2406356.6612 | 10761761.7349 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 22803914.4379 | 48735687.0755 | 177827.941 | 1.8203 | 12527.7521 | 26773.851 | 255.3952 | 545.8212
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5533 | 7.6394 | 0.47695 | 4 | 12229.624 | 25822.1757 | 249.3174 | 526.42 | 43.6726 | 3.8751 | 48.3865 | 1581664.8919 | 0 | 2063317.9099 | 0 | 0 | 0 | 0 | 1421543.2927 | 3698564.0489 | 2524345.9613 | 11289436.1047 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 23331588.8076 | 49263361.4453 | 237137.3706 | 1.9078 | 12229.624 | 25822.1757 | 249.3174 | 526.42
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.876 | 8.0455 | 0.49289 | 4 | 12042.4618 | 25195.3928 | 245.5019 | 513.6422 | 43.4211 | 3.8116 | 39.9398 | 1625353.6211 | 0 | 2152272.156 | 0 | 0 | 0 | 0 | 1473274.0531 | 3833156.8761 | 2616208.3314 | 11700265.0377 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 23742417.7406 | 49674190.3783 | 316227.766 | 1.9716 | 12042.4618 | 25195.3928 | 245.5019 | 513.6422
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9445 | 8.3547 | 0.50417 | 4 | 11924.8581 | 24783.5457 | 243.1044 | 505.2461 | 43.2212 | 3.7618 | 38.6404 | 1656903.6815 | 0 | 2219559.9964 | 0 | 0 | 0 | 0 | 1511820.8344 | 3933447.694 | 2684658.8754 | 12006391.0817 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24048543.7846 | 49980316.4223 | 421696.5034 | 2.0167 | 11924.8581 | 24783.5457 | 243.1044 | 505.2461
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.2166 | 8.6031 | 0.51242 | 4 | 11850.3308 | 24501.9992 | 241.585 | 499.5064 | 43.05 | 3.7193 | 45.2399 | 1680765.5176 | 0 | 2273428.1083 | 0 | 0 | 0 | 0 | 1542135.5141 | 4012320.2722 | 2738491.0307 | 12247140.443 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24289293.146 | 50221065.7836 | 562341.3252 | 2.0497 | 11850.3308 | 24501.9992 | 241.585 | 499.5064
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.7569 | 8.7956 | 0.51836 | 4 | 11803.1774 | 24309.9242 | 240.6237 | 495.5907 | 42.912 | 3.6853 | 50.9361 | 1698433.3422 | 0 | 2315065.3276 | 0 | 0 | 0 | 0 | 1565264.4812 | 4072497.1002 | 2779562.9523 | 12430823.2035 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24472975.9064 | 50404748.544 | 749894.2093 | 2.0734 | 11803.1774 | 24309.9242 | 240.6237 | 495.5907
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.6717 | 8.9405 | 0.5226 | 4 | 11772.6291 | 24177.7177 | 240.001 | 492.8955 | 42.8062 | 3.6593 | 52.4899 | 1711324.0564 | 0 | 2346308.6937 | 0 | 0 | 0 | 0 | 1582476.7725 | 4117279.9515 | 2810128.1685 | 12567517.6427 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24609670.3456 | 50541442.9832 | 1000000 | 2.0904 | 11772.6291 | 24177.7177 | 240.001 | 492.8955
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.2018 | 9.0563 | 0.52574 | 4 | 11753.7376 | 24084.8625 | 239.6158 | 491.0025 | 42.7178 | 3.6377 | 41.546 | 1721185.6053 | 0 | 2371279.3983 | 0 | 0 | 0 | 0 | 1596061.3514 | 4152624.2392 | 2834251.3711 | 12675401.9653 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24717554.6683 | 50649327.3059 | 1333521.4322 | 2.103 | 11753.7376 | 24084.8625 | 239.6158 | 491.0025
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1808 | 9.1301 | 0.5278 | 4 | 11740.4756 | 24023.4995 | 239.3455 | 489.7515 | 42.6636 | 3.6245 | 44.8985 | 1727552.1456 | 0 | 2387124.9313 | 0 | 0 | 0 | 0 | 1604724.06 | 4175162.8299 | 2849634.4224 | 12744198.3892 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24786351.0922 | 50718123.7298 | 1778279.41 | 2.1112 | 11740.4756 | 24023.4995 | 239.3455 | 489.7515
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.1166 | 9.2007 | 0.5296 | 4 | 11731.2385 | 23972.4335 | 239.1572 | 488.7105 | 42.6087 | 3.6111 | 44.4039 | 1733375.5502 | 0 | 2402329.425 | 0 | 0 | 0 | 0 | 1612924.9403 | 4196499.8384 | 2864197.3691 | 12809327.1231 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24851479.826 | 50783252.4636 | 2371373.7057 | 2.1184 | 11731.2385 | 23972.4335 | 239.1572 | 488.7105
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7428 | 9.2479 | 0.53081 | 4 | 11725.0412 | 23938.4187 | 239.0308 | 488.017 | 42.5723 | 3.6023 | 44.1788 | 1737262.8706 | 0 | 2412468.7112 | 0 | 0 | 0 | 0 | 1618395.3169 | 4210732.6361 | 2873911.546 | 12852771.0808 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24894923.7837 | 50826696.4213 | 3162277.6602 | 2.1232 | 11725.0412 | 23938.4187 | 239.0308 | 488.017
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.1495 | 9.2786 | 0.53158 | 4 | 11721.2788 | 23916.9593 | 238.9541 | 487.5796 | 42.5486 | 3.5966 | 48.2685 | 1739764.1641 | 0 | 2419048.0128 | 0 | 0 | 0 | 0 | 1621936.749 | 4219946.7159 | 2880200.3449 | 12880895.9867 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24923048.6897 | 50854821.3273 | 4216965.0343 | 2.1263 | 11721.2788 | 23916.9593 | 238.9541 | 487.5796
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.5903 | 9.3119 | 0.53237 | 4 | 11718.0589 | 23895.5643 | 238.8885 | 487.1434 | 42.5221 | 3.5901 | 41.2145 | 1742410.4269 | 0 | 2426197.9032 | 0 | 0 | 0 | 0 | 1625757.2487 | 4229886.8726 | 2886984.706 | 12911237.1574 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24953389.8603 | 50885162.498 | 5623413.2519 | 2.1295 | 11718.0589 | 23895.5643 | 238.8885 | 487.1434
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.8682 | 9.3328 | 0.53287 | 4 | 11716.0922 | 23882.2489 | 238.8484 | 486.8719 | 42.5054 | 3.5861 | 38.5728 | 1744071.3112 | 0 | 2430698.8441 | 0 | 0 | 0 | 0 | 1628160.3606 | 4236139.2766 | 2891252.1002 | 12930321.8928 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24972474.5957 | 50904247.2333 | 7498942.0933 | 2.1315 | 11716.0922 | 23882.2489 | 238.8484 | 486.8719
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9776 | 9.341 | 0.5331 | 4 | 11714.5609 | 23875.4306 | 238.8172 | 486.7329 | 42.4997 | 3.5847 | 48.5937 | 1744778.7393 | 0 | 2432442.4093 | 0 | 0 | 0 | 0 | 1629116.248 | 4238626.2995 | 2892949.5445 | 12937913.2405 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24980065.9434 | 50911838.581 | 10000000 | 2.1324 | 11714.5609 | 23875.4306 | 238.8172 | 486.7329
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0265 | [19 empty] | 100 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.018432 | 0.00014956 | 4 | 21037944.2936 | 65822247.5107 | 428886.9504 | 1341875.5467 | 27.8066 | 2.5618 | 30.1639 | 15603.814 | 0 | 1874.9163 | 0 | 0 | 0 | 14815.3211 | 12594.68 | 32768.7739 | 22365.3615 | 100022.8669 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 12585675.6179 | 39377300.5598 | 133.3521 | 0.00059824 | 21037944.2936 | 65822247.5107 | 428886.9504 | 1341875.5467
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.53564 | -0.016318 | 0.00039398 | 4 | 8039659.1114 | 25040157.75 | 163899.3254 | 510477.4851 | 32.5351 | 3.0965 | 32.1342 | 26527.3187 | 0 | 10693.4185 | 0 | 0 | 0 | 22283.9171 | 23206.8152 | 60379.3727 | 41210.1625 | 184301.0047 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 12669953.7557 | 39461578.6975 | 177.8279 | 0.0015759 | 8039659.1114 | 25040157.75 | 163899.3254 | 510477.4851
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81087 | -0.0062652 | 0.00088381 | 4 | 3614874.5111 | 11193304.4396 | 73694.1064 | 228190.6511 | 36.2114 | 3.5184 | 43.7112 | 40942.5567 | 0 | 22609.1572 | 0 | 0 | 0 | 31313.9699 | 36997.6167 | 96260.2093 | 65699.5708 | 293823.0806 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 12779475.8315 | 39571100.7734 | 237.1374 | 0.0035352 | 3614874.5111 | 11193304.4396 | 73694.1064 | 228190.6511
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1458 | 0.011635 | 0.001699 | 4 | 1898851.1172 | 5841116.9951 | 38710.6484 | 119079.0706 | 38.8115 | 3.8215 | 89.7184 | 57674.9861 | 0 | 36840.5103 | 0 | 0 | 0 | 40743.9202 | 52751.1725 | 137247.73 | 93674.3959 | 418932.7149 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 12904585.4659 | 39696210.4078 | 316.2278 | 0.006796 | 1898851.1172 | 5841116.9951 | 38710.6484 | 119079.0706
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5931 | 0.039767 | 0.0029333 | 4 | 1113163.8897 | 3396561.9375 | 22693.3516 | 69243.5093 | 40.853 | 4.0595 | 128.6612 | 78472.5799 | 0 | 55021.9522 | 0 | 0 | 0 | 52266.9911 | 72446.9941 | 188492.2176 | 128649.8117 | 575350.5466 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13061003.2975 | 39852628.2394 | 421.6965 | 0.011733 | 1113163.8897 | 3396561.9375 | 22693.3516 | 69243.5093
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.07764 | 0.0047012 | 4 | 703770.3503 | 2128497.4458 | 14347.3105 | 43392.2994 | 42.3336 | 4.2306 | 177.5158 | 101802.6729 | 0 | 75986.2861 | 0 | 0 | 0 | 63898.3416 | 94258.0472 | 245240.1039 | 167381.4101 | 748566.8619 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13234219.6128 | 40025844.5547 | 562.3413 | 0.018805 | 703770.3503 | 2128497.4458 | 14347.3105 | 43392.2994
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8667 | 0.13067 | 0.0071654 | 4 | 469252.5105 | 1404005.799 | 9566.3471 | 28622.5573 | 43.5255 | 4.3664 | 34.3292 | 130477.2504 | 0 | 102475.8639 | 0 | 0 | 0 | 78266.2343 | 121375.5459 | 315794.2729 | 215536.0802 | 963925.2476 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13449577.9985 | 40241202.9404 | 749.8942 | 0.028662 | 469252.5105 | 1404005.799 | 9566.3471 | 28622.5573
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 0.20121 | 0.010532 | 4 | 325298.7588 | 961230.3034 | 6631.6552 | 19595.9799 | 44.4433 | 4.4694 | 42.8712 | 164350.4493 | 0 | 134660.1951 | 0 | 0 | 0 | 94594.991 | 153506.1978 | 399391.6383 | 272592.9998 | 1219096.4713 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13704749.2223 | 40496374.1642 | 1000 | 0.04213 | 325298.7588 | 961230.3034 | 6631.6552 | 19595.9799
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.025 | 0.29421 | 0.015079 | 4 | 232259.5945 | 676442.4367 | 4734.926 | 13790.194 | 45.1538 | 4.5479 | 39.238 | 204564.029 | 0 | 173947.7465 | 0 | 0 | 0 | 113365.92 | 191832.3013 | 499108.2977 | 340651.6688 | 1523469.9634 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 14009122.7143 | 40800747.6562 | 1333.5214 | 0.060317 | 232259.5945 | 676442.4367 | 4734.926 | 13790.194
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6056 | 0.41616 | 0.02117 | 4 | 169739.9137 | 486125.1769 | 3460.3777 | 9910.3193 | 45.7035 | 4.6075 | 45.8408 | 252446.9065 | 0 | 222035.2095 | 0 | 0 | 0 | 135086.3025 | 237731.6833 | 618529.0744 | 422158.8028 | 1887987.979 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 14373640.73 | 41165265.6719 | 1778.2794 | 0.08468 | 169739.9137 | 486125.1769 | 3460.3777 | 9910.3193
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6667 | 0.57613 | 0.029286 | 4 | 126458.2063 | 355168.1489 | 2578.0216 | 7240.5831 | 46.1281 | 4.6524 | 41.2078 | 309800.5733 | 0 | 281233.4091 | 0 | 0 | 0 | 160587.1841 | 293132.2549 | 762669.9976 | 520537.9446 | 2327961.3636 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 14813614.1145 | 41605239.0564 | 2371.3737 | 0.11714 | 126458.2063 | 355168.1489 | 2578.0216 | 7240.5831
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3003 | 0.78157 | 0.040011 | 4 | 95799.3657 | 263200.0869 | 1952.9996 | 5365.6898 | 46.447 | 4.6848 | 39.874 | 377217.8363 | 0 | 352736.0341 | 0 | 0 | 0 | 189100.1271 | 358431.059 | 932564.0911 | 636494.1545 | 2846543.3019 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 15332196.0529 | 42123820.9948 | 3162.2777 | 0.16004 | 95799.3657 | 263200.0869 | 1952.9996 | 5365.6898
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.6714 | 1.0454 | 0.054098 | 4 | 73693.7941 | 197505.5321 | 1502.3477 | 4026.4174 | 46.6832 | 4.7069 | 43.2999 | 456733.3219 | 0 | 439390.0899 | 0 | 0 | 0 | 221301.7504 | 435795.8133 | 1133851.3122 | 773876.8189 | 3460949.1066 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 15946601.8576 | 42738226.7995 | 4216.965 | 0.21639 | 73693.7941 | 197505.5321 | 1502.3477 | 4026.4174
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.8908 | 1.3767 | 0.072371 | 4 | 57538.4541 | 150088.2542 | 1172.9992 | 3059.7521 | 46.8477 | 4.7193 | 41.3535 | 548582.9313 | 0 | 542272.1109 | 0 | 0 | 0 | 255747.9385 | 525175.1625 | 1366398.0446 | 932594.7421 | 4170770.9299 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 16656423.6809 | 43448048.6228 | 5623.4133 | 0.28948 | 57538.4541 | 150088.2542 | 1172.9992 | 3059.7521
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.1159 | 1.7881 | 0.095743 | 4 | 45614.4072 | 115571.5071 | 929.9114 | 2356.0815 | 46.9498 | 4.722 | 63.8798 | 653699.3765 | 0 | 663395.4733 | 0 | 0 | 0 | 291878.1657 | 627499.476 | 1632624.9188 | 1114300.0542 | 4983397.4645 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 17469050.2154 | 44260675.1573 | 7498.9421 | 0.38297 | 45614.4072 | 115571.5071 | 929.9114 | 2356.0815
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.377 | 2.283 | 0.12492 | 4 | 36755.8223 | 90373.3955 | 749.3172 | 1842.3839 | 46.9925 | 4.7142 | 54.8949 | 770255.811 | 0 | 801777.1275 | 0 | 0 | 0 | 326582.5926 | 740460.0571 | 1926525.1794 | 1314893.0211 | 5880493.7888 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 18366146.5397 | 45157771.4816 | 10000 | 0.49968 | 36755.8223 | 90373.3955 | 749.3172 | 1842.3839
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5996 | 2.8564 | 0.16015 | 4 | 30153.2743 | 71974.8817 | 614.7153 | 1467.3053 | 46.9771 | 4.695 | 53.4797 | 894855.9685 | 0 | 954551.6126 | 0 | 0 | 0 | 356108.2282 | 860151.1656 | 2237936.8917 | 1527437.9136 | 6831041.7803 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 19316694.5313 | 46108319.4731 | 13335.2143 | 0.64062 | 30153.2743 | 71974.8817 | 614.7153 | 1467.3053
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.5339 | 3.4895 | 0.20085 | 4 | 25231.5943 | 58578.8137 | 514.3802 | 1194.2084 | 46.9052 | 4.6638 | 45.7878 | 1021888.6189 | 0 | 1115894.5021 | 0 | 0 | 0 | 375980.9642 | 980367.9933 | 2550716.4174 | 1740916.3668 | 7785764.8627 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 20271417.6137 | 47063042.5556 | 17782.7941 | 0.80341 | 25231.5943 | 58578.8137 | 514.3802 | 1194.2084
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.724 | 4.1468 | 0.24529 | 4 | 21571.1745 | 48876.7174 | 439.7576 | 996.418 | 46.7827 | 4.6218 | 59.7342 | 1143811.356 | 0 | 1276821.0527 | 0 | 0 | 0 | 381698.7984 | 1092909.1708 | 2843525.4758 | 1940764.5659 | 8679530.4195 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 21165183.1705 | 47956808.1124 | 23713.7371 | 0.98118 | 21571.1745 | 48876.7174 | 439.7576 | 996.418
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.6286 | 4.7852 | 0.29086 | 4 | 18856.9044 | 41884.9092 | 384.4235 | 853.8805 | 46.6228 | 4.5722 | 62.4537 | 1253531.0256 | 0 | 1427702.937 | 0 | 0 | 0 | 370876.7871 | 1190323.1924 | 3096976.7777 | 2113750.2873 | 9453161.0071 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 21938813.758 | 48730438.6999 | 31622.7766 | 1.1634 | 18856.9044 | 41884.9092 | 384.4235 | 853.8805
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8512 | 5.3719 | 0.33489 | 4 | 16845.5518 | 36845.6777 | 343.4194 | 751.149 | 46.4409 | 4.5189 | 54.7123 | 1347326.8152 | 0 | 1562354.9144 | 0 | 0 | 0 | 344875.9604 | 1269277.4991 | 3302399.688 | 2253955.6446 | 10080190.5216 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 22565843.2725 | 49357468.2144 | 42169.6503 | 1.3396 | 16845.5518 | 36845.6777 | 343.4194 | 751.149
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0339 | 5.877 | 0.37492 | 4 | 15358.2697 | 33223.3876 | 313.0991 | 677.3037 | 46.2613 | 4.4681 | 52.3224 | 1423019.0302 | 0 | 1675405.698 | 0 | 0 | 0 | 306704.6561 | 1328000.4599 | 3455184.7863 | 2358234.6136 | 10546549.244 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23032201.995 | 49823826.9368 | 56234.1325 | 1.4997 | 15358.2697 | 33223.3876 | 313.0991 | 677.3037
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1009 | 6.2932 | 0.40964 | 4 | 14253.1361 | 30603.9087 | 290.5695 | 623.9021 | 46.0964 | 4.4225 | 51.3941 | 1481894.7512 | 0 | 1766702.3226 | 0 | 0 | 0 | 260602.5976 | 1368587.8718 | 3560784.9065 | 2430308.8655 | 10868881.3152 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23354534.0662 | 50146159.0081 | 74989.4209 | 1.6386 | 14253.1361 | 30603.9087 | 290.5695 | 623.9021
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0787 | 6.6219 | 0.43856 | 4 | 13427.7052 | 28700.3385 | 273.7419 | 585.0952 | 45.9559 | 4.3843 | 52.3004 | 1526135.4434 | 0 | 1837580.8092 | 0 | 0 | 0 | 210274.0925 | 1393856.2346 | 3626528.0031 | 2475179.8798 | 11069554.4626 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23555207.2135 | 50346832.1554 | 100000 | 1.7542 | 13427.7052 | 28700.3385 | 273.7419 | 585.0952
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.9681 | 6.8629 | 0.46157 | 4 | 12806.5645 | 27317.5976 | 261.0791 | 556.9062 | 45.8476 | 4.3551 | 58.5541 | 1557179.1974 | 0 | 1888649.3957 | 0 | 0 | 0 | 157048.211 | 1405121.9536 | 3655839.0931 | 2495185.301 | 11159023.1517 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23644675.9027 | 50436300.8446 | 133352.1432 | 1.8463 | 12806.5645 | 27317.5976 | 261.0791 | 556.9062
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.5345 | 6.9981 | 0.47828 | 4 | 12333.1127 | 26337.2778 | 251.4272 | 536.921 | 45.7866 | 4.3388 | 58.4262 | 1573618.2275 | 0 | 1916187.4804 | 0 | 0 | 0 | 96936.842 | 1398829.5944 | 3639467.6653 | 2484011.4652 | 11109051.2747 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23594704.0257 | 50386328.9676 | 177827.941 | 1.9131 | 12333.1127 | 26337.2778 | 251.4272 | 536.921
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4297 | 7.0009 | 0.48791 | 4 | 11931.1548 | 25659.0184 | 243.2327 | 523.0938 | 45.7886 | 4.3393 | 45.7427 | 1572409.8598 | 0 | 1914380.0958 | 0 | 0 | 0 | 0 | 1359848.0827 | 3538045.7679 | 2414788.9362 | 10799472.7423 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23285125.4932 | 50076750.4351 | 237137.3706 | 1.9516 | 11931.1548 | 25659.0184 | 243.2327 | 523.0938
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.5109 | 7.4036 | 0.50869 | 4 | 11657.2852 | 24824.2281 | 237.6495 | 506.0755 | 45.5817 | 4.2844 | 53.0406 | 1624002.6084 | 0 | 2003138.0622 | 0 | 0 | 0 | 0 | 1414584.8616 | 3680459.6385 | 2511989.3292 | 11234174.4999 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23719827.2508 | 50511452.1927 | 316227.766 | 2.0348 | 11657.2852 | 24824.2281 | 237.6495 | 506.0755
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.5601 | 7.7238 | 0.5243 | 4 | 11471.4007 | 24246.3207 | 233.86 | 494.294 | 45.4052 | 4.2381 | 56.0396 | 1663069.7147 | 0 | 2073216.2053 | 0 | 0 | 0 | 0 | 1457151.5088 | 3791209.323 | 2587578.2645 | 11572225.0162 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24057877.7672 | 50849502.7091 | 421696.5034 | 2.0972 | 11471.4007 | 24246.3207 | 233.86 | 494.294
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7123 | 7.9726 | 0.53586 | 4 | 11344.3714 | 23843.7169 | 231.2704 | 486.0864 | 45.2611 | 4.2007 | 54.9223 | 1692250.999 | 0 | 2127375.5658 | 0 | 0 | 0 | 0 | 1489654.3603 | 3875775.0753 | 2645296.1281 | 11830352.1285 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24316004.8795 | 51107629.8214 | 562341.3252 | 2.1434 | 11344.3714 | 23843.7169 | 231.2704 | 486.0864
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.1439 | 8.1642 | 0.54441 | 4 | 11256.3316 | 23559.4468 | 229.4755 | 480.2912 | 45.1459 | 4.1709 | 44.7005 | 1714016.8464 | 0 | 2168928.2601 | 0 | 0 | 0 | 0 | 1514348.5915 | 3940024.3996 | 2689147.6121 | 12026465.7098 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24512118.4608 | 51303743.4026 | 749894.2093 | 2.1776 | 11256.3316 | 23559.4468 | 229.4755 | 480.2912
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0244 | 8.3122 | 0.55077 | 4 | 11194.2977 | 23355.2701 | 228.2109 | 476.1288 | 45.0539 | 4.1472 | 50.652 | 1730374.2183 | 0 | 2200950.0336 | 0 | 0 | 0 | 0 | 1533216.4582 | 3989114.7184 | 2722652.7634 | 12176308.1919 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24661960.9429 | 51453585.8848 | 1000000 | 2.2031 | 11194.2977 | 23355.2701 | 228.2109 | 476.1288
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4502 | 8.4243 | 0.55547 | 4 | 11150.3354 | 23208.5002 | 227.3147 | 473.1367 | 44.9828 | 4.129 | 47.1669 | 1742524.5793 | 0 | 2225150.8261 | 0 | 0 | 0 | 0 | 1547393.4081 | 4026000.2339 | 2747827.8856 | 12288896.933 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24774549.684 | 51566174.6258 | 1333521.4322 | 2.2219 | 11150.3354 | 23208.5002 | 227.3147 | 473.1367
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5265 | 8.5088 | 0.55894 | 4 | 11118.8293 | 23102.0931 | 226.6724 | 470.9674 | 44.9285 | 4.1152 | 49.1185 | 1751555.0515 | 0 | 2243374.4414 | 0 | 0 | 0 | 0 | 1558022.5022 | 4053654.9565 | 2766702.8021 | 12373309.7537 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24858962.5046 | 51650587.4465 | 1778279.41 | 2.2358 | 11118.8293 | 23102.0931 | 226.6724 | 470.9674
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3353 | 8.5723 | 0.56151 | 4 | 11096.0414 | 23024.4606 | 226.2078 | 469.3848 | 44.8874 | 4.1047 | 55.847 | 1758264.7231 | 0 | 2257042.2941 | 0 | 0 | 0 | 0 | 1565969.7367 | 4074332.0303 | 2780815.3298 | 12436424.114 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24922076.865 | 51713701.8068 | 2371373.7057 | 2.246 | 11096.0414 | 23024.4606 | 226.2078 | 469.3848
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9491 | 8.6205 | 0.56343 | 4 | 11079.38 | 22967.136 | 225.8681 | 468.2161 | 44.8558 | 4.0966 | 43.3883 | 1763302.4172 | 0 | 2267404.7662 | 0 | 0 | 0 | 0 | 1571975.8015 | 4089958.5789 | 2791480.7704 | 12484122.3342 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 24969775.0851 | 51761400.027 | 3162277.6602 | 2.2537 | 11079.38 | 22967.136 | 225.8681 | 468.2161
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.4244 | 8.6578 | 0.56489 | 4 | 11067.0706 | 22924.1509 | 225.6172 | 467.3398 | 44.8308 | 4.0903 | 41.5143 | 1767153.171 | 0 | 2275431.0526 | 0 | 0 | 0 | 0 | 1576607.8472 | 4102010.2117 | 2799706.2573 | 12520908.5398 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 25006561.2908 | 51798186.2326 | 4216965.0343 | 2.2595 | 11067.0706 | 22924.1509 | 225.6172 | 467.3398
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.7728 | 8.6851 | 0.56596 | 4 | 11058.0457 | 22892.7142 | 225.4332 | 466.6989 | 44.8127 | 4.0857 | 45.2833 | 1769974.4561 | 0 | 2281303.0213 | 0 | 0 | 0 | 0 | 1579998.2162 | 4110831.2563 | 2805726.8016 | 12547833.7516 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 25033486.5025 | 51825111.4444 | 5623413.2519 | 2.2638 | 11058.0457 | 22892.7142 | 225.4332 | 466.6989
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.0286 | 8.7051 | 0.56674 | 4 | 11051.3916 | 22869.6149 | 225.2976 | 466.228 | 44.7995 | 4.0823 | 48.8381 | 1772047.1801 | 0 | 2285606.7082 | 0 | 0 | 0 | 0 | 1582485.0164 | 4117301.4005 | 2810142.8079 | 12567583.1131 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 25053235.8641 | 51844860.8059 | 7498942.0933 | 2.267 | 11051.3916 | 22869.6149 | 225.2976 | 466.228
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.2332 | 8.7212 | 0.56736 | 4 | 11046.3873 | 22851.8372 | 225.1955 | 465.8656 | 44.7885 | 4.0796 | 44.8332 | 1773679.5383 | 0 | 2289059.6922 | 0 | 0 | 0 | 0 | 1584468.2999 | 4122461.4972 | 2813664.68 | 12583333.7076 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 25068986.4586 | 51860611.4004 | 10000000 | 2.2694 | 11046.3873 | 22851.8372 | 225.1955 | 465.8656
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.6794 | [19 empty] | 100 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.019395 | 0.00014044 | 4 | 23212354.6986 | 72459451.1856 | 473215.2476 | 1477183.9211 | 27.8695 | 2.7751 | 29.8815 | 16403.7717 | 0 | 1397.104 | 0 | 0 | 0 | 16052.8379 | 13202.9483 | 34351.3632 | 23445.5112 | 104853.5364 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13039866.4262 | 40705114.8859 | 133.3521 | 0.00056176 | 23212354.6986 | 72459451.1856 | 473215.2476 | 1477183.9211
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.55046 | -0.017579 | 0.00040358 | 4 | 8135658.0066 | 25273068.6393 | 165856.3928 | 515225.6886 | 33.0665 | 3.3618 | 28.9222 | 28517.1177 | 0 | 10920.7533 | 0 | 0 | 0 | 24662.4074 | 24999.1086 | 65042.5525 | 44392.8786 | 198534.8181 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13133547.7079 | 40798796.1676 | 177.8279 | 0.0016143 | 8135658.0066 | 25273068.6393 | 165856.3928 | 515225.6886
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85995 | -0.0063433 | 0.00094551 | 4 | 3506676.8319 | 10821592.2553 | 71488.3503 | 220612.7954 | 37.2273 | 3.8352 | 37.8858 | 45329.2735 | 0 | 24447.2596 | 0 | 0 | 0 | 35914.8898 | 41219.6549 | 107245.0867 | 73196.9754 | 327353.1398 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13262366.0297 | 40927614.4893 | 237.1374 | 0.003782 | 3506676.8319 | 10821592.2553 | 71488.3503 | 220612.7954
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2236 | 0.013534 | 0.0018535 | 4 | 1807862.706 | 5539308.5569 | 36855.7266 | 112926.2974 | 40.0118 | 4.1548 | 99.258 | 64125.9417 | 0 | 40034.2055 | 0 | 0 | 0 | 47145.1521 | 59009.0667 | 153529.4871 | 104787.0297 | 468630.8827 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13403643.7726 | 41068892.2322 | 316.2278 | 0.0074141 | 1807862.706 | 5539308.5569 | 36855.7266 | 112926.2974
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.042692 | 0.0032287 | 4 | 1050225.9748 | 3192331.8725 | 21410.277 | 65080.0032 | 42.0522 | 4.3879 | 135.3943 | 85672.0809 | 0 | 58387.4236 | 0 | 0 | 0 | 58904.6467 | 79156.019 | 205947.7242 | 140563.5536 | 628631.448 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13563644.3379 | 41228892.7975 | 421.6965 | 0.012915 | 1050225.9748 | 3192331.8725 | 21410.277 | 65080.0032
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 0.085364 | 0.0052075 | 4 | 660800.8436 | 1988945.7816 | 13471.319 | 40547.35 | 43.6997 | 4.5737 | 194.6594 | 112437.5557 | 0 | 81817.0345 | 0 | 0 | 0 | 73551.5105 | 104444.3793 | 271742.8504 | 185470.0792 | 829463.4096 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13764476.2994 | 41429724.7591 | 562.3413 | 0.02083 | 660800.8436 | 1988945.7816 | 13471.319 | 40547.35
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0371 | 0.14248 | 0.0079622 | 4 | 439488.8641 | 1308137.4751 | 8959.5749 | 26668.1518 | 44.9458 | 4.7119 | 40.6367 | 143517.1452 | 0 | 109791.3463 | 0 | 0 | 0 | 89606.7094 | 133736.9283 | 347956.0543 | 237487.1568 | 1062095.3403 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13997108.2301 | 41662356.6898 | 749.8942 | 0.031849 | 439488.8641 | 1308137.4751 | 8959.5749 | 26668.1518
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0265 | 0.21874 | 0.011728 | 4 | 304296.5786 | 894041.3195 | 6203.4973 | 18226.2416 | 45.9163 | 4.8177 | 36.1512 | 180453.2785 | 0 | 143968.7568 | 0 | 0 | 0 | 108124.4325 | 168693.1224 | 438904.9008 | 299561.6134 | 1339706.1044 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 14274718.9942 | 41939967.4538 | 1000 | 0.046911 | 304296.5786 | 894041.3195 | 6203.4973 | 18226.2416
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3 | 0.31871 | 0.016809 | 4 | 217192.8073 | 628648.5833 | 4427.7692 | 12815.8517 | 46.6666 | 4.898 | 54.6444 | 224067.6086 | 0 | 185447.8128 | 0 | 0 | 0 | 129182.3427 | 210092.128 | 546616.6213 | 373077.0759 | 1668483.5894 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 14603496.4792 | 42268744.9389 | 1333.5214 | 0.067237 | 217192.8073 | 628648.5833 | 4427.7692 | 12815.8517
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9734 | 0.45129 | 0.023624 | 4 | 158778.7095 | 451549.8032 | 3236.9188 | 9205.4535 | 47.2559 | 4.9598 | 52.7958 | 276679.6043 | 0 | 236869.4503 | 0 | 0 | 0 | 154364.171 | 260486.158 | 677731.5501 | 462565.7089 | 2068696.6427 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 15003709.5325 | 42668957.9922 | 1778.2794 | 0.094494 | 158778.7095 | 451549.8032 | 3236.9188 | 9205.4535
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1271 | 0.62315 | 0.032686 | 4 | 118390.4072 | 329987.7098 | 2413.5486 | 6727.2458 | 47.706 | 5.0058 | 46.1836 | 338902.6938 | 0 | 299359.748 | 0 | 0 | 0 | 183083.9389 | 320325.0885 | 833420.1725 | 568826.3928 | 2543918.0344 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 15478930.9242 | 43144179.3839 | 2371.3737 | 0.13074 | 118390.4072 | 329987.7098 | 2413.5486 | 6727.2458
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9117 | 0.84627 | 0.044675 | 4 | 89801.9652 | 244614.2778 | 1830.7345 | 4986.7929 | 48.0484 | 5.0392 | 47.6205 | 412934.2927 | 0 | 375746.0341 | 0 | 0 | 0 | 216327.9381 | 391953.2233 | 1019781.8864 | 696022.0919 | 3112765.4666 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 16047778.3564 | 43713026.8161 | 3162.2777 | 0.1787 | 89801.9652 | 244614.2778 | 1830.7345 | 4986.7929
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4265 | 1.1291 | 0.060372 | 4 | 69196.8155 | 183758.5965 | 1410.6707 | 3746.1675 | 48.2985 | 5.0614 | 55.6071 | 499068.4881 | 0 | 467053.7765 | 0 | 0 | 0 | 252750.9216 | 475360.5426 | 1236790.622 | 844135.013 | 3775159.3639 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 16710172.2537 | 44375420.7133 | 4216.965 | 0.24149 | 69196.8155 | 183758.5965 | 1410.6707 | 3746.1675
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8434 | 1.4856 | 0.080717 | 4 | 54140.336 | 139826.4166 | 1103.724 | 2850.5506 | 48.4735 | 5.0734 | 56.156 | 599012.1572 | 0 | 575936.0489 | 0 | 0 | 0 | 292526.2976 | 572315.0564 | 1489046.3789 | 1016304.7504 | 4545140.6894 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 17480153.5792 | 45145402.0389 | 5623.4133 | 0.32287 | 54140.336 | 139826.4166 | 1103.724 | 2850.5506
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2903 | 1.9266 | 0.10666 | 4 | 43027.8874 | 107870.5742 | 877.1817 | 2199.0876 | 48.5813 | 5.075 | 57.1106 | 712956.0908 | 0 | 703636.9478 | 0 | 0 | 0 | 334284.6836 | 682842.3117 | 1776615.6247 | 1212576.6697 | 5422912.3282 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 18357925.2181 | 46023173.6777 | 7498.9421 | 0.42665 | 43027.8874 | 107870.5742 | 877.1817 | 2199.0876
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.7996 | 2.4557 | 0.13894 | 4 | 34772.9667 | 84552.8575 | 708.894 | 1723.7244 | 48.625 | 5.0653 | 51.0733 | 838999.2625 | 0 | 849199.6922 | 0 | 0 | 0 | 374956.3489 | 804630.5684 | 2093483.6867 | 1428845.6329 | 6390115.1918 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 19325128.0816 | 46990376.5412 | 10000 | 0.55575 | 34772.9667 | 84552.8575 | 708.894 | 1723.7244
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2392 | 3.0632 | 0.17766 | 4 | 28621.8544 | 67551.3115 | 583.4952 | 1377.1249 | 48.6066 | 5.0433 | 48.838 | 972557.1279 | 0 | 1008511.1651 | 0 | 0 | 0 | 409801.4303 | 932439.192 | 2426015.5081 | 1655805.4339 | 7405129.8573 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 20340142.7472 | 48005391.2068 | 13335.2143 | 0.71065 | 28621.8544 | 67551.3115 | 583.4952 | 1377.1249
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3561 | 3.7296 | 0.22208 | 4 | 24038.992 | 55182.6306 | 490.0674 | 1124.9726 | 48.5284 | 5.0085 | 55.3085 | 1107882.4845 | 0 | 1175735.6995 | 0 | 0 | 0 | 434627.8145 | 1060115.9394 | 2758204.2147 | 1882531.0519 | 8419097.2045 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 21354110.0944 | 49019358.554 | 17782.7941 | 0.88831 | 24038.992 | 55182.6306 | 490.0674 | 1124.9726
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6628 | 4.4157 | 0.27016 | 4 | 20633.1184 | 46233.7409 | 420.634 | 942.5373 | 48.3978 | 4.9625 | 66.4627 | 1236748.4977 | 0 | 1341224.96 | 0 | 0 | 0 | 444741.4927 | 1178858.8306 | 3067148.8601 | 2093392.1207 | 9362114.7618 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 22297127.6517 | 49962376.1113 | 23713.7371 | 1.0806 | 20633.1184 | 46233.7409 | 420.634 | 942.5373
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.6165 | 5.0768 | 0.31903 | 4 | 18109.7909 | 39788.9963 | 369.1926 | 811.1525 | 48.2292 | 4.9091 | 63.0884 | 1351908.7789 | 0 | 1495270.4321 | 0 | 0 | 0 | 438065.9965 | 1281245.6309 | 3333538.3121 | 2275208.3953 | 10175237.5458 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 23110250.4357 | 50775498.8953 | 31622.7766 | 1.2761 | 18109.7909 | 39788.9963 | 369.1926 | 811.1525
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.8197 | 5.6789 | 0.36581 | 4 | 16243.7933 | 35150.6719 | 331.1517 | 716.594 | 48.0414 | 4.8529 | 58.2157 | 1449676.8364 | 0 | 1631593.4995 | 0 | 0 | 0 | 416509.106 | 1364133.9823 | 3549196.7997 | 2422399.7445 | 10833509.9685 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 23768522.8583 | 51433771.318 | 42169.6503 | 1.4632 | 16243.7933 | 35150.6719 | 331.1517 | 716.594
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0265 | 6.2008 | 0.40826 | 4 | 14861.5469 | 31802.3194 | 302.9727 | 648.3333 | 47.8517 | 4.7981 | 64.3175 | 1529038.4471 | 0 | 1746948.0965 | 0 | 0 | 0 | 383623.8366 | 1427248.0482 | 3713406.6527 | 2534476.3433 | 11334741.4243 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24269754.3141 | 51935002.7738 | 56234.1325 | 1.6331 | 14861.5469 | 31802.3194 | 302.9727 | 648.3333
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.1233 | 6.6313 | 0.44492 | 4 | 13838.9943 | 29384.0379 | 282.1266 | 599.0334 | 47.6795 | 4.7495 | 54.2032 | 1591025.07 | 0 | 1840279.4353 | 0 | 0 | 0 | 344301.3879 | 1472486.2984 | 3831107.2999 | 2614809.4535 | 11694008.945 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24629021.8348 | 52294270.2945 | 74989.4209 | 1.7797 | 13838.9943 | 29384.0379 | 282.1266 | 599.0334
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.1982 | 6.9771 | 0.47552 | 4 | 13078.2502 | 27623.0658 | 266.6178 | 563.1336 | 47.5301 | 4.7081 | 54.0698 | 1638477.545 | 0 | 1914084.4992 | 0 | 0 | 0 | 302700.7407 | 1503552.4861 | 3911935.1478 | 2669976.1206 | 11940726.5395 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24875739.4293 | 52540987.889 | 100000 | 1.9021 | 13078.2502 | 27623.0658 | 266.6178 | 563.1336
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.3628 | 7.2468 | 0.5003 | 4 | 12510.0521 | 26334.3163 | 255.0343 | 536.8607 | 47.4068 | 4.6743 | 62.0102 | 1674040.9583 | 0 | 1970931.4446 | 0 | 0 | 0 | 261786.1432 | 1523635.8329 | 3964187.8966 | 2705639.6954 | 12100221.971 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25035234.8608 | 52700483.3205 | 133352.1432 | 2.0012 | 12510.0521 | 26334.3163 | 255.0343 | 536.8607
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.7406 | 7.4505 | 0.51986 | 4 | 12083.9785 | 25388.177 | 246.3482 | 517.5723 | 47.3099 | 4.648 | 58.5208 | 1700019.9652 | 0 | 2013384.9277 | 0 | 0 | 0 | 223264.855 | 1535301.2017 | 3994538.7932 | 2726354.8059 | 12192864.5486 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25127877.4385 | 52793125.8981 | 177827.941 | 2.0794 | 12083.9785 | 25388.177 | 246.3482 | 517.5723
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.4797 | 7.6004 | 0.53498 | 4 | 11763.2677 | 24691.4134 | 239.8101 | 503.3679 | 47.2368 | 4.6282 | 68.5988 | 1718615.4656 | 0 | 2044296.8843 | 0 | 0 | 0 | 188163.9782 | 1540919.768 | 4009157.1501 | 2736332.1349 | 12237485.3811 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25172498.2709 | 52837746.7306 | 237137.3706 | 2.1399 | 11763.2677 | 24691.4134 | 239.8101 | 503.3679
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6707 | 7.7042 | 0.54636 | 4 | 11520.9952 | 24179.9578 | 234.8711 | 492.9411 | 47.1855 | 4.6144 | 57.2691 | 1731150.9288 | 0 | 2065399.1273 | 0 | 0 | 0 | 156400.4009 | 1541650.6782 | 4011058.8287 | 2737630.0696 | 12243290.0336 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25178302.9234 | 52843551.3831 | 316227.766 | 2.1854 | 11520.9952 | 24179.9578 | 234.8711 | 492.9411
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.4166 | 7.7705 | 0.55468 | 4 | 11337.312 | 23806.2718 | 231.1264 | 485.3231 | 47.1529 | 4.6057 | 62.4102 | 1738917.103 | 0 | 2078585.7536 | 0 | 0 | 0 | 127739.2001 | 1538644.4021 | 4003237.1149 | 2732291.5892 | 12219415.163 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25154428.0529 | 52819676.5125 | 421696.5034 | 2.2187 | 11337.312 | 23806.2718 | 231.1264 | 485.3231
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.7501 | 7.8022 | 0.56041 | 4 | 11197.4509 | 23538.9131 | 228.2752 | 479.8726 | 47.1382 | 4.6017 | 65.8018 | 1742365.6158 | 0 | 2084472.2933 | 0 | 0 | 0 | 101081.1994 | 1531888.4523 | 3985659.5195 | 2720294.5191 | 12165761.5995 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 25100774.4894 | 52766022.949 | 562341.3252 | 2.2417 | 11197.4509 | 23538.9131 | 228.2752 | 479.8726
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.5138 | 7.7873 | 0.5634 | 4 | 11090.1841 | 23366.2566 | 226.0884 | 476.3527 | 47.1484 | 4.6045 | 60.9482 | 1739909.0209 | 0 | 2080286.9222 | 0 | 0 | 0 | 72842.7981 | 1518285.1091 | 3950266.4108 | 2696137.9952 | 12057728.2563 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24992741.1461 | 52657989.6058 | 749894.2093 | 2.2536 | 11090.1841 | 23366.2566 | 226.0884 | 476.3527
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.8459 | 7.5769 | 0.5582 | 4 | 10987.8553 | 23378.324 | 224.0023 | 476.5988 | 47.2612 | 4.6349 | 58.3801 | 1711739.3293 | 0 | 2033030.4557 | 0 | 0 | 0 | 0 | 1460460.2161 | 3799817.9008 | 2593453.7958 | 11598501.6977 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24533514.5875 | 52198763.0472 | 1000000 | 2.2328 | 10987.8553 | 23378.324 | 224.0023 | 476.5988
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2297 | 7.6899 | 0.5644 | 4 | 10920.8829 | 23175.1648 | 222.637 | 472.4571 | 47.2022 | 4.6189 | 50.797 | 1726391.3784 | 0 | 2057591.9879 | 0 | 0 | 0 | 0 | 1475753.5129 | 3839607.9218 | 2620611.3027 | 11719956.1036 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24654968.9935 | 52320217.4531 | 1333521.4322 | 2.2576 | 10920.8829 | 23175.1648 | 222.637 | 472.4571
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.2749 | 7.7751 | 0.56902 | 4 | 10872.1958 | 23026.9028 | 221.6444 | 469.4346 | 47.157 | 4.6068 | 57.6753 | 1737323.7419 | 0 | 2076093.545 | 0 | 0 | 0 | 0 | 1487232.7419 | 3869474.521 | 2640995.8704 | 11811120.4202 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24746133.31 | 52411381.7697 | 1778279.41 | 2.2761 | 10872.1958 | 23026.9028 | 221.6444 | 469.4346
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.0713 | 7.8401 | 0.5725 | 4 | 10836.2944 | 22917.1192 | 220.9125 | 467.1965 | 47.122 | 4.5974 | 53.9144 | 1745565.886 | 0 | 2090169.3515 | 0 | 0 | 0 | 0 | 1495936.7426 | 3892120.5455 | 2656452.2474 | 11880244.7731 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24815257.663 | 52480506.1226 | 2371373.7057 | 2.29 | 10836.2944 | 22917.1192 | 220.9125 | 467.1965
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.6781 | 7.8896 | 0.57513 | 4 | 10809.6616 | 22835.3732 | 220.3696 | 465.53 | 47.0949 | 4.5901 | 52.4717 | 1751790.6903 | 0 | 2100881.3647 | 0 | 0 | 0 | 0 | 1502542.1015 | 3909306.3343 | 2668181.9014 | 11932702.3922 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24867715.282 | 52532963.7417 | 3162277.6602 | 2.3005 | 10809.6616 | 22835.3732 | 220.3696 | 465.53
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.1191 | 7.9255 | 0.57704 | 4 | 10790.3966 | 22776.3351 | 219.9768 | 464.3264 | 47.0755 | 4.585 | 55.0133 | 1756309.8944 | 0 | 2108648.1011 | 0 | 0 | 0 | 0 | 1507333.6182 | 3921772.878 | 2676690.5736 | 11970755.0655 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24905767.9553 | 52571016.4149 | 4216965.0343 | 2.3081 | 10790.3966 | 22776.3351 | 219.9768 | 464.3264
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.4675 | 7.9539 | 0.57852 | 4 | 10775.6365 | 22730.7953 | 219.6759 | 463.398 | 47.0597 | 4.5807 | 55.2984 | 1759842.9596 | 0 | 2114790.0399 | 0 | 0 | 0 | 0 | 1511106.8698 | 3931590.1045 | 2683391.0324 | 12000721.0061 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24935733.896 | 52600982.3556 | 5623413.2519 | 2.3141 | 10775.6365 | 22730.7953 | 219.6759 | 463.398
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7303 | 7.9753 | 0.57964 | 4 | 10764.6295 | 22696.7769 | 219.4515 | 462.7045 | 47.0477 | 4.5775 | 55.5585 | 1762498.3513 | 0 | 2119421.5087 | 0 | 0 | 0 | 0 | 1513948.7454 | 3938984.0818 | 2688437.5739 | 12023290.261 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24958303.1509 | 52623551.6105 | 7498942.0933 | 2.3185 | 10764.6295 | 22696.7769 | 219.4515 | 462.7045
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.9155 | 7.9904 | 0.58043 | 4 | 10756.7484 | 22672.5643 | 219.2909 | 462.2109 | 47.0394 | 4.5753 | 50 | 1764380.5377 | 0 | 2122675.9436 | 0 | 0 | 0 | 0 | 1515952.0277 | 3944196.2116 | 2691994.9596 | 12039199.6802 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24974212.5701 | 52639461.0297 | 10000000 | 2.3217 | 10756.7484 | 22672.5643 | 219.2909 | 462.2109
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.192 | [19 empty] | 100 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.02032 | 0.00013032 | 4 | 25897242.1397 | 80671678.6807 | 527950.3096 | 1644601.2864 | 27.921 | 2.9872 | 30.6114 | 17177.8154 | 0 | 893.3618 | 0 | 0 | 0 | 17249.9477 | 13775.2387 | 35840.3454 | 24461.7722 | 109398.4812 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 13499631.6007 | 42052274.7917 | 133.3521 | 0.00052128 | 25897242.1397 | 80671678.6807 | 527950.3096 | 1644601.2864
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.58935 | -0.018471 | 0.00041512 | 4 | 8199346.3672 | 25394872.7813 | 167154.7661 | 517708.8308 | 34.022 | 3.6757 | 30.3969 | 31888.3661 | 0 | 12210.7594 | 0 | 0 | 0 | 28393.988 | 28272.3143 | 73558.7623 | 50205.3667 | 224529.5568 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 13614762.6764 | 42167405.8673 | 177.8279 | 0.0016605 | 8199346.3672 | 25394872.7813 | 167154.7661 | 517708.8308
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | -0.0065727 | 0.0010135 | 4 | 3391559.4486 | 10434734.1836 | 69141.5268 | 212726.1704 | 38.185 | 4.1459 | 42.6172 | 49538.2889 | 0 | 26078.6315 | 0 | 0 | 0 | 40280.0926 | 45199.8351 | 117600.6992 | 80264.8936 | 358962.4409 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 13749195.5605 | 42301838.7515 | 237.1374 | 0.0040539 | 3391559.4486 | 10434734.1836 | 69141.5268 | 212726.1704
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.014615 | 0.0020221 | 4 | 1718646.5621 | 5248790.2723 | 35036.9348 | 107003.6892 | 41.0965 | 4.4755 | 103.4469 | 69782.3248 | 0 | 42464.2006 | 0 | 0 | 0 | 52605.8613 | 64292.4308 | 167275.7168 | 114169.1139 | 510589.6481 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 13900822.7677 | 42453465.9586 | 316.2278 | 0.0080882 | 1718646.5621 | 5248790.2723 | 35036.9348 | 107003.6892
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.046889 | 0.0035546 | 4 | 990384.7998 | 2998536.3663 | 20190.3337 | 61129.2196 | 43.321 | 4.7248 | 144.8295 | 93999.2312 | 0 | 62603.6009 | 0 | 0 | 0 | 66635.2651 | 87062.8579 | 226519.6972 | 154604.3478 | 691425 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14081658.1196 | 42634301.3105 | 421.6965 | 0.014218 | 990384.7998 | 2998536.3663 | 20190.3337 | 61129.2196
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.092222 | 0.0057585 | 4 | 620587.4253 | 1860167.5478 | 12651.5141 | 37922.0315 | 45.027 | 4.9129 | 204.2081 | 122568.5832 | 0 | 87017.1158 | 0 | 0 | 0 | 82432.7073 | 113887.1785 | 296311.0769 | 202238.3985 | 904455.0602 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14294688.1797 | 42847331.3707 | 562.3413 | 0.023034 | 620587.4253 | 1860167.5478 | 12651.5141 | 37922.0315
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2003 | 0.15431 | 0.0088313 | 4 | 411888.3765 | 1220165.119 | 8396.9017 | 24874.7163 | 46.3604 | 5.0572 | 50.2198 | 156688.4483 | 0 | 116986.0605 | 0 | 0 | 0 | 100805.6347 | 146047.256 | 379985.0016 | 259347.5715 | 1159859.9727 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14550093.0922 | 43102736.2832 | 749.8942 | 0.035325 | 411888.3765 | 1220165.119 | 8396.9017 | 24874.7163
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 0.23699 | 0.013032 | 4 | 284930.8428 | 832654.0972 | 5808.7006 | 16974.78 | 47.3937 | 5.1668 | 45.6312 | 197078.2611 | 0 | 153454.3567 | 0 | 0 | 0 | 121861.1344 | 184233.5633 | 479337.9403 | 327157.9937 | 1463123.2495 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14853356.3691 | 43405999.5601 | 1000 | 0.05213 | 284930.8428 | 832654.0972 | 5808.7006 | 16974.78
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5922 | 0.34544 | 0.018703 | 4 | 203344.9625 | 585005.0579 | 4145.4621 | 11926.1194 | 48.1925 | 5.2499 | 50.8179 | 244781.2346 | 0 | 197718.7564 | 0 | 0 | 0 | 145876.3094 | 229466.7572 | 597025.432 | 407482.125 | 1822350.6146 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 15212583.7342 | 43765226.9252 | 1333.5214 | 0.074812 | 203344.9625 | 585005.0579 | 4145.4621 | 11926.1194
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3561 | 0.48891 | 0.026304 | 4 | 148722.1529 | 420089.4349 | 3031.9022 | 8564.0913 | 48.8182 | 5.3136 | 49.4067 | 302164.3475 | 0 | 252432.627 | 0 | 0 | 0 | 174426.5696 | 284319.1822 | 739740.1901 | 504887.8799 | 2257970.7963 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 15648203.9159 | 44200847.1068 | 1778.2794 | 0.10522 | 148722.1529 | 420089.4349 | 3031.9022 | 8564.0913
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.607 | 0.67346 | 0.036399 | 4 | 110992.4395 | 307098.647 | 2262.731 | 6260.6213 | 49.2931 | 5.3605 | 49.4686 | 369495.8501 | 0 | 318384.5164 | 0 | 0 | 0 | 206469.3895 | 348796.4048 | 907496.6973 | 619385.1431 | 2770028.0011 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 16160261.1207 | 44712904.3116 | 2371.3737 | 0.1456 | 110992.4395 | 307098.647 | 2262.731 | 6260.6213
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5112 | 0.91257 | 0.049739 | 4 | 84300.7481 | 227813.3488 | 1718.5848 | 4644.2833 | 49.655 | 5.3945 | 43.793 | 449499.8501 | 0 | 398872.9967 | 0 | 0 | 0 | 243522.648 | 425839.243 | 1107946.3586 | 756196.1558 | 3381877.2521 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 16772110.3717 | 45324753.5626 | 3162.2777 | 0.19896 | 84300.7481 | 227813.3488 | 1718.5848 | 4644.2833
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2159 | 1.2186 | 0.067217 | 4 | 65067.5445 | 171263.8102 | 1326.4899 | 3491.4444 | 49.9222 | 5.417 | 62.1544 | 543589.6078 | 0 | 496118.4171 | 0 | 0 | 0 | 285422.437 | 516800.8802 | 1344609.8798 | 917723.8719 | 4104265.0938 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 17494498.2134 | 46047141.4043 | 4216.965 | 0.26887 | 65067.5445 | 171263.8102 | 1326.4899 | 3491.4444
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.825 | 1.6009 | 0.089798 | 4 | 51014.5534 | 130505.8101 | 1040.0007 | 2660.5375 | 50.1067 | 5.4285 | 46.641 | 651692.0921 | 0 | 610945.3377 | 0 | 0 | 0 | 330321.8935 | 621254.1361 | 1616375.8254 | 1103209.714 | 4933798.9988 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 18324032.1184 | 46876675.3094 | 5623.4133 | 0.35919 | 51014.5534 | 130505.8101 | 1040.0007 | 2660.5375
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4935 | 2.0725 | 0.11852 | 4 | 40642.8595 | 100871.9445 | 828.5597 | 2056.411 | 50.2195 | 5.4288 | 48.1727 | 774650.1965 | 0 | 745304.3606 | 0 | 0 | 0 | 377603.9521 | 740047.8186 | 1925452.6193 | 1314160.9767 | 5877219.9238 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 19267453.0434 | 47820096.2343 | 7498.9421 | 0.47407 | 40642.8595 | 100871.9445 | 828.5597 | 2056.411
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.2144 | 2.634 | 0.15406 | 4 | 32938.7701 | 79272.0895 | 671.5014 | 1616.0688 | 50.2638 | 5.417 | 61.7783 | 909670.2479 | 0 | 897342.7138 | 0 | 0 | 0 | 423380.985 | 869853.6392 | 2263180.7377 | 1544667.3572 | 6908095.6807 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 20298328.8002 | 48850971.9912 | 10000 | 0.61624 | 32938.7701 | 79272.0895 | 671.5014 | 1616.0688
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.8936 | 3.2786 | 0.19653 | 4 | 27199.5481 | 63520.2476 | 554.4996 | 1294.9462 | 50.2419 | 5.3919 | 44.9259 | 1052765.4856 | 0 | 1063794.776 | 0 | 0 | 0 | 463802.107 | 1006341.3238 | 2618293.6954 | 1787039.2477 | 7992036.6355 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 21382269.755 | 49934912.946 | 13335.2143 | 0.78613 | 27199.5481 | 63520.2476 | 554.4996 | 1294.9462
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.1855 | 3.9787 | 0.24485 | 4 | 22925.7094 | 52078.5279 | 467.3716 | 1061.6912 | 50.157 | 5.3533 | 54.0522 | 1196324.8691 | 0 | 1236825.6332 | 0 | 0 | 0 | 493151.6336 | 1141257.833 | 2969318.7773 | 2026621.0789 | 9063499.825 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 22453732.9446 | 51006376.1355 | 17782.7941 | 0.97941 | 22925.7094 | 52078.5279 | 467.3716 | 1061.6912
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.5802 | 4.6918 | 0.29669 | 4 | 19751.6879 | 43811.324 | 402.6649 | 893.1531 | 50.0182 | 5.3034 | 54.6651 | 1331668.4757 | 0 | 1406353.1498 | 0 | 0 | 0 | 506780.6943 | 1265472.9047 | 3292500.9139 | 2247199.5279 | 10049975.6664 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 23440208.786 | 51992851.977 | 23713.7371 | 1.1867 | 19751.6879 | 43811.324 | 402.6649 | 893.1531
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5682 | 5.3748 | 0.34894 | 4 | 17401.8697 | 37858.7594 | 354.7607 | 771.802 | 49.8412 | 5.2461 | 56.8675 | 1451986.6912 | 0 | 1563296.5328 | 0 | 0 | 0 | 503438.9252 | 1372301.6382 | 3570447.3649 | 2436903.6919 | 10898374.8444 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 24288607.964 | 52841251.1549 | 31622.7766 | 1.3957 | 17401.8697 | 37858.7594 | 354.7607 | 771.802
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.7493 | 5.9924 | 0.39855 | 4 | 15665.3837 | 33575.7403 | 319.36 | 684.4869 | 49.6462 | 5.1865 | 62.753 | 1553506.9597 | 0 | 1701261.163 | 0 | 0 | 0 | 485151.6573 | 1458568.7142 | 3794896.6007 | 2590094.9073 | 11583480.0022 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 24973713.1218 | 53526356.3127 | 42169.6503 | 1.5942 | 15665.3837 | 33575.7403 | 319.36 | 684.4869
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.9024 | 6.5244 | 0.44323 | 4 | 14381.8756 | 30486.7359 | 293.194 | 621.5133 | 49.4526 | 5.1294 | 72.5873 | 1635648.0574 | 0 | 1817383.7906 | 0 | 0 | 0 | 456139.3312 | 1524576.7599 | 3966635.9956 | 2707310.5732 | 12107694.5079 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 25497927.6275 | 54050570.8184 | 56234.1325 | 1.7729 | 14381.8756 | 30486.7359 | 293.194 | 621.5133
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0056 | 6.9678 | 0.48185 | 4 | 13429.5658 | 28243.5134 | 273.7799 | 575.7822 | 49.2718 | 5.0774 | 63.4095 | 1700350.9362 | 0 | 1912407.2307 | 0 | 0 | 0 | 421180.1613 | 1573235.948 | 4093237.2216 | 2793718.5113 | 12494130.009 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 25884363.1286 | 54437006.3196 | 74989.4209 | 1.9274 | 13429.5658 | 28243.5134 | 273.7799 | 575.7822
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.0741 | 7.3226 | 0.51391 | 4 | 12724.2751 | 26614.1203 | 259.4016 | 542.5648 | 49.1175 | 5.0338 | 55.3364 | 1749875.7418 | 0 | 1987313.6194 | 0 | 0 | 0 | 384658.2532 | 1607520.5697 | 4182438.7744 | 2854600.4041 | 12766407.3626 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26156640.4822 | 54709283.6732 | 100000 | 2.0556 | 12724.2751 | 26614.1203 | 259.4016 | 542.5648
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.2607 | 7.6016 | 0.53988 | 4 | 12198.8541 | 25420.5467 | 248.6901 | 518.2322 | 48.9892 | 4.998 | 56.9735 | 1787335.5433 | 0 | 2045514.0894 | 0 | 0 | 0 | 349423.2369 | 1631086.4191 | 4243752.2808 | 2896448.132 | 12953559.7016 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26343792.8212 | 54896436.0121 | 133352.1432 | 2.1595 | 12198.8541 | 25420.5467 | 248.6901 | 518.2322
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7233 | 7.8178 | 0.56051 | 4 | 11806.3366 | 24541.4609 | 240.6881 | 500.3109 | 48.8856 | 4.9693 | 64.9893 | 1815481.664 | 0 | 2090218.6089 | 0 | 0 | 0 | 317406.3192 | 1647011.5709 | 4285186.259 | 2924727.6735 | 13080032.0955 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26470265.2151 | 55022908.4061 | 177827.941 | 2.242 | 11806.3366 | 24541.4609 | 240.6881 | 500.3109
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.5797 | 7.9814 | 0.57658 | 4 | 11512.437 | 23892.6602 | 234.6966 | 487.0842 | 48.8048 | 4.9471 | 68.1827 | 1836236.9906 | 0 | 2123768.3622 | 0 | 0 | 0 | 289251.208 | 1657210.0587 | 4311720.6323 | 2942837.9285 | 13161025.1803 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26551258.2999 | 55103901.4909 | 237137.3706 | 2.3063 | 11512.437 | 23892.6602 | 234.6966 | 487.0842
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.983 | 8.1054 | 0.58899 | 4 | 11292.0075 | 23411.2994 | 230.2028 | 477.271 | 48.7423 | 4.93 | 58.5546 | 1851660.4682 | 0 | 2149043.3031 | 0 | 0 | 0 | 265448.639 | 1663799.44 | 4328864.8506 | 2954539.2098 | 13213355.9106 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26603589.0302 | 55156232.2211 | 316227.766 | 2.356 | 11292.0075 | 23411.2994 | 230.2028 | 477.271
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0204 | 8.1974 | 0.59846 | 4 | 11126.4972 | 23054.1427 | 226.8287 | 469.9899 | 48.6952 | 4.9172 | 60.1002 | 1862916.0365 | 0 | 2167683.1252 | 0 | 0 | 0 | 245642.485 | 1667734.2422 | 4339102.3989 | 2961526.5469 | 13244604.8346 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26634837.9542 | 55187481.1451 | 421696.5034 | 2.3938 | 11126.4972 | 23054.1427 | 226.8287 | 469.9899
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7929 | 8.266 | 0.60565 | 4 | 11002.1445 | 22788.1324 | 224.2936 | 464.5669 | 48.6597 | 4.9075 | 53.6831 | 1871216.4659 | 0 | 2181538.8193 | 0 | 0 | 0 | 229579.5131 | 1670110.5713 | 4345285.1198 | 2965746.3809 | 13263476.8703 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26653709.9899 | 55206353.1809 | 562341.3252 | 2.4226 | 11002.1445 | 22788.1324 | 224.2936 | 464.5669
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.3628 | 8.3168 | 0.61108 | 4 | 10908.6902 | 22589.92 | 222.3884 | 460.5261 | 48.6333 | 4.9004 | 69.0869 | 1877294.9673 | 0 | 2191746.428 | 0 | 0 | 0 | 216715.924 | 1671445.3545 | 4348757.9519 | 2968116.6602 | 13274077.2859 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26664310.4055 | 55216953.5964 | 749894.2093 | 2.4443 | 10908.6902 | 22589.92 | 222.3884 | 460.5261
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.7797 | 8.354 | 0.61516 | 4 | 10838.4568 | 22442.2064 | 220.9566 | 457.5147 | 48.6138 | 4.8951 | 64.2065 | 1881717.6153 | 0 | 2199206.5232 | 0 | 0 | 0 | 206519.5917 | 1672103.0548 | 4350469.1531 | 2969284.5902 | 13279300.5282 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26669533.6478 | 55222176.8388 | 1000000 | 2.4606 | 10838.4568 | 22442.2064 | 220.9566 | 457.5147
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.0887 | 8.3817 | 0.61823 | 4 | 10785.6831 | 22331.8161 | 219.8807 | 455.2643 | 48.5993 | 4.8911 | 55.083 | 1884981.9227 | 0 | 2204730.9596 | 0 | 0 | 0 | 198563.551 | 1672427.809 | 4351314.0969 | 2969861.2817 | 13281879.6211 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26672112.7406 | 55224755.9316 | 1333521.4322 | 2.4729 | 10785.6831 | 22331.8161 | 219.8807 | 455.2643
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.323 | 8.4027 | 0.62055 | 4 | 10746.0384 | 22248.9985 | 219.0725 | 453.5759 | 48.5882 | 4.8881 | 55.1813 | 1887449.9775 | 0 | 2208918.2156 | 0 | 0 | 0 | 192457.0365 | 1672641.8395 | 4351870.9604 | 2970241.3525 | 13283579.3819 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26673812.5015 | 55226455.6925 | 1778279.41 | 2.4822 | 10746.0384 | 22248.9985 | 219.0725 | 453.5759
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4862 | 8.4174 | 0.62226 | 4 | 10716.2646 | 22187.5765 | 218.4655 | 452.3238 | 48.5805 | 4.8861 | 49.6364 | 1889164.7573 | 0 | 2211832.8817 | 0 | 0 | 0 | 187660.3498 | 1672576.6157 | 4351701.2614 | 2970125.5294 | 13283061.3954 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26673294.515 | 55225937.7059 | 2371373.7057 | 2.489 | 10716.2646 | 22187.5765 | 218.4655 | 452.3238
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6151 | 8.429 | 0.62357 | 4 | 10693.9101 | 22141.2093 | 218.0098 | 451.3785 | 48.5744 | 4.8844 | 53.9515 | 1890517.3285 | 0 | 2214134.9444 | 0 | 0 | 0 | 184068.1693 | 1672600.9725 | 4351764.6327 | 2970168.7816 | 13283254.829 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26673487.9486 | 55226131.1395 | 3162277.6602 | 2.4943 | 10693.9101 | 22141.2093 | 218.0098 | 451.3785
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7077 | 8.4373 | 0.62454 | 4 | 10677.1315 | 22106.6587 | 217.6678 | 450.6741 | 48.57 | 4.8832 | 52.9342 | 1891487.6657 | 0 | 2215788.4738 | 0 | 0 | 0 | 181302.1962 | 1672545.5509 | 4351620.4372 | 2970070.3653 | 13282814.6892 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26673047.8087 | 55225690.9997 | 4216965.0343 | 2.4981 | 10677.1315 | 22106.6587 | 217.6678 | 450.6741
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7756 | 8.4434 | 0.62526 | 4 | 10664.5395 | 22080.8346 | 217.4111 | 450.1477 | 48.5668 | 4.8823 | 64.1288 | 1892198.1745 | 0 | 2217000.1602 | 0 | 0 | 0 | 179193.5977 | 1672472.8537 | 4351431.2939 | 2969941.271 | 13282237.3511 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26672470.4707 | 55225113.6616 | 5623413.2519 | 2.501 | 10664.5395 | 22080.8346 | 217.4111 | 450.1477
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.8191 | 8.4474 | 0.62578 | 4 | 10655.0899 | 22061.84 | 217.2184 | 449.7604 | 48.5647 | 4.8818 | 68.0686 | 1892653.4963 | 0 | 2217776.8932 | 0 | 0 | 0 | 177530.55 | 1672304.7664 | 4350993.9654 | 2969642.7854 | 13280902.4568 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26671135.5764 | 55223778.7674 | 7498942.0933 | 2.5031 | 10655.0899 | 22061.84 | 217.2184 | 449.7604
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.8534 | 8.4506 | 0.62618 | 4 | 10647.9996 | 22047.5143 | 217.0739 | 449.4684 | 48.563 | 4.8813 | 63.9801 | 1893011.8808 | 0 | 2218388.3238 | 0 | 0 | 0 | 176292.5989 | 1672200.1934 | 4350721.8877 | 2969457.0868 | 13280071.9714 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 26670305.091 | 55222948.282 | 10000000 | 2.5047 | 10647.9996 | 22047.5143 | 217.0739 | 449.4684
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4188 | [19 empty] | 100 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.32634 | -0.02121 | 0.00011924 | 4 | 29279858.0555 | 91035095.7868 | 596909.5104 | 1855873.5617 | 27.9629 | 3.1982 | 29.6449 | 17928.2594 | 0 | 320.966 | 0 | 0 | 0 | 18411.7066 | 14297.7635 | 37199.8477 | 25389.6604 | 113548.2035 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 13964861.6437 | 43418670.7794 | 133.3521 | 0.00047694 | 29279858.0555 | 91035095.7868 | 596909.5104 | 1855873.5617
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6088 | -0.019653 | 0.00042752 | 4 | 8241055.6133 | 25464808.0959 | 168005.0655 | 519134.5567 | 34.6306 | 3.9512 | 32.2902 | 34223.5012 | 0 | 12668.8826 | 0 | 0 | 0 | 31067.7103 | 30404.4367 | 79106.1075 | 53991.5438 | 241462.1822 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14092775.6224 | 43546584.7581 | 177.8279 | 0.0017101 | 8241055.6133 | 25464808.0959 | 168005.0655 | 519134.5567
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95256 | -0.0065536 | 0.0010885 | 4 | 3271679.299 | 10036266.4047 | 66697.6078 | 204602.8657 | 39.196 | 4.4632 | 34.5188 | 54169.8399 | 0 | 27989.4363 | 0 | 0 | 0 | 45038.4566 | 49607.1158 | 129067.5395 | 88091.2478 | 393963.6359 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14245277.0761 | 43699086.2119 | 237.1374 | 0.0043541 | 3271679.299 | 10036266.4047 | 66697.6078 | 204602.8657
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3597 | 0.016758 | 0.002208 | 4 | 1632009.0563 | 4966902.5161 | 33270.7121 | 101257.026 | 42.2955 | 4.8095 | 109.9028 | 76621.4619 | 0 | 45774.2406 | 0 | 0 | 0 | 59250.7971 | 70842.1348 | 184316.7031 | 125799.9372 | 562605.2748 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14413918.715 | 43867727.8507 | 316.2278 | 0.008832 | 1632009.0563 | 4966902.5161 | 33270.7121 | 101257.026
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.051302 | 0.0039109 | 4 | 933731.6891 | 2816525.4392 | 19035.3834 | 57418.6807 | 44.591 | 5.0623 | 153.5176 | 102578.6018 | 0 | 66898.3217 | 0 | 0 | 0 | 74506.8007 | 95153.6524 | 247570.2849 | 168971.8065 | 755679.4681 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14606992.9083 | 44060802.0441 | 421.6965 | 0.015644 | 933731.6891 | 2816525.4392 | 19035.3834 | 57418.6807
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5266 | 0.10064 | 0.0063631 | 4 | 583066.1855 | 1740275.1352 | 11886.5928 | 35477.8625 | 46.3983 | 5.2574 | 214.7492 | 133875.0357 | 0 | 93062.0426 | 0 | 0 | 0 | 92427.3478 | 124552.1262 | 324059.0832 | 221176.983 | 989152.6186 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14840466.0587 | 44294275.1945 | 562.3413 | 0.025452 | 583066.1855 | 1740275.1352 | 11886.5928 | 35477.8625
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.364 | 0.16667 | 0.0097788 | 4 | 386329.9618 | 1139333.7977 | 7875.8588 | 23226.8605 | 47.7796 | 5.4034 | 41.5218 | 170281.2998 | 0 | 124333.9755 | 0 | 0 | 0 | 112201.8811 | 158658.691 | 412797.3687 | 281742.6862 | 1260015.9024 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 15111329.3426 | 44565138.4783 | 749.8942 | 0.039115 | 386329.9618 | 1139333.7977 | 7875.8588 | 23226.8605
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4675 | 0.25613 | 0.014454 | 4 | 267083.5846 | 776535.0753 | 5444.8601 | 15830.7179 | 48.8774 | 5.517 | 38.3483 | 214295.0416 | 0 | 163183.6853 | 0 | 0 | 0 | 135897.5364 | 200216.7427 | 520922.8944 | 355540.5793 | 1590056.4797 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 15441369.9199 | 44895179.0557 | 1000 | 0.057815 | 267083.5846 | 776535.0753 | 5444.8601 | 15830.7179
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8823 | 0.37307 | 0.020762 | 4 | 190619.8701 | 545286.2312 | 3886.0439 | 11116.3974 | 49.7227 | 5.6027 | 48.6208 | 266070.1809 | 0 | 210144.0478 | 0 | 0 | 0 | 162740.4055 | 249192.3073 | 648347.2673 | 442510.3322 | 1979004.5411 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 15830317.9813 | 45284127.1171 | 1333.5214 | 0.083047 | 190619.8701 | 545286.2312 | 3886.0439 | 11116.3974
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7239 | 0.52687 | 0.02921 | 4 | 139493.6722 | 391582.1269 | 2843.7672 | 7982.9313 | 50.382 | 5.6679 | 53.7201 | 327980.1323 | 0 | 267830.3313 | 0 | 0 | 0 | 194248.6013 | 308123.0353 | 801672.9332 | 547158.2496 | 2447013.283 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 16298326.7232 | 45752135.8589 | 1778.2794 | 0.11684 | 139493.6722 | 391582.1269 | 2843.7672 | 7982.9313
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1017 | 0.72683 | 0.04044 | 4 | 104206.7472 | 286287.9164 | 2124.3955 | 5836.3664 | 50.8886 | 5.7165 | 46.8357 | 401487.3568 | 0 | 338185.0405 | 0 | 0 | 0 | 230663.2467 | 378430.9011 | 984599.5779 | 672009.4434 | 3005375.5665 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 16856689.0067 | 46310498.1425 | 2371.3737 | 0.16176 | 104206.7472 | 286287.9164 | 2124.3955 | 5836.3664
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1567 | 0.98495 | 0.055267 | 4 | 79252.9863 | 212487.8559 | 1615.6793 | 4331.8524 | 51.2722 | 5.7512 | 46.3183 | 488450.3158 | 0 | 423675.9196 | 0 | 0 | 0 | 272436.8605 | 461979.6074 | 1201976.1734 | 820373.4365 | 3668892.3131 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 17520205.7533 | 46974014.8891 | 3162.2777 | 0.22107 | 79252.9863 | 212487.8559 | 1615.6793 | 4331.8524
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0077 | 1.3117 | 0.074633 | 4 | 61274.695 | 159936.9224 | 1249.1675 | 3260.5305 | 51.5523 | 5.7736 | 48.4357 | 589562.5957 | 0 | 525779.0621 | 0 | 0 | 0 | 318551.123 | 559218.1846 | 1454971.0048 | 993047.6074 | 4441129.5777 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 18292443.0179 | 47746252.1537 | 4216.965 | 0.29853 | 61274.695 | 159936.9224 | 1249.1675 | 3260.5305
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.8339 | 1.7226 | 0.09965 | 4 | 48138.6807 | 122031.4706 | 981.3721 | 2487.7766 | 51.7471 | 5.7845 | 40.6307 | 706628.273 | 0 | 647264.4795 | 0 | 0 | 0 | 369200.8624 | 672006.5098 | 1748423.091 | 1193334.6861 | 5336857.9017 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 19188171.3419 | 48641980.4777 | 5623.4133 | 0.3986 | 48138.6807 | 122031.4706 | 981.3721 | 2487.7766
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.7117 | 2.2249 | 0.13133 | 4 | 38443.5495 | 94511.4744 | 783.7238 | 1926.7442 | 51.8641 | 5.7833 | 53.6023 | 838527.8855 | 0 | 788084.7339 | 0 | 0 | 0 | 421651.6264 | 798823.0559 | 2078373.7303 | 1418532.7772 | 6343993.8092 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 20195307.2494 | 49649116.3852 | 7498.9421 | 0.52532 | 38443.5495 | 94511.4744 | 783.7238 | 1926.7442
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.6714 | 2.8222 | 0.17041 | 4 | 31242.4922 | 74453.7265 | 636.9205 | 1517.8399 | 51.9086 | 5.7691 | 47.093 | 983233.2629 | 0 | 947303.9007 | 0 | 0 | 0 | 472984.2152 | 937373.3377 | 2438853.1431 | 1664567.3836 | 7444315.2433 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 21295628.6835 | 50749437.8192 | 10000 | 0.68162 | 31242.4922 | 74453.7265 | 636.9205 | 1517.8399
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.5519 | 3.5019 | 0.21679 | 4 | 25879.4152 | 59845.1655 | 527.5869 | 1220.0246 | 51.8828 | 5.7408 | 48.2213 | 1135286.3978 | 0 | 1120161.0009 | 0 | 0 | 0 | 518084.9022 | 1081677.5973 | 2814303.2257 | 1920819.7797 | 8590332.9036 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 22441646.3438 | 51895455.4795 | 13335.2143 | 0.86716 | 25879.4152 | 59845.1655 | 527.5869 | 1220.0246
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.9977 | 4.2347 | 0.26918 | 4 | 21887.7063 | 49242.9982 | 446.2105 | 1003.8851 | 51.791 | 5.6983 | 67.9517 | 1286787.8426 | 0 | 1298640.9016 | 0 | 0 | 0 | 551373.801 | 1223352.9926 | 3182913.5426 | 2172403.8952 | 9715472.9757 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 23566786.4159 | 53020595.5516 | 17782.7941 | 1.0767 | 21887.7063 | 49242.9982 | 446.2105 | 1003.8851
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.4897 | 4.9763 | 0.32493 | 4 | 18925.1636 | 41586.9584 | 385.8151 | 847.8064 | 51.6436 | 5.6442 | 66.2832 | 1428739.493 | 0 | 1472437.3434 | 0 | 0 | 0 | 568332.6694 | 1353108.7073 | 3520511.2956 | 2402821.2985 | 10745950.8073 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 24597264.2475 | 54051073.3833 | 23713.7371 | 1.2997 | 18925.1636 | 41586.9584 | 385.8151 | 847.8064
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.4823 | 5.6789 | 0.3806 | 4 | 16733.2895 | 36080.2746 | 341.1307 | 735.5452 | 51.4587 | 5.583 | 69.2332 | 1553679.251 | 0 | 1631700.486 | 0 | 0 | 0 | 567432.4546 | 1463596.7547 | 3807978.5307 | 2599023.5934 | 11623411.0703 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 25474724.5105 | 54928533.6463 | 31622.7766 | 1.5224 | 16733.2895 | 36080.2746 | 341.1307 | 735.5452
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.6512 | 6.3126 | 0.43313 | 4 | 15114.3623 | 32114.9998 | 308.1267 | 654.7077 | 51.2563 | 5.5199 | 70.9932 | 1658981.8573 | 0 | 1771480.6042 | 0 | 0 | 0 | 551937.0553 | 1553135.8116 | 4040940.7897 | 2758025.122 | 12334501.2401 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 26185814.6803 | 55639623.816 | 42169.6503 | 1.7325 | 15114.3623 | 32114.9998 | 308.1267 | 654.7077
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.7466 | 6.8545 | 0.48009 | 4 | 13918.3209 | 29255.8936 | 283.7438 | 596.421 | 51.0575 | 5.4602 | 67.634 | 1743636.9311 | 0 | 1888295.223 | 0 | 0 | 0 | 525624.6264 | 1621447.1444 | 4218672.8652 | 2879330.9155 | 12877007.7056 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 26728321.1458 | 56182130.2816 | 56234.1325 | 1.9204 | 13918.3209 | 29255.8936 | 283.7438 | 596.421
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.7696 | 7.3031 | 0.5204 | 4 | 13033.1287 | 27182.6679 | 265.698 | 554.1555 | 50.8753 | 5.4068 | 80.5471 | 1810082.1359 | 0 | 1983279.1125 | 0 | 0 | 0 | 493845.1113 | 1672010.4803 | 4350228.2932 | 2969120.1984 | 13278565.3315 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27129878.7717 | 56583687.9075 | 74989.4209 | 2.0816 | 13033.1287 | 27182.6679 | 265.698 | 554.1555
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7966 | 7.6642 | 0.55386 | 4 | 12376.3128 | 25671.1026 | 252.3079 | 523.3402 | 50.7172 | 5.3613 | 162.0715 | 1861202.8769 | 0 | 2058652.3251 | 0 | 0 | 0 | 460691.8367 | 1708413.3451 | 4444941.0802 | 3033763.6217 | 13567665.0857 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27418978.5259 | 56872787.6617 | 100000 | 2.2154 | 12376.3128 | 25671.1026 | 252.3079 | 523.3402
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.9922 | 7.9517 | 0.58105 | 4 | 11886.2921 | 24558.9985 | 242.3181 | 500.6684 | 50.5828 | 5.323 | 68.984 | 1900328.4108 | 0 | 2118039.3701 | 0 | 0 | 0 | 429029.6371 | 1734484.993 | 4512774.1601 | 3080061.0925 | 13774717.6636 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27626031.1038 | 57079840.2396 | 133352.1432 | 2.3242 | 11886.2921 | 24558.9985 | 242.3181 | 500.6684
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.4406 | 8.1725 | 0.6025 | 4 | 11522.132 | 23743.5295 | 234.8942 | 484.044 | 50.4767 | 5.2932 | 69.579 | 1929570.3644 | 0 | 2163233.7286 | 0 | 0 | 0 | 400612.9189 | 1752432.6346 | 4559470.242 | 3111932.1279 | 13917252.0164 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27768565.4566 | 57222374.5924 | 177827.941 | 2.41 | 11522.132 | 23743.5295 | 234.8942 | 484.044
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.3165 | 8.3421 | 0.61928 | 4 | 11249.9866 | 23140.3831 | 229.3462 | 471.748 | 50.3928 | 5.2697 | 64.8298 | 1951495.9472 | 0 | 2197708.683 | 0 | 0 | 0 | 376137.0316 | 1764883.2481 | 4591864.1843 | 3134041.6591 | 14016130.7533 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27867444.1935 | 57321253.3293 | 237137.3706 | 2.4771 | 11249.9866 | 23140.3831 | 229.3462 | 471.748
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7346 | 8.4706 | 0.63222 | 4 | 11046.3137 | 22693.2615 | 225.194 | 462.6328 | 50.3277 | 5.2516 | 59.0756 | 1967793.8114 | 0 | 2223684.0378 | 0 | 0 | 0 | 355634.5536 | 1773373.8371 | 4613954.9551 | 3149119.0641 | 14083560.259 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27934873.6992 | 57388682.835 | 316227.766 | 2.5289 | 11046.3137 | 22693.2615 | 225.194 | 462.6328
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.8038 | 8.5677 | 0.64214 | 4 | 10893.7362 | 22360.8056 | 222.0835 | 455.8553 | 50.2778 | 5.2377 | 66.9524 | 1979925.2721 | 0 | 2243222.6545 | 0 | 0 | 0 | 338912.2763 | 1779203.4792 | 4629122.488 | 3159471.217 | 14129857.3871 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 27981170.8273 | 57434979.9631 | 421696.5034 | 2.5686 | 10893.7362 | 22360.8056 | 222.0835 | 455.8553
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6151 | 8.6414 | 0.64971 | 4 | 10779.3648 | 22112.7432 | 219.7519 | 450.7982 | 50.2394 | 5.2271 | 53.9709 | 1989039.1474 | 0 | 2258020.2355 | 0 | 0 | 0 | 325602.8413 | 1783338.2675 | 4639880.3589 | 3166813.685 | 14162694.5356 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28014007.9758 | 57467817.1116 | 562341.3252 | 2.5989 | 10779.3648 | 22112.7432 | 219.7519 | 450.7982
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2212 | 8.6966 | 0.65545 | 4 | 10693.6043 | 21927.7739 | 218.0036 | 447.0273 | 50.2105 | 5.2191 | 69.6674 | 1995796.9624 | 0 | 2269060.8833 | 0 | 0 | 0 | 315083.0649 | 1786176.9552 | 4647266.042 | 3171854.5655 | 14185238.4733 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28036551.9135 | 57490361.0493 | 749894.2093 | 2.6218 | 10693.6043 | 21927.7739 | 218.0036 | 447.0273
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6887 | 8.7391 | 0.65983 | 4 | 10629.2787 | 21788.949 | 216.6922 | 444.1972 | 50.188 | 5.2129 | 63.2387 | 2000980.0266 | 0 | 2277567.996 | 0 | 0 | 0 | 307007.6113 | 1788366.6972 | 4652963.3017 | 3175743.0623 | 14202628.6951 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28053942.1353 | 57507751.2711 | 1000000 | 2.6393 | 10629.2787 | 21788.949 | 216.6922 | 444.1972
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0176 | 8.7692 | 0.66307 | 4 | 10581.0324 | 21686.1586 | 215.7087 | 442.1017 | 50.172 | 5.2085 | 62.9327 | 2004610.8654 | 0 | 2283548.8397 | 0 | 0 | 0 | 300569.1247 | 1789604.2436 | 4656183.1436 | 3177940.6705 | 14212456.8875 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28063770.3277 | 57517579.4634 | 1333521.4322 | 2.6523 | 10581.0324 | 21686.1586 | 215.7087 | 442.1017
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2734 | 8.7925 | 0.66554 | 4 | 10544.844 | 21608.7974 | 214.9709 | 440.5246 | 50.1596 | 5.2051 | 65.7518 | 2007425.3199 | 0 | 2288197.0516 | 0 | 0 | 0 | 295720.4645 | 1790623.706 | 4658835.5756 | 3179751.0098 | 14220553.1273 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28071866.5675 | 57525675.7033 | 1778279.41 | 2.6621 | 10544.844 | 21608.7974 | 214.9709 | 440.5246
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.4781 | 8.8111 | 0.66743 | 4 | 10517.7003 | 21550.2686 | 214.4175 | 439.3314 | 50.1496 | 5.2023 | 65.8492 | 2009671.8896 | 0 | 2291915.0529 | 0 | 0 | 0 | 292142.6079 | 1791554.5247 | 4661257.3748 | 3181403.9376 | 14227945.3875 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28079258.8277 | 57533067.9635 | 2371373.7057 | 2.6697 | 10517.7003 | 21550.2686 | 214.4175 | 439.3314
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.6218 | 8.8242 | 0.66882 | 4 | 10497.3415 | 21506.8834 | 214.0025 | 438.4469 | 50.1426 | 5.2004 | 70.8933 | 2011246.3796 | 0 | 2294524.8728 | 0 | 0 | 0 | 289334.1346 | 1792091.101 | 4662653.4363 | 3182356.7782 | 14232206.7026 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28083520.1428 | 57537329.2786 | 3162277.6602 | 2.6753 | 10497.3415 | 21506.8834 | 214.0025 | 438.4469
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.7339 | 8.8344 | 0.66989 | 4 | 10482.072 | 21474.1764 | 213.6912 | 437.7801 | 50.1371 | 5.1989 | 68.6729 | 2012472.3272 | 0 | 2296559.309 | 0 | 0 | 0 | 287247.6384 | 1792548.9171 | 4663844.5799 | 3183169.7582 | 14235842.5299 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28087155.9701 | 57540965.1058 | 4216965.0343 | 2.6795 | 10482.072 | 21474.1764 | 213.6912 | 437.7801
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.807 | 8.8412 | 0.67065 | 4 | 10470.62 | 21450.1691 | 213.4578 | 437.2907 | 50.1335 | 5.1979 | 67.0675 | 2013271.8036 | 0 | 2297887.1427 | 0 | 0 | 0 | 285571.2057 | 1792724.7593 | 4664302.0853 | 3183482.015 | 14237239.0116 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28088552.4518 | 57542361.5876 | 5623413.2519 | 2.6826 | 10470.62 | 21450.1691 | 213.4578 | 437.2907
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.8607 | 8.8461 | 0.67122 | 4 | 10462.0313 | 21432.2271 | 213.2827 | 436.9249 | 50.1309 | 5.1972 | 62.0808 | 2013858.3368 | 0 | 2298861.8667 | 0 | 0 | 0 | 284297.0487 | 1792836.7284 | 4664593.4058 | 3183680.8473 | 14238128.2337 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28089441.6739 | 57543250.8097 | 7498942.0933 | 2.6849 | 10462.0313 | 21432.2271 | 213.2827 | 436.9249
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9191 | 8.8514 | 0.6717 | 4 | 10455.5902 | 21417.9398 | 213.1513 | 436.6337 | 50.128 | 5.1964 | 67.503 | 2014495.2908 | 0 | 2299920.9047 | 0 | 0 | 0 | 283504.5719 | 1793189.0993 | 4665510.2028 | 3184306.58 | 14240926.6496 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 28092240.0898 | 57546049.2256 | 10000000 | 2.6868 | 10455.5902 | 21417.9398 | 213.1513 | 436.6337
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8674 | [19 empty] | 100 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.02375 | 9.4606e-05 | 4 | 38271199.9041 | 118521869.955 | 780210.1757 | 2416228.6317 | 30.6643 | 3.7132 | 30.7777 | 24031.8841 | 0 | 4017.5909 | 0 | 0 | 0 | 25052.6781 | 20709.8397 | 53882.7548 | 36776.0873 | 164470.8349 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 14482724.6866 | 44851470.9807 | 133.3521 | 0.00037842 | 38271199.9041 | 118521869.955 | 780210.1757 | 2416228.6317
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6477 | -0.020517 | 0.00044196 | 4 | 8251219.2136 | 25429673.0577 | 168212.2643 | 518418.2815 | 35.5772 | 4.265 | 32.8642 | 37766.7797 | 0 | 14006.8144 | 0 | 0 | 0 | 34940.6405 | 33818.5515 | 87988.9338 | 60054.2553 | 268575.9753 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 14586829.8269 | 44955576.1211 | 177.8279 | 0.0017678 | 8251219.2136 | 25429673.0577 | 168212.2643 | 518418.2815
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.99609 | -0.0066896 | 0.0011712 | 4 | 3147426.7996 | 9629795.4786 | 64164.5525 | 196316.4061 | 40.1502 | 4.7747 | 41.4008 | 58599.2277 | 0 | 29687.7492 | 0 | 0 | 0 | 49538.9564 | 53752.114 | 139851.9745 | 95451.8463 | 426881.8682 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 14745135.7198 | 45113882.014 | 237.1374 | 0.0046848 | 3147426.7996 | 9629795.4786 | 64164.5525 | 196316.4061
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.018046 | 0.0024105 | 4 | 1547869.5358 | 4697486.5178 | 31555.4141 | 95764.6165 | 43.3802 | 5.1313 | 115.2759 | 82594.8178 | 0 | 48303.807 | 0 | 0 | 0 | 64878.9172 | 76353.2414 | 198655.4719 | 135586.4416 | 606372.697 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 14924626.5486 | 45293372.8427 | 316.2278 | 0.009642 | 1547869.5358 | 4697486.5178 | 31555.4141 | 95764.6165
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9626 | 0.055932 | 0.0042999 | 4 | 880240.8385 | 2645925.9237 | 17944.9001 | 53940.7788 | 45.8627 | 5.4002 | 162.6064 | 111405.7665 | 0 | 71270.5495 | 0 | 0 | 0 | 82517.1807 | 103425.4637 | 269091.8411 | 183660.7108 | 821371.5124 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 15139625.3641 | 45508371.6582 | 421.6965 | 0.017199 | 880240.8385 | 2645925.9237 | 17944.9001 | 53940.7788
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.10815 | 0.0070181 | 4 | 548075.3523 | 1629879.2756 | 11173.2574 | 33227.2936 | 47.7311 | 5.5981 | 219.4012 | 144611.568 | 0 | 98459.6773 | 0 | 0 | 0 | 101586.6853 | 134416.593 | 349724.4022 | 238694.0906 | 1067493.0165 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 15385746.8681 | 45754493.1622 | 562.3413 | 0.028072 | 548075.3523 | 1629879.2756 | 11173.2574 | 33227.2936
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5318 | 0.17982 | 0.01081 | 4 | 362685.081 | 1065028.9765 | 7393.8259 | 21712.0562 | 49.2077 | 5.7509 | 36.796 | 184441.9214 | 0 | 131961.2882 | 0 | 0 | 0 | 123966.6974 | 171744.2637 | 446843.3446 | 304979.7644 | 1363937.2796 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 15682191.1313 | 46050937.4254 | 749.8942 | 0.043239 | 362685.081 | 1065028.9765 | 7393.8259 | 21712.0562
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.689 | 0.27601 | 0.015997 | 4 | 250640.6087 | 725239.9828 | 5109.6478 | 14784.998 | 50.3655 | 5.868 | 47.1637 | 232023.4753 | 0 | 173085.9223 | 0 | 0 | 0 | 150150.4248 | 216551.3307 | 563422.1418 | 384547.1889 | 1719780.4838 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 16038034.3355 | 46406780.6296 | 1000 | 0.063988 | 250640.6087 | 725239.9828 | 5109.6478 | 14784.998
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1964 | 0.40357 | 0.023006 | 4 | 178924.4752 | 508929.2683 | 3647.6174 | 10375.2115 | 51.2692 | 5.9574 | 59.0247 | 288869.5281 | 0 | 223574.2609 | 0 | 0 | 0 | 180848.1379 | 270383.8515 | 703483.3183 | 480141.8199 | 2147300.9166 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 16465554.7683 | 46834301.0624 | 1333.5214 | 0.092025 | 178924.4752 | 508929.2683 | 3647.6174 | 10375.2115
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1138 | 0.56795 | 0.032371 | 4 | 131022.013 | 365557.764 | 2671.061 | 7452.3895 | 51.9576 | 6.0237 | 50.7549 | 355297.9624 | 0 | 284179.034 | 0 | 0 | 0 | 215172.7577 | 333313.4041 | 867213.1056 | 591890.764 | 2647067.0279 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 16965320.8796 | 47334067.1737 | 1778.2794 | 0.12948 | 131022.013 | 365557.764 | 2671.061 | 7452.3895
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6157 | 0.78371 | 0.04483 | 4 | 97979.2514 | 267332.9629 | 1997.4396 | 5449.944 | 52.4932 | 6.0736 | 46.5063 | 435043.2606 | 0 | 358897.4814 | 0 | 0 | 0 | 255867.9128 | 409425.3754 | 1065240.842 | 727048.7632 | 3251523.6354 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 17569777.4871 | 47938523.7812 | 2371.3737 | 0.17932 | 97979.2514 | 267332.9629 | 1997.4396 | 5449.944
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.805 | 1.0602 | 0.061249 | 4 | 74618.5036 | 198574.5045 | 1521.1991 | 4048.2099 | 52.8959 | 6.1087 | 44.3563 | 528673.4367 | 0 | 448996.1413 | 0 | 0 | 0 | 301849.2357 | 499012.3373 | 1298327.7402 | 886135.3606 | 3962994.2517 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 18281248.1034 | 48649994.3975 | 3162.2777 | 0.245 | 74618.5036 | 198574.5045 | 1521.1991 | 4048.2099
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8313 | 1.4107 | 0.082678 | 4 | 57788.746 | 149617.4059 | 1178.1018 | 3050.1532 | 53.1905 | 6.131 | 53.2028 | 637743.4479 | 0 | 556796.4442 | 0 | 0 | 0 | 352998.5725 | 603540.0012 | 1570287.28 | 1071753.3348 | 4793119.0807 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 19111372.9323 | 49480119.2265 | 4216.965 | 0.33071 | 57788.746 | 149617.4059 | 1178.1018 | 3050.1532
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8324 | 1.8478 | 0.11026 | 4 | 45491.3078 | 114345.6771 | 927.4018 | 2331.0913 | 53.3934 | 6.1411 | 46.9258 | 762958.1699 | 0 | 683970.8146 | 0 | 0 | 0 | 408274.4157 | 723529.3261 | 1882474.8902 | 1284827.7936 | 5746035.4101 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 20064289.2617 | 50433035.5559 | 5623.4133 | 0.44106 | 45491.3078 | 114345.6771 | 927.4018 | 2331.0913
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.9419 | 2.3837 | 0.14514 | 4 | 36414.6738 | 88723.5798 | 742.3624 | 1808.7502 | 53.5151 | 6.1384 | 49.9329 | 904534.5573 | 0 | 831906.189 | 0 | 0 | 0 | 466430.0534 | 859119.6119 | 2235253.0004 | 1525606.1026 | 6822849.5146 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 21141103.3662 | 51509849.6604 | 7498.9421 | 0.58057 | 36414.6738 | 88723.5798 | 742.3624 | 1808.7502
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.1381 | 3.0176 | 0.18797 | 4 | 29673.4545 | 70063.2313 | 604.9335 | 1428.3337 | 53.5592 | 6.1216 | 56.7323 | 1059081.5119 | 0 | 998366.4871 | 0 | 0 | 0 | 523217.8059 | 1006459.6639 | 2618601.5922 | 1787249.3936 | 7992976.4546 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 22311230.3062 | 52679976.6004 | 10000 | 0.75189 | 29673.4545 | 70063.2313 | 604.9335 | 1428.3337
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.2038 | 3.7322 | 0.23846 | 4 | 24654.2347 | 56492.1358 | 502.6099 | 1151.6686 | 53.5292 | 6.0899 | 56.6188 | 1219905.7129 | 0 | 1177368.0638 | 0 | 0 | 0 | 572555.7606 | 1158233.5195 | 3013486.0315 | 2056766.1374 | 9198315.2257 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 23516569.0774 | 53885315.3715 | 13335.2143 | 0.95386 | 24654.2347 | 56492.1358 | 502.6099 | 1151.6686
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.8077 | 4.4989 | 0.29512 | 4 | 20920.381 | 46646.2483 | 426.4903 | 950.9469 | 53.4302 | 6.0433 | 57.4337 | 1379486.5055 | 0 | 1361458.8911 | 0 | 0 | 0 | 609679.5841 | 1306743.7425 | 3399879.1679 | 2320487.3927 | 10377735.2838 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 24695989.1355 | 55064735.4296 | 17782.7941 | 1.1805 | 20920.381 | 46646.2483 | 426.4903 | 950.9469
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.3682 | 5.267 | 0.35487 | 4 | 18150.9548 | 39545.1909 | 370.0318 | 806.1822 | 53.2744 | 5.9849 | 63.1959 | 1527547.0631 | 0 | 1538975.2671 | 0 | 0 | 0 | 629239.2597 | 1441347.0201 | 3750089.2852 | 2559512.9938 | 11446710.889 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 25764964.7406 | 56133711.0348 | 23713.7371 | 1.4195 | 18150.9548 | 39545.1909 | 370.0318 | 806.1822
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.3823 | 5.9907 | 0.41409 | 4 | 16103.0951 | 34437.5919 | 328.2834 | 702.0569 | 53.0811 | 5.9197 | 79.8505 | 1657283.6701 | 0 | 1700893.4787 | 0 | 0 | 0 | 630666.8139 | 1555649.1455 | 4047479.969 | 2762488.2462 | 12354461.3234 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 26672715.1751 | 57041461.4692 | 31622.7766 | 1.6564 | 16103.0951 | 34437.5919 | 328.2834 | 702.0569
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.5077 | 6.6381 | 0.46952 | 4 | 14591.14 | 30761.2577 | 297.4601 | 627.1098 | 52.8722 | 5.8534 | 67.6752 | 1765795.174 | 0 | 1841855.4043 | 0 | 0 | 0 | 617075.7556 | 1647643.2702 | 4286829.811 | 2925849.4315 | 13085048.8466 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 27403302.6982 | 57772048.9924 | 42169.6503 | 1.8781 | 14591.14 | 30761.2577 | 297.4601 | 627.1098
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.5519 | 7.1902 | 0.51881 | 4 | 13474.4658 | 28108.2865 | 274.6952 | 573.0254 | 52.6681 | 5.7909 | 54.8112 | 1852938.8578 | 0 | 1959452.2811 | 0 | 0 | 0 | 592978.9578 | 1718094.3377 | 4470129.0371 | 3050954.9198 | 13644548.3913 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 27962802.2429 | 58331548.5371 | 56234.1325 | 2.0752 | 13474.4658 | 28108.2865 | 274.6952 | 573.0254
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.5166 | 7.6458 | 0.56092 | 4 | 12648.2808 | 26183.6157 | 257.8523 | 533.7884 | 52.4821 | 5.7354 | 69.1839 | 1921200.7871 | 0 | 2054805.776 | 0 | 0 | 0 | 563576.8587 | 1770437.5345 | 4606315.2981 | 3143904.8412 | 14060241.0955 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 28378494.9472 | 58747241.2413 | 74989.4209 | 2.2437 | 12648.2808 | 26183.6157 | 257.8523 | 533.7884
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4823 | 8.0112 | 0.59572 | 4 | 12035.5209 | 24780.0864 | 245.3604 | 505.1756 | 52.3218 | 5.6884 | 79.0149 | 1973591.8629 | 0 | 2130224.4608 | 0 | 0 | 0 | 532848.0337 | 1808299.0993 | 4704823.3233 | 3211138.5926 | 14360925.3726 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 28679179.2242 | 59047925.5184 | 100000 | 2.3829 | 12035.5209 | 24780.0864 | 245.3604 | 505.1756
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6124 | 8.3004 | 0.62385 | 4 | 11579.8999 | 23749.8641 | 236.0719 | 484.1731 | 52.1878 | 5.6496 | 68.5596 | 2013607.2552 | 0 | 2189307.7495 | 0 | 0 | 0 | 503853.2186 | 1835639.6071 | 4775957.7162 | 3259689.2774 | 14578054.824 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 28896308.6757 | 59265054.9698 | 133352.1432 | 2.4954 | 11579.8999 | 23749.8641 | 236.0719 | 484.1731
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.123 | 8.4468 | 0.64351 | 4 | 11239.725 | 23037.7221 | 229.137 | 469.6551 | 52.1188 | 5.6297 | 104.0499 | 2032384.5323 | 0 | 2217725.5681 | 0 | 0 | 0 | 468091.4649 | 1840098.6104 | 4787559.1282 | 3267607.4795 | 14613466.7835 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 28931720.6351 | 59300466.9293 | 177827.941 | 2.5741 | 11239.725 | 23037.7221 | 229.137 | 469.6551
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9218 | 8.7001 | 0.66363 | 4 | 10985.6055 | 22425.9732 | 223.9564 | 457.1838 | 51.9911 | 5.5933 | 70.2918 | 2066678.3961 | 0 | 2270086.3461 | 0 | 0 | 0 | 455647.0939 | 1869040.6161 | 4862860.2901 | 3319002.0698 | 14843314.8121 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29161568.6638 | 59530314.9579 | 237137.3706 | 2.6545 | 10985.6055 | 22425.9732 | 223.9564 | 457.1838
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.325 | 8.8307 | 0.67703 | 4 | 10796.2514 | 22010.2376 | 220.0962 | 448.7085 | 51.925 | 5.5745 | 60.3361 | 2083515.5988 | 0 | 2296222.4959 | 0 | 0 | 0 | 437180.7064 | 1878598.3324 | 4887727.5075 | 3335974.4566 | 14919219.0975 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29237472.9492 | 59606219.2433 | 316227.766 | 2.7081 | 10796.2514 | 22010.2376 | 220.0962 | 448.7085
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.4038 | 8.9311 | 0.68734 | 4 | 10654.5367 | 21700.2095 | 217.2071 | 442.3881 | 51.8733 | 5.5599 | 79.1262 | 2096297.7987 | 0 | 2316268.3977 | 0 | 0 | 0 | 422398.1395 | 1885636.091 | 4906038.3116 | 3348471.9567 | 14975110.6952 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29293364.5468 | 59662110.841 | 421696.5034 | 2.7494 | 10654.5367 | 21700.2095 | 217.2071 | 442.3881
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2151 | 9.0067 | 0.6952 | 4 | 10548.4041 | 21469.2863 | 215.0435 | 437.6804 | 51.834 | 5.5489 | 66.5381 | 2105817.2815 | 0 | 2331316.4076 | 0 | 0 | 0 | 410614.9984 | 1890621.9882 | 4919010.5933 | 3357325.8055 | 15014707.0745 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29332960.9261 | 59701707.2203 | 562341.3252 | 2.7808 | 10548.4041 | 21469.2863 | 215.0435 | 437.6804
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.8265 | 9.0638 | 0.70116 | 4 | 10468.8837 | 21296.9029 | 213.4224 | 434.1662 | 51.804 | 5.5404 | 70.4019 | 2112938.7223 | 0 | 2342642.107 | 0 | 0 | 0 | 401381.7438 | 1894215.4035 | 4928359.9229 | 3363706.9151 | 15043244.8146 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29361498.6662 | 59730244.9604 | 749894.2093 | 2.8046 | 10468.8837 | 21296.9029 | 213.4224 | 434.1662
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.2823 | 9.1063 | 0.70566 | 4 | 10409.2848 | 21168.2658 | 212.2073 | 431.5437 | 51.7815 | 5.5341 | 68.5582 | 2118218.3429 | 0 | 2351077.2759 | 0 | 0 | 0 | 394182.5246 | 1896756.4759 | 4934971.2721 | 3368219.2967 | 15063425.1881 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29381679.0397 | 59750425.3339 | 1000000 | 2.8226 | 10409.2848 | 21168.2658 | 212.2073 | 431.5437
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.6307 | 9.1389 | 0.70907 | 4 | 10364.6082 | 21071.7913 | 211.2966 | 429.577 | 51.7642 | 5.5293 | 68.0563 | 2122236.6568 | 0 | 2357519.7578 | 0 | 0 | 0 | 388701.2883 | 1898698.5041 | 4940024.0311 | 3371667.9086 | 15078848.1468 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29397101.9984 | 59765848.2926 | 1333521.4322 | 2.8363 | 10364.6082 | 21071.7913 | 211.2966 | 429.577
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8741 | 9.1617 | 0.71159 | 4 | 10331.1134 | 21000.397 | 210.6137 | 428.1215 | 51.752 | 5.5259 | 63.9269 | 2125034.9738 | 0 | 2362017.734 | 0 | 0 | 0 | 384338.5381 | 1899842.5859 | 4943000.6972 | 3373699.5443 | 15087934.0733 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29406187.925 | 59774934.2191 | 1778279.41 | 2.8464 | 10331.1134 | 21000.397 | 210.6137 | 428.1215
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.0787 | 9.1808 | 0.71355 | 4 | 10305.9998 | 20945.965 | 210.1017 | 427.0118 | 51.7418 | 5.523 | 62.5273 | 2127382.7156 | 0 | 2365799.0351 | 0 | 0 | 0 | 381228.0784 | 1901019.8334 | 4946063.6537 | 3375790.0751 | 15097283.3914 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29415537.243 | 59784283.5372 | 2371373.7057 | 2.8542 | 10305.9998 | 20945.965 | 210.1017 | 427.0118
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.2297 | 9.1949 | 0.71502 | 4 | 10287.1694 | 20905.31 | 209.7179 | 426.183 | 51.7342 | 5.5209 | 64.1575 | 2129111.0155 | 0 | 2368586.9975 | 0 | 0 | 0 | 378844.1555 | 1901851.4457 | 4948227.3384 | 3377266.8343 | 15103887.7869 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29422141.6385 | 59790887.9327 | 3162277.6602 | 2.8601 | 10287.1694 | 20905.31 | 209.7179 | 426.183
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.3345 | 9.2047 | 0.7161 | 4 | 10273.0495 | 20875.2187 | 209.43 | 425.5696 | 51.729 | 5.5194 | 61.1756 | 2130309.4696 | 0 | 2370522.3903 | 0 | 0 | 0 | 376962.2364 | 1902339.6976 | 4949497.6696 | 3378133.8615 | 15107765.325 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29426019.1766 | 59794765.4708 | 4216965.0343 | 2.8644 | 10273.0495 | 20875.2187 | 209.43 | 425.5696
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4077 | 9.2116 | 0.71689 | 4 | 10262.4617 | 20852.9069 | 209.2142 | 425.1147 | 51.7253 | 5.5184 | 60.9348 | 2131145.0664 | 0 | 2371872.8351 | 0 | 0 | 0 | 375491.2253 | 1902618.5595 | 4950223.211 | 3378629.0585 | 15109979.9559 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29428233.8075 | 59796980.1017 | 5623413.2519 | 2.8676 | 10262.4617 | 20852.9069 | 209.2142 | 425.1147
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.466 | 9.2171 | 0.7175 | 4 | 10254.5223 | 20836.031 | 209.0523 | 424.7707 | 51.7223 | 5.5176 | 66.4021 | 2131810.9971 | 0 | 2372949.724 | 0 | 0 | 0 | 374415.8274 | 1902878.8539 | 4950900.4438 | 3379091.2837 | 15112047.1299 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29430300.9815 | 59799047.2757 | 7498942.0933 | 2.87 | 10254.5223 | 20836.031 | 209.0523 | 424.7707
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.5197 | 9.2221 | 0.71798 | 4 | 10248.5686 | 20822.9452 | 208.9309 | 424.5039 | 51.7196 | 5.5168 | 61.6888 | 2132423.8122 | 0 | 2373941.2651 | 0 | 0 | 0 | 373699.7958 | 1903225.3005 | 4951801.8267 | 3379706.4961 | 15114798.4963 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 29433052.348 | 59801798.6421 | 10000000 | 2.8719 | 10248.5686 | 20822.9452 | 208.9309 | 424.5039
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.3402 | [19 empty] | 100 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.024792 | 8.5734e-05 | 4 | 43625304.2295 | 134889017.6446 | 889360.8343 | 2749895.0756 | 30.7474 | 3.9303 | 31.1505 | 24878.0066 | 0 | 3591.1516 | 0 | 0 | 0 | 26275.2695 | 21350.3268 | 55549.1708 | 37913.4505 | 169557.3757 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 14960611.7297 | 46258066.3957 | 133.3521 | 0.00034293 | 43625304.2295 | 134889017.6446 | 889360.8343 | 2749895.0756
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.68196 | -0.021433 | 0.00045814 | 4 | 8231639.5673 | 25310180.8114 | 167813.1067 | 515982.2704 | 36.4377 | 4.5697 | 27.1544 | 41122.3086 | 0 | 15163.8158 | 0 | 0 | 0 | 38611.0312 | 37009.8907 | 96292.1438 | 65721.3668 | 293920.557 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15084974.911 | 46382429.577 | 177.8279 | 0.0018326 | 8231639.5673 | 25310180.8114 | 167813.1067 | 515982.2704
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0452 | -0.0065636 | 0.0012624 | 4 | 3021023.5801 | 9219270.5499 | 61587.6519 | 187947.3001 | 41.158 | 5.0926 | 34.5041 | 63466.3686 | 0 | 31669.1624 | 0 | 0 | 0 | 54453.4425 | 58339.6996 | 151787.9314 | 103598.3821 | 463314.9866 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15254369.3406 | 46551824.0066 | 237.1374 | 0.0050494 | 3021023.5801 | 9219270.5499 | 61587.6519 | 187947.3001
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.020445 | 0.0026333 | 4 | 1466955.0807 | 4438278.7009 | 29905.8635 | 90480.3145 | 44.5795 | 5.466 | 119.3805 | 89807.939 | 0 | 51727.2735 | 0 | 0 | 0 | 71760.7967 | 83185.4436 | 216431.4605 | 147718.919 | 660631.8323 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15451686.1863 | 46749140.8523 | 316.2278 | 0.010533 | 1466955.0807 | 4438278.7009 | 29905.8635 | 90480.3145
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.060784 | 0.0047235 | 4 | 829872.1151 | 2486355.7694 | 16918.0656 | 50687.7254 | 47.1362 | 5.7387 | 174.8489 | 120476.6249 | 0 | 75719.2248 | 0 | 0 | 0 | 90663.2869 | 111875.0633 | 291075.9659 | 198665.3277 | 888475.4935 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15679529.8475 | 46976984.5135 | 421.6965 | 0.018894 | 829872.1151 | 2486355.7694 | 16918.0656 | 50687.7254
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7741 | 0.11692 | 0.0077323 | 4 | 515518.6568 | 1527423.1576 | 10509.5451 | 31138.5871 | 49.0968 | 5.9426 | 38.4825 | 156311.2965 | 0 | 104504.0044 | 0 | 0 | 0 | 111629.1201 | 145253.3242 | 377919.354 | 257937.7245 | 1153554.8237 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15944609.1777 | 47242063.8437 | 562.3413 | 0.030929 | 515518.6568 | 1527423.1576 | 10509.5451 | 31138.5871
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7144 | 0.19455 | 0.011933 | 4 | 340814.0624 | 996529.7695 | 6947.9556 | 20315.6073 | 50.6586 | 6.101 | 48.6829 | 199656.0881 | 0 | 140267.9453 | 0 | 0 | 0 | 136651.6258 | 185864.5071 | 483581.3214 | 330054.1884 | 1476075.676 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 16267130.03 | 47564584.696 | 749.8942 | 0.04773 | 340814.0624 | 996529.7695 | 6947.9556 | 20315.6073
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9324 | 0.29829 | 0.017678 | 4 | 235490.4738 | 678107.3077 | 4800.7918 | 13824.1347 | 51.8751 | 6.2215 | 44.6025 | 251144.1907 | 0 | 183920.701 | 0 | 0 | 0 | 165624.3155 | 234268.7908 | 609519.3386 | 416009.473 | 1860486.8097 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 16651541.1637 | 47948995.8297 | 1000 | 0.07071 | 235490.4738 | 678107.3077 | 4800.7918 | 13824.1347
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4935 | 0.4339 | 0.025427 | 4 | 168170.0192 | 475883.9716 | 3428.3733 | 9701.5384 | 52.8127 | 6.3121 | 45.0005 | 311716.4773 | 0 | 236676.7611 | 0 | 0 | 0 | 198541.5532 | 291304.5687 | 757914.733 | 517292.3788 | 2313446.472 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 17104500.826 | 48401955.492 | 1333.5214 | 0.10171 | 168170.0192 | 475883.9716 | 3428.3733 | 9701.5384
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5204 | 0.61186 | 0.0358 | 4 | 123239.9192 | 341798.4769 | 2512.4124 | 6968.0243 | 53.5432 | 6.3808 | 47.8913 | 383989.4289 | 0 | 301326.3654 | 0 | 0 | 0 | 237058.8944 | 359726.1286 | 935933.5966 | 638793.9112 | 2856828.3251 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 17647882.6791 | 48945337.3451 | 1778.2794 | 0.1432 | 123239.9192 | 341798.4769 | 2512.4124 | 6968.0243
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1345 | 0.84303 | 0.049576 | 4 | 92259.6785 | 250084.6736 | 1880.8383 | 5098.3143 | 54.1044 | 6.4315 | 46.8579 | 469747.8018 | 0 | 380107.4773 | 0 | 0 | 0 | 281625.5471 | 441277.5222 | 1148113.5944 | 783611.1195 | 3504483.0623 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 18295537.4163 | 49592992.0823 | 2371.3737 | 0.1983 | 92259.6785 | 250084.6736 | 1880.8383 | 5098.3143
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4527 | 1.1381 | 0.067703 | 4 | 70359.8622 | 185928.7888 | 1434.381 | 3790.4098 | 54.5255 | 6.467 | 45.0686 | 570064.1767 | 0 | 474735.7798 | 0 | 0 | 0 | 331658.9112 | 536818.9584 | 1396692.8131 | 953271.5441 | 4263242.1835 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 19054296.5375 | 50351751.2035 | 3162.2777 | 0.27081 | 70359.8622 | 185928.7888 | 1434.381 | 3790.4098
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6472 | 1.5126 | 0.091338 | 4 | 54582.1945 | 140246.3211 | 1112.7319 | 2859.111 | 54.8343 | 6.4892 | 40.6026 | 687128.474 | 0 | 588142.5724 | 0 | 0 | 0 | 387683.6697 | 648552.3393 | 1687400.1505 | 1151685.2753 | 5150592.4812 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 19941646.8352 | 51239101.5013 | 4216.965 | 0.36535 | 54582.1945 | 140246.3211 | 1112.7319 | 2859.111
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.8749 | 1.9811 | 0.12174 | 4 | 43052.3672 | 107322.6308 | 877.6807 | 2187.917 | 55.0471 | 6.4985 | 50.3902 | 821989.7397 | 0 | 722407.9295 | 0 | 0 | 0 | 448980.9324 | 777417.6546 | 2022681.2671 | 1380521.5267 | 6173999.0501 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 20965053.4041 | 52262508.0701 | 5623.4133 | 0.48697 | 43052.3672 | 107322.6308 | 877.6807 | 2187.917
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.1944 | 2.5497 | 0.16 | 4 | 34541.7635 | 83442.92 | 704.1806 | 1701.0968 | 55.1723 | 6.494 | 50.094 | 972909.214 | 0 | 877008.3412 | 0 | 0 | 0 | 512232.8982 | 921238.6768 | 2396874.065 | 1635915.8002 | 7316178.9954 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 22107233.3494 | 53404688.0154 | 7498.9421 | 0.64001 | 34541.7635 | 83442.92 | 704.1806 | 1701.0968
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5996 | 3.2192 | 0.20678 | 4 | 28221.3689 | 66060.8378 | 575.3308 | 1346.7395 | 55.2157 | 6.4745 | 54.3932 | 1136892.888 | 0 | 1050180.1091 | 0 | 0 | 0 | 573811.847 | 1076745.0892 | 2801469.8513 | 1912060.7379 | 8551160.5225 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 23342214.8765 | 54639669.5425 | 10000 | 0.82711 | 28221.3689 | 66060.8378 | 575.3308 | 1346.7395
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.8823 | 3.9722 | 0.26166 | 4 | 23516.8595 | 53420.0737 | 479.423 | 1089.0405 | 55.1809 | 6.439 | 55.3664 | 1307242.5794 | 0 | 1236118.0416 | 0 | 0 | 0 | 627926.7343 | 1236802.0686 | 3217905.2795 | 2196286.4746 | 9822281.1779 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 24613335.5319 | 55910790.1979 | 13335.2143 | 1.0466 | 23516.8595 | 53420.0737 | 479.423 | 1089.0405
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.5982 | 4.7698 | 0.32267 | 4 | 20018.9516 | 44267.4076 | 408.1134 | 902.451 | 55.0746 | 6.3883 | 54.2628 | 1474080.1391 | 0 | 1424892.111 | 0 | 0 | 0 | 667859.8773 | 1391064.5297 | 3619264.5597 | 2470222.4304 | 11047383.6472 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 25838438.0012 | 57135892.6672 | 17782.7941 | 1.2907 | 20018.9516 | 44267.4076 | 408.1134 | 902.451
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.2339 | 5.5653 | 0.38658 | 4 | 17426.0911 | 37666.0027 | 355.2544 | 767.8724 | 54.9101 | 6.3254 | 69.8298 | 1628338.6007 | 0 | 1606297.5199 | 0 | 0 | 0 | 689912.7293 | 1530574.0515 | 3982239.7181 | 2717960.4344 | 12155323.054 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 26946377.4079 | 58243832.074 | 23713.7371 | 1.5463 | 17426.0911 | 37666.0027 | 355.2544 | 767.8724
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.2607 | 6.3097 | 0.44943 | 4 | 15509.7367 | 32919.4534 | 316.187 | 671.1076 | 54.7084 | 6.2562 | 62.5794 | 1762650.2226 | 0 | 1770693.5413 | 0 | 0 | 0 | 693241.2514 | 1648368.156 | 4288715.8151 | 2927136.6681 | 13090805.6545 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 27881860.0085 | 59179314.6745 | 31622.7766 | 1.7977 | 15509.7367 | 32919.4534 | 316.187 | 671.1076
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.3371 | 6.97 | 0.50778 | 4 | 14095.3124 | 29504.2037 | 287.352 | 601.4831 | 54.4932 | 6.1865 | 66.927 | 1874156.635 | 0 | 1912691.3826 | 0 | 0 | 0 | 681094.5669 | 1742497.6079 | 4533621.3404 | 3094289.7214 | 13838351.2542 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 28629405.6082 | 59926860.2742 | 42169.6503 | 2.0311 | 14095.3124 | 29504.2037 | 287.352 | 601.4831
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3151 | 7.5309 | 0.55939 | 4 | 13050.8653 | 27038.2922 | 266.0595 | 551.2122 | 54.2845 | 6.1215 | 70.0829 | 1963452.4288 | 0 | 2030735.5227 | 0 | 0 | 0 | 658580.6961 | 1814579.7726 | 4721164.3468 | 3222291.6769 | 14410804.4439 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 29201858.7979 | 60499313.4639 | 56234.1325 | 2.2375 | 13050.8653 | 27038.2922 | 266.0595 | 551.2122
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.2191 | 7.993 | 0.60329 | 4 | 12278.2454 | 25247.7172 | 250.3086 | 514.7089 | 54.0951 | 6.064 | 72.6644 | 2033398.8399 | 0 | 2126374.8506 | 0 | 0 | 0 | 631037.7596 | 1868416.4655 | 4861236.3783 | 3317893.7166 | 14838358.0105 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 29629412.3645 | 60926867.0305 | 74989.4209 | 2.4132 | 12278.2454 | 25247.7172 | 250.3086 | 514.7089
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.1165 | 8.3618 | 0.63942 | 4 | 11705.3408 | 23941.9521 | 238.6292 | 488.0891 | 53.933 | 6.0156 | 80.2503 | 2086875.1153 | 0 | 2201665.1598 | 0 | 0 | 0 | 602107.1257 | 1907352.4863 | 4962539.9175 | 3387035.4637 | 15147575.2683 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 29938629.6223 | 61236084.2883 | 100000 | 2.5577 | 11705.3408 | 23941.9521 | 238.6292 | 488.0891
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1982 | 8.6542 | 0.66857 | 4 | 11279.4897 | 22982.5386 | 229.9477 | 468.5301 | 53.7974 | 5.9756 | 68.2696 | 2127836.1697 | 0 | 2260769.9913 | 0 | 0 | 0 | 575041.8131 | 1935822.7099 | 5036613.5994 | 3437592.2736 | 15373676.5571 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30164730.9111 | 61462185.5771 | 133352.1432 | 2.6743 | 11279.4897 | 22982.5386 | 229.9477 | 468.5301
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5734 | 8.8803 | 0.69159 | 4 | 10962.2596 | 22275.8977 | 223.4805 | 454.1243 | 53.6886 | 5.9438 | 78.1057 | 2158609.9615 | 0 | 2306078.7544 | 0 | 0 | 0 | 550840.4139 | 1956056.3606 | 5089257.408 | 3473522.7547 | 15534365.6532 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30325420.0071 | 61622874.6732 | 177827.941 | 2.7663 | 10962.2596 | 22275.8977 | 223.4805 | 454.1243
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.3982 | 9.0543 | 0.70954 | 4 | 10725.5269 | 21752.8665 | 218.6544 | 443.4616 | 53.6023 | 5.9188 | 67.4915 | 2181780.0083 | 0 | 2340745.8975 | 0 | 0 | 0 | 530274.7325 | 1970592.2489 | 5127076.8077 | 3499335.2722 | 15649804.9671 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30440859.3211 | 61738313.9871 | 237137.3706 | 2.8382 | 10725.5269 | 21752.8665 | 218.6544 | 443.4616
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.8083 | 9.1888 | 0.72347 | 4 | 10548.6249 | 21363.7417 | 215.048 | 435.5288 | 53.5341 | 5.8991 | 76.5974 | 2199404.356 | 0 | 2367454.1193 | 0 | 0 | 0 | 513516.5174 | 1981346.2471 | 5155056.5051 | 3518431.9905 | 15735209.7355 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30526264.0894 | 61823718.7555 | 316227.766 | 2.8939 | 10548.6249 | 21363.7417 | 215.048 | 435.5288
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.7 | 9.2753 | 0.73359 | 4 | 10416.3206 | 21082.2052 | 212.3508 | 429.7893 | 53.4902 | 5.8865 | 60.0846 | 2210418.5914 | 0 | 2384303.2467 | 0 | 0 | 0 | 498206.9938 | 1986242.2445 | 5167794.8858 | 3527126.1971 | 15774092.1593 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30565146.5133 | 61862601.1793 | 421696.5034 | 2.9344 | 10416.3206 | 21082.2052 | 212.3508 | 429.7893
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.689 | 9.3688 | 0.74233 | 4 | 10316.0085 | 20856.3205 | 210.3058 | 425.1843 | 53.4392 | 5.8718 | 73.2825 | 2222422.8218 | 0 | 2403014.1575 | 0 | 0 | 0 | 488891.8915 | 1994588.2596 | 5189509.5052 | 3541946.8711 | 15840373.5068 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30631427.8608 | 61928882.5268 | 562341.3252 | 2.9693 | 10316.0085 | 20856.3205 | 210.3058 | 425.1843
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.3003 | 9.4273 | 0.7485 | 4 | 10241.8988 | 20695.2814 | 208.795 | 421.9013 | 53.4086 | 5.863 | 72.1992 | 2229848.9067 | 0 | 2414526.4486 | 0 | 0 | 0 | 480557.7169 | 1998723.8982 | 5200269.5883 | 3549290.8489 | 15873217.4076 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30664271.7616 | 61961726.4276 | 749894.2093 | 2.994 | 10241.8988 | 20695.2814 | 208.795 | 421.9013
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7561 | 9.4709 | 0.75316 | 4 | 10186.3736 | 20575.1174 | 207.663 | 419.4516 | 53.3855 | 5.8565 | 67.9725 | 2235356.6365 | 0 | 2423103.2196 | 0 | 0 | 0 | 474065.6733 | 2001684.9565 | 5207973.6547 | 3554549.0325 | 15896733.1732 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30687787.5272 | 61985242.1932 | 1000000 | 3.0126 | 10186.3736 | 20575.1174 | 207.663 | 419.4516
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0922 | 9.5032 | 0.75665 | 4 | 10144.7619 | 20485.5173 | 206.8147 | 417.625 | 53.3684 | 5.8516 | 66.2239 | 2239402.1148 | 0 | 2429424.0792 | 0 | 0 | 0 | 469017.118 | 2003758.8917 | 5213369.6087 | 3558231.882 | 15913203.6945 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30704258.0485 | 62001712.7145 | 1333521.4322 | 3.0266 | 10144.7619 | 20485.5173 | 206.8147 | 417.625
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.346 | 9.5276 | 0.75929 | 4 | 10113.5718 | 20418.406 | 206.1788 | 416.2568 | 53.3555 | 5.8479 | 70.5622 | 2242446.4277 | 0 | 2434192.6871 | 0 | 0 | 0 | 465175.9768 | 2005307.8857 | 5217399.7734 | 3560982.5522 | 15925505.3029 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30716559.6569 | 62014014.3229 | 1778279.41 | 3.0372 | 10113.5718 | 20418.406 | 206.1788 | 416.2568
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.5332 | 9.5456 | 0.76127 | 4 | 10090.1904 | 20368.2909 | 205.7022 | 415.2352 | 53.3459 | 5.8452 | 66.7712 | 2244687.7313 | 0 | 2437710.0749 | 0 | 0 | 0 | 462225.2332 | 2006402.9854 | 5220248.9981 | 3562927.2066 | 15934202.2295 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30725256.5835 | 62022711.2495 | 2371373.7057 | 3.0451 | 10090.1904 | 20368.2909 | 205.7022 | 415.2352
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.677 | 9.5594 | 0.76276 | 4 | 10072.661 | 20330.6179 | 205.3448 | 414.4671 | 53.3385 | 5.8431 | 70.3375 | 2246405.0979 | 0 | 2440409.1038 | 0 | 0 | 0 | 460021.3777 | 2007265.876 | 5222494.0624 | 3564459.5091 | 15941055.0269 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30732109.3809 | 62029564.0469 | 3162277.6602 | 3.051 | 10072.661 | 20330.6179 | 205.3448 | 414.4671
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.789 | 9.5701 | 0.7639 | 4 | 10059.5182 | 20302.215 | 205.0769 | 413.8881 | 53.3327 | 5.8414 | 72.1186 | 2247742.3544 | 0 | 2442513.1162 | 0 | 0 | 0 | 458396.9079 | 2007974.4276 | 5224337.5685 | 3565717.7399 | 15946682.1146 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30737736.4686 | 62035191.1346 | 4216965.0343 | 3.0556 | 10059.5182 | 20302.215 | 205.0769 | 413.8881
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8692 | 9.5778 | 0.76474 | 4 | 10049.6638 | 20281.0899 | 204.876 | 413.4575 | 53.3286 | 5.8402 | 60.9845 | 2248698.6799 | 0 | 2444018.9896 | 0 | 0 | 0 | 457134.373 | 2008442.2966 | 5225554.8675 | 3566548.5715 | 15950397.7779 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30741452.1319 | 62038906.798 | 5623413.2519 | 3.059 | 10049.6638 | 20281.0899 | 204.876 | 413.4575
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9398 | 9.5845 | 0.7654 | 4 | 10042.2747 | 20264.8243 | 204.7254 | 413.1259 | 53.325 | 5.8392 | 69.0616 | 2249539.2647 | 0 | 2445343.5901 | 0 | 0 | 0 | 456283.7425 | 2008954.9729 | 5226888.7462 | 3567458.9711 | 15954469.2876 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30745523.6416 | 62042978.3076 | 7498942.0933 | 3.0616 | 10042.2747 | 20264.8243 | 204.7254 | 413.1259
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9741 | 9.5879 | 0.76584 | 4 | 10036.7342 | 20253.4064 | 204.6124 | 412.8931 | 53.3232 | 5.8387 | 62.7009 | 2249947.1251 | 0 | 2445986.4191 | 0 | 0 | 0 | 455463.6224 | 2009044.895 | 5227122.7049 | 3567618.6528 | 15955183.4193 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 30746237.7733 | 62043692.4393 | 10000000 | 3.0634 | 10036.7342 | 20253.4064 | 204.6124 | 412.8931
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.9049 | [19 empty] | 100 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.025801 | 7.5616e-05 | 4 | 51061003.47 | 157651302.5639 | 1040947.6209 | 3213935.0419 | 30.8194 | 4.1462 | 28.1742 | 25702.0639 | 0 | 3163.6774 | 0 | 0 | 0 | 27474.2049 | 21972.579 | 57168.1434 | 39018.4326 | 174499.1011 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 15444214.0483 | 47684148.2998 | 133.3521 | 0.00030247 | 51061003.47 | 157651302.5639 | 1040947.6209 | 3213935.0419
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.69881 | -0.022634 | 0.00047638 | 4 | 8176207.2244 | 25095271.2791 | 166683.0434 | 511601.0489 | 36.9968 | 4.8412 | 42.9875 | 43444.517 | 0 | 15550.7887 | 0 | 0 | 0 | 41211.4558 | 39080.637 | 101679.8009 | 69398.5534 | 310365.7527 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 15580080.6999 | 47820014.9513 | 177.8279 | 0.0019055 | 8176207.2244 | 25095271.2791 | 166683.0434 | 511601.0489
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.015214 | 0.00065069 | 4 | 6165553.8946 | 18552458.9317 | 125693.1557 | 378216.9694 | 45.9293 | 5.8168 | 22.2606 | 98744.8364 | 0 | 56369.9654 | 0 | 0 | 0 | 95958.9952 | 97918.7808 | 254764.5818 | 173882.062 | 777639.2215 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 16047354.1687 | 48287288.4201 | 237.1374 | 0.0026027 | 6165553.8946 | 18552458.9317 | 125693.1557 | 378216.9694
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.024399 | 0.0028765 | 4 | 1390531.8417 | 4192569.7686 | 28347.8724 | 85471.2056 | 45.9294 | 5.8169 | 22.155 | 98745.6697 | 0 | 56369.5153 | 0 | 0 | 0 | 80444.6447 | 91868.3336 | 239022.5592 | 163137.8081 | 729588.5305 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 15999303.4777 | 48239237.7292 | 316.2278 | 0.011506 | 1390531.8417 | 4192569.7686 | 28347.8724 | 85471.2056
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.031366 | 0.0045305 | 4 | 880747.8339 | 2659803.2053 | 17955.2359 | 54223.686 | 45.9295 | 5.817 | 22.0278 | 98746.1332 | 0 | 56369.265 | 0 | 0 | 0 | 68032.0486 | 87027.5042 | 226427.7142 | 154541.5676 | 691144.2328 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 15960859.18 | 48200793.4314 | 421.6965 | 0.018122 | 880747.8339 | 2659803.2053 | 17955.2359 | 54223.686
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.923 | 0.1273 | 0.008511 | 4 | 485230.6746 | 1432236.4965 | 9892.0836 | 29198.0782 | 50.5039 | 6.2916 | 40.4734 | 169223.8091 | 0 | 111366.279 | 0 | 0 | 0 | 122836.0325 | 157336.1871 | 409356.4847 | 279394.2122 | 1249513.0047 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 16519227.9519 | 48759162.2033 | 562.3413 | 0.034044 | 485230.6746 | 1432236.4965 | 9892.0836 | 29198.0782
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 0.21005 | 0.013149 | 4 | 320592.0391 | 933580.5128 | 6535.7023 | 19032.3015 | 52.1165 | 6.4521 | 40.0561 | 215417.0113 | 0 | 148810.777 | 0 | 0 | 0 | 149686.0902 | 200426.4126 | 521468.4125 | 355912.9066 | 1591721.6101 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 16861436.5573 | 49101370.8087 | 749.8942 | 0.052595 | 320592.0391 | 933580.5128 | 6535.7023 | 19032.3015
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1707 | 0.32102 | 0.019492 | 4 | 221526.9951 | 635029.223 | 4516.1274 | 12945.9297 | 53.385 | 6.5752 | 49.9177 | 270599.2034 | 0 | 194757.1083 | 0 | 0 | 0 | 181118.9441 | 252125.3498 | 655978.4422 | 447718.7658 | 2002297.8137 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 17272012.7608 | 49511947.0123 | 1000 | 0.077968 | 221526.9951 | 635029.223 | 4516.1274 | 12945.9297
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8102 | 0.46688 | 0.028052 | 4 | 158275.8095 | 445599.8733 | 3226.6665 | 9084.1561 | 54.3704 | 6.6684 | 42.6004 | 335951.705 | 0 | 250648.0637 | 0 | 0 | 0 | 217347.5121 | 313539.4395 | 815765.3058 | 556776.5835 | 2490028.6096 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 17759743.5568 | 49999677.8083 | 1333.5214 | 0.11221 | 158275.8095 | 445599.8733 | 3226.6665 | 9084.1561
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9297 | 0.65757 | 0.0395 | 4 | 116085.7113 | 320133.8778 | 2366.5642 | 6526.3621 | 55.135 | 6.7387 | 43.9277 | 413603.239 | 0 | 318846.9042 | 0 | 0 | 0 | 259400.0962 | 386821.5934 | 1006430.4379 | 686909.454 | 3072011.7247 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 18341726.6719 | 50581660.9233 | 1778.2794 | 0.158 | 116085.7113 | 320133.8778 | 2366.5642 | 6526.3621
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6487 | 0.90405 | 0.054686 | 4 | 87001.6381 | 234388.0298 | 1773.6461 | 4778.317 | 55.7206 | 6.7902 | 41.285 | 505295.8079 | 0 | 401534.1217 | 0 | 0 | 0 | 307600.2253 | 473627.7604 | 1232282.2783 | 841057.9758 | 3761398.1695 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 19031113.1167 | 51271047.3681 | 2371.3737 | 0.21874 | 87001.6381 | 234388.0298 | 1773.6461 | 4778.317
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1272 | 1.221 | 0.074677 | 4 | 66442.7677 | 174374.0994 | 1354.5257 | 3554.8519 | 56.1637 | 6.8263 | 46.586 | 613425.1545 | 0 | 501654.5537 | 0 | 0 | 0 | 362765.1302 | 576359.487 | 1499569.1575 | 1023486.7631 | 4577260.246 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 19846975.1932 | 52086909.4446 | 3162.2777 | 0.29871 | 66442.7677 | 174374.0994 | 1354.5257 | 3554.8519
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5 | 1.6211 | 0.10069 | 4 | 51629.6938 | 131675.9039 | 1052.5411 | 2684.3914 | 56.4864 | 6.8483 | 51.6539 | 738916.4331 | 0 | 620990.8045 | 0 | 0 | 0 | 423930.4344 | 695696.692 | 1810060.0857 | 1235403.2015 | 5524997.6512 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 20794712.5984 | 53034646.8498 | 4216.965 | 0.40277 | 51629.6938 | 131675.9039 | 1052.5411 | 2684.3914
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9271 | 2.1197 | 0.13407 | 4 | 40803.3189 | 100918.9203 | 831.8308 | 2057.3687 | 56.7073 | 6.8564 | 49.7283 | 882925.7591 | 0 | 761731.7481 | 0 | 0 | 0 | 490480.024 | 832703.6372 | 2166524.0529 | 1478697.1837 | 6613062.4049 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 21882777.3521 | 54122711.6035 | 5623.4133 | 0.5363 | 40803.3189 | 100918.9203 | 831.8308 | 2057.3687
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4512 | 2.7218 | 0.17593 | 4 | 32811.3281 | 78624.9742 | 668.9033 | 1602.8764 | 56.8356 | 6.85 | 44.7466 | 1043256.2684 | 0 | 922965.8949 | 0 | 0 | 0 | 558673.0596 | 984709.1369 | 2562011.1827 | 1748625.2763 | 7820240.8189 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 23089955.7661 | 55329890.0175 | 7498.9421 | 0.70372 | 32811.3281 | 78624.9742 | 668.9033 | 1602.8764
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.0929 | 3.4302 | 0.22693 | 4 | 26876.5347 | 62394.2762 | 547.9145 | 1271.9917 | 56.878 | 6.8275 | 59.7951 | 1217445.1238 | 0 | 1103578.4358 | 0 | 0 | 0 | 625612.4804 | 1149188.0556 | 2989951.5898 | 2040703.3974 | 9126479.0828 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 24396194.03 | 56636128.2814 | 10000 | 0.90771 | 26876.5347 | 62394.2762 | 547.9145 | 1271.9917
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.5413 | 4.2182 | 0.28632 | 4 | 22460.4193 | 50610.8471 | 457.886 | 1031.7706 | 56.8382 | 6.7882 | 50.2785 | 1396384.1224 | 0 | 1295389.7854 | 0 | 0 | 0 | 683346.6949 | 1316297.0351 | 3424734.8756 | 2337451.9238 | 10453604.4372 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 25723319.3844 | 57963253.6358 | 13335.2143 | 1.1453 | 22460.4193 | 50610.8471 | 457.886 | 1031.7706
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4035 | 5.0502 | 0.35196 | 4 | 19178.6767 | 42079.1478 | 390.9833 | 857.8403 | 56.7239 | 6.7329 | 44.1709 | 1571168.2416 | 0 | 1489645.2681 | 0 | 0 | 0 | 726597.1746 | 1477090.1669 | 3843085.6214 | 2622984.9041 | 11730571.3768 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 27000286.3239 | 59240220.5754 | 17782.7941 | 1.4078 | 19178.6767 | 42079.1478 | 390.9833 | 857.8403
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.0781 | 5.8704 | 0.42007 | 4 | 16747.4544 | 35934.9122 | 341.4195 | 732.5818 | 56.5509 | 6.6657 | 61.5602 | 1730923.1258 | 0 | 1674191.2038 | 0 | 0 | 0 | 750301.6583 | 1620612.2353 | 4216500.603 | 2877848.302 | 12870377.1283 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 28140092.0755 | 60380026.3269 | 23713.7371 | 1.6803 | 16747.4544 | 35934.9122 | 341.4195 | 732.5818
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0977 | 6.6338 | 0.48656 | 4 | 14951.3539 | 31516.5194 | 304.8036 | 642.5069 | 56.3414 | 6.5925 | 67.0318 | 1869400.2998 | 0 | 1840651.2846 | 0 | 0 | 0 | 754981.6452 | 1741362.9595 | 4530669.2181 | 3092274.8373 | 13829340.2445 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 29099055.1917 | 61338989.4432 | 31622.7766 | 1.9462 | 14951.3539 | 31516.5194 | 304.8036 | 642.5069
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1204 | 7.3065 | 0.54788 | 4 | 13626.0091 | 28337.317 | 277.7846 | 577.6945 | 56.1201 | 6.5196 | 68.6218 | 1983719.7846 | 0 | 1983560.1332 | 0 | 0 | 0 | 743919.4915 | 1837367.7696 | 4780454.0406 | 3262758.1112 | 14591779.3307 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 29861494.2779 | 62101428.5293 | 42169.6503 | 2.1915 | 13626.0091 | 28337.317 | 277.7846 | 577.6945
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.0519 | 7.8776 | 0.60187 | 4 | 12647.4445 | 26039.0705 | 257.8353 | 530.8417 | 55.9064 | 6.4518 | 73.8914 | 2075355.4126 | 0 | 2102402.7508 | 0 | 0 | 0 | 722914.059 | 1911262.1667 | 4972712.104 | 3393978.19 | 15178624.6831 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 30448339.6303 | 62688273.8817 | 56234.1325 | 2.4075 | 12647.4445 | 26039.0705 | 257.8353 | 530.8417
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.8781 | 8.3445 | 0.64753 | 4 | 11923.6055 | 24370.8629 | 243.0788 | 496.833 | 55.7144 | 6.3925 | 67.9808 | 2146632.2928 | 0 | 2197946.255 | 0 | 0 | 0 | 696628.3323 | 1966070.6832 | 5115312.6212 | 3491305.9731 | 15613896.1576 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 30883611.1047 | 63123545.3562 | 74989.4209 | 2.5901 | 11923.6055 | 24370.8629 | 243.0788 | 496.833
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7218 | 8.7179 | 0.68503 | 4 | 11386.921 | 23152.7325 | 232.1378 | 471.9998 | 55.55 | 6.3425 | 79.363 | 2201303.3453 | 0 | 2273347.6588 | 0 | 0 | 0 | 669263.5081 | 2006126.6597 | 5219530.0554 | 3562436.5135 | 15932007.7407 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31201722.6879 | 63441656.9393 | 100000 | 2.7401 | 11386.921 | 23152.7325 | 232.1378 | 471.9998
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7381 | 9.0117 | 0.71516 | 4 | 10988.0541 | 22258.2427 | 224.0063 | 453.7644 | 55.4138 | 6.3017 | 72.986 | 2242906.0059 | 0 | 2332109.6911 | 0 | 0 | 0 | 643521.9147 | 2035229.6686 | 5295250.1146 | 3614117.0097 | 16163134.4046 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31432849.3518 | 63672783.6032 | 133352.1432 | 2.8606 | 10988.0541 | 22258.2427 | 224.0063 | 453.7644
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.0887 | 9.2412 | 0.73898 | 4 | 10690.9858 | 21597.8298 | 217.9502 | 440.301 | 55.3033 | 6.2689 | 61.6655 | 2274535.7174 | 0 | 2377665.4824 | 0 | 0 | 0 | 620907.8935 | 2056512.5464 | 5350623.7969 | 3651910.6857 | 16332156.1223 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31601871.0695 | 63841805.3209 | 177827.941 | 2.9559 | 10690.9858 | 21597.8298 | 217.9502 | 440.301
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.8861 | 9.417 | 0.75752 | 4 | 10469.355 | 21109.2583 | 213.432 | 430.3408 | 55.2162 | 6.2432 | 68.8314 | 2298252.8482 | 0 | 2412363.6893 | 0 | 0 | 0 | 601651.5423 | 2071784.5511 | 5390358.4205 | 3679030.3828 | 16453441.434 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31723156.3812 | 63963090.6326 | 237137.3706 | 3.0301 | 10469.355 | 21109.2583 | 213.432 | 430.3408
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.248 | 9.5506 | 0.7718 | 4 | 10303.7822 | 20746.8707 | 210.0565 | 422.953 | 55.1487 | 6.2234 | 77.6181 | 2315951.9515 | 0 | 2438576.9982 | 0 | 0 | 0 | 585735.3569 | 2082703.0796 | 5418766.1919 | 3698419.2705 | 16540152.8485 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31809867.7957 | 64049802.0472 | 316227.766 | 3.0872 | 10303.7822 | 20746.8707 | 210.0565 | 422.953
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.3003 | 9.6537 | 0.7828 | 4 | 10179.9634 | 20476.3634 | 207.5323 | 417.4384 | 55.0957 | 6.2079 | 78.8716 | 2329466.7954 | 0 | 2458785.5532 | 0 | 0 | 0 | 573153.7749 | 2090948.3881 | 5440218.7935 | 3713061.1119 | 16605634.4169 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31875349.3641 | 64115283.6155 | 421696.5034 | 3.1312 | 10179.9634 | 20476.3634 | 207.5323 | 417.4384
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0728 | 9.7297 | 0.7911 | 4 | 10087.2998 | 20275.6588 | 205.6433 | 413.3467 | 55.0563 | 6.1964 | 66.6368 | 2339299.9155 | 0 | 2473597.8277 | 0 | 0 | 0 | 562970.9703 | 2096588.7983 | 5454893.9836 | 3723077.2307 | 16650428.726 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31920143.6732 | 64160077.9247 | 562341.3252 | 3.1644 | 10087.2998 | 20275.6588 | 205.6433 | 413.3467
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.677 | 9.789 | 0.79746 | 4 | 10017.9144 | 20124.9214 | 204.2287 | 410.2737 | 55.0252 | 6.1873 | 78.2168 | 2346937.786 | 0 | 2485167.871 | 0 | 0 | 0 | 555256.4292 | 2101071.2136 | 5466556.3088 | 3731037.0073 | 16686026.6159 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31955741.5631 | 64195675.8145 | 749894.2093 | 3.1899 | 10017.9144 | 20124.9214 | 204.2287 | 410.2737
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.123 | 9.8329 | 0.80225 | 4 | 9965.939 | 20012.6306 | 203.1691 | 407.9845 | 55.002 | 6.1806 | 69.4745 | 2352546.6461 | 0 | 2493701.3498 | 0 | 0 | 0 | 549204.0238 | 2104226.2877 | 5474765.1645 | 3736639.7199 | 16711083.1919 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31980798.1391 | 64220732.3905 | 1000000 | 3.209 | 9965.939 | 20012.6306 | 203.1691 | 407.9845
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.454 | 9.8655 | 0.80585 | 4 | 9926.9939 | 19928.8188 | 202.3752 | 406.2759 | 54.9848 | 6.1756 | 69.5201 | 2356692.2524 | 0 | 2500029.0736 | 0 | 0 | 0 | 544518.1252 | 2106483.3859 | 5480637.6711 | 3740647.8263 | 16729008.3345 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 31998723.2817 | 64238657.5331 | 1333521.4322 | 3.2234 | 9926.9939 | 19928.8188 | 202.3752 | 406.2759
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.7124 | 9.8909 | 0.80859 | 4 | 9897.8062 | 19865.6987 | 201.7802 | 404.9891 | 54.9713 | 6.1717 | 63.9854 | 2359919.2006 | 0 | 2504966.5934 | 0 | 0 | 0 | 541043.474 | 2108312.4145 | 5485396.4282 | 3743895.7759 | 16743533.8866 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32013248.8338 | 64253183.0852 | 1778279.41 | 3.2344 | 9897.8062 | 19865.6987 | 201.7802 | 404.9891
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.9 | 9.9093 | 0.81064 | 4 | 9875.928 | 19818.6913 | 201.3342 | 404.0308 | 54.9614 | 6.1688 | 71.8224 | 2362257.3074 | 0 | 2508550.9092 | 0 | 0 | 0 | 538339.5859 | 2109567.643 | 5488662.2752 | 3746124.7835 | 16753502.5042 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32023217.4514 | 64263151.7028 | 2371373.7057 | 3.2426 | 9875.928 | 19818.6913 | 201.3342 | 404.0308
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0413 | 9.9233 | 0.81218 | 4 | 9859.527 | 19783.4619 | 200.9998 | 403.3126 | 54.954 | 6.1667 | 64.7914 | 2364014.9096 | 0 | 2511249.0428 | 0 | 0 | 0 | 536297.151 | 2110508.8303 | 5491111.0516 | 3747796.1238 | 16760977.1091 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32030692.0563 | 64270626.3077 | 3162277.6602 | 3.2487 | 9859.527 | 19783.4619 | 200.9998 | 403.3126
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.1534 | 9.9343 | 0.81335 | 4 | 9847.2309 | 19756.8253 | 200.7491 | 402.7696 | 54.9481 | 6.165 | 64.6858 | 2365407.1637 | 0 | 2513388.5159 | 0 | 0 | 0 | 534815.0552 | 2111308.1866 | 5493190.8126 | 3749215.6034 | 16767325.3373 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32037040.2845 | 64276974.5359 | 4216965.0343 | 3.2534 | 9847.2309 | 19756.8253 | 200.7491 | 402.7696
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.2387 | 9.9426 | 0.81424 | 4 | 9838.0117 | 19736.8119 | 200.5612 | 402.3616 | 54.9436 | 6.1636 | 75.8311 | 2366466.8868 | 0 | 2515018.3307 | 0 | 0 | 0 | 533710.3832 | 2111926.2843 | 5494798.976 | 3750313.2079 | 16772234.0689 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32041949.0161 | 64281883.2675 | 5623413.2519 | 3.257 | 9838.0117 | 19736.8119 | 200.5612 | 402.3616
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.2971 | 9.9484 | 0.81489 | 4 | 9831.0992 | 19722.0379 | 200.4203 | 402.0604 | 54.9405 | 6.1628 | 71.6072 | 2367190.42 | 0 | 2516131.86 | 0 | 0 | 0 | 532821.3163 | 2112296.0026 | 5495760.9072 | 3750969.7457 | 16775170.2517 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32044885.1989 | 64284819.4503 | 7498942.0933 | 3.2595 | 9831.0992 | 19722.0379 | 200.4203 | 402.0604
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.336 | 9.9523 | 0.81536 | 4 | 9825.9161 | 19711.1559 | 200.3146 | 401.8386 | 54.9384 | 6.1622 | 74.5122 | 2367672.4266 | 0 | 2516874.0616 | 0 | 0 | 0 | 532103.9518 | 2112493.6716 | 5496275.2016 | 3751320.7622 | 16776740.0756 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 32046455.0228 | 64286389.2742 | 10000000 | 3.2614 | 9825.9161 | 19711.1559 | 200.3146 | 401.8386
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.9561 | [19 empty] | 100 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.026779 | 6.433e-05 | 4 | 61921530.8072 | 190929831.3762 | 1262354.1606 | 3892362.8643 | 30.8817 | 4.3609 | 28.7439 | 26505.8686 | 0 | 2733.372 | 0 | 0 | 0 | 28651.36 | 22577.3343 | 58741.5925 | 40092.3439 | 179301.8715 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 15933537.5027 | 49129722.5531 | 133.3521 | 0.00025732 | 61921530.8072 | 190929831.3762 | 1262354.1606 | 3892362.8643
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | -0.023521 | 0.00049751 | 4 | 8085732.1877 | 24767045.1439 | 164838.5874 | 504909.7152 | 37.8533 | 5.1463 | 34.8056 | 46932.963 | 0 | 16746.5498 | 0 | 0 | 0 | 44981.8726 | 42377.9403 | 110258.7077 | 75253.8336 | 336551.8669 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 16090787.4981 | 49286972.5485 | 177.8279 | 0.00199 | 8085732.1877 | 24767045.1439 | 164838.5874 | 504909.7152
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.013685 | 0.00091485 | 4 | 4521910.2572 | 13593371.3392 | 92185.2569 | 277119.2611 | 46.6756 | 6.1041 | 21.8502 | 101751.2238 | 0 | 56464.8182 | 0 | 0 | 0 | 97908.5533 | 99888.5922 | 259889.6269 | 177380.0106 | 793282.825 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 16547518.4563 | 49743703.5066 | 237.1374 | 0.0036594 | 4521910.2572 | 13593371.3392 | 92185.2569 | 277119.2611
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.022873 | 0.0031317 | 4 | 1317180.2016 | 3967180.6373 | 26852.5 | 80876.3433 | 46.6758 | 6.1042 | 21.064 | 101752.0974 | 0 | 56464.351 | 0 | 0 | 0 | 82608.7275 | 93921.8186 | 244365.306 | 166784.3425 | 745896.643 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 16500132.2743 | 49696317.3246 | 316.2278 | 0.012527 | 1317180.2016 | 3967180.6373 | 26852.5 | 80876.3433
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.02984 | 0.0047791 | 4 | 861166.6654 | 2597703.3663 | 17556.0473 | 52957.6968 | 46.6758 | 6.1043 | 21.6276 | 101752.5902 | 0 | 56464.0874 | 0 | 0 | 0 | 70404.8458 | 89162.3942 | 231982.2599 | 158332.6591 | 708098.8366 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 16462334.4678 | 49658519.5182 | 421.6965 | 0.019116 | 861166.6654 | 2597703.3663 | 17556.0473 | 52957.6968
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0714 | 0.13806 | 0.0093533 | 4 | 457097.1134 | 1344378.2527 | 9318.5429 | 27406.9691 | 51.9123 | 6.6409 | 34.3729 | 182464.8577 | 0 | 118317.7443 | 0 | 0 | 0 | 134219.4454 | 169650.7985 | 441396.5776 | 301262.234 | 1347311.6576 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 17101547.2888 | 50297732.3392 | 562.3413 | 0.037413 | 457097.1134 | 1344378.2527 | 9318.5429 | 27406.9691
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0971 | 0.22705 | 0.014466 | 4 | 301894.7415 | 875575.7667 | 6154.5326 | 17849.7963 | 53.5936 | 6.8053 | 41.0391 | 232175.2687 | 0 | 157951.5728 | 0 | 0 | 0 | 163580.9108 | 215946.0234 | 561847.2562 | 383472.2972 | 1714973.329 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 17469208.9603 | 50665394.0106 | 749.8942 | 0.057865 | 301894.7415 | 875575.7667 | 6154.5326 | 17849.7963
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4265 | 0.34594 | 0.021457 | 4 | 208652.3127 | 595429.3831 | 4253.6596 | 12138.6334 | 54.9128 | 6.9309 | 55.7239 | 291330.9215 | 0 | 206389.2848 | 0 | 0 | 0 | 197706.1428 | 271216.2762 | 705649.1165 | 481620.0217 | 2153911.7635 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 17908147.3948 | 51104332.4451 | 1000 | 0.085828 | 208652.3127 | 595429.3831 | 4253.6596 | 12138.6334
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1346 | 0.50164 | 0.030884 | 4 | 149165.9905 | 417883.7884 | 3040.9505 | 8519.1263 | 55.9365 | 7.0258 | 45.4377 | 361154.0811 | 0 | 265099.3346 | 0 | 0 | 0 | 236788.0263 | 336586.1624 | 875728.1512 | 597702.4576 | 2673058.2133 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 18427293.8445 | 51623478.8949 | 1333.5214 | 0.12354 | 149165.9905 | 417883.7884 | 3040.9505 | 8519.1263
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3512 | 0.70587 | 0.043492 | 4 | 109502.4397 | 300319.3092 | 2232.3553 | 6122.4153 | 56.7356 | 7.0976 | 43.4751 | 444478.1246 | 0 | 337036.852 | 0 | 0 | 0 | 282580.7342 | 414997.3272 | 1079737.9177 | 736943.3152 | 3295774.2709 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 19050009.9021 | 52246194.9525 | 1778.2794 | 0.17397 | 109502.4397 | 300319.3092 | 2232.3553 | 6122.4153
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1823 | 0.96879 | 0.060197 | 4 | 82162.8614 | 220027.6942 | 1675.0011 | 4485.5622 | 57.3459 | 7.1499 | 42.5197 | 542465.0605 | 0 | 423887.6716 | 0 | 0 | 0 | 334667.0142 | 507397.7011 | 1320144.7366 | 901025.909 | 4029588.0931 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 19783823.7243 | 52980008.7747 | 2371.3737 | 0.24079 | 82162.8614 | 220027.6942 | 1675.0011 | 4485.5622
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8091 | 1.3072 | 0.082175 | 4 | 62835.8005 | 163828.1881 | 1280.9928 | 3339.8592 | 57.8087 | 7.1864 | 51.1195 | 658216.1963 | 0 | 529220.7067 | 0 | 0 | 0 | 394572.407 | 616983.6309 | 1605264.8468 | 1095626.2429 | 4899884.0306 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 20654119.6618 | 53850304.7122 | 3162.2777 | 0.3287 | 62835.8005 | 163828.1881 | 1280.9928 | 3339.8592
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.3575 | 1.7337 | 0.11073 | 4 | 48908.0921 | 123856.0751 | 997.0576 | 2524.9736 | 58.1449 | 7.208 | 53.8566 | 792264.7016 | 0 | 654498.0867 | 0 | 0 | 0 | 460824.9306 | 743959.2104 | 1935629.2583 | 1321106.742 | 5908282.9296 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 21662518.5608 | 54858703.6112 | 4216.965 | 0.44292 | 48908.0921 | 123856.0751 | 997.0576 | 2524.9736
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9749 | 2.2625 | 0.14727 | 4 | 38727.1083 | 95078.1404 | 789.5045 | 1938.2965 | 58.3736 | 7.2149 | 49.5019 | 945395.938 | 0 | 801576.3344 | 0 | 0 | 0 | 532389.3551 | 888951.0347 | 2312868.2434 | 1578580.1008 | 7059761.0064 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 22813996.6377 | 56010181.688 | 5623.4133 | 0.5891 | 38727.1083 | 95078.1404 | 789.5045 | 1938.2965
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.7398 | 2.9021 | 0.19301 | 4 | 31210.901 | 74209.9158 | 636.2764 | 1512.8695 | 58.5055 | 7.2063 | 47.6689 | 1116227.083 | 0 | 970434.1726 | 0 | 0 | 0 | 606455.7421 | 1050315.6291 | 2732705.8175 | 1865127.8719 | 8341266.3161 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 24095501.9474 | 57291686.9977 | 7498.9421 | 0.77202 | 31210.901 | 74209.9158 | 636.2764 | 1512.8695
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5692 | 3.6464 | 0.24837 | 4 | 25629.9039 | 59043.4911 | 522.5003 | 1203.6814 | 58.5462 | 7.1807 | 41.8254 | 1299680.378 | 0 | 1157435.6238 | 0 | 0 | 0 | 677567.5704 | 1222526.5932 | 3180763.4208 | 2170936.3928 | 9708909.979 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 25463145.6103 | 58659330.6606 | 10000 | 0.99349 | 25629.9039 | 59043.4911 | 522.5003 | 1203.6814
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.2197 | 4.4736 | 0.31257 | 4 | 21478.4225 | 48029.4381 | 437.8667 | 979.1451 | 58.5008 | 7.1372 | 48.1272 | 1488091.8284 | 0 | 1356028.7816 | 0 | 0 | 0 | 739632.2239 | 1397663.6052 | 3636434.0005 | 2481940.9266 | 11099791.3662 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 26854026.9974 | 60050212.0478 | 13335.2143 | 1.2503 | 21478.4225 | 48029.4381 | 437.8667 | 979.1451
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.1861 | 5.337 | 0.38291 | 4 | 18394.9812 | 40068.4128 | 375.0066 | 816.8488 | 58.3786 | 7.0774 | 60.6747 | 1670020.7409 | 0 | 1554892.5802 | 0 | 0 | 0 | 785252.2513 | 1563964.5732 | 4069115.0063 | 2777254.6038 | 12420499.7558 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 28174735.387 | 61370920.4374 | 17782.7941 | 1.5317 | 18394.9812 | 40068.4128 | 375.0066 | 816.8488
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.9144 | 6.1834 | 0.45538 | 4 | 16111.9264 | 34336.2333 | 328.4634 | 699.9906 | 58.1967 | 7.0056 | 71.2515 | 1835499.8997 | 0 | 1742909.033 | 0 | 0 | 0 | 810698.149 | 1711751.7618 | 4453626.9558 | 3039691.9102 | 13594177.7095 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 29348413.3407 | 62544598.3911 | 23713.7371 | 1.8215 | 16111.9264 | 34336.2333 | 328.4634 | 699.9906
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.907 | 6.964 | 0.52555 | 4 | 14425.9487 | 30217.0082 | 294.0925 | 616.0146 | 57.9797 | 6.9285 | 72.4399 | 1977697.606 | 0 | 1911000.7072 | 0 | 0 | 0 | 816177.8234 | 1834901.6932 | 4774037.8157 | 3258378.9059 | 14572194.5514 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 30326430.1827 | 63522615.233 | 31622.7766 | 2.1022 | 14425.9487 | 30217.0082 | 294.0925 | 616.0146
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.9038 | 7.6514 | 0.58995 | 4 | 13182.0995 | 27249.5629 | 268.7349 | 555.5192 | 57.7516 | 6.8521 | 76.5853 | 2095167.3586 | 0 | 2055351.5359 | 0 | 0 | 0 | 806350.3607 | 1933179.0095 | 5029735.2332 | 3432897.6474 | 15352681.1453 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 31106916.7765 | 64303101.8269 | 42169.6503 | 2.3598 | 13182.0995 | 27249.5629 | 268.7349 | 555.5192
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.7575 | 8.2298 | 0.64625 | 4 | 12263.7512 | 25105.5571 | 250.0132 | 511.8107 | 57.534 | 6.7819 | 73.9347 | 2188536.5353 | 0 | 2174317.3094 | 0 | 0 | 0 | 786118.3449 | 2008099.1539 | 5224662.0807 | 3565939.2262 | 15947672.6503 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 31701908.2816 | 64898093.3319 | 56234.1325 | 2.585 | 12263.7512 | 25105.5571 | 250.0132 | 511.8107
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.5124 | 8.7018 | 0.6937 | 4 | 11584.4504 | 23547.9717 | 236.1647 | 480.0573 | 57.3394 | 6.7207 | 68.8729 | 2261125.2409 | 0 | 2269840.3667 | 0 | 0 | 0 | 760854.7919 | 2063809.9558 | 5369610.1594 | 3664869.2682 | 16390109.7829 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 32144345.4141 | 65340530.4645 | 74989.4209 | 2.7748 | 11584.4504 | 23547.9717 | 236.1647 | 480.0573
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.3102 | 9.0802 | 0.7326 | 4 | 11080.792 | 22409.0067 | 225.8969 | 456.8379 | 57.1725 | 6.6691 | 68.0567 | 2317021.412 | 0 | 2345470.5847 | 0 | 0 | 0 | 734838.8471 | 2104959.0291 | 5476671.6073 | 3737940.9063 | 16716902.3866 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 32471138.0178 | 65667323.0682 | 100000 | 2.9304 | 11080.792 | 22409.0067 | 225.8969 | 456.8379
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2682 | 9.3759 | 0.76372 | 4 | 10706.4875 | 21573.1572 | 218.2662 | 439.798 | 57.0354 | 6.6274 | 66.5773 | 2359274.7517 | 0 | 2403983.2019 | 0 | 0 | 0 | 710176.5595 | 2134639.4601 | 5553894.0005 | 3790646.7764 | 16952614.7502 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 32706850.3814 | 65903035.4318 | 133352.1432 | 3.0549 | 10706.4875 | 21573.1572 | 218.2662 | 439.798
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.565 | 9.606 | 0.78826 | 4 | 10427.7407 | 20956.0659 | 212.5836 | 427.2177 | 56.9248 | 6.5939 | 81.4083 | 2391310.4749 | 0 | 2449190.9083 | 0 | 0 | 0 | 688526.8469 | 2156321.0097 | 5610304.945 | 3829148.4052 | 17124802.59 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 32879038.2212 | 66075223.2716 | 177827.941 | 3.153 | 10427.7407 | 20956.0659 | 212.5836 | 427.2177
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.3406 | 9.7841 | 0.8074 | 4 | 10219.8059 | 20498.5088 | 208.3446 | 417.8898 | 56.8367 | 6.5675 | 77.344 | 2415614.3748 | 0 | 2484010.4422 | 0 | 0 | 0 | 670385.6116 | 2172304.0671 | 5651889.5819 | 3857530.7743 | 17251734.8519 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33005970.4831 | 66202155.5335 | 237137.3706 | 3.2296 | 10219.8059 | 20498.5088 | 208.3446 | 417.8898
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.6707 | 9.9179 | 0.82208 | 4 | 10064.4839 | 20159.6833 | 205.1781 | 410.9824 | 56.7692 | 6.5474 | 71.7228 | 2433552.8066 | 0 | 2510017.9086 | 0 | 0 | 0 | 655243.4166 | 2183537.5114 | 5681116.6996 | 3877478.8827 | 17340947.2256 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33095182.8568 | 66291367.9072 | 316227.766 | 3.2883 | 10064.4839 | 20159.6833 | 205.1781 | 410.9824
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.6964 | 10.0211 | 0.83337 | 4 | 9948.3484 | 19906.7891 | 202.8105 | 405.8268 | 56.7164 | 6.5317 | 82.8989 | 2447231.6236 | 0 | 2530032.4812 | 0 | 0 | 0 | 643298.3524 | 2192019.3583 | 5703184.7253 | 3892540.7638 | 17408307.3046 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33162542.9359 | 66358727.9862 | 421696.5034 | 3.3335 | 9948.3484 | 19906.7891 | 202.8105 | 405.8268
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4734 | 10.0994 | 0.84197 | 4 | 9861.4464 | 19718.164 | 201.0389 | 401.9814 | 56.6758 | 6.5196 | 71.9946 | 2457503.3307 | 0 | 2545169.7003 | 0 | 0 | 0 | 633893.2851 | 2198260.8633 | 5719423.8409 | 3903624.2938 | 17457875.3141 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33212110.9453 | 66408295.9957 | 562341.3252 | 3.3679 | 9861.4464 | 19718.164 | 201.0389 | 401.9814
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0413 | 10.1567 | 0.84843 | 4 | 9796.3826 | 19578.0448 | 199.7125 | 399.1249 | 56.6459 | 6.5108 | 70.4294 | 2464960.8394 | 0 | 2556219.4942 | 0 | 0 | 0 | 626373.5527 | 2202546.0156 | 5730572.9284 | 3911233.7751 | 17491906.6053 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33246142.2366 | 66442327.2869 | 749894.2093 | 3.3937 | 9796.3826 | 19578.0448 | 199.7125 | 399.1249
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4823 | 10.2012 | 0.85336 | 4 | 9747.6492 | 19472.7856 | 198.719 | 396.9791 | 56.6225 | 6.5039 | 71.3418 | 2470723.7496 | 0 | 2564793.2142 | 0 | 0 | 0 | 620718.4117 | 2205931.7965 | 5739382.0356 | 3917246.1718 | 17518795.3793 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33273031.0106 | 66469216.0609 | 1000000 | 3.4134 | 9747.6492 | 19472.7856 | 198.719 | 396.9791
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.8159 | 10.2348 | 0.85709 | 4 | 9711.1362 | 19393.976 | 197.9746 | 395.3724 | 56.6048 | 6.4986 | 81.5137 | 2475066.1677 | 0 | 2571274.0546 | 0 | 0 | 0 | 616405.4034 | 2208470.794 | 5745987.9864 | 3921754.8689 | 17538959.275 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33293194.9062 | 66489379.9566 | 1333521.4322 | 3.4284 | 9711.1362 | 19393.976 | 197.9746 | 395.3724
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0741 | 10.2608 | 0.85992 | 4 | 9683.7731 | 19334.6992 | 197.4168 | 394.164 | 56.5909 | 6.4946 | 63.3748 | 2478417.7846 | 0 | 2576288.2316 | 0 | 0 | 0 | 613197.0106 | 2210482.1805 | 5751221.2014 | 3925326.6457 | 17554933.0544 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33309168.6856 | 66505353.736 | 1778279.41 | 3.4397 | 9683.7731 | 19334.6992 | 197.4168 | 394.164
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.2593 | 10.2795 | 0.86203 | 4 | 9663.2636 | 19290.6465 | 196.9987 | 393.2659 | 56.581 | 6.4916 | 64.466 | 2480816.5046 | 0 | 2579883.5284 | 0 | 0 | 0 | 610669.4358 | 2211834.0928 | 5754738.6 | 3927727.3425 | 17565669.5041 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33319905.1354 | 66516090.1857 | 2371373.7057 | 3.4481 | 9663.2636 | 19290.6465 | 196.9987 | 393.2659
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3908 | 10.2929 | 0.86358 | 4 | 9647.8891 | 19257.935 | 196.6853 | 392.5991 | 56.5739 | 6.4895 | 64.9088 | 2482516.7304 | 0 | 2582435.3573 | 0 | 0 | 0 | 608678.1635 | 2212715.798 | 5757032.616 | 3929293.0556 | 17572671.7208 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33326907.352 | 66523092.4024 | 3162277.6602 | 3.4543 | 9647.8891 | 19257.935 | 196.6853 | 392.5991
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5003 | 10.3039 | 0.86479 | 4 | 9636.363 | 19233.0135 | 196.4503 | 392.091 | 56.568 | 6.4878 | 78.6579 | 2483930.4259 | 0 | 2584559.0798 | 0 | 0 | 0 | 607287.3809 | 2213552.9858 | 5759210.8068 | 3930779.7156 | 17579320.3947 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33333556.0259 | 66529741.0763 | 4216965.0343 | 3.4591 | 9636.363 | 19233.0135 | 196.4503 | 392.091
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5734 | 10.3113 | 0.86566 | 4 | 9627.7213 | 19214.678 | 196.2741 | 391.7172 | 56.5641 | 6.4866 | 71.7775 | 2484874.2985 | 0 | 2585978.225 | 0 | 0 | 0 | 606145.5658 | 2214029.2548 | 5760449.9612 | 3931625.4639 | 17583102.7692 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33337338.4004 | 66533523.4508 | 5623413.2519 | 3.4626 | 9627.7213 | 19214.678 | 196.2741 | 391.7172
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.642 | 10.3182 | 0.86636 | 4 | 9621.242 | 19200.4157 | 196.142 | 391.4264 | 56.5604 | 6.4856 | 68.2588 | 2485758.1375 | 0 | 2587307.6552 | 0 | 0 | 0 | 605428.0281 | 2214612.5901 | 5761967.68 | 3932661.3382 | 17587735.4291 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33341971.0604 | 66538156.1107 | 7498942.0933 | 3.4655 | 9621.242 | 19200.4157 | 196.142 | 391.4264
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6855 | 10.3226 | 0.86686 | 4 | 9616.3838 | 19190.0238 | 196.043 | 391.2146 | 56.558 | 6.4849 | 71.796 | 2486319.0247 | 0 | 2588151.8191 | 0 | 0 | 0 | 604806.2555 | 2214918.0687 | 5762762.4726 | 3933203.8005 | 17590161.4411 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 33344397.0723 | 66540582.1227 | 10000000 | 3.4675 | 9616.3838 | 19190.0238 | 196.043 | 391.2146
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7225 | [19 empty] | 100 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.027728 | 5.1943e-05 | 4 | 79069608.356 | 243509135.9286 | 1611940.9159 | 4964263.1064 | 30.9355 | 4.5743 | 28.1946 | 27291.0109 | 0 | 2297.6939 | 0 | 0 | 0 | 29808.3411 | 23164.8479 | 60270.1825 | 41135.638 | 183967.7144 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 16428584.1205 | 50594791.1833 | 133.3521 | 0.00020777 | 79069608.356 | 243509135.9286 | 1611940.9159 | 4964263.1064
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.77197 | -0.024297 | 0.0005217 | 4 | 7959784.9861 | 24332302.9991 | 162270.9833 | 496046.9085 | 38.7843 | 5.4599 | 36.5925 | 50812.9182 | 0 | 18180.1292 | 0 | 0 | 0 | 49137.62 | 46070.9603 | 119867.1883 | 81811.819 | 365880.6351 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 16610497.0412 | 50776704.1041 | 177.8279 | 0.0020868 | 7959784.9861 | 24332302.9991 | 162270.9833 | 496046.9085
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.01215 | 0.0011732 | 4 | 3633749.7188 | 10914012.7372 | 74078.903 | 222496.9119 | 47.3966 | 6.3898 | 21.8004 | 104677.9124 | 0 | 56538.1455 | 0 | 0 | 0 | 99833.7451 | 101809.4232 | 264887.2351 | 180790.9808 | 808537.442 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 17053153.8482 | 51219360.911 | 237.1374 | 0.004693 | 3633749.7188 | 10914012.7372 | 74078.903 | 222496.9119
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.021338 | 0.0033812 | 4 | 1257406.5514 | 3783561.2942 | 25633.9333 | 77133.0146 | 47.3968 | 6.3899 | 21.1953 | 104678.8262 | 0 | 56537.6615 | 0 | 0 | 0 | 84739.9187 | 95922.9985 | 249571.9656 | 170337.9947 | 761789.3652 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 17006405.7713 | 51172612.8342 | 316.2278 | 0.013525 | 1257406.5514 | 3783561.2942 | 25633.9333 | 77133.0146
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.028303 | 0.005022 | 4 | 844741.5757 | 2545563.0466 | 17221.1996 | 51894.7458 | 47.3968 | 6.39 | 20.4036 | 104679.3484 | 0 | 56537.385 | 0 | 0 | 0 | 72733.9811 | 91240.7787 | 237389.79 | 162023.4096 | 724604.6928 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 16969221.099 | 51135428.1618 | 421.6965 | 0.020088 | 844741.5757 | 2545563.0466 | 17221.1996 | 51894.7458
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.14891 | 0.010262 | 4 | 430958.1314 | 1263322.4081 | 8785.6644 | 25754.5361 | 53.3135 | 6.9896 | 37.7261 | 195816.999 | 0 | 125193.6761 | 0 | 0 | 0 | 145531.6789 | 181951.5181 | 473400.5266 | 323105.5868 | 1444999.9856 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 17689616.3918 | 51855823.4546 | 562.3413 | 0.041047 | 430958.1314 | 1263322.4081 | 8785.6644 | 25754.5361
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2823 | 0.24374 | 0.015882 | 4 | 284599.7507 | 822410.2102 | 5801.9509 | 16765.9445 | 55.0586 | 7.1575 | 37.4218 | 248802.4811 | 0 | 166774.256 | 0 | 0 | 0 | 177056.0479 | 231126.7862 | 601344.487 | 410429.9688 | 1835534.0271 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 18080150.4332 | 52246357.496 | 749.8942 | 0.063528 | 284599.7507 | 822410.2102 | 5801.9509 | 16765.9445
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6628 | 0.37017 | 0.023562 | 4 | 196772.2276 | 559283.6818 | 4011.468 | 11401.7543 | 56.4298 | 7.2858 | 54.5258 | 311771.0425 | 0 | 217510.2855 | 0 | 0 | 0 | 213601.3343 | 289724.2383 | 753803.0375 | 514486.0622 | 2300896.0004 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 18545512.4065 | 52711719.4693 | 1000 | 0.094249 | 196772.2276 | 559283.6818 | 4011.468 | 11401.7543
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4681 | 0.53837 | 0.033934 | 4 | 140770.9497 | 392479.1768 | 2869.8062 | 8001.2189 | 57.5119 | 7.3842 | 44.5268 | 387405.3458 | 0 | 280090.3075 | 0 | 0 | 0 | 256955.2482 | 360535.8516 | 938040.3297 | 640231.7998 | 2863258.8826 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 19107875.2887 | 53274082.3515 | 1333.5214 | 0.13574 | 140770.9497 | 392479.1768 | 2869.8062 | 8001.2189
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7728 | 0.75582 | 0.047779 | 4 | 103438.1359 | 282209.9003 | 2108.7263 | 5753.2305 | 58.3418 | 7.4571 | 43.1843 | 476185.8296 | 0 | 355513.004 | 0 | 0 | 0 | 306116.4746 | 443747.9702 | 1154541.1932 | 787998.0878 | 3524102.5595 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 19768718.9656 | 53934926.0284 | 1778.2794 | 0.19112 | 103438.1359 | 282209.9003 | 2108.7263 | 5753.2305
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7398 | 1.0378 | 0.066133 | 4 | 77704.7012 | 206861.9652 | 1584.1154 | 4217.161 | 58.9811 | 7.5106 | 43.6111 | 581446.5044 | 0 | 447312.581 | 0 | 0 | 0 | 363038.5321 | 542801.0708 | 1412257.0424 | 963894.4504 | 4310750.1811 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 20555366.5873 | 54721573.6501 | 2371.3737 | 0.26453 | 77704.7012 | 206861.9652 | 1584.1154 | 4217.161
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5083 | 1.3979 | 0.090231 | 4 | 59510.4176 | 154174.0588 | 1213.2004 | 3143.0467 | 59.4618 | 7.5472 | 45.8398 | 704749.0993 | 0 | 557711.973 | 0 | 0 | 0 | 427427.297 | 659056.464 | 1714729.7283 | 1170338.2738 | 5234012.8354 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 21478629.2415 | 55644836.3044 | 3162.2777 | 0.36092 | 59510.4176 | 154174.0588 | 1213.2004 | 3143.0467
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.2271 | 1.8509 | 0.12149 | 4 | 46396.286 | 116702.0011 | 945.851 | 2379.1281 | 59.8106 | 7.5682 | 42.4076 | 847381.7985 | 0 | 688858.5856 | 0 | 0 | 0 | 498599.2208 | 793587.4459 | 2064751.7471 | 1409235.4938 | 6302414.2918 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 22547030.698 | 56713237.7608 | 4216.965 | 0.48597 | 46396.286 | 116702.0011 | 945.851 | 2379.1281
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.0466 | 2.412 | 0.16142 | 4 | 36808.1966 | 89724.654 | 750.3849 | 1829.1584 | 60.0471 | 7.5739 | 47.8241 | 1010137.8459 | 0 | 842660.5793 | 0 | 0 | 0 | 575507.7642 | 947039.4138 | 2464002.2903 | 1681732.1933 | 7521080.0869 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 23765696.493 | 57931903.5558 | 5623.4133 | 0.64566 | 36808.1966 | 89724.654 | 750.3849 | 1829.1584
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0381 | 3.0891 | 0.21123 | 4 | 29729.0644 | 70165.6565 | 606.0672 | 1430.4218 | 60.1818 | 7.563 | 56.4874 | 1191315.4902 | 0 | 1018883.2936 | 0 | 0 | 0 | 655064.9092 | 1117452.8403 | 2907383.0693 | 1984348.6855 | 8874448.2881 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 25119064.6943 | 59285271.7571 | 7498.9421 | 0.84493 | 29729.0644 | 70165.6565 | 606.0672 | 1430.4218
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.0696 | 3.8714 | 0.27123 | 4 | 24473.1268 | 55964.6964 | 498.9178 | 1140.916 | 60.2205 | 7.534 | 62.6564 | 1384493.4383 | 0 | 1212690.1052 | 0 | 0 | 0 | 730622.2582 | 1297844.2627 | 3376724.547 | 2304683.8881 | 10307058.4994 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 26551674.9055 | 60717881.9683 | 10000 | 1.0849 | 24473.1268 | 55964.6964 | 498.9178 | 1140.916
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.8735 | 4.7343 | 0.34035 | 4 | 20564.8104 | 45661.451 | 419.2415 | 930.8704 | 60.1694 | 7.4863 | 48.8634 | 1581424.6441 | 0 | 1417026.6932 | 0 | 0 | 0 | 795885.0512 | 1479791.1915 | 3850113.1334 | 2627781.3254 | 11752022.0387 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 27996638.4449 | 62162845.5077 | 13335.2143 | 1.3614 | 20564.8104 | 45661.451 | 419.2415 | 930.8704
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.9501 | 5.6302 | 0.41558 | 4 | 17663.5274 | 38216.9443 | 360.0949 | 779.1041 | 60.039 | 7.4217 | 63.2196 | 1770663.1344 | 0 | 1620689.3695 | 0 | 0 | 0 | 843912.702 | 1651753.4303 | 4297523.6044 | 2933148.1653 | 13117690.406 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 29362306.8121 | 63528513.8749 | 17782.7941 | 1.6623 | 17663.5274 | 38216.9443 | 360.0949 | 779.1041
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.7197 | 6.5021 | 0.4925 | 4 | 15516.4752 | 32859.8854 | 316.3243 | 669.8932 | 59.8483 | 7.3453 | 61.7671 | 1941604.9307 | 0 | 1811929.1925 | 0 | 0 | 0 | 870743.8185 | 1803468.3973 | 4692254.8275 | 3202560.336 | 14322561.5025 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 30567177.9086 | 64733384.9714 | 23713.7371 | 1.97 | 15516.4752 | 32859.8854 | 316.3243 | 669.8932
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.7124 | 7.3024 | 0.56649 | 4 | 13931.4883 | 29009.6354 | 284.0122 | 591.4007 | 59.623 | 7.2639 | 62.3302 | 2087911.0537 | 0 | 1982201.6091 | 0 | 0 | 0 | 877279.4484 | 1929482.9234 | 5020118.7752 | 3426334.2172 | 15323328.027 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 31567944.4332 | 65734151.496 | 31622.7766 | 2.2659 | 13931.4883 | 29009.6354 | 284.0122 | 591.4007
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.6307 | 7.9996 | 0.63383 | 4 | 12762.3168 | 26238.3299 | 260.1771 | 534.9038 | 59.3899 | 7.1845 | 74.7983 | 2207540.0475 | 0 | 2126871.7029 | 0 | 0 | 0 | 867658.6969 | 2028807.4745 | 5278540.8829 | 3602712.6158 | 16112131.4205 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 32356747.8267 | 66522954.8895 | 42169.6503 | 2.5353 | 12762.3168 | 26238.3299 | 260.1771 | 534.9038
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.4313 | 8.5872 | 0.69254 | 4 | 11899.1085 | 24232.6977 | 242.5794 | 494.0163 | 59.1676 | 7.1116 | 71.0423 | 2302939.3836 | 0 | 2246421.8166 | 0 | 0 | 0 | 848324.8992 | 2105097.5788 | 5477032.0851 | 3738186.9398 | 16718002.7032 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 32962619.1093 | 67128826.1722 | 56234.1325 | 2.7702 | 11899.1085 | 24232.6977 | 242.5794 | 494.0163
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.1176 | 9.0642 | 0.74178 | 4 | 11260.562 | 22775.5176 | 229.5618 | 464.3097 | 58.9704 | 7.0486 | 73.3787 | 2376781.5732 | 0 | 2341934.0316 | 0 | 0 | 0 | 823864.2923 | 2161606.1598 | 5624055.8215 | 3838533.661 | 17166775.5394 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 33411391.9456 | 67577599.0084 | 74989.4209 | 2.9671 | 11260.562 | 22775.5176 | 229.5618 | 464.3097
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8501 | 9.4456 | 0.78202 | 4 | 10787.0978 | 21709.5258 | 219.9096 | 442.578 | 58.8021 | 6.9958 | 75.2694 | 2433539.31 | 0 | 2417365.4435 | 0 | 0 | 0 | 798702.6956 | 2203346.9052 | 5732656.6787 | 3912655.9775 | 17498267.0105 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 33742883.4167 | 67909090.4795 | 100000 | 3.1281 | 10787.0978 | 21709.5258 | 219.9096 | 442.578
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.764 | 9.7442 | 0.81417 | 4 | 10435.2275 | 20926.3475 | 212.7362 | 426.6119 | 58.6637 | 6.9529 | 68.2845 | 2476583.4113 | 0 | 2475877.363 | 0 | 0 | 0 | 775054.3778 | 2233730.9094 | 5811709.6249 | 3966611.2377 | 17739566.9242 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 33984183.3303 | 68150390.3932 | 133352.1432 | 3.2567 | 10435.2275 | 20926.3475 | 212.7362 | 426.6119
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0265 | 9.9766 | 0.83949 | 4 | 10173.1934 | 20347.8469 | 207.3943 | 414.8184 | 58.5521 | 6.9186 | 67.5314 | 2509240.3168 | 0 | 2521091.6366 | 0 | 0 | 0 | 754369.461 | 2256033.5516 | 5869736.5252 | 4006215.7895 | 17916687.2807 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34161303.6869 | 68327510.7497 | 177827.941 | 3.358 | 10173.1934 | 20347.8469 | 207.3943 | 414.8184
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7561 | 10.1546 | 0.85915 | 4 | 9977.7339 | 19919.5423 | 203.4096 | 406.0868 | 58.4643 | 6.8918 | 71.7146 | 2533752.707 | 0 | 2555530.3886 | 0 | 0 | 0 | 736863.3186 | 2272197.1015 | 5911790.7665 | 4034918.6733 | 18045052.9554 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34289669.3616 | 68455876.4244 | 237137.3706 | 3.4366 | 9977.7339 | 19919.5423 | 203.4096 | 406.0868
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.0667 | 10.2898 | 0.87427 | 4 | 9831.7431 | 19601.6653 | 200.4334 | 399.6065 | 58.3963 | 6.8712 | 66.462 | 2552066.2235 | 0 | 2581556.5344 | 0 | 0 | 0 | 722463.2649 | 2283873.5489 | 5942170.4874 | 4055653.457 | 18137783.5161 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34382399.9223 | 68548606.9851 | 316227.766 | 3.4971 | 9831.7431 | 19601.6653 | 200.4334 | 399.6065
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0607 | 10.3924 | 0.88583 | 4 | 9722.5914 | 19365.0046 | 198.2082 | 394.7818 | 58.3439 | 6.8554 | 72.3679 | 2565806.1264 | 0 | 2601256.776 | 0 | 0 | 0 | 710947.3369 | 2292423.9933 | 5964416.9898 | 4070837.152 | 18205688.3744 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34450304.7806 | 68616511.8434 | 421696.5034 | 3.5433 | 9722.5914 | 19365.0046 | 198.2082 | 394.7818
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.8307 | 10.4719 | 0.8947 | 4 | 9640.9209 | 19187.8041 | 196.5432 | 391.1693 | 58.3029 | 6.843 | 76.871 | 2576359.4584 | 0 | 2616492.5125 | 0 | 0 | 0 | 702090.3386 | 2299027.5007 | 5981597.9614 | 4082563.5182 | 18258131.2898 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34502747.696 | 68668954.7588 | 562341.3252 | 3.5788 | 9640.9209 | 19187.8041 | 196.5432 | 391.1693
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3908 | 10.5299 | 0.90134 | 4 | 9579.7779 | 19056.2665 | 195.2967 | 388.4878 | 58.2727 | 6.8339 | 66.4224 | 2583987.338 | 0 | 2627563.1835 | 0 | 0 | 0 | 694968.1269 | 2303542.2729 | 5993344.4725 | 4090580.7534 | 18293986.1472 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34538602.5534 | 68704809.6162 | 749894.2093 | 3.6054 | 9579.7779 | 19056.2665 | 195.2967 | 388.4878
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8124 | 10.5735 | 0.90636 | 4 | 9533.9877 | 18957.9536 | 194.3632 | 386.4835 | 58.2499 | 6.8271 | 69.3308 | 2589700.8843 | 0 | 2635888.1807 | 0 | 0 | 0 | 689480.4992 | 2306877.1301 | 6002021.0868 | 4096502.721 | 18320470.5021 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34565086.9083 | 68731293.9711 | 1000000 | 3.6255 | 9533.9877 | 18957.9536 | 194.3632 | 386.4835
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1413 | 10.6075 | 0.9102 | 4 | 9499.6741 | 18883.9505 | 193.6637 | 384.9749 | 58.232 | 6.8217 | 70.3294 | 2594143.3556 | 0 | 2642380.3023 | 0 | 0 | 0 | 685409.8799 | 2309554.0797 | 6008985.9608 | 4101256.3906 | 18341729.9689 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34586346.3751 | 68752553.4379 | 1333521.4322 | 3.6408 | 9499.6741 | 18883.9505 | 193.6637 | 384.9749
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3971 | 10.6339 | 0.91312 | 4 | 9473.9634 | 18828.248 | 193.1396 | 383.8393 | 58.218 | 6.8175 | 72.1427 | 2597588.0482 | 0 | 2647426.1551 | 0 | 0 | 0 | 682402.5967 | 2311692.552 | 6014549.8269 | 4105053.8435 | 18358713.0223 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34603329.4284 | 68769536.4912 | 1778279.41 | 3.6525 | 9473.9634 | 18828.248 | 193.1396 | 383.8393
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.5823 | 10.653 | 0.91529 | 4 | 9454.6929 | 18786.7903 | 192.7467 | 382.9941 | 58.2078 | 6.8145 | 71.8242 | 2600076.9445 | 0 | 2651078.5702 | 0 | 0 | 0 | 680044.5834 | 2313168.0382 | 6018388.7395 | 4107673.9802 | 18370430.8561 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34615047.2622 | 68781254.3251 | 2371373.7057 | 3.6611 | 9454.6929 | 18786.7903 | 192.7467 | 382.9941
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.7083 | 10.6662 | 0.91687 | 4 | 9440.2475 | 18756.2108 | 192.4522 | 382.3707 | 58.2009 | 6.8124 | 78.8475 | 2601767.7938 | 0 | 2653563.2172 | 0 | 0 | 0 | 678119.6875 | 2314045.7724 | 6020672.4237 | 4109232.6416 | 18377401.5361 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34622017.9422 | 68788225.0051 | 3162277.6602 | 3.6675 | 9440.2475 | 18756.2108 | 192.4522 | 382.3707
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.8056 | 10.6763 | 0.91807 | 4 | 9429.4181 | 18733.1998 | 192.2314 | 381.9016 | 58.1956 | 6.8108 | 77.8526 | 2603070.8681 | 0 | 2655479.7406 | 0 | 0 | 0 | 676696.1004 | 2314746.2165 | 6022494.8357 | 4110476.4753 | 18382964.2365 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34627580.6427 | 68793787.7055 | 4216965.0343 | 3.6723 | 9429.4181 | 18733.1998 | 192.2314 | 381.9016
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.8936 | 10.6853 | 0.91903 | 4 | 9421.2989 | 18715.4055 | 192.0659 | 381.5389 | 58.1907 | 6.8094 | 76.9914 | 2604249.1441 | 0 | 2657213.7661 | 0 | 0 | 0 | 675785.6998 | 2315526.9579 | 6024526.1645 | 4111862.8989 | 18389164.6312 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34633781.0374 | 68799988.1002 | 5623413.2519 | 3.6761 | 9421.2989 | 18715.4055 | 192.0659 | 381.5389
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.9519 | 10.6914 | 0.91972 | 4 | 9415.2114 | 18702.3475 | 191.9418 | 381.2727 | 58.1875 | 6.8084 | 73.6177 | 2605029.8036 | 0 | 2658363.4317 | 0 | 0 | 0 | 675017.3659 | 2315980.1344 | 6025705.2369 | 4112667.64 | 18392763.6124 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34637380.0186 | 68803587.0814 | 7498942.0933 | 3.6789 | 9415.2114 | 18702.3475 | 191.9418 | 381.2727
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.9908 | 10.6954 | 0.92022 | 4 | 9410.6469 | 18692.7361 | 191.8488 | 381.0767 | 58.1854 | 6.8078 | 75.5855 | 2605549.8775 | 0 | 2659129.7216 | 0 | 0 | 0 | 674387.0792 | 2316236.0046 | 6026370.9586 | 4113122.0088 | 18394795.6503 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 34639412.0565 | 68805619.1193 | 10000000 | 3.6809 | 9410.6469 | 18692.7361 | 191.8488 | 381.0767
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.1892 | [19 empty] | 100 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.028651 | 3.8525e-05 | 4 | 109860570.6067 | 337961410.0877 | 2239656.3292 | 6889800.4713 | 30.9819 | 4.7867 | 28.6134 | 28058.892 | 0 | 1852.7949 | 0 | 0 | 0 | 30946.5357 | 23734.7068 | 61752.8385 | 42147.5812 | 188493.3492 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 16929350.6211 | 52079350.91 | 133.3521 | 0.0001541 | 109860570.6067 | 337961410.0877 | 2239656.3292 | 6889800.4713
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81087 | -0.025039 | 0.00054911 | 4 | 7801964.9924 | 23805002.1792 | 159053.6093 | 485297.1681 | 39.7103 | 5.7732 | 41.6734 | 54785.7805 | 0 | 19640.4748 | 0 | 0 | 0 | 53374.6305 | 49842.3455 | 129679.5589 | 88508.9636 | 395831.7538 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 17136689.0257 | 52286689.3145 | 177.8279 | 0.0021965 | 7801964.9924 | 23805002.1792 | 159053.6093 | 485297.1681
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.010611 | 0.0014257 | 4 | 3079943.5934 | 9243590.1681 | 62788.8161 | 188443.0885 | 48.093 | 6.674 | 22.3675 | 107528.591 | 0 | 56590.8877 | 0 | 0 | 0 | 101736.4936 | 103683.8292 | 269764.055 | 184119.5106 | 823423.367 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 17564280.6389 | 52714280.9277 | 237.1374 | 0.0057028 | 3079943.5934 | 9243590.1681 | 62788.8161 | 188443.0885
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.019796 | 0.0036249 | 4 | 1208181.2507 | 3632385.8859 | 24630.409 | 74051.0994 | 48.0931 | 6.6741 | 21.8661 | 107529.545 | 0 | 56590.3875 | 0 | 0 | 0 | 86840.7787 | 97874.6774 | 254649.8337 | 173803.744 | 777288.9662 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 17518146.2382 | 52668146.527 | 316.2278 | 0.0145 | 1208181.2507 | 3632385.8859 | 24630.409 | 74051.0994
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.026756 | 0.0052591 | 4 | 831008.7819 | 2501911.4241 | 16941.238 | 51004.8485 | 48.0932 | 6.6742 | 22.5436 | 107530.0966 | 0 | 56590.0983 | 0 | 0 | 0 | 75023.0407 | 93265.8619 | 242658.6411 | 165619.5087 | 740687.2472 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 17481544.5192 | 52631544.808 | 421.6965 | 0.021037 | 831008.7819 | 2501911.4241 | 16941.238 | 51004.8485
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.364 | 0.16055 | 0.011242 | 4 | 406684.6788 | 1188345.4936 | 8290.8173 | 24226.0302 | 54.7282 | 7.3399 | 42.6061 | 209780.7154 | 0 | 132386.2761 | 0 | 0 | 0 | 157334.6843 | 194805.6536 | 506844.3504 | 345931.6838 | 1547083.3636 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 18287940.6355 | 53437940.9243 | 562.3413 | 0.044968 | 406684.6788 | 1188345.4936 | 8290.8173 | 24226.0302
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4797 | 0.26197 | 0.017409 | 4 | 268599.1499 | 773353.245 | 5475.757 | 15765.8519 | 56.5427 | 7.5117 | 49.3395 | 266443.5426 | 0 | 176198.6786 | 0 | 0 | 0 | 191408.3895 | 247279.7382 | 643371.1547 | 439114.033 | 1963815.5366 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 18704672.8086 | 53854673.0974 | 749.8942 | 0.069638 | 268599.1499 | 773353.245 | 5475.757 | 15765.8519
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9212 | 0.39705 | 0.025835 | 4 | 185802.9366 | 525948.3028 | 3787.8442 | 10722.1676 | 57.9683 | 7.6428 | 51.1436 | 333711.7147 | 0 | 229595.2337 | 0 | 0 | 0 | 230841.2942 | 309717.8146 | 805822.2218 | 549990.2244 | 2459678.5035 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 19200535.7754 | 54350536.0642 | 1000 | 0.10334 | 185802.9366 | 525948.3028 | 3787.8442 | 10722.1676
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7971 | 0.57593 | 0.037204 | 4 | 133026.7664 | 369226.1067 | 2711.9306 | 7527.1736 | 59.0902 | 7.743 | 47.6712 | 414152.4073 | 0 | 295153.4547 | 0 | 0 | 0 | 277219.2368 | 384744.7886 | 1001027.0178 | 683221.5087 | 3055518.4139 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 19796375.6859 | 54946375.9747 | 1333.5214 | 0.14881 | 133026.7664 | 369226.1067 | 2711.9306 | 7527.1736
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2092 | 0.80869 | 0.052386 | 4 | 97845.5798 | 265590.7827 | 1994.7145 | 5414.4273 | 59.9578 | 7.8177 | 43.8574 | 509278.7626 | 0 | 374747.1968 | 0 | 0 | 0 | 330629.699 | 473715.7068 | 1232511.0966 | 841214.149 | 3762096.6109 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 20502953.8828 | 55652954.1717 | 1778.2794 | 0.20954 | 97845.5798 | 265590.7827 | 1994.7145 | 5414.4273
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2929 | 1.1086 | 0.072484 | 4 | 73592.2498 | 194826.5636 | 1500.2776 | 3971.803 | 60.6217 | 7.8719 | 46.3366 | 621298.0068 | 0 | 470960.495 | 0 | 0 | 0 | 391659.0247 | 578727.8354 | 1505731.1142 | 1027692.4251 | 4596068.9013 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 21336926.1732 | 56486926.462 | 2371.3737 | 0.28993 | 73592.2498 | 194826.5636 | 1500.2776 | 3971.803
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.2124 | 1.4919 | 0.098851 | 4 | 56440.731 | 145336.8122 | 1150.6206 | 2962.8875 | 61.1217 | 7.9086 | 44.1038 | 752650.0816 | 0 | 586776.7043 | 0 | 0 | 0 | 460916.1895 | 702133.7604 | 1826808.0171 | 1246834.0088 | 5576118.7617 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 22316976.0336 | 57466976.3224 | 3162.2777 | 0.39541 | 56440.731 | 145336.8122 | 1150.6206 | 2962.8875
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.1091 | 1.9731 | 0.133 | 4 | 44075.1442 | 110145.3331 | 898.5314 | 2245.4616 | 61.4836 | 7.9291 | 45.722 | 904288.3757 | 0 | 724081.645 | 0 | 0 | 0 | 537277.5037 | 844602.5345 | 2197482.543 | 1499826.9893 | 6707559.5912 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 23448416.8631 | 58598417.1519 | 4216.965 | 0.53201 | 44075.1442 | 110145.3331 | 898.5314 | 2245.4616
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1332 | 2.5676 | 0.17652 | 4 | 35032.4429 | 84814.0994 | 714.1837 | 1729.0501 | 61.7278 | 7.9333 | 50.988 | 1076937.5411 | 0 | 884760.2301 | 0 | 0 | 0 | 619611.1519 | 1006710.4801 | 2619254.1644 | 1787694.7875 | 7994968.3551 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 24735825.6271 | 59885825.9159 | 5623.4133 | 0.70608 | 35032.4429 | 84814.0994 | 714.1837 | 1729.0501
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.3339 | 3.2816 | 0.23062 | 4 | 28355.3844 | 66458.4962 | 578.0629 | 1354.8463 | 61.8647 | 7.9198 | 56.5444 | 1268209.0994 | 0 | 1068005.6556 | 0 | 0 | 0 | 704186.9898 | 1185756.6805 | 3085095.6505 | 2105641.1738 | 9416895.2496 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 26157752.5215 | 61307752.8103 | 7498.9421 | 0.9225 | 28355.3844 | 66458.4962 | 578.0629 | 1354.8463
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5823 | 4.1043 | 0.29553 | 4 | 23398.5357 | 53133.747 | 477.0108 | 1083.2033 | 61.901 | 7.8872 | 66.5111 | 1471631.225 | 0 | 1269068.9763 | 0 | 0 | 0 | 784538.1545 | 1374842.9587 | 3577059.3596 | 2441416.5141 | 10918557.1882 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 27659414.4601 | 62809414.7489 | 10000 | 1.1821 | 23398.5357 | 53133.747 | 477.0108 | 1083.2033
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.5519 | 5.0049 | 0.3698 | 4 | 19713.9721 | 43476.6737 | 401.896 | 886.3308 | 61.8437 | 7.835 | 49.1341 | 1677415.6511 | 0 | 1479490.0463 | 0 | 0 | 0 | 853171.5572 | 1563930.1293 | 4069025.3902 | 2777193.4389 | 12420226.2129 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 29161083.4848 | 64311083.7736 | 13335.2143 | 1.4792 | 19713.9721 | 43476.6737 | 401.896 | 886.3308
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.7212 | 5.9322 | 0.45005 | 4 | 16980.2493 | 36505.8952 | 346.1653 | 744.2221 | 61.7048 | 7.7655 | 64.9471 | 1873577.4769 | 0 | 1687578.9719 | 0 | 0 | 0 | 903098.2249 | 1741059.3227 | 4529879.2173 | 3091735.6456 | 13826928.8593 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 30567786.1312 | 65717786.42 | 17782.7941 | 1.8002 | 16980.2493 | 36505.8952 | 346.1653 | 744.2221
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5102 | 6.8278 | 0.53147 | 4 | 14958.2067 | 31492.6801 | 304.9433 | 642.0209 | 61.5054 | 7.6845 | 57.7414 | 2049488.6113 | 0 | 1881563.2157 | 0 | 0 | 0 | 930745.1316 | 1896100.8139 | 4933265.3739 | 3367054.9862 | 15058218.1325 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 31799075.4045 | 66949075.6933 | 23713.7371 | 2.1259 | 14958.2067 | 31492.6801 | 304.9433 | 642.0209
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.4808 | 7.6457 | 0.60928 | 4 | 13465.9706 | 27888.834 | 274.522 | 568.5516 | 61.2725 | 7.599 | 73.3585 | 2199423.7304 | 0 | 2053531.8729 | 0 | 0 | 0 | 937803.3972 | 2024396.0101 | 5267063.1577 | 3594878.8324 | 16077097.0006 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 32817954.2726 | 67967954.5614 | 31622.7766 | 2.4371 | 13465.9706 | 27888.834 | 274.522 | 568.5516
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.348 | 8.355 | 0.67969 | 4 | 12365.3379 | 25293.9865 | 252.0841 | 515.6521 | 61.0335 | 7.5163 | 77.2672 | 2321564.1442 | 0 | 2199046.5674 | 0 | 0 | 0 | 928614.2802 | 2125197.7468 | 5529328.5991 | 3773880.3852 | 16877631.7229 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 33618488.9948 | 68768489.2836 | 42169.6503 | 2.7188 | 12365.3379 | 25293.9865 | 252.0841 | 515.6521
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.0755 | 8.9497 | 0.74075 | 4 | 11552.7103 | 23415.6232 | 235.5176 | 477.3592 | 60.8076 | 7.4411 | 68.7233 | 2418553.8149 | 0 | 2318719.9558 | 0 | 0 | 0 | 909667.1026 | 2202306.9406 | 5729950.9042 | 3910809.2308 | 17490007.949 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 34230865.2209 | 69380865.5097 | 56234.1325 | 2.963 | 11552.7103 | 23415.6232 | 235.5176 | 477.3592
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.6964 | 9.4319 | 0.79179 | 4 | 10951.5302 | 22049.7698 | 223.2618 | 449.5144 | 60.6078 | 7.3762 | 81.5651 | 2493602.8748 | 0 | 2414238.9426 | 0 | 0 | 0 | 885835.9367 | 2259534.3241 | 5878844.8171 | 4012432.3859 | 17944489.2813 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 34685346.5532 | 69835346.842 | 74989.4209 | 3.1672 | 10951.5302 | 22049.7698 | 223.2618 | 449.5144
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.3823 | 9.8177 | 0.83343 | 4 | 10505.7347 | 21049.4733 | 214.1736 | 429.122 | 60.4372 | 7.3218 | 81.4089 | 2551424.884 | 0 | 2489809.9315 | 0 | 0 | 0 | 861558.6066 | 2302089.4347 | 5989564.4855 | 4088000.8346 | 18282448.1769 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35023305.4489 | 70173305.7377 | 100000 | 3.3337 | 10505.7347 | 21049.4733 | 214.1736 | 429.122
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2345 | 10.1175 | 0.86655 | 4 | 10174.4086 | 20315.1687 | 207.4191 | 414.1522 | 60.2985 | 7.2781 | 75.1711 | 2594927.9553 | 0 | 2547930.9738 | 0 | 0 | 0 | 838496.8678 | 2332728.7608 | 6069281.7271 | 4142409.49 | 18525775.7747 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35266633.0467 | 70416633.3355 | 133352.1432 | 3.4662 | 10174.4086 | 20315.1687 | 207.4191 | 414.1522
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4466 | 10.3504 | 0.89259 | 4 | 9927.6676 | 19772.5583 | 202.3889 | 403.0903 | 60.1868 | 7.2433 | 76.6675 | 2627920.2808 | 0 | 2592799.1745 | 0 | 0 | 0 | 818401.0672 | 2355257.0038 | 6127895.5942 | 4182414.6587 | 18704687.7791 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35445545.0511 | 70595545.3399 | 177827.941 | 3.5704 | 9927.6676 | 19772.5583 | 202.3889 | 403.0903
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.1445 | 10.5295 | 0.91282 | 4 | 9743.6164 | 19370.3743 | 198.6368 | 394.8913 | 60.0987 | 7.216 | 76.4721 | 2652801.225 | 0 | 2627119.1593 | 0 | 0 | 0 | 801540.4054 | 2371769.708 | 6170858.2633 | 4211737.5632 | 18835826.3242 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35576683.5961 | 70726683.885 | 237137.3706 | 3.6513 | 9743.6164 | 19370.3743 | 198.6368 | 394.8913
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4286 | 10.6653 | 0.92835 | 4 | 9606.1495 | 19071.89 | 195.8344 | 388.8063 | 60.0306 | 7.195 | 77.9665 | 2671362.4808 | 0 | 2653007.6433 | 0 | 0 | 0 | 787669.5212 | 2383695.4617 | 6201886.6281 | 4232915.0597 | 18930536.7947 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35671394.0667 | 70821394.3555 | 316227.766 | 3.7134 | 9606.1495 | 19071.89 | 195.8344 | 388.8063
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4102 | 10.7691 | 0.94025 | 4 | 9503.3738 | 18849.3284 | 193.7391 | 384.2691 | 59.9777 | 7.1788 | 66.7245 | 2685403.5325 | 0 | 2672760.5199 | 0 | 0 | 0 | 776688.5938 | 2392592.532 | 6225034.98 | 4248714.2856 | 19001194.4438 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35742051.7157 | 70892052.0045 | 421696.5034 | 3.761 | 9503.3738 | 18849.3284 | 193.7391 | 384.2691
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1607 | 10.8485 | 0.94933 | 4 | 9426.4765 | 18683.0185 | 192.1715 | 380.8786 | 59.9369 | 7.1663 | 69.255 | 2696051.1809 | 0 | 2687839.7568 | 0 | 0 | 0 | 768152.132 | 2399296.7972 | 6242478.1028 | 4260619.5752 | 19054437.5448 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35795294.8167 | 70945295.1055 | 562341.3252 | 3.7973 | 9426.4765 | 18683.0185 | 192.1715 | 380.8786
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.713 | 10.907 | 0.95616 | 4 | 9368.9087 | 18559.3185 | 190.9979 | 378.3568 | 59.9065 | 7.157 | 79.0019 | 2703837.3882 | 0 | 2698922.9631 | 0 | 0 | 0 | 761357.7374 | 2404006.0546 | 6254730.6245 | 4268982.1731 | 19091836.9408 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35832694.2127 | 70982694.5015 | 749894.2093 | 3.8246 | 9368.9087 | 18559.3185 | 190.9979 | 378.3568
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1345 | 10.9517 | 0.96134 | 4 | 9325.7933 | 18466.6363 | 190.1189 | 376.4674 | 59.8832 | 7.1499 | 81.037 | 2709753.7067 | 0 | 2707376.7248 | 0 | 0 | 0 | 756192.6998 | 2407596.0212 | 6264070.9813 | 4275357.1585 | 19120347.2922 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35861204.5642 | 71011204.853 | 1000000 | 3.8454 | 9325.7933 | 18466.6363 | 190.1189 | 376.4674
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4512 | 10.9853 | 0.96525 | 4 | 9293.4918 | 18397.31 | 189.4604 | 375.054 | 59.8656 | 7.1445 | 78.0396 | 2714183.1314 | 0 | 2713724.4167 | 0 | 0 | 0 | 752237.3965 | 2410256.5284 | 6270993.0753 | 4280081.6299 | 19141476.1782 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35882333.4501 | 71032333.7389 | 1333521.4322 | 3.861 | 9293.4918 | 18397.31 | 189.4604 | 375.054
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6876 | 11.0104 | 0.96819 | 4 | 9269.2861 | 18345.475 | 188.9669 | 373.9973 | 59.8524 | 7.1405 | 80.1832 | 2717479.4187 | 0 | 2718458.6772 | 0 | 0 | 0 | 749207.4066 | 2412206.746 | 6276067.1414 | 4283544.7843 | 19156964.1743 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35897821.4462 | 71047821.735 | 1778279.41 | 3.8728 | 9269.2861 | 18345.475 | 188.9669 | 373.9973
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.8728 | 11.03 | 0.97043 | 4 | 9251.1439 | 18306.3835 | 188.5971 | 373.2004 | 59.842 | 7.1373 | 78.5573 | 2720057.7592 | 0 | 2722167.9081 | 0 | 0 | 0 | 746996.5586 | 2413796.6681 | 6280203.7925 | 4286368.1337 | 19169590.82 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35910448.092 | 71060448.3808 | 2371373.7057 | 3.8817 | 9251.1439 | 18306.3835 | 188.5971 | 373.2004
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.9971 | 11.0433 | 0.97206 | 4 | 9237.5446 | 18277.6202 | 188.3198 | 372.614 | 59.8351 | 7.1352 | 79.0805 | 2721784.7617 | 0 | 2724655.7141 | 0 | 0 | 0 | 745157.9303 | 2414723.3784 | 6282614.9028 | 4288013.766 | 19176950.4533 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35917807.7253 | 71067808.0141 | 3162277.6602 | 3.8882 | 9237.5446 | 18277.6202 | 188.3198 | 372.614
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.1091 | 11.0551 | 0.97335 | 4 | 9227.3495 | 18255.4059 | 188.112 | 372.1611 | 59.8288 | 7.1333 | 83.0725 | 2723340.7335 | 0 | 2726898.9341 | 0 | 0 | 0 | 743981.7729 | 2415746.3618 | 6285276.4957 | 4289830.3578 | 19185074.6559 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35925931.9278 | 71075932.2166 | 4216965.0343 | 3.8934 | 9227.3495 | 18255.4059 | 188.112 | 372.1611
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.1823 | 11.0629 | 0.97428 | 4 | 9219.706 | 18239.1411 | 187.9562 | 371.8296 | 59.8247 | 7.1321 | 78.518 | 2724355.4584 | 0 | 2728363.1018 | 0 | 0 | 0 | 742972.5943 | 2416319.5502 | 6286767.8144 | 4290848.2135 | 19189626.7326 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35930484.0046 | 71080484.2934 | 5623413.2519 | 3.8971 | 9219.706 | 18239.1411 | 187.9562 | 371.8296
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2406 | 11.069 | 0.975 | 4 | 9213.9751 | 18226.8283 | 187.8393 | 371.5785 | 59.8214 | 7.1311 | 82.1015 | 2725164.2434 | 0 | 2729530.6726 | 0 | 0 | 0 | 742251.8742 | 2416809.2481 | 6288041.9079 | 4291717.8085 | 19193515.7547 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35934373.0266 | 71084373.3154 | 7498942.0933 | 3.9 | 9213.9751 | 18226.8283 | 187.8393 | 371.5785
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2749 | 11.0727 | 0.97549 | 4 | 9209.6781 | 18217.9307 | 187.7517 | 371.3972 | 59.8195 | 7.1305 | 74.9267 | 2725638.797 | 0 | 2730216.1556 | 0 | 0 | 0 | 741603.6604 | 2417008.8591 | 6288561.2547 | 4292072.2733 | 19195101.0001 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 35935958.2721 | 71085958.5609 | 10000000 | 3.902 | 9209.6781 | 18217.9307 | 187.7517 | 371.3972
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7652 | [19 empty] | 100 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.029549 | 2.4136e-05 | 4 | 180601535.6561 | 555020633.0848 | 3681806.586 | 11314846.3264 | 31.0218 | 4.998 | 30.3933 | 28810.7528 | 0 | 1392.2129 | 0 | 0 | 0 | 32067.1519 | 24285.3459 | 63185.4884 | 43125.3941 | 192866.3461 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 17435824.5746 | 53583389.303 | 133.3521 | 9.6543e-05 | 180601535.6561 | 555020633.0848 | 3681806.586 | 11314846.3264
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | -0.025842 | 0.00058005 | 4 | 7614236.2084 | 23193689.5677 | 155226.5041 | 472834.7336 | 40.5561 | 6.078 | 35.5241 | 58522.6407 | 0 | 20908.001 | 0 | 0 | 0 | 57351.7727 | 53345.1416 | 138793.1159 | 94729.1535 | 423649.8256 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 17666608.0542 | 53814172.7825 | 177.8279 | 0.0023202 | 7614236.2084 | 23193689.5677 | 155226.5041 | 472834.7336
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0090702 | 0.0016721 | 4 | 2703387.152 | 8108027.7423 | 55112.2037 | 165293.1124 | 48.7654 | 6.9566 | 22.8569 | 110306.6909 | 0 | 56623.9741 | 0 | 0 | 0 | 103618.552 | 105514.1946 | 274526.2905 | 187369.8342 | 837959.5363 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 18080917.7649 | 54228482.4932 | 237.1374 | 0.0066882 | 2703387.152 | 8108027.7423 | 55112.2037 | 165293.1124
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.018248 | 0.0038625 | 4 | 1167325.5605 | 3506948.5392 | 23797.5105 | 71493.8895 | 48.7656 | 6.9567 | 21.2896 | 110307.685 | 0 | 56623.4581 | 0 | 0 | 0 | 88913.6222 | 99779.4584 | 259605.6833 | 177186.2132 | 792416.1202 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 18035374.3487 | 54182939.0771 | 316.2278 | 0.01545 | 1167325.5605 | 3506948.5392 | 23797.5105 | 71493.8895
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.025202 | 0.0054903 | 4 | 819596.2799 | 2465569.3611 | 16708.5788 | 50263.9664 | 48.7657 | 6.9568 | 21.0297 | 110308.266 | 0 | 56623.1565 | 0 | 0 | 0 | 77275.2194 | 95240.5903 | 247796.4795 | 169126.189 | 756369.9008 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 17999328.1294 | 54146892.8577 | 421.6965 | 0.021961 | 819596.2799 | 2465569.3611 | 16708.5788 | 50263.9664
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5124 | 0.17257 | 0.012296 | 4 | 384139.6436 | 1119073.5322 | 7831.2062 | 22813.8276 | 56.1443 | 7.6904 | 34.9773 | 224056.973 | 0 | 139663.5256 | 0 | 0 | 0 | 169289.5374 | 207873.914 | 540845.2835 | 369138.0193 | 1650867.2528 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 18893825.4814 | 55041390.2097 | 562.3413 | 0.049185 | 384139.6436 | 1119073.5322 | 7831.2062 | 22813.8276
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.687 | 0.28164 | 0.019053 | 4 | 253788.2322 | 728084.7403 | 5173.8164 | 14842.9922 | 58.0428 | 7.8676 | 45.1271 | 285014.7162 | 0 | 186142.3949 | 0 | 0 | 0 | 206542.3093 | 264302.774 | 687661.6019 | 469343.1733 | 2099006.9696 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 19341965.1982 | 55489529.9265 | 749.8942 | 0.076213 | 253788.2322 | 728084.7403 | 5173.8164 | 14842.9922
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1964 | 0.42624 | 0.02828 | 4 | 175665.8701 | 495213.5125 | 3581.1864 | 10095.5973 | 59.5242 | 8.0016 | 58.4473 | 356975.7751 | 0 | 242471.8744 | 0 | 0 | 0 | 249223.3775 | 330981.7005 | 861146.4911 | 587750.175 | 2628549.3935 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 19871507.6221 | 56019072.3505 | 1000 | 0.11312 | 175665.8701 | 495213.5125 | 3581.1864 | 10095.5973
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1332 | 0.61535 | 0.040709 | 4 | 125875.6799 | 347862.1248 | 2566.146 | 7091.6399 | 60.6772 | 8.1027 | 49.4302 | 441874.2592 | 0 | 310688.2957 | 0 | 0 | 0 | 298121.8485 | 409766.9173 | 1066129.4642 | 727655.2661 | 3254236.0511 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 20497194.2797 | 56644759.008 | 1333.5214 | 0.16284 | 125875.6799 | 347862.1248 | 2566.146 | 7091.6399
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6398 | 0.86276 | 0.057308 | 4 | 92681.9519 | 250372.207 | 1889.447 | 5104.1761 | 61.5782 | 8.1788 | 47.9924 | 542990.539 | 0 | 394081.9868 | 0 | 0 | 0 | 355252.8251 | 504006.8868 | 1311322.5336 | 895004.5741 | 4002659.3454 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 21245617.574 | 57393182.3023 | 1778.2794 | 0.22923 | 92681.9519 | 250372.207 | 1889.447 | 5104.1761
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8607 | 1.183 | 0.079286 | 4 | 69793.8381 | 183772.3362 | 1422.8418 | 3746.4476 | 62.2712 | 8.2339 | 39.604 | 662686.856 | 0 | 495413.5393 | 0 | 0 | 0 | 421272.733 | 615955.52 | 1602589.9132 | 1093800.5457 | 4891719.1072 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 22134677.3358 | 58282242.0642 | 2371.3737 | 0.31714 | 69793.8381 | 183772.3362 | 1422.8418 | 3746.4476
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.9239 | 1.5895 | 0.10806 | 4 | 53603.3586 | 137230.113 | 1092.777 | 2797.6215 | 62.7891 | 8.2706 | 54.1124 | 802009.5553 | 0 | 616493.0202 | 0 | 0 | 0 | 495137.7933 | 746319.7438 | 1941770.8822 | 1325298.5265 | 5927029.5213 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 23169987.7499 | 59317552.4782 | 3162.2777 | 0.43225 | 53603.3586 | 137230.113 | 1092.777 | 2797.6215
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0176 | 2.1014 | 0.14532 | 4 | 41927.3592 | 104115.5178 | 854.7459 | 2122.5357 | 63.165 | 8.2905 | 44.1372 | 963427.4175 | 0 | 760558.2376 | 0 | 0 | 0 | 577340.141 | 897517.0605 | 2335155.2853 | 1593791.4648 | 7127789.6066 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 24370747.8352 | 60518312.5635 | 4216.965 | 0.58126 | 41927.3592 | 104115.5178 | 854.7459 | 2122.5357
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2346 | 2.7293 | 0.19262 | 4 | 33387.034 | 80302.0349 | 680.6398 | 1637.0656 | 63.4157 | 8.293 | 46.7651 | 1145798.7868 | 0 | 927867.6795 | 0 | 0 | 0 | 664706.6245 | 1067965.5054 | 2778627.1753 | 1896470.1422 | 8481435.9139 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 25724394.1425 | 61871958.8708 | 5623.4133 | 0.77049 | 33387.034 | 80302.0349 | 680.6398 | 1637.0656
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6445 | 3.4813 | 0.25125 | 4 | 27080.3818 | 63048.3122 | 552.0702 | 1285.3251 | 63.5545 | 8.2768 | 55.1025 | 1347338.4202 | 0 | 1118223.0756 | 0 | 0 | 0 | 754281.6994 | 1255738.8461 | 3267174.8901 | 2229913.9962 | 9972670.9277 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 27215629.1562 | 63363193.8846 | 7498.9421 | 1.005 | 27080.3818 | 63048.3122 | 552.0702 | 1285.3251
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0929 | 4.3439 | 0.32125 | 4 | 22399.1219 | 50529.2451 | 456.6364 | 1030.107 | 63.5881 | 8.2403 | 51.1661 | 1560745.4015 | 0 | 1326221.4164 | 0 | 0 | 0 | 838978.4164 | 1453118.6414 | 3780716.6292 | 2580416.7854 | 11540197.2903 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 28783155.5189 | 64930720.2472 | 10000 | 1.285 | 22399.1219 | 50529.2451 | 456.6364 | 1030.107
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.2038 | 5.2806 | 0.40084 | 4 | 18920.7453 | 41465.6683 | 385.725 | 845.3337 | 63.5244 | 8.1835 | 57.8259 | 1774923.234 | 0 | 1542228.8917 | 0 | 0 | 0 | 910385.1399 | 1648739.5336 | 4289682.0634 | 2927796.1524 | 13093755.0151 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 30336713.2437 | 66484277.972 | 13335.2143 | 1.6034 | 18920.7453 | 41465.6683 | 385.725 | 845.3337
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.4728 | 6.2406 | 0.48628 | 4 | 16341.3682 | 34925.0739 | 333.1409 | 711.9949 | 63.3766 | 8.109 | 60.5285 | 1978194.7823 | 0 | 1754952.0232 | 0 | 0 | 0 | 962299.433 | 1831224.033 | 4764469.2982 | 3251848.1961 | 14542987.7659 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 31785945.9945 | 67933510.7228 | 17782.7941 | 1.9451 | 16341.3682 | 34925.0739 | 333.1409 | 711.9949
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.2935 | 7.1612 | 0.57234 | 4 | 14434.3908 | 30223.8218 | 294.2646 | 616.1535 | 63.1682 | 8.0231 | 62.6373 | 2159264.3461 | 0 | 1951951.2133 | 0 | 0 | 0 | 990866.6791 | 1989812.073 | 5177082.8474 | 3533465.4218 | 15802442.5807 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 33045400.8093 | 69192965.5376 | 23713.7371 | 2.2894 | 14434.3908 | 30223.8218 | 294.2646 | 616.1535
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.2324 | 7.9957 | 0.654 | 4 | 13027.4631 | 26845.3817 | 265.5825 | 547.2794 | 62.9279 | 7.9335 | 63.0712 | 2312545.9286 | 0 | 2125379.4248 | 0 | 0 | 0 | 998110.3717 | 2120053.9328 | 5515945.4503 | 3764746.1112 | 16836781.2196 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 34079739.4481 | 70227304.1765 | 31622.7766 | 2.616 | 13027.4631 | 26845.3817 | 265.5825 | 547.2794
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.0413 | 8.7162 | 0.72749 | 4 | 11989.8336 | 24411.9122 | 244.429 | 497.6698 | 62.6833 | 7.8477 | 64.8011 | 2436961.4091 | 0 | 2271543.9738 | 0 | 0 | 0 | 989057.4928 | 2222049.5215 | 5781317.05 | 3945867.6808 | 17646797.128 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 34889755.3566 | 71037320.0849 | 42169.6503 | 2.9099 | 11989.8336 | 24411.9122 | 244.429 | 497.6698
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7 | 9.3182 | 0.79092 | 4 | 11223.6834 | 22649.4418 | 228.81 | 461.7395 | 62.4536 | 7.77 | 80.8886 | 2535505.3897 | 0 | 2391382.1047 | 0 | 0 | 0 | 970370.6155 | 2299930.6629 | 5983947.8041 | 4084167.3341 | 18265303.911 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 35508262.1396 | 71655826.8679 | 56234.1325 | 3.1637 | 11223.6834 | 22649.4418 | 228.81 | 461.7395
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.2628 | 9.8059 | 0.84379 | 4 | 10656.8269 | 21366.6819 | 217.2538 | 435.5887 | 62.2511 | 7.7032 | 78.3368 | 2611785.928 | 0 | 2487014.145 | 0 | 0 | 0 | 947081.3726 | 2357893.7638 | 6134755.9029 | 4187096.9604 | 18725628.0727 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 35968586.3013 | 72116151.0296 | 74989.4209 | 3.3752 | 10656.8269 | 21366.6819 | 217.2538 | 435.5887
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.8728 | 10.1932 | 0.88672 | 4 | 10236.4384 | 20427.7641 | 208.6836 | 416.4476 | 62.0799 | 7.6478 | 75.7457 | 2670134.2655 | 0 | 2562083.9787 | 0 | 0 | 0 | 923111.2912 | 2400578.5188 | 6245812.8795 | 4262895.6289 | 19064616.5626 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 36307574.7911 | 72455139.5195 | 100000 | 3.5469 | 10236.4384 | 20427.7641 | 208.6836 | 416.4476
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.687 | 10.4961 | 0.92089 | 4 | 9923.9693 | 19737.149 | 202.3135 | 402.3685 | 61.9397 | 7.6029 | 82.0343 | 2714393.7667 | 0 | 2620260.0232 | 0 | 0 | 0 | 900776.116 | 2431817.6633 | 6327090.7255 | 4318369.4289 | 19312707.7236 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 36555665.9522 | 72703230.6805 | 133352.1432 | 3.6836 | 9923.9693 | 19737.149 | 202.3135 | 402.3685
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8498 | 10.7295 | 0.94765 | 4 | 9691.2587 | 19227.3472 | 197.5694 | 391.9755 | 61.828 | 7.5676 | 66.2489 | 2747677.7184 | 0 | 2664772.1374 | 0 | 0 | 0 | 881124.5767 | 2454494.0287 | 6386089.9766 | 4358637.6301 | 19492796.0678 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 36735754.2964 | 72883319.0247 | 177827.941 | 3.7906 | 9691.2587 | 19227.3472 | 197.5694 | 391.9755
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5212 | 10.9101 | 0.96846 | 4 | 9517.6684 | 18848.8892 | 194.0305 | 384.2601 | 61.7393 | 7.5397 | 74.8879 | 2772963.9905 | 0 | 2699056.4925 | 0 | 0 | 0 | 864842.9465 | 2471376.7375 | 6430015.322 | 4388617.5809 | 19626873.07 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 36869831.2986 | 73017396.0269 | 237137.3706 | 3.8738 | 9517.6684 | 18848.8892 | 194.0305 | 384.2601
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.7929 | 11.0477 | 0.98445 | 4 | 9388.0137 | 18567.6556 | 191.3874 | 378.5268 | 61.6705 | 7.5181 | 66.7307 | 2791948.8739 | 0 | 2725077.1582 | 0 | 0 | 0 | 851562.0434 | 2483749.3494 | 6462206.3202 | 4410588.5986 | 19725132.3437 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 36968090.5723 | 73115655.3006 | 316227.766 | 3.9378 | 9388.0137 | 18567.6556 | 191.3874 | 378.5268
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.7519 | 11.1516 | 0.99664 | 4 | 9291.0789 | 18358.3914 | 189.4112 | 374.2606 | 61.6177 | 7.5017 | 82.4544 | 2806118.9261 | 0 | 2744661.7797 | 0 | 0 | 0 | 840904.175 | 2492757.1036 | 6485642.6487 | 4426584.3744 | 19796669.0075 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37039627.2361 | 73187191.9644 | 421696.5034 | 3.9866 | 9291.0789 | 18358.3914 | 189.4112 | 374.2606
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4707 | 11.2297 | 1.0059 | 4 | 9218.5524 | 18202.4941 | 187.9327 | 371.0825 | 61.5777 | 7.4892 | 82.38 | 2816658.2405 | 0 | 2759321.6894 | 0 | 0 | 0 | 832465.3049 | 2499293.6415 | 6502649.3797 | 4438191.8177 | 19848580.0737 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37091538.3022 | 73239103.0306 | 562341.3252 | 4.0236 | 9218.5524 | 18202.4941 | 187.9327 | 371.0825
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0313 | 11.2904 | 1.013 | 4 | 9164.2576 | 18085.4035 | 186.8258 | 368.6954 | 61.5463 | 7.4795 | 88.0402 | 2824829.7568 | 0 | 2770743.823 | 0 | 0 | 0 | 826138.2221 | 2504467.6028 | 6516110.9655 | 4447379.6266 | 19889669.9968 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37132628.2254 | 73280192.9537 | 749894.2093 | 4.0519 | 9164.2576 | 18085.4035 | 186.8258 | 368.6954
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4381 | 11.3346 | 1.0183 | 4 | 9123.5936 | 17998.3987 | 185.9968 | 366.9217 | 61.5233 | 7.4724 | 85.2857 | 2830730.704 | 0 | 2779023.4977 | 0 | 0 | 0 | 821083.4336 | 2508026.6778 | 6525370.9485 | 4453699.7553 | 19917935.0169 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37160893.2455 | 73308457.9738 | 1000000 | 4.0731 | 9123.5936 | 17998.3987 | 185.9968 | 366.9217
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7398 | 11.3675 | 1.0222 | 4 | 9093.129 | 17933.4454 | 185.3757 | 365.5975 | 61.5062 | 7.4671 | 81.9194 | 2835093.5831 | 0 | 2785162.1058 | 0 | 0 | 0 | 817171.0947 | 2510596.4456 | 6532056.9573 | 4458263.0937 | 19938343.2801 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37181301.5087 | 73328866.237 | 1333521.4322 | 4.0889 | 9093.129 | 17933.4454 | 185.3757 | 365.5975
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9787 | 11.3934 | 1.0253 | 4 | 9070.3001 | 17884.4042 | 184.9103 | 364.5978 | 61.4926 | 7.4629 | 75.9237 | 2838539.8922 | 0 | 2790021.1877 | 0 | 0 | 0 | 814338.1197 | 2512730.6879 | 6537609.8179 | 4462053.0352 | 19955292.7406 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37198250.9692 | 73345815.6975 | 1778279.41 | 4.1011 | 9070.3001 | 17884.4042 | 184.9103 | 364.5978
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.1567 | 11.4127 | 1.0276 | 4 | 9053.1899 | 17847.7273 | 184.5615 | 363.8501 | 61.4825 | 7.4597 | 81.6192 | 2841102.0163 | 0 | 2793639.5866 | 0 | 0 | 0 | 812172.4242 | 2514296.4706 | 6541683.6634 | 4464833.5184 | 19967727.6795 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37210685.9081 | 73358250.6364 | 2371373.7057 | 4.1102 | 9053.1899 | 17847.7273 | 184.5615 | 363.8501
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.2929 | 11.4275 | 1.0293 | 4 | 9040.3643 | 17820.1659 | 184.3001 | 363.2882 | 61.4747 | 7.4573 | 84.0592 | 2843058.8361 | 0 | 2796406.5255 | 0 | 0 | 0 | 810563.9282 | 2515511.423 | 6544844.7203 | 4466991.0047 | 19977376.4377 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37220334.6663 | 73367899.3946 | 3162277.6602 | 4.1171 | 9040.3643 | 17820.1659 | 184.3001 | 363.2882
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3855 | 11.4376 | 1.0305 | 4 | 9030.7492 | 17799.8366 | 184.104 | 362.8737 | 61.4694 | 7.4557 | 81.6835 | 2844388.3109 | 0 | 2798288.2631 | 0 | 0 | 0 | 809238.7843 | 2516246.9897 | 6546758.514 | 4468297.2083 | 19983218.0703 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37226176.2988 | 73373741.0272 | 4216965.0343 | 4.1222 | 9030.7492 | 17799.8366 | 184.104 | 362.8737
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.4586 | 11.4456 | 1.0315 | 4 | 9023.5406 | 17784.4761 | 183.9571 | 362.5606 | 61.4652 | 7.4544 | 74.976 | 2845437.8684 | 0 | 2799774.7158 | 0 | 0 | 0 | 808283.4157 | 2516863.44 | 6548362.3912 | 4469391.8874 | 19988113.7185 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37231071.9471 | 73378636.6754 | 5623413.2519 | 4.126 | 9023.5406 | 17784.4761 | 183.9571 | 362.5606
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5124 | 11.4514 | 1.0322 | 4 | 9018.1358 | 17773.0017 | 183.8469 | 362.3267 | 61.4621 | 7.4534 | 73.5758 | 2846207.9311 | 0 | 2800865.8997 | 0 | 0 | 0 | 807550.9113 | 2517303.6494 | 6549507.7258 | 4470173.6018 | 19991609.7192 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37234567.9478 | 73382132.6761 | 7498942.0933 | 4.1289 | 9018.1358 | 17773.0017 | 183.8469 | 362.3267
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5512 | 11.4557 | 1.0327 | 4 | 9014.0833 | 17764.4468 | 183.7643 | 362.1523 | 61.4598 | 7.4528 | 76.5795 | 2846765.2773 | 0 | 2801655.9789 | 0 | 0 | 0 | 806984.0468 | 2517608.0682 | 6550299.7611 | 4470714.1821 | 19994027.3145 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 37236985.5431 | 73384550.2714 | 10000000 | 4.131 | 9014.0833 | 17764.4468 | 183.7643 | 362.1523
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3919 | [19 empty] | 100 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.41895 | -0.030424 | 8.8117e-06 | 4 | 509205851.4739 | 1563449173.2838 | 10380850.0342 | 31873026.1189 | 31.0561 | 5.2082 | 29.5898 | 29547.4826 | 0 | 902.9934 | 0 | 0 | 0 | 33171.2491 | 24812.4728 | 64556.9645 | 44061.4548 | 197052.6172 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 17947971.8933 | 55106872.2746 | 133.3521 | 3.5247e-05 | 509205851.4739 | 1563449173.2838 | 10380850.0342 | 31873026.1189
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | -0.026517 | 0.00061521 | 4 | 7398173.818 | 22498314.4418 | 150821.7801 | 458658.5711 | 41.4748 | 6.3911 | 37.1687 | 62668.5281 | 0 | 22418.6495 | 0 | 0 | 0 | 61732.9765 | 57259.8601 | 148978.4104 | 101680.8263 | 454739.2508 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 18205658.5269 | 55364558.9083 | 177.8279 | 0.0024608 | 7398173.818 | 22498314.4418 | 150821.7801 | 458658.5711
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0075285 | 0.0019122 | 4 | 2432126.8613 | 7290201.1959 | 49582.1958 | 148620.6121 | 49.4147 | 7.2377 | 21.6382 | 113015.4172 | 0 | 56638.3175 | 0 | 0 | 0 | 105481.5206 | 107302.7495 | 279179.7435 | 190545.9115 | 852163.6598 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 18603082.9359 | 55761983.3173 | 237.1374 | 0.0076489 | 2432126.8613 | 7290201.1959 | 49582.1958 | 148620.6121
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.016697 | 0.0040941 | 4 | 1133232.7737 | 3402304.6361 | 23102.4829 | 69360.582 | 49.4148 | 7.2378 | 21.7516 | 113016.4512 | 0 | 56637.7861 | 0 | 0 | 0 | 90960.5454 | 101639.7652 | 264445.82 | 180489.706 | 807190.0739 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 18558109.35 | 55717009.7314 | 316.2278 | 0.016376 | 1133232.7737 | 3402304.6361 | 23102.4829 | 69360.582
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7157 | 0.099761 | 0.0081298 | 4 | 587607.2095 | 1730281.1843 | 11979.1678 | 35274.1223 | 55.0642 | 7.8035 | 44.0804 | 184196.1182 | 0 | 107117.3917 | 0 | 0 | 0 | 147018.8016 | 170949.6015 | 444775.7966 | 303568.6204 | 1357626.33 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 19108545.6061 | 56267445.9875 | 421.6965 | 0.032519 | 587607.2095 | 1730281.1843 | 11979.1678 | 35274.1223
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.18466 | 0.013426 | 4 | 363201.105 | 1055126.3513 | 7404.3458 | 21510.1778 | 57.5534 | 8.0405 | 42.6337 | 238414.9424 | 0 | 146856.7162 | 0 | 0 | 0 | 181133.3796 | 220897.9649 | 574731.1923 | 392265.8483 | 1754300.0436 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 19505219.3197 | 56664119.7011 | 562.3413 | 0.053704 | 363201.105 | 1055126.3513 | 7404.3458 | 21510.1778
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8741 | 0.30031 | 0.020805 | 4 | 240067.6713 | 686580.3047 | 4894.1042 | 13996.8682 | 59.5212 | 8.2215 | 34.7197 | 303014.2197 | 0 | 195448.027 | 0 | 0 | 0 | 220747.9365 | 280491.9715 | 729782.5729 | 498091.6015 | 2227576.3291 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 19978495.6052 | 57137395.9866 | 749.8942 | 0.08322 | 240067.6713 | 686580.3047 | 4894.1042 | 13996.8682
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4593 | 0.45533 | 0.03089 | 4 | 166288.7807 | 467028.309 | 3390.0217 | 9521.0038 | 61.0752 | 8.36 | 52.3485 | 380239.6985 | 0 | 255082.779 | 0 | 0 | 0 | 267238.236 | 351998.6783 | 915828.356 | 625071.6713 | 2795459.4191 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 20546378.6952 | 57705279.0765 | 1000 | 0.12356 | 166288.7807 | 467028.309 | 3390.0217 | 9521.0038
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4887 | 0.65773 | 0.044471 | 4 | 119264.5164 | 328159.6744 | 2431.3685 | 6689.9788 | 62.2786 | 8.4637 | 40.9915 | 471102.0409 | 0 | 327113.5898 | 0 | 0 | 0 | 320263.1368 | 436206.7194 | 1134920.4054 | 774606.497 | 3464212.3894 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 21215131.6655 | 58374032.0468 | 1333.5214 | 0.17788 | 119264.5164 | 328159.6744 | 2431.3685 | 6689.9788
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1003 | 0.92122 | 0.062592 | 4 | 87908.2383 | 236325.4741 | 1792.1283 | 4817.8144 | 63.2129 | 8.541 | 51.2329 | 578705.827 | 0 | 414668.9604 | 0 | 0 | 0 | 381544.9417 | 536218.6943 | 1395131.0491 | 952205.6081 | 4258475.0805 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 22009394.3566 | 59168294.7379 | 1778.2794 | 0.25037 | 87908.2383 | 236325.4741 | 1792.1283 | 4817.8144
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4332 | 1.2602 | 0.086546 | 4 | 66280.865 | 173619.4176 | 1351.2251 | 3539.4667 | 63.9279 | 8.5966 | 44.5782 | 705266.422 | 0 | 520363.4141 | 0 | 0 | 0 | 451489.0152 | 654076.352 | 1701772.4984 | 1161494.6981 | 5194462.3998 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 22945381.6759 | 60104282.0572 | 2371.3737 | 0.34618 | 66280.865 | 173619.4176 | 1351.2251 | 3539.4667
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6519 | 1.6917 | 0.1179 | 4 | 50977.1845 | 129771.8853 | 1039.2389 | 2645.5754 | 64.4649 | 8.6333 | 50.1817 | 853127.4253 | 0 | 647116.2928 | 0 | 0 | 0 | 530420.049 | 791958.8691 | 2060514.5244 | 1406343.5022 | 6289480.6627 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 24040399.9388 | 61199300.3202 | 3162.2777 | 0.47159 | 50977.1845 | 129771.8853 | 1039.2389 | 2645.5754
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9138 | 2.2325 | 0.15839 | 4 | 39937.2937 | 98587.1506 | 814.1758 | 2009.8324 | 64.8527 | 8.6522 | 54.6153 | 1023628.0054 | 0 | 797218.5395 | 0 | 0 | 0 | 617516.0078 | 950961.3955 | 2474206.4822 | 1688696.7639 | 7552227.1943 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 25303146.4704 | 62462046.8518 | 4216.965 | 0.63357 | 39937.2937 | 98587.1506 | 814.1758 | 2009.8324
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3381 | 2.896 | 0.20973 | 4 | 31860.38 | 76154.3406 | 649.5169 | 1552.5092 | 65.1107 | 8.6529 | 51.2748 | 1216374.7337 | 0 | 971654.313 | 0 | 0 | 0 | 710427.4227 | 1130398.0231 | 2941063.7795 | 2007336.4623 | 8977254.7343 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 26728174.0104 | 63887074.3917 | 5623.4133 | 0.83892 | 31860.38 | 76154.3406 | 649.5169 | 1552.5092
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.9675 | 3.6881 | 0.27314 | 4 | 25895.4511 | 59906.4987 | 527.9138 | 1221.275 | 65.2515 | 8.6338 | 58.9558 | 1428647.9548 | 0 | 1169473.9298 | 0 | 0 | 0 | 805298.1518 | 1327333.8142 | 3453450.311 | 2357050.7985 | 10541254.9601 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 28292174.2362 | 65451074.6176 | 7498.9421 | 1.0926 | 25895.4511 | 59906.4987 | 527.9138 | 1221.275
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.6009 | 4.59 | 0.34845 | 4 | 21468.4984 | 48128.7794 | 437.6644 | 981.1703 | 65.2819 | 8.5934 | 54.5974 | 1651798.9463 | 0 | 1384119.5057 | 0 | 0 | 0 | 893922.2898 | 1532637.8893 | 3987609.4008 | 2721625.3532 | 12171713.3851 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 29922632.6612 | 67081533.0426 | 10000 | 1.3938 | 21468.4984 | 48128.7794 | 437.6644 | 981.1703
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.8675 | 5.5651 | 0.43359 | 4 | 18180.3946 | 39605.5059 | 370.6319 | 807.4118 | 65.2113 | 8.5317 | 65.9759 | 1874772.0447 | 0 | 1606109.1632 | 0 | 0 | 0 | 968372.6135 | 1735208.9903 | 4514657.8525 | 3081346.7513 | 13780467.4155 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 31531386.6916 | 68690287.073 | 13335.2143 | 1.7344 | 18180.3946 | 39605.5059 | 370.6319 | 807.4118
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2024 | 6.5549 | 0.52428 | 4 | 15743.3909 | 33462.2914 | 320.9503 | 682.1741 | 65.0549 | 8.4521 | 63.9008 | 2084410.3145 | 0 | 1822719.3841 | 0 | 0 | 0 | 1021454.0383 | 1922147.6574 | 5001033.9179 | 3413308.41 | 15265073.7223 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 33015992.9984 | 70174893.3798 | 17782.7941 | 2.0971 | 15743.3909 | 33462.2914 | 320.9503 | 682.1741
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.0381 | 7.499 | 0.61503 | 4 | 13942.475 | 29047.0318 | 284.2362 | 592.163 | 64.8378 | 8.3614 | 65.9174 | 2270264.985 | 0 | 2022369.6624 | 0 | 0 | 0 | 1050528.0197 | 2083833.4402 | 5421707.1583 | 3700426.5405 | 16549129.8061 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 34300049.0822 | 71458949.4636 | 23713.7371 | 2.4601 | 13942.475 | 29047.0318 | 284.2362 | 592.163
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.9575 | 8.3513 | 0.70063 | 4 | 12614.1254 | 25873.191 | 257.156 | 527.46 | 64.5897 | 8.2676 | 71.0353 | 2427056.8964 | 0 | 2197504.9072 | 0 | 0 | 0 | 1058059.1242 | 2216222.1619 | 5766155.4555 | 3935519.581 | 17600518.1262 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 35351437.4023 | 72510337.7836 | 31622.7766 | 2.8025 | 12614.1254 | 25873.191 | 257.156 | 527.46
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.7197 | 9.084 | 0.77726 | 4 | 11634.5006 | 23586.4114 | 237.185 | 480.8409 | 64.3392 | 8.1784 | 68.4217 | 2553860.7423 | 0 | 2344530.6036 | 0 | 0 | 0 | 1049181.6555 | 2319553.4706 | 6035002.3246 | 4119013.0934 | 18421141.8901 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 36172061.1662 | 73330961.5475 | 42169.6503 | 3.109 | 11634.5006 | 23586.4114 | 237.185 | 480.8409
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3151 | 9.6935 | 0.8431 | 4 | 10911.1282 | 21929.6959 | 222.4381 | 447.0665 | 64.1057 | 8.0982 | 73.9751 | 2653944.8399 | 0 | 2464599.1387 | 0 | 0 | 0 | 1030662.9563 | 2398190.7046 | 6239600.2769 | 4258655.3999 | 19045653.3163 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 36796572.5924 | 73955472.9738 | 56234.1325 | 3.3724 | 10911.1282 | 21929.6959 | 222.4381 | 447.0665
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7929 | 10.1838 | 0.89769 | 4 | 10375.8566 | 20724.2814 | 211.5259 | 422.4925 | 63.9017 | 8.0299 | 64.0443 | 2730911.1915 | 0 | 2559731.4974 | 0 | 0 | 0 | 1007350.5982 | 2456217.382 | 6390573.7885 | 4361697.9238 | 19506482.3815 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 37257401.6576 | 74416302.0389 | 74989.4209 | 3.5908 | 10375.8566 | 20724.2814 | 211.5259 | 422.4925
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.3466 | 10.5742 | 0.94198 | 4 | 9978.8426 | 19840.722 | 203.4322 | 404.48 | 63.7291 | 7.9732 | 78.9437 | 2790020.3826 | 0 | 2634662.1753 | 0 | 0 | 0 | 983798.3842 | 2499307.5674 | 6502685.6119 | 4438216.547 | 19848690.6683 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 37599609.9444 | 74758510.3258 | 100000 | 3.7679 | 9978.8426 | 19840.722 | 203.4322 | 404.48
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1265 | 10.8805 | 0.97722 | 4 | 9683.7176 | 19190.0235 | 197.4157 | 391.2146 | 63.5874 | 7.9272 | 71.4832 | 2835043.7631 | 0 | 2692944.6667 | 0 | 0 | 0 | 962103.4333 | 2531135.8266 | 6585496.2135 | 4494736.4841 | 20101460.3873 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 37852379.6634 | 75011280.0447 | 133352.1432 | 3.9089 | 9683.7176 | 19190.0235 | 197.4157 | 391.2146
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.2434 | 11.1145 | 1.0047 | 4 | 9463.908 | 18710.2047 | 192.9346 | 381.4328 | 63.4756 | 7.8913 | 81.7974 | 2868610.7975 | 0 | 2737135.6463 | 0 | 0 | 0 | 942801.6693 | 2553933.7641 | 6644811.7704 | 4535220.5705 | 20282514.218 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38033433.4941 | 75192333.8755 | 177827.941 | 4.0188 | 9463.908 | 18710.2047 | 192.9346 | 381.4328
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8855 | 11.2962 | 1.0261 | 4 | 9299.9334 | 18353.6296 | 189.5917 | 374.1636 | 63.3866 | 7.8629 | 63.7475 | 2894223.8278 | 0 | 2771307.9307 | 0 | 0 | 0 | 926956.2729 | 2571070.3323 | 6689397.6055 | 4565651.3191 | 20418607.2884 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38169526.5645 | 75328426.9458 | 237137.3706 | 4.1043 | 9299.9334 | 18353.6296 | 189.5917 | 374.1636
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1151 | 11.4326 | 1.0424 | 4 | 9177.4571 | 18089.2798 | 187.0949 | 368.7744 | 63.3186 | 7.8413 | 80.2698 | 2913156.3379 | 0 | 2796832.7645 | 0 | 0 | 0 | 913806.7044 | 2583280.3647 | 6721165.6052 | 4587333.6317 | 20515575.4083 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38266494.6844 | 75425395.0658 | 316227.766 | 4.1696 | 9177.4571 | 18089.2798 | 187.0949 | 368.7744
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0554 | 11.537 | 1.0549 | 4 | 9085.8879 | 17892.065 | 185.2281 | 364.7539 | 63.2658 | 7.8246 | 87.1383 | 2927494.1521 | 0 | 2816319.0105 | 0 | 0 | 0 | 903450.2651 | 2592432.7368 | 6744978.2001 | 4603586.217 | 20588260.5816 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38339179.8577 | 75498080.239 | 421696.5034 | 4.2196 | 9085.8879 | 17892.065 | 185.2281 | 364.7539
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7741 | 11.6167 | 1.0644 | 4 | 9017.3755 | 17744.6523 | 183.8314 | 361.7487 | 63.225 | 7.8117 | 73.9792 | 2938369.1601 | 0 | 2831191.3907 | 0 | 0 | 0 | 895427.9714 | 2599345.5237 | 6762963.8535 | 4615861.795 | 20643159.6944 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38394078.9705 | 75552979.3519 | 562341.3252 | 4.2578 | 9017.3755 | 17744.6523 | 183.8314 | 361.7487
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3077 | 11.676 | 1.0716 | 4 | 8966.0854 | 17634.8175 | 182.7858 | 359.5096 | 63.1945 | 7.8021 | 74.7655 | 2946397.2916 | 0 | 2842222.9867 | 0 | 0 | 0 | 889101.8084 | 2604311.6138 | 6775884.6014 | 4624680.4709 | 20682598.7728 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38433518.0489 | 75592418.4303 | 749894.2093 | 4.2865 | 8966.0854 | 17634.8175 | 182.7858 | 359.5096
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.7144 | 11.7213 | 1.0771 | 4 | 8927.6721 | 17552.5284 | 182.0027 | 357.832 | 63.1711 | 7.7947 | 85.385 | 2952490.1116 | 0 | 2850625.3957 | 0 | 0 | 0 | 884298.5889 | 2608091.4975 | 6785719.0834 | 4631392.707 | 20712617.3842 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38463536.6603 | 75622437.0416 | 1000000 | 4.3084 | 8927.6721 | 17552.5284 | 182.0027 | 357.832
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.0265 | 11.7559 | 1.0812 | 4 | 8898.8937 | 17490.7536 | 181.416 | 356.5727 | 63.153 | 7.789 | 71.9887 | 2957149.7803 | 0 | 2857069.1323 | 0 | 0 | 0 | 880702.631 | 2611019.402 | 6793336.8903 | 4636592.0168 | 20735869.8527 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38486789.1288 | 75645689.5102 | 1333521.4322 | 4.3249 | 8898.8937 | 17490.7536 | 181.416 | 356.5727
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.248 | 11.7806 | 1.0843 | 4 | 8877.3282 | 17444.936 | 180.9763 | 355.6386 | 63.1402 | 7.785 | 83.4118 | 2960448.4737 | 0 | 2861640.4772 | 0 | 0 | 0 | 877808.5763 | 2612960.0356 | 6798386.0208 | 4640038.1521 | 20751281.7357 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38502201.0118 | 75661101.3931 | 1778279.41 | 4.3371 | 8877.3282 | 17444.936 | 180.9763 | 355.6386
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.4138 | 11.7991 | 1.0866 | 4 | 8861.1652 | 17410.6399 | 180.6468 | 354.9394 | 63.1305 | 7.782 | 78.9747 | 2962912.5817 | 0 | 2865060.412 | 0 | 0 | 0 | 875608.8737 | 2614396.9283 | 6802124.5208 | 4642589.7551 | 20762693.0716 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38513612.3477 | 75672512.729 | 2371373.7057 | 4.3463 | 8861.1652 | 17410.6399 | 180.6468 | 354.9394
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5575 | 11.815 | 1.0884 | 4 | 8849.0494 | 17384.3165 | 180.3998 | 354.4028 | 63.1221 | 7.7793 | 85.9343 | 2965046.3796 | 0 | 2868025.1369 | 0 | 0 | 0 | 874178.7419 | 2615827.6008 | 6805846.8372 | 4645130.3125 | 20774055.0088 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38524974.2849 | 75683874.6663 | 3162277.6602 | 4.3536 | 8849.0494 | 17384.3165 | 180.3998 | 354.4028
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.6501 | 11.8253 | 1.0897 | 4 | 8839.9666 | 17365.089 | 180.2147 | 354.0108 | 63.1167 | 7.7777 | 85.0037 | 2966419.4285 | 0 | 2869934.8723 | 0 | 0 | 0 | 872915.2424 | 2616615.1219 | 6807895.8056 | 4646528.7756 | 20780309.2464 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38531228.5225 | 75690128.9039 | 4216965.0343 | 4.3588 | 8839.9666 | 17365.089 | 180.2147 | 354.0108
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7233 | 11.8335 | 1.0907 | 4 | 8833.157 | 17350.5586 | 180.0759 | 353.7146 | 63.1124 | 7.7763 | 75.8967 | 2967503.3978 | 0 | 2871443.4461 | 0 | 0 | 0 | 872007.817 | 2617272.3177 | 6809605.6944 | 4647695.8098 | 20785528.4828 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38536447.7589 | 75695348.1402 | 5623413.2519 | 4.3627 | 8833.157 | 17350.5586 | 180.0759 | 353.7146
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7692 | 11.8387 | 1.0914 | 4 | 8828.0514 | 17339.9569 | 179.9718 | 353.4985 | 63.1097 | 7.7755 | 72.4642 | 2968183.6285 | 0 | 2872390.7322 | 0 | 0 | 0 | 871217.7849 | 2617598.9368 | 6810455.4902 | 4648275.813 | 20788122.3857 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38539041.6618 | 75697942.0432 | 7498942.0933 | 4.3655 | 8828.0514 | 17339.9569 | 179.9718 | 353.4985
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.8157 | 11.8438 | 1.092 | 4 | 8824.2232 | 17331.6193 | 179.8937 | 353.3285 | 63.107 | 7.7746 | 82.0999 | 2968871.7598 | 0 | 2873349.114 | 0 | 0 | 0 | 870768.1594 | 2618065.723 | 6811669.972 | 4649104.7217 | 20791829.4499 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 38542748.726 | 75701649.1073 | 10000000 | 4.3678 | 8824.2232 | 17331.6193 | 179.8937 | 353.3285
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.6972 | [19 empty] | 100 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.9654 | [19 empty] | 133.3521 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | -0.026814 | 0.0006551 | 4 | 7159268.0708 | 21731001.479 | 145951.3633 | 443015.8585 | 42.6246 | 6.7296 | 36.6264 | 67994.3789 | 0 | 24669.9302 | 0 | 0 | 0 | 67323.2655 | 62395.1541 | 162339.392 | 110799.9708 | 495522.0915 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 18760262.506 | 56944269.7539 | 177.8279 | 0.0026204 | 7159268.0708 | 21731001.479 | 145951.3633 | 443015.8585
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0059873 | 0.0021461 | 4 | 2228555.5563 | 6676629.5403 | 45432.1194 | 136112.124 | 50.0414 | 7.5172 | 21.6611 | 115657.7751 | 0 | 56634.8105 | 0 | 0 | 0 | 107326.8597 | 109051.5836 | 283729.8511 | 193651.4534 | 866052.3333 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 19130792.7478 | 57314799.9957 | 237.1374 | 0.0085844 | 2228555.5563 | 6676629.5403 | 45432.1194 | 136112.124
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.015144 | 0.0043194 | 4 | 1104692.2834 | 3314729.0748 | 22520.6464 | 67575.2357 | 50.0416 | 7.5173 | 20.7623 | 115658.8488 | 0 | 56634.2642 | 0 | 0 | 0 | 92983.4499 | 103457.8595 | 269176.1283 | 183718.2386 | 821628.7892 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 19086369.2037 | 57270376.4516 | 316.2278 | 0.017278 | 1104692.2834 | 3314729.0748 | 22520.6464 | 67575.2357
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.10773 | 0.0088628 | 4 | 555970.2897 | 1633058.9858 | 11334.2064 | 33292.1163 | 56.4159 | 8.1512 | 44.3027 | 196168.3887 | 0 | 112951.9372 | 0 | 0 | 0 | 157432.5156 | 181955.6082 | 473411.1682 | 323112.8499 | 1445032.4678 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 19709772.8823 | 57893780.1302 | 421.6965 | 0.035451 | 555970.2897 | 1633058.9858 | 11334.2064 | 33292.1163
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 0.19927 | 0.014646 | 4 | 343745.9179 | 995539.3936 | 7007.7255 | 20295.4171 | 59.0204 | 8.396 | 47.513 | 254604.4451 | 0 | 155257.0274 | 0 | 0 | 0 | 194842.4655 | 235834.5358 | 613593.0858 | 418789.8891 | 1872921.4487 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 20137661.8631 | 58321669.111 | 562.3413 | 0.058583 | 343745.9179 | 995539.3936 | 7007.7255 | 20295.4171
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0936 | 0.3223 | 0.022694 | 4 | 227348.1201 | 647979.0335 | 4634.7989 | 13209.9291 | 61.0442 | 8.5796 | 36.5792 | 323105.8818 | 0 | 206151.2785 | 0 | 0 | 0 | 237051.8306 | 298860.5064 | 777573.733 | 530710.0503 | 2373453.2806 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 20638193.695 | 58822200.943 | 749.8942 | 0.090778 | 227348.1201 | 647979.0335 | 4634.7989 | 13209.9291
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7371 | 0.48666 | 0.033686 | 4 | 157606.5945 | 440987.6494 | 3213.0236 | 8990.1297 | 62.6425 | 8.7198 | 48.9641 | 404768.1471 | 0 | 268424.3078 | 0 | 0 | 0 | 286323.4047 | 374211.1853 | 973620.7428 | 664516.1629 | 2971863.9506 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 21236604.365 | 59420611.613 | 1000 | 0.13474 | 157606.5945 | 440987.6494 | 3213.0236 | 8990.1297
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8325 | 0.70039 | 0.048473 | 4 | 113145.7384 | 310078.9447 | 2306.6289 | 6321.3787 | 63.8802 | 8.8247 | 36.1215 | 500521.5894 | 0 | 343364.4869 | 0 | 0 | 0 | 342147.7552 | 462553.1943 | 1203468.5288 | 821391.9997 | 3673447.5542 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 21938187.9686 | 60122195.2165 | 1333.5214 | 0.19389 | 113145.7384 | 310078.9447 | 2306.6289 | 6321.3787
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5561 | 0.98106 | 0.068218 | 4 | 83489.5435 | 223422.5351 | 1702.0473 | 4554.7706 | 64.8525 | 8.9037 | 45.6411 | 615098.8 | 0 | 435394.6161 | 0 | 0 | 0 | 408006.7139 | 568815.0507 | 1479940.082 | 1010089.5157 | 4517344.7785 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 22782085.1929 | 60966092.4408 | 1778.2794 | 0.27287 | 83489.5435 | 223422.5351 | 1702.0473 | 4554.7706
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0197 | 1.341 | 0.094293 | 4 | 63027.5473 | 164265.2172 | 1284.9018 | 3348.7686 | 65.5938 | 8.9599 | 49.4922 | 749386.8433 | 0 | 546100.1639 | 0 | 0 | 0 | 482695.1842 | 693491.0547 | 1804321.4696 | 1231486.4781 | 5507481.1938 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 23772221.6083 | 61956228.8562 | 2371.3737 | 0.37717 | 63027.5473 | 164265.2172 | 1284.9018 | 3348.7686
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3829 | 1.7972 | 0.12836 | 4 | 48543.1742 | 122911.5297 | 989.6183 | 2505.7178 | 66.1481 | 8.9963 | 53.1278 | 905573.6622 | 0 | 678262.9734 | 0 | 0 | 0 | 566285.9821 | 838547.8209 | 2181729.4201 | 1489075.1593 | 6659475.0179 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 24924215.4324 | 63108222.6803 | 3162.2777 | 0.51344 | 48543.1742 | 122911.5297 | 989.6183 | 2505.7178
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8345 | 2.3698 | 0.17233 | 4 | 38090.8532 | 93486.0099 | 776.5336 | 1905.8388 | 66.5489 | 9.0144 | 55.248 | 1086028.0292 | 0 | 835082.4935 | 0 | 0 | 0 | 659036.9681 | 1006257.5214 | 2618075.6588 | 1786890.4332 | 7991371.1041 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 26256111.5186 | 64440118.7665 | 4216.965 | 0.6893 | 38090.8532 | 93486.0099 | 776.5336 | 1905.8388
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4707 | 3.0705 | 0.22793 | 4 | 30442.0012 | 72323.5876 | 620.6014 | 1474.4142 | 66.8138 | 9.0131 | 47.8511 | 1289449.2451 | 0 | 1016833.1427 | 0 | 0 | 0 | 757607.0863 | 1194916.8949 | 3108928.6494 | 2121907.6853 | 9489642.7036 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 27754383.1181 | 65938390.366 | 5623.4133 | 0.91171 | 30442.0012 | 72323.5876 | 620.6014 | 1474.4142
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2929 | 3.9009 | 0.29631 | 4 | 24792.7945 | 57009.6008 | 505.4347 | 1162.2178 | 66.9555 | 8.9909 | 45.9375 | 1511869.7237 | 0 | 1221501.4899 | 0 | 0 | 0 | 856963.9783 | 1400230.7249 | 3643113.1193 | 2486499.5624 | 11120178.5984 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 29384919.0129 | 67568926.2608 | 7498.9421 | 1.1852 | 24792.7945 | 57009.6008 | 505.4347 | 1162.2178
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.1092 | 4.843 | 0.37715 | 4 | 20600.8576 | 45911.8231 | 419.9763 | 935.9746 | 66.9825 | 8.9462 | 55.3159 | 1744839.7466 | 0 | 1442817.7418 | 0 | 0 | 0 | 949433.3076 | 1613465.4104 | 4197906.0307 | 2865157.1243 | 12813619.3613 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 31078359.7758 | 69262367.0237 | 10000 | 1.5086 | 20600.8576 | 45911.8231 | 419.9763 | 935.9746
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.5265 | 5.8567 | 0.46804 | 4 | 17488.5927 | 37884.2135 | 356.5286 | 772.3209 | 66.9046 | 8.8794 | 64.2046 | 1976574.3084 | 0 | 1670737.9101 | 0 | 0 | 0 | 1026772.2682 | 1822892.9498 | 4742793.5287 | 3237054.038 | 14476825.0033 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 32741565.4178 | 70925572.6657 | 13335.2143 | 1.8722 | 17488.5927 | 37884.2135 | 356.5286 | 772.3209
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.9339 | 6.8774 | 0.56416 | 4 | 15183.1016 | 32103.9354 | 309.5281 | 654.4821 | 66.7392 | 8.7945 | 77.0271 | 2192706.206 | 0 | 1891405.3967 | 0 | 0 | 0 | 1081062.3537 | 2014417.843 | 5241102.0136 | 3577159.8181 | 15997853.6311 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 34262594.0456 | 72446601.2935 | 17782.7941 | 2.2566 | 15183.1016 | 32103.9354 | 309.5281 | 654.4821
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.787 | 7.8454 | 0.6597 | 4 | 13480.0862 | 27950.397 | 274.8098 | 569.8066 | 66.513 | 8.6988 | 78.0163 | 2383318.3531 | 0 | 2093748.1255 | 0 | 0 | 0 | 1110554.4886 | 2179172.1772 | 5669758.9954 | 3869727.0163 | 17306279.156 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 35571019.5705 | 73755026.8184 | 23713.7371 | 2.6388 | 13480.0862 | 27950.397 | 274.8098 | 569.8066
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.6501 | 8.7118 | 0.74916 | 4 | 12224.2217 | 24966.4551 | 249.2073 | 508.975 | 66.2583 | 8.6012 | 80.0644 | 2542790.1453 | 0 | 2269740.9431 | 0 | 0 | 0 | 1117550.8116 | 2312731.941 | 6017254.1039 | 4106899.5681 | 18366967.513 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 36631707.9275 | 74815715.1754 | 31622.7766 | 2.9966 | 12224.2217 | 24966.4551 | 249.2073 | 508.975
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.3593 | 9.4557 | 0.82893 | 4 | 11298.082 | 22814.1943 | 230.3267 | 465.0982 | 66.0024 | 8.5087 | 60.7664 | 2671783.2998 | 0 | 2417455.436 | 0 | 0 | 0 | 1108620.961 | 2417165.2817 | 6288968.2343 | 4292350.0453 | 19196343.258 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 37461083.6725 | 75645090.9204 | 42169.6503 | 3.3157 | 11298.082 | 22814.1943 | 230.3267 | 465.0982
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.8887 | 10.0723 | 0.89716 | 4 | 10614.1455 | 21254.38 | 216.3837 | 433.2993 | 65.7653 | 8.4262 | 69.1293 | 2773280.3906 | 0 | 2537658.5918 | 0 | 0 | 0 | 1090100.5023 | 2496405.399 | 6495134.7651 | 4433062.9389 | 19825642.5878 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 38090383.0022 | 76274390.2501 | 56234.1325 | 3.5886 | 10614.1455 | 21254.38 | 216.3837 | 433.2993
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.323 | 10.5691 | 0.95364 | 4 | 10107.9879 | 20118.0048 | 206.065 | 410.1327 | 65.5582 | 8.3558 | 70.3876 | 2851558.7624 | 0 | 2633127.8559 | 0 | 0 | 0 | 1067242.0256 | 2555252.1711 | 6648241.9949 | 4537561.7692 | 20292984.5791 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 38557724.9935 | 76741732.2415 | 74989.4209 | 3.8146 | 10107.9879 | 20118.0048 | 206.065 | 410.1327
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8157 | 10.9619 | 0.99927 | 4 | 9732.5176 | 19285.5194 | 198.4105 | 393.1614 | 65.3845 | 8.2979 | 79.3542 | 2911268.2043 | 0 | 2707778.8527 | 0 | 0 | 0 | 1043889.4278 | 2598545.2291 | 6760881.6511 | 4614440.6491 | 20636804.014 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 38901544.4285 | 77085551.6764 | 100000 | 3.9971 | 9732.5176 | 19285.5194 | 198.4105 | 393.1614
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5271 | 11.2679 | 1.0354 | 4 | 9453.3758 | 18672.8181 | 192.7199 | 380.6707 | 65.2432 | 8.2514 | 72.6251 | 2956437.7814 | 0 | 2765413.8494 | 0 | 0 | 0 | 1022234.6005 | 2630193.6302 | 6843224.2989 | 4670641.1982 | 20888145.3588 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39152885.7732 | 77336893.0211 | 133352.1432 | 4.1417 | 9453.3758 | 18672.8181 | 192.7199 | 380.6707
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6271 | 11.5053 | 1.0637 | 4 | 9245.4527 | 18219.4773 | 188.4811 | 371.4287 | 65.1299 | 8.2144 | 73.8517 | 2990711.2274 | 0 | 2809869.634 | 0 | 0 | 0 | 1003569.6375 | 2653618.6946 | 6904171.5112 | 4712238.9229 | 21074179.6275 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39338920.042 | 77522927.2899 | 177827.941 | 4.2549 | 9245.4527 | 18219.4773 | 188.4811 | 371.4287
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.2271 | 11.6866 | 1.0856 | 4 | 9090.336 | 17883.4832 | 185.3188 | 364.579 | 65.0413 | 8.1857 | 81.8499 | 3016407.0913 | 0 | 2843636.3381 | 0 | 0 | 0 | 987894.7295 | 2670695.8819 | 6948602.8498 | 4742564.2245 | 21209801.115 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39474541.5295 | 77658548.7774 | 237137.3706 | 4.3425 | 9090.336 | 17883.4832 | 185.3188 | 364.579
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4381 | 11.8241 | 1.1024 | 4 | 8974.4711 | 17633.8653 | 182.9567 | 359.4902 | 64.9729 | 8.1637 | 90.0251 | 3035614.3909 | 0 | 2869133.4952 | 0 | 0 | 0 | 975093.4874 | 2683138.1357 | 6980975.0417 | 4764658.9107 | 21308613.4615 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39573353.876 | 77757361.1239 | 316227.766 | 4.4095 | 8974.4711 | 17633.8653 | 182.9567 | 359.4902
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.364 | 11.9292 | 1.1152 | 4 | 8887.8426 | 17447.6089 | 181.1907 | 355.6931 | 64.9199 | 8.1467 | 83.6742 | 3050161.3521 | 0 | 2888596.0643 | 0 | 0 | 0 | 965027.4474 | 2692476.0969 | 7005270.5013 | 4781241.0611 | 21382772.5232 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39647512.9376 | 77831520.1856 | 421696.5034 | 4.4609 | 8887.8426 | 17447.6089 | 181.1907 | 355.6931
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.0628 | 12.0087 | 1.125 | 4 | 8823.0257 | 17308.654 | 179.8693 | 352.8603 | 64.8794 | 8.1337 | 92.2934 | 3061059.8193 | 0 | 2903265.698 | 0 | 0 | 0 | 957129.8844 | 2699367.6066 | 7023200.7961 | 4793478.8557 | 21437502.66 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39702243.0745 | 77886250.3224 | 562341.3252 | 4.4998 | 8823.0257 | 17308.654 | 179.8693 | 352.8603
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.577 | 12.0673 | 1.1323 | 4 | 8774.5017 | 17205.2562 | 178.8801 | 350.7524 | 64.8494 | 8.1241 | 90.8155 | 3069034.0708 | 0 | 2914048.5504 | 0 | 0 | 0 | 950848.7797 | 2704233.2464 | 7035860.1926 | 4802119.1539 | 21476143.9938 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39740884.4082 | 77924891.6562 | 749894.2093 | 4.5291 | 8774.5017 | 17205.2562 | 178.8801 | 350.7524
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9861 | 12.1137 | 1.1379 | 4 | 8738.1598 | 17127.2294 | 178.1392 | 349.1617 | 64.8254 | 8.1164 | 78.9036 | 3075353.7211 | 0 | 2922623.6181 | 0 | 0 | 0 | 946303.56 | 2708269.5507 | 7046361.8284 | 4809286.7361 | 21508199.0143 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39772939.4287 | 77956946.6767 | 1000000 | 4.5516 | 8738.1598 | 17127.2294 | 178.1392 | 349.1617
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2808 | 12.1473 | 1.1421 | 4 | 8710.9331 | 17069.2618 | 177.5842 | 347.98 | 64.808 | 8.1109 | 86.6706 | 3079890.041 | 0 | 2928795.671 | 0 | 0 | 0 | 942665.2416 | 2711026.8719 | 7053535.8126 | 4814183.1278 | 21530096.766 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39794837.1804 | 77978844.4284 | 1333521.4322 | 4.5684 | 8710.9331 | 17069.2618 | 177.5842 | 347.98
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5003 | 12.1724 | 1.1452 | 4 | 8690.5304 | 17025.9245 | 177.1682 | 347.0965 | 64.795 | 8.1068 | 74.7581 | 3083260.7972 | 0 | 2933390.9572 | 0 | 0 | 0 | 939875.1661 | 2713045.499 | 7058787.8663 | 4817767.7623 | 21546128.0482 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39810868.4627 | 77994875.7106 | 1778279.41 | 4.5809 | 8690.5304 | 17025.9245 | 177.1682 | 347.0965
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.6707 | 12.1917 | 1.1476 | 4 | 8675.2388 | 16993.2901 | 176.8565 | 346.4312 | 64.7849 | 8.1036 | 78.42 | 3085873.2053 | 0 | 2936957.6453 | 0 | 0 | 0 | 937831.0514 | 2714658.1418 | 7062983.632 | 4820631.4586 | 21558935.1345 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39823675.549 | 78007682.7969 | 2371373.7057 | 4.5905 | 8675.2388 | 16993.2901 | 176.8565 | 346.4312
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8 | 12.2064 | 1.1494 | 4 | 8663.7762 | 16968.7975 | 176.6228 | 345.9319 | 64.7772 | 8.1011 | 84.6677 | 3087852.8205 | 0 | 2939663.4895 | 0 | 0 | 0 | 936303.1155 | 2715889.576 | 7066187.5711 | 4822818.2129 | 21568714.7855 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39833455.1999 | 78017462.4479 | 3162277.6602 | 4.5977 | 8663.7762 | 16968.7975 | 176.6228 | 345.9319
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8876 | 12.2165 | 1.1507 | 4 | 8655.1831 | 16950.7409 | 176.4476 | 345.5638 | 64.772 | 8.0994 | 82.431 | 3089192.047 | 0 | 2941495.7191 | 0 | 0 | 0 | 935032.7609 | 2716631.0055 | 7068116.6187 | 4824134.8275 | 21574602.9786 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39839343.3931 | 78023350.641 | 4216965.0343 | 4.6029 | 8655.1831 | 16950.7409 | 176.4476 | 345.5638
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9607 | 12.2248 | 1.1518 | 4 | 8648.7406 | 16936.9736 | 176.3163 | 345.2831 | 64.7676 | 8.0981 | 77.5252 | 3090310.1938 | 0 | 2943026.2888 | 0 | 0 | 0 | 934168.8105 | 2717327.0643 | 7069927.6209 | 4825370.8738 | 21580130.8521 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39844871.2665 | 78028878.5145 | 5623413.2519 | 4.607 | 8648.7406 | 16936.9736 | 176.3163 | 345.2831
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.0191 | 12.2314 | 1.1525 | 4 | 8643.9103 | 16926.5455 | 176.2178 | 345.0705 | 64.7642 | 8.097 | 85.3404 | 3091201.4348 | 0 | 2944246.8193 | 0 | 0 | 0 | 933561.5917 | 2717913.8399 | 7071454.2905 | 4826412.8572 | 21584790.8334 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39849531.2478 | 78033538.4958 | 7498942.0933 | 4.6101 | 8643.9103 | 16926.5455 | 176.2178 | 345.0705
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.0534 | 12.2354 | 1.1531 | 4 | 8640.2885 | 16919.0254 | 176.144 | 344.9172 | 64.7621 | 8.0963 | 78.1614 | 3091724.381 | 0 | 2944963.3971 | 0 | 0 | 0 | 932987.1488 | 2718173.2215 | 7072129.1484 | 4826873.4615 | 21586850.7583 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 39851591.1728 | 78035598.4207 | 10000000 | 4.6123 | 8640.2885 | 16919.0254 | 176.144 | 344.9172
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.8011 | [19 empty] | 100 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.391 | [19 empty] | 133.3521 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | -0.027398 | 0.00069989 | 4 | 6898304.0865 | 20908591.9932 | 140631.2594 | 426249.9287 | 43.534 | 7.042 | 39.0013 | 72336.6388 | 0 | 26238.0778 | 0 | 0 | 0 | 71871.3019 | 66473.9472 | 172951.5749 | 118043.0037 | 527914.5441 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 19312336.1878 | 58535221.5159 | 177.8279 | 0.0027996 | 6898304.0865 | 20908591.9932 | 140631.2594 | 426249.9287
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.004448 | 0.0023736 | 4 | 2071104.6295 | 6202229.5301 | 42222.2692 | 126440.8381 | 50.6463 | 7.7952 | 21.3773 | 118236.5909 | 0 | 56614.3223 | 0 | 0 | 0 | 109155.903 | 110762.6583 | 288181.7164 | 196689.943 | 879641.134 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 19664062.7777 | 58886948.1058 | 237.1374 | 0.0094945 | 2071104.6295 | 6202229.5301 | 42222.2692 | 126440.8381
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.01359 | 0.0045385 | 4 | 1080774.8291 | 3241362.9207 | 22033.0567 | 66079.5674 | 50.6464 | 7.7953 | 22.7339 | 118237.7041 | 0 | 56613.7617 | 0 | 0 | 0 | 94984.0632 | 105235.8563 | 273802.1113 | 186875.567 | 835749.0636 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 19620170.7073 | 58843056.0353 | 316.2278 | 0.018154 | 1080774.8291 | 3241362.9207 | 22033.0567 | 66079.5674
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9593 | 0.11674 | 0.0096514 | 4 | 526454.6122 | 1542449.2375 | 10732.4894 | 31444.914 | 57.8031 | 8.5023 | 35.1001 | 209044.3078 | 0 | 119318.0181 | 0 | 0 | 0 | 168714.3651 | 193859.9095 | 504383.7183 | 344252.2518 | 1539572.5706 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 20323994.2143 | 59546879.5423 | 421.6965 | 0.038605 | 526454.6122 | 1542449.2375 | 10732.4894 | 31444.914
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9728 | 0.21245 | 0.015941 | 4 | 325661.226 | 940773.3799 | 6639.0446 | 19178.9378 | 60.4407 | 8.7474 | 40.9464 | 269787.128 | 0 | 162770.2387 | 0 | 0 | 0 | 207204.0878 | 249506.9673 | 649165.948 | 443069.0985 | 1981503.4683 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 20765925.112 | 59988810.44 | 562.3413 | 0.063765 | 325661.226 | 940773.3799 | 6639.0446 | 19178.9378
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3 | 0.3439 | 0.024705 | 4 | 215548.3882 | 612464.5221 | 4394.2454 | 12485.9177 | 62.5548 | 8.9366 | 53.0018 | 342978.3324 | 0 | 216489.6517 | 0 | 0 | 0 | 252822.8688 | 316793.4326 | 824231.5284 | 562554.9544 | 2515870.7682 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 21300292.4119 | 60523177.7399 | 749.8942 | 0.098819 | 215548.3882 | 612464.5221 | 4394.2454 | 12485.9177
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0077 | 0.51832 | 0.036662 | 4 | 149558.5995 | 417018.2051 | 3048.9543 | 8501.4802 | 64.2093 | 9.0797 | 47.3718 | 429517.042 | 0 | 281681.6197 | 0 | 0 | 0 | 305285.804 | 396428.9416 | 1031426.7874 | 703969.9761 | 3148310.1708 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 21932731.8145 | 61155617.1425 | 1000 | 0.14665 | 149558.5995 | 417018.2051 | 3048.9543 | 8501.4802
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2003 | 0.74656 | 0.052758 | 4 | 107475.4234 | 293339.4103 | 2191.0319 | 5980.1207 | 65.4987 | 9.1872 | 39.1047 | 531696.9705 | 0 | 360682.7685 | 0 | 0 | 0 | 365548.1472 | 490591.8756 | 1276419.4261 | 871182.4861 | 3896121.674 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 22680543.3177 | 61903428.6457 | 1333.5214 | 0.21103 | 107475.4234 | 293339.4103 | 2191.0319 | 5980.1207
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0165 | 1.0431 | 0.074209 | 4 | 79394.1096 | 211530.8505 | 1618.5563 | 4312.3425 | 66.4999 | 9.2669 | 46.6848 | 652531.9725 | 0 | 456558.6405 | 0 | 0 | 0 | 435043.335 | 602212.2397 | 1566832.717 | 1069395.5246 | 4782574.4292 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 23566996.0729 | 62789881.4009 | 1778.2794 | 0.29684 | 79394.1096 | 211530.8505 | 1618.5563 | 4312.3425
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.6117 | 1.4247 | 0.10253 | 4 | 60010.619 | 155644.9329 | 1223.3976 | 3173.0325 | 67.2673 | 9.3236 | 54.0595 | 794746.496 | 0 | 572361.8968 | 0 | 0 | 0 | 514550.4461 | 733846.9472 | 1909319.2238 | 1303149.6028 | 5827974.6127 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 24612396.2564 | 63835281.5844 | 2371.3737 | 0.41013 | 60010.619 | 155644.9329 | 1223.3976 | 3173.0325
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1406 | 1.9083 | 0.13951 | 4 | 46284.158 | 116569.5839 | 943.5652 | 2376.4286 | 67.841 | 9.36 | 49.9822 | 960172.2721 | 0 | 710630.6968 | 0 | 0 | 0 | 603638.1121 | 887032.0216 | 2307875.3649 | 1575172.3586 | 7044520.8261 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 25828942.4698 | 65051827.7978 | 3162.2777 | 0.55805 | 46284.158 | 116569.5839 | 943.5652 | 2376.4286
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7554 | 2.5112 | 0.1871 | 4 | 36375.3222 | 88785.5473 | 741.5601 | 1810.0135 | 68.2525 | 9.3768 | 60.8586 | 1149870.6289 | 0 | 873470.093 | 0 | 0 | 0 | 701081.3256 | 1062524.5985 | 2764471.0515 | 1886808.2969 | 8438225.9942 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 27222647.6379 | 66445532.966 | 4216.965 | 0.74838 | 36375.3222 | 88785.5473 | 741.5601 | 1810.0135
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.589 | 3.2485 | 0.24716 | 4 | 29122.4408 | 68796.4042 | 593.7003 | 1402.5078 | 68.5238 | 9.3734 | 55.6571 | 1363753.2812 | 0 | 1062244.2809 | 0 | 0 | 0 | 804899.6052 | 1260049.8952 | 3278391.3556 | 2237569.4644 | 10006907.8825 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 28791329.5262 | 68014214.8542 | 5623.4133 | 0.98863 | 29122.4408 | 68796.4042 | 593.7003 | 1402.5078
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.6204 | 4.1199 | 0.32078 | 4 | 23765.3564 | 54333.8527 | 484.4889 | 1107.6691 | 68.6666 | 9.3479 | 54.1788 | 1596980.2697 | 0 | 1274287.0981 | 0 | 0 | 0 | 909261.0724 | 1474406.0917 | 3836102.2082 | 2618218.5811 | 11709255.3212 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 30493676.9649 | 69716562.2929 | 7498.9421 | 1.2831 | 23765.3564 | 54333.8527 | 484.4889 | 1107.6691
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.6265 | 5.1038 | 0.40741 | 4 | 19790.9238 | 43859.1465 | 403.4648 | 894.128 | 68.6899 | 9.2987 | 62.2861 | 1840082.4051 | 0 | 1502526.3954 | 0 | 0 | 0 | 1005741.8199 | 1695856.7419 | 4412271.3745 | 3011465.8762 | 13467944.613 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 32252366.2567 | 71475251.5847 | 10000 | 1.6297 | 19790.9238 | 43859.1465 | 403.4648 | 894.128
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.1607 | 6.1533 | 0.50415 | 4 | 16841.3902 | 36291.2501 | 343.3345 | 739.8462 | 68.6048 | 9.2268 | 67.516 | 2079816.1713 | 0 | 1735615.4525 | 0 | 0 | 0 | 1085098.2669 | 1911206.6573 | 4972567.68 | 3393879.6177 | 15178183.8457 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 33962605.4894 | 73185490.8174 | 13335.2143 | 2.0166 | 16841.3902 | 36291.2501 | 343.3345 | 739.8462
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.642 | 7.2055 | 0.60584 | 4 | 14657.5492 | 30842.9451 | 298.814 | 628.7752 | 68.4302 | 9.1365 | 69.8711 | 2302492.4134 | 0 | 1960405.2102 | 0 | 0 | 0 | 1140584.9459 | 2107358.2021 | 5482913.7633 | 3742201.3061 | 16735955.841 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 35520377.4847 | 74743262.8127 | 17782.7941 | 2.4234 | 14657.5492 | 30842.9451 | 298.814 | 628.7752
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.5017 | 8.1965 | 0.70622 | 4 | 13045.0283 | 26929.8113 | 265.9405 | 549.0006 | 68.1952 | 9.0358 | 71.6023 | 2497593.9222 | 0 | 2165195.8776 | 0 | 0 | 0 | 1170201.998 | 2274866.8012 | 5918736.7773 | 4039659.4684 | 18066254.8446 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 36850676.4883 | 76073561.8163 | 23713.7371 | 2.8249 | 13045.0283 | 26929.8113 | 265.9405 | 549.0006
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.3286 | 9.0787 | 0.79967 | 4 | 11856.1259 | 24118.4104 | 241.7032 | 491.6864 | 67.9333 | 8.9342 | 78.1879 | 2660059.5565 | 0 | 2342460.7626 | 0 | 0 | 0 | 1176922.1895 | 2409982.5784 | 6270280.3135 | 4279595.1554 | 19139300.5559 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 37923722.1996 | 77146607.5276 | 31622.7766 | 3.1987 | 11856.1259 | 24118.4104 | 241.7032 | 491.6864
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.9787 | 9.8332 | 0.88256 | 4 | 10979.3787 | 22089.8989 | 223.8295 | 450.3325 | 67.6723 | 8.8385 | 74.9445 | 2791029.522 | 0 | 2490691.1256 | 0 | 0 | 0 | 1167703.3552 | 2515275.3611 | 6544230.5357 | 4466571.8111 | 19975501.7107 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 38759923.3544 | 77982808.6824 | 42169.6503 | 3.5302 | 10979.3787 | 22089.8989 | 223.8295 | 450.3325
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.446 | 10.4569 | 0.95321 | 4 | 10331.8549 | 20618.8787 | 210.6288 | 420.3437 | 67.4316 | 8.7535 | 82.8736 | 2893915.0296 | 0 | 2611065.7561 | 0 | 0 | 0 | 1149107.1927 | 2595094.3116 | 6751903.0717 | 4608312.5842 | 20609397.9459 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 39393819.5896 | 78616704.9176 | 56234.1325 | 3.8129 | 10331.8549 | 20618.8787 | 210.6288 | 420.3437
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.813 | 10.9575 | 1.0115 | 4 | 9852.5779 | 19546.9599 | 200.8581 | 398.4912 | 67.2227 | 8.6815 | 82.8234 | 2973013.865 | 0 | 2706321.3713 | 0 | 0 | 0 | 1126214.8557 | 2654164.5359 | 6905591.6783 | 4713208.2162 | 21078514.5224 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 39862936.1661 | 79085821.4941 | 74989.4209 | 4.0459 | 9852.5779 | 19546.9599 | 200.8581 | 398.4912
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.2554 | 11.3536 | 1.0585 | 4 | 9496.9979 | 18760.9766 | 193.6091 | 382.4679 | 67.0475 | 8.6222 | 88.4796 | 3033443.6358 | 0 | 2780884.4911 | 0 | 0 | 0 | 1103105.7011 | 2697799.1929 | 7019120.1053 | 4790693.7004 | 21425046.8266 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40209468.4703 | 79432353.7983 | 100000 | 4.2339 | 9496.9979 | 18760.9766 | 193.6091 | 382.4679
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.9233 | 11.6616 | 1.0956 | 4 | 9232.6117 | 18182.3212 | 188.2193 | 370.6712 | 66.9054 | 8.5748 | 78.0847 | 3079110.1843 | 0 | 2838366.0598 | 0 | 0 | 0 | 1081726.9129 | 2729689.2312 | 7102091.4434 | 4847323.3435 | 21678307.1752 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40462728.8189 | 79685614.1469 | 133352.1432 | 4.3826 | 9232.6117 | 18182.3212 | 188.2193 | 370.6712
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.9714 | 11.8987 | 1.1246 | 4 | 9035.6612 | 17754.6007 | 184.2042 | 361.9515 | 66.7925 | 8.5374 | 79.8307 | 3113475.5627 | 0 | 2882319.2514 | 0 | 0 | 0 | 1063124.4004 | 2752978.4937 | 7162685.327 | 4888679.9142 | 21863262.9495 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40647684.5932 | 79870569.9212 | 177827.941 | 4.4986 | 9035.6612 | 17754.6007 | 184.2042 | 361.9515
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.5501 | 12.0816 | 1.1471 | 4 | 8888.7201 | 17436.8445 | 181.2086 | 355.4737 | 66.7033 | 8.5081 | 86.8442 | 3139556.5249 | 0 | 2916101.3733 | 0 | 0 | 0 | 1047822.3939 | 2770357.3139 | 7207901.4524 | 4919540.8488 | 22001279.9072 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40785701.5509 | 80008586.8789 | 237137.3706 | 4.5885 | 8888.7201 | 17436.8445 | 181.2086 | 355.4737
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.7487 | 12.2208 | 1.1643 | 4 | 8778.9568 | 17200.5988 | 178.9709 | 350.6575 | 66.6343 | 8.4856 | 80.6748 | 3159117.2141 | 0 | 2941690.4874 | 0 | 0 | 0 | 1035391.4 | 2783117.6496 | 7241101.2282 | 4942200.378 | 22102618.3573 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40887040.001 | 80109925.329 | 316227.766 | 4.6574 | 8778.9568 | 17200.5988 | 178.9709 | 350.6575
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.6501 | 12.3256 | 1.1775 | 4 | 8696.8874 | 17024.7677 | 177.2978 | 347.0729 | 66.5816 | 8.4684 | 86.2085 | 3173692.8283 | 0 | 2960904.4 | 0 | 0 | 0 | 1025431.0735 | 2792411.0377 | 7265280.7179 | 4958703.3765 | 22176423.434 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 40960845.0777 | 80183730.4057 | 421696.5034 | 4.7098 | 8696.8874 | 17024.7677 | 177.2978 | 347.0729
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.3345 | 12.4052 | 1.1874 | 4 | 8635.4802 | 16893.438 | 176.0459 | 344.3956 | 66.5412 | 8.4553 | 82.9044 | 3184680.7929 | 0 | 2975473.8317 | 0 | 0 | 0 | 1017683.5002 | 2799356.8687 | 7283352.3453 | 4971037.6336 | 22231584.9723 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41016006.616 | 80238891.9441 | 562341.3252 | 4.7497 | 8635.4802 | 16893.438 | 176.0459 | 344.3956
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8487 | 12.465 | 1.195 | 4 | 8589.5081 | 16795.3712 | 175.1087 | 342.3964 | 66.5106 | 8.4454 | 80.1168 | 3192891.2806 | 0 | 2986409.2102 | 0 | 0 | 0 | 1011661.6124 | 2804475.2203 | 7296669.2461 | 4980126.692 | 22272233.2617 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41056654.9053 | 80279540.2334 | 749894.2093 | 4.7799 | 8589.5081 | 16795.3712 | 175.1087 | 342.3964
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.236 | 12.5102 | 1.2007 | 4 | 8555.077 | 16722.0283 | 174.4068 | 340.9012 | 66.4875 | 8.4379 | 85.4275 | 3199050.5701 | 0 | 2994640.4354 | 0 | 0 | 0 | 1007040.0652 | 2808285.1176 | 7306581.8175 | 4986892.2257 | 22302490.2315 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41086911.8752 | 80309797.2032 | 1000000 | 4.8026 | 8555.077 | 16722.0283 | 174.4068 | 340.9012
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5332 | 12.5447 | 1.205 | 4 | 8529.2817 | 16666.9589 | 173.8809 | 339.7785 | 66.4696 | 8.4321 | 84.5986 | 3203763.899 | 0 | 3000955.4817 | 0 | 0 | 0 | 1003590.1037 | 2811240.6989 | 7314271.6338 | 4992140.6833 | 22325962.5003 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41110384.144 | 80333269.472 | 1333521.4322 | 4.8199 | 8529.2817 | 16666.9589 | 173.8809 | 339.7785
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7501 | 12.57 | 1.2082 | 4 | 8509.9515 | 16625.9278 | 173.4869 | 338.942 | 66.4565 | 8.4279 | 83.7315 | 3207194.3409 | 0 | 3005560.7689 | 0 | 0 | 0 | 1000883.1294 | 2813318.9133 | 7319678.7213 | 4995831.1317 | 22342467.0056 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41126888.6492 | 80349773.9773 | 1778279.41 | 4.8328 | 8509.9515 | 16625.9278 | 173.4869 | 338.942
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9157 | 12.5893 | 1.2106 | 4 | 8495.4637 | 16595.1128 | 173.1915 | 338.3138 | 66.4465 | 8.4246 | 82.9506 | 3209809.1018 | 0 | 3009076.0862 | 0 | 0 | 0 | 998867.8754 | 2814923.6947 | 7323854.0334 | 4998680.868 | 22355211.6596 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41139633.3032 | 80362518.6313 | 2371373.7057 | 4.8425 | 8495.4637 | 16595.1128 | 173.1915 | 338.3138
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.0324 | 12.603 | 1.2124 | 4 | 8484.6036 | 16572.2575 | 172.9701 | 337.8479 | 66.4394 | 8.4224 | 81.9531 | 3211648.9855 | 0 | 3011552.4565 | 0 | 0 | 0 | 997247.0501 | 2815974.9119 | 7326589.085 | 5000547.5968 | 22363560.0859 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41147981.7296 | 80370867.0576 | 3162277.6602 | 4.8497 | 8484.6036 | 16572.2575 | 172.9701 | 337.8479
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.125 | 12.6138 | 1.2138 | 4 | 8476.4621 | 16554.977 | 172.8041 | 337.4956 | 66.4338 | 8.4205 | 79.1985 | 3213107.9739 | 0 | 3013517.6369 | 0 | 0 | 0 | 996089.8234 | 2816859.0193 | 7328889.3511 | 5002117.5758 | 22370581.3804 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41155003.0241 | 80377888.3521 | 4216965.0343 | 4.8552 | 8476.4621 | 16554.977 | 172.8041 | 337.4956
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1982 | 12.6223 | 1.2148 | 4 | 8470.3583 | 16541.9139 | 172.6797 | 337.2293 | 66.4294 | 8.4191 | 77.0724 | 3214259.8122 | 0 | 3015070.0176 | 0 | 0 | 0 | 995265.4062 | 2817592.1421 | 7330796.786 | 5003419.4393 | 22376403.6033 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41160825.247 | 80383710.575 | 5623413.2519 | 4.8594 | 8470.3583 | 16541.9139 | 172.6797 | 337.2293
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.2519 | 12.6286 | 1.2156 | 4 | 8465.7818 | 16532.1574 | 172.5864 | 337.0304 | 66.4261 | 8.4181 | 70.7421 | 3215104.9391 | 0 | 3016209.6052 | 0 | 0 | 0 | 994630.005 | 2818118.3742 | 7332165.9341 | 5004353.911 | 22380582.7685 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41165004.4122 | 80387889.7402 | 7498942.0933 | 4.8625 | 8465.7818 | 16532.1574 | 172.5864 | 337.0304
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.2908 | 12.6331 | 1.2162 | 4 | 8462.3503 | 16524.8853 | 172.5165 | 336.8821 | 66.4237 | 8.4173 | 76.6034 | 3215716.6252 | 0 | 3017034.7351 | 0 | 0 | 0 | 994134.4466 | 2818485.4647 | 7333121.0282 | 5005005.7823 | 22383498.082 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 41167919.7257 | 80390805.0537 | 10000000 | 4.8648 | 8462.3503 | 16524.8853 | 172.5165 | 336.8821
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.4554 | [19 empty] | 100 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6391 | [19 empty] | 133.3521 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0109 | -0.02806 | 0.00074994 | 4 | 6623138.234 | 20049367.9206 | 135021.6314 | 408733.4838 | 44.3694 | 7.3466 | 32.4817 | 76408.2199 | 0 | 27603.6354 | 0 | 0 | 0 | 76114.0662 | 70249.1094 | 182773.7725 | 124746.8553 | 557895.6586 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 19867858.6224 | 60143393.244 | 177.8279 | 0.0029998 | 6623138.234 | 20049367.9206 | 135021.6314 | 408733.4838
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0029118 | 0.0025947 | 4 | 1946518.5514 | 5827003.311 | 39682.4135 | 118791.3441 | 51.23 | 8.0716 | 21.8282 | 120754.5305 | 0 | 56577.6972 | 0 | 0 | 0 | 110969.8682 | 112437.8174 | 292540.1367 | 199664.6544 | 892944.7044 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 20202907.6682 | 60478442.2898 | 237.1374 | 0.010379 | 1946518.5514 | 5827003.311 | 39682.4135 | 118791.3441
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.012037 | 0.0047512 | 4 | 1060755.4596 | 3179976.1999 | 21624.9348 | 64828.1161 | 51.2301 | 8.0717 | 23.1845 | 120755.6828 | 0 | 56577.1226 | 0 | 0 | 0 | 96963.9566 | 106975.7372 | 278328.9244 | 189965.21 | 849566.6336 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 20159529.5973 | 60435064.219 | 316.2278 | 0.019005 | 1060755.4596 | 3179976.1999 | 21624.9348 | 64828.1161
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0714 | 0.12497 | 0.010492 | 4 | 498902.3761 | 1458593.0502 | 10170.7998 | 29735.3922 | 59.1426 | 8.849 | 37.7739 | 221264.2948 | 0 | 125112.7783 | 0 | 0 | 0 | 179112.669 | 204940.9994 | 533214.4413 | 363929.8127 | 1627574.9955 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 20937537.9593 | 61213072.5809 | 421.6965 | 0.041967 | 498902.3761 | 1458593.0502 | 10170.7998 | 29735.3922
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.136 | 0.22744 | 0.017331 | 4 | 308841.5771 | 889805.1968 | 6296.1533 | 18139.8825 | 61.8984 | 9.1021 | 49.0882 | 286281.5895 | 0 | 171092.6083 | 0 | 0 | 0 | 220840.3762 | 264503.6839 | 688184.3283 | 469699.9448 | 2100602.5309 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 21410565.4947 | 61686100.1164 | 562.3413 | 0.069325 | 308841.5771 | 889805.1968 | 6296.1533 | 18139.8825
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5191 | 0.36728 | 0.026854 | 4 | 204591.6338 | 579534.4563 | 4170.8772 | 11814.5938 | 64.0852 | 9.2954 | 54.859 | 363973.3552 | 0 | 227468.5741 | 0 | 0 | 0 | 269585.7426 | 335800.7921 | 873684.7787 | 596307.8139 | 2666821.0567 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 21976784.0205 | 62252318.6421 | 749.8942 | 0.10742 | 204591.6338 | 579534.4563 | 4170.8772 | 11814.5938
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2829 | 0.55137 | 0.039833 | 4 | 142090.9909 | 394866.3397 | 2896.717 | 8049.8844 | 65.7848 | 9.4402 | 53.7104 | 455048.9478 | 0 | 295290.1543 | 0 | 0 | 0 | 324763.638 | 419290.0686 | 1090906.7503 | 744566.273 | 3329865.832 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 22639828.7957 | 62915363.4174 | 1000 | 0.15933 | 142090.9909 | 394866.3397 | 2896.717 | 8049.8844
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5681 | 0.79411 | 0.057313 | 4 | 102214.6214 | 277898.4849 | 2083.7833 | 5665.3365 | 67.123 | 9.55 | 46.254 | 563585.6519 | 0 | 378234.0556 | 0 | 0 | 0 | 389277.0406 | 519127.7318 | 1350663.8703 | 921855.8449 | 4122744.1951 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 23432707.1589 | 63708241.7805 | 1333.5214 | 0.22925 | 102214.6214 | 277898.4849 | 2083.7833 | 5665.3365
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.477 | 1.107 | 0.08057 | 4 | 75593.3805 | 200563.2767 | 1541.0733 | 4088.7537 | 68.1538 | 9.6306 | 52.6599 | 690814.3523 | 0 | 478006.2974 | 0 | 0 | 0 | 462435.7497 | 636189.9958 | 1655235.8685 | 1129732.492 | 5052414.7557 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 24362377.7195 | 64637912.3411 | 1778.2794 | 0.32228 | 75593.3805 | 200563.2767 | 1541.0733 | 4088.7537
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1964 | 1.5101 | 0.11126 | 4 | 57209.1352 | 147703.9397 | 1166.2856 | 3011.1446 | 68.9466 | 9.6878 | 58.5212 | 840856.191 | 0 | 598746.66 | 0 | 0 | 0 | 546505.8324 | 774582.3865 | 2015304.481 | 1375486.7186 | 6151482.2694 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 25461445.2332 | 65736979.8548 | 2371.3737 | 0.44506 | 57209.1352 | 147703.9397 | 1166.2856 | 3011.1446
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8936 | 2.0222 | 0.15132 | 4 | 44184.6871 | 110723.7019 | 900.7646 | 2257.2524 | 69.5407 | 9.7239 | 40.863 | 1015839.8348 | 0 | 743288.0453 | 0 | 0 | 0 | 641281.1523 | 936159.5227 | 2435695.0453 | 1662411.9169 | 7434675.5174 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 26744638.4811 | 67020173.1028 | 3162.2777 | 0.60529 | 44184.6871 | 110723.7019 | 900.7646 | 2257.2524
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6982 | 2.6586 | 0.20277 | 4 | 34779.2312 | 84435.077 | 709.0217 | 1721.3233 | 69.9645 | 9.7395 | 48.4539 | 1215864.2253 | 0 | 912993.9922 | 0 | 0 | 0 | 744411.8174 | 1120575.3136 | 2915507.1045 | 1989893.5065 | 8899245.9595 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 28209208.9233 | 68484743.5449 | 4216.965 | 0.81109 | 34779.2312 | 84435.077 | 709.0217 | 1721.3233
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.7286 | 3.4335 | 0.26753 | 4 | 27893.1599 | 65530.0818 | 568.6398 | 1335.9194 | 70.2416 | 9.7338 | 61.7986 | 1440338.9058 | 0 | 1108836.5499 | 0 | 0 | 0 | 853420.7572 | 1327012.523 | 3452614.3772 | 2356480.2566 | 10538703.3698 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 29848666.3336 | 70124200.9552 | 5623.4133 | 1.0701 | 27893.1599 | 65530.0818 | 568.6398 | 1335.9194
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.9575 | 4.3459 | 0.34661 | 4 | 22806.7541 | 51856.205 | 464.9465 | 1057.1589 | 70.385 | 9.7048 | 65.4142 | 1684186.5704 | 0 | 1328022.7493 | 0 | 0 | 0 | 962409.1252 | 1550101.1935 | 4033045.3359 | 2752636.3126 | 12310401.2867 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 31620364.2505 | 71895898.8722 | 7498.9421 | 1.3864 | 22806.7541 | 51856.205 | 464.9465 | 1057.1589
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.1487 | 5.372 | 0.43926 | 4 | 19033.9097 | 41956.0838 | 388.032 | 855.3315 | 70.4042 | 9.6509 | 60.4393 | 1937413.1387 | 0 | 1563135.7764 | 0 | 0 | 0 | 1062743.8548 | 1779684.1803 | 4630373.1736 | 3160324.8356 | 14133674.9594 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 33443637.9232 | 73719172.5448 | 10000 | 1.7571 | 19033.9097 | 41956.0838 | 388.032 | 855.3315
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8003 | 6.4581 | 0.54205 | 4 | 16235.1886 | 34810.8354 | 330.9763 | 709.666 | 70.3113 | 9.5736 | 58.7036 | 2185186.038 | 0 | 1801440.8547 | 0 | 0 | 0 | 1144051.8326 | 2000964.7029 | 5206099.7026 | 3553270.0216 | 15891013.1523 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 35200976.1161 | 75476510.7378 | 13335.2143 | 2.1682 | 16235.1886 | 34810.8354 | 330.9763 | 709.666
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.3445 | 7.5409 | 0.64941 | 4 | 14164.03 | 29668.7751 | 288.7529 | 604.8381 | 70.1274 | 9.4777 | 70.3495 | 2414132.5226 | 0 | 2030110.9797 | 0 | 0 | 0 | 1200400.8008 | 2201411.2782 | 5727620.5744 | 3909218.7328 | 17482894.8885 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 36792857.8523 | 77068392.4739 | 17782.7941 | 2.5976 | 14164.03 | 29668.7751 | 288.7529 | 604.8381
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.1996 | 8.5538 | 0.75468 | 4 | 12635.2749 | 25977.2715 | 257.5872 | 529.5818 | 69.8838 | 9.3722 | 71.9633 | 2613407.4686 | 0 | 2237074.9304 | 0 | 0 | 0 | 1229803.7812 | 2371311.6103 | 6169666.3871 | 4210924.0831 | 18832188.2607 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 38142151.2245 | 78417685.8461 | 23713.7371 | 3.0187 | 12635.2749 | 25977.2715 | 257.5872 | 529.5818
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.9876 | 9.4515 | 0.85213 | 4 | 11508.3218 | 23324.4579 | 234.6127 | 475.5006 | 69.615 | 9.2664 | 73.7385 | 2778726.3424 | 0 | 2415521.6237 | 0 | 0 | 0 | 1236087.7314 | 2507830.922 | 6524861.6322 | 4453352.1365 | 19916380.3881 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 39226343.3519 | 79501877.9735 | 31622.7766 | 3.4085 | 11508.3218 | 23324.4579 | 234.6127 | 475.5006
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.577 | 10.216 | 0.93817 | 4 | 10677.256 | 21409.7501 | 217.6703 | 436.4667 | 69.349 | 9.1676 | 84.9877 | 2911543.3626 | 0 | 2564185.7065 | 0 | 0 | 0 | 1226428.3829 | 2613841.4063 | 6800679.1665 | 4641603.2711 | 20758281.2958 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 40068244.2595 | 80343778.8812 | 42169.6503 | 3.7527 | 10677.256 | 21409.7501 | 217.6703 | 436.4667
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9755 | 10.8459 | 1.0112 | 4 | 10063.4056 | 20020.6861 | 205.1561 | 408.1488 | 69.1053 | 9.0803 | 72.3051 | 3015606.678 | 0 | 2684543.0434 | 0 | 0 | 0 | 1207527.9861 | 2693994.3059 | 7009220.5697 | 4783937.0639 | 21394829.647 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 40704792.6108 | 80980327.2324 | 56234.1325 | 4.0448 | 10063.4056 | 20020.6861 | 205.1561 | 408.1488
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.2823 | 11.3509 | 1.0713 | 4 | 9608.9868 | 19007.7963 | 195.8922 | 387.4996 | 68.8943 | 9.0066 | 76.2533 | 3095576.9415 | 0 | 2779697.9695 | 0 | 0 | 0 | 1184598.3851 | 2753350.5854 | 7163653.4335 | 4889340.6667 | 21866217.9816 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 41176180.9454 | 81451715.567 | 74989.4209 | 4.2852 | 9608.9868 | 19007.7963 | 195.8922 | 387.4996
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.6781 | 11.7505 | 1.1197 | 4 | 9271.8008 | 18264.5281 | 189.0182 | 372.3471 | 68.7176 | 8.946 | 79.528 | 3156729.2812 | 0 | 2854217.9065 | 0 | 0 | 0 | 1161682.0507 | 2797325.403 | 7278066.8882 | 4967430.2005 | 22215451.73 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 41525414.6938 | 81800949.3154 | 100000 | 4.4787 | 9271.8008 | 18264.5281 | 189.0182 | 372.3471
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3038 | 12.0605 | 1.1579 | 4 | 9021.0601 | 17717.2236 | 183.9065 | 361.1896 | 68.5747 | 8.8976 | 96.1132 | 3202863.7014 | 0 | 2911545.8142 | 0 | 0 | 0 | 1140502.3807 | 2829415.6395 | 7361559.1012 | 5024415.3514 | 22470301.9884 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 41780264.9522 | 82055799.5738 | 133352.1432 | 4.6314 | 9021.0601 | 17717.2236 | 183.9065 | 361.1896
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3138 | 12.2985 | 1.1876 | 4 | 8834.2563 | 17312.6845 | 180.0983 | 352.9425 | 68.4617 | 8.8597 | 84.1727 | 3237500.9022 | 0 | 2955263.7374 | 0 | 0 | 0 | 1122064.4381 | 2852783.3403 | 7422357.0651 | 5065911.2111 | 22655880.6942 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 41965843.658 | 82241378.2796 | 177827.941 | 4.7504 | 8834.2563 | 17312.6845 | 180.0983 | 352.9425
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.8607 | 12.4818 | 1.2106 | 4 | 8694.8752 | 17012.1216 | 177.2568 | 346.8151 | 68.3725 | 8.83 | 80.4731 | 3263757.6625 | 0 | 2988814.7939 | 0 | 0 | 0 | 1106917.1212 | 2870200.9353 | 7467674.0745 | 5096841.0012 | 22794205.5886 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42104168.5524 | 82379703.174 | 237137.3706 | 4.8424 | 8694.8752 | 17012.1216 | 177.2568 | 346.8151
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.025 | 12.6202 | 1.2282 | 4 | 8590.7534 | 16788.9122 | 175.1341 | 342.2647 | 68.3041 | 8.8073 | 78.0038 | 3283288.648 | 0 | 3014012.6303 | 0 | 0 | 0 | 1094502.8965 | 2882803.6282 | 7500463.6961 | 5119220.5917 | 22894292.0907 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42204255.0545 | 82479789.6762 | 316227.766 | 4.9128 | 8590.7534 | 16788.9122 | 175.1341 | 342.2647
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9265 | 12.7272 | 1.2417 | 4 | 8512.8991 | 16621.9455 | 173.547 | 338.8608 | 68.2505 | 8.7896 | 83.4068 | 3298274.9263 | 0 | 3033491.2854 | 0 | 0 | 0 | 1084934.639 | 2892513.3317 | 7525726.3531 | 5136462.8742 | 22971403.4097 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42281366.3735 | 82556900.9951 | 421696.5034 | 4.9667 | 8512.8991 | 16621.9455 | 173.547 | 338.8608
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5844 | 12.8056 | 1.2518 | 4 | 8454.6442 | 16498.0297 | 172.3594 | 336.3347 | 68.2109 | 8.7765 | 85.7848 | 3309136.261 | 0 | 3047689.4986 | 0 | 0 | 0 | 1077135.05 | 2899244.7157 | 7543240.0335 | 5148416.321 | 23024861.8798 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42334824.8436 | 82610359.4652 | 562341.3252 | 5.0073 | 8454.6442 | 16498.0297 | 172.3594 | 336.3347
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.101 | 12.867 | 1.2596 | 4 | 8411.0311 | 16404.8107 | 171.4702 | 334.4343 | 68.1796 | 8.7662 | 73.4835 | 3317621.0854 | 0 | 3058828.8671 | 0 | 0 | 0 | 1071385.4111 | 2904655.7918 | 7557318.5434 | 5158025.1932 | 23067834.892 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42377797.8558 | 82653332.4774 | 749894.2093 | 5.0384 | 8411.0311 | 16404.8107 | 171.4702 | 334.4343
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4734 | 12.9114 | 1.2654 | 4 | 8378.3664 | 16335.5871 | 170.8043 | 333.023 | 68.1569 | 8.7588 | 77.943 | 3323713.9913 | 0 | 3066854.7625 | 0 | 0 | 0 | 1066749.0714 | 2908353.9518 | 7566940.3972 | 5164592.3062 | 23097204.4805 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42407167.4443 | 82682702.0659 | 1000000 | 5.0615 | 8378.3664 | 16335.5871 | 170.8043 | 333.023
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7707 | 12.9467 | 1.2698 | 4 | 8353.8942 | 16283.2713 | 170.3054 | 331.9565 | 68.1387 | 8.7528 | 76.4086 | 3328562.8636 | 0 | 3073257.64 | 0 | 0 | 0 | 1063442.4901 | 2911452.5675 | 7575002.3597 | 5170094.7612 | 23121812.6822 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42431775.6459 | 82707310.2676 | 1333521.4322 | 5.0793 | 8353.8942 | 16283.2713 | 170.3054 | 331.9565
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.983 | 12.9721 | 1.2731 | 4 | 8335.5553 | 16244.4306 | 169.9316 | 331.1647 | 68.1256 | 8.7485 | 77.914 | 3332016.629 | 0 | 3077827.2335 | 0 | 0 | 0 | 1060780.2242 | 2913543.3938 | 7580442.2609 | 5173807.6055 | 23138417.347 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42448380.3108 | 82723914.9325 | 1778279.41 | 5.0924 | 8335.5553 | 16244.4306 | 169.9316 | 331.1647
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.1339 | 12.9902 | 1.2755 | 4 | 8321.8104 | 16215.5864 | 169.6514 | 330.5767 | 68.1163 | 8.7455 | 70.9262 | 3334468.6414 | 0 | 3081076.0406 | 0 | 0 | 0 | 1058652.3569 | 2914936.8452 | 7584067.7354 | 5176282.0664 | 23149483.686 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42459446.6498 | 82734981.2715 | 2371373.7057 | 5.1022 | 8321.8104 | 16215.5864 | 169.6514 | 330.5767
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2628 | 13.0055 | 1.2775 | 4 | 8311.5071 | 16193.5172 | 169.4413 | 330.1268 | 68.1084 | 8.7429 | 85.4766 | 3336560.3722 | 0 | 3083850.101 | 0 | 0 | 0 | 1057252.3917 | 2916288.5173 | 7587584.5089 | 5178682.3366 | 23160218.2277 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42470181.1915 | 82745715.8131 | 3162277.6602 | 5.1098 | 8311.5071 | 16193.5172 | 169.4413 | 330.1268
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3554 | 13.0165 | 1.2789 | 4 | 8303.7831 | 16177.1001 | 169.2839 | 329.7921 | 68.1026 | 8.741 | 82.3492 | 3338061.5238 | 0 | 3085842.6774 | 0 | 0 | 0 | 1056141.4771 | 2917217.8145 | 7590002.3498 | 5180332.5627 | 23167598.4054 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42477561.3692 | 82753095.9908 | 4216965.0343 | 5.1154 | 8303.7831 | 16177.1001 | 169.2839 | 329.7921
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.424 | 13.0246 | 1.2799 | 4 | 8297.9922 | 16164.8232 | 169.1658 | 329.5418 | 68.0984 | 8.7396 | 80.3884 | 3339171.534 | 0 | 3087316.9852 | 0 | 0 | 0 | 1055292.1915 | 2917894.4772 | 7591762.8872 | 5181534.1656 | 23172972.2407 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42482935.2045 | 82758469.8261 | 5623413.2519 | 5.1197 | 8297.9922 | 16164.8232 | 169.1658 | 329.5418
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.4823 | 13.0315 | 1.2807 | 4 | 8293.6503 | 16155.4179 | 169.0773 | 329.35 | 68.0948 | 8.7385 | 73.0759 | 3340116.2234 | 0 | 3088572.1835 | 0 | 0 | 0 | 1054744.8665 | 2918538.9767 | 7593439.7426 | 5182678.6539 | 23178090.6466 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42488053.6104 | 82763588.232 | 7498942.0933 | 5.123 | 8293.6503 | 16155.4179 | 169.0773 | 329.35
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.5166 | 13.0357 | 1.2813 | 4 | 8290.3948 | 16148.6443 | 169.0109 | 329.212 | 68.0927 | 8.7378 | 78.993 | 3340670.5367 | 0 | 3089309.1161 | 0 | 0 | 0 | 1054207.8061 | 2918833.1089 | 7594205.0145 | 5183200.9677 | 23180426.5499 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 42490389.5137 | 82765924.1354 | 10000000 | 5.1253 | 8290.3948 | 16148.6443 | 169.0109 | 329.212
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4487 | [19 empty] | 100 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0593 | [19 empty] | 133.3521 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5141 | [19 empty] | 177.8279 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0013798 | 0.0028095 | 4 | 1846202.5044 | 5525017.0747 | 37637.3352 | 112634.9462 | 51.7932 | 8.3465 | 22.6964 | 123214.1134 | 0 | 56525.7525 | 0 | 0 | 0 | 112769.8673 | 114078.796 | 296809.6263 | 202578.6688 | 905976.8242 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 20747341.199 | 62089296.3278 | 237.1374 | 0.011238 | 1846202.5044 | 5525017.0747 | 37637.3352 | 112634.9462
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.010485 | 0.0049577 | 4 | 1044060.503 | 3128804.6178 | 21284.5856 | 63784.9142 | 51.7934 | 8.3466 | 22.771 | 123215.3045 | 0 | 56525.1645 | 0 | 0 | 0 | 98924.5603 | 108679.3614 | 282761.4052 | 192990.4692 | 863096.2652 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 20704460.6399 | 62046415.7687 | 316.2278 | 0.019831 | 1044060.503 | 3128804.6178 | 21284.5856 | 63784.9142
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2003 | 0.13477 | 0.011395 | 4 | 473195.7385 | 1380231.3842 | 9646.7352 | 28137.8837 | 60.5395 | 9.2012 | 49.2391 | 234826.8746 | 0 | 131738.9249 | 0 | 0 | 0 | 190868.9406 | 217399.5487 | 565629.0308 | 386053.436 | 1726516.7556 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 21567881.1304 | 62909836.2592 | 421.6965 | 0.045579 | 473195.7385 | 1380231.3842 | 9646.7352 | 28137.8837
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3166 | 0.24437 | 0.018821 | 4 | 293188.8123 | 842339.4621 | 5977.0505 | 17172.2293 | 63.3942 | 9.4603 | 43.0535 | 304172.6657 | 0 | 180262.0681 | 0 | 0 | 0 | 235848.787 | 280910.5731 | 730871.6885 | 498834.9453 | 2230900.7277 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 22072265.1024 | 63414220.2312 | 562.3413 | 0.075283 | 293188.8123 | 842339.4621 | 5977.0505 | 17172.2293
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.736 | 0.39118 | 0.029141 | 4 | 194408.1281 | 549084.8443 | 3963.2726 | 11193.8372 | 65.6172 | 9.6542 | 56.6124 | 385308.887 | 0 | 238504.4428 | 0 | 0 | 0 | 286446.6106 | 355001.3768 | 923640.7615 | 630403.7987 | 2819305.8774 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 22660670.2522 | 64002625.3809 | 749.8942 | 0.11656 | 194408.1281 | 549084.8443 | 3963.2726 | 11193.8372
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5756 | 0.58701 | 0.043217 | 4 | 135153.77 | 374307.5456 | 2755.2924 | 7630.7656 | 67.3786 | 9.8022 | 50.8037 | 482017.6833 | 0 | 309733.2186 | 0 | 0 | 0 | 345499.3596 | 443527.6019 | 1153967.8402 | 787606.7626 | 3522352.4662 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 23363716.8409 | 64705671.9697 | 1000 | 0.17287 | 135153.77 | 374307.5456 | 2755.2924 | 7630.7656
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.936 | 0.84305 | 0.062147 | 4 | 97327.5949 | 263633.7197 | 1984.1547 | 5374.53 | 68.7534 | 9.9132 | 50.8379 | 596181.392 | 0 | 396015.5746 | 0 | 0 | 0 | 413323.3964 | 548152.9416 | 1426181.5123 | 973398.1873 | 4353253.0041 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 24194617.3789 | 65536572.5076 | 1333.5214 | 0.24859 | 97327.5949 | 263633.7197 | 1984.1547 | 5374.53
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9593 | 1.1749 | 0.087344 | 4 | 72061.4094 | 190391.8503 | 1469.0693 | 3881.3954 | 69.8202 | 9.9951 | 35.4184 | 730876.0365 | 0 | 500469.99 | 0 | 0 | 0 | 491227.569 | 671803.7023 | 1747895.4274 | 1192974.5449 | 5335247.2701 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 25176611.6448 | 66518566.7736 | 1778.2794 | 0.34938 | 72061.4094 | 190391.8503 | 1469.0693 | 3881.3954
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.8102 | 1.6009 | 0.12056 | 4 | 54604.1658 | 140333.6704 | 1113.1798 | 2860.8917 | 70.6377 | 10.0526 | 46.0392 | 889128.2267 | 0 | 626402.7264 | 0 | 0 | 0 | 580130.4755 | 817307.9572 | 2126467.6516 | 1451357.8668 | 6490794.9041 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 26332159.2788 | 67674114.4076 | 2371.3737 | 0.48224 | 54604.1658 | 140333.6704 | 1113.1798 | 2860.8917
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6487 | 2.1395 | 0.16382 | 4 | 42230.8374 | 105320.3705 | 860.9327 | 2147.0982 | 71.2477 | 10.0882 | 45.3448 | 1072812.1082 | 0 | 776437.9854 | 0 | 0 | 0 | 679471.1952 | 986201.3026 | 2565893.4917 | 1751275.0319 | 7832091.115 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 27673455.4898 | 69015410.6185 | 3162.2777 | 0.65529 | 42230.8374 | 105320.3705 | 860.9327 | 2147.0982
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6534 | 2.8115 | 0.21937 | 4 | 33292.2539 | 80406.9781 | 678.7076 | 1639.205 | 71.6845 | 10.1025 | 47.8726 | 1283718.3977 | 0 | 953389.7263 | 0 | 0 | 0 | 788711.16 | 1180069.5207 | 3070298.8274 | 2095542.038 | 9371729.6701 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 29213094.0449 | 70555049.1737 | 4216.965 | 0.87747 | 33292.2539 | 80406.9781 | 678.7076 | 1639.205
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8734 | 3.6242 | 0.28903 | 4 | 26746.4501 | 62505.7641 | 545.2626 | 1274.2645 | 71.9669 | 10.0942 | 60.7986 | 1518731.1797 | 0 | 1156179.0196 | 0 | 0 | 0 | 902667.2272 | 1395255.1963 | 3630167.8146 | 2477664.126 | 11080664.5634 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 30922028.9382 | 72263984.0669 | 5623.4133 | 1.1561 | 26746.4501 | 62505.7641 | 545.2626 | 1274.2645
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.305 | 4.5789 | 0.37384 | 4 | 21911.2124 | 49558.0333 | 446.6897 | 1010.3075 | 72.1106 | 10.0614 | 63.453 | 1773507.5694 | 0 | 1382721.8936 | 0 | 0 | 0 | 1016431.7829 | 1627337.8859 | 4233999.3663 | 2889791.5675 | 12923790.0656 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 32765154.4403 | 74107109.5691 | 7498.9421 | 1.4954 | 21911.2124 | 49558.0333 | 446.6897 | 1010.3075
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6567 | 5.6456 | 0.47267 | 4 | 18325.4705 | 40191.7702 | 373.5895 | 819.3636 | 72.1252 | 10.0028 | 63.8056 | 2036305.8488 | 0 | 1624155.3836 | 0 | 0 | 0 | 1119919.5272 | 1864348.4963 | 4850652.3568 | 3310669.9045 | 14806051.5172 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 34647415.8919 | 75989371.0207 | 10000 | 1.8907 | 18325.4705 | 40191.7702 | 373.5895 | 819.3636
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.425 | 6.7688 | 0.58168 | 4 | 15666.7111 | 33435.0775 | 319.3871 | 681.6193 | 72.0245 | 9.9199 | 63.1855 | 2292166.3502 | 0 | 1867713.0253 | 0 | 0 | 0 | 1203141.0543 | 2091577.9676 | 5441856.83 | 3714179.1055 | 16610634.3328 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 36451998.7076 | 77793953.8364 | 13335.2143 | 2.3267 | 15666.7111 | 33435.0775 | 319.3871 | 681.6193
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.0112 | 7.8804 | 0.69477 | 4 | 13700.0706 | 28576.3002 | 279.2945 | 582.5665 | 71.8316 | 9.8186 | 64.7097 | 2526887.0078 | 0 | 2099784.9252 | 0 | 0 | 0 | 1259824.6551 | 2295733.6694 | 5973028.088 | 4076714.4035 | 18231972.749 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 38073337.1237 | 79415292.2525 | 17782.7941 | 2.7791 | 13700.0706 | 28576.3002 | 279.2945 | 582.5665
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8781 | 8.917 | 0.80506 | 4 | 12248.9603 | 25087.0814 | 249.7116 | 511.4341 | 71.579 | 9.7078 | 65.7092 | 2730664.1867 | 0 | 2309300.0271 | 0 | 0 | 0 | 1289303.0119 | 2468414.218 | 6422307.454 | 4383356.8026 | 19603345.7003 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 39444710.075 | 80786665.2038 | 23713.7371 | 3.2202 | 12248.9603 | 25087.0814 | 249.7116 | 511.4341
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.6271 | 9.83 | 0.90656 | 4 | 11179.4008 | 22580.1218 | 227.9072 | 460.3263 | 71.3033 | 9.5979 | 68.8754 | 2898753.8898 | 0 | 2488897.4333 | 0 | 0 | 0 | 1295051.9227 | 2606254.2658 | 6780938.9835 | 4628130.1906 | 20698026.6857 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 40539391.0604 | 81881346.1892 | 31622.7766 | 3.6263 | 11179.4008 | 22580.1218 | 227.9072 | 460.3263
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1628 | 10.6052 | 0.99579 | 4 | 10390.6464 | 20769.8437 | 211.8274 | 423.4214 | 71.0323 | 9.4959 | 84.1484 | 3033467.2647 | 0 | 2638112.5299 | 0 | 0 | 0 | 1284968.5309 | 2713053.8469 | 7058809.5858 | 4817782.5864 | 21546194.3446 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 41387558.7194 | 82729513.8481 | 42169.6503 | 3.9832 | 10390.6464 | 20769.8437 | 211.8274 | 423.4214
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4977 | 11.2415 | 1.0712 | 4 | 9807.9834 | 19456.1285 | 199.949 | 396.6395 | 70.7854 | 9.4062 | 81.1253 | 3138710.1993 | 0 | 2758518.3349 | 0 | 0 | 0 | 1265727.7371 | 2793552.9458 | 7268251.7284 | 4960731.1523 | 22185492.0976 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 42026856.4724 | 83368811.6012 | 56234.1325 | 4.285 | 9807.9834 | 19456.1285 | 199.949 | 396.6395
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7413 | 11.7503 | 1.1331 | 4 | 9376.5882 | 18497.8489 | 191.1544 | 377.1037 | 70.5726 | 9.3309 | 85.7963 | 3219411.7476 | 0 | 2853461.5287 | 0 | 0 | 0 | 1242594.2573 | 2853032.3381 | 7423004.9064 | 5066353.3761 | 22657858.1542 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 42499222.5289 | 83841177.6577 | 74989.4209 | 4.5325 | 9376.5882 | 18497.8489 | 191.1544 | 377.1037
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0741 | 12.1513 | 1.1828 | 4 | 9056.4395 | 17794.6153 | 184.6278 | 362.7673 | 70.3954 | 9.2693 | 72.2288 | 3280927.0234 | 0 | 2927542.7712 | 0 | 0 | 0 | 1219516.27 | 2896914.5652 | 7537177.4597 | 5144278.4898 | 23006356.5793 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 42847720.954 | 84189676.0828 | 100000 | 4.7312 | 9056.4395 | 17794.6153 | 184.6278 | 362.7673
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6681 | 12.4643 | 1.222 | 4 | 8818.3384 | 17275.905 | 179.7738 | 352.1927 | 70.2513 | 9.2198 | 80.7671 | 3327670.0525 | 0 | 2984920.6184 | 0 | 0 | 0 | 1198612.7371 | 2929369.3291 | 7621618.098 | 5201910.9605 | 23264101.7955 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43105466.1702 | 84447421.299 | 133352.1432 | 4.8882 | 8818.3384 | 17275.905 | 179.7738 | 352.1927
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.6413 | 12.7032 | 1.2525 | 4 | 8640.9333 | 16892.7558 | 176.1571 | 344.3817 | 70.1381 | 9.1813 | 88.5323 | 3362556.6407 | 0 | 3028403.8733 | 0 | 0 | 0 | 1180279.7569 | 2952783.7056 | 7682537.5028 | 5243489.706 | 23450051.1853 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43291415.56 | 84633370.6888 | 177827.941 | 5.01 | 8640.9333 | 16892.7558 | 176.1571 | 344.3817
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.1519 | 12.8863 | 1.276 | 4 | 8508.5548 | 16608.2324 | 173.4584 | 338.5813 | 70.0493 | 9.1513 | 71.8536 | 3388876.1494 | 0 | 3061604.4345 | 0 | 0 | 0 | 1165156.8167 | 2970098.5863 | 7727587.2705 | 5274237.0981 | 23587560.3555 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43428924.7302 | 84770879.859 | 237137.3706 | 5.1041 | 8508.5548 | 16608.2324 | 173.4584 | 338.5813
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.3091 | 13.0267 | 1.2941 | 4 | 8409.6584 | 16396.2563 | 171.4423 | 334.2599 | 69.9801 | 9.128 | 83.9022 | 3408809.2015 | 0 | 3086985.6733 | 0 | 0 | 0 | 1153087.2998 | 2983064.0481 | 7761320.7425 | 5297260.886 | 23690527.8511 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43531892.2258 | 84873847.3546 | 316227.766 | 5.1764 | 8409.6584 | 16396.2563 | 171.4423 | 334.2599
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1787 | 13.1324 | 1.3078 | 4 | 8335.7082 | 16238.4492 | 169.9347 | 331.0428 | 69.9273 | 9.1104 | 70.9621 | 3423656.8511 | 0 | 3106029.1862 | 0 | 0 | 0 | 1143431.5533 | 2992515.8603 | 7785912.4191 | 5314045.2106 | 23765591.0806 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43606955.4553 | 84948910.5841 | 421696.5034 | 5.2313 | 8335.7082 | 16238.4492 | 169.9347 | 331.0428
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8413 | 13.2129 | 1.3183 | 4 | 8280.3729 | 16120.4792 | 168.8066 | 328.6378 | 69.8867 | 9.0968 | 86.5522 | 3434893.2025 | 0 | 3120520.9763 | 0 | 0 | 0 | 1135973.0181 | 2999641.0068 | 7804450.5887 | 5326697.8922 | 23822176.6846 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43663541.0593 | 85005496.1881 | 562341.3252 | 5.2731 | 8280.3729 | 16120.4792 | 168.8066 | 328.6378
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.336 | 13.2732 | 1.3262 | 4 | 8238.9446 | 16032.4573 | 167.962 | 326.8433 | 69.8562 | 9.0866 | 81.5335 | 3443240.8354 | 0 | 3131332.8791 | 0 | 0 | 0 | 1130141.43 | 3004838.9064 | 7817974.4571 | 5335928.2103 | 23863456.7183 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43704821.093 | 85046776.2218 | 749894.2093 | 5.3047 | 8238.9446 | 16032.4573 | 167.962 | 326.8433
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7038 | 13.318 | 1.3321 | 4 | 8207.9157 | 15966.7538 | 167.3295 | 325.5039 | 69.8333 | 9.079 | 89.6882 | 3449423.8067 | 0 | 3139366.6884 | 0 | 0 | 0 | 1125605.9791 | 3008614.6249 | 7827798.1023 | 5342633.05 | 23893442.2513 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43734806.626 | 85076761.7548 | 1000000 | 5.3284 | 8207.9157 | 15966.7538 | 167.3295 | 325.5039
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.9808 | 13.3518 | 1.3366 | 4 | 8184.6687 | 15917.5683 | 166.8555 | 324.5012 | 69.816 | 9.0733 | 95.9694 | 3454066.5721 | 0 | 3145413.6695 | 0 | 0 | 0 | 1122153.5239 | 3011437.1685 | 7835141.7818 | 5347645.2622 | 23915857.978 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43757222.3528 | 85099177.4816 | 1333521.4322 | 5.3462 | 8184.6687 | 15917.5683 | 166.8555 | 324.5012
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.2003 | 13.3785 | 1.34 | 4 | 8167.2479 | 15880.4153 | 166.5004 | 323.7437 | 69.8023 | 9.0687 | 81.0284 | 3457737.599 | 0 | 3150203.6258 | 0 | 0 | 0 | 1119687.4972 | 3013775.2016 | 7841224.8642 | 5351797.0909 | 23934425.8787 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43775790.2534 | 85117745.3822 | 1778279.41 | 5.3599 | 8167.2479 | 15880.4153 | 166.5004 | 323.7437
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.3512 | 13.3969 | 1.3425 | 4 | 8154.191 | 15852.9817 | 166.2342 | 323.1845 | 69.7928 | 9.0656 | 86.6889 | 3460257.7762 | 0 | 3153496.7689 | 0 | 0 | 0 | 1117629.6188 | 3015239.8239 | 7845035.511 | 5354397.9356 | 23946057.4343 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43787421.809 | 85129376.9378 | 2371373.7057 | 5.3699 | 8154.191 | 15852.9817 | 166.2342 | 323.1845
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4755 | 13.412 | 1.3444 | 4 | 8144.4034 | 15832.1156 | 166.0347 | 322.7591 | 69.785 | 9.063 | 91.7815 | 3462330.3564 | 0 | 3156207.595 | 0 | 0 | 0 | 1116225.5202 | 3016557.7539 | 7848464.4946 | 5356738.2873 | 23956524.0073 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43797888.3821 | 85139843.5108 | 3162277.6602 | 5.3777 | 8144.4034 | 15832.1156 | 166.0347 | 322.7591
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5681 | 13.4233 | 1.3459 | 4 | 8137.0659 | 15816.4972 | 165.8851 | 322.4407 | 69.7792 | 9.0611 | 90.1877 | 3463873.342 | 0 | 3158227.3932 | 0 | 0 | 0 | 1115157.5531 | 3017530.7324 | 7850995.9851 | 5358466.0817 | 23964251.0876 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43805615.4623 | 85147570.5911 | 4216965.0343 | 5.3835 | 8137.0659 | 15816.4972 | 165.8851 | 322.4407
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6413 | 13.4321 | 1.347 | 4 | 8131.5648 | 15804.6871 | 165.7729 | 322.1999 | 69.7746 | 9.0595 | 86.592 | 3465091.5157 | 0 | 3159822.9275 | 0 | 0 | 0 | 1114403.2693 | 3018333.9079 | 7853085.6829 | 5359892.3434 | 23970629.6467 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43811994.0215 | 85153949.1503 | 5623413.2519 | 5.3879 | 8131.5648 | 15804.6871 | 165.7729 | 322.1999
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6802 | 13.437 | 1.3477 | 4 | 8127.4402 | 15796.2858 | 165.6889 | 322.0287 | 69.7722 | 9.0587 | 87.4869 | 3465738.328 | 0 | 3160670.7596 | 0 | 0 | 0 | 1113618.0704 | 3018610.5916 | 7853805.5573 | 5360383.6724 | 23972826.9794 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43814191.3541 | 85156146.4829 | 7498942.0933 | 5.3909 | 8127.4402 | 15796.2858 | 165.6889 | 322.0287
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.7191 | 13.4417 | 1.3483 | 4 | 8124.3476 | 15789.7128 | 165.6258 | 321.8947 | 69.7697 | 9.0579 | 92.8943 | 3466385.3418 | 0 | 3161518.85 | 0 | 0 | 0 | 1113160.4434 | 3019015.2077 | 7854858.2854 | 5361102.181 | 23976040.3093 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 43817404.684 | 85159359.8128 | 10000000 | 5.3933 | 8124.3476 | 15789.7128 | 165.6258 | 321.8947
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0002 | [19 empty] | 100 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4886 | [19 empty] | 133.3521 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.012148 | 0.00012989 | 4 | 41094596.7586 | 122743595.6607 | 837768.9395 | 2502294.2205 | 52.3371 | 8.6204 | 25.1402 | 125621.3655 | 0 | 56457.4993 | 0 | 0 | 0 | 131999.7973 | 122490.6782 | 318695.6184 | 217516.3081 | 972781.2668 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 21351407.1434 | 63773553.9929 | 177.8279 | 0.00051957 | 41094596.7586 | 122743595.6607 | 837768.9395 | 2502294.2205
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.00014722 | 0.0030178 | 4 | 1764340.1082 | 5278721.1253 | 35968.4596 | 107613.8701 | 52.3366 | 8.6198 | 22.9879 | 125617.7261 | 0 | 56459.278 | 0 | 0 | 0 | 114556.9155 | 115687.2286 | 300994.4382 | 205434.8889 | 918750.4752 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 21297376.3518 | 63719523.2012 | 237.1374 | 0.012071 | 1764340.1082 | 5278721.1253 | 35968.4596 | 107613.8701
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0089372 | 0.0051578 | 4 | 1030230.2445 | 3086434.646 | 21002.637 | 62921.145 | 52.3368 | 8.62 | 24.3794 | 125618.9557 | 0 | 56458.6771 | 0 | 0 | 0 | 100867.1776 | 110348.476 | 287104.099 | 195954.447 | 876351.8323 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 21254977.7088 | 63677124.5583 | 316.2278 | 0.020631 | 1030230.2445 | 3086434.646 | 21002.637 | 62921.145
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.14475 | 0.012358 | 4 | 449201.7893 | 1307406.8897 | 9157.5861 | 26653.2578 | 61.9313 | 9.5528 | 39.7559 | 248541.8449 | 0 | 138360.3752 | 0 | 0 | 0 | 202645.2318 | 229923.5063 | 598213.7995 | 408293.2102 | 1825977.968 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 22204603.8445 | 64626750.694 | 421.6965 | 0.049431 | 449201.7893 | 1307406.8897 | 9157.5861 | 26653.2578
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4797 | 0.26036 | 0.020398 | 4 | 278610.6998 | 798531.7735 | 5679.856 | 16279.1503 | 64.8581 | 9.8156 | 51.4319 | 321395.1582 | 0 | 188808.995 | 0 | 0 | 0 | 249881.6273 | 296433.4544 | 771259.0416 | 526400.1437 | 2354178.4203 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 22732804.2968 | 65154951.1463 | 562.3413 | 0.081593 | 278610.6998 | 798531.7735 | 5679.856 | 16279.1503
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9601 | 0.41646 | 0.031574 | 4 | 184934.1478 | 520827.5023 | 3770.1327 | 10617.7731 | 67.1624 | 10.0141 | 59.1465 | 407501.5348 | 0 | 249972.9311 | 0 | 0 | 0 | 303991.911 | 374971.887 | 975599.9326 | 665867.0006 | 2977905.1972 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 23356531.0737 | 65778677.9232 | 749.8942 | 0.1263 | 184934.1478 | 520827.5023 | 3770.1327 | 10617.7731
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8554 | 0.62249 | 0.046796 | 4 | 128702.2466 | 355336.9646 | 2623.7694 | 7244.0247 | 68.9681 | 10.1638 | 56.4135 | 508913.0646 | 0 | 323876.9473 | 0 | 0 | 0 | 365767.1952 | 467437.3108 | 1216175.998 | 830065.1086 | 3712235.6244 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 24090861.5009 | 66513008.3504 | 1000 | 0.18718 | 128702.2466 | 355336.9646 | 2623.7694 | 7244.0247
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3038 | 0.89338 | 0.067271 | 4 | 92782.2302 | 250436.1385 | 1891.4913 | 5105.4794 | 70.3898 | 10.2768 | 57.0973 | 629478.2832 | 0 | 414024.5833 | 0 | 0 | 0 | 437676.8733 | 577660.0985 | 1502953.082 | 1025796.361 | 4587589.2813 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 24966215.1579 | 67388362.0073 | 1333.5214 | 0.26908 | 92782.2302 | 250436.1385 | 1891.4913 | 5105.4794
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4392 | 1.2444 | 0.094513 | 4 | 68775.0341 | 180987.7361 | 1402.0721 | 3689.6798 | 71.4925 | 10.3599 | 40.2276 | 771701.4292 | 0 | 523138.9064 | 0 | 0 | 0 | 520270.464 | 707893.2118 | 1841792.9283 | 1257061.5186 | 5621858.4582 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 26000484.3347 | 68422631.1842 | 1778.2794 | 0.37805 | 68775.0341 | 180987.7361 | 1402.0721 | 3689.6798
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.4339 | 1.6951 | 0.13041 | 4 | 52178.7327 | 133505.0653 | 1063.734 | 2721.6813 | 72.3372 | 10.4178 | 57.0795 | 938840.2092 | 0 | 654726.385 | 0 | 0 | 0 | 614614.6007 | 861190.666 | 2240641.4585 | 1529283.836 | 6839297.1554 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 27217923.032 | 69640069.8814 | 2371.3737 | 0.52163 | 52178.7327 | 133505.0653 | 1063.734 | 2721.6813
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4186 | 2.2615 | 0.17706 | 4 | 40410.0491 | 100308.9461 | 823.8135 | 2044.9335 | 72.9632 | 10.4527 | 47.459 | 1131553.4735 | 0 | 810461.1037 | 0 | 0 | 0 | 718713.678 | 1037684.0195 | 2699840.9606 | 1842696.9318 | 8240950.1672 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 28619576.0438 | 71041722.8932 | 3162.2777 | 0.70823 | 40410.0491 | 100308.9461 | 823.8135 | 2044.9335
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5935 | 2.9669 | 0.23684 | 4 | 31905.0634 | 76684.0001 | 650.4279 | 1563.3071 | 73.4109 | 10.4655 | 47.7496 | 1352501.2983 | 0 | 993865.0973 | 0 | 0 | 0 | 832973.1802 | 1239942.4345 | 3226075.8675 | 2201863.0688 | 9847220.9465 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 30225846.8231 | 72647993.6725 | 4216.965 | 0.94737 | 31905.0634 | 76684.0001 | 650.4279 | 1563.3071
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.0332 | 3.8214 | 0.31172 | 4 | 25675.3503 | 59697.8753 | 523.4267 | 1217.0219 | 73.6996 | 10.4546 | 55.2448 | 1599236.5041 | 0 | 1204536.2973 | 0 | 0 | 0 | 952962.2506 | 1465126.6703 | 3811959.0573 | 2601740.3845 | 11635561.1641 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 32014187.0406 | 74436333.8901 | 5623.4133 | 1.2469 | 25675.3503 | 59697.8753 | 523.4267 | 1217.0219
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.6519 | 4.8179 | 0.40246 | 4 | 21073.5056 | 47425.1558 | 429.6119 | 966.8259 | 73.8431 | 10.4179 | 48.0485 | 1864622.1331 | 0 | 1438093.4033 | 0 | 0 | 0 | 1071001.6885 | 1705749.7177 | 4438010.8681 | 3029033.6095 | 13546511.4201 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 33925137.2967 | 76347284.1461 | 7498.9421 | 1.6098 | 21073.5056 | 47425.1558 | 429.6119 | 966.8259
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.165 | 5.926 | 0.5077 | 4 | 17661.6666 | 38551.2056 | 360.057 | 785.9185 | 73.8529 | 10.3542 | 63.7932 | 2137117.9469 | 0 | 1685931.5902 | 0 | 0 | 0 | 1177641.5801 | 1950269.5357 | 5074201.2766 | 3463246.6357 | 15488408.565 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 35867034.4416 | 78289181.291 | 10000 | 2.0308 | 17661.6666 | 38551.2056 | 360.057 | 785.9185
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.0575 | 7.0878 | 0.62315 | 4 | 15132.9748 | 32152.0826 | 308.5062 | 655.4637 | 73.7439 | 10.2654 | 68.3536 | 2401300.8292 | 0 | 1934969.7266 | 0 | 0 | 0 | 1262919.241 | 2183684.0208 | 5681497.8869 | 3877739.0509 | 17342110.7555 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 37720736.6321 | 80142883.4815 | 13335.2143 | 2.4926 | 15132.9748 | 32152.0826 | 308.5062 | 655.4637
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.6897 | 8.2289 | 0.74211 | 4 | 13263.41 | 27554.3776 | 270.3926 | 561.7333 | 73.5416 | 10.1584 | 63.9522 | 2641836.1636 | 0 | 2170534.8169 | 0 | 0 | 0 | 1319919.4661 | 2391593.2741 | 6222435.1161 | 4246939.825 | 18993258.6617 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 39371884.5382 | 81794031.3877 | 17782.7941 | 2.9685 | 13263.41 | 27554.3776 | 270.3926 | 561.7333
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.5176 | 9.2837 | 0.8573 | 4 | 11884.3692 | 24255.1761 | 242.2789 | 494.4746 | 73.2814 | 10.043 | 63.261 | 2848881.7133 | 0 | 2381385.6528 | 0 | 0 | 0 | 1348277.5132 | 2565632.5029 | 6675249.489 | 4555994.9389 | 20375421.81 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 40754047.6866 | 83176194.536 | 23713.7371 | 3.4292 | 11884.3692 | 24255.1761 | 242.2789 | 494.4746
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.2519 | 10.2146 | 0.963 | 4 | 10868.0578 | 21881.1162 | 221.5601 | 446.0762 | 72.9981 | 9.9287 | 73.114 | 3020205.9404 | 0 | 2562670.5473 | 0 | 0 | 0 | 1353907.8664 | 2705345.8981 | 7038755.0842 | 4804094.9769 | 21484980.3135 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 41863606.19 | 84285753.0395 | 31622.7766 | 3.852 | 10868.0578 | 21881.1162 | 221.5601 | 446.0762
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.7124 | 10.9978 | 1.0553 | 4 | 10118.5502 | 20168.1511 | 206.2803 | 411.155 | 72.7231 | 9.8237 | 67.1625 | 3156285.9105 | 0 | 2711903.5673 | 0 | 0 | 0 | 1342900.6153 | 2812325.1363 | 7317093.1175 | 4994066.4039 | 22334574.7508 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 42713200.6274 | 85135347.4768 | 42169.6503 | 4.2213 | 10118.5502 | 20168.1511 | 206.2803 | 411.155
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.9787 | 11.6398 | 1.1332 | 4 | 9564.8147 | 18924.1005 | 194.9917 | 385.7934 | 72.4735 | 9.7319 | 72.8601 | 3262541.403 | 0 | 2832206.7344 | 0 | 0 | 0 | 1323148.4421 | 2892979.666 | 7526939.6592 | 5137290.9806 | 22975106.8853 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 43353732.7619 | 85775879.6113 | 56234.1325 | 4.5326 | 9564.8147 | 18924.1005 | 194.9917 | 385.7934
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.1787 | 12.1542 | 1.1969 | 4 | 9154.7762 | 18015.479 | 186.6325 | 367.2699 | 72.2582 | 9.6547 | 67.3875 | 3344289.9677 | 0 | 2927344.8608 | 0 | 0 | 0 | 1300056.3981 | 2952959.5784 | 7682995.0876 | 5243802.017 | 23451447.9095 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 43830073.7861 | 86252220.6355 | 74989.4209 | 4.7877 | 9154.7762 | 18015.479 | 186.6325 | 367.2699
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.465 | 12.5583 | 1.248 | 4 | 8850.4325 | 17348.7022 | 180.428 | 353.6768 | 72.0797 | 9.5918 | 88.5584 | 3406404.4776 | 0 | 3001314.0939 | 0 | 0 | 0 | 1276982.3154 | 2997033.3458 | 7797665.9898 | 5322067.2641 | 23801467.4865 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44180093.3631 | 86602240.2126 | 100000 | 4.9919 | 8850.4325 | 17348.7022 | 180.428 | 353.6768
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9982 | 12.8709 | 1.2881 | 4 | 8624.0575 | 16857.416 | 175.8131 | 343.6612 | 71.9362 | 9.5418 | 73.9046 | 3453178.6113 | 0 | 3058065.7215 | 0 | 0 | 0 | 1255825.8636 | 3029157.3766 | 7881246.1284 | 5379112.426 | 24056586.1276 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44435212.0041 | 86857358.8536 | 133352.1432 | 5.1525 | 8624.0575 | 16857.416 | 175.8131 | 343.6612
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9519 | 13.1124 | 1.3194 | 4 | 8455.3722 | 16493.51 | 172.3742 | 336.2425 | 71.8219 | 9.5024 | 81.7059 | 3488592.2583 | 0 | 3101679.3393 | 0 | 0 | 0 | 1237799.329 | 3052947.6614 | 7943143.5693 | 5421358.7013 | 24245520.8586 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44624146.7352 | 87046293.5846 | 177827.941 | 5.2776 | 8455.3722 | 16493.51 | 172.3742 | 336.2425
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.4406 | 13.2968 | 1.3435 | 4 | 8329.4905 | 16223.4122 | 169.8079 | 330.7362 | 71.7327 | 9.4718 | 82.8408 | 3515192.4967 | 0 | 3134826.643 | 0 | 0 | 0 | 1222852.4354 | 3070419.9143 | 7988602.7873 | 5452385.5517 | 24384279.8286 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44762905.7051 | 87185052.5546 | 237137.3706 | 5.374 | 8329.4905 | 16223.4122 | 169.8079 | 330.7362
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.566 | 13.4365 | 1.3619 | 4 | 8235.4423 | 16022.5779 | 167.8906 | 326.6419 | 71.6641 | 9.4485 | 79.302 | 3535077.9204 | 0 | 3159833.7987 | 0 | 0 | 0 | 1210727.7916 | 3083199.4092 | 8021852.4115 | 5475079.1034 | 24485770.4347 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44864396.3113 | 87286543.1607 | 316227.766 | 5.4477 | 8235.4423 | 16022.5779 | 167.8906 | 326.6419
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.424 | 13.543 | 1.376 | 4 | 8165.1141 | 15872.6769 | 166.4569 | 323.586 | 71.6111 | 9.4305 | 80.9597 | 3550108.8452 | 0 | 3178869.587 | 0 | 0 | 0 | 1201230.0699 | 3092781.3158 | 8046782.5671 | 5492094.4469 | 24561866.8321 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44940492.7086 | 87362639.5581 | 421696.5034 | 5.504 | 8165.1141 | 15872.6769 | 166.4569 | 323.586
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.0734 | 13.6237 | 1.3867 | 4 | 8112.4874 | 15760.7198 | 165.384 | 321.3036 | 71.5706 | 9.4167 | 88.9645 | 3561413.6432 | 0 | 3193264.224 | 0 | 0 | 0 | 1193843.1258 | 3099923.1873 | 8065364.2516 | 5504776.8283 | 24618585.2601 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 44997211.1367 | 87419357.9861 | 562341.3252 | 5.5467 | 8112.4874 | 15760.7198 | 165.384 | 321.3036
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5681 | 13.6851 | 1.3948 | 4 | 8073.0861 | 15676.9013 | 164.5808 | 319.5948 | 71.5395 | 9.4062 | 87.2315 | 3569982.0667 | 0 | 3204219.8864 | 0 | 0 | 0 | 1188210.7247 | 3105340.9444 | 8079460.1442 | 5514397.5647 | 24661611.3311 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45040237.2077 | 87462384.0571 | 749894.2093 | 5.5791 | 8073.0861 | 15676.9013 | 164.5808 | 319.5948
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.9313 | 13.7304 | 1.4008 | 4 | 8043.5748 | 15614.4636 | 163.9792 | 318.322 | 71.5165 | 9.3985 | 90.0066 | 3576248.891 | 0 | 3212258.0577 | 0 | 0 | 0 | 1183760.464 | 3109184.2909 | 8089459.7436 | 5521222.4968 | 24692133.9441 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45070759.8206 | 87492906.6701 | 1000000 | 5.6033 | 8043.5748 | 15614.4636 | 163.9792 | 318.322
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1944 | 13.7633 | 1.4053 | 4 | 8021.4645 | 15568.0115 | 163.5284 | 317.375 | 71.4998 | 9.3929 | 82.423 | 3580774.0918 | 0 | 3218075.9145 | 0 | 0 | 0 | 1180225.7769 | 3111839.5554 | 8096368.1972 | 5525937.6583 | 24713221.1941 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45091847.0707 | 87513993.9201 | 1333521.4322 | 5.6214 | 8021.4645 | 15568.0115 | 163.5284 | 317.375
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4159 | 13.7907 | 1.4089 | 4 | 8004.8954 | 15532.5668 | 163.1906 | 316.6524 | 71.4857 | 9.3881 | 92.0588 | 3584578.0407 | 0 | 3222974.7383 | 0 | 0 | 0 | 1177881.0152 | 3114319.1797 | 8102819.6709 | 5530340.9217 | 24732913.5665 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45111539.443 | 87533686.2925 | 1778279.41 | 5.6355 | 8004.8954 | 15532.5668 | 163.1906 | 316.6524
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.5692 | 13.8098 | 1.4115 | 4 | 7992.4766 | 15506.3747 | 162.9374 | 316.1184 | 71.476 | 9.3848 | 77.9246 | 3587207.2 | 0 | 3226365.5888 | 0 | 0 | 0 | 1175921.8698 | 3115902.9168 | 8106940.23 | 5533153.2879 | 24745491.0932 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45124116.9698 | 87546263.8193 | 2371373.7057 | 5.6458 | 7992.4766 | 15506.3747 | 162.9374 | 316.1184
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.6741 | 13.823 | 1.4133 | 4 | 7983.1674 | 15487.0328 | 162.7477 | 315.7241 | 71.4692 | 9.3826 | 81.844 | 3589001.6187 | 0 | 3228682.3032 | 0 | 0 | 0 | 1174297.7942 | 3116872.8693 | 8109463.8474 | 5534875.7087 | 24753194.1416 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45131820.0182 | 87553966.8676 | 3162277.6602 | 5.6534 | 7983.1674 | 15487.0328 | 162.7477 | 315.7241
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7667 | 13.8345 | 1.4148 | 4 | 7976.1885 | 15472.1547 | 162.6054 | 315.4208 | 71.4633 | 9.3806 | 78.8771 | 3590586.0899 | 0 | 3230729.1428 | 0 | 0 | 0 | 1173269.8757 | 3117888.1923 | 8112105.5095 | 5536678.6973 | 24761257.5076 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45139883.3841 | 87562030.2336 | 4216965.0343 | 5.6593 | 7976.1885 | 15472.1547 | 162.6054 | 315.4208
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.825 | 13.8418 | 1.4159 | 4 | 7970.9563 | 15461.3083 | 162.4987 | 315.1997 | 71.4596 | 9.3793 | 82.5926 | 3591583.2625 | 0 | 3232018.2466 | 0 | 0 | 0 | 1172339.6105 | 3118417.0367 | 8113481.4541 | 5537617.8078 | 24765457.4182 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45144083.2948 | 87566230.1443 | 5623413.2519 | 5.6636 | 7970.9563 | 15461.3083 | 162.4987 | 315.1997
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8787 | 13.8485 | 1.4167 | 4 | 7967.0332 | 15452.9053 | 162.4187 | 315.0284 | 71.4561 | 9.3782 | 76.9806 | 3592501.2369 | 0 | 3233205.2281 | 0 | 0 | 0 | 1171779.4499 | 3119019.5068 | 8115048.9578 | 5538687.6613 | 24770242.0408 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45148867.9173 | 87571014.7668 | 7498942.0933 | 5.667 | 7967.0332 | 15452.9053 | 162.4187 | 315.0284
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9176 | 13.8533 | 1.4174 | 4 | 7964.0917 | 15446.6439 | 162.3588 | 314.9007 | 71.4536 | 9.3773 | 80.4852 | 3593165.6578 | 0 | 3234064.6773 | 0 | 0 | 0 | 1171338.7763 | 3119441.9535 | 8116148.0774 | 5539437.833 | 24773596.9755 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 45152222.852 | 87574369.7015 | 10000000 | 5.6695 | 7964.0917 | 15446.6439 | 162.3588 | 314.9007
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.5908 | [19 empty] | 100 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2125 | [19 empty] | 133.3521 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.013643 | 0.00034264 | 4 | 15983669.4823 | 47734329.5762 | 325848.7219 | 973128.8739 | 52.8613 | 8.8922 | 25.2284 | 127971.4752 | 0 | 56377.1758 | 0 | 0 | 0 | 133608.1554 | 124003.1545 | 322630.7715 | 220202.1309 | 984792.8634 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 21906540.3326 | 65422650.1163 | 177.8279 | 0.0013706 | 15983669.4823 | 47734329.5762 | 325848.7219 | 973128.8739
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0016683 | 0.0032196 | 4 | 1696855.2112 | 5075816.9989 | 34592.6886 | 103477.3951 | 52.8608 | 8.8917 | 23.0106 | 127967.6326 | 0 | 56379.0351 | 0 | 0 | 0 | 116331.9392 | 117264.6567 | 305098.5824 | 208236.0516 | 931277.8976 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 21853025.3669 | 65369135.1505 | 237.1374 | 0.012879 | 1696855.2112 | 5075816.9989 | 34592.6886 | 103477.3951
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.0073931 | 0.0053517 | 4 | 1018892.1399 | 3051721.0531 | 20771.4944 | 62213.4614 | 52.861 | 8.8919 | 23.4 | 127968.9002 | 0 | 56378.4218 | 0 | 0 | 0 | 102792.9966 | 111984.7243 | 291361.2813 | 198860.0614 | 889346.3856 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 21811093.8548 | 65327203.6385 | 316.2278 | 0.021407 | 1018892.1399 | 3051721.0531 | 20771.4944 | 62213.4614
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4586 | 0.15544 | 0.013385 | 4 | 426799.5976 | 1239553.9149 | 8700.8871 | 25269.9832 | 63.3399 | 9.906 | 39.0785 | 262846.1176 | 0 | 145276.5424 | 0 | 0 | 0 | 214931.2776 | 242991.0356 | 632212.8304 | 431498.2474 | 1929756.0509 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 22851503.5201 | 66367613.3038 | 421.6965 | 0.053542 | 426799.5976 | 1239553.9149 | 8700.8871 | 25269.9832
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6501 | 0.27747 | 0.022078 | 4 | 265025.2393 | 757775.6269 | 5402.898 | 15448.2811 | 66.3398 | 10.1724 | 44.9387 | 339414.2419 | 0 | 197773.8617 | 0 | 0 | 0 | 264600.6242 | 312697.6038 | 813575.022 | 555281.6698 | 2483343.0232 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 23405090.4925 | 66921200.2761 | 562.3413 | 0.088313 | 265025.2393 | 757775.6269 | 5402.898 | 15448.2811
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.177 | 0.44181 | 0.034151 | 4 | 176111.6439 | 494672.7285 | 3590.2741 | 10084.5727 | 68.7034 | 10.3736 | 57.9269 | 429746.2826 | 0 | 261293.2406 | 0 | 0 | 0 | 321299.6248 | 394812.2677 | 1027220.5335 | 701099.1214 | 3135471.0707 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 24057218.5399 | 67573328.3236 | 749.8942 | 0.1366 | 176111.6439 | 494672.7285 | 3590.2741 | 10084.5727
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1481 | 0.66021 | 0.050599 | 4 | 122695.2396 | 337701.5676 | 2501.3084 | 6884.5032 | 70.5726 | 10.5264 | 41.6241 | 537033.3948 | 0 | 338685.8945 | 0 | 0 | 0 | 387044.8577 | 492478.0173 | 1281326.7799 | 874531.8559 | 3911100.8 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 24832848.2692 | 68348958.0529 | 1000 | 0.20239 | 122695.2396 | 337701.5676 | 2501.3084 | 6884.5032
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6935 | 0.94729 | 0.072719 | 4 | 88549.2184 | 238152.8016 | 1805.1956 | 4855.067 | 72.0421 | 10.6415 | 42.2081 | 664523.8071 | 0 | 433047.5748 | 0 | 0 | 0 | 463523.1305 | 608826.8598 | 1584042.6018 | 1081141.6245 | 4835105.5986 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 25756853.0678 | 69272962.8515 | 1333.5214 | 0.29088 | 88549.2184 | 238152.8016 | 1805.1956 | 4855.067
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9339 | 1.3173 | 0.10211 | 4 | 65713.1502 | 172251.939 | 1339.6515 | 3511.5888 | 73.1754 | 10.7253 | 37.1807 | 814043.396 | 0 | 546596.3452 | 0 | 0 | 0 | 550407.9549 | 745308.6015 | 1939140.0972 | 1323502.9617 | 5918999.3564 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 26840746.8256 | 70356856.6093 | 1778.2794 | 0.40845 | 65713.1502 | 172251.939 | 1339.6515 | 3511.5888
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.0406 | 1.7902 | 0.14078 | 4 | 49917.4517 | 127195.6405 | 1017.6348 | 2593.0552 | 74.0407 | 10.7831 | 52.2703 | 988913.7485 | 0 | 682859.1114 | 0 | 0 | 0 | 648754.4602 | 905005.6548 | 2354639.0717 | 1607089.5494 | 7187261.596 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 28109009.0652 | 71625118.8489 | 2371.3737 | 0.56311 | 49917.4517 | 127195.6405 | 1017.6348 | 2593.0552
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.2151 | 2.3896 | 0.19108 | 4 | 38710.9955 | 95646.3117 | 789.176 | 1949.8794 | 74.6883 | 10.8177 | 40.2354 | 1192527.2922 | 0 | 845721.2936 | 0 | 0 | 0 | 759510.9344 | 1091126.2129 | 2838886.5851 | 1937598.4276 | 8665370.7458 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 29587118.215 | 73103227.9987 | 3162.2777 | 0.76431 | 38710.9955 | 95646.3117 | 789.176 | 1949.8794
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5681 | 3.13 | 0.25534 | 4 | 30609.2502 | 73215.6733 | 624.011 | 1492.6005 | 75.1461 | 10.8287 | 47.2741 | 1423908.2323 | 0 | 1035848.348 | 0 | 0 | 0 | 879020.2706 | 1302122.9719 | 3387856.8706 | 2312281.9277 | 10341038.6211 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 31262786.0903 | 74778895.874 | 4216.965 | 1.0214 | 30609.2502 | 73215.6733 | 624.011 | 1492.6005
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.1929 | 4.0238 | 0.33559 | 4 | 24673.5705 | 57091.2189 | 503.0041 | 1163.8817 | 75.4394 | 10.8149 | 44.7242 | 1681374.6426 | 0 | 1253487.5297 | 0 | 0 | 0 | 1003799.0161 | 1536077.8635 | 3996559.5079 | 2727733.9852 | 12199032.545 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 33120780.0142 | 76636889.7979 | 5623.4133 | 1.3424 | 24673.5705 | 57091.2189 | 503.0041 | 1163.8817
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9944 | 5.0625 | 0.43249 | 4 | 20288.9045 | 45443.2007 | 413.6168 | 926.4211 | 75.5824 | 10.7741 | 53.4037 | 1957397.1454 | 0 | 1494023.974 | 0 | 0 | 0 | 1125986.9831 | 1785189.16 | 4644696.0016 | 3170100.4601 | 14177393.7243 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 35099141.1935 | 78615250.9771 | 7498.9421 | 1.73 | 20288.9045 | 45443.2007 | 413.6168 | 926.4211
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6628 | 6.2122 | 0.54434 | 4 | 17038.9222 | 37024.7265 | 347.3615 | 754.7991 | 75.5872 | 10.7051 | 67.2128 | 2239537.1371 | 0 | 1748182.4697 | 0 | 0 | 0 | 1235606.6217 | 2037097.2291 | 5300109.1241 | 3617433.3835 | 16177965.9653 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 37099713.4345 | 80615823.2182 | 10000 | 2.1774 | 17038.9222 | 37024.7265 | 347.3615 | 754.7991
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.6628 | 7.4114 | 0.66636 | 4 | 14631.2645 | 30957.2806 | 298.2781 | 631.106 | 75.4698 | 10.6105 | 68.4769 | 2511665.5151 | 0 | 2002330.7484 | 0 | 0 | 0 | 1322495.149 | 2276231.6508 | 5922287.8361 | 4042083.139 | 18077094.0384 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 38998841.5076 | 82514951.2913 | 13335.2143 | 2.6654 | 14631.2645 | 30957.2806 | 298.2781 | 631.106
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.3286 | 8.5809 | 0.79126 | 4 | 12851.9823 | 26600.9732 | 262.005 | 542.2968 | 75.2584 | 10.4978 | 76.0922 | 2757719.4145 | 0 | 2241108.8715 | 0 | 0 | 0 | 1379498.1052 | 2487547.2926 | 6472087.7891 | 4417332.9042 | 19755294.377 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 40677041.8463 | 84193151.6299 | 17782.7941 | 3.165 | 12851.9823 | 26600.9732 | 262.005 | 542.2968
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.1714 | 9.6597 | 0.91164 | 4 | 11539.9262 | 23473.3901 | 235.257 | 478.5368 | 74.9891 | 10.377 | 66.7288 | 2969226.0959 | 0 | 2454559.8675 | 0 | 0 | 0 | 1407847.956 | 2664337.2286 | 6932058.938 | 4731272.6648 | 21159302.7507 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 42081050.2199 | 85597160.0036 | 23713.7371 | 3.6466 | 11539.9262 | 23473.3901 | 235.257 | 478.5368
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.8324 | 10.6019 | 1.0213 | 4 | 10573.085 | 21225.2948 | 215.5466 | 432.7063 | 74.7004 | 10.259 | 75.6905 | 3142406.5655 | 0 | 2636129.3206 | 0 | 0 | 0 | 1412068.1774 | 2804335.5848 | 7296305.9433 | 4979878.7304 | 22271124.3219 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 43192871.7911 | 86708981.5748 | 31622.7766 | 4.0852 | 10573.085 | 21225.2948 | 215.5466 | 432.7063
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.2593 | 11.3975 | 1.1169 | 4 | 9860.0334 | 19600.2453 | 201.0101 | 399.5775 | 74.4198 | 10.1505 | 64.9851 | 3280652.912 | 0 | 2786303.8828 | 0 | 0 | 0 | 1400848.1579 | 2912443.9315 | 7577581.6855 | 5171855.2041 | 23129685.7737 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 44051433.243 | 87567543.0266 | 42169.6503 | 4.4677 | 9860.0334 | 19600.2453 | 201.0101 | 399.5775
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4675 | 12.0461 | 1.1972 | 4 | 9333.1683 | 18420.2949 | 190.2693 | 375.5226 | 74.1671 | 10.0564 | 72.5358 | 3388032.4076 | 0 | 2906693.7488 | 0 | 0 | 0 | 1380653.6642 | 2993398.13 | 7788207.904 | 5315611.9262 | 23772597.7808 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 44694345.2501 | 88210455.0337 | 56234.1325 | 4.7888 | 9333.1683 | 18420.2949 | 190.2693 | 375.5226
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5944 | 12.5627 | 1.2627 | 4 | 8942.9692 | 17558.7696 | 182.3145 | 357.9593 | 73.951 | 9.9778 | 73.6376 | 3470173.4686 | 0 | 3001313.997 | 0 | 0 | 0 | 1356998.067 | 3053109.3577 | 7943564.27 | 5421645.8382 | 24246804.9985 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 45168552.4677 | 88684662.2514 | 74989.4209 | 5.0507 | 8942.9692 | 17558.7696 | 182.3145 | 357.9593
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.8339 | 12.9696 | 1.3151 | 4 | 8653.3093 | 16925.756 | 176.4094 | 345.0544 | 73.7714 | 9.9136 | 77.1089 | 3532833.4408 | 0 | 3075138.9183 | 0 | 0 | 0 | 1333850.7298 | 3097311.0047 | 8058567.8883 | 5500138.1708 | 24597840.1525 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 45519587.6218 | 89035697.4054 | 100000 | 5.2604 | 8653.3093 | 16925.756 | 176.4094 | 345.0544
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3212 | 13.2831 | 1.3562 | 4 | 8437.8295 | 16459.4213 | 172.0166 | 335.5476 | 73.6277 | 9.8629 | 83.3037 | 3579855.0508 | 0 | 3131562.6217 | 0 | 0 | 0 | 1312593.8098 | 3129364.4781 | 8141964.4512 | 5557058.0386 | 24852398.4502 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 45774145.9194 | 89290255.7031 | 133352.1432 | 5.4249 | 8437.8295 | 16459.4213 | 172.0166 | 335.5476
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.2554 | 13.5273 | 1.3883 | 4 | 8277.2466 | 16113.373 | 168.7429 | 328.4929 | 73.5124 | 9.8226 | 86.3429 | 3615768.2275 | 0 | 3175291.3835 | 0 | 0 | 0 | 1294820.3521 | 3153493.1856 | 8204742.3986 | 5599905.2776 | 25044020.8249 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 45965768.2942 | 89481878.0778 | 177827.941 | 5.5533 | 8277.2466 | 16113.373 | 168.7429 | 328.4929
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7124 | 13.7117 | 1.4129 | 4 | 8157.4019 | 15856.9554 | 166.2997 | 323.2655 | 73.4236 | 9.7918 | 71.0541 | 3642440.5795 | 0 | 3208145.1143 | 0 | 0 | 0 | 1279848.4482 | 3170869.3154 | 8249951.524 | 5630761.4347 | 25182016.4161 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46103763.8853 | 89619873.669 | 237137.3706 | 5.6518 | 8157.4019 | 15856.9554 | 166.2997 | 323.2655
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.8176 | 13.8518 | 1.4318 | 4 | 8067.8586 | 15666.1304 | 164.4742 | 319.3753 | 73.3549 | 9.7681 | 85.8495 | 3662458.0662 | 0 | 3233021.9922 | 0 | 0 | 0 | 1267796.1142 | 3183677.7073 | 8283276.3322 | 5653506.3011 | 25283736.5131 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46205483.9823 | 89721593.766 | 316227.766 | 5.7271 | 8067.8586 | 15666.1304 | 164.4742 | 319.3753
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6607 | 13.9588 | 1.4461 | 4 | 8000.8963 | 15523.6601 | 163.1091 | 316.4708 | 73.3019 | 9.7498 | 84.9768 | 3677601.3524 | 0 | 3251971.0799 | 0 | 0 | 0 | 1258379.318 | 3193301.1827 | 8308314.6411 | 5670595.4614 | 25360163.0355 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46281910.5048 | 89798020.2884 | 421696.5034 | 5.7846 | 8000.8963 | 15523.6601 | 163.1091 | 316.4708
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.2844 | 14.0381 | 1.457 | 4 | 7950.7866 | 15417.6405 | 162.0875 | 314.3095 | 73.2623 | 9.7362 | 96.228 | 3688731.6244 | 0 | 3265971.9883 | 0 | 0 | 0 | 1250848.4533 | 3200165.3057 | 8326173.6813 | 5682784.6233 | 25414675.6763 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46336423.1456 | 89852532.9292 | 562341.3252 | 5.8279 | 7950.7866 | 15417.6405 | 162.0875 | 314.3095
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7667 | 14.0993 | 1.4652 | 4 | 7913.2687 | 15338.0584 | 161.3227 | 312.6871 | 73.2315 | 9.7257 | 76.4357 | 3697299.4935 | 0 | 3276792.4164 | 0 | 0 | 0 | 1245221.9911 | 3205532.4214 | 8340137.8153 | 5692315.4316 | 25457299.5692 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46379047.0384 | 89895156.822 | 749894.2093 | 5.8609 | 7913.2687 | 15338.0584 | 161.3227 | 312.6871
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.1345 | 14.146 | 1.4715 | 4 | 7885.1676 | 15278.3991 | 160.7498 | 311.4708 | 73.2078 | 9.7176 | 86.5157 | 3703809.7737 | 0 | 3285039.6055 | 0 | 0 | 0 | 1240980.0704 | 3209633.4853 | 8350807.9425 | 5699598.0127 | 25489868.8901 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46411616.3593 | 89927726.143 | 1000000 | 5.8859 | 7885.1676 | 15278.3991 | 160.7498 | 311.4708
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3929 | 14.179 | 1.4761 | 4 | 7864.1136 | 15234.2349 | 160.3206 | 310.5705 | 73.1911 | 9.7119 | 77.6831 | 3708369.7019 | 0 | 3290829.6849 | 0 | 0 | 0 | 1237481.2942 | 3212305.4656 | 8357759.8871 | 5704342.8577 | 25511088.8914 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46432836.3607 | 89948946.1443 | 1333521.4322 | 5.9044 | 7864.1136 | 15234.2349 | 160.3206 | 310.5705
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6 | 14.2053 | 1.4796 | 4 | 7848.3359 | 15200.8152 | 159.9989 | 309.8892 | 73.1777 | 9.7073 | 91.1421 | 3712017.5964 | 0 | 3295469.3113 | 0 | 0 | 0 | 1235015.542 | 3214575.9554 | 8363667.2358 | 5708374.7446 | 25529120.3855 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46450867.8548 | 89966977.6384 | 1778279.41 | 5.9186 | 7848.3359 | 15200.8152 | 159.9989 | 309.8892
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7607 | 14.2256 | 1.4823 | 4 | 7836.5102 | 15175.6421 | 159.7579 | 309.376 | 73.1673 | 9.7038 | 82.2386 | 3714844.632 | 0 | 3299069.6708 | 0 | 0 | 0 | 1233224.5578 | 3216384.1556 | 8368371.8019 | 5711585.7076 | 25543480.5257 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46465227.995 | 89981337.7786 | 2371373.7057 | 5.9293 | 7836.5102 | 15175.6421 | 159.7579 | 309.376
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8728 | 14.2399 | 1.4843 | 4 | 7827.6455 | 15157.0097 | 159.5771 | 308.9961 | 73.16 | 9.7013 | 82.9845 | 3716812.7794 | 0 | 3301578.8906 | 0 | 0 | 0 | 1231747.2974 | 3217554.1973 | 8371416.0102 | 5713663.4423 | 25552772.6171 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46474520.0863 | 89990629.87 | 3162277.6602 | 5.9372 | 7827.6455 | 15157.0097 | 159.5771 | 308.9961
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9628 | 14.2513 | 1.4858 | 4 | 7820.9999 | 15142.8888 | 159.4417 | 308.7083 | 73.1542 | 9.6993 | 91.1754 | 3718392.4708 | 0 | 3303594.2349 | 0 | 0 | 0 | 1230719.2151 | 3218555.3091 | 8374020.6979 | 5715441.1952 | 25560723.1231 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46482470.5924 | 89998580.376 | 4216965.0343 | 5.9433 | 7820.9999 | 15142.8888 | 159.4417 | 308.7083
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0165 | 14.2583 | 1.4869 | 4 | 7816.0174 | 15132.6711 | 159.3401 | 308.5 | 73.1507 | 9.6981 | 85.511 | 3719334.0887 | 0 | 3304796.4583 | 0 | 0 | 0 | 1229746.0579 | 3219011.8759 | 8375208.591 | 5716251.9567 | 25564349.0286 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46486096.4978 | 90002206.2815 | 5623413.2519 | 5.9475 | 7816.0174 | 15132.6711 | 159.3401 | 308.5
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0749 | 14.2656 | 1.4878 | 4 | 7812.2816 | 15124.5332 | 159.2639 | 308.3341 | 73.1469 | 9.6968 | 90.4703 | 3720357.1864 | 0 | 3306102.7855 | 0 | 0 | 0 | 1229274.339 | 3219736.3813 | 8377093.6053 | 5717538.5177 | 25570102.8153 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46491850.2845 | 90007960.0681 | 7498942.0933 | 5.9511 | 7812.2816 | 15124.5332 | 159.2639 | 308.3341
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.1091 | 14.27 | 1.4884 | 4 | 7809.4805 | 15118.6838 | 159.2068 | 308.2148 | 73.1446 | 9.696 | 80.6678 | 3720957.5136 | 0 | 3306869.7376 | 0 | 0 | 0 | 1228782.8824 | 3220077.9521 | 8377982.3025 | 5718145.0718 | 25572815.46 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 46494562.9292 | 90010672.7128 | 10000000 | 5.9536 | 7809.4805 | 15118.6838 | 159.2068 | 308.2148
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.2189 | [19 empty] | 100 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2619 | [19 empty] | 133.3521 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.015128 | 0.00054886 | 4 | 10233683.7263 | 30559493.5989 | 208627.4848 | 622996.6118 | 53.367 | 9.1626 | 25.9438 | 130270.034 | 0 | 56283.8166 | 0 | 0 | 0 | 135209.4438 | 125487.6848 | 326493.2148 | 222838.3279 | 996582.5218 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 22467311.6746 | 67091155.6059 | 177.8279 | 0.0021954 | 10233683.7263 | 30559493.5989 | 208627.4848 | 622996.6118
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0031965 | 0.0034142 | 4 | 1641267.2235 | 4908802.4366 | 33459.4523 | 100072.5773 | 53.367 | 9.1626 | 24.1145 | 130270.0353 | 0 | 56283.816 | 0 | 0 | 0 | 118107.3659 | 118817.8747 | 309139.737 | 210994.2227 | 943613.0516 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 22414342.2044 | 67038186.1358 | 237.1374 | 0.013657 | 1641267.2235 | 4908802.4366 | 33459.4523 | 100072.5773
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.005854 | 0.0055392 | 4 | 1009741.2522 | 3023726.6726 | 20584.9412 | 61642.7581 | 53.3667 | 9.1622 | 22.531 | 130267.289 | 0 | 56285.1316 | 0 | 0 | 0 | 104703.1014 | 113589.6536 | 295536.9782 | 201710.0603 | 902092.2142 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 22372821.367 | 66996665.2984 | 316.2278 | 0.022157 | 1009741.2522 | 3023726.6726 | 20584.9412 | 61642.7581
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5829 | 0.16589 | 0.014476 | 4 | 405872.1265 | 1176522.9626 | 8274.2523 | 23985.012 | 64.7273 | 10.2572 | 43.3375 | 276944.1479 | 0 | 151948.9271 | 0 | 0 | 0 | 226827.0419 | 255730.8456 | 665359.2026 | 454121.3275 | 2030931.4925 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 23501660.6453 | 68125504.5767 | 421.6965 | 0.057904 | 405872.1265 | 1176522.9626 | 8274.2523 | 23985.012
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8204 | 0.29508 | 0.023861 | 4 | 252353.8315 | 719902.4633 | 5144.5742 | 14676.1855 | 67.8246 | 10.5294 | 39.3596 | 357784.131 | 0 | 206842.1251 | 0 | 0 | 0 | 279496.2961 | 329207.7954 | 856531.1538 | 584600.1124 | 2614461.6138 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 24085190.7666 | 68709034.698 | 562.3413 | 0.095442 | 252353.8315 | 719902.4633 | 5144.5742 | 14676.1855
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4157 | 0.46994 | 0.036896 | 4 | 167886.6896 | 470249.2935 | 3422.5973 | 9586.6679 | 70.2753 | 10.7355 | 51.7051 | 453700.1876 | 0 | 273643.3525 | 0 | 0 | 0 | 340259.9057 | 416365.3438 | 1083297.2164 | 739372.6097 | 3306638.6157 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 24777367.7685 | 69401211.6999 | 749.8942 | 0.14758 | 167886.6896 | 470249.2935 | 3422.5973 | 9586.6679
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4498 | 0.69987 | 0.054631 | 4 | 117095.5962 | 321301.7389 | 2387.1521 | 6550.1705 | 72.1892 | 10.8899 | 40.5229 | 566211.2482 | 0 | 354025.7109 | 0 | 0 | 0 | 409138.215 | 518456.3179 | 1348916.9892 | 920663.5626 | 4117412.0438 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 25588141.1965 | 70211985.1279 | 1000 | 0.21852 | 117095.5962 | 321301.7389 | 2387.1521 | 6550.1705
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0808 | 1.0024 | 0.078474 | 4 | 84602.4049 | 226764.0631 | 1724.7345 | 4622.8921 | 73.6993 | 11.0064 | 49.5449 | 700176.5296 | 0 | 452215.556 | 0 | 0 | 0 | 489562.1903 | 640362.1676 | 1666091.0037 | 1137141.3448 | 5085548.7919 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 26556277.9447 | 71180121.8761 | 1333.5214 | 0.3139 | 84602.4049 | 226764.0631 | 1724.7345 | 4622.8921
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4332 | 1.3927 | 0.11015 | 4 | 62856.8122 | 164141.049 | 1281.4211 | 3346.2373 | 74.8659 | 11.0911 | 44.7668 | 857469.34 | 0 | 570499.5808 | 0 | 0 | 0 | 581148.7161 | 783555.8784 | 2038651.6662 | 1391421.6523 | 6222746.8338 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 27693475.9866 | 72317319.918 | 1778.2794 | 0.44058 | 62856.8122 | 164141.049 | 1281.4211 | 3346.2373
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6861 | 1.8919 | 0.15179 | 4 | 47806.4627 | 121303.3668 | 974.5994 | 2472.9332 | 75.7573 | 11.1491 | 44.1324 | 1041621.0911 | 0 | 712594.5157 | 0 | 0 | 0 | 685072.4869 | 951322.3565 | 2475145.6286 | 1689337.7507 | 7555093.8295 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 29025822.9823 | 73649666.9137 | 2371.3737 | 0.60715 | 47806.4627 | 121303.3668 | 974.5994 | 2472.9332
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0038 | 2.5202 | 0.20583 | 4 | 37123.4676 | 91323.2423 | 756.8121 | 1861.7478 | 76.4195 | 11.1827 | 64.634 | 1254457.697 | 0 | 881173.1164 | 0 | 0 | 0 | 800461.5595 | 1145076.0255 | 2979252.9309 | 2033401.3428 | 9093822.6722 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 30564551.8249 | 75188395.7563 | 3162.2777 | 0.82332 | 37123.4676 | 91323.2423 | 756.8121 | 1861.7478
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.5427 | 3.2974 | 0.2748 | 4 | 29397.2213 | 69994.1008 | 599.3021 | 1426.9244 | 76.8882 | 11.192 | 50.7416 | 1496762.616 | 0 | 1078342.1624 | 0 | 0 | 0 | 925583.1814 | 1365268.3043 | 3552148.0728 | 2424414.049 | 10842518.3859 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 32313247.5386 | 76937091.47 | 4216.965 | 1.0992 | 29397.2213 | 69994.1008 | 599.3021 | 1426.9244
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.3501 | 4.2311 | 0.36065 | 4 | 23735.4242 | 54668.0722 | 483.8787 | 1114.4826 | 77.1858 | 11.1752 | 54.6035 | 1765057.9851 | 0 | 1302961.7306 | 0 | 0 | 0 | 1055086.4086 | 1608011.3884 | 4183715.7842 | 2855471.9895 | 12770305.2863 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 34241034.439 | 78864878.3704 | 5623.4133 | 1.4426 | 23735.4242 | 54668.0722 | 483.8787 | 1114.4826
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3561 | 5.3153 | 0.46404 | 4 | 19553.1254 | 43594.1658 | 398.6169 | 888.726 | 77.3284 | 11.1299 | 54.4954 | 2052541.893 | 0 | 1551143.0543 | 0 | 0 | 0 | 1182122.3979 | 1866464.8646 | 4856158.7131 | 3314428.1058 | 14822859.0287 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 36293588.1814 | 80917432.1128 | 7498.9421 | 1.8562 | 19553.1254 | 43594.1658 | 398.6169 | 888.726
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.1781 | 6.5072 | 0.58272 | 4 | 16453.9899 | 35598.5471 | 335.4368 | 725.7245 | 77.3276 | 11.0554 | 56.8732 | 2344328.8527 | 0 | 1811615.1225 | 0 | 0 | 0 | 1294594.6166 | 2125710.0508 | 5530661.5091 | 3774790.1237 | 16881700.2753 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 38352429.428 | 82976273.3594 | 10000 | 2.3309 | 16453.9899 | 35598.5471 | 335.4368 | 725.7245
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.2628 | 7.7417 | 0.7114 | 4 | 14159.1086 | 29840.7707 | 288.6526 | 608.3445 | 77.2018 | 10.9548 | 76.7033 | 2623792.0134 | 0 | 2070320.2628 | 0 | 0 | 0 | 1382408.5755 | 2369843.1322 | 6165845.7083 | 4208316.3913 | 18820526.0835 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 40291255.2363 | 84915099.1677 | 13335.2143 | 2.8456 | 14159.1086 | 29840.7707 | 288.6526 | 608.3445
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9681 | 8.9405 | 0.84238 | 4 | 12463.9003 | 25707.2312 | 254.0935 | 524.0767 | 76.981 | 10.8362 | 70.3853 | 2875476.536 | 0 | 2312458.4782 | 0 | 0 | 0 | 1439483.953 | 2584693.3972 | 6724842.026 | 4589842.8644 | 20526797.2548 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 41997526.4076 | 86621370.339 | 17782.7941 | 3.3695 | 12463.9003 | 25707.2312 | 254.0935 | 524.0767
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.787 | 10.0391 | 0.96785 | 4 | 11214.1851 | 22740.7432 | 228.6163 | 463.6008 | 76.7038 | 10.7105 | 81.5607 | 3090468.7616 | 0 | 2527562.5831 | 0 | 0 | 0 | 1466889.2899 | 2763119.0475 | 7189068.9679 | 4906687.2912 | 21943795.9412 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 43414525.094 | 88038369.0254 | 23713.7371 | 3.8714 | 11214.1851 | 22740.7432 | 228.6163 | 463.6008
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.4138 | 10.9968 | 1.0817 | 4 | 10293.3669 | 20607.0237 | 209.8442 | 420.1021 | 76.4083 | 10.5883 | 79.1531 | 3266298.6225 | 0 | 2710300.8394 | 0 | 0 | 0 | 1470426.3252 | 2904340.057 | 7556497.0663 | 5157464.5182 | 23065327.4287 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 44536056.5814 | 89159900.5128 | 31622.7766 | 4.3267 | 10293.3669 | 20607.0237 | 209.8442 | 420.1021
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.7649 | 11.7999 | 1.1804 | 4 | 9614.2259 | 19065.2189 | 195.999 | 388.6703 | 76.1242 | 10.477 | 80.9959 | 3405726.9798 | 0 | 2860393.4947 | 0 | 0 | 0 | 1458089.008 | 3012441.6981 | 7837755.3618 | 5349429.0842 | 23923835.6265 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 45394564.7792 | 90018408.7106 | 42169.6503 | 4.7216 | 9614.2259 | 19065.2189 | 195.999 | 388.6703
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.907 | 12.4538 | 1.2631 | 4 | 9112.3556 | 17944.8331 | 185.7677 | 365.8297 | 75.8691 | 10.3806 | 80.4225 | 3514010.4701 | 0 | 2980650.5048 | 0 | 0 | 0 | 1437246.1508 | 3093443.779 | 8048506.1603 | 5493270.8347 | 24567127.8996 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 46037857.0524 | 90661700.9838 | 56234.1325 | 5.0522 | 9112.3556 | 17944.8331 | 185.7677 | 365.8297
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9897 | 12.9755 | 1.3304 | 4 | 8740.6131 | 17125.89 | 178.1892 | 349.1344 | 75.6508 | 10.3002 | 83.3135 | 3597063.4297 | 0 | 3075381.3825 | 0 | 0 | 0 | 1413461.9076 | 3153503.6207 | 8204769.5486 | 5599923.8081 | 25044103.6973 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 46514832.85 | 91138676.7814 | 74989.4209 | 5.3217 | 8740.6131 | 17125.89 | 178.1892 | 349.1344
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.1808 | 13.3849 | 1.3842 | 4 | 8464.6149 | 16524.2534 | 172.5626 | 336.8693 | 75.4705 | 10.2349 | 87.7942 | 3660182.0112 | 0 | 3148990.0588 | 0 | 0 | 0 | 1390140.201 | 3197731.7857 | 8319842.1614 | 5678463.2308 | 25395349.4488 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 46866078.6016 | 91489922.5329 | 100000 | 5.5367 | 8464.6149 | 16524.2534 | 172.5626 | 336.8693
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.6512 | 13.7026 | 1.4264 | 4 | 8259.2729 | 16080.2026 | 168.3764 | 327.8167 | 75.325 | 10.1829 | 78.8138 | 3707961.7189 | 0 | 3205723.9485 | 0 | 0 | 0 | 1369190.2919 | 3230321.6241 | 8404634.2359 | 5736335.564 | 25654167.3834 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47124896.5362 | 91748740.4676 | 133352.1432 | 5.7057 | 8259.2729 | 16080.2026 | 168.3764 | 327.8167
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.5271 | 13.9448 | 1.4591 | 4 | 8106.2298 | 15751.8916 | 165.2565 | 321.1236 | 75.2111 | 10.1426 | 78.0465 | 3743608.814 | 0 | 3248662.0223 | 0 | 0 | 0 | 1350996.7892 | 3253874.3739 | 8465913.6596 | 5778160.0298 | 25841215.6887 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47311944.8415 | 91935788.7729 | 177827.941 | 5.8365 | 8106.2298 | 15751.8916 | 165.2565 | 321.1236
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.9614 | 14.1301 | 1.4843 | 4 | 7992.0033 | 15507.9181 | 162.9278 | 316.1499 | 75.122 | 10.1112 | 89.6056 | 3770494.1436 | 0 | 3281410.7185 | 0 | 0 | 0 | 1336097.1614 | 3271320.7892 | 8511305.6533 | 5809140.9982 | 25979769.4643 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47450498.6171 | 92074342.5485 | 237137.3706 | 5.9372 | 7992.0033 | 15507.9181 | 162.9278 | 316.1499
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.048 | 14.2708 | 1.5036 | 4 | 7906.6526 | 15326.352 | 161.1878 | 312.4484 | 75.0534 | 10.0872 | 91.2523 | 3790650.8633 | 0 | 3306177.9513 | 0 | 0 | 0 | 1324104.9824 | 3284164.1809 | 8544721.5239 | 5831948.0165 | 26081767.5184 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47552496.6711 | 92176340.6025 | 316227.766 | 6.0142 | 7906.6526 | 15326.352 | 161.1878 | 312.4484
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8787 | 14.3784 | 1.5183 | 4 | 7842.8227 | 15190.7223 | 159.8865 | 309.6834 | 75.0003 | 10.0687 | 77.542 | 3805935.951 | 0 | 3325085.7473 | 0 | 0 | 0 | 1314778.5795 | 3293862.1083 | 8569953.5419 | 5849169.3873 | 26158785.3153 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47629514.468 | 92253358.3994 | 421696.5034 | 6.073 | 7842.8227 | 15190.7223 | 159.8865 | 309.6834
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.5024 | 14.4592 | 1.5294 | 4 | 7795.0554 | 15089.5376 | 158.9127 | 307.6206 | 74.96 | 10.0547 | 88.8582 | 3817339.5631 | 0 | 3339265.163 | 0 | 0 | 0 | 1307461.7298 | 3300985.9178 | 8588488.2328 | 5861819.6947 | 26215360.3011 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47686089.4539 | 92309933.3852 | 562341.3252 | 6.1175 | 7795.0554 | 15089.5376 | 158.9127 | 307.6206
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9823 | 14.5214 | 1.5378 | 4 | 7759.2905 | 15013.6399 | 158.1836 | 306.0734 | 74.9288 | 10.0439 | 96.058 | 3826074.0407 | 0 | 3350168.5275 | 0 | 0 | 0 | 1301968.6802 | 3306502.3869 | 8602840.9538 | 5871615.7216 | 26259170.3107 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47729899.4634 | 92353743.3948 | 749894.2093 | 6.1513 | 7759.2905 | 15013.6399 | 158.1836 | 306.0734
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.3332 | 14.567 | 1.5442 | 4 | 7732.5019 | 14957.1305 | 157.6375 | 304.9213 | 74.9058 | 10.0359 | 84.6587 | 3832439.1852 | 0 | 3358138.2698 | 0 | 0 | 0 | 1297606.8581 | 3310391.8821 | 8612960.6225 | 5878522.6035 | 26290059.4212 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47760788.574 | 92384632.5054 | 1000000 | 6.1766 | 7732.5019 | 14957.1305 | 157.6375 | 304.9213
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.589 | 14.6003 | 1.5489 | 4 | 7712.4309 | 14915.0427 | 157.2283 | 304.0633 | 74.889 | 10.0301 | 92.493 | 3837065.2293 | 0 | 3363943.4301 | 0 | 0 | 0 | 1294163.8027 | 3313117.2602 | 8620051.4972 | 5883362.2712 | 26311703.4907 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47782432.6435 | 92406276.5748 | 1333521.4322 | 6.1955 | 7712.4309 | 14915.0427 | 157.2283 | 304.0633
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.7935 | 14.6268 | 1.5525 | 4 | 7697.3897 | 14883.2045 | 156.9217 | 303.4143 | 74.8756 | 10.0254 | 77.661 | 3840756.8318 | 0 | 3368583.461 | 0 | 0 | 0 | 1291736.2293 | 3315419.8436 | 8626042.347 | 5887451.1493 | 26329989.862 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47800719.0148 | 92424562.9461 | 1778279.41 | 6.21 | 7697.3897 | 14883.2045 | 156.9217 | 303.4143
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9445 | 14.6464 | 1.5552 | 4 | 7686.116 | 14859.4221 | 156.6919 | 302.9294 | 74.8656 | 10.022 | 82.5518 | 3843477.6193 | 0 | 3372007.754 | 0 | 0 | 0 | 1289860.2529 | 3317084.7942 | 8630374.2069 | 5890407.7327 | 26343212.36 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47813941.5128 | 92437785.4442 | 2371373.7057 | 6.2208 | 7686.116 | 14859.4221 | 156.6919 | 302.9294
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.0519 | 14.6604 | 1.5572 | 4 | 7677.665 | 14841.7537 | 156.5196 | 302.5692 | 74.8585 | 10.0195 | 72.5238 | 3845411.4837 | 0 | 3374444.0823 | 0 | 0 | 0 | 1288356.7456 | 3318202.8015 | 8633283.0325 | 5892393.0659 | 26352091.2113 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47822820.3641 | 92446664.2955 | 3162277.6602 | 6.2288 | 7677.665 | 14841.7537 | 156.5196 | 302.5692
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1445 | 14.6724 | 1.5588 | 4 | 7671.3295 | 14828.2033 | 156.3904 | 302.293 | 74.8524 | 10.0174 | 73.2937 | 3847077.6461 | 0 | 3376544.4139 | 0 | 0 | 0 | 1287401.451 | 3319299.1693 | 8636135.5566 | 5894339.9722 | 26360798.2092 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47831527.362 | 92455371.2934 | 4216965.0343 | 6.2351 | 7671.3295 | 14828.2033 | 156.3904 | 302.293
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2003 | 14.6797 | 1.5599 | 4 | 7666.5794 | 14818.4 | 156.2936 | 302.0931 | 74.8487 | 10.0161 | 88.0436 | 3848079.3798 | 0 | 3377808.146 | 0 | 0 | 0 | 1286478.7083 | 3319822.8313 | 8637498.0177 | 5895269.8799 | 26364956.9631 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47835686.1159 | 92459530.0473 | 5623413.2519 | 6.2395 | 7666.5794 | 14818.4 | 156.2936 | 302.0931
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2493 | 14.6861 | 1.5607 | 4 | 7663.018 | 14810.8643 | 156.221 | 301.9395 | 74.8454 | 10.015 | 84.3942 | 3848961.3639 | 0 | 3378921.0529 | 0 | 0 | 0 | 1285892.4783 | 3320372.2091 | 8638927.386 | 5896245.4531 | 26369319.9432 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47840049.096 | 92463893.0274 | 7498942.0933 | 6.243 | 7663.018 | 14810.8643 | 156.221 | 301.9395
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2929 | 14.6916 | 1.5614 | 4 | 7660.3476 | 14805.0428 | 156.1665 | 301.8208 | 74.8425 | 10.014 | 88.7992 | 3849743.4399 | 0 | 3379908.0838 | 0 | 0 | 0 | 1285550.9605 | 3320928.9688 | 8640375.9607 | 5897234.1351 | 26373741.5488 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 47844470.7016 | 92468314.633 | 10000000 | 6.2457 | 7660.3476 | 14805.0428 | 156.1665 | 301.8208
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1509 | [19 empty] | 100 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4989 | [19 empty] | 133.3521 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.016604 | 0.00074858 | 4 | 7692503.6174 | 22969935.4596 | 156822.0911 | 468273.2035 | 53.8548 | 9.4315 | 25.384 | 132519.0875 | 0 | 56178.1264 | 0 | 0 | 0 | 136804.2865 | 126945.5851 | 330286.3724 | 225427.2359 | 1008160.6938 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 23033731.621 | 68779080.9136 | 177.8279 | 0.0029943 | 7692503.6174 | 22969935.4596 | 156822.0911 | 468273.2035
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0047042 | 0.0036033 | 4 | 1594469.0056 | 4768340.0982 | 32505.4074 | 97209.0626 | 53.8548 | 9.4315 | 25.8309 | 132519.0889 | 0 | 56178.1257 | 0 | 0 | 0 | 119861.4021 | 120337.8605 | 313094.4284 | 213693.3808 | 955684.2866 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 22981255.2137 | 68726604.5064 | 237.1374 | 0.014413 | 1594469.0056 | 4768340.0982 | 32505.4074 | 97209.0626
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7157 | 0.079355 | 0.00857 | 4 | 689753.3286 | 2024212.7364 | 14061.5546 | 41266.3146 | 62.1143 | 10.2431 | 51.6459 | 220020.7127 | 0 | 111907.5238 | 0 | 0 | 0 | 190862.3221 | 203888.3178 | 530475.5798 | 362060.4834 | 1619214.9396 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 23644785.8668 | 69390135.1594 | 316.2278 | 0.03428 | 689753.3286 | 2024212.7364 | 14061.5546 | 41266.3146
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7144 | 0.17727 | 0.015637 | 4 | 386315.1817 | 1117670.2234 | 7875.5575 | 22785.2193 | 66.1401 | 10.6106 | 49.1714 | 291811.0199 | 0 | 159035.1504 | 0 | 0 | 0 | 239431.101 | 269208.1358 | 700424.3472 | 478054.0092 | 2137963.7636 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 24163534.6907 | 69908883.9834 | 421.6965 | 0.062549 | 386315.1817 | 1117670.2234 | 7875.5575 | 22785.2193
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.001 | 0.31414 | 0.025755 | 4 | 240524.5252 | 684566.048 | 4903.4178 | 13955.8048 | 69.3332 | 10.8883 | 36.9545 | 377173.2167 | 0 | 216470.0766 | 0 | 0 | 0 | 295327.9713 | 346698.7932 | 902039.1422 | 615660.2496 | 2753369.4498 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 24778940.3769 | 70524289.6696 | 562.3413 | 0.10302 | 240524.5252 | 684566.048 | 4903.4178 | 13955.8048
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6445 | 0.49792 | 0.039793 | 4 | 160211.4876 | 447609.9872 | 3266.1279 | 9125.135 | 71.8397 | 11.0967 | 53.537 | 477549.5083 | 0 | 285732.2302 | 0 | 0 | 0 | 358797.5381 | 437610.9179 | 1138573.842 | 777100.0425 | 3475364.079 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 25500935.0062 | 71246284.2988 | 749.8942 | 0.15917 | 160211.4876 | 447609.9872 | 3266.1279 | 9125.135
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7593 | 0.7414 | 0.058899 | 4 | 111869.8842 | 306037.4597 | 2280.6189 | 6238.9876 | 73.8167 | 11.2541 | 40.6259 | 596393.9711 | 0 | 369849.9585 | 0 | 0 | 0 | 431984.3514 | 545309.0296 | 1418782.2368 | 968348.0296 | 4330667.577 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 26356238.5042 | 72101587.7968 | 1000 | 0.2356 | 111869.8842 | 306037.4597 | 2280.6189 | 6238.9876
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4707 | 1.0593 | 0.084551 | 4 | 80917.8798 | 216178.1878 | 1649.6204 | 4407.0848 | 75.3635 | 11.3717 | 46.9417 | 736675.353 | 0 | 471708.036 | 0 | 0 | 0 | 516061.5565 | 672533.5287 | 1749794.2862 | 1194270.555 | 5341043.3155 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 27366614.2426 | 73111963.5353 | 1333.5214 | 0.3382 | 80917.8798 | 216178.1878 | 1649.6204 | 4407.0848
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9271 | 1.4695 | 0.1186 | 4 | 60188.8328 | 156613.341 | 1227.0308 | 3192.7748 | 76.5612 | 11.4571 | 51.1128 | 901520.3717 | 0 | 594499.5172 | 0 | 0 | 0 | 611972.4134 | 822116.9979 | 2138979.7891 | 1459897.6577 | 6528986.747 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 28554557.6742 | 74299906.9668 | 1778.2794 | 0.47442 | 60188.8328 | 156613.341 | 1227.0308 | 3192.7748
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3124 | 1.9942 | 0.16335 | 4 | 45833.2411 | 115845.6506 | 934.3726 | 2361.6703 | 77.4772 | 11.5151 | 42.2079 | 1094578.6893 | 0 | 742053.4023 | 0 | 0 | 0 | 720914.9809 | 997443.3583 | 2595143.0145 | 1771238.4323 | 7921371.8776 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 29946942.8047 | 75692292.0974 | 2371.3737 | 0.65339 | 45833.2411 | 115845.6506 | 934.3726 | 2361.6703
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8003 | 2.6551 | 0.22137 | 4 | 35638.2329 | 87299.6338 | 726.5336 | 1779.7211 | 78.158 | 11.5479 | 63.925 | 1317925.0945 | 0 | 917286.888 | 0 | 0 | 0 | 842197.5723 | 1200189.7264 | 3122647.4753 | 2131271.0659 | 9531517.8223 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 31557088.7495 | 77302438.0421 | 3162.2777 | 0.88548 | 35638.2329 | 87299.6338 | 726.5336 | 1779.7211
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.5024 | 3.4674 | 0.2952 | 4 | 28262.1074 | 67002.6581 | 576.1613 | 1365.9398 | 78.6363 | 11.5552 | 55.2128 | 1570509.3035 | 0 | 1120895.4566 | 0 | 0 | 0 | 972065.1213 | 1428753.2538 | 3717322.8887 | 2537149.2549 | 11346695.2788 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 33372266.206 | 79117615.4986 | 4216.965 | 1.1808 | 28262.1074 | 67002.6581 | 576.1613 | 1365.9398
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.5339 | 4.4465 | 0.38703 | 4 | 22855.7669 | 52404.6622 | 465.9457 | 1068.3399 | 78.9396 | 11.5352 | 59.5503 | 1851245.3537 | 0 | 1353771.0315 | 0 | 0 | 0 | 1107832.5011 | 1682011.0657 | 4376247.765 | 2986879.0225 | 13357986.7395 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 35383557.6667 | 81128906.9593 | 5623.4133 | 1.5481 | 22855.7669 | 52404.6622 | 465.9457 | 1068.3399
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.7056 | 5.5728 | 0.49702 | 4 | 18862.285 | 41872.0802 | 384.5332 | 853.619 | 79.0807 | 11.4854 | 49.6371 | 2149087.1348 | 0 | 1608597.5814 | 0 | 0 | 0 | 1238415.606 | 1948479.1257 | 5069542.997 | 3460067.2642 | 15474189.7092 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 37499760.6364 | 83245109.929 | 7498.9421 | 1.9881 | 18862.285 | 41872.0802 | 384.5332 | 853.619
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.666 | 6.806 | 0.6227 | 4 | 15903.9214 | 34269.6213 | 324.223 | 698.6326 | 79.0743 | 11.4053 | 66.5279 | 2450198.4863 | 0 | 1875055.6855 | 0 | 0 | 0 | 1353316.0598 | 2214642.3903 | 5762045.2141 | 3932714.2568 | 17587972.0929 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 39613543.0201 | 85358892.3127 | 10000 | 2.4908 | 15903.9214 | 34269.6213 | 324.223 | 698.6326
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8512 | 8.0781 | 0.75827 | 4 | 13714.2554 | 28796.4468 | 279.5836 | 587.0545 | 78.9398 | 11.2985 | 66.1611 | 2737486.727 | 0 | 2138764.7508 | 0 | 0 | 0 | 1442485.9279 | 2464307.5882 | 6411622.8455 | 4376064.3378 | 19570732.1772 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 41596303.1044 | 87341652.397 | 13335.2143 | 3.0331 | 13714.2554 | 28796.4468 | 279.5836 | 587.0545
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.5734 | 9.3038 | 0.89534 | 4 | 12097.439 | 24870.644 | 246.6227 | 507.0217 | 78.7101 | 11.1741 | 69.56 | 2994201.8876 | 0 | 2383705.3625 | 0 | 0 | 0 | 1499031.2775 | 2682006.0258 | 6978029.524 | 4762648.5343 | 21299622.6117 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 43325193.5389 | 89070542.8315 | 17782.7941 | 3.5814 | 12097.439 | 24870.644 | 246.6227 | 507.0217
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.3897 | 10.4246 | 1.026 | 4 | 10905.8185 | 22051.8224 | 222.3299 | 449.5562 | 78.4243 | 11.0431 | 71.5906 | 3213152.2339 | 0 | 2600968.5806 | 0 | 0 | 0 | 1525934.1064 | 2862621.4191 | 7447953.7282 | 5083381.4596 | 22734011.5278 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 44759582.4549 | 90504931.7476 | 23713.7371 | 4.1042 | 10905.8185 | 22051.8224 | 222.3299 | 449.5562
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9607 | 11.3951 | 1.144 | 4 | 10027.8735 | 20025.0619 | 204.4318 | 408.238 | 78.1232 | 10.9169 | 73.6837 | 3391066.6547 | 0 | 2784329.6405 | 0 | 0 | 0 | 1528263.3512 | 3004427.2621 | 7816903.4432 | 5335197.2213 | 23860187.5729 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 45885758.5001 | 91631107.7927 | 31622.7766 | 4.5758 | 10027.8735 | 20025.0619 | 204.4318 | 408.238
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2555 | 12.2076 | 1.2459 | 4 | 9380.3183 | 18559.5415 | 191.2305 | 378.3614 | 77.8349 | 10.8026 | 75.5658 | 3532022.5969 | 0 | 2934755.9801 | 0 | 0 | 0 | 1515115.793 | 3112938.8043 | 8099228.2172 | 5527889.6807 | 24721951.0722 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 46747521.9994 | 92492871.292 | 42169.6503 | 4.9836 | 9380.3183 | 18559.5415 | 191.2305 | 378.3614
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.3567 | 12.8697 | 1.3311 | 4 | 8901.7302 | 17493.5352 | 181.4738 | 356.6294 | 77.5763 | 10.7036 | 76.9798 | 3641662.1316 | 0 | 3055431.3128 | 0 | 0 | 0 | 1494006.3061 | 3194528.9027 | 8311508.9168 | 5672775.6202 | 25369913.1902 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 47395484.1174 | 93140833.41 | 56234.1325 | 5.3243 | 8901.7302 | 17493.5352 | 181.4738 | 356.6294
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.3781 | 13.3943 | 1.4002 | 4 | 8547.1815 | 16714.7772 | 174.2459 | 340.7533 | 77.3568 | 10.6217 | 86.9583 | 3725204.5661 | 0 | 3149837.0232 | 0 | 0 | 0 | 1469698.2102 | 3254448.5218 | 8467407.4745 | 5779179.5892 | 25845775.3849 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 47871346.312 | 93616695.6047 | 74989.4209 | 5.6008 | 8547.1815 | 16714.7772 | 174.2459 | 340.7533
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5233 | 13.8062 | 1.4553 | 4 | 8283.9121 | 16142.2463 | 168.8788 | 329.0815 | 77.1756 | 10.5552 | 93.5771 | 3788772.3306 | 0 | 3223253.8324 | 0 | 0 | 0 | 1446168.6676 | 3298695.9839 | 8582530.2946 | 5857753.2794 | 26197174.3886 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48222745.3158 | 93968094.6084 | 100000 | 5.8213 | 8283.9121 | 16142.2463 | 168.8788 | 329.0815
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9398 | 14.1237 | 1.4985 | 4 | 8088.0165 | 15720.0083 | 164.8852 | 320.4736 | 77.0307 | 10.5027 | 79.6275 | 3836555.6495 | 0 | 3279423.1124 | 0 | 0 | 0 | 1424859.459 | 3330926.9062 | 8666388.5427 | 5914988.2569 | 26453141.9267 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48478712.8539 | 94224062.1465 | 133352.1432 | 5.9939 | 8088.0165 | 15720.0083 | 164.8852 | 320.4736
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7936 | 14.3678 | 1.532 | 4 | 7941.9998 | 15407.1628 | 161.9084 | 314.0959 | 76.9162 | 10.4616 | 83.9499 | 3872586.5632 | 0 | 3322374.7043 | 0 | 0 | 0 | 1406775.0756 | 3354677.1738 | 8728181.8673 | 5957163.4706 | 26641758.8549 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48667329.782 | 94412679.0747 | 177827.941 | 6.1278 | 7941.9998 | 15407.1628 | 161.9084 | 314.0959
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.2092 | 14.5546 | 1.5577 | 4 | 7833.0091 | 15174.6683 | 159.6865 | 309.3561 | 76.8267 | 10.4298 | 86.5886 | 3899736.1042 | 0 | 3355097.0082 | 0 | 0 | 0 | 1391970.6118 | 3372253.4524 | 8773911.7389 | 5988375.0477 | 26781343.9632 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48806914.8903 | 94552264.183 | 237137.3706 | 6.2309 | 7833.0091 | 15174.6683 | 159.6865 | 309.3561
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.2855 | 14.6967 | 1.5774 | 4 | 7751.5659 | 15001.5112 | 158.0262 | 305.8261 | 76.7576 | 10.4052 | 89.353 | 3920166.2366 | 0 | 3379932.1908 | 0 | 0 | 0 | 1380133.3325 | 3385290.3864 | 8807831.1667 | 6011525.7541 | 26884879.0671 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48910449.9943 | 94655799.2869 | 316227.766 | 6.3098 | 7751.5659 | 15001.5112 | 158.0262 | 305.8261
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0897 | 14.8032 | 1.5924 | 4 | 7690.6554 | 14872.6293 | 156.7844 | 303.1987 | 76.7053 | 10.3867 | 84.5896 | 3935311.3359 | 0 | 3398464.1089 | 0 | 0 | 0 | 1370648.6763 | 3394725.4072 | 8832379.1557 | 6028280.261 | 26959808.9449 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48985379.8721 | 94730729.1648 | 421696.5034 | 6.3695 | 7690.6554 | 14872.6293 | 156.7844 | 303.1987
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.7009 | 14.8841 | 1.6037 | 4 | 7645.0714 | 14776.2674 | 155.8551 | 301.2342 | 76.6651 | 10.3726 | 82.9093 | 3946753.7559 | 0 | 3412535.3323 | 0 | 0 | 0 | 1363340.9717 | 3401825.7234 | 8850852.7218 | 6040888.8495 | 27016197.3546 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49041768.2818 | 94787117.5744 | 562341.3252 | 6.4148 | 7645.0714 | 14776.2674 | 155.8551 | 301.2342
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1614 | 14.9451 | 1.6123 | 4 | 7610.9403 | 14704.2337 | 155.1593 | 299.7657 | 76.6347 | 10.3619 | 86.5201 | 3955334.3599 | 0 | 3423127.5846 | 0 | 0 | 0 | 1357708.3109 | 3407106.3996 | 8864591.9582 | 6050266.1606 | 27058134.7738 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49083705.701 | 94829054.9936 | 749894.2093 | 6.4491 | 7610.9403 | 14704.2337 | 155.1593 | 299.7657
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.5124 | 14.9915 | 1.6188 | 4 | 7585.375 | 14650.2294 | 154.6381 | 298.6647 | 76.6114 | 10.3537 | 77.0507 | 3961852.7756 | 0 | 3431197.5155 | 0 | 0 | 0 | 1353466.555 | 3411141.57 | 8875090.6437 | 6057431.7292 | 27090180.7889 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49115751.7161 | 94861101.0087 | 1000000 | 6.4751 | 7585.375 | 14650.2294 | 154.6381 | 298.6647
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.7681 | 15.0255 | 1.6236 | 4 | 7566.2203 | 14610.0091 | 154.2476 | 297.8448 | 76.5943 | 10.3477 | 81.0867 | 3966590.3212 | 0 | 3437075.7022 | 0 | 0 | 0 | 1350111.839 | 3413973.3664 | 8882458.3971 | 6062460.3723 | 27112669.9981 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49138240.9253 | 94883590.218 | 1333521.4322 | 6.4944 | 7566.2203 | 14610.0091 | 154.2476 | 297.8448
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.9682 | 15.052 | 1.6273 | 4 | 7551.8656 | 14579.6905 | 153.955 | 297.2267 | 76.5809 | 10.343 | 81.7302 | 3970288.4836 | 0 | 3441671.6449 | 0 | 0 | 0 | 1347688.0649 | 3416262.7954 | 8888415.0218 | 6066525.8911 | 27130851.9018 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49156422.8289 | 94901772.1216 | 1778279.41 | 6.5092 | 7551.8656 | 14579.6905 | 153.955 | 297.2267
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.1165 | 15.0716 | 1.6301 | 4 | 7541.1063 | 14557.0248 | 153.7357 | 296.7646 | 76.571 | 10.3395 | 87.2111 | 3973026.9417 | 0 | 3445079.2444 | 0 | 0 | 0 | 1345825.8903 | 3417933.5098 | 8892761.878 | 6069492.7097 | 27144120.1741 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49169691.1013 | 94915040.3939 | 2371373.7057 | 6.5202 | 7541.1063 | 14557.0248 | 153.7357 | 296.7646
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.224 | 15.0859 | 1.6321 | 4 | 7533.041 | 14540.1394 | 153.5712 | 296.4204 | 76.5638 | 10.337 | 85.2976 | 3975007.6192 | 0 | 3447546.2804 | 0 | 0 | 0 | 1344360.4929 | 3419096.6131 | 8895788.0341 | 6071558.1235 | 27153357.1632 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49178928.0904 | 94924277.383 | 3162277.6602 | 6.5284 | 7533.041 | 14540.1394 | 153.5712 | 296.4204
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3017 | 15.0963 | 1.6336 | 4 | 7526.9945 | 14527.555 | 153.448 | 296.1639 | 76.5585 | 10.3352 | 81.7214 | 3976440.6372 | 0 | 3449332.4495 | 0 | 0 | 0 | 1343213.5672 | 3419904.795 | 8897890.7577 | 6072993.2755 | 27159775.482 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49185346.4092 | 94930695.7018 | 4216965.0343 | 6.5345 | 7526.9945 | 14527.555 | 153.448 | 296.1639
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3749 | 15.1059 | 1.6349 | 4 | 7522.4612 | 14517.753 | 153.3555 | 295.964 | 76.5536 | 10.3335 | 80.3774 | 3977788.1226 | 0 | 3451012.5682 | 0 | 0 | 0 | 1342575.0429 | 3420836.5362 | 8900314.9571 | 6074647.8414 | 27167175.0684 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49192745.9955 | 94938095.2882 | 5623413.2519 | 6.5394 | 7522.4612 | 14517.753 | 153.3555 | 295.964
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4138 | 15.1111 | 1.6357 | 4 | 7519.0622 | 14510.8035 | 153.2863 | 295.8224 | 76.551 | 10.3325 | 81.0451 | 3978503.6037 | 0 | 3451905.3479 | 0 | 0 | 0 | 1341852.0394 | 3421181.7865 | 8901213.2276 | 6075260.9295 | 27169916.9346 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49195487.8618 | 94940837.1544 | 7498942.0933 | 6.5428 | 7519.0622 | 14510.8035 | 153.2863 | 295.8224
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4527 | 15.1162 | 1.6364 | 4 | 7516.5136 | 14505.3514 | 153.2343 | 295.7112 | 76.5484 | 10.3316 | 87.104 | 3979219.3221 | 0 | 3452798.4074 | 0 | 0 | 0 | 1341456.2667 | 3421654.8585 | 8902444.0639 | 6076101.0005 | 27173673.9191 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 49199244.8463 | 94944594.1389 | 10000000 | 6.5455 | 7516.5136 | 14505.3514 | 153.2343 | 295.7112
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5019 | [19 empty] | 100 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9751 | [19 empty] | 133.3521 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.01807 | 0.00094185 | 4 | 6265842.1699 | 18709668.5785 | 127737.6678 | 381421.9007 | 54.3253 | 9.699 | 23.3161 | 134720.5836 | 0 | 56060.7815 | 0 | 0 | 0 | 138393.249 | 128378.0995 | 334013.481 | 227971.0641 | 1019537.2588 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 23605810.0513 | 70486435.9187 | 177.8279 | 0.0037674 | 6265842.1699 | 18709668.5785 | 127737.6678 | 381421.9007
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0062041 | 0.0037861 | 4 | 1555293.2787 | 4650890.4326 | 31706.7572 | 94814.6923 | 54.3253 | 9.699 | 24.4669 | 134720.5851 | 0 | 56060.7808 | 0 | 0 | 0 | 121605.7402 | 121830.9714 | 316979.1965 | 216344.8149 | 967542.0889 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 23553814.8813 | 70434440.7488 | 237.1374 | 0.015144 | 1555293.2787 | 4650890.4326 | 31706.7572 | 94814.6923
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.813 | 0.085702 | 0.0092579 | 4 | 655903.9848 | 1921867.3329 | 13371.4899 | 39179.8651 | 63.4236 | 10.5903 | 47.4267 | 231558.8484 | 0 | 117142.8773 | 0 | 0 | 0 | 201104.5866 | 214424.4618 | 557888.4651 | 380770.3409 | 1702889.58 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 24289162.3725 | 71169788.2399 | 316.2278 | 0.037032 | 655903.9848 | 1921867.3329 | 13371.4899 | 39179.8651
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8607 | 0.19025 | 0.016875 | 4 | 368028.5215 | 1062557.4126 | 7502.7592 | 21661.6701 | 67.6017 | 10.9683 | 39.9668 | 308000.4162 | 0 | 166891.6487 | 0 | 0 | 0 | 253370.2404 | 284022.299 | 738967.7611 | 504360.6812 | 2255613.0466 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 24841885.8391 | 71722511.7065 | 421.6965 | 0.0675 | 368028.5215 | 1062557.4126 | 7502.7592 | 21661.6701
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1862 | 0.33418 | 0.027763 | 4 | 229472.7047 | 651624.4979 | 4678.1115 | 13284.2468 | 70.8542 | 11.2482 | 31.0687 | 397238.0969 | 0 | 226414.6697 | 0 | 0 | 0 | 311703.2676 | 364788.8534 | 949105.768 | 647784.1888 | 2897034.8444 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 25483307.6369 | 72363933.5043 | 562.3413 | 0.11105 | 229472.7047 | 651624.4979 | 4678.1115 | 13284.2468
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8808 | 0.52741 | 0.042859 | 4 | 153041.6999 | 426499.8864 | 3119.9621 | 8694.7771 | 73.4177 | 11.4588 | 56.1341 | 502311.6055 | 0 | 298276.2982 | 0 | 0 | 0 | 378072.7843 | 459677.6683 | 1195987 | 816285.7026 | 3650611.0587 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 26236883.8512 | 73117509.7186 | 749.8942 | 0.17144 | 153041.6999 | 426499.8864 | 3119.9621 | 8694.7771
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0734 | 0.78451 | 0.063409 | 4 | 106987.6893 | 291823.3301 | 2181.0888 | 5949.2133 | 75.4528 | 11.6188 | 51.1441 | 627425.2988 | 0 | 386040.6214 | 0 | 0 | 0 | 455401.8845 | 572858.4438 | 1490460.1614 | 1017269.686 | 4549456.0958 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 27135728.8883 | 74016354.7557 | 1000 | 0.25363 | 106987.6893 | 291823.3301 | 2181.0888 | 5949.2133
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8682 | 1.1185 | 0.090966 | 4 | 77474.0724 | 206314.8501 | 1579.4138 | 4206.0073 | 77.0368 | 11.7375 | 43.7546 | 774273.101 | 0 | 491707.7776 | 0 | 0 | 0 | 543304.7095 | 705621.3793 | 1835882.0862 | 1253027.2474 | 5603816.301 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 28190089.0934 | 75070714.9608 | 1333.5214 | 0.36386 | 77474.0724 | 206314.8501 | 1579.4138 | 4206.0073
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4413 | 1.5505 | 0.12755 | 4 | 57693.703 | 149583.0196 | 1176.1642 | 3049.4522 | 78.2681 | 11.8236 | 48.1645 | 947377.7725 | 0 | 619485.5822 | 0 | 0 | 0 | 644203.9265 | 862316.2397 | 2243569.9703 | 1531282.6055 | 6848236.0966 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 29434508.8891 | 76315134.7565 | 1778.2794 | 0.51019 | 57693.703 | 149583.0196 | 1176.1642 | 3049.4522
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9554 | 2.1009 | 0.17554 | 4 | 43986.4901 | 110752.1387 | 896.7241 | 2257.8322 | 79.2063 | 11.8815 | 56.1429 | 1149294.288 | 0 | 772411.2523 | 0 | 0 | 0 | 757953.2425 | 1045066.9253 | 2719049.7669 | 1855807.3368 | 8299582.8118 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 30885855.6043 | 77766481.4717 | 2371.3737 | 0.70217 | 43986.4901 | 110752.1387 | 896.7241 | 2257.8322
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.5922 | 2.7928 | 0.23769 | 4 | 34246.9431 | 83555.8088 | 698.1703 | 1703.3982 | 79.9027 | 11.9133 | 53.6905 | 1382450.9151 | 0 | 953680.998 | 0 | 0 | 0 | 884192.8298 | 1255926.6497 | 3267663.5166 | 2230247.4939 | 9974162.4031 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 32560435.1955 | 79441061.063 | 3162.2777 | 0.95075 | 34246.9431 | 83555.8088 | 698.1703 | 1703.3982
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4964 | 3.6454 | 0.31672 | 4 | 27197.6968 | 64202.8922 | 554.4618 | 1308.8628 | 80.3926 | 11.9185 | 57.7632 | 1646935.9186 | 0 | 1164970.4031 | 0 | 0 | 0 | 1020381.0817 | 1494592.0873 | 3888622.0283 | 2654064.4375 | 11869565.9566 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 34455838.749 | 81336464.6164 | 4216.965 | 1.2669 | 27197.6968 | 64202.8922 | 554.4618 | 1308.8628
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.6935 | 4.6643 | 0.41458 | 4 | 22029.9355 | 50299.5576 | 449.11 | 1025.4245 | 80.6992 | 11.895 | 48.6432 | 1938236.6129 | 0 | 1404479.6097 | 0 | 0 | 0 | 1160252.2563 | 1756157.7068 | 4569162.1156 | 3118547.0308 | 13946835.3321 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 36533108.1246 | 83413733.992 | 5623.4133 | 1.6583 | 22029.9355 | 50299.5576 | 449.11 | 1025.4245
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.0692 | 5.8381 | 0.53156 | 4 | 18212.8613 | 40261.4536 | 371.2938 | 820.7842 | 80.8393 | 11.8404 | 54.3634 | 2247840.1859 | 0 | 1667095.7734 | 0 | 0 | 0 | 1295700.8683 | 2032148.3628 | 5287233.189 | 3608645.2933 | 16138663.6727 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 38724936.4652 | 85605562.3326 | 7498.9421 | 2.1262 | 18212.8613 | 40261.4536 | 371.2938 | 820.7842
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1741 | 7.114 | 0.66449 | 4 | 15386.0344 | 33023.9323 | 313.6651 | 673.2375 | 80.8268 | 11.7544 | 61.4676 | 2558498.5508 | 0 | 1939734.6165 | 0 | 0 | 0 | 1413137.9575 | 2305434.7387 | 5998268.2804 | 4093941.3534 | 18309015.4973 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 40895288.2897 | 87775914.1571 | 10000 | 2.6579 | 15386.0344 | 33023.9323 | 313.6651 | 673.2375
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.4176 | 8.4193 | 0.80693 | 4 | 13294.6531 | 27819.1143 | 271.0295 | 567.1303 | 80.6838 | 11.6415 | 64.8725 | 2852427.6505 | 0 | 2207376.5104 | 0 | 0 | 0 | 1502428.7617 | 2559270.8398 | 6658697.7465 | 4544698.0345 | 20324899.5434 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 42911172.3358 | 89791798.2032 | 13335.2143 | 3.2277 | 13294.6531 | 27819.1143 | 271.0295 | 567.1303
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1935 | 9.6763 | 0.95037 | 4 | 11751.0217 | 24083.2474 | 239.5605 | 490.9696 | 80.4442 | 11.5108 | 66.6855 | 3115112.8274 | 0 | 2456049.2417 | 0 | 0 | 0 | 1559323.4233 | 2780889.342 | 7235303.6291 | 4938243.3975 | 22084921.8609 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 44671194.6534 | 91551820.5208 | 17782.7941 | 3.8015 | 11751.0217 | 24083.2474 | 239.5605 | 490.9696
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9561 | 10.8134 | 1.0861 | 4 | 10613.6079 | 21404.3988 | 216.3728 | 436.3576 | 80.1515 | 11.3752 | 69.6032 | 3336675.0511 | 0 | 2674184.1488 | 0 | 0 | 0 | 1584444.2546 | 2962168.3473 | 7706954.4153 | 5260154.7505 | 23524580.9675 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 46110853.76 | 92991479.6274 | 23713.7371 | 4.3445 | 10613.6079 | 21404.3988 | 216.3728 | 436.3576
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.5077 | 11.8008 | 1.2083 | 4 | 9775.6538 | 19475.0942 | 199.2899 | 397.0261 | 79.8434 | 11.2445 | 71.7127 | 3517460.7075 | 0 | 2859018.4102 | 0 | 0 | 0 | 1586290.83 | 3105480.2796 | 8079822.6658 | 5514644.9932 | 24662717.8862 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 47248990.6787 | 94129616.5461 | 31622.7766 | 4.8333 | 9775.6538 | 19475.0942 | 199.2899 | 397.0261
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.7487 | 12.6227 | 1.3135 | 4 | 9157.5584 | 18080.3986 | 186.6892 | 368.5934 | 79.5508 | 11.127 | 76.2744 | 3659910.8421 | 0 | 3009799.5341 | 0 | 0 | 0 | 1572289.2491 | 3214379.8539 | 8363157.0198 | 5708026.5117 | 25527563.0106 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 48113835.8031 | 94994461.6705 | 42169.6503 | 5.254 | 9157.5584 | 18080.3986 | 186.6892 | 368.5934
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7723 | 13.2884 | 1.401 | 4 | 8700.6864 | 17066.2672 | 177.3753 | 347.9189 | 79.2908 | 11.0262 | 80.4804 | 3770042.4758 | 0 | 3129982.9114 | 0 | 0 | 0 | 1550132.2147 | 3295561.4647 | 8574374.9186 | 5852187.0678 | 26172281.053 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 48758553.8455 | 95639179.7129 | 56234.1325 | 5.604 | 8700.6864 | 17066.2672 | 177.3753 | 347.9189
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7398 | 13.8166 | 1.4719 | 4 | 8362.1769 | 16324.6019 | 170.4743 | 332.7991 | 79.07 | 10.9427 | 82.5692 | 3854172.2862 | 0 | 3224201.8973 | 0 | 0 | 0 | 1525372.4276 | 3355461.1783 | 8730221.6863 | 5958555.689 | 26647985.1648 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 49234257.9573 | 96114883.8247 | 74989.4209 | 5.8877 | 8362.1769 | 16324.6019 | 170.4743 | 332.7991
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8292 | 14.2296 | 1.5283 | 4 | 8110.7831 | 15779.4292 | 165.3493 | 321.685 | 78.8887 | 10.8753 | 74.2624 | 3917943.609 | 0 | 3297166.7149 | 0 | 0 | 0 | 1501406.3941 | 3399441.52 | 8844649.5137 | 6036655.0325 | 26997262.7843 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 49583535.5767 | 96464161.4441 | 100000 | 6.1133 | 8110.7831 | 15779.4292 | 165.3493 | 321.685
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2265 | 14.5508 | 1.5726 | 4 | 7923.702 | 15376.5065 | 161.5354 | 313.4709 | 78.7424 | 10.8216 | 69.7458 | 3966377.5047 | 0 | 3353552.5535 | 0 | 0 | 0 | 1480271.2266 | 3432078.5011 | 8929564.2437 | 6094611.0805 | 27256455.1102 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 49842727.9026 | 96723353.77 | 133352.1432 | 6.2903 | 7923.702 | 15376.5065 | 161.5354 | 313.4709
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.048 | 14.7956 | 1.6068 | 4 | 7784.242 | 15078.3575 | 158.6923 | 307.3927 | 78.6279 | 10.7799 | 91.1834 | 4002563.512 | 0 | 3396264.4279 | 0 | 0 | 0 | 1462082.5384 | 3455755.0865 | 8991165.8623 | 6136655.451 | 27444486.8782 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50030759.6707 | 96911385.5381 | 177827.941 | 6.4272 | 7784.242 | 15078.3575 | 158.6923 | 307.3927
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.4318 | 14.982 | 1.6331 | 4 | 7680.1377 | 14856.9117 | 156.57 | 302.8782 | 78.539 | 10.7478 | 81.3269 | 4029697.7373 | 0 | 3428637.9792 | 0 | 0 | 0 | 1447121.9941 | 3473128.5071 | 9036367.9389 | 6167506.7971 | 27582460.9536 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50168733.7461 | 97049359.6135 | 237137.3706 | 6.5323 | 7680.1377 | 14856.9117 | 156.57 | 302.8782
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.4964 | 15.1254 | 1.6532 | 4 | 7602.3413 | 14691.6216 | 154.984 | 299.5086 | 78.4695 | 10.7228 | 95.4273 | 4050365.0366 | 0 | 3453502.7475 | 0 | 0 | 0 | 1435396.4173 | 3486313.0385 | 9070671.3852 | 6190919.604 | 27687168.2291 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50273441.0216 | 97154066.889 | 316227.766 | 6.6129 | 7602.3413 | 14691.6216 | 154.984 | 299.5086
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2929 | 15.2329 | 1.6685 | 4 | 7544.1557 | 14568.5549 | 153.7978 | 296.9997 | 78.4168 | 10.704 | 88.5722 | 4065706.9084 | 0 | 3472080.2141 | 0 | 0 | 0 | 1426022.5091 | 3495885.7563 | 9095577.6332 | 6207918.6301 | 27763191.6513 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50349464.4438 | 97230090.3112 | 421696.5034 | 6.674 | 7544.1557 | 14568.5549 | 153.7978 | 296.9997
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8996 | 15.3148 | 1.6801 | 4 | 7500.6095 | 14476.4952 | 152.9101 | 295.1229 | 78.3763 | 10.6895 | 84.5511 | 4077326.7881 | 0 | 3486220.0418 | 0 | 0 | 0 | 1418829.4566 | 3503126.7517 | 9114417.2179 | 6220777.0338 | 27820697.29 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50406970.0824 | 97287595.9498 | 562341.3252 | 6.7204 | 7500.6095 | 14476.4952 | 152.9101 | 295.1229
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3406 | 15.3746 | 1.6888 | 4 | 7468.0033 | 14408.0716 | 152.2453 | 293.728 | 78.3467 | 10.679 | 87.188 | 4085734.2088 | 0 | 3496489.1064 | 0 | 0 | 0 | 1413032.9749 | 3508149.9531 | 9127486.5575 | 6229697.1266 | 27860589.9273 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50446862.7198 | 97327488.5872 | 749894.2093 | 6.7551 | 7468.0033 | 14408.0716 | 152.2453 | 293.728
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.687 | 15.4214 | 1.6954 | 4 | 7443.5798 | 14356.5194 | 151.7474 | 292.6771 | 78.3233 | 10.6707 | 91.4966 | 4092316.0285 | 0 | 3504550.5763 | 0 | 0 | 0 | 1408831.2209 | 3512222.152 | 9138081.5838 | 6236928.4497 | 27892930.0112 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50479202.8037 | 97359828.6711 | 1000000 | 6.7816 | 7443.5798 | 14356.5194 | 151.7474 | 292.6771
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9324 | 15.4547 | 1.7003 | 4 | 7425.2803 | 14318.2955 | 151.3744 | 291.8978 | 78.3067 | 10.6647 | 82.6386 | 4096967.3276 | 0 | 3510259.9506 | 0 | 0 | 0 | 1405397.1992 | 3514923.5462 | 9145110.0572 | 6241725.5273 | 27914383.6081 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50500656.4006 | 97381282.268 | 1333521.4322 | 6.8012 | 7425.2803 | 14318.2955 | 151.3744 | 291.8978
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.1371 | 15.4822 | 1.7041 | 4 | 7411.5664 | 14289.1729 | 151.0948 | 291.3041 | 78.2928 | 10.6598 | 78.262 | 4100839.7608 | 0 | 3515020.4849 | 0 | 0 | 0 | 1403112.2181 | 3517399.2609 | 9151551.359 | 6246121.8481 | 27934044.9317 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50520317.7241 | 97400943.5915 | 1778279.41 | 6.8164 | 7411.5664 | 14289.1729 | 151.0948 | 291.3041
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.2808 | 15.5017 | 1.7069 | 4 | 7401.2873 | 14267.5992 | 150.8853 | 290.8643 | 78.283 | 10.6563 | 82.618 | 4103554.6222 | 0 | 3518362.3826 | 0 | 0 | 0 | 1401227.1857 | 3519026.2343 | 9155784.4101 | 6249010.9924 | 27946965.8273 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50533238.6198 | 97413864.4872 | 2371373.7057 | 6.8276 | 7401.2873 | 14267.5992 | 150.8853 | 290.8643
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3929 | 15.5168 | 1.709 | 4 | 7393.5819 | 14251.332 | 150.7282 | 290.5327 | 78.2753 | 10.6536 | 84.5612 | 4105669.2292 | 0 | 3520967.6949 | 0 | 0 | 0 | 1399869.8009 | 3520337.6227 | 9159196.3738 | 6251339.7278 | 27957380.4492 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50543653.2416 | 97424279.109 | 3162277.6602 | 6.8362 | 7393.5819 | 14251.332 | 150.7282 | 290.5327
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.466 | 15.5268 | 1.7106 | 4 | 7387.8051 | 14239.4052 | 150.6104 | 290.2895 | 78.2703 | 10.6518 | 83.0507 | 4107048.2941 | 0 | 3522668.1695 | 0 | 0 | 0 | 1398676.6963 | 3521073.3324 | 9161110.5393 | 6252646.1851 | 27963223.2166 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50549496.0091 | 97430121.8765 | 4216965.0343 | 6.8423 | 7387.8051 | 14239.4052 | 150.6104 | 290.2895
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5346 | 15.536 | 1.7118 | 4 | 7383.4741 | 14230.1348 | 150.5221 | 290.1005 | 78.2657 | 10.6502 | 75.8372 | 4108339.9409 | 0 | 3524261.3079 | 0 | 0 | 0 | 1397991.3432 | 3521931.1109 | 9163342.3031 | 6254169.4097 | 27970035.4156 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50556308.2081 | 97436934.0755 | 5623413.2519 | 6.8472 | 7383.4741 | 14230.1348 | 150.5221 | 290.1005
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5781 | 15.5419 | 1.7127 | 4 | 7380.2268 | 14223.376 | 150.4559 | 289.9628 | 78.2627 | 10.6491 | 81.8843 | 4109159.6163 | 0 | 3525272.8876 | 0 | 0 | 0 | 1397353.1746 | 3522396.4146 | 9164552.9281 | 6254995.6861 | 27973730.7074 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50560003.4999 | 97440629.3673 | 7498942.0933 | 6.8507 | 7380.2268 | 14223.376 | 150.4559 | 289.9628
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6124 | 15.5466 | 1.7134 | 4 | 7377.7919 | 14218.2698 | 150.4063 | 289.8587 | 78.2603 | 10.6483 | 72.5209 | 4109804.7502 | 0 | 3526069.2459 | 0 | 0 | 0 | 1396898.8255 | 3522781.4005 | 9165554.5821 | 6255679.3356 | 27976788.1399 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 50563060.9323 | 97443686.7998 | 10000000 | 6.8534 | 7377.7919 | 14218.2698 | 150.4063 | 289.8587
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.3478 | [19 empty] | 100 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1857 | [19 empty] | 133.3521 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.019526 | 0.0011287 | 4 | 5356432.4755 | 15994557.8403 | 109198.1211 | 326070.6958 | 54.779 | 9.9649 | 24.9703 | 136876.3784 | 0 | 55932.4308 | 0 | 0 | 0 | 139976.8427 | 129786.4042 | 337677.6009 | 230471.9012 | 1030721.5582 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 24183556.3068 | 72213229.9625 | 177.8279 | 0.0045149 | 5356432.4755 | 15994557.8403 | 109198.1211 | 326070.6958
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0076956 | 0.0039626 | 4 | 1522476.3298 | 4552641.5671 | 31037.7393 | 92811.7562 | 54.779 | 9.9649 | 25.2295 | 136876.3799 | 0 | 55932.43 | 0 | 0 | 0 | 123341.0186 | 123298.4331 | 320797.231 | 218950.7019 | 979196.1946 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 24132030.9432 | 72161704.5989 | 237.1374 | 0.015851 | 1522476.3298 | 4552641.5671 | 31037.7393 | 92811.7562
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.923 | 0.093213 | 0.0099926 | 4 | 624186.9989 | 1825816.5916 | 12724.8962 | 37221.7408 | 64.7983 | 10.9436 | 47.6839 | 244291.5218 | 0 | 123068.5179 | 0 | 0 | 0 | 212572.9352 | 226173.8602 | 588457.9897 | 401634.6696 | 1796199.4944 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 24949034.243 | 72978707.8987 | 316.2278 | 0.03997 | 624186.9989 | 1825816.5916 | 12724.8962 | 37221.7408
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 0.20234 | 0.018178 | 4 | 350962.0885 | 1011515.6717 | 7154.8369 | 20621.1151 | 69.0198 | 11.3226 | 46.85 | 323451.2789 | 0 | 174148.0998 | 0 | 0 | 0 | 266321.2058 | 297929.0279 | 775150.2171 | 529055.9509 | 2366055.7803 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 25518890.5289 | 73548564.1846 | 421.6965 | 0.072711 | 350962.0885 | 1011515.6717 | 7154.8369 | 20621.1151
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.354 | 0.35317 | 0.029874 | 4 | 219136.663 | 621075.2443 | 4467.3973 | 12661.4589 | 72.3452 | 11.6054 | 41.2222 | 416540.8137 | 0 | 235709.007 | 0 | 0 | 0 | 326976.8291 | 381898.3934 | 993621.2815 | 678166.9415 | 3032913.2661 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 26185748.0147 | 74215421.6704 | 562.3413 | 0.1195 | 219136.663 | 621075.2443 | 4467.3973 | 12661.4589
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1197 | 0.55795 | 0.046097 | 4 | 146337.0109 | 406819.4979 | 2983.2779 | 8293.5657 | 75.0033 | 11.8214 | 46.6888 | 527702.3424 | 0 | 311073.1832 | 0 | 0 | 0 | 397757.9853 | 482248.0693 | 1254710.5536 | 856365.7345 | 3829857.8684 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 26982692.617 | 75012366.2727 | 749.8942 | 0.18439 | 146337.0109 | 406819.4979 | 2983.2779 | 8293.5657
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3661 | 0.82654 | 0.068135 | 4 | 102420.8964 | 278650.3916 | 2087.9885 | 5680.6651 | 77.0786 | 11.9826 | 37.3437 | 657859.4344 | 0 | 401576.1179 | 0 | 0 | 0 | 477734.9662 | 599496.5022 | 1559766.9251 | 1064572.9764 | 4761006.9221 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 27913841.6707 | 75943515.3264 | 1000 | 0.27254 | 102420.8964 | 278650.3916 | 2087.9885 | 5680.6651
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2555 | 1.1781 | 0.097704 | 4 | 74251.4407 | 197147.0344 | 1513.7161 | 4019.109 | 78.7113 | 12.1031 | 40.3768 | 812070.9795 | 0 | 511559.4275 | 0 | 0 | 0 | 570267.5655 | 738620.2093 | 1921738.2727 | 1311625.8589 | 5865882.3134 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 29018717.062 | 77048390.7177 | 1333.5214 | 0.39082 | 74251.4407 | 197147.0344 | 1513.7161 | 4019.109
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9406 | 1.6319 | 0.13692 | 4 | 55357.3737 | 143051.8398 | 1128.5349 | 2916.3052 | 79.977 | 12.1901 | 55.1509 | 993419.0066 | 0 | 644238.2552 | 0 | 0 | 0 | 676014.852 | 902332.1244 | 2347683.0939 | 1602341.9517 | 7166029.2838 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 30318864.0324 | 78348537.6881 | 1778.2794 | 0.54769 | 55357.3737 | 143051.8398 | 1128.5349 | 2916.3052
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6009 | 2.2105 | 0.18836 | 4 | 42255.9617 | 106003.5125 | 861.4449 | 2161.025 | 80.9419 | 12.2481 | 45.7689 | 1205164.8145 | 0 | 803196.2397 | 0 | 0 | 0 | 795513.5668 | 1093511.1022 | 2845091.578 | 1941833.4627 | 8684310.7639 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 31837145.5125 | 79866819.1682 | 2371.3737 | 0.75344 | 42255.9617 | 106003.5125 | 861.4449 | 2161.025
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4009 | 2.9357 | 0.25486 | 4 | 32942.0537 | 80056.3852 | 671.5683 | 1632.0577 | 81.6552 | 12.2787 | 52.8339 | 1448873.3226 | 0 | 991015.3233 | 0 | 0 | 0 | 927359.2325 | 1313226.6726 | 3416746.4223 | 2331999.6404 | 10429220.6138 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 33582055.3624 | 81611729.0181 | 3162.2777 | 1.0194 | 32942.0537 | 80056.3852 | 671.5683 | 1632.0577
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4922 | 3.8279 | 0.33927 | 4 | 26198.3684 | 61590.1467 | 534.0892 | 1255.5984 | 82.1553 | 12.2817 | 54.5185 | 1724868.8589 | 0 | 1209600.0285 | 0 | 0 | 0 | 1069269.9098 | 1561458.1309 | 4062593.7576 | 2772803.7175 | 12400594.4033 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 35553429.1519 | 83583102.8076 | 4216.965 | 1.3571 | 26198.3684 | 61590.1467 | 534.0892 | 1255.5984
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8797 | 4.8904 | 0.44351 | 4 | 21253.7056 | 48327.2664 | 433.2855 | 985.2167 | 82.4656 | 12.2546 | 69.299 | 2027742.8321 | 0 | 1456523.7165 | 0 | 0 | 0 | 1214142.0192 | 1832379.3415 | 4767475.1738 | 3253899.7679 | 14552162.851 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 37704997.5996 | 85734671.2553 | 5623.4133 | 1.774 | 21253.7056 | 48327.2664 | 433.2855 | 985.2167
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.4071 | 6.1064 | 0.56753 | 4 | 17601.654 | 38759.1039 | 358.8335 | 790.1568 | 82.6037 | 12.1951 | 52.7853 | 2347514.5356 | 0 | 1725531.0958 | 0 | 0 | 0 | 1352665.1065 | 2116027.1878 | 5505468.6857 | 3757595.5041 | 16804802.1154 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 39957636.864 | 87987310.5197 | 7498.9421 | 2.2701 | 17601.654 | 38759.1039 | 358.8335 | 790.1568
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.6675 | 7.4271 | 0.70796 | 4 | 14897.8897 | 31858.4826 | 303.7136 | 649.4783 | 82.5849 | 12.1029 | 64.225 | 2668196.2206 | 0 | 2004727.5083 | 0 | 0 | 0 | 1473035.7728 | 2396924.2057 | 6236305.1064 | 4256406.3784 | 19035595.1921 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 42188429.9407 | 90218103.5964 | 10000 | 2.8318 | 14897.8897 | 31858.4826 | 303.7136 | 649.4783
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9964 | 8.7692 | 0.85755 | 4 | 12898.4302 | 26900.4072 | 262.9519 | 548.4012 | 82.4329 | 11.9834 | 75.0796 | 2969541.1519 | 0 | 2277026.2252 | 0 | 0 | 0 | 1563157.6425 | 2655792.7577 | 6909827.9774 | 4716099.5774 | 21091445.3321 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 44244280.0806 | 92273953.7363 | 13335.2143 | 3.4302 | 12898.4302 | 26900.4072 | 262.9519 | 548.4012
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.7749 | 10.0518 | 1.0072 | 4 | 11423.2063 | 23344.5212 | 232.8775 | 475.9096 | 82.1845 | 11.847 | 62.5522 | 3236799.0241 | 0 | 2528133.3303 | 0 | 0 | 0 | 1619033.154 | 2879746.5483 | 7492509.8014 | 5113791.8951 | 22870013.7532 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 46022848.5018 | 94052522.1575 | 17782.7941 | 4.0289 | 11423.2063 | 23344.5212 | 232.8775 | 475.9096
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.5297 | 11.2104 | 1.1483 | 4 | 10336.4344 | 20793.0128 | 210.7222 | 423.8937 | 81.8836 | 11.706 | 67.4694 | 3462066.9702 | 0 | 2748258.6333 | 0 | 0 | 0 | 1643402.5595 | 3062953.9836 | 7969177.967 | 5439127.7127 | 24324987.8262 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 47477822.5748 | 95507496.2305 | 23713.7371 | 4.5932 | 10336.4344 | 20793.0128 | 210.7222 | 423.8937
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0157 | 12.2091 | 1.2746 | 4 | 9535.8306 | 18956.4005 | 194.4008 | 386.4519 | 81.5705 | 11.5715 | 76.4763 | 3644547.6286 | 0 | 2933404.5264 | 0 | 0 | 0 | 1643680.5749 | 3206436.7647 | 8342490.731 | 5693921.345 | 25464481.5706 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 48617316.3191 | 96646989.9748 | 31622.7766 | 5.0984 | 9535.8306 | 18956.4005 | 194.4008 | 386.4519
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1908 | 13.0388 | 1.3829 | 4 | 8945.2475 | 17627.8914 | 182.361 | 359.3684 | 81.2746 | 11.4512 | 72.354 | 3788163.7911 | 0 | 3084212.5389 | 0 | 0 | 0 | 1628535.5016 | 3315355.6143 | 8625875.2354 | 5887337.0922 | 26329479.7735 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 49482314.522 | 97511988.1777 | 42169.6503 | 5.5317 | 8945.2475 | 17627.8914 | 182.361 | 359.3684
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1749 | 13.7122 | 1.4729 | 4 | 8508.6575 | 16660.6538 | 173.4605 | 339.65 | 81.0113 | 11.3478 | 78.9163 | 3899565.7486 | 0 | 3204779.5296 | 0 | 0 | 0 | 1606018.0109 | 3397041.6828 | 8838405.6295 | 6032393.4532 | 26978204.0547 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 50131038.8032 | 98160712.459 | 56234.1325 | 5.8918 | 8508.6575 | 16660.6538 | 173.4605 | 339.65
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.0971 | 14.2449 | 1.5457 | 4 | 8185.13 | 15953.2883 | 166.8649 | 325.2294 | 80.7889 | 11.2626 | 81.5984 | 3984403.921 | 0 | 3298981.7822 | 0 | 0 | 0 | 1580896.1036 | 3457069.9046 | 8994586.7493 | 6138990.2767 | 27454928.7373 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 50607763.4859 | 98637437.1416 | 74989.4209 | 6.1829 | 8185.13 | 15953.2883 | 166.8649 | 325.2294
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1445 | 14.6604 | 1.6035 | 4 | 7944.8304 | 15433.2485 | 161.9661 | 314.6276 | 80.6068 | 11.194 | 79.0322 | 4048601.1005 | 0 | 3371785.1076 | 0 | 0 | 0 | 1556664.9331 | 3501049.9451 | 9109013.793 | 6217089.0852 | 27804203.9645 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 50957038.7131 | 98986712.3688 | 100000 | 6.4139 | 7944.8304 | 15433.2485 | 161.9661 | 314.6276
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4903 | 14.9813 | 1.6486 | 4 | 7765.985 | 15049.2466 | 158.3201 | 306.7992 | 80.4611 | 11.1398 | 89.235 | 4096993.9705 | 0 | 3427606.6719 | 0 | 0 | 0 | 1535094.0183 | 3533280.9177 | 9192872.1722 | 6274324.1522 | 28060171.9028 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51213006.6514 | 99242680.3071 | 133352.1432 | 6.5945 | 7765.985 | 15049.2466 | 158.3201 | 306.7992
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.2808 | 15.2269 | 1.6836 | 4 | 7632.6519 | 14764.7715 | 155.6019 | 300.9998 | 80.3467 | 11.0977 | 77.0152 | 4133328.857 | 0 | 3470087.4726 | 0 | 0 | 0 | 1516780.4247 | 3556876.7342 | 9254263.6466 | 6316225.0949 | 28247562.23 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51400396.9786 | 99430070.6343 | 177827.941 | 6.7343 | 7632.6519 | 14764.7715 | 155.6019 | 300.9998
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.6498 | 15.4149 | 1.7104 | 4 | 7533.1138 | 14553.2015 | 153.5727 | 296.6867 | 80.2573 | 11.065 | 76.2479 | 4160757.5867 | 0 | 3502495.4276 | 0 | 0 | 0 | 1501910.0147 | 3574413.5813 | 9299890.9256 | 6347366.6504 | 28386834.1863 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51539668.9349 | 99569342.5906 | 237137.3706 | 6.8417 | 7533.1138 | 14553.2015 | 153.5727 | 296.6867
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.695 | 15.5585 | 1.731 | 4 | 7458.7255 | 14395.4549 | 152.0562 | 293.4708 | 80.188 | 11.0397 | 86.206 | 4181493.63 | 0 | 3527197.612 | 0 | 0 | 0 | 1490142.5941 | 3587545.1961 | 9334056.6935 | 6370685.489 | 28491121.2146 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51643955.9631 | 99673629.6188 | 316227.766 | 6.924 | 7458.7255 | 14395.4549 | 152.0562 | 293.4708
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4797 | 15.6666 | 1.7466 | 4 | 7403.0865 | 14277.9151 | 150.9219 | 291.0746 | 80.1353 | 11.0206 | 91.7337 | 4196945.7978 | 0 | 3545722.0468 | 0 | 0 | 0 | 1480797.4863 | 3597151.479 | 9359050.2713 | 6387744.1194 | 28567411.2006 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51720245.9492 | 99749919.6049 | 421696.5034 | 6.9863 | 7403.0865 | 14277.9151 | 150.9219 | 291.0746
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0593 | 15.7466 | 1.7583 | 4 | 7361.4448 | 14190.4243 | 150.073 | 289.291 | 80.096 | 11.0064 | 72.3688 | 4208292.4976 | 0 | 3559389.9739 | 0 | 0 | 0 | 1473336.9421 | 3603997.5713 | 9376862.399 | 6399901.2626 | 28621780.6464 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51774615.395 | 99804289.0507 | 562341.3252 | 7.0332 | 7361.4448 | 14190.4243 | 150.073 | 289.291
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5197 | 15.8099 | 1.7673 | 4 | 7330.2639 | 14124.4337 | 149.4373 | 287.9457 | 80.0646 | 10.9951 | 78.6719 | 4217269.0379 | 0 | 3570241.9763 | 0 | 0 | 0 | 1467986.2124 | 3609643.9184 | 9391553.0359 | 6409927.9241 | 28666622.1052 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51819456.8537 | 99849130.5095 | 749894.2093 | 7.0692 | 7330.2639 | 14124.4337 | 149.4373 | 287.9457
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8487 | 15.8554 | 1.774 | 4 | 7306.9076 | 14075.4801 | 148.9612 | 286.9477 | 80.042 | 10.9869 | 80.6392 | 4223659.8668 | 0 | 3577990.0738 | 0 | 0 | 0 | 1463608.6183 | 3613450.838 | 9401457.8597 | 6416688.1699 | 28696855.4264 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51849690.175 | 99879363.8307 | 1000000 | 7.096 | 7306.9076 | 14075.4801 | 148.9612 | 286.9477
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0922 | 15.8891 | 1.779 | 4 | 7289.4074 | 14038.92 | 148.6044 | 286.2024 | 80.0253 | 10.9809 | 84.5985 | 4228380.3592 | 0 | 3583724.8654 | 0 | 0 | 0 | 1460219.7567 | 3616206.7427 | 9408628.1585 | 6421582.0461 | 28718741.9285 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51871576.6771 | 99901250.3328 | 1333521.4322 | 7.116 | 7289.4074 | 14038.92 | 148.6044 | 286.2024
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.2897 | 15.9162 | 1.7829 | 4 | 7276.2924 | 14011.1956 | 148.3371 | 285.6372 | 80.0117 | 10.976 | 86.9187 | 4232200.366 | 0 | 3588372.6429 | 0 | 0 | 0 | 1457883.5719 | 3618598.0665 | 9414849.8925 | 6425828.5075 | 28737733.0473 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51890567.7959 | 99920241.4516 | 1778279.41 | 7.1315 | 7276.2924 | 14011.1956 | 148.3371 | 285.6372
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.4406 | 15.9369 | 1.7858 | 4 | 7266.4622 | 13990.3621 | 148.1367 | 285.2125 | 80.0012 | 10.9722 | 88.2241 | 4235116.8558 | 0 | 3591925.4855 | 0 | 0 | 0 | 1456159.3713 | 3620448.6679 | 9419664.7778 | 6429114.7656 | 28752429.9238 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51905264.6724 | 99934938.3281 | 2371373.7057 | 7.1431 | 7266.4622 | 13990.3621 | 148.1367 | 285.2125
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.5332 | 15.9499 | 1.7878 | 4 | 7259.0931 | 13975.2392 | 147.9864 | 284.9042 | 79.9948 | 10.9699 | 85.8955 | 4236903.399 | 0 | 3594104.2189 | 0 | 0 | 0 | 1454527.2539 | 3621358.6 | 9422032.2344 | 6430730.6034 | 28759656.3095 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51912491.0581 | 99942164.7138 | 3162277.6602 | 7.1514 | 7259.0931 | 13975.2392 | 147.9864 | 284.9042
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.6233 | 15.9622 | 1.7895 | 4 | 7253.5686 | 13963.4214 | 147.8738 | 284.6632 | 79.9886 | 10.9677 | 93.8043 | 4238639.4534 | 0 | 3596222.191 | 0 | 0 | 0 | 1453625.6635 | 3622510.0501 | 9425028.0713 | 6432775.3236 | 28768800.7529 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51921635.5014 | 99951309.1572 | 4216965.0343 | 7.1581 | 7253.5686 | 13963.4214 | 147.8738 | 284.6632
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.677 | 15.9697 | 1.7907 | 4 | 7249.4266 | 13954.8882 | 147.7894 | 284.4893 | 79.9848 | 10.9663 | 88.1777 | 4239674.2908 | 0 | 3597485.6407 | 0 | 0 | 0 | 1452726.5721 | 3623055.7364 | 9426447.8352 | 6433744.3417 | 28773134.417 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51925969.1656 | 99955642.8213 | 5623413.2519 | 7.1628 | 7249.4266 | 13954.8882 | 147.7894 | 284.4893
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7307 | 15.977 | 1.7917 | 4 | 7246.321 | 13948.1759 | 147.7261 | 284.3524 | 79.9811 | 10.965 | 83.0161 | 4240709.3266 | 0 | 3598749.4507 | 0 | 0 | 0 | 1452264.4445 | 3623772.0565 | 9428311.5531 | 6435016.3674 | 28778823.1987 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51931657.9472 | 99961331.603 | 7498942.0933 | 7.1666 | 7246.321 | 13948.1759 | 147.7261 | 284.3524
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7501 | 15.9799 | 1.7922 | 4 | 7243.9924 | 13943.633 | 147.6786 | 284.2598 | 79.9797 | 10.9645 | 83.2309 | 4241083.1806 | 0 | 3599206.4918 | 0 | 0 | 0 | 1451585.3284 | 3623831.2503 | 9428465.5634 | 6435121.4826 | 28779293.2973 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51932128.0458 | 99961801.7015 | 10000000 | 7.169 | 7243.9924 | 13943.633 | 147.6786 | 284.2598
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5079 | [19 empty] | 100 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9346 | [19 empty] | 133.3521 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.020971 | 0.0013093 | 4 | 4729218.2392 | 14122452.3278 | 96411.5105 | 287905.2927 | 55.2166 | 10.2295 | 24.6427 | 138988.242 | 0 | 55793.6953 | 0 | 0 | 0 | 141555.5287 | 131171.6118 | 341281.6268 | 232931.7229 | 1041722.4275 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 24766979.2231 | 73959471.8807 | 177.8279 | 0.005237 | 4729218.2392 | 14122452.3278 | 96411.5105 | 287905.2927
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.0091783 | 0.004133 | 4 | 1495030.7088 | 4470615.2376 | 30478.2232 | 91139.5386 | 55.2166 | 10.2295 | 24.7592 | 138988.2437 | 0 | 55793.6945 | 0 | 0 | 0 | 125067.8184 | 124741.4051 | 324551.5481 | 221513.1004 | 990655.8102 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 24715912.6058 | 73908405.2633 | 237.1374 | 0.016532 | 1495030.7088 | 4470615.2376 | 30478.2232 | 91139.5386
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0176 | 0.099833 | 0.010769 | 4 | 594436.9073 | 1736431.2309 | 12118.4004 | 35399.4993 | 66.0962 | 11.2897 | 45.9052 | 256057.5009 | 0 | 128303.6036 | 0 | 0 | 0 | 222847.4516 | 236811.3369 | 616134.5219 | 420524.4715 | 1880678.8863 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 25605935.6819 | 74798428.3394 | 316.2278 | 0.043076 | 594436.9073 | 1736431.2309 | 12118.4004 | 35399.4993
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1313 | 0.21547 | 0.019562 | 4 | 334939.1766 | 963621.429 | 6828.1882 | 19644.7262 | 70.4631 | 11.6784 | 53.52 | 339721.1854 | 0 | 181845.708 | 0 | 0 | 0 | 280022.2735 | 312619.7751 | 813372.5277 | 555143.4633 | 2482724.933 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 26207981.7286 | 75400474.3861 | 421.6965 | 0.078247 | 334939.1766 | 963621.429 | 6828.1882 | 19644.7262
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5534 | 0.37567 | 0.032123 | 4 | 209462.1683 | 592306.5085 | 4270.1696 | 12074.9693 | 73.9004 | 11.9677 | 48.977 | 438294.6412 | 0 | 246505.7826 | 0 | 0 | 0 | 344817.4619 | 401550.9755 | 1044753.2687 | 713065.5734 | 3188987.7034 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 26914244.4989 | 76106737.1565 | 562.3413 | 0.12849 | 209462.1683 | 592306.5085 | 4270.1696 | 12074.9693
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3561 | 0.58904 | 0.049506 | 4 | 140060.6924 | 388475.6746 | 2855.3267 | 7919.6021 | 76.5903 | 12.1839 | 51.7158 | 553406.114 | 0 | 323906.1127 | 0 | 0 | 0 | 417488.7944 | 504972.3982 | 1313834.5962 | 896719.1085 | 4010327.124 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 27735583.9196 | 76928076.5771 | 749.8942 | 0.19803 | 140060.6924 | 388475.6746 | 2855.3267 | 7919.6021
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6802 | 0.87191 | 0.073136 | 4 | 98144.5078 | 266299.2909 | 2000.8085 | 5428.8712 | 78.7249 | 12.3477 | 48.021 | 690065.6062 | 0 | 418132.5466 | 0 | 0 | 0 | 501687.7556 | 627855.5042 | 1633551.2312 | 1114932.2814 | 4986224.9251 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 28711481.7206 | 77903974.3782 | 1000 | 0.29254 | 98144.5078 | 266299.2909 | 2000.8085 | 5428.8712
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6692 | 1.2421 | 0.10483 | 4 | 71232.1528 | 188546.7751 | 1452.1638 | 3843.781 | 80.403 | 12.4699 | 38.5116 | 851951.2522 | 0 | 532621.2809 | 0 | 0 | 0 | 599083.418 | 773625.8209 | 2012815.6936 | 1373788.0701 | 6143885.5357 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 29869142.3313 | 79061634.9888 | 1333.5214 | 0.41932 | 71232.1528 | 188546.7751 | 1452.1638 | 3843.781
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4741 | 1.7191 | 0.14684 | 4 | 53167.1122 | 136919.2655 | 1083.8835 | 2791.2844 | 81.7007 | 12.5574 | 47.4007 | 1041956.1437 | 0 | 670470.3262 | 0 | 0 | 0 | 709999.9673 | 944746.3105 | 2458036.1058 | 1677660.1498 | 7502869.0032 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 31228125.7988 | 80420618.4563 | 1778.2794 | 0.58736 | 53167.1122 | 136919.2655 | 1083.8835 | 2791.2844
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.264 | 2.3249 | 0.20185 | 4 | 40632.3867 | 101559.1272 | 828.3462 | 2070.4202 | 82.6863 | 12.6149 | 49.0993 | 1262861.6715 | 0 | 834913.807 | 0 | 0 | 0 | 834336.3279 | 1143523.6045 | 2975213.8499 | 2030644.5871 | 9081493.8478 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 32806750.6434 | 81999243.3009 | 2371.3737 | 0.8074 | 40632.3867 | 101559.1272 | 828.3462 | 2070.4202
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.2124 | 3.0825 | 0.27286 | 4 | 31716.7204 | 76787.7165 | 646.5882 | 1565.4215 | 83.414 | 12.6442 | 47.2638 | 1516644.6834 | 0 | 1028854.0568 | 0 | 0 | 0 | 971095.6397 | 1371471.8081 | 3568288.3173 | 2435430.0975 | 10891784.6028 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 34617041.3984 | 83809534.0559 | 3162.2777 | 1.0914 | 31716.7204 | 76787.7165 | 646.5882 | 1565.4215
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.4861 | 4.0146 | 0.36288 | 4 | 25259.0182 | 59149.5801 | 514.9393 | 1205.8442 | 83.924 | 12.6448 | 51.1991 | 1804159.821 | 0 | 1254667.0056 | 0 | 0 | 0 | 1118571.8407 | 1629185.4803 | 4238806.4277 | 2893072.4857 | 12938463.061 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 36663719.8565 | 85856212.5141 | 4216.965 | 1.4515 | 25259.0182 | 59149.5801 | 514.9393 | 1205.8442
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.0707 | 5.1224 | 0.47376 | 4 | 20523.2425 | 46481.6252 | 418.3941 | 947.5908 | 84.2381 | 12.6138 | 60.1112 | 2119026.0608 | 0 | 1509281.4699 | 0 | 0 | 0 | 1268728.0399 | 1909843.8725 | 4969021.9935 | 3391459.6138 | 15167361.0504 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 38892617.846 | 88085110.5035 | 5623.4133 | 1.8951 | 20523.2425 | 46481.6252 | 418.3941 | 947.5908
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7734 | 6.3843 | 0.60516 | 4 | 17025.7555 | 37347.7767 | 347.0931 | 761.3849 | 84.3741 | 12.549 | 66.0913 | 2449846.4209 | 0 | 1785397.148 | 0 | 0 | 0 | 1411091.4632 | 2202070.6625 | 5729336.1571 | 3910389.6533 | 17488131.5051 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 41213388.3006 | 90405880.9582 | 7498.9421 | 2.4206 | 17025.7555 | 37347.7767 | 347.0931 | 761.3849
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1413 | 7.7447 | 0.75311 | 4 | 14437.2648 | 30767.0581 | 294.3232 | 627.2281 | 84.3487 | 12.4508 | 72.278 | 2779103.3673 | 0 | 2069881.5337 | 0 | 0 | 0 | 1532833.6802 | 2488909.2466 | 6475631.3142 | 4419751.4329 | 19766110.5749 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 43491367.3704 | 92683860.028 | 10000 | 3.0124 | 14437.2648 | 30767.0581 | 294.3232 | 627.2281
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.5434 | 9.1225 | 0.90995 | 4 | 12523.8786 | 26039.0631 | 255.3162 | 530.8415 | 84.1878 | 12.3249 | 72.8144 | 3087562.8733 | 0 | 2346554.1594 | 0 | 0 | 0 | 1623453.6247 | 2752452.5564 | 7161316.9461 | 4887745.9661 | 21859086.126 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 45584342.9216 | 94776835.5791 | 13335.2143 | 3.6398 | 12523.8786 | 26039.0631 | 255.3162 | 530.8415
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.3406 | 10.4327 | 1.066 | 4 | 11112.673 | 22649.1628 | 226.5469 | 461.7338 | 83.9303 | 12.1823 | 82.2693 | 3359817.2521 | 0 | 2600512.5511 | 0 | 0 | 0 | 1678711.2783 | 2979226.0218 | 7751334.9854 | 5290445.4016 | 23660047.4904 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 47385304.2859 | 96577796.9435 | 17782.7941 | 4.2641 | 11112.673 | 22649.1628 | 226.5469 | 461.7338
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.0714 | 11.6108 | 1.2124 | 4 | 10073.2705 | 20216.8506 | 205.3572 | 412.1478 | 83.6218 | 12.0361 | 71.364 | 3588329.9097 | 0 | 2822203.3991 | 0 | 0 | 0 | 1701899.4541 | 3163848.7775 | 8231685.5245 | 5618294.5147 | 25126261.5795 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 48851518.3751 | 98044011.0326 | 23713.7371 | 4.8496 | 10073.2705 | 20216.8506 | 205.3572 | 412.1478
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5091 | 12.6227 | 1.3429 | 4 | 9307.594 | 18465.6584 | 189.7479 | 376.4474 | 83.3032 | 11.8977 | 76.1882 | 3772856.0138 | 0 | 3008053.3031 | 0 | 0 | 0 | 1700938.6028 | 3307920.6887 | 8606531.0843 | 5874134.3115 | 26270434.0043 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 49995690.7999 | 99188183.4575 | 31622.7766 | 5.3715 | 9307.594 | 18465.6584 | 189.7479 | 376.4474
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.6381 | 13.4624 | 1.4545 | 4 | 8742.7372 | 17198.0985 | 178.2325 | 350.6065 | 83.0032 | 11.7741 | 82.7337 | 3918015.3363 | 0 | 3159331.1104 | 0 | 0 | 0 | 1684984.8812 | 3417309.2179 | 8891137.5985 | 6068384.1056 | 27139162.2499 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 50864419.0455 | 100056911.703 | 42169.6503 | 5.8179 | 8742.7372 | 17198.0985 | 178.2325 | 350.6065
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.5561 | 14.1402 | 1.5469 | 4 | 8325.114 | 16275.4947 | 169.7187 | 331.798 | 82.7382 | 11.6687 | 84.7404 | 4030024.0087 | 0 | 3279602.003 | 0 | 0 | 0 | 1661507.3746 | 3498742.0207 | 9103009.0471 | 6212990.7228 | 27785875.1769 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 51511131.9725 | 100703624.6301 | 56234.1325 | 6.1874 | 8325.114 | 16275.4947 | 169.7187 | 331.798
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.4271 | 14.6764 | 1.6214 | 4 | 8015.5987 | 15600.2829 | 163.4088 | 318.0329 | 82.5147 | 11.5819 | 77.7637 | 4115395.6876 | 0 | 3373617.0487 | 0 | 0 | 0 | 1635860.6337 | 3558700.6143 | 9259009.0086 | 6319463.902 | 28262046.8949 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 51987303.6905 | 101179796.348 | 74989.4209 | 6.4858 | 8015.5987 | 15600.2829 | 163.4088 | 318.0329
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.4286 | 15.0938 | 1.6805 | 4 | 7785.677 | 15103.7918 | 158.7216 | 307.9112 | 82.3322 | 11.5123 | 82.1858 | 4179895.4167 | 0 | 3446137.6416 | 0 | 0 | 0 | 1611246.2855 | 3602538.944 | 9373067.3501 | 6397311.0637 | 28610196.7015 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 52335453.4971 | 101527946.1546 | 100000 | 6.722 | 7785.677 | 15103.7918 | 158.7216 | 307.9112
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7519 | 15.4177 | 1.7267 | 4 | 7614.5363 | 14736.6837 | 155.2326 | 300.4272 | 82.1855 | 11.4571 | 91.1801 | 4228805.1174 | 0 | 3502057.8298 | 0 | 0 | 0 | 1589701.9407 | 3635020.3062 | 9457577.1917 | 6454990.7671 | 28868153.1528 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 52593409.9484 | 101785902.6059 | 133352.1432 | 6.907 | 7614.5363 | 14736.6837 | 155.2326 | 300.4272
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.5159 | 15.6645 | 1.7624 | 4 | 7486.9356 | 14464.8833 | 152.6313 | 294.8862 | 82.0709 | 11.4143 | 95.5666 | 4265346.4245 | 0 | 3544394.7915 | 0 | 0 | 0 | 1571296.213 | 3658604.5973 | 9518938.6792 | 6496871.2432 | 29055451.9487 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 52780708.7443 | 101973201.4018 | 177827.941 | 7.0497 | 7486.9356 | 14464.8833 | 152.6313 | 294.8862
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8607 | 15.8529 | 1.7898 | 4 | 7391.6702 | 14262.784 | 150.6892 | 290.7661 | 81.9817 | 11.3812 | 81.825 | 4292860.6502 | 0 | 3576604.0928 | 0 | 0 | 0 | 1556326.263 | 3676058.4923 | 9564350.1337 | 6527865.494 | 29194065.126 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 52919321.9215 | 102111814.5791 | 237137.3706 | 7.1593 | 7391.6702 | 14262.784 | 150.6892 | 290.7661
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8741 | 15.9951 | 1.8107 | 4 | 7320.4711 | 14112.3947 | 149.2377 | 287.7003 | 81.9134 | 11.356 | 76.7341 | 4313394.1946 | 0 | 3600834.4596 | 0 | 0 | 0 | 1544278.7581 | 3688817.8908 | 9597547.4712 | 6550523.359 | 29295396.1332 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53020652.9287 | 102213145.5863 | 316227.766 | 7.2428 | 7320.4711 | 14112.3947 | 149.2377 | 287.7003
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6512 | 16.1041 | 1.8266 | 4 | 7267.2152 | 13999.9232 | 148.152 | 285.4074 | 81.8604 | 11.3366 | 78.5223 | 4329027.6945 | 0 | 3619396.2092 | 0 | 0 | 0 | 1535013.2972 | 3698540.5083 | 9622843.7277 | 6567788.5739 | 29372610.0108 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53097866.8064 | 102290359.4639 | 421696.5034 | 7.3065 | 7267.2152 | 13999.9232 | 148.152 | 285.4074
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.236 | 16.1863 | 1.8387 | 4 | 7227.3558 | 13915.9451 | 147.3394 | 283.6954 | 81.8202 | 11.3218 | 85.8919 | 4340723.8134 | 0 | 3633348.9877 | 0 | 0 | 0 | 1527795.5625 | 3705728.6618 | 9641545.8285 | 6580553.1419 | 29429695.9956 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53154952.7912 | 102347445.4487 | 562341.3252 | 7.3547 | 7227.3558 | 13915.9451 | 147.3394 | 283.6954
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.6723 | 16.2477 | 1.8477 | 4 | 7197.5089 | 13853.2493 | 146.731 | 282.4172 | 81.79 | 11.3108 | 90.595 | 4349415.3266 | 0 | 3643754.7094 | 0 | 0 | 0 | 1522175.9669 | 3710984.9411 | 9655221.5892 | 6589887.1296 | 29471439.6629 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53196696.4584 | 102389189.116 | 749894.2093 | 7.391 | 7197.5089 | 13853.2493 | 146.731 | 282.4172
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0083 | 16.2948 | 1.8546 | 4 | 7175.1513 | 13806.1584 | 146.2752 | 281.4572 | 81.7666 | 11.3022 | 79.4668 | 4356086.515 | 0 | 3651763.2362 | 0 | 0 | 0 | 1518008.8109 | 3715084.8392 | 9665888.683 | 6597167.6403 | 29503999.7248 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53229256.5204 | 102421749.1779 | 1000000 | 7.4186 | 7175.1513 | 13806.1584 | 146.2752 | 281.4572
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.2512 | 16.3291 | 1.8598 | 4 | 7158.3992 | 13771.128 | 145.9337 | 280.7431 | 81.7497 | 11.296 | 85.7805 | 4360897.2904 | 0 | 3657550.4947 | 0 | 0 | 0 | 1514679.1199 | 3717919.4929 | 9673263.8704 | 6602201.3573 | 29526511.6256 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53251768.4211 | 102444261.0787 | 1333521.4322 | 7.4391 | 7158.3992 | 13771.128 | 145.9337 | 280.7431
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.4339 | 16.3549 | 1.8636 | 4 | 7145.8447 | 13744.8882 | 145.6777 | 280.2081 | 81.7369 | 11.2914 | 94.5758 | 4364507.5684 | 0 | 3661900.1557 | 0 | 0 | 0 | 1512158.7042 | 3720040.907 | 9678783.3547 | 6605968.5187 | 29543359.2086 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53268616.0042 | 102461108.6617 | 1778279.41 | 7.4545 | 7145.8447 | 13744.8882 | 145.6777 | 280.2081
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.5756 | 16.3748 | 1.8666 | 4 | 7136.4345 | 13725.1245 | 145.4859 | 279.8052 | 81.7269 | 11.2878 | 90.2666 | 4367305.1772 | 0 | 3665274.4962 | 0 | 0 | 0 | 1510328.7412 | 3721734.2817 | 9683189.1683 | 6608975.577 | 29556807.4416 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53282064.2372 | 102474556.8947 | 2371373.7057 | 7.4662 | 7136.4345 | 13725.1245 | 145.4859 | 279.8052
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.6728 | 16.3886 | 1.8687 | 4 | 7129.3803 | 13710.5235 | 145.3421 | 279.5076 | 81.7201 | 11.2853 | 88.7848 | 4369222.7558 | 0 | 3667589.5904 | 0 | 0 | 0 | 1508799.1619 | 3722788.4882 | 9685931.9973 | 6610847.6142 | 29565179.6077 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53290436.4033 | 102482929.0609 | 3162277.6602 | 7.4748 | 7129.3803 | 13710.5235 | 145.3421 | 279.5076
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.7628 | 16.4011 | 1.8704 | 4 | 7124.0918 | 13699.1899 | 145.2342 | 279.2765 | 81.7138 | 11.283 | 99.7603 | 4370997.1654 | 0 | 3669732.8046 | 0 | 0 | 0 | 1507925.463 | 3723975.6189 | 9689020.6678 | 6612955.6953 | 29574607.4149 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53299864.2105 | 102492356.868 | 4216965.0343 | 7.4816 | 7124.0918 | 13699.1899 | 145.2342 | 279.2765
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8165 | 16.4087 | 1.8716 | 4 | 7120.1268 | 13691.0106 | 145.1534 | 279.1098 | 81.71 | 11.2816 | 95.315 | 4372054.8683 | 0 | 3671011.3133 | 0 | 0 | 0 | 1507042.1822 | 3724542.2619 | 9690494.9568 | 6613961.9278 | 29579107.5102 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53304364.3058 | 102496856.9633 | 5623413.2519 | 7.4864 | 7120.1268 | 13691.0106 | 145.1534 | 279.1098
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8554 | 16.4143 | 1.8725 | 4 | 7117.1538 | 13684.9107 | 145.0928 | 278.9854 | 81.7072 | 11.2806 | 96.911 | 4372820.4191 | 0 | 3671937.0275 | 0 | 0 | 0 | 1506355.573 | 3724934.0776 | 9691514.381 | 6614657.7057 | 29582219.184 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53307475.9796 | 102499968.6371 | 7498942.0933 | 7.49 | 7117.1538 | 13684.9107 | 145.0928 | 278.9854
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8897 | 16.4191 | 1.8732 | 4 | 7114.9247 | 13680.2211 | 145.0474 | 278.8898 | 81.7048 | 11.2797 | 87.7491 | 4373494.8952 | 0 | 3672752.6785 | 0 | 0 | 0 | 1505922.7534 | 3725346.4275 | 9692587.2308 | 6615389.9478 | 29585493.933 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 53310750.7286 | 102503243.3862 | 10000000 | 7.4928 | 7114.9247 | 13680.2211 | 145.0474 | 278.8898
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6681 | [19 empty] | 100 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.511 | [19 empty] | 133.3521 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.022405 | 0.0014835 | 4 | 4272929.1594 | 12760970.772 | 87109.4405 | 260149.6497 | 55.6387 | 10.4926 | 23.7209 | 141057.864 | 0 | 55645.1697 | 0 | 0 | 0 | 143129.722 | 132534.7747 | 344828.2972 | 235352.3984 | 1052548.2261 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 25356087.1595 | 75725170.0324 | 177.8279 | 0.0059341 | 4272929.1594 | 12760970.772 | 87109.4405 | 260149.6497
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.010652 | 0.0042973 | 4 | 1472173.9878 | 4402451.8195 | 30012.258 | 89749.9351 | 55.6387 | 10.4926 | 25.3288 | 141057.8657 | 0 | 55645.1689 | 0 | 0 | 0 | 126786.6675 | 126160.9839 | 328245.0008 | 224033.9578 | 1001929.6447 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 25305468.5781 | 75674551.451 | 237.1374 | 0.017189 | 1472173.9878 | 4402451.8195 | 30012.258 | 89749.9351
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1297 | 0.108 | 0.011597 | 4 | 566550.581 | 1652353.5696 | 11549.8999 | 33685.4625 | 67.4819 | 11.6437 | 46.2345 | 269404.0415 | 0 | 134464.1506 | 0 | 0 | 0 | 234779.8446 | 249072.7343 | 648036.1629 | 442297.997 | 1978054.931 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 26281593.8645 | 76650676.7374 | 316.2278 | 0.046389 | 566550.581 | 1652353.5696 | 11549.8999 | 33685.4625
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.22872 | 0.021023 | 4 | 319925.7442 | 918911.9116 | 6522.119 | 18733.2622 | 71.8999 | 12.0336 | 57.2286 | 356065.2051 | 0 | 189490.8542 | 0 | 0 | 0 | 293637.8625 | 327285.6295 | 851530.0724 | 581186.7716 | 2599196.3954 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 26902735.3288 | 77271818.2017 | 421.6965 | 0.084091 | 319925.7442 | 918911.9116 | 6522.119 | 18733.2622
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7313 | 0.3967 | 0.034476 | 4 | 200417.8363 | 565664.579 | 4085.7887 | 11531.8376 | 75.4191 | 12.3274 | 63.1342 | 459015.3644 | 0 | 256467.8992 | 0 | 0 | 0 | 361256.1684 | 419928.3785 | 1092567.5017 | 745699.7699 | 3334935.0821 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 27638474.0155 | 78007556.8885 | 562.3413 | 0.1379 | 200417.8363 | 565664.579 | 4085.7887 | 11531.8376
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5996 | 0.62168 | 0.053102 | 4 | 134179.2433 | 371312.2627 | 2735.4254 | 7569.7027 | 78.1901 | 12.5472 | 52.1313 | 580025.0018 | 0 | 337184.8914 | 0 | 0 | 0 | 437952.2288 | 528513.2276 | 1375083.0053 | 938522.4062 | 4197280.7612 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 28500819.6946 | 78869902.5675 | 749.8942 | 0.21241 | 134179.2433 | 371312.2627 | 2735.4254 | 7569.7027
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10 | 0.91903 | 0.0784 | 4 | 94135.5688 | 254750.4545 | 1919.0809 | 5193.4326 | 80.3803 | 12.7133 | 50.0834 | 723188.1018 | 0 | 435097.2796 | 0 | 0 | 0 | 526279.5346 | 656980.3172 | 1709328.0202 | 1166651.497 | 5217524.7505 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 29521063.6839 | 79890146.5568 | 1000 | 0.3136 | 94135.5688 | 254750.4545 | 1919.0809 | 5193.4326
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0714 | 1.3064 | 0.11229 | 4 | 68400.2403 | 180535.9624 | 1394.4314 | 3680.4698 | 82.0949 | 12.8364 | 37.0182 | 891952.3601 | 0 | 553476.7663 | 0 | 0 | 0 | 627522.2578 | 808451.0399 | 2103423.7696 | 1435629.9438 | 6420456.1375 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 30723995.071 | 81093077.9439 | 1333.5214 | 0.44918 | 68400.2403 | 180535.9624 | 1394.4314 | 3680.4698
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9929 | 1.8068 | 0.15721 | 4 | 51111.3679 | 131207.469 | 1041.9744 | 2674.8417 | 83.4262 | 12.9246 | 56.3941 | 1090680.525 | 0 | 696471.0858 | 0 | 0 | 0 | 743561.2146 | 986978.0019 | 2567914.3039 | 1752654.2778 | 7838259.409 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 32141798.3425 | 82510881.2154 | 1778.2794 | 0.62886 | 51111.3679 | 131207.469 | 1041.9744 | 2674.8417
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.9071 | 2.4396 | 0.21594 | 4 | 39107.349 | 97420.2089 | 797.2562 | 1986.0427 | 84.4333 | 12.9817 | 36.9708 | 1320718.2138 | 0 | 866304.4851 | 0 | 0 | 0 | 872571.5456 | 1193241.7553 | 3104570.2798 | 2118933.0085 | 9476339.288 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 33779878.2214 | 84148961.0943 | 2371.3737 | 0.86377 | 39107.349 | 97420.2089 | 797.2562 | 1986.0427
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0406 | 3.2347 | 0.29176 | 4 | 30564.7336 | 73724.078 | 623.1034 | 1502.965 | 85.1803 | 13.0098 | 55.4555 | 1586349.2089 | 0 | 1067645.2455 | 0 | 0 | 0 | 1016035.0619 | 1431311.5114 | 3723978.9502 | 2541692.1536 | 11367012.1315 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 35670551.0649 | 86039633.9378 | 3162.2777 | 1.167 | 30564.7336 | 73724.078 | 623.1034 | 1502.965
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.2057 | 0.38756 | 4 | 24375.0184 | 56865.9953 | 496.9177 | 1159.2902 | 85.6986 | 13.0077 | 54.7023 | 1884877.9544 | 0 | 1300229.3213 | 0 | 0 | 0 | 1168360.1968 | 1697852.3143 | 4417463.4443 | 3015009.5705 | 13483792.8016 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 37787331.735 | 88156414.6079 | 4216.965 | 1.5502 | 24375.0184 | 56865.9953 | 496.9177 | 1159.2902
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.2498 | 5.3582 | 0.5053 | 4 | 19835.0595 | 44755.4245 | 404.3645 | 912.3999 | 86.0161 | 12.9728 | 49.9318 | 2211486.0288 | 0 | 1562263.1465 | 0 | 0 | 0 | 1323384.6934 | 1987882.2088 | 5172061.7366 | 3530038.4105 | 15787116.2247 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 40090655.1581 | 90459738.031 | 5623.4133 | 2.0212 | 19835.0595 | 44755.4245 | 404.3645 | 912.3999
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.1307 | 6.6672 | 0.64434 | 4 | 16482.5195 | 36025.4639 | 336.0185 | 734.4278 | 86.1498 | 12.9026 | 62.1376 | 2553610.4285 | 0 | 1845646.7895 | 0 | 0 | 0 | 1469731.3528 | 2288905.5426 | 5955262.7028 | 4064589.163 | 18177745.9792 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 42481284.9126 | 92850367.7855 | 7498.9421 | 2.5774 | 16482.5195 | 36025.4639 | 336.0185 | 734.4278
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.6176 | 8.0694 | 0.80006 | 4 | 14002.1339 | 29741.3696 | 285.4524 | 606.318 | 86.1177 | 12.798 | 59.0323 | 2891870.3912 | 0 | 2135780.1638 | 0 | 0 | 0 | 1593192.1892 | 2582128.6702 | 6718169.1326 | 4585288.4775 | 20506429.0245 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 44809967.958 | 95179050.8309 | 10000 | 3.2002 | 14002.1339 | 29741.3696 | 285.4524 | 606.318
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0922 | 9.4833 | 0.9643 | 4 | 12169.438 | 25227.9522 | 248.0905 | 514.3059 | 85.9476 | 12.6653 | 72.0015 | 3207419.768 | 0 | 2416823.9025 | 0 | 0 | 0 | 1684235.8128 | 2850306.9985 | 7415914.1317 | 5061513.7767 | 22636214.3901 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 46939753.3235 | 97308836.1965 | 13335.2143 | 3.8572 | 12169.438 | 25227.9522 | 248.0905 | 514.3059
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.8876 | 10.8186 | 1.1267 | 4 | 10818.2129 | 21993.9798 | 220.5439 | 448.377 | 85.6816 | 12.5167 | 74.9221 | 3484048.7291 | 0 | 2673086.4661 | 0 | 0 | 0 | 1738263.1235 | 3079205.3443 | 8011460.674 | 5467986.529 | 24454050.8659 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 48757589.7994 | 99126672.6723 | 17782.7941 | 4.507 | 10818.2129 | 21993.9798 | 220.5439 | 448.377
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.5964 | 12.0165 | 1.2785 | 4 | 9823.1716 | 19672.5249 | 200.2586 | 401.051 | 85.3655 | 12.3654 | 86.7473 | 3715810.1169 | 0 | 2896378.3518 | 0 | 0 | 0 | 1760278.1261 | 3265261.972 | 8495541.8537 | 5798381.8811 | 25931652.3016 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 50235191.235 | 100604274.1079 | 23713.7371 | 5.1139 | 9823.1716 | 19672.5249 | 200.2586 | 401.051
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9776 | 13.0403 | 1.4131 | 4 | 9090.1967 | 18001.2505 | 185.316 | 366.9798 | 85.042 | 12.2231 | 81.7184 | 3902106.3508 | 0 | 3082689.7755 | 0 | 0 | 0 | 1757831.9716 | 3409624.9581 | 8871144.7309 | 6054738.5626 | 27078136.3494 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 51381675.2829 | 101750758.1558 | 31622.7766 | 5.6524 | 9090.1967 | 18001.2505 | 185.316 | 366.9798
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0607 | 13.8898 | 1.528 | 4 | 8549.4257 | 16790.4857 | 174.2916 | 342.2968 | 84.7379 | 12.0963 | 74.8373 | 4048762.9741 | 0 | 3234414.8569 | 0 | 0 | 0 | 1741031.6298 | 3519441.6897 | 9156865.3399 | 6249748.7492 | 27950265.2396 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 52253804.173 | 102622887.0459 | 42169.6503 | 6.112 | 8549.4257 | 16790.4857 | 174.2916 | 342.2968
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.923 | 14.573 | 1.6228 | 4 | 8149.5613 | 15909.1968 | 166.1398 | 324.3305 | 84.471 | 11.9887 | 79.0259 | 4161548.9666 | 0 | 3354604.6121 | 0 | 0 | 0 | 1716741.5282 | 3600829.0917 | 9368618.6649 | 6394274.7447 | 28596617.6081 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 52900156.5415 | 103269239.4144 | 56234.1325 | 6.4912 | 8149.5613 | 15909.1968 | 166.1398 | 324.3305
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7307 | 15.1109 | 1.6991 | 4 | 7853.1678 | 15264.3737 | 160.0974 | 311.1849 | 84.2471 | 11.9008 | 81.1369 | 4247125.6482 | 0 | 3448098.5664 | 0 | 0 | 0 | 1690274.066 | 3660344.3294 | 9523465.1053 | 6499960.622 | 29069268.3372 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 53372807.2706 | 103741890.1435 | 74989.4209 | 6.7963 | 7853.1678 | 15264.3737 | 160.0974 | 311.1849
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6996 | 15.5317 | 1.7595 | 4 | 7632.9657 | 14789.5176 | 155.6083 | 301.5043 | 84.0636 | 11.8298 | 86.9984 | 4312177.6961 | 0 | 3520636.5234 | 0 | 0 | 0 | 1665481.0668 | 3704335.1616 | 9637920.227 | 6578078.5944 | 29418629.2693 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 53722168.2027 | 104091251.0756 | 100000 | 7.0382 | 7632.9657 | 14789.5176 | 155.6083 | 301.5043
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9971 | 15.8582 | 1.8068 | 4 | 7469.0421 | 14438.2949 | 152.2665 | 294.3442 | 83.9162 | 11.7736 | 86.7477 | 4361508.0308 | 0 | 3576559.5875 | 0 | 0 | 0 | 1643868.1965 | 3736954.9678 | 9722790.2713 | 6636004.1435 | 29677685.1974 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 53981224.1308 | 104350307.0037 | 133352.1432 | 7.2273 | 7469.0421 | 14438.2949 | 152.2665 | 294.3442
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.7339 | 16.1059 | 1.8433 | 4 | 7346.8116 | 14178.3693 | 149.7747 | 289.0452 | 83.8016 | 11.7302 | 91.6865 | 4398214.2522 | 0 | 3618718.4153 | 0 | 0 | 0 | 1625323.1276 | 3760479.7601 | 9783996.9553 | 6677778.963 | 29864511.4735 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54168050.407 | 104537133.2799 | 177827.941 | 7.373 | 7346.8116 | 14178.3693 | 149.7747 | 289.0452
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0593 | 16.2952 | 1.8712 | 4 | 7255.5492 | 13985.0217 | 147.9142 | 285.1036 | 83.7123 | 11.6967 | 73.2061 | 4425886.9794 | 0 | 3650825.9206 | 0 | 0 | 0 | 1610304.2677 | 3777936.6954 | 9829416.3201 | 6708778.6128 | 30003148.796 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54306687.7294 | 104675770.6023 | 237137.3706 | 7.4848 | 7255.5492 | 13985.0217 | 147.9142 | 285.1036
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0534 | 16.4375 | 1.8925 | 4 | 7187.3383 | 13841.2279 | 146.5236 | 282.1722 | 83.6443 | 11.6713 | 78.8255 | 4446447.5099 | 0 | 3674869.1745 | 0 | 0 | 0 | 1598158.9612 | 3790595.5018 | 9862351.9375 | 6731257.8484 | 30103680.9332 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54407219.8667 | 104776302.7396 | 316227.766 | 7.5699 | 7187.3383 | 13841.2279 | 146.5236 | 282.1722
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8233 | 16.5475 | 1.9087 | 4 | 7136.3154 | 13733.4985 | 145.4834 | 279.9759 | 83.5911 | 11.6514 | 80.1922 | 4462259.3773 | 0 | 3693470.9473 | 0 | 0 | 0 | 1588962.3803 | 3800430.1549 | 9887939.6877 | 6748722.0137 | 30181784.5613 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54485323.4947 | 104854406.3676 | 421696.5034 | 7.6349 | 7136.3154 | 13733.4985 | 145.4834 | 279.9759
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3903 | 16.6288 | 1.921 | 4 | 7098.126 | 13653.3348 | 144.7049 | 278.3417 | 83.5515 | 11.6368 | 92.77 | 4473840.1504 | 0 | 3707158.5733 | 0 | 0 | 0 | 1581594.1897 | 3807411.2362 | 9906103.0292 | 6761118.8675 | 30237226.0462 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54540764.9796 | 104909847.8525 | 562341.3252 | 7.6838 | 7098.126 | 13653.3348 | 144.7049 | 278.3417
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8165 | 16.69 | 1.9302 | 4 | 7069.529 | 13593.4106 | 144.1219 | 277.1201 | 83.5215 | 11.6257 | 92.1891 | 4482508.4186 | 0 | 3717439.419 | 0 | 0 | 0 | 1575918.0996 | 3812587.7155 | 9919571.1664 | 6770311.1479 | 30278335.967 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54581874.9004 | 104950957.7733 | 749894.2093 | 7.7207 | 7069.529 | 13593.4106 | 144.1219 | 277.1201
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1527 | 16.738 | 1.9372 | 4 | 7048.1073 | 13548.2183 | 143.6852 | 276.1988 | 83.4978 | 11.6169 | 94.8482 | 4489325.1526 | 0 | 3725545.5519 | 0 | 0 | 0 | 1571846.0595 | 3816819.538 | 9930581.5004 | 6777825.9271 | 30311943.7294 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54615482.6629 | 104984565.5358 | 1000000 | 7.749 | 7048.1073 | 13548.2183 | 143.6852 | 276.1988
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.387 | 16.7718 | 1.9424 | 4 | 7032.0562 | 13514.7986 | 143.358 | 275.5174 | 83.4812 | 11.6107 | 99.6552 | 4494064.1086 | 0 | 3731192.6929 | 0 | 0 | 0 | 1568438.4202 | 3819541.1365 | 9937662.5415 | 6782658.8831 | 30333557.7827 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54637096.7161 | 105006179.589 | 1333521.4322 | 7.7697 | 7032.0562 | 13514.7986 | 143.358 | 275.5174
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5741 | 16.7986 | 1.9464 | 4 | 7020.027 | 13489.5194 | 143.1127 | 275.0021 | 83.4679 | 11.6058 | 84.3787 | 4497841.7311 | 0 | 3735700.6904 | 0 | 0 | 0 | 1566043.5317 | 3821838.5217 | 9943639.8667 | 6786738.5304 | 30351802.8719 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54655341.8053 | 105024424.6782 | 1778279.41 | 7.7856 | 7020.027 | 13489.5194 | 143.1127 | 275.0021
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7056 | 16.8176 | 1.9493 | 4 | 7011.0104 | 13470.7806 | 142.9289 | 274.6201 | 83.4586 | 11.6024 | 86.8997 | 4500493.3035 | 0 | 3738868.7322 | 0 | 0 | 0 | 1564083.2484 | 3823343.6608 | 9947555.9298 | 6789411.3239 | 30363756.1985 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54667295.1319 | 105036378.0048 | 2371373.7057 | 7.7973 | 7011.0104 | 13470.7806 | 142.9289 | 274.6201
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.8176 | 16.8335 | 1.9516 | 4 | 7004.2513 | 13456.4404 | 142.7911 | 274.3277 | 83.4506 | 11.5994 | 87.159 | 4502751.1159 | 0 | 3741568.2895 | 0 | 0 | 0 | 1562828.1913 | 3824787.5627 | 9951312.6663 | 6791975.3738 | 30375223.1994 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54678762.1328 | 105047845.0057 | 3162277.6602 | 7.8065 | 7004.2513 | 13456.4404 | 142.7911 | 274.3277
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.8862 | 16.8435 | 1.9532 | 4 | 6999.1839 | 13446.039 | 142.6878 | 274.1157 | 83.4457 | 11.5976 | 81.4182 | 4504130.1879 | 0 | 3743218.6172 | 0 | 0 | 0 | 1561622.6359 | 3825498.862 | 9953163.3212 | 6793238.4838 | 30380872.1081 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54684411.0416 | 105053493.9145 | 4216965.0343 | 7.813 | 6999.1839 | 13446.039 | 142.6878 | 274.1157
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9419 | 16.8515 | 1.9545 | 4 | 6995.3847 | 13438.1458 | 142.6104 | 273.9548 | 83.4417 | 11.5962 | 91.5757 | 4505251.5566 | 0 | 3744561.0189 | 0 | 0 | 0 | 1560788.2245 | 3826134.312 | 9954816.6318 | 6794366.9022 | 30385918.6461 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54689457.5795 | 105058540.4524 | 5623413.2519 | 7.8179 | 6995.3847 | 13438.1458 | 142.6104 | 273.9548
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9808 | 16.8572 | 1.9554 | 4 | 6992.5361 | 13432.2933 | 142.5523 | 273.8355 | 83.4389 | 11.5951 | 89.7976 | 4506033.5714 | 0 | 3745497.5738 | 0 | 0 | 0 | 1560112.394 | 3826540.9803 | 9955874.6993 | 6795089.055 | 30389148.2738 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54692687.2072 | 105061770.0801 | 7498942.0933 | 7.8216 | 6992.5361 | 13432.2933 | 142.5523 | 273.8355
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0151 | 16.8621 | 1.9561 | 4 | 6990.4001 | 13427.7925 | 142.5088 | 273.7437 | 83.4365 | 11.5942 | 85.9136 | 4506722.5556 | 0 | 3746322.778 | 0 | 0 | 0 | 1559689.564 | 3826966.61 | 9956982.1005 | 6795844.8791 | 30392528.4872 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54696067.4207 | 105065150.2936 | 10000000 | 7.8245 | 6990.4001 | 13427.7925 | 142.5088 | 273.7437
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.3389 | [19 empty] | 100 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1559 | [19 empty] | 133.3521 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.023829 | 0.0016516 | 4 | 3928078.2578 | 11732417.4366 | 80079.1884 | 239181.1987 | 56.0457 | 10.7543 | 25.668 | 143086.8571 | 0 | 55487.4227 | 0 | 0 | 0 | 144699.7951 | 133876.8892 | 348320.2038 | 237735.6964 | 1063206.8644 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 25950888.0265 | 77510332.3283 | 177.8279 | 0.0066065 | 3928078.2578 | 11732417.4366 | 80079.1884 | 239181.1987
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.012116 | 0.0044556 | 4 | 1453278.4968 | 4346258.6542 | 29627.0479 | 88604.3614 | 56.0457 | 10.7543 | 25.9436 | 143086.859 | 0 | 55487.4218 | 0 | 0 | 0 | 128498.0453 | 127558.2072 | 331880.2893 | 226515.1169 | 1013025.9394 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 25900707.1015 | 77460151.4033 | 237.1374 | 0.017822 | 1453278.4968 | 4346258.6542 | 29627.0479 | 88604.3614
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2345 | 0.11588 | 0.012472 | 4 | 540384.8779 | 1573855.557 | 11016.4767 | 32085.1743 | 68.8325 | 11.9944 | 47.7859 | 282406.2621 | 0 | 140332.7302 | 0 | 0 | 0 | 246210.7907 | 260890.4154 | 678783.3448 | 463283.5805 | 2071907.1237 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 26959588.2858 | 78519032.5876 | 316.2278 | 0.04989 | 540384.8779 | 1573855.557 | 11016.4767 | 32085.1743
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4138 | 0.24326 | 0.02257 | 4 | 305847.6997 | 876963.4377 | 6235.119 | 17878.0859 | 73.3703 | 12.3914 | 46.2144 | 373449.3822 | 0 | 197703.0947 | 0 | 0 | 0 | 308263.8794 | 342972.379 | 892343.7767 | 609042.9635 | 2723775.4754 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 27611456.6376 | 79170900.9394 | 421.6965 | 0.090278 | 305847.6997 | 876963.4377 | 6235.119 | 17878.0859
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9212 | 0.41947 | 0.036966 | 4 | 191917.6533 | 540615.2055 | 3912.5009 | 11021.1722 | 76.963 | 12.6886 | 60.5697 | 480901.2047 | 0 | 267072.9793 | 0 | 0 | 0 | 378774.6133 | 439432.031 | 1143312.0046 | 780333.9359 | 3489826.7688 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 28377507.9309 | 79936952.2327 | 562.3413 | 0.14786 | 191917.6533 | 540615.2055 | 3912.5009 | 11021.1722
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8554 | 0.65643 | 0.056896 | 4 | 128662.1843 | 355214.9982 | 2622.9527 | 7241.5382 | 79.8084 | 12.9118 | 57.7287 | 607889.3651 | 0 | 351124.25 | 0 | 0 | 0 | 459525.0158 | 553230.066 | 1439391.1487 | 982414.0355 | 4393573.8811 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 29281255.0432 | 80840699.345 | 749.8942 | 0.22758 | 128662.1843 | 355214.9982 | 2622.9527 | 7241.5382
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3233 | 0.96769 | 0.083934 | 4 | 90373.2863 | 243944.9462 | 1842.3817 | 4973.1477 | 82.0429 | 13.0792 | 59.5598 | 757106.9049 | 0 | 452383.2394 | 0 | 0 | 0 | 551370.266 | 686735.56 | 1786745.0584 | 1219490.2163 | 5453831.245 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 30341512.4071 | 81900956.7089 | 1000 | 0.33574 | 90373.2863 | 243944.9462 | 1842.3817 | 4973.1477
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4929 | 1.3744 | 0.12016 | 4 | 65741.0024 | 173013.6742 | 1340.2193 | 3527.1178 | 83.8005 | 13.2037 | 36.7779 | 933711.5245 | 0 | 575290.7153 | 0 | 0 | 0 | 657438.8463 | 844912.0236 | 2198287.7701 | 1500376.5734 | 6710017.4533 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 31597698.6154 | 83157142.9172 | 1333.5214 | 0.48064 | 65741.0024 | 173013.6742 | 1340.2193 | 3527.1178
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.507 | 1.896 | 0.16808 | 4 | 49179.6891 | 125869.7641 | 1002.5945 | 2566.0254 | 85.156 | 13.2918 | 54.8216 | 1140050.7207 | 0 | 722585.4372 | 0 | 0 | 0 | 777211.3151 | 1029540.5145 | 2678653.2308 | 1828235.8709 | 8176277.0891 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 33063958.2513 | 84623402.5531 | 1778.2794 | 0.67231 | 49179.6891 | 125869.7641 | 1002.5945 | 2566.0254
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.587 | 2.5614 | 0.23079 | 4 | 37673.2126 | 93523.106 | 768.0194 | 1906.595 | 86.1918 | 13.3488 | 54.8501 | 1381289.3144 | 0 | 899280.7515 | 0 | 0 | 0 | 913044.6008 | 1245509.72 | 3240560.8024 | 2211749.3345 | 9891434.5236 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 34779115.6858 | 86338559.9876 | 2371.3737 | 0.92318 | 37673.2126 | 93523.106 | 768.0194 | 1906.595
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8714 | 3.3907 | 0.31154 | 4 | 29480.4616 | 70855.1381 | 600.9991 | 1444.4778 | 86.9525 | 13.3754 | 41.3844 | 1657399.8945 | 0 | 1106930.2545 | 0 | 0 | 0 | 1061535.0858 | 1492087.4416 | 3882105.4538 | 2649616.7415 | 11849674.8717 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 36737356.0338 | 88296800.3356 | 3162.2777 | 1.2462 | 29480.4616 | 70855.1381 | 600.9991 | 1444.4778
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4935 | 4.4034 | 0.41342 | 4 | 23542.1609 | 54721.0859 | 479.9388 | 1115.5634 | 87.4799 | 13.3705 | 51.3748 | 1967764.1584 | 0 | 1346869.5426 | 0 | 0 | 0 | 1219423.959 | 1768282.4874 | 4600708.3076 | 3140077.955 | 14043126.41 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 38930807.5721 | 90490251.8739 | 4216.965 | 1.6537 | 23542.1609 | 54721.0859 | 479.9388 | 1115.5634
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.4413 | 5.6009 | 0.53824 | 4 | 19185.9867 | 43134.1333 | 391.1323 | 879.3476 | 87.7999 | 13.3314 | 52.0627 | 2305976.8948 | 0 | 1616169.605 | 0 | 0 | 0 | 1379006.4732 | 2067449.6595 | 5379079.9217 | 3671332.5756 | 16419015.1299 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 41306696.292 | 92866140.5938 | 5623.4133 | 2.153 | 19185.9867 | 43134.1333 | 391.1323 | 879.3476
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.4756 | 6.9548 | 0.68506 | 4 | 15969.5341 | 34785.2885 | 325.5606 | 709.1452 | 87.9309 | 13.2556 | 57.6771 | 2658668.3656 | 0 | 1906173.0525 | 0 | 0 | 0 | 1528451.0988 | 2376384.0816 | 6182863.9169 | 4219931.6684 | 18872472.1838 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 43760153.3459 | 95319597.6477 | 7498.9421 | 2.7402 | 15969.5341 | 34785.2885 | 325.5606 | 709.1452
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.0861 | 8.3999 | 0.84877 | 4 | 13590.6481 | 28777.1966 | 277.0637 | 586.6621 | 87.8918 | 13.1444 | 63.4377 | 3006156.3731 | 0 | 2202129.6197 | 0 | 0 | 0 | 1653781.7696 | 2676206.4273 | 6962940.1585 | 4752349.7323 | 21253564.0805 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 46141245.2426 | 97700689.5444 | 10000 | 3.3951 | 13590.6481 | 28777.1966 | 277.0637 | 586.6621
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6197 | 9.8486 | 1.0205 | 4 | 11833.6814 | 24464.808 | 241.2456 | 498.7482 | 87.7127 | 13.0049 | 68.1435 | 3328411.1821 | 0 | 2487205.8926 | 0 | 0 | 0 | 1744836.8861 | 2948577.0447 | 7671592.634 | 5236019.6082 | 23416643.2476 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 48304324.4097 | 99863768.7115 | 13335.2143 | 4.0819 | 11833.6814 | 24464.808 | 241.2456 | 498.7482
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.4345 | 11.2118 | 1.1895 | 4 | 10538.7178 | 21374.885 | 214.846 | 435.7559 | 87.4374 | 12.85 | 75.0421 | 3609979.9243 | 0 | 2746325.0644 | 0 | 0 | 0 | 1798168.3551 | 3180244.6041 | 8274344.102 | 5647409.8704 | 25256471.9203 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 50144153.0824 | 101703597.3842 | 17782.7941 | 4.7581 | 10538.7178 | 21374.885 | 214.846 | 435.7559
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1117 | 12.4281 | 1.3466 | 4 | 9585.2691 | 19157.3898 | 195.4087 | 390.5493 | 87.1142 | 12.6936 | 78.1549 | 3844655.4788 | 0 | 2970939.1426 | 0 | 0 | 0 | 1818695.2948 | 3367373.0674 | 8761213.9781 | 5979708.565 | 26742585.5267 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 51630266.6888 | 103189710.9906 | 23713.7371 | 5.3864 | 9585.2691 | 19157.3898 | 195.4087 | 390.5493
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.4392 | 13.464 | 1.4854 | 4 | 8882.948 | 17560.6225 | 181.0909 | 357.997 | 86.7857 | 12.5474 | 78.2313 | 4032709.8334 | 0 | 3157744.6211 | 0 | 0 | 0 | 1814756.0814 | 3512032.109 | 9137587.1308 | 6236590.9754 | 27891420.7511 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 52779101.9133 | 104338546.2151 | 31622.7766 | 5.9416 | 8882.948 | 17560.6225 | 181.0909 | 357.997
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4614 | 14.3212 | 1.6035 | 4 | 8364.7542 | 16403.4421 | 170.5268 | 334.4064 | 86.4786 | 12.4177 | 75.891 | 4180431.1368 | 0 | 3309503.5023 | 0 | 0 | 0 | 1796719.9788 | 3621795.301 | 9423168.4408 | 6431506.0876 | 28763124.4472 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 53650805.6093 | 105210249.9111 | 42169.6503 | 6.4139 | 8364.7542 | 16403.4421 | 170.5268 | 334.4064
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2675 | 15.0095 | 1.7007 | 4 | 7981.5379 | 15560.764 | 162.7144 | 317.2272 | 86.2099 | 12.3081 | 87.7732 | 4293927.6845 | 0 | 3429567.1889 | 0 | 0 | 0 | 1771556.6287 | 3703070.0858 | 9634628.7593 | 6575832.1 | 29408582.4473 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 54296263.6094 | 105855707.9112 | 56234.1325 | 6.8027 | 7981.5379 | 15560.764 | 162.7144 | 317.2272
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0413 | 15.5526 | 1.7789 | 4 | 7697.4471 | 14943.5421 | 156.9229 | 304.6443 | 85.9842 | 12.2182 | 71.9013 | 4380316.2808 | 0 | 3523232.6014 | 0 | 0 | 0 | 1744789.413 | 3762851.9351 | 9790168.8681 | 6681991.4204 | 29883350.5188 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 54771031.6809 | 106330475.9827 | 74989.4209 | 7.1155 | 7697.4471 | 14943.5421 | 156.9229 | 304.6443
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9714 | 15.9759 | 1.8407 | 4 | 7486.3594 | 14489.1381 | 152.6196 | 295.3807 | 85.8 | 12.1461 | 76.9448 | 4445732.5261 | 0 | 3595605.737 | 0 | 0 | 0 | 1719640.896 | 3806781.872 | 9904465.5527 | 6760001.2561 | 30232227.8399 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55119909.0021 | 106679353.3039 | 100000 | 7.3627 | 7486.3594 | 14489.1381 | 152.6196 | 295.3807
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2151 | 16.3012 | 1.8888 | 4 | 7329.2042 | 14153.4993 | 149.4157 | 288.5382 | 85.6538 | 12.0896 | 82.3348 | 4494844.0776 | 0 | 3650827.5157 | 0 | 0 | 0 | 1697400.9109 | 3838798.2766 | 9987765.67 | 6816855.2979 | 30486491.7487 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55374172.9109 | 106933617.2126 | 133352.1432 | 7.5553 | 7329.2042 | 14153.4993 | 149.4157 | 288.5382
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9324 | 16.5507 | 1.926 | 4 | 7212.0107 | 13904.5029 | 147.0266 | 283.4621 | 85.5388 | 12.0455 | 82.1389 | 4531858.0111 | 0 | 3692981.8043 | 0 | 0 | 0 | 1678828.2175 | 3862430.5328 | 10049251.953 | 6858820.9494 | 30674171.4682 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55561852.6303 | 107121296.9321 | 177827.941 | 7.7041 | 7212.0107 | 13904.5029 | 147.0266 | 283.4621
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.236 | 16.7405 | 1.9545 | 4 | 7124.5033 | 13719.4105 | 145.2426 | 279.6887 | 85.4497 | 12.0116 | 87.437 | 4559619.2009 | 0 | 3724915.4772 | 0 | 0 | 0 | 1663692.4291 | 3879808.5719 | 10094466.0458 | 6889680.4968 | 30812182.2217 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55699863.3839 | 107259307.6857 | 237137.3706 | 7.8181 | 7124.5033 | 13719.4105 | 145.2426 | 279.6887
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.2272 | 16.8849 | 1.9763 | 4 | 7059.0954 | 13581.4206 | 143.9092 | 276.8756 | 85.3809 | 11.9856 | 89.1822 | 4580535.1707 | 0 | 3749161.4374 | 0 | 0 | 0 | 1651716.9808 | 3892751.2997 | 10128140.3687 | 6912663.9141 | 30914969.1713 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55802650.3334 | 107362094.6352 | 316227.766 | 7.9051 | 7059.0954 | 13581.4206 | 143.9092 | 276.8756
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.9628 | 16.9924 | 1.9927 | 4 | 7010.1673 | 13478.749 | 142.9117 | 274.7825 | 85.3292 | 11.9661 | 87.3675 | 4595950.3977 | 0 | 3767136.767 | 0 | 0 | 0 | 1642101.7522 | 3902023.6776 | 10152265.194 | 6929129.6031 | 30988607.3916 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55876288.5537 | 107435732.8555 | 421696.5034 | 7.9707 | 7010.1673 | 13478.749 | 142.9117 | 274.7825
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5398 | 17.0765 | 2.0053 | 4 | 6973.5448 | 13401.5433 | 142.1651 | 273.2086 | 85.2884 | 11.9507 | 92.5371 | 4607976.4982 | 0 | 3781223.1404 | 0 | 0 | 0 | 1635045.5694 | 3909455.6311 | 10171601.6126 | 6942327.1061 | 31047629.5578 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55935310.72 | 107494755.0217 | 562341.3252 | 8.0211 | 6973.5448 | 13401.5433 | 142.1651 | 273.2086
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9567 | 17.1375 | 2.0146 | 4 | 6946.1204 | 13344.2002 | 141.6061 | 272.0396 | 85.2587 | 11.9396 | 92.481 | 4616630.5583 | 0 | 3791395.2854 | 0 | 0 | 0 | 1629315.8287 | 3914563.2522 | 10184890.5949 | 6951397.1096 | 31088192.6291 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55975873.7913 | 107535318.0931 | 749894.2093 | 8.0586 | 6946.1204 | 13344.2002 | 141.6061 | 272.0396
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2781 | 17.1844 | 2.0218 | 4 | 6925.5767 | 13301.1184 | 141.1872 | 271.1613 | 85.2357 | 11.931 | 90.6071 | 4623281.1094 | 0 | 3799232.464 | 0 | 0 | 0 | 1625076.5391 | 3918560.1438 | 10195289.6871 | 6958494.7037 | 31119934.647 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56007615.8091 | 107567060.1109 | 1000000 | 8.0871 | 6925.5767 | 13301.1184 | 141.1872 | 271.1613
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5144 | 17.219 | 2.0271 | 4 | 6910.1834 | 13268.9771 | 140.8734 | 270.506 | 85.2187 | 11.9246 | 95.6567 | 4628160.5388 | 0 | 3804993.9161 | 0 | 0 | 0 | 1621764.513 | 3921418.3975 | 10202726.2768 | 6963570.329 | 31142633.9713 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56030315.1334 | 107589759.4352 | 1333521.4322 | 8.1084 | 6910.1834 | 13268.9771 | 140.8734 | 270.506
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6996 | 17.2461 | 2.0312 | 4 | 6898.6469 | 13244.7354 | 140.6382 | 270.0118 | 85.2054 | 11.9196 | 89.0251 | 4631978.4046 | 0 | 3809508.4049 | 0 | 0 | 0 | 1619387.9979 | 3923741.1749 | 10208769.6671 | 6967695.067 | 31161080.7163 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56048761.8785 | 107608206.1803 | 1778279.41 | 8.1246 | 6898.6469 | 13244.7354 | 140.6382 | 270.0118
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8239 | 17.2644 | 2.0341 | 4 | 6889.9997 | 13226.8953 | 140.462 | 269.6482 | 85.1964 | 11.9163 | 92.9695 | 4634535.9993 | 0 | 3812536.3655 | 0 | 0 | 0 | 1617338.7487 | 3925120.3342 | 10212357.9568 | 6970144.1485 | 31172033.553 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56059714.7151 | 107619159.0169 | 2371373.7057 | 8.1364 | 6889.9997 | 13226.8953 | 140.462 | 269.6482
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.9313 | 17.28 | 2.0364 | 4 | 6883.5174 | 13213.2185 | 140.3298 | 269.3693 | 85.1886 | 11.9134 | 94.0345 | 4636745.5411 | 0 | 3815153.9923 | 0 | 0 | 0 | 1616035.8764 | 3926494.8098 | 10215934.0603 | 6972584.9126 | 31182949.1925 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56070630.3547 | 107630074.6565 | 3162277.6602 | 8.1456 | 6883.5174 | 13213.2185 | 140.3298 | 269.3693
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0091 | 17.2914 | 2.0381 | 4 | 6878.6575 | 13203.029 | 140.2307 | 269.1616 | 85.183 | 11.9113 | 87.0696 | 4638344.1879 | 0 | 3817049.2127 | 0 | 0 | 0 | 1615006.1125 | 3927455.8101 | 10218434.3859 | 6974291.4362 | 31190581.1451 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56078262.3073 | 107637706.6091 | 4216965.0343 | 8.1525 | 6878.6575 | 13203.029 | 140.2307 | 269.1616
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0675 | 17.2999 | 2.0394 | 4 | 6875.0139 | 13195.3914 | 140.1565 | 269.0059 | 85.1788 | 11.9097 | 90.4171 | 4639542.4928 | 0 | 3818470.5085 | 0 | 0 | 0 | 1614230.9645 | 3928175.1466 | 10220305.9521 | 6975568.8186 | 31196293.883 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56083975.0452 | 107643419.347 | 5623413.2519 | 8.1577 | 6875.0139 | 13195.3914 | 140.1565 | 269.0059
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1017 | 17.3051 | 2.0403 | 4 | 6872.2819 | 13189.8713 | 140.1008 | 268.8934 | 85.1763 | 11.9088 | 85.143 | 4640245.5148 | 0 | 3819304.8844 | 0 | 0 | 0 | 1613486.3913 | 3928484.3483 | 10221110.4313 | 6976117.8922 | 31198749.4622 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56086430.6244 | 107645874.9262 | 7498942.0933 | 8.1613 | 6872.2819 | 13189.8713 | 140.1008 | 268.8934
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1406 | 17.3107 | 2.0411 | 4 | 6870.2334 | 13185.4473 | 140.059 | 268.8032 | 85.1735 | 11.9077 | 89.4661 | 4641044.1351 | 0 | 3820252.5138 | 0 | 0 | 0 | 1613151.908 | 3929034.9372 | 10222542.9507 | 6977095.6161 | 31203122.0609 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 56090803.223 | 107650247.5248 | 10000000 | 8.1643 | 6870.2334 | 13185.4473 | 140.059 | 268.8032
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2153 | [19 empty] | 100 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6507 | [19 empty] | 133.3521 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.025241 | 0.0018136 | 4 | 3659980.0755 | 10933182.9225 | 74613.6443 | 222887.7221 | 56.4382 | 11.0147 | 25.9993 | 145076.7625 | 0 | 55320.9973 | 0 | 0 | 0 | 146266.0812 | 135198.898 | 351759.7995 | 240083.2911 | 1073705.8296 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 26551389.3113 | 79314966.2555 | 177.8279 | 0.0072545 | 3659980.0755 | 10933182.9225 | 74613.6443 | 222887.7221
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.013571 | 0.0046079 | 4 | 1437835.1659 | 4300500.9452 | 29312.2147 | 87671.5286 | 56.4382 | 11.0147 | 24.5365 | 145076.7644 | 0 | 55320.9964 | 0 | 0 | 0 | 130202.3862 | 128934.0573 | 335459.9692 | 228958.322 | 1023952.4956 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 26501635.9773 | 79265212.9215 | 237.1374 | 0.018432 | 1437835.1659 | 4300500.9452 | 29312.2147 | 87671.5286
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3419 | 0.12421 | 0.013399 | 4 | 515829.7911 | 1500294.5843 | 10515.888 | 30585.5344 | 70.1969 | 12.3462 | 46.8622 | 295839.4939 | 0 | 146396.8788 | 0 | 0 | 0 | 258008.4463 | 273095.4794 | 710538.4179 | 484957.0703 | 2168835.7866 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 27646519.2683 | 80410096.2125 | 316.2278 | 0.053596 | 515829.7911 | 1500294.5843 | 10515.888 | 30585.5344
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5575 | 0.25798 | 0.024199 | 4 | 292636.7874 | 837737.2204 | 5965.7967 | 17078.4064 | 74.8352 | 12.7487 | 52.333 | 390938.8184 | 0 | 205880.4963 | 0 | 0 | 0 | 322836.0917 | 358665.6085 | 933174.3408 | 636910.6624 | 2848406.018 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 28326089.4997 | 81089666.4439 | 421.6965 | 0.096796 | 292636.7874 | 837737.2204 | 5965.7967 | 17078.4064
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1038 | 0.44212 | 0.039579 | 4 | 183939.2775 | 517223.3353 | 3749.851 | 10544.2973 | 78.497 | 13.0487 | 69.7354 | 502665.2363 | 0 | 277466.1297 | 0 | 0 | 0 | 395911.7946 | 458656.8326 | 1193330.995 | 814472.9246 | 3642503.9128 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 29120187.3945 | 81883764.3387 | 562.3413 | 0.15831 | 183939.2775 | 517223.3353 | 3749.851 | 10544.2973
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0944 | 0.69024 | 0.060856 | 4 | 123491.7588 | 340246.3281 | 2517.5465 | 6936.3816 | 81.4123 | 13.2756 | 51.3815 | 635180.8235 | 0 | 364492.0464 | 0 | 0 | 0 | 480138.963 | 577126.6148 | 1501565.0669 | 1024849.0122 | 4583352.5269 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 30061036.0086 | 82824612.9528 | 749.8942 | 0.24343 | 123491.7588 | 340246.3281 | 2517.5465 | 6936.3816
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6398 | 1.0168 | 0.089728 | 4 | 86838.7572 | 233847.8527 | 1770.3255 | 4767.3048 | 83.7054 | 13.445 | 46.7353 | 791228.4984 | 0 | 469583.3156 | 0 | 0 | 0 | 576278.726 | 716465.3106 | 1864095.7709 | 1272283.667 | 5689935.2884 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 31167618.7701 | 83931195.7143 | 1000 | 0.35891 | 86838.7572 | 233847.8527 | 1770.3255 | 4767.3048
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8996 | 1.4424 | 0.12837 | 4 | 63241.1988 | 165994.5198 | 1289.2574 | 3384.0228 | 85.5047 | 13.5707 | 42.578 | 975406.6444 | 0 | 596772.9048 | 0 | 0 | 0 | 686762.4244 | 880987.3697 | 2292148.4206 | 1564438.396 | 6996516.16 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 32474199.6417 | 85237776.5859 | 1333.5214 | 0.5135 | 63241.1988 | 165994.5198 | 1289.2574 | 3384.0228
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.0406 | 1.9896 | 0.17949 | 4 | 47362.5339 | 120852.0036 | 965.5493 | 2463.7316 | 86.8962 | 13.6595 | 53.9655 | 1191259.4956 | 0 | 749673.5154 | 0 | 0 | 0 | 812285.405 | 1073755.1822 | 2793690.7267 | 1906751.3256 | 8527415.6504 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 34005099.1321 | 86768676.0763 | 1778.2794 | 0.71797 | 47362.5339 | 120852.0036 | 965.5493 | 2463.7316
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.254 | 2.6845 | 0.24629 | 4 | 36323.048 | 89880.5537 | 740.4945 | 1832.3367 | 87.9537 | 13.7159 | 46.5836 | 1442330.2334 | 0 | 932162.287 | 0 | 0 | 0 | 953267.5565 | 1297826.43 | 3376678.15 | 2304652.2212 | 10306916.8781 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 35784600.3598 | 88548177.304 | 2371.3737 | 0.98518 | 36323.048 | 89880.5537 | 740.4945 | 1832.3367
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.6996 | 3.55 | 0.3322 | 4 | 28458.7776 | 68166.9277 | 580.1707 | 1389.675 | 88.73 | 13.7409 | 48.6615 | 1729585.0794 | 0 | 1146548.5642 | 0 | 0 | 0 | 1107363.5369 | 1553563.9004 | 4042054.589 | 2758785.3129 | 12337900.9828 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 37815584.4645 | 90579161.4087 | 3162.2777 | 1.3288 | 28458.7776 | 68166.9277 | 580.1707 | 1389.675
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.505 | 4.6054 | 0.44039 | 4 | 22756.6181 | 52709.5547 | 463.9244 | 1074.5556 | 89.2665 | 13.7331 | 54.1834 | 2052001.2239 | 0 | 1393940.09 | 0 | 0 | 0 | 1270890.1173 | 1839564.2582 | 4786168.8532 | 3266658.5882 | 14609223.1308 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 40086906.6125 | 92850483.5567 | 4216.965 | 1.7615 | 22756.6181 | 52709.5547 | 463.9244 | 1074.5556
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.625 | 5.8479 | 0.57252 | 4 | 18573.1365 | 41613.0457 | 378.6385 | 848.3382 | 89.589 | 13.6897 | 55.1296 | 2401762.8636 | 0 | 1670404.4375 | 0 | 0 | 0 | 1434827.7269 | 2147728.0609 | 5587947.8549 | 3813889.2318 | 17056560.1755 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 42534243.6572 | 95297820.6014 | 5623.4133 | 2.2901 | 18573.1365 | 41613.0457 | 378.6385 | 848.3382
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.8297 | 7.2496 | 0.72744 | 4 | 15484.6 | 33617.9557 | 315.6745 | 685.3475 | 89.7171 | 13.6079 | 55.4027 | 2765734.8965 | 0 | 1967579.8291 | 0 | 0 | 0 | 1587985.5664 | 2465307.1139 | 6414223.4062 | 4377839.2739 | 19578670.0859 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 45056353.5676 | 97819930.5118 | 7498.9421 | 2.9098 | 15484.6 | 33617.9557 | 315.6745 | 685.3475
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.5601 | 8.7378 | 0.89933 | 4 | 13201.1179 | 27868.5271 | 269.1226 | 568.1376 | 89.6707 | 13.4899 | 72.5984 | 3122366.0026 | 0 | 2269286.6157 | 0 | 0 | 0 | 1715015.3938 | 2771600.5248 | 7211136.032 | 4921748.5158 | 22011153.0847 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 47488836.5665 | 100252413.5107 | 10000 | 3.5973 | 13201.1179 | 27868.5271 | 269.1226 | 568.1376
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.1324 | 10.219 | 1.0786 | 4 | 11515.3028 | 23745.4603 | 234.755 | 484.0833 | 89.4827 | 13.3438 | 67.8035 | 3450693.2552 | 0 | 2557854.9132 | 0 | 0 | 0 | 1805424.0476 | 3047449.1643 | 7928837.6076 | 5411594.5885 | 24201853.5764 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 49679537.0581 | 102443114.0023 | 13335.2143 | 4.3142 | 11515.3028 | 23745.4603 | 234.755 | 484.0833
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9498 | 11.6081 | 1.2542 | 4 | 10273.1709 | 20790.8482 | 209.4325 | 423.8496 | 89.1988 | 13.1827 | 63.9204 | 3736705.2185 | 0 | 2819386.7328 | 0 | 0 | 0 | 1857584.1927 | 3281333.6961 | 8537357.1833 | 5826921.7027 | 26059288.7262 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 51536972.2079 | 104300549.1521 | 17782.7941 | 5.0167 | 10273.1709 | 20790.8482 | 209.4325 | 423.8496
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.6003 | 12.8434 | 1.4167 | 4 | 9358.7631 | 18670.0554 | 190.791 | 380.6143 | 88.8684 | 13.021 | 67.5761 | 3974392.5164 | 0 | 3045434.3605 | 0 | 0 | 0 | 1876729.9252 | 3469657.1528 | 9027336.187 | 6161342.4409 | 27554892.5827 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 53032576.0644 | 105796153.0086 | 23713.7371 | 5.6666 | 9358.7631 | 18670.0554 | 190.791 | 380.6143
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8935 | 13.8937 | 1.5598 | 4 | 8685.21 | 17142.1408 | 177.0598 | 349.4657 | 88.5343 | 12.8706 | 75.4948 | 4164642.5521 | 0 | 3233199.3723 | 0 | 0 | 0 | 1871708.5205 | 3615124.6735 | 9405812.8365 | 6419660.531 | 28710148.4859 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 54187831.9676 | 106951408.9118 | 31622.7766 | 6.2391 | 8685.21 | 17142.1408 | 177.0598 | 349.4657
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.8445 | 14.757 | 1.681 | 4 | 8188.2041 | 16035.4341 | 166.9276 | 326.904 | 88.2249 | 12.7383 | 80.6854 | 4313097.6343 | 0 | 3384690.3907 | 0 | 0 | 0 | 1852140.6599 | 3724472.1871 | 9690312.6365 | 6613837.4904 | 29578550.9989 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 55056234.4806 | 107819811.4248 | 42169.6503 | 6.7238 | 8188.2041 | 16035.4341 | 166.9276 | 326.904
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5929 | 15.4499 | 1.7806 | 4 | 7820.6129 | 15228.9345 | 159.4338 | 310.4624 | 87.9546 | 12.6266 | 71.1714 | 4427208.1762 | 0 | 3504553.3853 | 0 | 0 | 0 | 1826017.3571 | 3805533.7783 | 9901218.2687 | 6757784.9181 | 30222315.8837 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 55699999.3654 | 108463576.3096 | 56234.1325 | 7.1222 | 7820.6129 | 15228.9345 | 159.4338 | 310.4624
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.3272 | 15.9975 | 1.8606 | 4 | 7548.0705 | 14637.7093 | 153.8776 | 298.4095 | 87.7275 | 12.5351 | 79.98 | 4514241.2857 | 0 | 3598225.0752 | 0 | 0 | 0 | 1798799.3429 | 3865393.6245 | 10056961.3097 | 6864082.7438 | 30697703.3818 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 56175386.8636 | 108938963.8078 | 74989.4209 | 7.4424 | 7548.0705 | 14637.7093 | 153.8776 | 298.4095
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2166 | 16.4228 | 1.9237 | 4 | 7345.5396 | 14202.5034 | 149.7488 | 289.5372 | 87.5431 | 12.4619 | 85.4762 | 4579946.4194 | 0 | 3670365.0459 | 0 | 0 | 0 | 1773223.6716 | 3909178.7034 | 10170881.1034 | 6941835.3438 | 31045430.2876 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 56523113.7693 | 109286690.7135 | 100000 | 7.6949 | 7345.5396 | 14202.5034 | 149.7488 | 289.5372
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4332 | 16.7502 | 1.9729 | 4 | 7194.7397 | 13880.8253 | 146.6745 | 282.9794 | 87.3964 | 12.4045 | 80.4588 | 4629384.3412 | 0 | 3725517.5859 | 0 | 0 | 0 | 1750813.2561 | 3941228.9214 | 10254269.1964 | 6998749.4307 | 31299962.7316 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 56777646.2133 | 109541223.1575 | 133352.1432 | 7.8915 | 7194.7397 | 13880.8253 | 146.6745 | 282.9794
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.1265 | 17.0008 | 2.0108 | 4 | 7082.2762 | 13642.2 | 144.3818 | 278.1147 | 87.2813 | 12.3598 | 72.5129 | 4666580.1704 | 0 | 3767538.448 | 0 | 0 | 0 | 1732095.288 | 3964823.4235 | 10315657.2508 | 7040648.0393 | 31487342.62 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 56965026.1017 | 109728603.0459 | 177827.941 | 8.0433 | 7082.2762 | 13642.2 | 144.3818 | 278.1147
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.4144 | 17.1918 | 2.0399 | 4 | 6998.2952 | 13464.7186 | 142.6697 | 274.4965 | 87.192 | 12.3254 | 95.9656 | 4694541.2075 | 0 | 3799438.2768 | 0 | 0 | 0 | 1716927.0037 | 3982253.5303 | 10361006.8134 | 7071600.0476 | 31625766.8794 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57103450.3611 | 109867027.3053 | 237137.3706 | 8.1596 | 6998.2952 | 13464.7186 | 142.6697 | 274.4965
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.387 | 17.3363 | 2.062 | 4 | 6935.5199 | 13332.5317 | 141.39 | 271.8017 | 87.1235 | 12.2991 | 96.3014 | 4715466.835 | 0 | 3823493.3456 | 0 | 0 | 0 | 1704823.3247 | 3995075.567 | 10394367.1228 | 7094369.1442 | 31727595.3393 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57205278.821 | 109968855.7652 | 316227.766 | 8.2482 | 6935.5199 | 13332.5317 | 141.39 | 271.8017
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.1077 | 17.4436 | 2.0787 | 4 | 6888.5594 | 13234.1886 | 140.4326 | 269.7968 | 87.0722 | 12.2795 | 84.1767 | 4730866.7412 | 0 | 3841298.8599 | 0 | 0 | 0 | 1695101.7414 | 4004234.2636 | 10418196.1725 | 7110632.9602 | 31800330.7389 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57278014.2206 | 110041591.1648 | 421696.5034 | 8.3149 | 6888.5594 | 13234.1886 | 140.4326 | 269.7968
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6756 | 17.5279 | 2.0915 | 4 | 6853.4086 | 13160.1741 | 139.716 | 268.2879 | 87.0314 | 12.264 | 85.0913 | 4742939.3863 | 0 | 3855318.623 | 0 | 0 | 0 | 1688019.8917 | 4011648.3814 | 10437486.1861 | 7123798.7909 | 31859211.2594 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57336894.7411 | 110100471.6853 | 562341.3252 | 8.3662 | 6853.4086 | 13160.1741 | 139.716 | 268.2879
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0823 | 17.5886 | 2.1011 | 4 | 6827.0856 | 13105.2747 | 139.1794 | 267.1688 | 87.0021 | 12.2528 | 86.6374 | 4751550.9661 | 0 | 3865353.4389 | 0 | 0 | 0 | 1682209.1157 | 4016654.2731 | 10450510.4894 | 7132688.1455 | 31898966.4286 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57376649.9103 | 110140226.8545 | 749894.2093 | 8.4043 | 6827.0856 | 13105.2747 | 139.1794 | 267.1688
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3964 | 17.6354 | 2.1083 | 4 | 6807.3667 | 13064.0141 | 138.7774 | 266.3276 | 86.9793 | 12.2442 | 94.5243 | 4758182.5913 | 0 | 3873100.2688 | 0 | 0 | 0 | 1677921.7982 | 4020589.8168 | 10460749.9669 | 7139676.7993 | 31930221.2414 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57407904.7231 | 110171481.6673 | 1000000 | 8.4332 | 6807.3667 | 13064.0141 | 138.7774 | 266.3276
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.6398 | 17.6716 | 2.1138 | 4 | 6792.5912 | 13032.9657 | 138.4762 | 265.6946 | 86.9615 | 12.2375 | 90.1844 | 4763309.5423 | 0 | 3879100.8792 | 0 | 0 | 0 | 1674792.1469 | 4023709.0017 | 10468865.4462 | 7145215.7807 | 31954992.7971 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57432676.2789 | 110196253.2231 | 1333521.4322 | 8.4552 | 6792.5912 | 13032.9657 | 138.4762 | 265.6946
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8056 | 17.6965 | 2.1178 | 4 | 6781.5177 | 13010.0727 | 138.2504 | 265.2279 | 86.9494 | 12.2329 | 85.3539 | 4766794.7494 | 0 | 3883186.3032 | 0 | 0 | 0 | 1672122.5818 | 4025620.4174 | 10473838.5579 | 7148610.0316 | 31970172.6414 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57447856.1231 | 110211433.0673 | 1778279.41 | 8.4712 | 6781.5177 | 13010.0727 | 138.2504 | 265.2279
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.9519 | 17.7181 | 2.121 | 4 | 6773.2174 | 12992.4568 | 138.0812 | 264.8688 | 86.9387 | 12.2288 | 79.2181 | 4769868.3436 | 0 | 3886792.5335 | 0 | 0 | 0 | 1670488.9885 | 4027588.4476 | 10478958.9687 | 7152104.8172 | 31985802.0991 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57463485.5808 | 110227062.525 | 2371373.7057 | 8.4839 | 6773.2174 | 12992.4568 | 138.0812 | 264.8688
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.0419 | 17.7316 | 2.1232 | 4 | 6766.9951 | 12979.6751 | 137.9543 | 264.6082 | 86.9321 | 12.2263 | 90.584 | 4771756.2117 | 0 | 3889009.9097 | 0 | 0 | 0 | 1668910.2799 | 4028573.7965 | 10481522.6444 | 7153854.5785 | 31993627.4206 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57471310.9024 | 110234887.8466 | 3162277.6602 | 8.4929 | 6766.9951 | 12979.6751 | 137.9543 | 264.6082
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1151 | 17.7426 | 2.1249 | 4 | 6762.3302 | 12969.976 | 137.8592 | 264.4105 | 86.9268 | 12.2243 | 86.9103 | 4773290.0328 | 0 | 3890812.3067 | 0 | 0 | 0 | 1667820.1141 | 4029449.7569 | 10483801.7137 | 7155410.0902 | 32000584.0144 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57478267.4961 | 110241844.4403 | 4216965.0343 | 8.4998 | 6762.3302 | 12969.976 | 137.8592 | 264.4105
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1734 | 17.7512 | 2.1263 | 4 | 6758.8326 | 12962.6326 | 137.7879 | 264.2608 | 86.9225 | 12.2227 | 90.5292 | 4774512.7282 | 0 | 3892249.6668 | 0 | 0 | 0 | 1667060.2567 | 4030190.8341 | 10485729.8446 | 7156726.0792 | 32006469.4096 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57484152.8913 | 110247729.8355 | 5623413.2519 | 8.505 | 6758.8326 | 12962.6326 | 137.7879 | 264.2608
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2271 | 17.7591 | 2.1273 | 4 | 6756.2102 | 12956.9179 | 137.7345 | 264.1443 | 86.9186 | 12.2212 | 83.6256 | 4775638.3703 | 0 | 3893573.1867 | 0 | 0 | 0 | 1666662.0509 | 4030990.7071 | 10487810.95 | 7158146.4763 | 32012821.7414 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57490505.2231 | 110254082.1673 | 7498942.0933 | 8.5093 | 6756.2102 | 12956.9179 | 137.7345 | 264.1443
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2466 | 17.7622 | 2.128 | 4 | 6754.2439 | 12953.0724 | 137.6944 | 264.0659 | 86.9171 | 12.2206 | 86.431 | 4776044.9398 | 0 | 3894051.816 | 0 | 0 | 0 | 1666000.0751 | 4031077.7641 | 10488037.4544 | 7158301.0702 | 32013513.1196 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57491196.6013 | 110254773.5455 | 10000000 | 8.5119 | 6754.2439 | 12953.0724 | 137.6944 | 264.0659
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.8516 | [19 empty] | 100 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8504 | [19 empty] | 133.3521 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.026643 | 0.0019696 | 4 | 3447047.493 | 10298784.7991 | 70272.7256 | 209954.6583 | 56.8167 | 11.2736 | 25.2105 | 147029.0526 | 0 | 55146.4124 | 0 | 0 | 0 | 147828.8774 | 136501.6936 | 355149.4063 | 242396.7674 | 1084052.2099 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 27157598.102 | 81139078.9021 | 177.8279 | 0.0078785 | 3447047.493 | 10298784.7991 | 70272.7256 | 209954.6583
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.015016 | 0.0047544 | 4 | 1425427.0637 | 4263921.9105 | 29059.2587 | 86925.8155 | 56.8167 | 11.2736 | 25.1599 | 147029.0547 | 0 | 55146.4115 | 0 | 0 | 0 | 131900.0838 | 130289.4645 | 338986.4606 | 231365.2248 | 1034716.7 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 27108262.5922 | 81089743.3923 | 237.1374 | 0.019018 | 1425427.0637 | 4263921.9105 | 29059.2587 | 86925.8155
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4392 | 0.13198 | 0.014374 | 4 | 492777.9954 | 1431627.8038 | 10045.946 | 29185.6692 | 71.5135 | 12.6937 | 46.4531 | 308655.7324 | 0 | 152011.2572 | 0 | 0 | 0 | 268991.6888 | 284566.8846 | 740384.661 | 505327.7445 | 2259937.9685 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 28333483.8606 | 82314964.6608 | 316.2278 | 0.057497 | 492777.9954 | 1431627.8038 | 10045.946 | 29185.6692
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7085 | 0.27377 | 0.025919 | 4 | 280230.5194 | 800908.7824 | 5712.8782 | 16327.6088 | 76.3241 | 13.1078 | 56.5245 | 409274.2722 | 0 | 214491.5634 | 0 | 0 | 0 | 338196.1864 | 375165.1886 | 976102.8638 | 666210.2614 | 2979440.3359 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 29052986.2281 | 83034467.0282 | 421.6965 | 0.10368 | 280230.5194 | 800908.7824 | 5712.8782 | 16327.6088
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3085 | 0.46758 | 0.042342 | 4 | 176443.2757 | 495163.1365 | 3597.0348 | 10094.5703 | 80.0753 | 13.4122 | 67.5883 | 526345.906 | 0 | 288967.0566 | 0 | 0 | 0 | 415001.2832 | 479822.5559 | 1248399.8652 | 852058.5601 | 3810595.2269 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 29884141.1191 | 83865621.9192 | 562.3413 | 0.16937 | 176443.2757 | 495163.1365 | 3597.0348 | 10094.5703
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3501 | 0.72671 | 0.065035 | 4 | 118622.0815 | 326130.0958 | 2418.2716 | 6648.6031 | 83.0388 | 13.6405 | 58.2458 | 664014.3355 | 0 | 378723.4326 | 0 | 0 | 0 | 502179.3695 | 602517.6837 | 1567627.4195 | 1069937.9253 | 4785000.1661 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 30858546.0583 | 84840026.8584 | 749.8942 | 0.26014 | 118622.0815 | 326130.0958 | 2418.2716 | 6648.6031
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9714 | 1.0688 | 0.095823 | 4 | 83514.4855 | 224350.4681 | 1702.5557 | 4573.6877 | 85.3831 | 13.8116 | 38.2423 | 826829.0222 | 0 | 487567.5838 | 0 | 0 | 0 | 602460.4079 | 747574.2354 | 1945034.812 | 1327526.2257 | 5936992.2871 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 32010538.1793 | 85992018.9794 | 1000 | 0.38329 | 83514.4855 | 224350.4681 | 1702.5557 | 4573.6877
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3212 | 1.5137 | 0.137 | 4 | 60888.6815 | 159393.5534 | 1241.2981 | 3249.4532 | 87.2202 | 13.9382 | 43.3479 | 1018632.2269 | 0 | 619043.18 | 0 | 0 | 0 | 717298.983 | 918440.0121 | 2389592.5134 | 1630945.9916 | 7293952.907 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 33367498.7992 | 87348979.5993 | 1333.5214 | 0.54801 | 60888.6815 | 159393.5534 | 1241.2981 | 3249.4532
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5741 | 2.0853 | 0.19143 | 4 | 45651.2548 | 116147.6434 | 930.6626 | 2367.8268 | 88.6415 | 14.0273 | 44.499 | 1243344.5692 | 0 | 777035.2834 | 0 | 0 | 0 | 847700.2844 | 1118551.2534 | 2910240.915 | 1986299.2239 | 8883171.5292 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 34956717.4214 | 88938198.2215 | 1778.2794 | 0.76573 | 45651.2548 | 116147.6434 | 930.6626 | 2367.8268
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9339 | 2.8119 | 0.26253 | 4 | 35050.5437 | 86456.2835 | 714.5527 | 1762.5283 | 89.723 | 14.0832 | 37.9014 | 1505028.3587 | 0 | 965827.6519 | 0 | 0 | 0 | 994550.7786 | 1351508.6478 | 3516348.269 | 2399979.9473 | 10733243.6534 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 36806789.5455 | 90788270.3457 | 2371.3737 | 1.0501 | 35050.5437 | 86456.2835 | 714.5527 | 1762.5283
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.5427 | 3.7147 | 0.35381 | 4 | 27495.019 | 65638.3183 | 560.5232 | 1338.1259 | 90.5143 | 14.1064 | 50.8202 | 1803643.7653 | 0 | 1187057.989 | 0 | 0 | 0 | 1154320.8304 | 1616558.808 | 4205954.4167 | 2870650.3131 | 12838186.1227 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 38911732.0148 | 92893212.815 | 3162.2777 | 1.4152 | 27495.019 | 65638.3183 | 560.5232 | 1338.1259
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5204 | 4.8123 | 0.46852 | 4 | 22014.9027 | 50819.2431 | 448.8036 | 1036.019 | 91.0588 | 14.0955 | 52.9493 | 2137808.9028 | 0 | 1441613.6591 | 0 | 0 | 0 | 1322992.4515 | 1911941.8552 | 4974480.514 | 3395185.1662 | 15184022.5488 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 41257568.4409 | 95239049.2411 | 4216.965 | 1.8741 | 22014.9027 | 50819.2431 | 448.8036 | 1036.019
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.8313 | 6.103 | 0.60831 | 4 | 17993.8731 | 40179.035 | 366.8294 | 819.104 | 91.3837 | 14.0473 | 61.1282 | 2499959.5823 | 0 | 1725864.1194 | 0 | 0 | 0 | 1492012.2488 | 2229956.0207 | 5801888.139 | 3959907.8718 | 17709587.982 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 43783133.8742 | 97764614.6743 | 5623.4133 | 2.4332 | 17993.8731 | 40179.035 | 366.8294 | 819.104
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.1861 | 7.5509 | 0.77147 | 4 | 15025.7089 | 32518.6775 | 306.3194 | 662.9372 | 91.5084 | 13.9596 | 60.8868 | 2874569.2357 | 0 | 2029665.9669 | 0 | 0 | 0 | 1648094.9941 | 2555408.7767 | 6648649.4506 | 4537839.8661 | 20294228.2903 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 46367774.1824 | 100349254.9825 | 7498.9421 | 3.0859 | 15025.7089 | 32518.6775 | 306.3194 | 662.9372
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.0144 | 9.08 | 0.95164 | 4 | 12831.9981 | 27013.2416 | 261.5976 | 550.7015 | 91.4545 | 13.8347 | 70.236 | 3239677.6737 | 0 | 2336547.8678 | 0 | 0 | 0 | 1776087.2736 | 2867401.9979 | 7460391.8135 | 5091870.7084 | 22771977.3349 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 48845523.2271 | 102827004.0272 | 10000 | 3.8065 | 12831.9981 | 27013.2416 | 261.5976 | 550.7015
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.6406 | 10.596 | 1.1386 | 4 | 11213.1053 | 23065.9325 | 228.5943 | 470.2302 | 91.2573 | 13.6816 | 70.4455 | 3574550.0885 | 0 | 2629035.174 | 0 | 0 | 0 | 1866287.2503 | 3147250.28 | 8188499.6389 | 5588819.2604 | 24994441.6922 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 51067987.5843 | 105049468.3845 | 13335.2143 | 4.5543 | 11213.1053 | 23065.9325 | 228.5943 | 470.2302
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.4554 | 12.0103 | 1.3208 | 4 | 10020.6385 | 20238.1572 | 204.2843 | 412.5822 | 90.9649 | 13.5144 | 74.3835 | 3864803.831 | 0 | 2892827.4629 | 0 | 0 | 0 | 1917077.3097 | 3383136.3554 | 8802226.8201 | 6007700.6724 | 26867772.4514 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 52941318.3436 | 106922799.1437 | 17782.7941 | 5.2832 | 10020.6385 | 20238.1572 | 204.2843 | 412.5822
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0741 | 13.2638 | 1.4887 | 4 | 9142.9174 | 18208.042 | 186.3907 | 371.1956 | 90.6276 | 13.3476 | 68.1831 | 4105300.3713 | 0 | 3120148.7938 | 0 | 0 | 0 | 1934659.516 | 3572442.3856 | 9294762.2787 | 6343866.2435 | 28371179.5889 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 54444725.481 | 108426206.2812 | 23713.7371 | 5.9549 | 9142.9174 | 18208.042 | 186.3907 | 371.1956
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.3091 | 14.3252 | 1.636 | 4 | 8496.3927 | 16745.3879 | 173.2105 | 341.3774 | 90.2891 | 13.1933 | 77.2758 | 4297072.6045 | 0 | 3308229.3901 | 0 | 0 | 0 | 1927951.9067 | 3717969.0215 | 9673392.7337 | 6602289.3091 | 29526904.9655 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 55600450.8577 | 109581931.6578 | 31622.7766 | 6.544 | 8496.3927 | 16745.3879 | 173.2105 | 341.3774
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2166 | 15.1979 | 1.7605 | 4 | 8019.2935 | 15685.0038 | 163.4841 | 319.76 | 89.9762 | 13.0578 | 83.3763 | 4446895.9418 | 0 | 3460123.1794 | 0 | 0 | 0 | 1907432.911 | 3827636.2926 | 9958724.4771 | 6797034.0869 | 30397846.8888 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 56471392.781 | 110452873.5811 | 42169.6503 | 7.0419 | 8019.2935 | 15685.0038 | 163.4841 | 319.76
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9157 | 15.8965 | 1.8625 | 4 | 7666.3842 | 14912.1892 | 156.2896 | 304.0051 | 89.704 | 12.944 | 78.8907 | 4561758.4011 | 0 | 3579962.6939 | 0 | 0 | 0 | 1880468.5705 | 3908653.9696 | 10169515.8537 | 6940903.5328 | 31041263.0216 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 57114808.9137 | 111096289.7139 | 56234.1325 | 7.45 | 7666.3842 | 14912.1892 | 156.2896 | 304.0051
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.6035 | 16.4472 | 1.9443 | 4 | 7404.6947 | 14345.5495 | 150.9547 | 292.4534 | 89.4761 | 12.8509 | 76.7082 | 4649222.9896 | 0 | 3673437.5903 | 0 | 0 | 0 | 1852606.2307 | 3968354.0562 | 10324843.2328 | 7046917.6607 | 31515381.7602 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 57588927.6524 | 111570408.4525 | 74989.4209 | 7.7774 | 7404.6947 | 14345.5495 | 150.9547 | 292.4534
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.4392 | 16.8727 | 2.0087 | 4 | 7210.2064 | 13928.6852 | 146.9898 | 283.9551 | 89.2923 | 12.7771 | 84.975 | 4714874.1738 | 0 | 3744989.1685 | 0 | 0 | 0 | 1826299.9833 | 4011603.697 | 10437369.9265 | 7123719.4413 | 31858856.3904 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 57932402.2825 | 111913883.0827 | 100000 | 8.0348 | 7210.2064 | 13928.6852 | 146.9898 | 283.9551
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6318 | 17.2025 | 2.0589 | 4 | 7065.3806 | 13620.0367 | 144.0373 | 277.6629 | 89.1451 | 12.7187 | 78.9 | 4764680.5753 | 0 | 3800129.5645 | 0 | 0 | 0 | 1803748.0389 | 4043737.6897 | 10520975.9839 | 7180782.2935 | 32114054.1458 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58187600.038 | 112169080.8381 | 133352.1432 | 8.2356 | 7065.3806 | 13620.0367 | 144.0373 | 277.6629
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3024 | 17.4543 | 2.0976 | 4 | 6957.3639 | 13391.1168 | 141.8353 | 272.996 | 89.0299 | 12.6735 | 96.682 | 4802066.6511 | 0 | 3842036.2101 | 0 | 0 | 0 | 1784884.3911 | 4067305.0284 | 10582293.3649 | 7222632.666 | 32301218.3116 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58374764.2038 | 112356245.0039 | 177827.941 | 8.3904 | 6957.3639 | 13391.1168 | 141.8353 | 272.996
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5741 | 17.6464 | 2.1272 | 4 | 6876.6985 | 13220.795 | 140.1908 | 269.5238 | 88.9405 | 12.6385 | 87.1276 | 4830200.6939 | 0 | 3873878.3464 | 0 | 0 | 0 | 1769654.1085 | 4084755.928 | 10627697.0261 | 7253621.5977 | 32439807.7007 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58513353.5929 | 112494834.393 | 237137.3706 | 8.5089 | 6876.6985 | 13220.795 | 140.1908 | 269.5238
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5339 | 17.7916 | 2.1498 | 4 | 6816.3986 | 13093.9334 | 138.9615 | 266.9375 | 88.872 | 12.6119 | 95.5625 | 4851246.9027 | 0 | 3897876.9167 | 0 | 0 | 0 | 1757509.2825 | 4097586.9097 | 10661080.6084 | 7276406.5786 | 32541707.1986 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58615253.0907 | 112596733.8909 | 316227.766 | 8.5992 | 6816.3986 | 13093.9334 | 138.9615 | 266.9375
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2527 | 17.9005 | 2.1669 | 4 | 6771.2882 | 12999.3786 | 138.0419 | 265.0099 | 88.8201 | 12.5919 | 93.4537 | 4866903.4573 | 0 | 3915831.7653 | 0 | 0 | 0 | 1747903.6237 | 4106949.1501 | 10685439.2373 | 7293031.8433 | 32616059.077 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58689604.9692 | 112671085.7693 | 421696.5034 | 8.6674 | 6771.2882 | 12999.3786 | 138.0419 | 265.0099
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.801 | 17.9836 | 2.1798 | 4 | 6737.5212 | 12928.5897 | 137.3535 | 263.5668 | 88.7802 | 12.5765 | 84.0206 | 4878784.2419 | 0 | 3929515.6329 | 0 | 0 | 0 | 1740592.2138 | 4114067.9145 | 10703960.8023 | 7305673.1919 | 32672593.9973 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58746139.8895 | 112727620.6896 | 562341.3252 | 8.7193 | 6737.5212 | 12928.5897 | 137.3535 | 263.5668
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2077 | 18.0453 | 2.1895 | 4 | 6712.234 | 12875.775 | 136.838 | 262.4901 | 88.7505 | 12.565 | 84.1066 | 4887563.9099 | 0 | 3939661.2748 | 0 | 0 | 0 | 1734872.3874 | 4119218.0531 | 10717360.4063 | 7314818.697 | 32713494.7284 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58787040.6205 | 112768521.4207 | 749894.2093 | 8.7582 | 6712.234 | 12875.775 | 136.838 | 262.4901
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5218 | 18.0929 | 2.1969 | 4 | 6693.2908 | 12836.078 | 136.4518 | 261.6808 | 88.7274 | 12.5561 | 92.6104 | 4894325.1026 | 0 | 3947493.732 | 0 | 0 | 0 | 1730657.6769 | 4123265.8395 | 10727891.9163 | 7322006.669 | 32745640.9364 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58819186.8286 | 112800667.6287 | 1000000 | 8.7878 | 6693.2908 | 12836.078 | 136.4518 | 261.6808
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7413 | 18.1264 | 2.2024 | 4 | 6679.0963 | 12806.6997 | 136.1624 | 261.0819 | 88.7112 | 12.5499 | 84.5601 | 4899038.1385 | 0 | 3952964.1422 | 0 | 0 | 0 | 1727158.3094 | 4125872.6301 | 10734674.2507 | 7326635.7516 | 32766343.2223 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58839889.1145 | 112821369.9146 | 1333521.4322 | 8.8096 | 6679.0963 | 12806.6997 | 136.1624 | 261.0819
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9265 | 18.1543 | 2.2066 | 4 | 6668.4581 | 12784.2723 | 135.9455 | 260.6247 | 88.6975 | 12.5446 | 82.9395 | 4903009.9704 | 0 | 3957580.1497 | 0 | 0 | 0 | 1724874.5425 | 4128331.2184 | 10741070.9932 | 7331001.6598 | 32785868.5341 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58859414.4263 | 112840895.2264 | 1778279.41 | 8.8265 | 6668.4581 | 12784.2723 | 135.9455 | 260.6247
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.0554 | 18.174 | 2.2097 | 4 | 6660.484 | 12767.6789 | 135.783 | 260.2864 | 88.6879 | 12.541 | 95.4895 | 4905770.0994 | 0 | 3960791.7424 | 0 | 0 | 0 | 1722967.1252 | 4129916.2971 | 10745195.0428 | 7333816.4084 | 32798456.7154 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58872002.6075 | 112853483.4077 | 2371373.7057 | 8.839 | 6660.484 | 12767.6789 | 135.783 | 260.2864
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.148 | 18.1881 | 2.2121 | 4 | 6654.5063 | 12755.3288 | 135.6611 | 260.0346 | 88.681 | 12.5383 | 92.453 | 4907751.0529 | 0 | 3963098.6291 | 0 | 0 | 0 | 1721455.5166 | 4130999.0275 | 10748012.085 | 7335739.0976 | 32807055.4087 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58880601.3009 | 112862082.101 | 3162277.6602 | 8.8482 | 6654.5063 | 12755.3288 | 135.6611 | 260.0346
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2212 | 18.1992 | 2.2138 | 4 | 6650.0247 | 12745.9966 | 135.5697 | 259.8444 | 88.6756 | 12.5363 | 90.2371 | 4909315.1534 | 0 | 3964921.0255 | 0 | 0 | 0 | 1720383.0218 | 4131901.4883 | 10750360.1029 | 7337341.6681 | 32814222.4599 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58887768.3521 | 112869249.1522 | 4216965.0343 | 8.8553 | 6650.0247 | 12745.9966 | 135.5697 | 259.8444
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2749 | 18.2074 | 2.2151 | 4 | 6646.6646 | 12739.0251 | 135.5012 | 259.7023 | 88.6716 | 12.5347 | 82.7484 | 4910462.8159 | 0 | 3966258.8456 | 0 | 0 | 0 | 1719555.4342 | 4132548.0673 | 10752042.369 | 7338489.8492 | 32819357.3814 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58892903.2735 | 112874384.0737 | 5623413.2519 | 8.8605 | 6646.6646 | 12739.0251 | 135.5012 | 259.7023
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3138 | 18.2134 | 2.2161 | 4 | 6644.1452 | 12733.8273 | 135.4499 | 259.5963 | 88.6687 | 12.5336 | 85.5013 | 4911293.4857 | 0 | 3967227.5083 | 0 | 0 | 0 | 1718908.648 | 4132997.5604 | 10753211.8577 | 7339288.0493 | 32822927.1092 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58896473.0014 | 112877953.8015 | 7498942.0933 | 8.8644 | 6644.1452 | 12733.8273 | 135.4499 | 259.5963
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3527 | 18.2192 | 2.2169 | 4 | 6642.2562 | 12729.7309 | 135.4114 | 259.5128 | 88.6658 | 12.5325 | 90.9382 | 4912124.4618 | 0 | 3968196.4892 | 0 | 0 | 0 | 1718595.4523 | 4133577.3972 | 10754720.4743 | 7340317.7111 | 32827531.9859 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58901077.8781 | 112882558.6782 | 10000000 | 8.8676 | 6642.2562 | 12729.7309 | 135.4114 | 259.5128
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.1497 | [19 empty] | 100 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0247 | [19 empty] | 133.3521 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.028034 | 0.0021197 | 4 | 3275144.0619 | 9786997.0704 | 66768.2417 | 199521.1732 | 57.1818 | 11.5312 | 25.0161 | 148945.1355 | 0 | 54964.1632 | 0 | 0 | 0 | 149388.4476 | 137786.121 | 358491.2231 | 244677.626 | 1094252.7165 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 27769521.1099 | 82982676.9795 | 177.8279 | 0.0084789 | 3275144.0619 | 9786997.0704 | 66768.2417 | 199521.1732
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.016451 | 0.0048952 | 4 | 1415709.7271 | 4235483.4301 | 28861.1577 | 86346.0586 | 57.1818 | 11.5312 | 25.5196 | 148945.1377 | 0 | 54964.1622 | 0 | 0 | 0 | 133591.494 | 131625.3096 | 342462.0555 | 233737.3898 | 1045325.5488 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 27720593.9423 | 82933749.8119 | 237.1374 | 0.019581 | 1415709.7271 | 4235483.4301 | 28861.1577 | 86346.0586
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.1412 | 0.015409 | 4 | 471115.4986 | 1366901.9721 | 9604.3267 | 27866.1456 | 72.9029 | 13.0475 | 45.3334 | 322910.0461 | 0 | 158438.8832 | 0 | 0 | 0 | 281471.6593 | 297500.0296 | 774034.0512 | 528294.1448 | 2362648.8142 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 29037917.2076 | 84251073.0772 | 316.2278 | 0.061637 | 471115.4986 | 1366901.9721 | 9604.3267 | 27866.1456
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8593 | 0.28996 | 0.027728 | 4 | 268570.0741 | 766384.8417 | 5475.1642 | 15623.7916 | 77.8148 | 13.4668 | 52.2057 | 427902.6437 | 0 | 223184.3468 | 0 | 0 | 0 | 353712.5735 | 391871.8299 | 1019570.1176 | 695877.5553 | 3112119.0668 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 29787387.4602 | 85000543.3298 | 421.6965 | 0.11091 | 268570.0741 | 766384.8417 | 5475.1642 | 15623.7916
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4935 | 0.49167 | 0.045226 | 4 | 169394.1843 | 474600.247 | 3453.3296 | 9675.368 | 81.6207 | 13.7729 | 56.2569 | 549030.9478 | 0 | 299693.5451 | 0 | 0 | 0 | 432702.6942 | 499756.603 | 1300264.1668 | 887457.0116 | 3968904.9684 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 30644173.3619 | 85857329.2315 | 562.3413 | 0.1809 | 169394.1843 | 474600.247 | 3453.3296 | 9675.368
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6083 | 0.76433 | 0.069418 | 4 | 114040.2891 | 312882.2103 | 2324.8655 | 6378.5271 | 84.672 | 14.0057 | 55.148 | 693494.1392 | 0 | 393205.3788 | 0 | 0 | 0 | 524634.9257 | 628420.433 | 1635021.06 | 1115935.4698 | 4990711.4064 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 31665979.7999 | 86879135.6695 | 749.8942 | 0.27767 | 114040.2891 | 312882.2103 | 2324.8655 | 6378.5271
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3003 | 1.1216 | 0.10219 | 4 | 80390.5108 | 215461.3229 | 1638.8693 | 4392.4705 | 87.0644 | 14.1789 | 45.3269 | 862891.0817 | 0 | 505624.7907 | 0 | 0 | 0 | 628774.7077 | 778943.3262 | 2026650.7516 | 1383230.7815 | 6186115.4395 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 32861383.833 | 88074539.7026 | 1000 | 0.40877 | 80390.5108 | 215461.3229 | 1638.8693 | 4392.4705
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7567 | 1.5883 | 0.14605 | 4 | 58672.4404 | 153180.5187 | 1196.1171 | 3122.7921 | 88.9464 | 14.3063 | 58.3279 | 1063370.4986 | 0 | 642077.543 | 0 | 0 | 0 | 749024.9192 | 957244.4547 | 2490553.7133 | 1699854.0851 | 7602125.2139 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 34277393.6073 | 89490549.4769 | 1333.5214 | 0.58422 | 58672.4404 | 153180.5187 | 1196.1171 | 3122.7921
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1271 | 2.1856 | 0.20396 | 4 | 44037.9374 | 111714.8022 | 897.7729 | 2277.4573 | 90.3968 | 14.3955 | 48.1982 | 1297320.5192 | 0 | 805388.6905 | 0 | 0 | 0 | 884589.8585 | 1165046.6366 | 3031212.3645 | 2068864.724 | 9252422.7932 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 35927691.1867 | 91140847.0563 | 1778.2794 | 0.81584 | 44037.9374 | 111714.8022 | 897.7729 | 2277.4573
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6176 | 2.9427 | 0.27948 | 4 | 33849.9457 | 83238.5387 | 690.0769 | 1696.9302 | 91.498 | 14.4505 | 53.2863 | 1568965.9814 | 0 | 999965.0423 | 0 | 0 | 0 | 1036429.326 | 1406090.5364 | 3658359.1468 | 2496905.2895 | 11166715.3223 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 37841983.7158 | 93055139.5854 | 2371.3737 | 1.1179 | 33849.9457 | 83238.5387 | 690.0769 | 1696.9302
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.3735 | 3.8815 | 0.3763 | 4 | 26584.9336 | 63266.7566 | 541.9698 | 1289.7784 | 92.3026 | 14.4718 | 38.7889 | 1878394.6451 | 0 | 1227568.6563 | 0 | 0 | 0 | 1201123.0219 | 1679763.6661 | 4370400.4923 | 2982888.1387 | 13340138.6204 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 40015407.0138 | 95228562.8834 | 3162.2777 | 1.5052 | 26584.9336 | 63266.7566 | 541.9698 | 1289.7784
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.5487 | 5.0253 | 0.49787 | 4 | 21313.8346 | 49038.5502 | 434.5113 | 999.7172 | 92.8568 | 14.4576 | 48.9762 | 2225556.9333 | 0 | 1490173.0099 | 0 | 0 | 0 | 1376123.1458 | 1985822.7047 | 5166703.3295 | 3526381.1875 | 15770760.3108 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 42446028.7043 | 97659184.5739 | 4216.965 | 1.9915 | 21313.8346 | 49038.5502 | 434.5113 | 999.7172
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.0345 | 6.3632 | 0.6455 | 4 | 17445.794 | 38829.6935 | 355.6561 | 791.5958 | 93.1835 | 14.4046 | 51.8096 | 2599614.7279 | 0 | 1781782.934 | 0 | 0 | 0 | 1549570.5076 | 2313077.5861 | 6018153.4016 | 4107513.3573 | 18369712.5145 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 45044980.908 | 100258136.7776 | 5623.4133 | 2.582 | 17445.794 | 38829.6935 | 355.6561 | 791.5958
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.524 | 7.856 | 0.81708 | 4 | 14591.0233 | 31484.5542 | 297.4577 | 641.8552 | 93.3043 | 14.3108 | 69.6441 | 2984422.7873 | 0 | 2091819.1826 | 0 | 0 | 0 | 1708025.8806 | 2645864.4617 | 6883996.5879 | 4698469.1232 | 21012598.0234 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 47687866.4169 | 102901022.2865 | 7498.9421 | 3.2683 | 14591.0233 | 31484.5542 | 297.4577 | 641.8552
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.4519 | 9.4267 | 1.0057 | 4 | 12481.8739 | 26206.9948 | 254.4599 | 534.265 | 93.243 | 14.1789 | 54.7813 | 3358143.6304 | 0 | 2403971.3327 | 0 | 0 | 0 | 1837061.6843 | 2963678.8925 | 7710884.5441 | 5262837.1442 | 23536577.2281 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 50211845.6215 | 105425001.4911 | 10000 | 4.0228 | 12481.8739 | 26206.9948 | 254.4599 | 534.265
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.1339 | 10.978 | 1.2005 | 4 | 10925.9915 | 22423.9219 | 222.7411 | 457.142 | 93.0366 | 14.0186 | 75.0875 | 3699638.2915 | 0 | 2700448.1622 | 0 | 0 | 0 | 1927107.6124 | 3247605.6858 | 8449603.8189 | 5767028.2284 | 25791431.7992 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 52466700.1926 | 107679856.0622 | 13335.2143 | 4.802 | 10925.9915 | 22423.9219 | 222.7411 | 457.142
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.9512 | 12.4183 | 1.3895 | 4 | 9780.2623 | 19714.5643 | 199.3839 | 401.9081 | 92.7355 | 13.845 | 65.8659 | 3994249.266 | 0 | 2966630.7173 | 0 | 0 | 0 | 1976638.3956 | 3485632.1678 | 9068899.899 | 6189710.5283 | 27681760.974 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 54357029.3674 | 109570185.237 | 17782.7941 | 5.5578 | 9780.2623 | 19714.5643 | 199.3839 | 401.9081
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5286 | 13.6886 | 1.5627 | 4 | 8937.0528 | 17769.754 | 182.1939 | 362.2605 | 92.3919 | 13.6732 | 75.5329 | 4237228.7047 | 0 | 3194948.2404 | 0 | 0 | 0 | 1992362.2335 | 3675570.2796 | 9563079.9045 | 6526998.5365 | 29190187.8992 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 55865456.2926 | 111078612.1622 | 23713.7371 | 6.251 | 8937.0528 | 17769.754 | 182.1939 | 362.2605
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.7272 | 14.7638 | 1.7144 | 4 | 8315.9502 | 16367.4942 | 169.5319 | 333.6735 | 92.0482 | 13.5147 | 72.5218 | 4431027.2996 | 0 | 3383874.5851 | 0 | 0 | 0 | 1984438.4618 | 3821742.7351 | 9943390.6496 | 6786568.4346 | 30351042.1658 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 57026310.5593 | 112239466.4288 | 31622.7766 | 6.8575 | 8315.9502 | 16367.4942 | 169.5319 | 333.6735
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5707 | 15.643 | 1.842 | 4 | 7857.5749 | 15351.2176 | 160.1873 | 312.9553 | 91.7329 | 13.3765 | 81.759 | 4581631.9741 | 0 | 3535610.3439 | 0 | 0 | 0 | 1962442.4347 | 3931077.0536 | 10227856.1186 | 6980721.9624 | 31219339.8872 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 57894608.2807 | 113107764.1503 | 42169.6503 | 7.368 | 7857.5749 | 15351.2176 | 160.1873 | 312.9553
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2233 | 16.3473 | 1.9465 | 4 | 7518.4765 | 14609.9337 | 153.2743 | 297.8433 | 91.4589 | 13.2605 | 102.496 | 4697260.0167 | 0 | 3655463.2183 | 0 | 0 | 0 | 1934650.1226 | 4012075.6095 | 10438597.7459 | 7124557.4533 | 31862604.1663 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 58537872.5598 | 113751028.4294 | 56234.1325 | 7.7859 | 7518.4765 | 14609.9337 | 153.2743 | 297.8433
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8534 | 16.8996 | 2.03 | 4 | 7266.9976 | 14066.66 | 148.1476 | 286.7679 | 91.231 | 13.1663 | 82.3848 | 4784841.5251 | 0 | 3748425.3953 | 0 | 0 | 0 | 1905866.3937 | 4071261.9925 | 10592588.5737 | 7229659.3575 | 32332643.2377 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 59007911.6312 | 114221067.5008 | 74989.4209 | 8.12 | 7266.9976 | 14066.66 | 148.1476 | 286.7679
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.6696 | 17.3297 | 2.0958 | 4 | 7080.077 | 13666.2021 | 144.3369 | 278.604 | 91.0457 | 13.0909 | 85.2779 | 4851194.0842 | 0 | 3820230.2 | 0 | 0 | 0 | 1879475.2631 | 4114850.8234 | 10705997.7706 | 7307063.4647 | 32678811.606 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 59354079.9994 | 114567235.869 | 100000 | 8.3833 | 7080.077 | 13666.2021 | 144.3369 | 278.604
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8233 | 17.6597 | 2.1469 | 4 | 6940.8734 | 13370.1593 | 141.4991 | 272.5688 | 90.8989 | 13.032 | 81.2059 | 4900995.4003 | 0 | 3874964.4217 | 0 | 0 | 0 | 1856452.4212 | 4146640.7748 | 10788708.7032 | 7363515.3757 | 32931277.0969 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 59606545.4904 | 114819701.36 | 133352.1432 | 8.5878 | 6940.8734 | 13370.1593 | 141.4991 | 272.5688
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4692 | 17.9124 | 2.1864 | 4 | 6837.0419 | 13150.4126 | 139.3823 | 268.0889 | 90.7839 | 12.9862 | 84.3685 | 4938504.3162 | 0 | 3916693.6831 | 0 | 0 | 0 | 1837377.9816 | 4170104.6325 | 10849756.8478 | 7405181.9888 | 33117619.45 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 59792887.8435 | 115006043.7131 | 177827.941 | 8.7454 | 6837.0419 | 13150.4126 | 139.3823 | 268.0889
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.7191 | 18.1046 | 2.2165 | 4 | 6759.4972 | 12986.9494 | 137.8015 | 264.7565 | 90.6948 | 12.9509 | 90.1166 | 4966666.558 | 0 | 3948323.3897 | 0 | 0 | 0 | 1821956.6746 | 4187409.1827 | 10894779.7377 | 7435911.0363 | 33255046.579 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 59930314.9725 | 115143470.8421 | 237137.3706 | 8.8661 | 6759.4972 | 12986.9494 | 137.8015 | 264.7565
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.6593 | 18.2496 | 2.2394 | 4 | 6701.5275 | 12865.2414 | 136.6197 | 262.2753 | 90.6268 | 12.9242 | 94.6422 | 4987668.5961 | 0 | 3972084.3173 | 0 | 0 | 0 | 1809626.8191 | 4200058.0957 | 10927689.6146 | 7458372.7035 | 33355500.1463 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60030768.5397 | 115243924.4093 | 316227.766 | 8.9578 | 6701.5275 | 12865.2414 | 136.6197 | 262.2753
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.3781 | 18.3603 | 2.2569 | 4 | 6658.1587 | 12774.2088 | 135.7356 | 260.4195 | 90.5743 | 12.9036 | 90.0508 | 5003620.9913 | 0 | 3990233.4585 | 0 | 0 | 0 | 1800166.0339 | 4209667.9887 | 10952692.5848 | 7475437.7445 | 33431818.8017 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60107087.1952 | 115320243.0648 | 421696.5034 | 9.0276 | 6658.1587 | 12774.2088 | 135.7356 | 260.4195
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9117 | 18.4427 | 2.27 | 4 | 6625.6945 | 12706.3534 | 135.0737 | 259.0362 | 90.5349 | 12.8882 | 87.6472 | 5015403.2054 | 0 | 4003695.7925 | 0 | 0 | 0 | 1792699.2167 | 4216601.3037 | 10970731.6483 | 7487749.776 | 33486880.9426 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60162149.336 | 115375305.2056 | 562341.3252 | 9.0801 | 6625.6945 | 12706.3534 | 135.0737 | 259.0362
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3138 | 18.5049 | 2.2799 | 4 | 6601.3825 | 12655.5941 | 134.5781 | 258.0014 | 90.5051 | 12.8766 | 86.9467 | 5024248.3355 | 0 | 4013834.7761 | 0 | 0 | 0 | 1786982.0204 | 4221775.4015 | 10984193.5895 | 7496937.8274 | 33527971.9505 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60203240.3439 | 115416396.2135 | 749894.2093 | 9.1198 | 6601.3825 | 12655.5941 | 134.5781 | 258.0014
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.6233 | 18.5526 | 2.2875 | 4 | 6583.1694 | 12617.4613 | 134.2068 | 257.224 | 90.4821 | 12.8676 | 84.2969 | 5031037.1339 | 0 | 4021635.5939 | 0 | 0 | 0 | 1782752.9478 | 4225816.0135 | 10994706.4329 | 7504113.0591 | 33560061.181 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60235329.5745 | 115448485.4441 | 1000000 | 9.1499 | 6583.1694 | 12617.4613 | 134.2068 | 257.224
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.8519 | 18.5879 | 2.2931 | 4 | 6569.5219 | 12588.9901 | 133.9286 | 256.6436 | 90.465 | 12.861 | 85.5993 | 5036039.7502 | 0 | 4027394.826 | 0 | 0 | 0 | 1779467.227 | 4228731.7032 | 11002292.4596 | 7509290.6782 | 33583216.6441 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60258485.0376 | 115471640.9072 | 1333521.4322 | 9.1724 | 6569.5219 | 12588.9901 | 133.9286 | 256.6436
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0176 | 18.6137 | 2.2973 | 4 | 6559.2935 | 12567.7829 | 133.7201 | 256.2113 | 90.4526 | 12.8561 | 82.2096 | 5039661.7409 | 0 | 4031570.5303 | 0 | 0 | 0 | 1776872.5573 | 4230760.8831 | 11007571.9694 | 7512894.0521 | 33599331.7331 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60274600.1265 | 115487755.9961 | 1778279.41 | 9.1892 | 6559.2935 | 12567.7829 | 133.7201 | 256.2113
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1419 | 18.633 | 2.3004 | 4 | 6551.6266 | 12551.8967 | 133.5638 | 255.8874 | 90.4432 | 12.8525 | 84.4794 | 5042373.8084 | 0 | 4034700.3824 | 0 | 0 | 0 | 1774910.5562 | 4232274.0513 | 11011508.9228 | 7515581.1037 | 33611348.8249 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60286617.2183 | 115499773.0879 | 2371373.7057 | 9.2018 | 6551.6266 | 12551.8967 | 133.5638 | 255.8874
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2493 | 18.6494 | 2.3029 | 4 | 6545.8791 | 12539.7068 | 133.4466 | 255.6389 | 90.4352 | 12.8494 | 86.2164 | 5044716.8572 | 0 | 4037406.1212 | 0 | 0 | 0 | 1773688.9974 | 4233766.6705 | 11015392.4117 | 7518231.6647 | 33623202.7227 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60298471.1161 | 115511626.9857 | 3162277.6602 | 9.2117 | 6545.8791 | 12539.7068 | 133.4466 | 255.6389
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.3077 | 18.6587 | 2.3046 | 4 | 6541.5702 | 12531.017 | 133.3588 | 255.4617 | 90.4308 | 12.8477 | 81.3448 | 5045987.3676 | 0 | 4038874.7567 | 0 | 0 | 0 | 1772364.5175 | 4234318.3903 | 11016827.8734 | 7519211.3968 | 33627584.3022 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60302852.6956 | 115516008.5652 | 4216965.0343 | 9.2184 | 6541.5702 | 12531.017 | 133.3588 | 255.4617
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.366 | 18.6676 | 2.306 | 4 | 6538.3394 | 12524.2107 | 133.2929 | 255.323 | 90.4264 | 12.846 | 88.283 | 5047258.3084 | 0 | 4040343.9429 | 0 | 0 | 0 | 1771633.3396 | 4235101.8805 | 11018866.3541 | 7520602.7017 | 33633806.5272 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60309074.9206 | 115522230.7902 | 5623413.2519 | 9.2239 | 6538.3394 | 12524.2107 | 133.2929 | 255.323
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4197 | 18.6757 | 2.3071 | 4 | 6535.9171 | 12518.909 | 133.2435 | 255.2149 | 90.4223 | 12.8444 | 80.4862 | 5048428.3786 | 0 | 4041696.7738 | 0 | 0 | 0 | 1771263.908 | 4235941.7335 | 11021051.4796 | 7522094.0948 | 33640476.3682 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60315744.7617 | 115528900.6313 | 7498942.0933 | 9.2284 | 6535.9171 | 12518.909 | 133.2435 | 255.2149
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4392 | 18.6789 | 2.3078 | 4 | 6534.1008 | 12515.3512 | 133.2065 | 255.1424 | 90.4209 | 12.8438 | 83.0482 | 5048850.9877 | 0 | 4042186.0002 | 0 | 0 | 0 | 1770608.4237 | 4236041.7105 | 11021311.5992 | 7522271.6317 | 33641270.353 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60316538.7465 | 115529694.6161 | 10000000 | 9.231 | 6534.1008 | 12515.3512 | 133.2065 | 255.1424
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.0494 | [19 empty] | 100 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3052 | [19 empty] | 133.3521 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.029413 | 0.002264 | 4 | 3134626.583 | 9369015.8598 | 63903.6028 | 191000.0608 | 57.5339 | 11.7875 | 26.2448 | 150826.3575 | 0 | 54774.7217 | 0 | 0 | 0 | 150945.025 | 139052.9807 | 361787.332 | 246927.2881 | 1104313.705 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 28387164.6906 | 84845766.8432 | 177.8279 | 0.009056 | 3134626.583 | 9369015.8598 | 63903.6028 | 191000.0608
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.017876 | 0.0050303 | 4 | 1408396.3332 | 4214321.3048 | 28712.0642 | 85914.6401 | 57.5339 | 11.7875 | 25.7389 | 150826.3598 | 0 | 54774.7207 | 0 | 0 | 0 | 135276.938 | 132942.4272 | 345888.9253 | 236076.2989 | 1055785.6699 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 28338636.6555 | 84797238.8081 | 237.1374 | 0.020121 | 1408396.3332 | 4214321.3048 | 28712.0642 | 85914.6401
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6755 | 0.15171 | 0.016505 | 4 | 450753.0026 | 1305939.0608 | 9189.2096 | 26623.3342 | 74.3512 | 13.4063 | 53.2215 | 338427.243 | 0 | 165558.8114 | 0 | 0 | 0 | 295254.4007 | 311703.7775 | 810989.2898 | 553516.8544 | 2475450.3768 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 29758301.3625 | 86216903.5151 | 316.2278 | 0.066019 | 450753.0026 | 1305939.0608 | 9189.2096 | 26623.3342
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.001 | 0.30573 | 0.029623 | 4 | 257599.6479 | 734078.7551 | 5251.5173 | 14965.1883 | 79.2812 | 13.8237 | 44.3758 | 446124.3946 | 0 | 231525.9635 | 0 | 0 | 0 | 368583.5513 | 408031.2247 | 1061613.5479 | 724573.0604 | 3240451.7424 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 30523302.728 | 86981904.8806 | 421.6965 | 0.11849 | 257599.6479 | 734078.7551 | 5251.5173 | 14965.1883
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6936 | 0.51791 | 0.048264 | 4 | 162759.316 | 455208.7007 | 3318.0688 | 9280.0451 | 83.197 | 14.1359 | 53.3114 | 573163.1085 | 0 | 311215.0372 | 0 | 0 | 0 | 451815.2423 | 521115.4213 | 1355835.4309 | 925385.5412 | 4138529.7814 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 31421380.7671 | 87879982.9197 | 562.3413 | 0.19305 | 162759.316 | 455208.7007 | 3318.0688 | 9280.0451
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8714 | 0.80338 | 0.074014 | 4 | 109725.181 | 300428.0629 | 2236.8962 | 6124.6324 | 86.3145 | 14.3713 | 45.9286 | 723781.5537 | 0 | 408041.1108 | 0 | 0 | 0 | 547688.5873 | 655009.3882 | 1704200.0672 | 1163151.5637 | 5201872.2709 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 32484723.2566 | 88943325.4091 | 749.8942 | 0.29606 | 109725.181 | 300428.0629 | 2236.8962 | 6124.6324
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6487 | 1.178 | 0.10889 | 4 | 77441.1439 | 207059.3201 | 1578.7425 | 4221.1843 | 88.7625 | 14.5466 | 50.5936 | 900727.4232 | 0 | 524662.4176 | 0 | 0 | 0 | 656672.1219 | 812004.1654 | 2112668.2735 | 1441939.5077 | 6448673.9093 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 33731524.8949 | 90190127.0475 | 1000 | 0.43558 | 77441.1439 | 207059.3201 | 1578.7425 | 4221.1843
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1855 | 1.6637 | 0.1555 | 4 | 56582.4352 | 147353.0118 | 1153.5095 | 3003.9905 | 90.6743 | 14.6743 | 46.3874 | 1108475.6558 | 0 | 665081.2989 | 0 | 0 | 0 | 780638.0016 | 996136.033 | 2591741.6222 | 1768916.9121 | 7910989.5235 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 35193840.5091 | 91652442.6617 | 1333.5214 | 0.62199 | 56582.4352 | 147353.0118 | 1153.5095 | 3003.9905
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6756 | 2.2876 | 0.21702 | 4 | 42515.4098 | 107553.1339 | 866.7341 | 2192.6161 | 92.1559 | 14.7637 | 47.6742 | 1351956.4206 | 0 | 833855.4047 | 0 | 0 | 0 | 921571.4213 | 1211879.4661 | 3153061.7803 | 2152029.454 | 9624353.9469 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 36907204.9325 | 93365807.0851 | 1778.2794 | 0.86809 | 42515.4098 | 107553.1339 | 866.7341 | 2192.6161
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.295 | 3.0755 | 0.29715 | 4 | 32716.0034 | 80216.5396 | 666.96 | 1635.3227 | 93.277 | 14.8177 | 60.1511 | 1633651.8824 | 0 | 1034218.624 | 0 | 0 | 0 | 1078358.7365 | 1461029.4048 | 3801298.8128 | 2594464.5486 | 11603022.0092 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 38885872.9948 | 95344475.1474 | 2371.3737 | 1.1886 | 32716.0034 | 80216.5396 | 666.96 | 1635.3227
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2212 | 4.054 | 0.39979 | 4 | 25724.6406 | 61029.7413 | 524.4316 | 1244.1738 | 94.0976 | 14.8371 | 50.5613 | 1955123.9994 | 0 | 1269042.403 | 0 | 0 | 0 | 1249163.245 | 1744598.5625 | 4539087.5932 | 3098020.5513 | 13855036.3543 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 41137887.3399 | 97596489.4925 | 3162.2777 | 1.5992 | 25724.6406 | 61029.7413 | 524.4316 | 1244.1738
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5692 | 5.2418 | 0.52838 | 4 | 20650.5071 | 47363.8196 | 420.9885 | 965.5755 | 94.6595 | 14.8195 | 45.5519 | 2314398.722 | 0 | 1538966.0447 | 0 | 0 | 0 | 1429382.5434 | 2060271.451 | 5360403.6956 | 3658585.6675 | 16362008.1242 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 43644859.1099 | 100103461.2625 | 4216.965 | 2.1135 | 20650.5071 | 47363.8196 | 420.9885 | 965.5755
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.213 | 6.6255 | 0.68401 | 4 | 16926.6993 | 37561.7334 | 345.0737 | 765.7467 | 94.9876 | 14.7616 | 62.9244 | 2699880.477 | 0 | 1837497.6274 | 0 | 0 | 0 | 1606626.581 | 2396161.8273 | 6234321.5543 | 4255052.5633 | 19029540.6303 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 46312391.6159 | 102770993.7685 | 5623.4133 | 2.7361 | 16926.6993 | 37561.7334 | 345.0737 | 765.7467
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8586 | 8.1667 | 0.86434 | 4 | 14178.863 | 30508.9052 | 289.0553 | 621.9653 | 95.1049 | 14.6612 | 64.8831 | 3095813.1334 | 0 | 2154474.0251 | 0 | 0 | 0 | 1768311.8516 | 2737253.6139 | 7121772.4156 | 4860756.0114 | 21738381.051 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 49021232.0366 | 105479834.1892 | 7498.9421 | 3.4573 | 14178.863 | 30508.9052 | 289.0553 | 621.9653
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9038 | 9.782 | 1.0617 | 4 | 12149.4486 | 25443.709 | 247.6829 | 518.7044 | 95.0358 | 14.5219 | 74.1289 | 3478776.2972 | 0 | 2472425.6382 | 0 | 0 | 0 | 1898952.2991 | 3061560.1515 | 7965551.5018 | 5436652.5757 | 24313918.4634 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 51596769.4491 | 108055371.6016 | 10000 | 4.2468 | 12149.4486 | 25443.709 | 247.6829 | 518.7044
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.6102 | 11.3646 | 1.2643 | 4 | 10652.9533 | 21816.7814 | 217.1749 | 444.7646 | 94.8204 | 14.3547 | 60.1914 | 3825868.616 | 0 | 2772025.8228 | 0 | 0 | 0 | 1987813.2332 | 3348425.9921 | 8711917.5747 | 5946062.7567 | 26592113.9955 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 53874964.9811 | 110333567.1337 | 13335.2143 | 5.0573 | 10652.9533 | 21816.7814 | 217.1749 | 444.7646
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.4346 | 12.8316 | 1.4601 | 4 | 9551.2524 | 19218.1369 | 194.7152 | 391.7877 | 94.5106 | 14.1746 | 73.9713 | 4124938.2854 | 0 | 3040709.6666 | 0 | 0 | 0 | 2036185.3254 | 3588714.9782 | 9337100.2266 | 6372762.7629 | 28500411.2451 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 55783262.2307 | 112241864.3833 | 17782.7941 | 5.8404 | 9551.2524 | 19218.1369 | 194.7152 | 391.7877
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9628 | 14.1176 | 1.6388 | 4 | 8740.5427 | 17353.5929 | 178.1878 | 353.7765 | 94.1611 | 13.998 | 89.2981 | 4370116.7459 | 0 | 3269786.5019 | 0 | 0 | 0 | 2049799.0236 | 3778983.8859 | 9832140.8948 | 6710638.191 | 30011465.2431 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 57294316.2287 | 113752918.3813 | 23713.7371 | 6.555 | 8740.5427 | 17353.5929 | 178.1878 | 353.7765
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.113 | 15.2047 | 1.7946 | 4 | 8143.377 | 16008.3489 | 166.0138 | 326.3518 | 93.8129 | 13.8355 | 72.7117 | 4565576.3786 | 0 | 3459218.7254 | 0 | 0 | 0 | 2040340.7891 | 3925402.9983 | 10213093.3906 | 6970646.0972 | 31174278.3791 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 58457129.3647 | 114915731.5173 | 31622.7766 | 7.1785 | 8143.377 | 16008.3489 | 166.0138 | 326.3518
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9083 | 16.0924 | 1.9255 | 4 | 7702.6321 | 15032.9665 | 157.0286 | 306.4674 | 93.4947 | 13.6944 | 77.9409 | 4717315.4991 | 0 | 3611172.1441 | 0 | 0 | 0 | 2017196.303 | 4034816.739 | 10497765.5003 | 7164940.6615 | 32043206.8471 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 59326057.8327 | 115784659.9853 | 42169.6503 | 7.7021 | 7702.6321 | 15032.9665 | 157.0286 | 306.4674
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5144 | 16.8021 | 2.0324 | 4 | 7376.5396 | 14321.2996 | 150.3807 | 291.9591 | 93.219 | 13.5761 | 93.0354 | 4833663.3977 | 0 | 3731011.9796 | 0 | 0 | 0 | 1988537.4632 | 4115753.0078 | 10708345.0693 | 7308665.5443 | 32685976.4619 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 59968827.4476 | 116427429.6002 | 56234.1325 | 8.1297 | 7376.5396 | 14321.2996 | 150.3807 | 291.9591
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1102 | 17.359 | 2.1178 | 4 | 7134.6775 | 13799.4216 | 145.4501 | 281.3199 | 92.9898 | 13.4802 | 77.7487 | 4921875.1917 | 0 | 3824031.7228 | 0 | 0 | 0 | 1959275.9796 | 4175021.3287 | 10862549.0826 | 7413912.9519 | 33156666.2573 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 60439517.243 | 116898119.3955 | 74989.4209 | 8.4712 | 7134.6775 | 13799.4216 | 145.4501 | 281.3199
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.883 | 17.7902 | 2.1849 | 4 | 6954.8854 | 13414.9776 | 141.7847 | 273.4825 | 92.8047 | 13.4039 | 81.8931 | 4988324.1898 | 0 | 3895453.878 | 0 | 0 | 0 | 1932270.106 | 4218258.7878 | 10975044.082 | 7490693.1006 | 33500044.1441 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 60782895.1298 | 117241497.2824 | 100000 | 8.7396 | 6954.8854 | 13414.9776 | 141.7847 | 273.4825
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0017 | 18.1208 | 2.237 | 4 | 6820.9784 | 13130.7081 | 139.0549 | 267.6872 | 92.6583 | 13.3444 | 91.617 | 5038178.1207 | 0 | 3949860.5031 | 0 | 0 | 0 | 1908819.7862 | 4249774.7799 | 11057042.2287 | 7546658.5206 | 33750333.9392 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61033184.9248 | 117491787.0774 | 133352.1432 | 8.9479 | 6820.9784 | 13130.7081 | 139.0549 | 267.6872
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6265 | 18.3748 | 2.2771 | 4 | 6721.0902 | 12919.5253 | 137.0185 | 263.382 | 92.5431 | 13.298 | 94.4407 | 5075864.3899 | 0 | 3991483.6149 | 0 | 0 | 0 | 1889574.4607 | 4273199.7615 | 11117989.2257 | 7588256.0984 | 33936367.5511 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61219218.5367 | 117677820.6893 | 177827.941 | 9.1085 | 6721.0902 | 12919.5253 | 137.0185 | 263.382
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8593 | 18.5678 | 2.3078 | 4 | 6646.4861 | 12762.4218 | 135.4976 | 260.1792 | 92.4541 | 13.2623 | 79.6167 | 5104144.691 | 0 | 4023011.4432 | 0 | 0 | 0 | 1874031.8258 | 4290463.3044 | 11162905.423 | 7618912.326 | 34073469.0133 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61356319.9989 | 117814922.1515 | 237137.3706 | 9.2314 | 6646.4861 | 12762.4218 | 135.4976 | 260.1792
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7802 | 18.7125 | 2.3311 | 4 | 6590.7121 | 12645.5648 | 134.3606 | 257.7969 | 92.3866 | 13.2354 | 85.3376 | 5125091.1544 | 0 | 4046531.4672 | 0 | 0 | 0 | 1861501.6712 | 4302918.4742 | 11195311.2199 | 7641029.9482 | 34172383.9351 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61455234.9207 | 117913837.0733 | 316227.766 | 9.3245 | 6590.7121 | 12645.5648 | 134.3606 | 257.7969
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.4964 | 18.8247 | 2.3489 | 4 | 6548.9846 | 12557.9038 | 133.5099 | 256.0099 | 92.3336 | 13.2144 | 97.6578 | 5141278.1736 | 0 | 4064807.219 | 0 | 0 | 0 | 1852130.1621 | 4312704.0663 | 11220771.3233 | 7658406.992 | 34250097.9363 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61532948.9219 | 117991551.0745 | 421696.5034 | 9.3958 | 6548.9846 | 12557.9038 | 133.5099 | 256.0099
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0176 | 18.9067 | 2.3623 | 4 | 6517.7482 | 12492.7691 | 132.8731 | 254.682 | 92.2947 | 13.199 | 84.9034 | 5152998.9256 | 0 | 4078096.7439 | 0 | 0 | 0 | 1844535.2259 | 4319496.0492 | 11238442.6695 | 7670468.0488 | 34304037.6628 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61586888.6484 | 118045490.801 | 562341.3252 | 9.4491 | 6517.7482 | 12492.7691 | 132.8731 | 254.682
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4197 | 18.9699 | 2.3724 | 4 | 6494.3551 | 12443.8552 | 132.3962 | 253.6848 | 92.2645 | 13.1871 | 81.8151 | 5162008.2493 | 0 | 4088344.0191 | 0 | 0 | 0 | 1838900.2796 | 4324808.4937 | 11252264.5605 | 7679901.7734 | 34346227.3756 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61629078.3613 | 118087680.5138 | 749894.2093 | 9.4896 | 6494.3551 | 12443.8552 | 132.3962 | 253.6848
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.7144 | 19.0163 | 2.38 | 4 | 6476.8302 | 12407.3997 | 132.0389 | 252.9416 | 92.2423 | 13.1783 | 93.0521 | 5168591.6742 | 0 | 4095850.2946 | 0 | 0 | 0 | 1834460.1808 | 4328571.8383 | 11262056.0111 | 7686584.6397 | 34376114.6387 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61658965.6243 | 118117567.7769 | 1000000 | 9.5199 | 6476.8302 | 12407.3997 | 132.0389 | 252.9416
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.9339 | 19.051 | 2.3857 | 4 | 6463.6982 | 12380.1401 | 131.7712 | 252.3859 | 92.2257 | 13.1717 | 78.1372 | 5173484.964 | 0 | 4101439.517 | 0 | 0 | 0 | 1831054.5199 | 4331331.8103 | 11269236.8922 | 7691485.7386 | 34398033.4419 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61680884.4275 | 118139486.5801 | 1333521.4322 | 9.5427 | 6463.6982 | 12380.1401 | 131.7712 | 252.3859
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0971 | 19.0768 | 2.3899 | 4 | 6453.8562 | 12359.7534 | 131.5706 | 251.9703 | 92.2133 | 13.1669 | 88.2378 | 5177116.9998 | 0 | 4105593.6785 | 0 | 0 | 0 | 1828447.0434 | 4333351.5114 | 11274491.7401 | 7695072.2803 | 34414073.2534 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61696924.2391 | 118155526.3917 | 1778279.41 | 9.5597 | 6453.8562 | 12359.7534 | 131.5706 | 251.9703
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.2286 | 19.0974 | 2.3932 | 4 | 6446.4787 | 12344.3012 | 131.4202 | 251.6553 | 92.2033 | 13.1629 | 89.0541 | 5180041.2806 | 0 | 4108941.4854 | 0 | 0 | 0 | 1826646.0037 | 4335095.2202 | 11279028.5125 | 7698168.7207 | 34427921.223 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61710772.2086 | 118169374.3612 | 2371373.7057 | 9.5728 | 6446.4787 | 12344.3012 | 131.4202 | 251.6553
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3212 | 19.112 | 2.3956 | 4 | 6440.9482 | 12332.8405 | 131.3074 | 251.4216 | 92.1963 | 13.1602 | 84.0485 | 5182098.4132 | 0 | 4111298.5779 | 0 | 0 | 0 | 1825175.2284 | 4336243.1656 | 11282015.2311 | 7700207.2175 | 34437037.8337 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61719888.8194 | 118178490.972 | 3162277.6602 | 9.5824 | 6440.9482 | 12332.8405 | 131.3074 | 251.4216
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3944 | 19.1235 | 2.3974 | 4 | 6436.8019 | 12324.1783 | 131.2229 | 251.245 | 92.1907 | 13.158 | 83.734 | 5183722.6779 | 0 | 4113160.6441 | 0 | 0 | 0 | 1824136.1456 | 4337197.5924 | 11284498.4538 | 7701902.068 | 34444617.5817 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61727468.5674 | 118186070.72 | 4216965.0343 | 9.5898 | 6436.8019 | 12324.1783 | 131.2229 | 251.245
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4527 | 19.1326 | 2.3988 | 4 | 6433.6932 | 12317.6173 | 131.1595 | 251.1113 | 92.1863 | 13.1562 | 88.7725 | 5185017.487 | 0 | 4114645.5968 | 0 | 0 | 0 | 1823418.4756 | 4338001.8081 | 11286590.8583 | 7703330.177 | 34451004.4027 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61733855.3884 | 118192457.541 | 5623413.2519 | 9.5954 | 6433.6932 | 12317.6173 | 131.1595 | 251.1113
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4844 | 19.1377 | 2.3998 | 4 | 6431.3623 | 12312.9352 | 131.112 | 251.0158 | 92.1838 | 13.1553 | 96.2289 | 5185719.2668 | 0 | 4115451.036 | 0 | 0 | 0 | 1822655.2408 | 4338291.962 | 11287345.7791 | 7703845.426 | 34453308.7108 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61736159.6965 | 118194761.8491 | 7498942.0933 | 9.5992 | 6431.3623 | 12312.9352 | 131.112 | 251.0158
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5233 | 19.1437 | 2.4006 | 4 | 6429.6145 | 12309.1289 | 131.0764 | 250.9382 | 92.1809 | 13.1541 | 95.0193 | 5186582.2425 | 0 | 4116441.121 | 0 | 0 | 0 | 1822362.0357 | 4338900.3057 | 11288928.5645 | 7704925.7096 | 34458139.9789 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61740990.9645 | 118199593.1171 | 10000000 | 9.6026 | 6429.6145 | 12309.1289 | 131.0764 | 250.9382
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.5024 | [19 empty] | 100 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.968 | [19 empty] | 133.3521 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.030783 | 0.0024026 | 4 | 3018692.8282 | 9024523.7808 | 61540.1364 | 183977.1238 | 57.8734 | 12.0425 | 25.639 | 152674.0067 | 0 | 54578.5382 | 0 | 0 | 0 | 152498.8151 | 140303.0304 | 365039.705 | 249147.0995 | 1114241.195 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 29010534.8637 | 86728354.5128 | 177.8279 | 0.0096103 | 3018692.8282 | 9024523.7808 | 61540.1364 | 183977.1238
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.019292 | 0.0051599 | 4 | 1403246.3786 | 4199711.0969 | 28607.0755 | 85616.7912 | 57.8734 | 12.0425 | 24.3252 | 152674.0091 | 0 | 54578.5372 | 0 | 0 | 0 | 136956.7053 | 134241.6081 | 349269.1276 | 238383.3564 | 1066103.3437 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 28962397.0124 | 86680216.6615 | 237.1374 | 0.02064 | 1403246.3786 | 4199711.0969 | 28607.0755 | 85616.7912
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.783 | 0.1611 | 0.017652 | 4 | 431599.3118 | 1249052.787 | 8798.7358 | 25463.6305 | 75.7209 | 13.7581 | 49.1452 | 352756.5327 | 0 | 171885.6284 | 0 | 0 | 0 | 307571.4837 | 324563.3215 | 844447.1855 | 576352.5558 | 2577576.7077 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 30473870.3763 | 88191690.0254 | 316.2278 | 0.070607 | 431599.3118 | 1249052.787 | 8798.7358 | 25463.6305
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1519 | 0.32279 | 0.031618 | 4 | 247273.2655 | 703644.8278 | 5041 | 14344.7516 | 80.7773 | 14.1828 | 34.8335 | 465364.5233 | 0 | 240402.5968 | 0 | 0 | 0 | 384434.7146 | 425178.7155 | 1106227.8017 | 755023.2054 | 3376631.5573 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 31272925.226 | 88990744.8751 | 421.6965 | 0.12647 | 247273.2655 | 703644.8278 | 5041 | 14344.7516
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9003 | 0.5455 | 0.051452 | 4 | 156508.9182 | 436953.712 | 3190.646 | 8907.8924 | 84.7884 | 14.4998 | 61.7919 | 598171.5985 | 0 | 323158.1178 | 0 | 0 | 0 | 471683.3414 | 543275.0925 | 1413490.3497 | 964736.208 | 4314514.708 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 32210808.3766 | 89928628.0257 | 562.3413 | 0.20581 | 156508.9182 | 436953.712 | 3190.646 | 8907.8924
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1271 | 0.84253 | 0.078811 | 4 | 105657.065 | 288746.038 | 2153.9622 | 5886.4785 | 87.9525 | 14.7365 | 49.7111 | 754075.7806 | 0 | 422709.2901 | 0 | 0 | 0 | 570418.0161 | 681409.2038 | 1772886.9722 | 1210031.7877 | 5411531.0505 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 33307824.7191 | 91025644.3682 | 749.8942 | 0.31524 | 105657.065 | 288746.038 | 2153.9622 | 5886.4785
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9823 | 1.2339 | 0.11587 | 4 | 74658.7991 | 199189.9158 | 1522.0206 | 4060.7559 | 90.4545 | 14.9137 | 62.6012 | 938268.0865 | 0 | 543279.2298 | 0 | 0 | 0 | 683806.2408 | 844487.8873 | 2197184.2544 | 1499623.4013 | 6706649.1002 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 34602942.7688 | 92320762.4179 | 1000 | 0.46348 | 74658.7991 | 199189.9158 | 1522.0206 | 4060.7559
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.6117 | 1.7405 | 0.16534 | 4 | 54612.8122 | 141883.6615 | 1113.356 | 2892.4904 | 92.4067 | 15.0429 | 61.1976 | 1154185.7325 | 0 | 688202.9822 | 0 | 0 | 0 | 812436.7813 | 1035381.9435 | 2693851.4308 | 1838608.9547 | 8222667.825 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 36118961.4937 | 93836781.1428 | 1333.5214 | 0.66136 | 54612.8122 | 141883.6615 | 1113.356 | 2892.4904
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2138 | 2.3905 | 0.23062 | 4 | 41077.0859 | 103645.5333 | 837.412 | 2112.9544 | 93.917 | 15.1318 | 47.0757 | 1406944.3968 | 0 | 862224.9217 | 0 | 0 | 0 | 958298.172 | 1258712.3213 | 3274911.2626 | 2235194.2294 | 9996285.3038 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 37892578.9724 | 95610398.6215 | 1778.2794 | 0.92247 | 41077.0859 | 103645.5333 | 837.412 | 2112.9544
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9944 | 3.2139 | 0.31562 | 4 | 31643.9389 | 77361.0429 | 645.1045 | 1577.1095 | 95.0642 | 15.1851 | 51.4784 | 1700459.5625 | 0 | 1069576.5651 | 0 | 0 | 0 | 1121851.3598 | 1517836.1201 | 3949098.2335 | 2695340.6902 | 12054162.5312 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 39950456.1998 | 97668275.8489 | 2371.3737 | 1.2625 | 31643.9389 | 77361.0429 | 645.1045 | 1577.1095
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.0855 | 4.2323 | 0.42431 | 4 | 24910.5957 | 58917.5437 | 507.8362 | 1201.1138 | 95.8989 | 15.2023 | 48.8531 | 2033835.5231 | 0 | 1311471.6069 | 0 | 0 | 0 | 1298441.9417 | 1811062.138 | 4712012.1831 | 3216045.1371 | 14382868.5298 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 42279162.1985 | 99996981.8476 | 3162.2777 | 1.6972 | 24910.5957 | 58917.5437 | 507.8362 | 1201.1138
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.5897 | 5.4628 | 0.56009 | 4 | 20022.2657 | 45785.2293 | 408.181 | 933.3938 | 96.4671 | 15.1811 | 63.1944 | 2404634.053 | 0 | 1588226.0295 | 0 | 0 | 0 | 1483090.0241 | 2135620.5416 | 5556446.5732 | 3792388.9598 | 16960406.1812 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 44856699.8499 | 102574519.499 | 4216.965 | 2.2403 | 20022.2657 | 45785.2293 | 408.181 | 933.3938
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.4265 | 6.8978 | 0.72417 | 4 | 16434.5769 | 36360.2049 | 335.0411 | 741.252 | 96.7973 | 15.1178 | 55.4471 | 2803046.7008 | 0 | 1894815.0022 | 0 | 0 | 0 | 1665559.4043 | 2481734.2319 | 6456963.3976 | 4407010.1962 | 19709128.933 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 47605422.6017 | 105323242.2508 | 5623.4133 | 2.8967 | 16434.5769 | 36360.2049 | 335.0411 | 741.252
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2009 | 8.4846 | 0.91334 | 4 | 13787.6867 | 29586.3085 | 281.0806 | 603.1569 | 96.9101 | 15.0109 | 62.4189 | 3209114.8376 | 0 | 2217938.1459 | 0 | 0 | 0 | 1829338.9131 | 2829992.8397 | 7363060.8575 | 5025440.331 | 22474885.9248 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 50371179.5934 | 108088999.2425 | 7498.9421 | 3.6533 | 13787.6867 | 29586.3085 | 281.0806 | 603.1569
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.3265 | 10.14 | 1.1194 | 4 | 11833.5315 | 24723.4967 | 241.2425 | 504.0219 | 96.8331 | 14.8643 | 68.5208 | 3600101.9329 | 0 | 2540666.5635 | 0 | 0 | 0 | 1960311.1616 | 3159421.0666 | 8220165.529 | 5610431.881 | 25091098.1346 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 52987391.8033 | 110705211.4524 | 10000 | 4.4777 | 11833.5315 | 24723.4967 | 241.2425 | 504.0219
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0787 | 11.7572 | 1.3301 | 4 | 10393.0643 | 21241.4983 | 211.8767 | 433.0367 | 96.6086 | 14.6898 | 69.4288 | 3953493.0902 | 0 | 2844000.0784 | 0 | 0 | 0 | 2048661.645 | 3450000.3773 | 8976193.2894 | 6126436.3623 | 27398784.8426 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 55295078.5113 | 113012898.1604 | 13335.2143 | 5.3204 | 10393.0643 | 21241.4983 | 211.8767 | 433.0367
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8935 | 13.2486 | 1.5327 | 4 | 9332.8811 | 18747.4973 | 190.2634 | 382.1931 | 96.2906 | 14.5034 | 73.5759 | 4256490.7299 | 0 | 3114726.5386 | 0 | 0 | 0 | 2095374.6644 | 3691970.8538 | 9605750.8343 | 6556122.3228 | 29320435.9437 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 57216729.6124 | 114934549.2615 | 17782.7941 | 6.1307 | 9332.8811 | 18747.4973 | 190.2634 | 382.1931
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.4003 | 14.5538 | 1.7169 | 4 | 8552.8084 | 16957.2059 | 174.3606 | 345.6956 | 95.9342 | 14.3213 | 72.8406 | 4504599.7094 | 0 | 3345277.1631 | 0 | 0 | 0 | 2107573.4683 | 3883405.6329 | 10103824.8609 | 6896068.0804 | 30840748.9151 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 58737042.5837 | 116454862.2328 | 23713.7371 | 6.8676 | 8552.8084 | 16957.2059 | 174.3606 | 345.6956
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.487 | 15.6506 | 1.8769 | 4 | 7978.2047 | 15666.0728 | 162.6465 | 319.3741 | 95.5824 | 14.1553 | 91.6475 | 4701228.7102 | 0 | 3534777.797 | 0 | 0 | 0 | 2096138.0626 | 4029536.3822 | 10484027.095 | 7155563.9176 | 32001271.9646 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 59897565.6333 | 117615385.2824 | 31622.7766 | 7.5076 | 7978.2047 | 15666.0728 | 162.6465 | 319.3741
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.2313 | 16.5462 | 2.011 | 4 | 7554.0782 | 14729.2207 | 154.0001 | 300.2751 | 95.2615 | 14.0112 | 84.9863 | 4853969.2617 | 0 | 3686841.1097 | 0 | 0 | 0 | 2071732.3647 | 4138891.6671 | 10768547.1143 | 7349754.677 | 32869736.1945 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 60766029.8631 | 118483849.5122 | 42169.6503 | 8.0441 | 7554.0782 | 14729.2207 | 154.0001 | 300.2751
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7861 | 17.2605 | 2.1203 | 4 | 7240.2462 | 14045.5346 | 147.6022 | 286.3372 | 94.9845 | 13.891 | 80.9305 | 4970866.2991 | 0 | 3806512.2937 | 0 | 0 | 0 | 2042058.9544 | 4219580.6434 | 10978483.2791 | 7493040.4233 | 33510541.893 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 61406835.5616 | 119124655.2107 | 56234.1325 | 8.4813 | 7240.2462 | 14045.5346 | 147.6022 | 286.3372
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3406 | 17.8208 | 2.2075 | 4 | 7007.451 | 13543.9527 | 142.8564 | 276.1118 | 94.7546 | 13.7935 | 85.0746 | 5059501.4989 | 0 | 3899383.5834 | 0 | 0 | 0 | 2012139.4524 | 4278699.5685 | 11132298.5954 | 7598022.5372 | 33980045.2358 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 61876338.9044 | 119594158.5535 | 74989.4209 | 8.8301 | 7007.451 | 13543.9527 | 142.8564 | 276.1118
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.066 | 18.2524 | 2.2758 | 4 | 6834.381 | 13174.6599 | 139.3281 | 268.5833 | 94.5701 | 13.7166 | 88.5988 | 5125920.2471 | 0 | 3970299.2339 | 0 | 0 | 0 | 1984408.1501 | 4321444.7761 | 11243512.8573 | 7673928.5562 | 34319513.8208 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62215807.4894 | 119933627.1385 | 100000 | 9.1034 | 6834.381 | 13174.6599 | 139.3281 | 268.5833
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.166 | 18.5858 | 2.329 | 4 | 6705.4691 | 12901.1216 | 136.7001 | 263.0068 | 94.423 | 13.656 | 89.2977 | 5176184.1274 | 0 | 4024776.3625 | 0 | 0 | 0 | 1960832.6896 | 4353099.34 | 11325871.5392 | 7730140.0489 | 34570904.1077 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62467197.7763 | 120185017.4254 | 133352.1432 | 9.3159 | 6705.4691 | 12901.1216 | 136.7001 | 263.0068
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.7667 | 18.8405 | 2.3698 | 4 | 6609.3001 | 12698.0694 | 134.7395 | 258.8673 | 94.3081 | 13.6091 | 79.3312 | 5213960.3215 | 0 | 4066205.8059 | 0 | 0 | 0 | 1941336.9953 | 4376386.2179 | 11386459.2187 | 7771492.3851 | 34755840.9444 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62652134.6131 | 120369954.2622 | 177827.941 | 9.4794 | 6609.3001 | 12698.0694 | 134.7395 | 258.8673
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9823 | 19.0342 | 2.4011 | 4 | 6537.4697 | 12546.9641 | 133.2752 | 255.7868 | 94.2192 | 13.573 | 93.8256 | 5242338.0951 | 0 | 4097615.2648 | 0 | 0 | 0 | 1925651.0115 | 4393585.7048 | 11431208.7556 | 7802034.8636 | 34892433.6954 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62788727.364 | 120506547.0132 | 237137.3706 | 9.6044 | 6537.4697 | 12546.9641 | 133.2752 | 255.7868
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.901 | 19.1809 | 2.4249 | 4 | 6483.7671 | 12434.3383 | 132.1804 | 253.4908 | 94.1511 | 13.5455 | 84.9659 | 5263607.0451 | 0 | 4121323.7825 | 0 | 0 | 0 | 1913234.4394 | 4406284.4541 | 11464248.2964 | 7824585.029 | 34993283.0464 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62889576.7151 | 120607396.3642 | 316227.766 | 9.6995 | 6483.7671 | 12434.3383 | 132.1804 | 253.4908
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5977 | 19.2921 | 2.4429 | 4 | 6443.5879 | 12350.1924 | 131.3613 | 251.7754 | 94.0988 | 13.5245 | 89.0733 | 5279636.2248 | 0 | 4139288.6978 | 0 | 0 | 0 | 1903618.8304 | 4415792.0637 | 11488985.1462 | 7841468.4373 | 35068789.4003 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 62965083.0689 | 120682902.7181 | 421696.5034 | 9.7717 | 6443.5879 | 12350.1924 | 131.3613 | 251.7754
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1165 | 19.3752 | 2.4565 | 4 | 6413.5097 | 12287.4287 | 130.7481 | 250.4959 | 94.0596 | 13.5088 | 89.6002 | 5291513.0676 | 0 | 4152655.0341 | 0 | 0 | 0 | 1896075.0247 | 4422694.8193 | 11506944.7004 | 7853726.2021 | 35123608.8483 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63019902.517 | 120737722.1661 | 562341.3252 | 9.8261 | 6413.5097 | 12287.4287 | 130.7481 | 250.4959
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5038 | 19.4372 | 2.4668 | 4 | 6390.9836 | 12240.5434 | 130.2888 | 249.54 | 94.0302 | 13.497 | 96.329 | 5300347.1249 | 0 | 4162627.9258 | 0 | 0 | 0 | 1890236.2854 | 4427752.4211 | 11520103.5427 | 7862707.3824 | 35163774.6823 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63060068.351 | 120777888.0001 | 749894.2093 | 9.867 | 6390.9836 | 12240.5434 | 130.2888 | 249.54
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8035 | 19.4851 | 2.4745 | 4 | 6374.108 | 12205.287 | 129.9448 | 248.8213 | 94.0073 | 13.4879 | 68.2325 | 5307165.1947 | 0 | 4170342.8699 | 0 | 0 | 0 | 1885950.5429 | 4431748.8569 | 11530501.449 | 7869804.1671 | 35195513.0805 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63091806.7491 | 120809626.3982 | 1000000 | 9.8981 | 6374.108 | 12205.287 | 129.9448 | 248.8213
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.023 | 19.5203 | 2.4803 | 4 | 6361.4624 | 12178.997 | 129.687 | 248.2853 | 93.9905 | 13.4812 | 82.0534 | 5312147.5802 | 0 | 4175990.946 | 0 | 0 | 0 | 1882588.6286 | 4434583.5904 | 11537876.844 | 7874838.0257 | 35218025.6148 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63114319.2834 | 120832138.9325 | 1333521.4322 | 9.9214 | 6361.4624 | 12178.997 | 129.687 | 248.2853
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1862 | 19.5465 | 2.4847 | 4 | 6351.9848 | 12159.3357 | 129.4938 | 247.8845 | 93.978 | 13.4762 | 80.6072 | 5315845.7787 | 0 | 4180188.8681 | 0 | 0 | 0 | 1880013.7399 | 4436658.8708 | 11543276.2979 | 7878523.2639 | 35234506.8193 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63130800.488 | 120848620.1371 | 1778279.41 | 9.9388 | 6351.9848 | 12159.3357 | 129.4938 | 247.8845
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.3151 | 19.5671 | 2.488 | 4 | 6344.8805 | 12144.4808 | 129.349 | 247.5817 | 93.9681 | 13.4722 | 82.3997 | 5318764.3183 | 0 | 4183504.9295 | 0 | 0 | 0 | 1878191.406 | 4438379.655 | 11547753.4254 | 7881578.9955 | 35248172.7297 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63144466.3984 | 120862286.0475 | 2371373.7057 | 9.952 | 6344.8805 | 12144.4808 | 129.349 | 247.5817
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4077 | 19.582 | 2.4905 | 4 | 6339.5547 | 12133.4274 | 129.2404 | 247.3563 | 93.9609 | 13.4694 | 79.2165 | 5320858.9925 | 0 | 4185886.873 | 0 | 0 | 0 | 1876739.5381 | 4439559.3074 | 11550822.6391 | 7883673.7969 | 35257541.1471 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63153834.8157 | 120871654.4648 | 3162277.6602 | 9.9619 | 6339.5547 | 12133.4274 | 129.2404 | 247.3563
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.466 | 19.5916 | 2.4922 | 4 | 6335.5619 | 12125.3552 | 129.159 | 247.1918 | 93.9564 | 13.4676 | 86.1624 | 5322177.1336 | 0 | 4187386.9407 | 0 | 0 | 0 | 1875436.5526 | 4440150.2445 | 11552360.1361 | 7884723.1702 | 35262234.1777 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63158527.8463 | 120876347.4954 | 4216965.0343 | 9.9689 | 6335.5619 | 12125.3552 | 129.159 | 247.1918
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5346 | 19.6022 | 2.4937 | 4 | 6332.5682 | 12118.8312 | 129.098 | 247.0588 | 93.9512 | 13.4655 | 82.0347 | 5323726.4806 | 0 | 4189149.9371 | 0 | 0 | 0 | 1874924.015 | 4441242.1688 | 11555201.0991 | 7886662.1858 | 35270905.8863 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63167199.555 | 120885019.2041 | 5623413.2519 | 9.975 | 6332.5682 | 12118.8312 | 129.098 | 247.0588
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5586 | 19.6064 | 2.4947 | 4 | 6330.3236 | 12114.4616 | 129.0522 | 246.9697 | 93.9493 | 13.4647 | 83.7482 | 5324269.3362 | 0 | 4189768.5331 | 0 | 0 | 0 | 1874023.3262 | 4441343.8662 | 11555465.695 | 7886842.7779 | 35271713.5344 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63168007.2031 | 120885826.8522 | 7498942.0933 | 9.9786 | 6330.3236 | 12114.4616 | 129.0522 | 246.9697
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5922 | 19.6117 | 2.4955 | 4 | 6328.6405 | 12110.889 | 129.0179 | 246.8969 | 93.9467 | 13.4637 | 93.8117 | 5325028.4875 | 0 | 4190632.9453 | 0 | 0 | 0 | 1873640.1295 | 4441827.6093 | 11556724.2953 | 7887701.7985 | 35275555.2654 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63171848.934 | 120889668.5831 | 10000000 | 9.9819 | 6328.6405 | 12110.889 | 129.0179 | 246.8969
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6567 | [19 empty] | 100 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7251 | [19 empty] | 133.3521 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.032141 | 0.0025355 | 4 | 2922408.4779 | 8738783.238 | 59577.2497 | 178151.9164 | 58.2009 | 12.2962 | 25.2144 | 154489.3156 | 0 | 54376.0416 | 0 | 0 | 0 | 154049.9975 | 141536.9883 | 368250.2104 | 251338.3354 | 1124040.8888 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 29639637.3313 | 88630445.6905 | 177.8279 | 0.010142 | 2922408.4779 | 8738783.238 | 59577.2497 | 178151.9164
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7741 | 0.053313 | 0.0088768 | 4 | 858435.1511 | 2519814.1876 | 17500.3617 | 51369.8205 | 70.4934 | 13.5183 | 45.3901 | 267192.8118 | 0 | 119135.9641 | 0 | 0 | 0 | 248096.3953 | 247425.8167 | 643751.2212 | 439373.4362 | 1964975.6452 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 30480572.0878 | 89471380.4469 | 237.1374 | 0.035507 | 858435.1511 | 2519814.1876 | 17500.3617 | 51369.8205
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 0.17156 | 0.018862 | 4 | 413573.9111 | 1195447.8801 | 8431.2636 | 24370.822 | 77.1352 | 14.1135 | 52.0992 | 368105.3867 | 0 | 178755.0206 | 0 | 0 | 0 | 320914.2007 | 338432.0971 | 880530.8947 | 600980.4288 | 2687718.0287 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 31203314.4712 | 90194122.8303 | 316.2278 | 0.075448 | 413573.9111 | 1195447.8801 | 8431.2636 | 24370.822
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2956 | 0.33957 | 0.033704 | 4 | 237545.0638 | 675106.5151 | 4842.6774 | 13762.9595 | 82.2549 | 14.5403 | 43.4163 | 484325.9115 | 0 | 249012.5728 | 0 | 0 | 0 | 399782.5493 | 441917.2031 | 1149777.9127 | 784747.051 | 3509563.2004 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 32025159.643 | 91015968.0021 | 421.6965 | 0.13482 | 237545.0638 | 675106.5151 | 4842.6774 | 13762.9595
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1003 | 0.57304 | 0.054782 | 4 | 150614.9763 | 419820.8769 | 3070.49 | 8558.6164 | 86.3709 | 14.8628 | 50.2606 | 623087.3829 | 0 | 334910.1201 | 0 | 0 | 0 | 491191.6371 | 565183.7646 | 1470492.2203 | 1003641.156 | 4488506.2809 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 33004102.7234 | 91994911.0826 | 562.3413 | 0.21913 | 150614.9763 | 419820.8769 | 3070.49 | 8558.6164
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3829 | 0.88257 | 0.083824 | 4 | 101818.416 | 277754.5605 | 2075.7061 | 5662.4024 | 89.5944 | 15.1018 | 58.9677 | 784848.9692 | 0 | 437519.6344 | 0 | 0 | 0 | 593363.3213 | 708135.4507 | 1842423.1842 | 1257491.6812 | 5623782.241 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 34139378.6835 | 93130187.0427 | 749.8942 | 0.3353 | 101818.416 | 277754.5605 | 2075.7061 | 5662.4024
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 1.2908 | 0.12315 | 4 | 72031.5344 | 191786.9283 | 1468.4603 | 3909.8359 | 92.1493 | 15.2808 | 50.3019 | 976278.7889 | 0 | 561991.7877 | 0 | 0 | 0 | 711050.2816 | 877235.1347 | 2282385.8748 | 1557775.2579 | 6966717.1257 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 35482313.5682 | 94473121.9274 | 1000 | 0.49259 | 72031.5344 | 191786.9283 | 1468.4603 | 3909.8359
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0527 | 1.8208 | 0.17565 | 4 | 52748.482 | 136709.2577 | 1075.3492 | 2787.0031 | 94.1488 | 15.4114 | 61.9522 | 1201464.0778 | 0 | 712131.9809 | 0 | 0 | 0 | 845450.3751 | 1076028.1092 | 2799604.4164 | 1910787.5403 | 8545466.4997 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 37061062.9422 | 96051871.3013 | 1333.5214 | 0.7026 | 52748.482 | 136709.2577 | 1075.3492 | 2787.0031
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.7667 | 2.4974 | 0.24482 | 4 | 39719.0903 | 99959.1117 | 809.7274 | 2037.8017 | 95.6875 | 15.5007 | 46.1583 | 1463610.7195 | 0 | 891401.0997 | 0 | 0 | 0 | 996289.0923 | 1307007.3555 | 3400565.0348 | 2320955.5109 | 10379828.8126 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 38895425.2551 | 97886233.6143 | 1778.2794 | 0.97926 | 39719.0903 | 99959.1117 | 809.7274 | 2037.8017
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6787 | 3.3534 | 0.33481 | 4 | 30629.3591 | 74677.3915 | 624.4209 | 1522.3996 | 96.854 | 15.5524 | 47.2985 | 1767590.3824 | 0 | 1104745.6058 | 0 | 0 | 0 | 1164922.0146 | 1574530.6211 | 4096605.6955 | 2796017.564 | 12504411.8834 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 41020008.3259 | 100010816.685 | 2371.3737 | 1.3392 | 30629.3591 | 74677.3915 | 624.4209 | 1522.3996
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.9332 | 4.4122 | 0.44974 | 4 | 24139.5579 | 56931.1538 | 492.1175 | 1160.6186 | 97.7037 | 15.5673 | 60.9989 | 2113028.9614 | 0 | 1353750.2057 | 0 | 0 | 0 | 1347334.6171 | 1877504.3758 | 4884881.2568 | 3334031.832 | 14910531.2489 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 43426127.6914 | 102416936.0506 | 3162.2777 | 1.799 | 24139.5579 | 56931.1538 | 492.1175 | 1160.6186
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.6297 | 5.691 | 0.59311 | 4 | 19426.6797 | 44291.6304 | 396.0391 | 902.9448 | 98.2805 | 15.5423 | 57.5554 | 2497093.9037 | 0 | 1638579.774 | 0 | 0 | 0 | 1538125.7261 | 2212781.7675 | 5757204.255 | 3929410.2028 | 17573195.629 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 46088792.0716 | 105079600.4307 | 4216.965 | 2.3724 | 19426.6797 | 44291.6304 | 396.0391 | 902.9448
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6102 | 7.1715 | 0.76565 | 4 | 15967.5835 | 35229.3749 | 325.5208 | 718.1985 | 98.6109 | 15.4737 | 56.1115 | 2906588.8842 | 0 | 1951755.0818 | 0 | 0 | 0 | 1723755.4761 | 2567018.7824 | 6678856.304 | 4558456.6642 | 20386431.1928 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 48902027.6353 | 107892835.9945 | 5623.4133 | 3.0626 | 15967.5835 | 35229.3749 | 325.5208 | 718.1985
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.5387 | 8.808 | 0.96403 | 4 | 13416.0809 | 28714.099 | 273.505 | 585.3757 | 98.7196 | 15.3598 | 66.5644 | 3323884.5135 | 0 | 2281853.1221 | 0 | 0 | 0 | 1890664.7472 | 2923596.9292 | 7606599.4977 | 5191660.4572 | 23218259.2668 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 51733855.7094 | 110724664.0685 | 7498.9421 | 3.8561 | 13416.0809 | 28714.099 | 273.505 | 585.3757
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.7561 | 10.5056 | 1.1791 | 4 | 11533.0294 | 24040.6526 | 235.1164 | 490.1012 | 98.6345 | 15.2057 | 69.4436 | 3723314.0503 | 0 | 2609710.1348 | 0 | 0 | 0 | 2022329.5577 | 3258587.9597 | 8478177.4429 | 5786530.3139 | 25878649.4593 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 54394245.9019 | 113385054.261 | 10000 | 4.7164 | 11533.0294 | 24040.6526 | 235.1164 | 490.1012
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5332 | 12.1546 | 1.3978 | 4 | 10145.4721 | 20696.1564 | 206.8292 | 421.9191 | 98.401 | 15.024 | 73.0493 | 4082294.2541 | 0 | 2916188.2849 | 0 | 0 | 0 | 2109456.3885 | 3552096.1817 | 9241825.6298 | 6307735.8928 | 28209596.6319 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 56725193.0744 | 115716001.4336 | 13335.2143 | 5.5912 | 10145.4721 | 20696.1564 | 206.8292 | 421.9191
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.3286 | 13.6691 | 1.6071 | 4 | 9124.4778 | 18300.8366 | 186.0148 | 373.0873 | 98.0753 | 14.8315 | 81.3709 | 4388879.9019 | 0 | 3188670.9386 | 0 | 0 | 0 | 2154197.3058 | 3795381.7771 | 9874804.8441 | 6739757.213 | 30141691.9805 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 58657288.4231 | 117648096.7822 | 17782.7941 | 6.4286 | 9124.4778 | 18300.8366 | 186.0148 | 373.0873
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8009 | 14.9917 | 1.7969 | 4 | 8373.3148 | 16580.7062 | 170.7013 | 338.0201 | 97.7128 | 14.6442 | 74.1147 | 4639517.1549 | 0 | 3420328.3642 | 0 | 0 | 0 | 2164628.9236 | 3987545.0326 | 10374774.2169 | 7080996.5834 | 31667790.2756 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 60183386.7181 | 119174195.0772 | 23713.7371 | 7.1875 | 8373.3148 | 16580.7062 | 170.7013 | 338.0201
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.8534 | 16.1021 | 1.9613 | 4 | 7819.9991 | 15339.4653 | 159.4213 | 312.7157 | 97.3562 | 14.474 | 75.6144 | 4838076.1286 | 0 | 3610648.9489 | 0 | 0 | 0 | 2151929.6435 | 4134255.3412 | 10756484.3454 | 7341521.5894 | 32832915.9969 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 61348512.4394 | 120339320.7986 | 31622.7766 | 7.8451 | 7819.9991 | 15339.4653 | 159.4213 | 312.7157
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.542 | 17.0045 | 2.0986 | 4 | 7411.5528 | 14439.0216 | 151.0945 | 294.359 | 97.0331 | 14.3271 | 75.9099 | 4991629.9147 | 0 | 3762662.6779 | 0 | 0 | 0 | 2126100.1158 | 4243353.1563 | 11040334.4812 | 7535255.1396 | 33699335.4856 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 62214931.9281 | 121205740.2873 | 42169.6503 | 8.3943 | 7411.5528 | 14439.0216 | 151.0945 | 294.359
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.036 | 17.722 | 2.2102 | 4 | 7109.2907 | 13781.9238 | 144.9325 | 280.9632 | 96.7556 | 14.2052 | 88.3006 | 5108778.4952 | 0 | 3881881.9348 | 0 | 0 | 0 | 2095152.8403 | 4323467.1754 | 11248774.7254 | 7677519.8893 | 34335575.0604 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 62851171.5029 | 121841979.8621 | 56234.1325 | 8.8407 | 7109.2907 | 13781.9238 | 144.9325 | 280.9632
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5586 | 18.2868 | 2.2992 | 4 | 6885.0529 | 13299.2372 | 140.3611 | 271.1229 | 96.5244 | 14.1059 | 77.965 | 5198038.6983 | 0 | 3974829.7438 | 0 | 0 | 0 | 2064751.4091 | 4382671.742 | 11402812.8631 | 7782654.0835 | 34805758.54 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 63321354.9825 | 122312163.3417 | 74989.4209 | 9.1969 | 6885.0529 | 13299.2372 | 140.3611 | 271.1229
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.2575 | 18.7216 | 2.3689 | 4 | 6718.328 | 12943.778 | 136.9622 | 263.8764 | 96.3392 | 14.0277 | 94.1258 | 5264894.0393 | 0 | 4045756.9309 | 0 | 0 | 0 | 2036692.5702 | 4425463.9807 | 11514149.4904 | 7858643.6193 | 35145600.6308 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 63661197.0734 | 122652005.4325 | 100000 | 9.4758 | 6718.328 | 12943.778 | 136.9622 | 263.8764
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3381 | 19.0576 | 2.4231 | 4 | 6594.1317 | 12680.3932 | 134.4303 | 258.507 | 96.1916 | 13.9662 | 87.02 | 5315524.5247 | 0 | 4100273.2565 | 0 | 0 | 0 | 2012947.071 | 4457210.4924 | 11596747.4015 | 7915018.3909 | 35397721.137 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 63913317.5795 | 122904125.9387 | 133352.1432 | 9.6925 | 6594.1317 | 12680.3932 | 134.4303 | 258.507
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9117 | 19.3124 | 2.4647 | 4 | 6501.4743 | 12485.0857 | 132.5413 | 254.5254 | 96.0771 | 13.9189 | 84.3967 | 5353291.5193 | 0 | 4141415.832 | 0 | 0 | 0 | 1993109.5452 | 4480248.5897 | 11656687.8049 | 7955928.9478 | 35580682.239 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64096278.6815 | 123087087.0407 | 177827.941 | 9.8587 | 6501.4743 | 12485.0857 | 132.5413 | 254.5254
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0908 | 19.5041 | 2.4963 | 4 | 6432.2629 | 12340.0318 | 131.1304 | 251.5682 | 95.9898 | 13.883 | 77.023 | 5381291.2186 | 0 | 4172193.3316 | 0 | 0 | 0 | 1976872.3764 | 4496839.2014 | 11699853.1734 | 7985390.1988 | 35712439.5003 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64228035.9428 | 123218844.302 | 237137.3706 | 9.9853 | 6432.2629 | 12340.0318 | 131.1304 | 251.5682
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0117 | 19.6533 | 2.5206 | 4 | 6380.5162 | 12231.3117 | 130.0755 | 249.3518 | 95.9206 | 13.8547 | 83.4731 | 5402983.2248 | 0 | 4196202.9046 | 0 | 0 | 0 | 1964650.5836 | 4509896.3181 | 11733825.1128 | 8008576.7455 | 35816134.8895 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64331731.332 | 123322539.6912 | 316227.766 | 10.0825 | 6380.5162 | 12231.3117 | 130.0755 | 249.3518
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.687 | 19.7633 | 2.5389 | 4 | 6341.799 | 12150.5257 | 129.2862 | 247.7049 | 95.8694 | 13.8339 | 89.5337 | 5418789.7719 | 0 | 4213792.6825 | 0 | 0 | 0 | 1954732.8679 | 4519052.9757 | 11757648.8576 | 8024836.9408 | 35888854.0965 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64404450.5391 | 123395258.8982 | 421696.5034 | 10.1555 | 6341.799 | 12150.5257 | 129.2862 | 247.7049
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1908 | 19.8455 | 2.5526 | 4 | 6312.8147 | 12090.2401 | 128.6953 | 246.4759 | 95.8309 | 13.8182 | 74.4301 | 5430526.9152 | 0 | 4226906.3643 | 0 | 0 | 0 | 1946989.919 | 4525725.0474 | 11775008.2196 | 8036685.0621 | 35941841.5276 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64457437.9702 | 123448246.3293 | 562341.3252 | 10.2106 | 6312.8147 | 12090.2401 | 128.6953 | 246.4759
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5922 | 19.9106 | 2.5632 | 4 | 6291.1074 | 12044.7201 | 128.2527 | 245.5479 | 95.8 | 13.8057 | 90.35 | 5439847.4006 | 0 | 4237351.4287 | 0 | 0 | 0 | 1941498.8807 | 4531292.1069 | 11789492.5664 | 8046570.9264 | 35986053.3098 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64501649.7523 | 123492458.1115 | 749894.2093 | 10.2528 | 6291.1074 | 12044.7201 | 128.2527 | 245.5479
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.8823 | 19.9578 | 2.5711 | 4 | 6274.8449 | 12010.8735 | 127.9212 | 244.8579 | 95.7776 | 13.7966 | 93.4583 | 5446562.2057 | 0 | 4244894.6393 | 0 | 0 | 0 | 1937083.4663 | 4535130.7214 | 11799479.8538 | 8053387.4553 | 36016538.3417 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64532134.7842 | 123522943.1434 | 1000000 | 10.2843 | 6274.8449 | 12010.8735 | 127.9212 | 244.8579
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.0844 | 19.9911 | 2.5768 | 4 | 6262.6586 | 11985.8266 | 127.6728 | 244.3473 | 95.7619 | 13.7903 | 101.0604 | 5451230.0088 | 0 | 4250147.7204 | 0 | 0 | 0 | 1933427.1997 | 4537573.9222 | 11805836.5613 | 8057726.0387 | 36035941.451 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64551537.8936 | 123542346.2527 | 1333521.4322 | 10.3074 | 6262.6586 | 11985.8266 | 127.6728 | 244.3473
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.265 | 20.0202 | 2.5814 | 4 | 6253.5252 | 11966.5222 | 127.4866 | 243.9537 | 95.7479 | 13.7846 | 96.7023 | 5455397.2822 | 0 | 4254842.6887 | 0 | 0 | 0 | 1931220.2817 | 4540169.4985 | 11812589.7183 | 8062335.2072 | 36056554.6766 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64572151.1191 | 123562959.4783 | 1778279.41 | 10.3257 | 6253.5252 | 11966.5222 | 127.4866 | 243.9537
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.3887 | 20.0404 | 2.5848 | 4 | 6246.6789 | 11952.2796 | 127.347 | 243.6634 | 95.7383 | 13.7808 | 90.2374 | 5458248.6887 | 0 | 4258058.9021 | 0 | 0 | 0 | 1929324.6842 | 4541796.5872 | 11816823.0694 | 8065224.5563 | 36069476.4879 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64585072.9305 | 123575881.2896 | 2371373.7057 | 10.3391 | 6246.6789 | 11952.2796 | 127.347 | 243.6634
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.4741 | 20.0544 | 2.5872 | 4 | 6241.5464 | 11941.7455 | 127.2424 | 243.4486 | 95.7316 | 13.7781 | 86.9462 | 5460213.853 | 0 | 4260277.3443 | 0 | 0 | 0 | 1927752.0087 | 4542814.8504 | 11819472.3812 | 8067032.766 | 36077563.2037 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64593159.6462 | 123583968.0054 | 3162277.6602 | 10.3489 | 6241.5464 | 11941.7455 | 127.2424 | 243.4486
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5519 | 20.067 | 2.5892 | 4 | 6237.6986 | 11933.5935 | 127.1639 | 243.2824 | 95.7256 | 13.7756 | 92.6107 | 5462004.2057 | 0 | 4262299.0935 | 0 | 0 | 0 | 1926832.6723 | 4543943.0289 | 11822407.6702 | 8069036.1611 | 36086522.8316 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64602119.2742 | 123592927.6333 | 4216965.0343 | 10.3567 | 6237.6986 | 11933.5935 | 127.1639 | 243.2824
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.601 | 20.075 | 2.5906 | 4 | 6234.8136 | 11927.6554 | 127.1051 | 243.1614 | 95.7218 | 13.7741 | 89.1598 | 5463132.725 | 0 | 4263574.3083 | 0 | 0 | 0 | 1925962.7073 | 4544541.1988 | 11823963.9858 | 8070098.3784 | 36091273.3036 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64606869.7461 | 123597678.1053 | 5623413.2519 | 10.3623 | 6234.8136 | 11927.6554 | 127.1051 | 243.1614
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.625 | 20.0793 | 2.5915 | 4 | 6232.6504 | 11923.4409 | 127.061 | 243.0755 | 95.7199 | 13.7733 | 92.5716 | 5463685.3043 | 0 | 4264199.3299 | 0 | 0 | 0 | 1925064.5439 | 4544650.1795 | 11824247.5311 | 8070291.904 | 36092138.7927 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64607735.2353 | 123598543.5944 | 7498942.0933 | 10.366 | 6232.6504 | 11923.4409 | 127.061 | 243.0755
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6593 | 20.0847 | 2.5923 | 4 | 6231.0284 | 11919.9792 | 127.0279 | 243.0049 | 95.7172 | 13.7722 | 86.0351 | 5464473.175 | 0 | 4265089.786 | 0 | 0 | 0 | 1924701.3554 | 4545163.0834 | 11825582.0018 | 8071202.7077 | 36096212.1093 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64611808.5518 | 123602616.911 | 10000000 | 10.3694 | 6231.0284 | 11919.9792 | 127.0279 | 243.0049
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.7702 | [19 empty] | 100 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1755 | [19 empty] | 133.3521 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.033489 | 0.002663 | 4 | 2842108.418 | 8500848.0034 | 57940.2243 | 173301.2848 | 58.5167 | 12.5486 | 25.0701 | 156273.4636 | 0 | 54167.6406 | 0 | 0 | 0 | 155598.7282 | 142755.5346 | 371420.6179 | 253502.2037 | 1133718.1887 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 30274477.496 | 90552045.7787 | 177.8279 | 0.010652 | 2842108.418 | 8500848.0034 | 57940.2243 | 173301.2848
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8667 | 0.05902 | 0.0095157 | 4 | 819577.3109 | 2403211.427 | 16708.192 | 48992.7155 | 71.8405 | 13.8718 | 43.1684 | 279440.3463 | 0 | 124474.5975 | 0 | 0 | 0 | 259465.7143 | 258718.4567 | 673132.3538 | 459426.663 | 2054658.1316 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 31195417.4389 | 91472985.7216 | 237.1374 | 0.038063 | 819577.3109 | 2403211.427 | 16708.192 | 48992.7155
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0117 | 0.1819 | 0.020132 | 4 | 396597.1374 | 1145140.8447 | 8085.1691 | 23345.245 | 78.5295 | 14.4671 | 49.7565 | 383283.8043 | 0 | 185451.7625 | 0 | 0 | 0 | 333935.3359 | 352041.6521 | 915940.1651 | 625147.9833 | 2795800.7033 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 31936560.0106 | 92214128.2933 | 316.2278 | 0.080526 | 396597.1374 | 1145140.8447 | 8085.1691 | 23345.245
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.464 | 0.35924 | 0.035909 | 4 | 228370.2992 | 648029.5225 | 4655.6374 | 13210.9583 | 83.8061 | 14.9035 | 48.2898 | 505572.3561 | 0 | 258920.578 | 0 | 0 | 0 | 417556.9759 | 460999.4649 | 1199426.0436 | 818632.9205 | 3661108.3388 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 32801867.6461 | 93079435.9288 | 421.6965 | 0.14363 | 228370.2992 | 648029.5225 | 4655.6374 | 13210.9583
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2977 | 0.60093 | 0.058261 | 4 | 145052.4065 | 403704.6646 | 2957.0895 | 8230.0656 | 87.9519 | 15.2256 | 62.4828 | 648194.3123 | 0 | 346653.9349 | 0 | 0 | 0 | 510663.6968 | 587149.6582 | 1527642.9696 | 1042647.7167 | 4662952.2886 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 33803711.5959 | 94081279.8786 | 562.3413 | 0.23304 | 145052.4065 | 403704.6646 | 2957.0895 | 8230.0656
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6607 | 0.92606 | 0.089091 | 4 | 98192.9647 | 267338.8314 | 2001.7964 | 5450.0637 | 91.2643 | 15.4688 | 53.9075 | 817618.7188 | 0 | 453440.4071 | 0 | 0 | 0 | 618266.1131 | 736836.8432 | 1917098.3201 | 1308458.9959 | 5851719.3982 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 34992478.7055 | 95270046.9882 | 749.8942 | 0.35636 | 98192.9647 | 267338.8314 | 2001.7964 | 5450.0637
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6498 | 1.3495 | 0.13075 | 4 | 69548.3867 | 184803.9725 | 1417.8379 | 3767.4789 | 93.8512 | 15.6483 | 43.2107 | 1015163.9973 | 0 | 581066.5299 | 0 | 0 | 0 | 738864.4573 | 910687.0439 | 2369420.8807 | 1617178.4378 | 7232381.3469 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 36373140.6542 | 96650708.9369 | 1000 | 0.52299 | 69548.3867 | 184803.9725 | 1417.8379 | 3767.4789
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4935 | 1.9028 | 0.18639 | 4 | 50985.1174 | 131832.9122 | 1039.4006 | 2687.5922 | 95.8951 | 15.78 | 60.0123 | 1249476.8993 | 0 | 736280.6093 | 0 | 0 | 0 | 878760.1576 | 1117161.8898 | 2906626.0759 | 1983832.022 | 8872137.6539 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 38012896.9612 | 98290465.2439 | 1333.5214 | 0.74557 | 50985.1174 | 131832.9122 | 1039.4006 | 2687.5922
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3346 | 2.6085 | 0.25965 | 4 | 38431.6655 | 96468.274 | 783.4815 | 1966.6362 | 97.4655 | 15.8693 | 49.3433 | 1521956.0571 | 0 | 921417.6602 | 0 | 0 | 0 | 1035470.5503 | 1356749.2643 | 3529983.2783 | 2409286.1213 | 10774862.9315 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 39915622.2388 | 100193190.5215 | 1778.2794 | 1.0386 | 38431.6655 | 96468.274 | 783.4815 | 1966.6362
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3755 | 3.4974 | 0.35481 | 4 | 29668.2656 | 72140.1724 | 604.8277 | 1470.675 | 98.6503 | 15.9196 | 57.5397 | 1836383.8177 | 0 | 1140682.7249 | 0 | 0 | 0 | 1209044.648 | 1632583.3644 | 4247647.0252 | 2899106.3751 | 12965447.9552 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 42106207.2625 | 102383775.5452 | 2371.3737 | 1.4192 | 29668.2656 | 72140.1724 | 604.8277 | 1470.675
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8003 | 4.5983 | 0.47625 | 4 | 23408.5561 | 55050.5391 | 477.2151 | 1122.2797 | 99.5148 | 15.9322 | 64.0458 | 2194335.2217 | 0 | 1397073.919 | 0 | 0 | 0 | 1397603.4859 | 1945714.9244 | 5062351.1122 | 3455158.655 | 15452237.3183 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 44592996.6256 | 104870564.9083 | 3162.2777 | 1.905 | 23408.5561 | 55050.5391 | 477.2151 | 1122.2797
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.6554 | 5.9218 | 0.62732 | 4 | 18861.5188 | 42883.4855 | 384.5176 | 874.2379 | 100.0978 | 15.9032 | 67.906 | 2590341.8565 | 0 | 1688942.53 | 0 | 0 | 0 | 1592969.2891 | 2290178.9335 | 5958575.8046 | 4066850.4231 | 18187858.8368 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 47328618.1441 | 107606186.4268 | 4216.965 | 2.5093 | 18861.5188 | 42883.4855 | 384.5176 | 874.2379
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.8166 | 7.4537 | 0.80875 | 4 | 15524.0263 | 34157.0281 | 316.4783 | 696.3372 | 100.4295 | 15.8289 | 64.7314 | 3012552.4709 | 0 | 2009916.6094 | 0 | 0 | 0 | 1783336.3105 | 2654264.1024 | 6905850.7301 | 4713385.0243 | 21079305.2477 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 50220064.555 | 110497632.8377 | 5623.4133 | 3.235 | 15524.0263 | 34157.0281 | 316.4783 | 696.3372
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.8734 | 9.1371 | 1.0164 | 4 | 13062.7471 | 27888.5198 | 266.3018 | 568.5452 | 100.5334 | 15.708 | 64.5752 | 3440155.015 | 0 | 2346250.0361 | 0 | 0 | 0 | 1952330.0232 | 3018106.679 | 7852494.48 | 5359488.8352 | 23968825.0685 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 53109584.3758 | 113387152.6585 | 7498.9421 | 4.0657 | 13062.7471 | 27888.5198 | 266.3018 | 568.5452
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1593 | 10.8741 | 1.2405 | 4 | 11246.9362 | 23394.7915 | 229.284 | 476.9345 | 100.4403 | 15.5464 | 63.8393 | 3847250.3673 | 0 | 2678588.417 | 0 | 0 | 0 | 2083871.1457 | 3357786.8727 | 8736272.6659 | 5962685.6069 | 26666455.0754 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 55807214.3827 | 116084782.6654 | 10000 | 4.962 | 11246.9362 | 23394.7915 | 229.284 | 476.9345
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.983 | 12.5582 | 1.4675 | 4 | 9909.3914 | 20178.207 | 202.0163 | 411.36 | 100.1975 | 15.3571 | 76.8848 | 4212543.897 | 0 | 2988835.442 | 0 | 0 | 0 | 2170472.6907 | 3655022.2916 | 9509618.2545 | 6490509.8618 | 29027002.4377 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 58167761.745 | 118445330.0277 | 13335.2143 | 5.87 | 9909.3914 | 20178.207 | 202.0163 | 411.36
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.7707 | 14.0973 | 1.6838 | 4 | 8925.4232 | 17875.2685 | 181.9568 | 364.4115 | 99.8636 | 15.1581 | 72.6283 | 4523020.4927 | 0 | 3263381.6114 | 0 | 0 | 0 | 2213529.9987 | 3899973.5201 | 10146931.1047 | 6925488.9775 | 30972325.7051 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 60113085.0124 | 120390653.2951 | 17782.7941 | 6.735 | 8925.4232 | 17875.2685 | 181.9568 | 364.4115
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1971 | 15.4356 | 1.879 | 4 | 8201.5669 | 16221.6748 | 167.2 | 330.7008 | 99.4955 | 14.9659 | 80.4271 | 4775763.3769 | 0 | 3495796.8322 | 0 | 0 | 0 | 2221807.1269 | 4092413.2611 | 10647619.8359 | 7267219.3247 | 32500619.7577 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 61641379.065 | 121918947.3477 | 23713.7371 | 7.5158 | 8201.5669 | 16221.6748 | 167.2 | 330.7008
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.2003 | 16.5572 | 2.0476 | 4 | 7668.3567 | 15027.889 | 156.3298 | 306.3638 | 99.1349 | 14.7917 | 88.6476 | 4975773.9494 | 0 | 3686503.6617 | 0 | 0 | 0 | 2207418.9135 | 4239181.6446 | 11029481.0635 | 7527847.459 | 33666206.6917 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 62806965.999 | 123084534.2817 | 31622.7766 | 8.1904 | 7668.3567 | 15027.889 | 156.3298 | 306.3638
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.8371 | 17.467 | 2.1881 | 4 | 7274.7205 | 14161.6261 | 148.305 | 288.7039 | 98.8095 | 14.6421 | 85.1731 | 5130194.2994 | 0 | 3838541.3404 | 0 | 0 | 0 | 2180223.8028 | 4348094.1826 | 11312849.1464 | 7721251.9982 | 34531154.7699 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 63671914.0772 | 123949482.3599 | 42169.6503 | 8.7525 | 7274.7205 | 14161.6261 | 148.305 | 288.7039
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2929 | 18.1905 | 2.3022 | 4 | 6983.3874 | 13529.0542 | 142.3658 | 275.8081 | 98.5302 | 14.5179 | 88.4225 | 5248124.6707 | 0 | 3957874.7231 | 0 | 0 | 0 | 2148472.6276 | 4428244.0883 | 11521382.7601 | 7863580.4745 | 35167679.3443 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 64308438.6515 | 124586006.9343 | 56234.1325 | 9.2088 | 6983.3874 | 13529.0542 | 142.3658 | 275.8081
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7519 | 18.7552 | 2.3928 | 4 | 6767.2341 | 13064.9352 | 137.9592 | 266.3464 | 98.3 | 14.4178 | 81.9369 | 5337154.0896 | 0 | 4050029.7234 | 0 | 0 | 0 | 2116840.1777 | 4486569.3564 | 11673133.1434 | 7967153.2292 | 35630879.7196 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 64771639.0269 | 125049207.3097 | 74989.4209 | 9.5714 | 6767.2341 | 13064.9352 | 137.9592 | 266.3464
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.4218 | 19.1927 | 2.4639 | 4 | 6606.5046 | 12722.5723 | 134.6825 | 259.3668 | 98.1144 | 14.3385 | 95.3333 | 5404363.2089 | 0 | 4120886.558 | 0 | 0 | 0 | 2088382.226 | 4529316.4772 | 11784352.3832 | 8043062.6458 | 35970363.4992 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65111122.8065 | 125388691.0892 | 100000 | 9.8556 | 6606.5046 | 12722.5723 | 134.6825 | 259.3668
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4707 | 19.5293 | 2.519 | 4 | 6486.7645 | 12469.0116 | 132.2415 | 254.1977 | 97.9672 | 14.2763 | 84.5433 | 5455045.5935 | 0 | 4175106.7994 | 0 | 0 | 0 | 2064196.3815 | 4560796.022 | 11866255.7013 | 8098963.3433 | 36220363.841 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65361123.1483 | 125638691.431 | 133352.1432 | 10.0761 | 6486.7645 | 12469.0116 | 132.2415 | 254.1977
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0371 | 19.7872 | 2.5614 | 4 | 6397.4257 | 12280.611 | 130.4202 | 250.3569 | 97.8518 | 14.228 | 86.8887 | 5493267.9002 | 0 | 4216470.5486 | 0 | 0 | 0 | 2044410.5746 | 4584118.1191 | 11926935.014 | 8140378.2211 | 36405580.3775 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65546339.6848 | 125823907.9675 | 177827.941 | 10.2457 | 6397.4257 | 12280.611 | 130.4202 | 250.3569
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.2091 | 19.9808 | 2.5937 | 4 | 6330.6897 | 12140.7028 | 129.0597 | 247.5046 | 97.764 | 14.1915 | 85.0379 | 5521568.3673 | 0 | 4247371.4494 | 0 | 0 | 0 | 2028192.411 | 4600881.5688 | 11970550.0714 | 8170146.394 | 36538710.2619 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65679469.5692 | 125957037.8519 | 237137.3706 | 10.3748 | 6330.6897 | 12140.7028 | 129.0597 | 247.5046
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.0982 | 20.1278 | 2.6182 | 4 | 6280.7917 | 12036.3285 | 128.0424 | 245.3768 | 97.6964 | 14.1635 | 77.0198 | 5542865.2702 | 0 | 4270784.1377 | 0 | 0 | 0 | 2015471.6077 | 4613357.1961 | 12003009.0945 | 8192300.3441 | 36637787.6502 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65778546.9575 | 126056115.2402 | 316227.766 | 10.473 | 6280.7917 | 12036.3285 | 128.0424 | 245.3768
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.7749 | 20.2396 | 2.6369 | 4 | 6243.4566 | 11958.2859 | 127.2813 | 243.7858 | 97.6444 | 14.1421 | 101.0584 | 5558976.2329 | 0 | 4288588.5297 | 0 | 0 | 0 | 2005692.0591 | 4622770.1605 | 12027499.697 | 8209015.6836 | 36712542.3628 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65853301.6701 | 126130869.9528 | 421696.5034 | 10.5476 | 6243.4566 | 11958.2859 | 127.2813 | 243.7858
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.2696 | 20.3218 | 2.6509 | 4 | 6215.5062 | 11900.2354 | 126.7115 | 242.6024 | 97.6062 | 14.1263 | 96.2706 | 5570699.7874 | 0 | 4301596.1922 | 0 | 0 | 0 | 1997852.6995 | 4629357.9848 | 12044639.8647 | 8220714.2002 | 36764860.7288 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65905620.0361 | 126183188.3189 | 562341.3252 | 10.6034 | 6215.5062 | 11900.2354 | 126.7115 | 242.6024
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6593 | 20.3862 | 2.6615 | 4 | 6194.5729 | 11856.4851 | 126.2847 | 241.7105 | 97.5759 | 14.1139 | 85.5861 | 5579904.0218 | 0 | 4311838.7709 | 0 | 0 | 0 | 1992203.1024 | 4634738.8991 | 12058639.8997 | 8230269.5118 | 36807594.2056 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65948353.5129 | 126225921.7956 | 749894.2093 | 10.6462 | 6194.5729 | 11856.4851 | 126.2847 | 241.7105
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9493 | 20.4342 | 2.6696 | 4 | 6178.89 | 11823.7932 | 125.965 | 241.044 | 97.5532 | 14.1046 | 90.9358 | 5586735.6785 | 0 | 4319458.9009 | 0 | 0 | 0 | 1987840.6601 | 4638673.7434 | 12068877.5575 | 8237256.9236 | 36838843.4639 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 65979602.7712 | 126257171.0539 | 1000000 | 10.6782 | 6178.89 | 11823.7932 | 125.965 | 241.044
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1586 | 20.469 | 2.6755 | 4 | 6167.138 | 11799.4705 | 125.7254 | 240.5482 | 97.5368 | 14.0979 | 87.5485 | 5591655.0994 | 0 | 4324955.7977 | 0 | 0 | 0 | 1984361.4057 | 4641379.1981 | 12075916.5957 | 8242061.2118 | 36860329.3085 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66001088.6158 | 126278656.8985 | 1333521.4322 | 10.7021 | 6167.138 | 11799.4705 | 125.7254 | 240.5482
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3218 | 20.496 | 2.68 | 4 | 6158.3299 | 11781.1401 | 125.5459 | 240.1745 | 97.524 | 14.0926 | 94.9655 | 5595485.0141 | 0 | 4329240.5788 | 0 | 0 | 0 | 1981848.7361 | 4643563.9883 | 12081600.9716 | 8245940.9152 | 36877680.2041 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66018439.5114 | 126296007.7941 | 1778279.41 | 10.7202 | 6158.3299 | 11781.1401 | 125.5459 | 240.1745
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4487 | 20.517 | 2.6835 | 4 | 6151.7275 | 11767.3249 | 125.4113 | 239.8928 | 97.514 | 14.0886 | 86.8738 | 5598459.8743 | 0 | 4332571.9374 | 0 | 0 | 0 | 1980038.2256 | 4645317.3145 | 12086162.7668 | 8249054.4341 | 36891604.5527 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66032363.86 | 126309932.1427 | 2371373.7057 | 10.734 | 6151.7275 | 11767.3249 | 125.4113 | 239.8928
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5413 | 20.5323 | 2.6861 | 4 | 6146.7779 | 11757.019 | 125.3104 | 239.6827 | 97.5067 | 14.0856 | 84.5451 | 5600629.2361 | 0 | 4335003.1983 | 0 | 0 | 0 | 1978622.3987 | 4646559.3849 | 12089394.3792 | 8251260.076 | 36901468.6732 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66042227.9805 | 126319796.2632 | 3162277.6602 | 10.7442 | 6146.7779 | 11757.019 | 125.3104 | 239.6827
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5996 | 20.5422 | 2.6879 | 4 | 6143.067 | 11749.4972 | 125.2347 | 239.5294 | 97.5021 | 14.0837 | 92.6567 | 5601994.3773 | 0 | 4336534.3266 | 0 | 0 | 0 | 1977338.664 | 4647188.2735 | 12091030.6183 | 8252376.8428 | 36906463.1025 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66047222.4098 | 126324790.6925 | 4216965.0343 | 10.7515 | 6143.067 | 11749.4972 | 125.2347 | 239.5294
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.6534 | 20.551 | 2.6893 | 4 | 6140.2847 | 11743.6773 | 125.178 | 239.4107 | 97.4978 | 14.082 | 85.8271 | 5603251.3866 | 0 | 4337944.3204 | 0 | 0 | 0 | 1976568.3942 | 4647927.9995 | 12092955.2336 | 8253690.4323 | 36912337.7666 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66053097.0739 | 126330665.3566 | 5623413.2519 | 10.7573 | 6140.2847 | 11743.6773 | 125.178 | 239.4107
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.6922 | 20.5575 | 2.6904 | 4 | 6138.1986 | 11739.3395 | 125.1355 | 239.3223 | 97.4948 | 14.0807 | 89.3611 | 5604161.2082 | 0 | 4338965.2458 | 0 | 0 | 0 | 1975962.2052 | 4648444.5771 | 12094299.2625 | 8254607.7596 | 36916440.2583 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66057199.5656 | 126334767.8483 | 7498942.0933 | 10.7617 | 6138.1986 | 11739.3395 | 125.1355 | 239.3223
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7265 | 20.5631 | 2.6913 | 4 | 6136.6343 | 11735.9947 | 125.1036 | 239.2541 | 97.4921 | 14.0796 | 83.8346 | 5604962.8199 | 0 | 4339864.8005 | 0 | 0 | 0 | 1975606.4012 | 4648969.2684 | 12095664.4017 | 8255539.4952 | 36920607.1871 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66061366.4944 | 126338934.7771 | 10000000 | 10.7651 | 6136.6343 | 11735.9947 | 125.1036 | 239.2541
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0864 | [19 empty] | 100 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9103 | [19 empty] | 133.3521 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.034827 | 0.0027851 | 4 | 2775014.4948 | 8302421.3904 | 56572.424 | 169256.0899 | 58.8213 | 12.7998 | 23.9088 | 158027.58 | 0 | 53953.724 | 0 | 0 | 0 | 157145.142 | 143959.3139 | 374552.6047 | 255639.849 | 1143278.2137 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 30915060.4766 | 92493159.8964 | 177.8279 | 0.011141 | 2775014.4948 | 8302421.3904 | 56572.424 | 169256.0899
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9593 | 0.064923 | 0.01019 | 4 | 783059.8187 | 2293819.873 | 15963.7336 | 46762.6207 | 73.1862 | 14.225 | 38.8968 | 291874.9273 | 0 | 129867.4137 | 0 | 0 | 0 | 270963.9174 | 270155.4408 | 702889.0405 | 479736.2131 | 2145486.9528 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 31917269.2157 | 93495368.6355 | 237.1374 | 0.04076 | 783059.8187 | 2293819.873 | 15963.7336 | 46762.6207
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1313 | 0.1932 | 0.021468 | 4 | 380596.8566 | 1097688.5245 | 7758.9817 | 22377.8653 | 79.96 | 14.8236 | 54.9323 | 399358.9346 | 0 | 192610.1943 | 0 | 0 | 0 | 347841.8622 | 366526.2865 | 953626.2126 | 650869.4852 | 2910832.9754 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 32682615.2383 | 94260714.6581 | 316.2278 | 0.085872 | 380596.8566 | 1097688.5245 | 7758.9817 | 22377.8653
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6071 | 0.37682 | 0.038196 | 4 | 219713.0128 | 622752.7636 | 4479.1469 | 12695.6574 | 85.2868 | 15.2609 | 47.5673 | 525073.4035 | 0 | 267670.5483 | 0 | 0 | 0 | 433145.6844 | 478096.9581 | 1243910.2138 | 848994.2807 | 3796891.0887 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 33568673.3516 | 95146772.7714 | 421.6965 | 0.15278 | 219713.0128 | 622752.7636 | 4479.1469 | 12695.6574
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.505 | 0.63055 | 0.061906 | 4 | 139798.1167 | 388472.0489 | 2849.9737 | 7919.5282 | 89.5534 | 15.5897 | 59.6025 | 674424.6481 | 0 | 358968.674 | 0 | 0 | 0 | 531169.6649 | 610179.5649 | 1587562.0629 | 1083543.7291 | 4845848.3438 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 34617630.6067 | 96195730.0266 | 562.3413 | 0.24763 | 139798.1167 | 388472.0489 | 2849.9737 | 7919.5282
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9165 | 0.96793 | 0.094552 | 4 | 94765.4263 | 257581.0796 | 1931.9214 | 5251.1387 | 92.9133 | 15.8342 | 57.7452 | 849360.7319 | 0 | 468536.6263 | 0 | 0 | 0 | 641648.8859 | 764223.0352 | 1988351.5739 | 1357090.8057 | 6069211.6589 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 35840993.9219 | 97419093.3417 | 749.8942 | 0.37821 | 94765.4263 | 257581.0796 | 1931.9214 | 5251.1387
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9982 | 1.4109 | 0.13869 | 4 | 67199.1643 | 178197.2852 | 1369.9459 | 3632.7927 | 95.5655 | 16.0163 | 44.9031 | 1055441.2041 | 0 | 600836.4517 | 0 | 0 | 0 | 767837.5304 | 945404.9227 | 2459749.6795 | 1678829.6991 | 7508099.4875 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 37279881.7505 | 98857981.1703 | 1000 | 0.55477 | 67199.1643 | 178197.2852 | 1369.9459 | 3632.7927
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9345 | 1.9865 | 0.19758 | 4 | 49315.6759 | 127232.2017 | 1005.3668 | 2593.8005 | 97.6457 | 16.1486 | 56.3235 | 1298240.8341 | 0 | 760660.4627 | 0 | 0 | 0 | 912382.6721 | 1158800.7478 | 3014961.8431 | 2057773.4092 | 9202819.9689 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 38974602.2318 | 100552701.6517 | 1333.5214 | 0.79031 | 49315.6759 | 127232.2017 | 1005.3668 | 2593.8005
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.8922 | 2.7206 | 0.27506 | 4 | 37211.9078 | 93180.3926 | 758.6151 | 1899.6083 | 99.2452 | 16.2378 | 54.1727 | 1580645.36 | 0 | 951330.9189 | 0 | 0 | 0 | 1074381.348 | 1406479.4745 | 3659371.084 | 2497595.9574 | 11169804.1426 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 40941586.4055 | 102519685.8253 | 1778.2794 | 1.1002 | 37211.9078 | 93180.3926 | 758.6151 | 1899.6083
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0749 | 3.6446 | 0.37559 | 4 | 28758.3891 | 69746.2476 | 586.2787 | 1421.8716 | 100.4525 | 16.2875 | 53.1419 | 1906388.5749 | 0 | 1177035.1537 | 0 | 0 | 0 | 1253766.082 | 1691504.0261 | 4400946.5008 | 3003736.4172 | 13433376.7547 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 43205159.0176 | 104783258.4374 | 2371.3737 | 1.5023 | 28758.3891 | 69746.2476 | 586.2787 | 1421.8716
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.6628 | 4.7875 | 0.50375 | 4 | 22714.868 | 53274.8407 | 463.0733 | 1086.0797 | 101.3301 | 16.2968 | 63.0479 | 2276664.9855 | 0 | 1440645.4416 | 0 | 0 | 0 | 1448070.3602 | 2014498.5071 | 5241311.8849 | 3577303.0596 | 15998494.2389 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 45770276.5018 | 107348375.9217 | 3162.2777 | 2.015 | 22714.868 | 53274.8407 | 463.0733 | 1086.0797
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.6908 | 6.1585 | 0.66283 | 4 | 18324.7395 | 41550.0605 | 373.5746 | 847.0542 | 101.9201 | 16.2637 | 49.9652 | 2685392.785 | 0 | 1740078.4741 | 0 | 0 | 0 | 1648695.6119 | 2368925.0797 | 6163457.124 | 4206686.1335 | 18813235.2082 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 48585017.4711 | 110163116.891 | 4216.965 | 2.6513 | 18324.7395 | 41550.0605 | 373.5746 | 847.0542
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.0197 | 7.7409 | 0.85336 | 4 | 15102.3519 | 33142.3521 | 307.8819 | 675.6517 | 102.2525 | 16.1835 | 53.3538 | 3119919.2216 | 0 | 2068507.0163 | 0 | 0 | 0 | 1843251.6055 | 2742354.3589 | 7135043.5077 | 4869813.8045 | 21778889.5146 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 51550671.7775 | 113128771.1973 | 5623.4133 | 3.4134 | 15102.3519 | 33142.3521 | 307.8819 | 675.6517
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.1982 | 9.4709 | 1.0705 | 4 | 12726.4906 | 27106.857 | 259.4467 | 552.6099 | 102.3514 | 16.0555 | 64.4607 | 3557655.2246 | 0 | 2410916.8973 | 0 | 0 | 0 | 2014068.9265 | 3113230.0089 | 8099985.8718 | 5528406.7956 | 24724263.7247 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 54496045.9876 | 116074145.4074 | 7498.9421 | 4.2821 | 12726.4906 | 27106.857 | 259.4467 | 552.6099
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.5749 | 11.2508 | 1.3039 | 4 | 10974.3259 | 22780.8044 | 223.7265 | 464.4175 | 102.2499 | 15.8859 | 66.0475 | 3973233.759 | 0 | 2748412.128 | 0 | 0 | 0 | 2146251.0264 | 3458479.7962 | 8998254.9981 | 6141493.9318 | 27466125.6396 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 57237907.9025 | 118816007.3224 | 10000 | 5.2156 | 10974.3259 | 22780.8044 | 223.7265 | 464.4175
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4102 | 12.9653 | 1.5391 | 4 | 9684.0981 | 19686.6533 | 197.4234 | 401.3391 | 101.9983 | 15.6895 | 67.1939 | 4343643.3485 | 0 | 3061430.3538 | 0 | 0 | 0 | 2231147.3617 | 3758126.215 | 9777873.5136 | 6673599.5883 | 29845820.3809 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 59617602.6438 | 121195702.0636 | 13335.2143 | 6.1562 | 9684.0981 | 19686.6533 | 197.4234 | 401.3391
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.1861 | 14.5286 | 1.7623 | 4 | 8735.1454 | 17470.7447 | 178.0778 | 356.1648 | 101.6566 | 15.484 | 68.1878 | 4657859.2719 | 0 | 3337912.9678 | 0 | 0 | 0 | 2272394.7545 | 4004585.1277 | 10419109.0489 | 7111256.0172 | 31803117.188 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 61574899.4509 | 123152998.8707 | 17782.7941 | 7.0491 | 8735.1454 | 17470.7447 | 178.0778 | 356.1648
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5855 | 15.885 | 1.9631 | 4 | 8037.1061 | 15879.1112 | 163.8473 | 323.7172 | 101.2822 | 15.2864 | 77.9278 | 4913227.547 | 0 | 3571583.9 | 0 | 0 | 0 | 2279020.2162 | 4197894.3486 | 10922059.9886 | 7454530.3681 | 33338316.3686 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 63110098.6315 | 124688198.0513 | 23713.7371 | 7.8523 | 8037.1061 | 15879.1112 | 163.8473 | 323.7172
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5233 | 17.0154 | 2.1359 | 4 | 7522.9031 | 14730.5333 | 153.3646 | 300.3018 | 100.9187 | 15.1088 | 90.6101 | 5114166.0659 | 0 | 3762202.0502 | 0 | 0 | 0 | 2262480.1745 | 4344150.8333 | 11302589.3605 | 7714249.4835 | 34499837.968 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 64271620.2309 | 125849719.6507 | 31622.7766 | 8.5435 | 7522.9031 | 14730.5333 | 153.3646 | 300.3018
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1166 | 17.9334 | 2.2797 | 4 | 7143.2686 | 13896.2706 | 145.6252 | 283.2943 | 100.5907 | 14.9562 | 85.0683 | 5269633.5128 | 0 | 3914457.235 | 0 | 0 | 0 | 2234093.3548 | 4453091.8 | 11586031.4089 | 7907704.5057 | 35365011.8173 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 65136794.0802 | 126714893.5 | 42169.6503 | 9.1186 | 7143.2686 | 13896.2706 | 145.6252 | 283.2943
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.5233 | 18.6612 | 2.3961 | 4 | 6862.2692 | 13287.0942 | 139.8966 | 270.8754 | 100.3105 | 14.83 | 94.1342 | 5388019.682 | 0 | 4033587.8491 | 0 | 0 | 0 | 2201256.5634 | 4532916.9969 | 11793720.1967 | 8049456.371 | 35998957.6591 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 65770739.922 | 127348839.3419 | 56234.1325 | 9.5844 | 6862.2692 | 13287.0942 | 139.8966 | 270.8754
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.948 | 19.2298 | 2.4886 | 4 | 6653.7611 | 12839.8528 | 135.6459 | 261.7578 | 100.0795 | 14.7283 | 97.1837 | 5477528.3726 | 0 | 4125703.6542 | 0 | 0 | 0 | 2169013.5516 | 4591175.7756 | 11945297.5884 | 8152911.0554 | 36461629.9977 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 66233412.2606 | 127811511.6805 | 74989.4209 | 9.9543 | 6653.7611 | 12839.8528 | 135.6459 | 261.7578
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.5887 | 19.6698 | 2.561 | 4 | 6498.7019 | 12509.8859 | 132.4848 | 255.0309 | 99.8935 | 14.6478 | 83.6244 | 5545048.7756 | 0 | 4196463.5308 | 0 | 0 | 0 | 2140114.5969 | 4633834.4923 | 12056286.8189 | 8228663.4858 | 36800411.7003 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 66572193.9632 | 128150293.3831 | 100000 | 10.2439 | 6498.7019 | 12509.8859 | 132.4848 | 255.0309
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.6085 | 20.0074 | 2.6171 | 4 | 6383.1769 | 12265.5729 | 130.1297 | 250.0503 | 99.7465 | 14.585 | 95.4761 | 5595812.1585 | 0 | 4250435.8775 | 0 | 0 | 0 | 2115507.5876 | 4665084.6932 | 12137593.4313 | 8284156.9195 | 37048590.6676 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 66820372.9305 | 128398472.3504 | 133352.1432 | 10.4682 | 6383.1769 | 12265.5729 | 130.1297 | 250.0503
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.136 | 20.2635 | 2.66 | 4 | 6296.9774 | 12084.3245 | 128.3724 | 246.3553 | 99.6327 | 14.5367 | 88.7094 | 5633693.6528 | 0 | 4291169.3523 | 0 | 0 | 0 | 2095091.7042 | 4687782.3366 | 12196648.0435 | 8324462.9057 | 37228847.9951 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67000630.258 | 128578729.6778 | 177827.941 | 10.6401 | 6296.9774 | 12084.3245 | 128.3724 | 246.3553
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.2956 | 20.4583 | 2.6929 | 4 | 6232.5833 | 11949.3767 | 127.0596 | 243.6042 | 99.5447 | 14.4997 | 79.3609 | 5662159.7389 | 0 | 4322046.7963 | 0 | 0 | 0 | 2078776.4022 | 4704563.3456 | 12240308.7866 | 8354262.2601 | 37362117.3297 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67133899.5926 | 128711999.0124 | 237137.3706 | 10.7714 | 6232.5833 | 11949.3767 | 127.0596 | 243.6042
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.177 | 20.6064 | 2.7179 | 4 | 6184.4344 | 11848.6598 | 126.0781 | 241.551 | 99.477 | 14.4713 | 98.6674 | 5683624.8355 | 0 | 4345487.3608 | 0 | 0 | 0 | 2066029.2868 | 4717105.1784 | 12272940.063 | 8376533.7767 | 37461720.5012 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67233502.7641 | 128811602.184 | 316227.766 | 10.8714 | 6184.4344 | 11848.6598 | 126.0781 | 241.551
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8419 | 20.7183 | 2.7368 | 4 | 6148.4069 | 11773.4534 | 125.3436 | 240.0178 | 99.4253 | 14.4498 | 90.8731 | 5699722.3952 | 0 | 4363157.4031 | 0 | 0 | 0 | 2056118.2387 | 4726409.2344 | 12297147.3081 | 8393055.7189 | 37535610.2985 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67307392.5614 | 128885491.9812 | 421696.5034 | 10.9471 | 6148.4069 | 11773.4534 | 125.3436 | 240.0178
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3366 | 20.8017 | 2.751 | 4 | 6121.4349 | 11717.3504 | 124.7937 | 238.874 | 99.3866 | 14.4336 | 88.7536 | 5711644.2688 | 0 | 4376295.3072 | 0 | 0 | 0 | 2048358.4954 | 4733156.2478 | 12314701.653 | 8405036.92 | 37589192.892 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67360975.1549 | 128939074.5748 | 562341.3252 | 11.0041 | 6121.4349 | 11717.3504 | 124.7937 | 238.874
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7265 | 20.8671 | 2.7619 | 4 | 6101.2339 | 11675.06 | 124.3819 | 238.0119 | 99.356 | 14.4209 | 82.5226 | 5721008.5627 | 0 | 4386645.1767 | 0 | 0 | 0 | 2042779.9604 | 4738669.1429 | 12329045.0752 | 8414826.6004 | 37632974.5183 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67404756.7812 | 128982856.201 | 749894.2093 | 11.0477 | 6101.2339 | 11675.06 | 124.3819 | 238.0119
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.0017 | 20.9136 | 2.77 | 4 | 6086.0995 | 11643.7282 | 124.0734 | 237.3731 | 99.3342 | 14.4119 | 90.7051 | 5727600.4695 | 0 | 4393948.011 | 0 | 0 | 0 | 2038170.6718 | 4742290.4694 | 12338467.0239 | 8421257.2739 | 37661733.9195 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67433516.1824 | 129011615.6022 | 1000000 | 11.0799 | 6086.0995 | 11643.7282 | 124.0734 | 237.3731
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.2233 | 20.9508 | 2.7762 | 4 | 6074.7584 | 11619.9997 | 123.8422 | 236.8894 | 99.3167 | 14.4046 | 101.7484 | 5732896.4987 | 0 | 4399824.6735 | 0 | 0 | 0 | 2034972.299 | 4745400.4538 | 12346558.5653 | 8426779.9172 | 37686432.4075 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67458214.6704 | 129036314.0903 | 1333521.4322 | 11.1047 | 6074.7584 | 11619.9997 | 123.8422 | 236.8894
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3696 | 20.9757 | 2.7806 | 4 | 6066.2582 | 11602.5832 | 123.6689 | 236.5344 | 99.305 | 14.3998 | 95.1246 | 5736388.435 | 0 | 4403705.0241 | 0 | 0 | 0 | 2032152.0889 | 4747175.7637 | 12351177.5576 | 8429932.4744 | 37700531.3438 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67472313.6067 | 129050413.0265 | 1778279.41 | 11.1226 | 6066.2582 | 11602.5832 | 123.6689 | 236.5344
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.4841 | 20.9952 | 2.784 | 4 | 6059.8866 | 11589.4492 | 123.539 | 236.2666 | 99.2959 | 14.396 | 74.3466 | 5739118.0854 | 0 | 4406740.8475 | 0 | 0 | 0 | 2030118.3749 | 4748631.15 | 12354964.1742 | 8432516.918 | 37712089.5501 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67483871.813 | 129061971.2328 | 2371373.7057 | 11.1362 | 6059.8866 | 11589.4492 | 123.539 | 236.2666
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5741 | 21.0103 | 2.7866 | 4 | 6055.1099 | 11579.5327 | 123.4416 | 236.0644 | 99.2888 | 14.393 | 84.4541 | 5741262.6716 | 0 | 4409127.5139 | 0 | 0 | 0 | 2028668.1811 | 4749832.763 | 12358090.5246 | 8434650.7164 | 37721632.3706 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67493414.6335 | 129071514.0533 | 3162277.6602 | 11.1465 | 6055.1099 | 11579.5327 | 123.4416 | 236.0644
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6519 | 21.0232 | 2.7887 | 4 | 6051.5287 | 11571.9168 | 123.3686 | 235.9092 | 99.2826 | 14.3905 | 91.1578 | 5743115.6698 | 0 | 4411190.5077 | 0 | 0 | 0 | 2027781.1694 | 4751014.0653 | 12361164.0309 | 8436748.4476 | 37731013.8907 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67502796.1536 | 129080895.5734 | 4216965.0343 | 11.1547 | 6051.5287 | 11571.9168 | 123.3686 | 235.9092
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.701 | 21.0316 | 2.7901 | 4 | 6048.8436 | 11566.373 | 123.3139 | 235.7962 | 99.2786 | 14.3889 | 87.4427 | 5744283.677 | 0 | 4412491.7389 | 0 | 0 | 0 | 2026928.9905 | 4751644.7185 | 12362804.8611 | 8437868.348 | 37736022.334 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67507804.5969 | 129085904.0167 | 5623413.2519 | 11.1604 | 6048.8436 | 11566.373 | 123.3139 | 235.7962
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7445 | 21.0388 | 2.7913 | 4 | 6046.8304 | 11562.0974 | 123.2728 | 235.709 | 99.2752 | 14.3874 | 92.105 | 5745319.5537 | 0 | 4413645.8911 | 0 | 0 | 0 | 2026422.2211 | 4752301.1897 | 12364512.8646 | 8439034.0954 | 37741235.8156 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67513018.0785 | 129091117.4983 | 7498942.0933 | 11.165 | 6046.8304 | 11562.0974 | 123.2728 | 235.709
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7593 | 21.0416 | 2.792 | 4 | 6045.3208 | 11559.2089 | 123.242 | 235.6501 | 99.274 | 14.3869 | 80.4733 | 5745671.0321 | 0 | 4414038.137 | 0 | 0 | 0 | 2025686.775 | 4752304.4182 | 12364521.2645 | 8439039.8285 | 37741261.4553 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 67513043.7182 | 129091143.138 | 10000000 | 11.1678 | 6045.3208 | 11559.2089 | 123.242 | 235.6501
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5541 | [19 empty] | 100 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3945 | [19 empty] | 133.3521 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.036155 | 0.0029019 | 4 | 2718983.6185 | 8137103.7981 | 55430.1588 | 165885.8672 | 59.1151 | 13.0498 | 23.9726 | 159752.7459 | 0 | 53734.6622 | 0 | 0 | 0 | 158689.3536 | 145148.9371 | 377647.7601 | 257752.3562 | 1152725.8151 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 31561391.1245 | 94453792.895 | 177.8279 | 0.011608 | 2718983.6185 | 8137103.7981 | 55430.1588 | 165885.8672
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0325 | 0.069608 | 0.010896 | 4 | 748702.8115 | 2191759.1375 | 15263.3195 | 44681.9746 | 74.3896 | 14.5649 | 34.2702 | 302627.606 | 0 | 134242.3285 | 0 | 0 | 0 | 280501.8102 | 279774.9804 | 727917.1093 | 496818.3843 | 2221882.2187 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 32630547.5281 | 95522949.2985 | 237.1374 | 0.043583 | 748702.8115 | 2191759.1375 | 15263.3195 | 44681.9746
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.248 | 0.20454 | 0.022868 | 4 | 365507.0855 | 1053065.7978 | 7451.3563 | 21468.1707 | 81.3782 | 15.1789 | 53.7772 | 415407.8177 | 0 | 199682.0494 | 0 | 0 | 0 | 361586.8307 | 380903.9121 | 991033.8452 | 676400.9631 | 3025015.4182 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 33433680.7275 | 96326082.498 | 316.2278 | 0.091472 | 365507.0855 | 1053065.7978 | 7451.3563 | 21468.1707
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7749 | 0.39737 | 0.040608 | 4 | 211535.7225 | 598726.2295 | 4312.4418 | 12205.844 | 86.8404 | 15.6239 | 67.2028 | 546907.8263 | 0 | 277733.6109 | 0 | 0 | 0 | 451216.1459 | 497584.4574 | 1294612.6896 | 883599.7623 | 3951654.4923 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 34360319.8017 | 97252721.5722 | 421.6965 | 0.16243 | 211535.7225 | 598726.2295 | 4312.4418 | 12205.844
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7117 | 0.66078 | 0.065711 | 4 | 134830.6524 | 374108.6503 | 2748.7052 | 7626.7109 | 91.1568 | 15.9537 | 56.7986 | 701005.5274 | 0 | 371371.0252 | 0 | 0 | 0 | 551819.2034 | 633436.3448 | 1648071.4336 | 1124842.6179 | 5030546.1524 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 35439211.4618 | 98331613.2323 | 562.3413 | 0.26284 | 134830.6524 | 374108.6503 | 2748.7052 | 7626.7109
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1944 | 1.0133 | 0.10028 | 4 | 91522.472 | 248315.4031 | 1865.8094 | 5062.2454 | 94.5901 | 16.2014 | 52.22 | 883129.994 | 0 | 484751.1082 | 0 | 0 | 0 | 667020.9044 | 793611.7826 | 2064815.0661 | 1409278.7103 | 6302607.5656 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 36711272.875 | 99603674.6454 | 749.8942 | 0.40112 | 91522.472 | 248315.4031 | 1865.8094 | 5062.2454
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3466 | 1.4737 | 0.14696 | 4 | 64974.6893 | 171960.7738 | 1324.5969 | 3505.653 | 97.2835 | 16.3844 | 48.8903 | 1096329.3005 | 0 | 620787.8149 | 0 | 0 | 0 | 797074.6872 | 980534.803 | 2551150.4221 | 1741212.584 | 7787089.6117 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 38195754.9211 | 101088156.6916 | 1000 | 0.58786 | 64974.6893 | 171960.7738 | 1324.5969 | 3505.653
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3755 | 2.072 | 0.20921 | 4 | 47733.7103 | 122887.2573 | 973.1162 | 2505.223 | 99.4004 | 16.5173 | 58.8362 | 1347742.2091 | 0 | 785262.687 | 0 | 0 | 0 | 946300.338 | 1200929.0413 | 3124571.021 | 2132583.9254 | 9537389.2218 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 39946054.5312 | 102838456.3016 | 1333.5214 | 0.83685 | 47733.7103 | 122887.2573 | 973.1162 | 2505.223
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4575 | 2.836 | 0.29109 | 4 | 36055.2031 | 90069.2151 | 735.0341 | 1836.1828 | 101.0312 | 16.6063 | 60.9242 | 1640640.4234 | 0 | 981801.8584 | 0 | 0 | 0 | 1114094.716 | 1457249.4291 | 3791464.0917 | 2587752.1494 | 11573002.668 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 41981667.9774 | 104874069.7478 | 1778.2794 | 1.1644 | 36055.2031 | 90069.2151 | 735.0341 | 1836.1828
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.7936 | 3.7974 | 0.39726 | 4 | 27893.5348 | 67472.6255 | 568.6474 | 1375.5207 | 102.2611 | 16.6547 | 53.0195 | 1978406.5297 | 0 | 1214415.7463 | 0 | 0 | 0 | 1299876.014 | 1752152.3331 | 4558740.9548 | 3111434.3744 | 13915025.9523 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 44323691.2617 | 107216093.0321 | 2371.3737 | 1.589 | 27893.5348 | 67472.6255 | 568.6474 | 1375.5207
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.5324 | 4.9815 | 0.53231 | 4 | 22055.9932 | 51593.4189 | 449.6413 | 1051.8016 | 103.1505 | 16.6613 | 59.5794 | 2360552.3894 | 0 | 1484851.5171 | 0 | 0 | 0 | 1499310.9428 | 2084438.7912 | 5423282.1576 | 3701501.5099 | 16553937.3079 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 46962602.6173 | 109855004.3878 | 3162.2777 | 2.1292 | 22055.9932 | 51593.4189 | 449.6413 | 1051.8016
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.7313 | 6.4005 | 0.69966 | 4 | 17814.4623 | 40286.9237 | 363.1719 | 821.3034 | 103.7471 | 16.6237 | 66.4391 | 2782055.7313 | 0 | 1791842.1739 | 0 | 0 | 0 | 1705103.1692 | 2448810.419 | 6371302.3903 | 4348544.7985 | 19447658.6823 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 49856323.9917 | 112748725.7622 | 4216.965 | 2.7986 | 17814.4623 | 40286.9237 | 363.1719 | 821.3034
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.2159 | 8.0325 | 0.89946 | 4 | 14701.1305 | 32181.7161 | 299.7024 | 656.0678 | 104.0796 | 16.5375 | 73.77 | 3228514.1543 | 0 | 2127396.0053 | 0 | 0 | 0 | 1903325.468 | 2831101.8947 | 7365946.3913 | 5027409.7671 | 22483693.6807 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 52892358.9901 | 115784760.7605 | 5623.4133 | 3.5978 | 14701.1305 | 32181.7161 | 299.7024 | 656.0678
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.5166 | 9.8099 | 1.1263 | 4 | 12406.212 | 26365.7246 | 252.9174 | 537.501 | 104.1734 | 16.4022 | 73.1154 | 3676495.8469 | 0 | 2475948.5722 | 0 | 0 | 0 | 2076001.391 | 3209093.8659 | 8349403.9635 | 5698639.7682 | 25485583.4076 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 55894248.717 | 118786650.4874 | 7498.9421 | 4.5053 | 12406.212 | 26365.7246 | 252.9174 | 537.501
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.9561 | 11.6292 | 1.369 | 4 | 10714.3445 | 22199.425 | 218.4264 | 452.5653 | 104.0638 | 16.2248 | 70.5551 | 4099596.6114 | 0 | 2817804.1116 | 0 | 0 | 0 | 2207838.305 | 3558843.2209 | 9259380.0417 | 6319717.1397 | 28263179.4303 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 58671844.7397 | 121564246.5101 | 10000 | 5.476 | 10714.3445 | 22199.425 | 218.4264 | 452.5653
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.8381 | 13.3793 | 1.6127 | 4 | 9468.9237 | 19218.627 | 193.0368 | 391.7977 | 103.8028 | 16.0205 | 74.0451 | 4476323.2467 | 0 | 3134612.7584 | 0 | 0 | 0 | 2292196.2109 | 3862221.5642 | 10048708.2595 | 6858449.8674 | 30672511.9069 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 61081177.2163 | 123973578.9867 | 13335.2143 | 6.4507 | 9468.9237 | 19218.627 | 193.0368 | 391.7977
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5823 | 14.9637 | 1.8427 | 4 | 8553.1151 | 17085.5938 | 174.3668 | 348.3129 | 103.454 | 15.809 | 70.2327 | 4793588.8484 | 0 | 3412451.0315 | 0 | 0 | 0 | 2330987.7879 | 4109440.7905 | 10691921.9746 | 7297456.4447 | 32635846.8777 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 63044512.1871 | 125936913.9575 | 17782.7941 | 7.3709 | 8553.1151 | 17085.5938 | 174.3668 | 348.3129
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.9427 | 16.3365 | 2.0491 | 4 | 7879.5071 | 15552.72 | 160.6344 | 317.0632 | 103.0741 | 15.6063 | 78.8898 | 5051190.5789 | 0 | 3647028.2131 | 0 | 0 | 0 | 2335620.25 | 4303197.2264 | 11196036.4759 | 7641524.9503 | 34174597.6944 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 64583263.0038 | 127475664.7743 | 23713.7371 | 8.1964 | 7879.5071 | 15552.72 | 160.6344 | 317.0632
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8339 | 17.4781 | 2.2261 | 4 | 7383.2899 | 14446.2073 | 150.5184 | 294.5055 | 102.7069 | 15.4248 | 89.3555 | 5253548.6723 | 0 | 3838040.8533 | 0 | 0 | 0 | 2317396.5374 | 4449504.5645 | 11576698.158 | 7901334.3702 | 35336523.1556 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 65745188.465 | 128637590.2354 | 31622.7766 | 8.9046 | 7383.2899 | 14446.2073 | 150.5184 | 294.5055
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3781 | 18.4033 | 2.3732 | 4 | 7016.9054 | 13642.2997 | 143.0491 | 278.1167 | 102.3768 | 15.2694 | 91.116 | 5409860.5412 | 0 | 3990333.2207 | 0 | 0 | 0 | 2287646.4716 | 4558257.6911 | 11859651.485 | 8094455.8299 | 36200205.2395 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 66608870.5489 | 129501272.3193 | 42169.6503 | 9.4926 | 7016.9054 | 13642.2997 | 143.0491 | 278.1167
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.7413 | 19.1361 | 2.492 | 4 | 6745.686 | 13055.0932 | 137.5199 | 266.1457 | 102.0955 | 15.1411 | 92.5687 | 5528807.4517 | 0 | 4109383.1907 | 0 | 0 | 0 | 2253822.3227 | 4637885.0564 | 12066825.5557 | 8235856.3903 | 36832579.9676 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 67241245.277 | 130133647.0474 | 56234.1325 | 9.968 | 6745.686 | 13055.0932 | 137.5199 | 266.1457
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.1271 | 19.7077 | 2.5863 | 4 | 6544.4146 | 12623.9063 | 133.4167 | 257.3554 | 101.8641 | 15.0381 | 88.9929 | 5618639.5138 | 0 | 4201312.4929 | 0 | 0 | 0 | 2220834.0081 | 4695906.5458 | 12217785.5693 | 8338889.7014 | 37293367.8314 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 67702033.1408 | 130594434.9112 | 74989.4209 | 10.345 | 6544.4146 | 12623.9063 | 133.4167 | 257.3554
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7413 | 20.1505 | 2.66 | 4 | 6394.7233 | 12305.6038 | 130.3651 | 250.8664 | 101.6776 | 14.9564 | 85.1838 | 5686515.6216 | 0 | 4272031.2775 | 0 | 0 | 0 | 2191531.6901 | 4738530.6498 | 12328684.7445 | 8414580.6672 | 37631874.6507 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68040539.9601 | 130932941.7306 | 100000 | 10.6401 | 6394.7233 | 12305.6038 | 130.3651 | 250.8664
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.7339 | 20.4893 | 2.7171 | 4 | 6283.189 | 12070.0026 | 128.0913 | 246.0633 | 101.5308 | 14.8928 | 92.5304 | 5737382.3155 | 0 | 4325789.4924 | 0 | 0 | 0 | 2166520.1719 | 4769579.8721 | 12409468.452 | 8469717.2075 | 37878457.5115 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68287122.8209 | 131179524.5913 | 133352.1432 | 10.8682 | 6283.189 | 12070.0026 | 128.0913 | 246.0633
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.2419 | 20.7464 | 2.7608 | 4 | 6199.9622 | 11895.1577 | 126.3946 | 242.4989 | 101.4171 | 14.844 | 85.4796 | 5775377.9373 | 0 | 4366394.4077 | 0 | 0 | 0 | 2145857.4988 | 4792175.6391 | 12468258.0025 | 8509842.2838 | 38057905.7691 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68466571.0785 | 131358972.8489 | 177827.941 | 11.0431 | 6199.9622 | 11895.1577 | 126.3946 | 242.4989
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.3841 | 20.9414 | 2.7941 | 4 | 6137.7857 | 11765.0077 | 125.1271 | 239.8456 | 101.3295 | 14.8067 | 77.563 | 5803866.5036 | 0 | 4397102.2154 | 0 | 0 | 0 | 2129319.2516 | 4808812.3085 | 12511543.2038 | 8539385.3231 | 38190028.806 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68598694.1154 | 131491095.8858 | 237137.3706 | 11.1765 | 6137.7857 | 11765.0077 | 125.1271 | 239.8456
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.2512 | 21.0897 | 2.8195 | 4 | 6091.2931 | 11667.8748 | 124.1792 | 237.8654 | 101.2621 | 14.7781 | 90.5071 | 5825330.5057 | 0 | 4420391.7602 | 0 | 0 | 0 | 2116399.5471 | 4821227.5071 | 12543845.0037 | 8561431.9652 | 38288626.289 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68697291.5984 | 131589693.3689 | 316227.766 | 11.2779 | 6091.2931 | 11667.8748 | 124.1792 | 237.8654
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9091 | 21.2022 | 2.8387 | 4 | 6056.5041 | 11595.272 | 123.47 | 236.3853 | 101.2104 | 14.7562 | 93.5644 | 5841518.4522 | 0 | 4438045.9013 | 0 | 0 | 0 | 2106441.602 | 4830542.3226 | 12568080.2431 | 8577973.0141 | 38362601.5353 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68771266.8447 | 131663668.6151 | 421696.5034 | 11.3549 | 6056.5041 | 11595.272 | 123.47 | 236.3853
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.4085 | 21.2875 | 2.8533 | 4 | 6030.4586 | 11540.9316 | 122.9391 | 235.2775 | 101.1709 | 14.7396 | 103.1379 | 5853750.3461 | 0 | 4451437.5667 | 0 | 0 | 0 | 2098853.0954 | 4837575.9932 | 12586380.4111 | 8590463.2548 | 38418460.6675 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68827125.9769 | 131719527.7473 | 562341.3252 | 11.4132 | 6030.4586 | 11540.9316 | 122.9391 | 235.2775
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7787 | 21.351 | 2.8643 | 4 | 6010.9512 | 11500.3759 | 122.5414 | 234.4507 | 101.1415 | 14.7272 | 86.4608 | 5862789.1397 | 0 | 4461362.7497 | 0 | 0 | 0 | 2092936.8133 | 4842664.594 | 12599619.9066 | 8599499.4825 | 38458872.6858 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68867537.9952 | 131759939.7656 | 749894.2093 | 11.457 | 6010.9512 | 11500.3759 | 122.5414 | 234.4507
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.054 | 21.3982 | 2.8725 | 4 | 5996.3363 | 11470.0726 | 122.2434 | 233.8329 | 101.1195 | 14.718 | 96.8228 | 5869490.6628 | 0 | 4468737.7587 | 0 | 0 | 0 | 2088371.8172 | 4846374.0931 | 12609271.2621 | 8606086.731 | 38488332.3249 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68896997.6343 | 131789399.4047 | 1000000 | 11.4898 | 5996.3363 | 11470.0726 | 122.2434 | 233.8329
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2586 | 21.4334 | 2.8786 | 4 | 5985.3843 | 11447.4156 | 122.0202 | 233.3711 | 101.1031 | 14.7111 | 90.267 | 5874464.5504 | 0 | 4474220.5724 | 0 | 0 | 0 | 2084869.1209 | 4849086.1551 | 12616327.4911 | 8610902.7523 | 38509870.6422 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68918535.9516 | 131810937.7221 | 1333521.4322 | 11.5145 | 5985.3843 | 11447.4156 | 122.0202 | 233.3711
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4218 | 21.4613 | 2.8833 | 4 | 5977.1758 | 11430.2761 | 121.8528 | 233.0216 | 101.09 | 14.7056 | 96.2713 | 5878424.8731 | 0 | 4478591.2697 | 0 | 0 | 0 | 2082414.6216 | 4851377.9981 | 12622290.3967 | 8614972.5579 | 38528071.7171 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68936737.0265 | 131829138.7969 | 1778279.41 | 11.5333 | 5977.1758 | 11430.2761 | 121.8528 | 233.0216
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.5292 | 21.48 | 2.8867 | 4 | 5971.0227 | 11417.6965 | 121.7274 | 232.7652 | 101.0813 | 14.702 | 88.3644 | 5881028.4394 | 0 | 4481467.8232 | 0 | 0 | 0 | 2080256.2355 | 4852673.4743 | 12625660.9598 | 8617273.0365 | 38538359.9686 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68947025.278 | 131839427.0485 | 2371373.7057 | 11.5469 | 5971.0227 | 11417.6965 | 121.7274 | 232.7652
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.6265 | 21.4964 | 2.8894 | 4 | 5966.4099 | 11407.9782 | 121.6333 | 232.5671 | 101.0735 | 14.6987 | 94.762 | 5883384.51 | 0 | 4484072.0958 | 0 | 0 | 0 | 2078968.4221 | 4854105.7609 | 12629387.4758 | 8619816.4602 | 38549734.7247 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68958400.0341 | 131850801.8046 | 3162277.6602 | 11.5578 | 5966.4099 | 11407.9782 | 121.6333 | 232.5671
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.6996 | 21.5089 | 2.8915 | 4 | 5962.9515 | 11400.6904 | 121.5628 | 232.4185 | 101.0676 | 14.6962 | 92.9106 | 5885155.9909 | 0 | 4486031.3364 | 0 | 0 | 0 | 2078002.8365 | 4855184.1639 | 12632193.2592 | 8621731.465 | 38558299.0519 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68966964.3613 | 131859366.1317 | 4216965.0343 | 11.5659 | 5962.9515 | 11400.6904 | 121.5628 | 232.4185
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7339 | 21.5151 | 2.8928 | 4 | 5960.3585 | 11395.5862 | 121.51 | 232.3144 | 101.0648 | 14.6951 | 85.7175 | 5885983.9732 | 0 | 4486948.1071 | 0 | 0 | 0 | 2076858.7893 | 4855418.4391 | 12632802.7953 | 8622147.4859 | 38560159.5899 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68968824.8993 | 131861226.6697 | 5623413.2519 | 11.5713 | 5960.3585 | 11395.5862 | 121.51 | 232.3144
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7728 | 21.5217 | 2.8939 | 4 | 5958.4143 | 11391.5297 | 121.4703 | 232.2317 | 101.0617 | 14.6937 | 90.3086 | 5886924.9497 | 0 | 4487989.5429 | 0 | 0 | 0 | 2076266.9769 | 4855960.7731 | 12634213.8372 | 8623110.551 | 38564466.6309 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68973131.9403 | 131865533.7107 | 7498942.0933 | 11.5758 | 5958.4143 | 11391.5297 | 121.4703 | 232.2317
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.8117 | 21.5282 | 2.8949 | 4 | 5956.9565 | 11388.3193 | 121.4406 | 232.1663 | 101.0586 | 14.6924 | 93.861 | 5887866.3089 | 0 | 4489031.3356 | 0 | 0 | 0 | 2076019.2703 | 4856637.5968 | 12635974.7934 | 8624312.4398 | 38569841.7447 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 68978507.0541 | 131870908.8246 | 10000000 | 11.5795 | 5956.9565 | 11388.3193 | 121.4406 | 232.1663
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.3377 | [19 empty] | 100 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5733 | [19 empty] | 133.3521 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.037473 | 0.0030136 | 4 | 2672337.1472 | 7999883.057 | 54479.2073 | 163088.4368 | 59.3985 | 13.2985 | 25.8044 | 161449.9966 | 0 | 53510.8074 | 0 | 0 | 0 | 160231.4603 | 146324.983 | 380707.5905 | 259840.7533 | 1162065.5911 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 32213474.0378 | 96433949.3724 | 177.8279 | 0.012054 | 2672337.1472 | 7999883.057 | 54479.2073 | 163088.4368
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1297 | 0.076226 | 0.011646 | 4 | 716351.7517 | 2094970.8498 | 14603.7994 | 42708.8144 | 75.7683 | 14.9207 | 47.4115 | 315862.4499 | 0 | 139993.207 | 0 | 0 | 0 | 292724.079 | 291946.097 | 759583.8581 | 518431.591 | 2318541.2821 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 33369949.7288 | 97590425.0634 | 237.1374 | 0.046583 | 716351.7517 | 2094970.8498 | 14603.7994 | 42708.8144
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3749 | 0.2171 | 0.02434 | 4 | 351266.7864 | 1010878.4189 | 7161.0486 | 20608.1239 | 82.8436 | 15.5379 | 43.4294 | 432610.8147 | 0 | 207358.6514 | 0 | 0 | 0 | 376509.0123 | 396426.6066 | 1031420.712 | 703965.8295 | 3148291.6264 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 34199700.0731 | 98420175.4077 | 316.2278 | 0.097361 | 351266.7864 | 1010878.4189 | 7161.0486 | 20608.1239
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9406 | 0.41819 | 0.043127 | 4 | 203807.7926 | 576085.5612 | 4154.8975 | 11744.2834 | 88.39 | 15.9863 | 65.3162 | 568897.761 | 0 | 287788.6793 | 0 | 0 | 0 | 469274.5352 | 517124.7804 | 1345452.6017 | 918299.047 | 4106837.4045 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 35158245.8513 | 99378721.1858 | 421.6965 | 0.17251 | 203807.7926 | 576085.5612 | 4154.8975 | 11744.2834
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9239 | 0.69231 | 0.069685 | 4 | 130130.4455 | 360526.5818 | 2652.8851 | 7349.822 | 92.7729 | 16.3185 | 57.6435 | 728407.8446 | 0 | 384149.4553 | 0 | 0 | 0 | 573152.507 | 657426.8247 | 1710489.741 | 1167444.3953 | 5221070.7677 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 36272479.2144 | 100492954.549 | 562.3413 | 0.27874 | 130130.4455 | 360526.5818 | 2652.8851 | 7349.822
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.465 | 1.0588 | 0.10623 | 4 | 88451.2699 | 239582.6194 | 1803.1988 | 4884.2158 | 96.2622 | 16.5681 | 57.9979 | 916888.3169 | 0 | 500790.0722 | 0 | 0 | 0 | 692037.4185 | 822789.1649 | 2140728.6299 | 1461091.2775 | 6534324.8799 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 37585733.3266 | 101806208.6612 | 749.8942 | 0.42493 | 88451.2699 | 239582.6194 | 1803.1988 | 4884.2158
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7 | 1.5384 | 0.15558 | 4 | 62866.4416 | 166060.2811 | 1281.6174 | 3385.3634 | 99.0087 | 16.7528 | 52.8942 | 1138156.2896 | 0 | 641131.4311 | 0 | 0 | 0 | 826948.5544 | 1016432.1473 | 2644547.9483 | 1804958.3147 | 8072174.6854 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 39123583.1321 | 103344058.4667 | 1000 | 0.62233 | 62866.4416 | 166060.2811 | 1281.6174 | 3385.3634
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8313 | 2.1612 | 0.22135 | 4 | 46233.3029 | 118765.9817 | 942.5284 | 2421.2052 | 101.1653 | 16.8863 | 62.4057 | 1398877.3059 | 0 | 810677.5925 | 0 | 0 | 0 | 981525.2139 | 1244521.2438 | 3237988.9899 | 2209994.0197 | 9883584.3657 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 40934992.8124 | 105155468.147 | 1333.5214 | 0.8854 | 46233.3029 | 118765.9817 | 942.5284 | 2421.2052
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0176 | 2.953 | 0.30773 | 4 | 34957.3115 | 87129.9385 | 712.6521 | 1776.2616 | 102.8201 | 16.9748 | 49.9056 | 1701236.5198 | 0 | 1012349.7268 | 0 | 0 | 0 | 1153821.5411 | 1508289.0372 | 3924258.6821 | 2678387.186 | 11978342.6929 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 43029751.1396 | 107250226.4742 | 1778.2794 | 1.2309 | 34957.3115 | 87129.9385 | 712.6521 | 1776.2616
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5 | 3.9516 | 0.4197 | 4 | 27072.0196 | 65326.1193 | 551.8997 | 1331.7613 | 104.0722 | 17.0218 | 61.6152 | 2050857.4417 | 0 | 1251690.458 | 0 | 0 | 0 | 1345679.5204 | 1812808.6939 | 4716556.3632 | 3219146.6334 | 14396739.1107 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 45448147.5574 | 109668622.892 | 2371.3737 | 1.6788 | 27072.0196 | 65326.1193 | 551.8997 | 1331.7613
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.4 | 5.1789 | 0.56189 | 4 | 21430.6013 | 50004.0009 | 436.8918 | 1019.3992 | 104.9761 | 17.0261 | 63.6493 | 2445600.0587 | 0 | 1529370.1466 | 0 | 0 | 0 | 1550953.6966 | 2155110.3217 | 5607154.9832 | 3826998.4916 | 17115187.6985 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 48166596.1452 | 112387071.4798 | 3162.2777 | 2.2476 | 21430.6013 | 50004.0009 | 436.8918 | 1019.3992
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.7714 | 6.647 | 0.73779 | 4 | 17328.959 | 39090.1331 | 353.2743 | 796.9052 | 105.5785 | 16.9834 | 48.8531 | 2880077.3268 | 0 | 1844045.6833 | 0 | 0 | 0 | 1761925.8155 | 2529559.042 | 6581393.7434 | 4491936.464 | 20088938.0752 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 51140346.5219 | 115360821.8565 | 4216.965 | 2.9511 | 17328.959 | 39090.1331 | 353.2743 | 796.9052
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4144 | 8.3299 | 0.94714 | 4 | 14319.0462 | 31270.2546 | 291.9131 | 637.4864 | 105.9109 | 16.8909 | 62.1134 | 3338712.4947 | 0 | 2186874.1417 | 0 | 0 | 0 | 1963949.4344 | 2920919.0676 | 7599632.251 | 5186905.1682 | 23196992.5576 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 54248401.0043 | 118468876.3389 | 5623.4133 | 3.7885 | 14319.0462 | 31270.2546 | 291.9131 | 637.4864
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8318 | 10.1545 | 1.1839 | 4 | 12100.8975 | 25662.0714 | 246.6932 | 523.156 | 105.9993 | 16.748 | 63.4741 | 3796785.1682 | 0 | 2541435.7832 | 0 | 0 | 0 | 2138244.3457 | 3305821.4659 | 8601069.3369 | 5870406.5568 | 26253762.6566 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 57305171.1033 | 121525646.4379 | 7498.9421 | 4.7356 | 12100.8975 | 25662.0714 | 246.6932 | 523.156
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.3593 | 12.0173 | 1.4362 | 4 | 10466.2043 | 21645.0674 | 213.3677 | 441.264 | 105.881 | 16.5624 | 57.7399 | 4228327.7468 | 0 | 2888413.5675 | 0 | 0 | 0 | 2270599.4888 | 3661062.9132 | 9525334.7129 | 6501236.6676 | 29074975.0968 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 60126383.5436 | 124346858.8782 | 10000 | 5.7448 | 10466.2043 | 21645.0674 | 213.3677 | 441.264
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.2413 | 13.7963 | 1.6881 | 4 | 9263.2504 | 18773.7327 | 188.8439 | 382.7279 | 105.6116 | 16.3508 | 63.5952 | 4609721.6406 | 0 | 3207648.94 | 0 | 0 | 0 | 2352803.8611 | 3966368.0323 | 10319676.006 | 7043390.9222 | 31499609.4022 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 62551017.849 | 126771493.1835 | 13335.2143 | 6.7526 | 9263.2504 | 18773.7327 | 188.8439 | 382.7279
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9823 | 15.406 | 1.9253 | 4 | 8378.8425 | 16717.7282 | 170.814 | 340.8135 | 105.2548 | 16.1326 | 91.4313 | 4930916.5352 | 0 | 3487635.6797 | 0 | 0 | 0 | 2389987.1919 | 4215330.3686 | 10967424.936 | 7485492.8769 | 33476787.5884 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 64528196.0351 | 128748671.3697 | 17782.7941 | 7.7013 | 8378.8425 | 16717.7282 | 170.814 | 340.8135
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2844 | 16.7921 | 2.1371 | 4 | 7728.3755 | 15241.0072 | 157.5534 | 310.7085 | 104.8703 | 15.9253 | 93.3908 | 5190079.2627 | 0 | 3722539.1712 | 0 | 0 | 0 | 2392015.2097 | 4408807.121 | 11470811.7582 | 7829064.7266 | 35013317.2495 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 66064725.6963 | 130285201.0308 | 23713.7371 | 8.5483 | 7728.3755 | 15241.0072 | 157.5534 | 310.7085
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1445 | 17.9471 | 2.3186 | 4 | 7249.1932 | 14173.8016 | 147.7846 | 288.9521 | 104.4987 | 15.7395 | 79.8199 | 5394262.2166 | 0 | 3914352.7882 | 0 | 0 | 0 | 2372489.8739 | 4555630.9027 | 11852817.1204 | 8089791.2357 | 36179344.1376 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 67230752.5843 | 131451227.9189 | 31622.7766 | 9.2742 | 7249.1932 | 14173.8016 | 147.7846 | 288.9521
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.6233 | 18.8769 | 2.4686 | 4 | 6895.3588 | 13399.0109 | 140.5712 | 273.157 | 104.1676 | 15.5817 | 85.4715 | 5550894.8752 | 0 | 4066198.1916 | 0 | 0 | 0 | 2340915.2215 | 4663623.2324 | 12133791.0101 | 8281561.6889 | 37036984.2198 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 68088392.6665 | 132308868.0011 | 42169.6503 | 9.8745 | 6895.3588 | 13399.0109 | 140.5712 | 273.157
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9493 | 19.6154 | 2.5899 | 4 | 6633.404 | 12832.4365 | 135.2309 | 261.6066 | 103.8849 | 15.4513 | 92.1118 | 5670536.7345 | 0 | 4185317.1213 | 0 | 0 | 0 | 2306227.5703 | 4743211.7562 | 12340864.023 | 8422893.2751 | 37669050.4803 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 68720458.9271 | 132940934.2617 | 56234.1325 | 10.3598 | 6633.404 | 12832.4365 | 135.2309 | 261.6066
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3038 | 20.191 | 2.686 | 4 | 6438.9886 | 12416.2913 | 131.2675 | 253.1229 | 103.6526 | 15.3466 | 100.6257 | 5760852.9592 | 0 | 4277240.8821 | 0 | 0 | 0 | 2272634.1698 | 4801183.9243 | 12491695.7128 | 8525839.0027 | 38129446.6509 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 69180855.0976 | 133401330.4322 | 74989.4209 | 10.7441 | 6438.9886 | 12416.2913 | 131.2675 | 253.1229
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.8667 | 20.6328 | 2.7609 | 4 | 6294.3837 | 12109.5294 | 128.3195 | 246.8691 | 103.4675 | 15.2645 | 81.0112 | 5828405.8063 | 0 | 4347224.4836 | 0 | 0 | 0 | 2242341.0561 | 4843008.8249 | 12600515.5248 | 8600110.7603 | 38461606.456 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 69513014.9027 | 133733490.2373 | 100000 | 11.0437 | 6294.3837 | 12109.5294 | 128.3195 | 246.8691
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8398 | 20.9737 | 2.819 | 4 | 6186.6313 | 11882.0213 | 126.1228 | 242.2311 | 103.3205 | 15.2001 | 86.2695 | 5879556.7675 | 0 | 4400964.3355 | 0 | 0 | 0 | 2217079.8707 | 4874064.3798 | 12681315.708 | 8655258.5457 | 38708239.6072 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 69759648.054 | 133980123.3885 | 133352.1432 | 11.2759 | 6186.6313 | 11882.0213 | 126.1228 | 242.2311
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.3427 | 21.2338 | 2.8635 | 4 | 6106.2217 | 11712.9742 | 124.4836 | 238.7848 | 103.2059 | 15.1503 | 94.6641 | 5918016.5868 | 0 | 4441818.978 | 0 | 0 | 0 | 2196466.3146 | 4896957.733 | 12740879.5171 | 8695912.0693 | 38890051.1987 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 69941459.6455 | 134161934.9801 | 177827.941 | 11.4541 | 6106.2217 | 11712.9742 | 124.4836 | 238.7848
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4681 | 21.4293 | 2.8974 | 4 | 6046.147 | 11587.3598 | 123.2589 | 236.224 | 103.1186 | 15.1126 | 92.7539 | 5946529.2305 | 0 | 4472366.4324 | 0 | 0 | 0 | 2179703.2224 | 4913453.5653 | 12783798.2889 | 8725205.013 | 39021055.7525 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70072464.1992 | 134292939.5338 | 237137.3706 | 11.5896 | 6046.147 | 11587.3598 | 123.2589 | 236.224
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3307 | 21.579 | 2.9232 | 4 | 6001.2245 | 11493.4561 | 122.3431 | 234.3096 | 103.0508 | 15.0835 | 94.2496 | 5968217.9453 | 0 | 4495755.0039 | 0 | 0 | 0 | 2166798.5491 | 4926000.8843 | 12816443.8392 | 8747486.2719 | 39120702.4936 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70172110.9404 | 134392586.2749 | 316227.766 | 11.693 | 6001.2245 | 11493.4561 | 122.3431 | 234.3096
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.9808 | 21.692 | 2.9428 | 4 | 5967.6093 | 11423.3369 | 121.6578 | 232.8802 | 102.9992 | 15.0614 | 94.9847 | 5984470.0933 | 0 | 4513369.3798 | 0 | 0 | 0 | 2156768.8634 | 4935297.2512 | 12840631.079 | 8763994.56 | 39194531.2268 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70245939.6735 | 134466415.0081 | 421696.5034 | 11.7712 | 5967.6093 | 11423.3369 | 121.6578 | 232.8802
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4561 | 21.775 | 2.9574 | 4 | 5942.4421 | 11371.1691 | 121.1447 | 231.8167 | 102.9612 | 15.0451 | 88.438 | 5996298.2316 | 0 | 4526237.9793 | 0 | 0 | 0 | 2148750.0607 | 4941801.6459 | 12857554.1798 | 8775544.924 | 39246187.0214 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70297595.4681 | 134518070.8027 | 562341.3252 | 11.8297 | 5942.4421 | 11371.1691 | 121.1447 | 231.8167
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.8265 | 21.8394 | 2.9686 | 4 | 5923.5923 | 11331.9154 | 120.7604 | 231.0164 | 102.9314 | 15.0325 | 83.9603 | 6005488.1128 | 0 | 4536264.3993 | 0 | 0 | 0 | 2142894.4647 | 4947012.321 | 12871111.2874 | 8784797.9285 | 39287568.5136 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70338976.9604 | 134559452.2949 | 749894.2093 | 11.8744 | 5923.5923 | 11331.9154 | 120.7604 | 231.0164
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1017 | 21.8874 | 2.977 | 4 | 5909.4698 | 11302.5871 | 120.4725 | 230.4185 | 102.9092 | 15.023 | 90.0707 | 6012298.5122 | 0 | 4543711.1717 | 0 | 0 | 0 | 2138372.0645 | 4950808.8819 | 12880989.1602 | 8791539.7797 | 39317719.5702 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70369128.0169 | 134589603.3515 | 1000000 | 11.9079 | 5909.4698 | 11302.5871 | 120.4725 | 230.4185
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3038 | 21.9227 | 2.9832 | 4 | 5898.8868 | 11280.7039 | 120.2568 | 229.9724 | 102.8928 | 15.0161 | 101.1802 | 6017288.8487 | 0 | 4549176.8777 | 0 | 0 | 0 | 2134847.1759 | 4953512.0319 | 12888022.2019 | 8796339.9752 | 39339187.1113 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70390595.5581 | 134611070.8926 | 1333521.4322 | 11.9329 | 5898.8868 | 11280.7039 | 120.2568 | 229.9724
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.4501 | 21.9484 | 2.9879 | 4 | 5890.9547 | 11264.4025 | 120.0951 | 229.6401 | 102.881 | 15.011 | 91.9092 | 6020897.1815 | 0 | 4553133.8547 | 0 | 0 | 0 | 2132071.7207 | 4955380.0752 | 12892882.4674 | 8799657.2063 | 39354022.5058 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70405430.9525 | 134625906.2871 | 1778279.41 | 11.9514 | 5890.9547 | 11264.4025 | 120.0951 | 229.6401
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5692 | 21.9691 | 2.9914 | 4 | 5885.0088 | 11252.0283 | 119.9739 | 229.3878 | 102.8713 | 15.0069 | 83.0518 | 6023832.2314 | 0 | 4556355.0555 | 0 | 0 | 0 | 2130170.7718 | 4957039.6429 | 12897200.3223 | 8802604.2309 | 39367202.2549 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70418610.7016 | 134639086.0362 | 2371373.7057 | 11.9658 | 5885.0088 | 11252.0283 | 119.9739 | 229.3878
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6593 | 21.9848 | 2.9941 | 4 | 5880.5512 | 11242.7437 | 119.883 | 229.1985 | 102.864 | 15.0038 | 96.3078 | 6026048.2685 | 0 | 4558788.8672 | 0 | 0 | 0 | 2128751.3648 | 4958299.5152 | 12900478.2514 | 8804841.4849 | 39377207.752 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70428616.1988 | 134649091.5333 | 3162277.6602 | 11.9765 | 5880.5512 | 11242.7437 | 119.883 | 229.1985
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7324 | 21.9974 | 2.9962 | 4 | 5877.2093 | 11235.6883 | 119.8149 | 229.0547 | 102.858 | 15.0013 | 91.6858 | 6027848.7922 | 0 | 4560767.2334 | 0 | 0 | 0 | 2127799.2429 | 4959401.9547 | 12903346.5729 | 8806799.1733 | 39385962.9694 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70437371.4161 | 134657846.7507 | 4216965.0343 | 11.9848 | 5877.2093 | 11235.6883 | 119.8149 | 229.0547
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7667 | 22.0037 | 2.9976 | 4 | 5874.7036 | 11230.7507 | 119.7638 | 228.954 | 102.8552 | 15.0001 | 85.3251 | 6028690.3431 | 0 | 4561692.9519 | 0 | 0 | 0 | 2126658.1486 | 4959646.163 | 12903981.9528 | 8807232.8331 | 39387902.3924 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70439310.8392 | 134659786.1737 | 5623413.2519 | 11.9903 | 5874.7036 | 11230.7507 | 119.7638 | 228.954
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8056 | 22.0104 | 2.9987 | 4 | 5872.8249 | 11226.824 | 119.7255 | 228.874 | 102.852 | 14.9987 | 88.3036 | 6029646.749 | 0 | 4562744.5556 | 0 | 0 | 0 | 2126073.1558 | 4960201.1395 | 12905425.8879 | 8808218.3485 | 39392309.8363 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70443718.283 | 134664193.6176 | 7498942.0933 | 11.9949 | 5872.8249 | 11226.824 | 119.7255 | 228.874
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8445 | 22.017 | 2.9997 | 4 | 5871.4161 | 11223.7145 | 119.6968 | 228.8106 | 102.8489 | 14.9974 | 93.0725 | 6030603.549 | 0 | 4563796.5217 | 0 | 0 | 0 | 2125833.9573 | 4960891.2709 | 12907221.4682 | 8809443.8689 | 39397790.636 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 70449199.0828 | 134669674.4173 | 10000000 | 11.9987 | 5871.4161 | 11223.7145 | 119.6968 | 228.8106
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6887 | [19 empty] | 100 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4908 | [19 empty] | 133.3521 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.038782 | 0.0031202 | 4 | 2633742.5182 | 7886780.8452 | 53692.4036 | 160782.6952 | 59.6719 | 13.546 | 26.0419 | 163120.3236 | 0 | 53282.4945 | 0 | 0 | 0 | 161771.5427 | 147488.0007 | 383733.5239 | 261906.015 | 1171301.9004 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 32871313.5753 | 98433633.6876 | 177.8279 | 0.012481 | 2633742.5182 | 7886780.8452 | 53692.4036 | 160782.6952
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.08216 | 0.012431 | 4 | 685902.8824 | 2004393.9084 | 13983.058 | 40862.281 | 77.0611 | 15.2686 | 46.4825 | 328126.2388 | 0 | 145138.9783 | 0 | 0 | 0 | 303775.8458 | 303046.0146 | 788463.5666 | 538142.5855 | 2406693.2296 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 34106704.9045 | 99669025.0168 | 237.1374 | 0.049725 | 685902.8824 | 2004393.9084 | 13983.058 | 40862.281
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4844 | 0.22837 | 0.025872 | 4 | 337816.446 | 971348.235 | 6886.8452 | 19802.2476 | 84.2323 | 15.8903 | 61.1292 | 448469.135 | 0 | 214181.8835 | 0 | 0 | 0 | 389767.5922 | 410443.2581 | 1067889.1642 | 728856.2975 | 3259607.3305 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 34959619.0054 | 100521939.1177 | 316.2278 | 0.10349 | 337816.446 | 971348.235 | 6886.8452 | 19802.2476
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0844 | 0.43717 | 0.045736 | 4 | 196496.2836 | 554868.3384 | 4005.8425 | 11311.7416 | 89.8803 | 16.3439 | 69.4679 | 589339.4799 | 0 | 296826.8011 | 0 | 0 | 0 | 485361.8729 | 534895.98 | 1391689.6177 | 949856.7604 | 4247970.5119 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 35947982.1868 | 101510302.2991 | 421.6965 | 0.18294 | 196496.2836 | 554868.3384 | 4005.8425 | 11311.7416
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1332 | 0.72419 | 0.073823 | 4 | 125679.2684 | 347706.1538 | 2562.1419 | 7088.4603 | 94.3866 | 16.683 | 57.7659 | 755978.2092 | 0 | 396902.582 | 0 | 0 | 0 | 594415.6291 | 681445.6039 | 1772981.6777 | 1210096.4262 | 5411820.1282 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 37111831.8031 | 102674151.9154 | 562.3413 | 0.29529 | 125679.2684 | 347706.1538 | 2562.1419 | 7088.4603
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7324 | 1.1049 | 0.11242 | 4 | 85540.2778 | 231334.1781 | 1743.8543 | 4716.0601 | 97.9344 | 16.9345 | 54.1152 | 950912.134 | 0 | 516831.5087 | 0 | 0 | 0 | 717014.1724 | 852055.5479 | 2216873.755 | 1513061.89 | 6766749.008 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 38466760.6829 | 104029080.7952 | 749.8942 | 0.44969 | 85540.2778 | 231334.1781 | 1743.8543 | 4716.0601
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0628 | 1.6057 | 0.16456 | 4 | 60866.6406 | 160466.4604 | 1240.8488 | 3271.3258 | 100.7438 | 17.1216 | 61.8077 | 1181220.3683 | 0 | 662054.1048 | 0 | 0 | 0 | 857797.8543 | 1053418.2077 | 2740778.0905 | 1870637.3642 | 8365905.9897 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 40065917.6646 | 105628237.7769 | 1000 | 0.65826 | 60866.6406 | 160466.4604 | 1240.8488 | 3271.3258
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.277 | 2.2508 | 0.23393 | 4 | 44808.9883 | 114875.6679 | 913.4918 | 2341.8959 | 102.9299 | 17.2552 | 66.4329 | 1450137.87 | 0 | 835907.91 | 0 | 0 | 0 | 1016348.372 | 1287933.7193 | 3350939.346 | 2287084.9586 | 10228352.1757 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 41928363.8507 | 107490683.9629 | 1333.5214 | 0.93571 | 44808.9883 | 114875.6679 | 913.4918 | 2341.8959
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5977 | 3.0751 | 0.32507 | 4 | 33914.3245 | 84336.1104 | 691.3894 | 1719.3057 | 104.6181 | 17.3435 | 59.5709 | 1763846.342 | 0 | 1043926.8476 | 0 | 0 | 0 | 1195136.2691 | 1561134.6889 | 4061752.2277 | 2772229.3561 | 12398025.7312 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 44098037.4062 | 109660357.5184 | 1778.2794 | 1.3003 | 33914.3245 | 84336.1104 | 691.3894 | 1719.3057
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2138 | 4.1098 | 0.443 | 4 | 26290.9974 | 63290.4056 | 535.9775 | 1290.2605 | 105.8887 | 17.3888 | 57.9784 | 2124743.0057 | 0 | 1289558.1693 | 0 | 0 | 0 | 1392275.611 | 1874564.9465 | 4877233.4647 | 3328812.0568 | 14887187.2541 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 46587198.929 | 112149519.0413 | 2371.3737 | 1.772 | 26290.9974 | 63290.4056 | 535.9775 | 1290.2605
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.277 | 5.3815 | 0.5926 | 4 | 20834.6391 | 48493.4858 | 424.7423 | 988.6053 | 106.8059 | 17.3901 | 72.7997 | 2532288.1911 | 0 | 1574611.6629 | 0 | 0 | 0 | 1603403.7291 | 2227018.3974 | 5794245.0458 | 3954691.3036 | 17686258.3299 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 49386270.0048 | 114948590.1171 | 3162.2777 | 2.3704 | 20834.6391 | 48493.4858 | 424.7423 | 988.6053
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.8191 | 6.8993 | 0.77728 | 4 | 16866.6384 | 37953.7957 | 343.8492 | 773.7395 | 107.4144 | 17.3426 | 47.3335 | 2979824.3313 | 0 | 1896958.6446 | 0 | 0 | 0 | 1819551.2822 | 2611570.3607 | 6794770.3718 | 4637570.3973 | 20740245.388 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 52440257.0629 | 118002577.1752 | 4216.965 | 3.1091 | 16866.6384 | 37953.7957 | 343.8492 | 773.7395
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.6077 | 8.632 | 0.99635 | 4 | 13954.8855 | 30405.4599 | 284.4892 | 619.8564 | 107.7462 | 17.2437 | 64.3514 | 3450184.8587 | 0 | 2246692.8447 | 0 | 0 | 0 | 2024788.8046 | 3011449.9381 | 7835175.0057 | 5347667.9381 | 23915959.39 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 55615971.065 | 121178291.1772 | 5623.4133 | 3.9854 | 13954.8855 | 30405.4599 | 284.4892 | 619.8564
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.1398 | 10.5041 | 1.2432 | 4 | 11809.6118 | 24993.6848 | 240.7549 | 509.5301 | 107.8291 | 17.0931 | 68.8645 | 3918348.6659 | 0 | 2607245.3139 | 0 | 0 | 0 | 2200630.2519 | 3403227.4504 | 8854499.728 | 6043378.0061 | 27027329.4162 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 58727341.0911 | 124289661.2034 | 7498.9421 | 4.9728 | 11809.6118 | 24993.6848 | 240.7549 | 509.5301
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.7212 | 12.4057 | 1.505 | 4 | 10229.1772 | 21119.585 | 208.5356 | 430.5513 | 107.7026 | 16.8995 | 68.5578 | 4357125.6014 | 0 | 2958354.6713 | 0 | 0 | 0 | 2332284.7761 | 3762628.3691 | 9789587.1951 | 6681594.4165 | 29881575.0295 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 61581586.7044 | 127143906.8167 | 10000 | 6.0202 | 10229.1772 | 21119.585 | 208.5356 | 430.5513
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.6413 | 14.2194 | 1.7657 | 4 | 9066.5069 | 18349.5168 | 184.833 | 374.0797 | 107.424 | 16.68 | 87.6499 | 4744532.205 | 0 | 3281141.821 | 0 | 0 | 0 | 2413648.9894 | 4071335.9761 | 10592781.0638 | 7229790.736 | 32333230.7914 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 64033242.4663 | 129595562.5786 | 13335.2143 | 7.0626 | 9066.5069 | 18349.5168 | 184.833 | 374.0797
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.364 | 15.8523 | 2.0099 | 4 | 8211.8738 | 16366.8543 | 167.4102 | 333.6605 | 107.0598 | 16.4552 | 83.6713 | 5069124.451 | 0 | 3562832.7076 | 0 | 0 | 0 | 2448731.8846 | 4321468.7268 | 11243575.1721 | 7673971.0873 | 34319704.0294 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 66019715.7044 | 131582035.8166 | 17782.7941 | 8.0395 | 8211.8738 | 16366.8543 | 167.4102 | 333.6605
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6339 | 17.2553 | 2.2273 | 4 | 7583.3448 | 14942.38 | 154.5967 | 304.6206 | 106.6696 | 16.2427 | 90.6852 | 5330593.9538 | 0 | 3798769.5615 | 0 | 0 | 0 | 2448862.6867 | 4515508.2187 | 11748426.1271 | 8018542.2377 | 35860702.7855 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 67560714.4604 | 133123034.5726 | 23713.7371 | 8.9091 | 7583.3448 | 14942.38 | 154.5967 | 304.6206
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.4233 | 18.4175 | 2.4128 | 4 | 7120.311 | 13913.4433 | 145.1572 | 283.6444 | 106.2959 | 16.0537 | 86.5007 | 5535361.6439 | 0 | 3990241.938 | 0 | 0 | 0 | 2426920.1187 | 4661484.2432 | 12128225.799 | 8277763.318 | 37019997.0609 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 68720008.7358 | 134282328.8481 | 31622.7766 | 9.6513 | 7120.311 | 13913.4433 | 145.1572 | 283.6444
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8607 | 19.3554 | 2.5662 | 4 | 6778.3746 | 13165.5931 | 138.1863 | 268.3984 | 105.9626 | 15.8929 | 82.0658 | 5692956.4128 | 0 | 4142276.2066 | 0 | 0 | 0 | 2394109.3221 | 4769443.3572 | 12409113.268 | 8469474.7872 | 37877373.3538 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 69577385.0287 | 135139705.1409 | 42169.6503 | 10.2646 | 6778.3746 | 13165.5931 | 138.1863 | 268.3984
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1332 | 20.0969 | 2.6898 | 4 | 6525.2039 | 12618.9127 | 133.0251 | 257.2536 | 105.6796 | 15.7608 | 94.7767 | 5812797.0205 | 0 | 4260984.5418 | 0 | 0 | 0 | 2358126.3206 | 4848444.0743 | 12614656.9288 | 8609762.5592 | 38504771.4453 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 70204783.1202 | 135767103.2325 | 56234.1325 | 10.759 | 6525.2039 | 12618.9127 | 133.0251 | 257.2536
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4512 | 20.6755 | 2.7876 | 4 | 6337.2899 | 12217.1021 | 129.1942 | 249.0622 | 105.4471 | 15.6547 | 86.1261 | 5903437.19 | 0 | 4352744.3643 | 0 | 0 | 0 | 2323793.4712 | 4906190.2599 | 12764900.6583 | 8712306.9918 | 38963372.9354 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 70663384.6104 | 136225704.7226 | 74989.4209 | 11.1504 | 6337.2899 | 12217.1021 | 129.1942 | 249.0622
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0117 | 21.1235 | 2.8641 | 4 | 6197.5088 | 11920.3235 | 126.3446 | 243.0119 | 105.26 | 15.5707 | 88.1298 | 5971928.3425 | 0 | 4423311.2622 | 0 | 0 | 0 | 2293598.4489 | 4948646.8409 | 12875363.973 | 8787700.4738 | 39300549.3414 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71000561.0163 | 136562881.1286 | 100000 | 11.4563 | 6197.5088 | 11920.3235 | 126.3446 | 243.0119
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.9406 | 21.4627 | 2.9229 | 4 | 6093.3434 | 11700.9674 | 124.221 | 238.54 | 105.1146 | 15.5062 | 91.5907 | 6022685.4688 | 0 | 4476338.3484 | 0 | 0 | 0 | 2267501.2013 | 4978944.7572 | 12954192.9363 | 8841502.861 | 39541165.573 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71241177.2479 | 136803497.3602 | 133352.1432 | 11.6916 | 6093.3434 | 11700.9674 | 124.221 | 238.54
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4144 | 21.7223 | 2.9681 | 4 | 6015.6061 | 11537.8538 | 122.6363 | 235.2148 | 105.0009 | 15.4562 | 91.0356 | 6060978.466 | 0 | 4516777.8155 | 0 | 0 | 0 | 2246397.3534 | 5001419.9176 | 13012668.6933 | 8881413.7668 | 39719656.0126 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71419667.6876 | 136981987.7998 | 177827.941 | 11.8724 | 6015.6061 | 11537.8538 | 122.6363 | 235.2148
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5398 | 21.9206 | 3.0026 | 4 | 5957.5254 | 11416.2384 | 121.4522 | 232.7355 | 104.9126 | 15.4176 | 88.6449 | 6089934.7723 | 0 | 4547615.1606 | 0 | 0 | 0 | 2229764.0934 | 5018252.4703 | 13056463.5425 | 8911304.6513 | 39853334.6905 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71553346.3654 | 137115666.4777 | 237137.3706 | 12.0106 | 5957.5254 | 11416.2384 | 121.4522 | 232.7355
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.3855 | 22.07 | 3.0288 | 4 | 5914.0923 | 11325.6098 | 120.5668 | 230.8879 | 104.8454 | 15.3884 | 74.7688 | 6111531.6551 | 0 | 4570764.5539 | 0 | 0 | 0 | 2216605.4141 | 5030571.633 | 13088515.477 | 8933180.7552 | 39951169.4883 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71651181.1632 | 137213501.2755 | 316227.766 | 12.1153 | 5914.0923 | 11325.6098 | 120.5668 | 230.8879
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.024 | 22.1828 | 3.0487 | 4 | 5881.5908 | 11257.9113 | 119.9042 | 229.5078 | 104.7942 | 15.3662 | 88.0659 | 6127742.8093 | 0 | 4588226.9468 | 0 | 0 | 0 | 2206414.3588 | 5039729.8048 | 13112343.1613 | 8949443.6393 | 40023900.7202 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71723912.3952 | 137286232.5074 | 421696.5034 | 12.1946 | 5881.5908 | 11257.9113 | 119.9042 | 229.5078
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5085 | 22.2684 | 3.0637 | 4 | 5857.257 | 11207.2358 | 119.4081 | 228.4747 | 104.7551 | 15.3493 | 94.7551 | 6139992.8898 | 0 | 4601472.1645 | 0 | 0 | 0 | 2198658.0917 | 5046648.027 | 13130342.9563 | 8961728.8692 | 40078842.9986 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71778854.6735 | 137341174.7858 | 562341.3252 | 12.2547 | 5857.257 | 11207.2358 | 119.4081 | 228.4747
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8593 | 22.3308 | 3.0749 | 4 | 5839.031 | 11169.5543 | 119.0365 | 227.7065 | 104.7266 | 15.337 | 78.1959 | 6148832.7122 | 0 | 4611057.5826 | 0 | 0 | 0 | 2192441.0479 | 5051409.2236 | 13142730.6134 | 8970183.6997 | 40116654.8794 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71816666.5544 | 137378986.6666 | 749894.2093 | 12.2994 | 5839.031 | 11169.5543 | 119.0365 | 227.7065
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.1345 | 22.3794 | 3.0834 | 4 | 5825.3758 | 11141.1505 | 118.7582 | 227.1274 | 104.7041 | 15.3274 | 88.0431 | 6155751.8301 | 0 | 4618575.7938 | 0 | 0 | 0 | 2187960.3869 | 5055292.3242 | 13152833.6447 | 8977079.2262 | 40147493.206 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71847504.8809 | 137409824.9932 | 1000000 | 12.3335 | 5825.3758 | 11141.1505 | 118.7582 | 227.1274
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3346 | 22.4149 | 3.0897 | 4 | 5815.1427 | 11119.9915 | 118.5495 | 226.6961 | 104.6878 | 15.3203 | 85.6137 | 6160770.8548 | 0 | 4624038.4763 | 0 | 0 | 0 | 2184422.9294 | 5058000.5816 | 13159879.9748 | 8981888.4913 | 40169001.3083 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71869012.9832 | 137431333.0955 | 1333521.4322 | 12.3589 | 5815.1427 | 11119.9915 | 118.5495 | 226.6961
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4829 | 22.4413 | 3.0945 | 4 | 5807.4729 | 11104.171 | 118.3932 | 226.3735 | 104.6756 | 15.3151 | 91.6051 | 6164487.8541 | 0 | 4628088.9297 | 0 | 0 | 0 | 2181711.2373 | 5059972.3282 | 13165010.055 | 8985389.8764 | 40184660.2807 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71884671.9556 | 137446992.0679 | 1778279.41 | 12.378 | 5807.4729 | 11104.171 | 118.3932 | 226.3735
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.6 | 22.462 | 3.0981 | 4 | 5801.7236 | 11092.2199 | 118.276 | 226.1299 | 104.666 | 15.311 | 92.2124 | 6167418.9052 | 0 | 4631285.5996 | 0 | 0 | 0 | 2179786.8238 | 5061611.6182 | 13169275.1511 | 8988300.8922 | 40197678.9901 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71897690.665 | 137460010.7773 | 2371373.7057 | 12.3925 | 5801.7236 | 11092.2199 | 118.276 | 226.1299
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.6876 | 22.4775 | 3.1008 | 4 | 5797.4135 | 11083.2676 | 118.1881 | 225.9474 | 104.6588 | 15.3079 | 89.4434 | 6169609.5232 | 0 | 4633676.4232 | 0 | 0 | 0 | 2178331.185 | 5062830.6812 | 13172446.9032 | 8990465.6782 | 40207360.394 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71907372.069 | 137469692.1812 | 3162277.6602 | 12.4034 | 5797.4135 | 11083.2676 | 118.1881 | 225.9474
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7607 | 22.4903 | 3.103 | 4 | 5794.182 | 11076.4328 | 118.1222 | 225.8081 | 104.6528 | 15.3053 | 86.4696 | 6171438.9033 | 0 | 4635673.8079 | 0 | 0 | 0 | 2177392.1278 | 5063956.8872 | 13175377.0601 | 8992465.5704 | 40216304.3566 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71916316.0315 | 137478636.1438 | 4216965.0343 | 12.4118 | 5794.182 | 11076.4328 | 118.1222 | 225.8081
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7996 | 22.4974 | 3.1044 | 4 | 5791.7592 | 11071.5758 | 118.0728 | 225.709 | 104.6496 | 15.3039 | 90.7465 | 6172409.9677 | 0 | 4636735.0152 | 0 | 0 | 0 | 2176350.7262 | 5064343.3265 | 13176382.4959 | 8993151.801 | 40219373.3325 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71919385.0074 | 137481705.1196 | 5623413.2519 | 12.4175 | 5791.7592 | 11071.5758 | 118.0728 | 225.709
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8339 | 22.5036 | 3.1055 | 4 | 5789.9425 | 11067.8496 | 118.0358 | 225.6331 | 104.6467 | 15.3027 | 82.9988 | 6173265.6713 | 0 | 4637670.1386 | 0 | 0 | 0 | 2175675.3123 | 5064778.3376 | 13177514.3057 | 8993924.2845 | 40222828.0499 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71922839.7249 | 137485159.8371 | 7498942.0933 | 12.422 | 5789.9425 | 11067.8496 | 118.0358 | 225.6331
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8682 | 22.5095 | 3.1064 | 4 | 5788.5803 | 11064.9131 | 118.008 | 225.5732 | 104.6439 | 15.3015 | 79.1873 | 6174121.8464 | 0 | 4638605.6388 | 0 | 0 | 0 | 2175347.4933 | 5065349.2416 | 13178999.6807 | 8994938.0834 | 40227361.9843 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 71927373.6592 | 137489693.7715 | 10000000 | 12.4257 | 5788.5803 | 11064.9131 | 118.008 | 225.5732
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6693 | [19 empty] | 100 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8966 | [19 empty] | 133.3521 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.040082 | 0.0032219 | 4 | 2602129.369 | 7794602.1311 | 53047.9268 | 158903.5074 | 59.9357 | 13.7924 | 23.9296 | 164764.6769 | 0 | 53050.042 | 0 | 0 | 0 | 163309.6668 | 148638.5104 | 386726.9142 | 263949.0654 | 1180438.8758 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 33534913.8698 | 100452849.9733 | 177.8279 | 0.012887 | 2602129.369 | 7794602.1311 | 53047.9268 | 158903.5074
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3077 | 0.08883 | 0.013259 | 4 | 657212.1121 | 1918944.6249 | 13398.1579 | 39120.2817 | 78.4057 | 15.6209 | 42.8394 | 341275.3469 | 0 | 150738.0379 | 0 | 0 | 0 | 315730.0567 | 315019.9422 | 819617.2701 | 559405.6283 | 2501786.2819 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 34856261.2759 | 101774197.3794 | 237.1374 | 0.053037 | 657212.1121 | 1918944.6249 | 13398.1579 | 39120.2817
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6159 | 0.24201 | 0.027486 | 4 | 325104.0202 | 933750.2014 | 6627.6852 | 19035.7608 | 85.7206 | 16.2509 | 60.7535 | 466582.8445 | 0 | 222243.5461 | 0 | 0 | 0 | 405453.9393 | 426769.3287 | 1110366.2508 | 757847.7819 | 3389263.6913 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 35743738.6853 | 102661674.7888 | 316.2278 | 0.10995 | 325104.0202 | 933750.2014 | 6627.6852 | 19035.7608
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2501 | 0.45894 | 0.048478 | 4 | 189574.5871 | 534666.0844 | 3864.7344 | 10899.8913 | 91.4343 | 16.7063 | 61.0881 | 611949.2277 | 0 | 307059.4024 | 0 | 0 | 0 | 503741.0249 | 554872.3655 | 1443664.075 | 985330.3955 | 4406616.491 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 36761091.485 | 103679027.5884 | 421.6965 | 0.19391 | 189574.5871 | 534666.0844 | 3864.7344 | 10899.8913
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3501 | 0.75765 | 0.078141 | 4 | 121460.7183 | 335553.9476 | 2476.141 | 6840.7211 | 96.0162 | 17.0484 | 60.2136 | 784540.4738 | 0 | 410130.7056 | 0 | 0 | 0 | 616555.9271 | 706378.5715 | 1837852.1449 | 1254371.853 | 5609829.6759 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 37964304.6699 | 104882240.7734 | 562.3413 | 0.31256 | 121460.7183 | 335553.9476 | 2476.141 | 6840.7211
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0102 | 1.1532 | 0.11888 | 4 | 82778.8646 | 223505.734 | 1687.5591 | 4556.4667 | 99.6209 | 17.3018 | 46.7291 | 986175.2979 | 0 | 533480.8252 | 0 | 0 | 0 | 743069.0592 | 882462.8211 | 2295987.2425 | 1567058.4708 | 7008233.7168 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 39362708.7108 | 106280644.8142 | 749.8942 | 0.47552 | 82778.8646 | 223505.734 | 1687.5591 | 4556.4667
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4138 | 1.6727 | 0.17387 | 4 | 58968.05 | 155187.5216 | 1202.1435 | 3163.7075 | 102.4746 | 17.4899 | 49.5253 | 1224113.5411 | 0 | 682655.7354 | 0 | 0 | 0 | 888011.6071 | 1089964.5446 | 2835864.1625 | 1935535.5621 | 8656145.1527 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 41010620.1467 | 107928556.2502 | 1000 | 0.69547 | 58968.05 | 155187.5216 | 1202.1435 | 3163.7075
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.725 | 2.3425 | 0.24699 | 4 | 43455.7786 | 111188.9822 | 885.9048 | 2266.7378 | 104.6994 | 17.6241 | 54.0823 | 1502282.8283 | 0 | 861454.7851 | 0 | 0 | 0 | 1051626.9597 | 1331992.1835 | 3465570.4324 | 2365323.0305 | 10578250.2195 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 42932725.2135 | 109850661.317 | 1333.5214 | 0.98796 | 43455.7786 | 111188.9822 | 885.9048 | 2266.7378
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.1696 | 3.1984 | 0.34302 | 4 | 32922.6646 | 81693.5212 | 671.173 | 1665.4329 | 106.4182 | 17.712 | 68.1862 | 1826884.3604 | 0 | 1075461.924 | 0 | 0 | 0 | 1236267.8309 | 1614059.505 | 4199451.7429 | 2866212.1046 | 12818337.4679 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 45172812.4619 | 112090748.5653 | 1778.2794 | 1.3721 | 32922.6646 | 81693.5212 | 671.173 | 1665.4329
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9371 | 4.2724 | 0.46718 | 4 | 25547.8462 | 61357.2756 | 520.8274 | 1250.8511 | 107.7108 | 17.7558 | 57.3102 | 2200184.4011 | 0 | 1328097.91 | 0 | 0 | 0 | 1439795.0627 | 1937550.1758 | 5041108.1112 | 3440659.8703 | 15387395.531 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 47741870.525 | 114659806.6285 | 2371.3737 | 1.8687 | 25547.8462 | 61357.2756 | 520.8274 | 1250.8511
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.1466 | 5.5868 | 0.62435 | 4 | 20267.1301 | 47062.2785 | 413.1729 | 959.4282 | 108.6393 | 17.7538 | 60.6645 | 2619833.5105 | 0 | 1619986.1202 | 0 | 0 | 0 | 1655872.3961 | 2299319.8905 | 5982358.6996 | 4083082.7377 | 18260453.3545 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 50614928.3485 | 117532864.452 | 3162.2777 | 2.4974 | 20267.1301 | 47062.2785 | 413.1729 | 959.4282
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.8519 | 7.154 | 0.81799 | 4 | 16426.715 | 36878.6484 | 334.8808 | 751.8211 | 109.2548 | 17.7021 | 51.7541 | 3080302.4237 | 0 | 1949812.0443 | 0 | 0 | 0 | 1877005.4132 | 2693776.7537 | 7008654.5436 | 4783550.7394 | 21393101.918 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 53747576.912 | 120665513.0154 | 4216.965 | 3.272 | 16426.715 | 36878.6484 | 334.8808 | 751.8211
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8038 | 8.9399 | 1.0472 | 4 | 13607.5291 | 29583.3293 | 277.4079 | 603.0962 | 109.5855 | 17.5957 | 75.9954 | 3563261.7606 | 0 | 2307105.0671 | 0 | 0 | 0 | 2086188.3188 | 3103056.5072 | 8073516.5072 | 5510340.9103 | 24643469.0712 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 56997944.0652 | 123915880.1687 | 5623.4133 | 4.1887 | 13607.5291 | 29583.3293 | 277.4079 | 603.0962
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.4628 | 10.862 | 1.3044 | 4 | 11531.4908 | 24356.5897 | 235.085 | 496.542 | 109.6626 | 17.437 | 75.1244 | 4042048.4772 | 0 | 2674056.0597 | 0 | 0 | 0 | 2264031.9575 | 3502253.2328 | 9112144.5009 | 6219225.8577 | 27813760.0858 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 60168235.0798 | 127086171.1833 | 7498.9421 | 5.2177 | 11531.4908 | 24356.5897 | 235.085 | 496.542
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.0971 | 12.8027 | 1.576 | 4 | 10002.5903 | 20618.0126 | 203.9163 | 420.3261 | 109.5275 | 17.2352 | 77.0006 | 4487976.6159 | 0 | 3029261.8798 | 0 | 0 | 0 | 2394854.3866 | 3865716.2241 | 10057800.6477 | 6864655.6092 | 30700265.3633 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 63054740.3573 | 129972676.4608 | 10000 | 6.3038 | 10002.5903 | 20618.0126 | 203.9163 | 420.3261
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.023 | 14.6464 | 1.8451 | 4 | 8878.1638 | 17945.3 | 180.9934 | 365.8392 | 109.2404 | 17.0082 | 74.8971 | 4880221.6202 | 0 | 3354643.9027 | 0 | 0 | 0 | 2474232.642 | 4176548.2843 | 10866521.9079 | 7416624.4868 | 33168792.844 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 65523267.8379 | 132441203.9414 | 13335.2143 | 7.3803 | 8878.1638 | 17945.3 | 180.9934 | 365.8392
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.7233 | 16.3016 | 2.0964 | 4 | 8051.7875 | 16032.0542 | 164.1466 | 326.8351 | 108.8691 | 16.7771 | 77.364 | 5208043.5937 | 0 | 3637902.9498 | 0 | 0 | 0 | 2507077.1709 | 4427679.2486 | 11519913.163 | 7862577.4443 | 35163193.5703 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 67517668.5643 | 134435604.6677 | 17782.7941 | 8.3854 | 8051.7875 | 16032.0542 | 164.1466 | 326.8351
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9593 | 17.7213 | 2.3194 | 4 | 7444.0742 | 14656.9887 | 151.7575 | 298.8025 | 108.4735 | 16.5593 | 72.7266 | 5471738.5888 | 0 | 3874807.4422 | 0 | 0 | 0 | 2505259.9601 | 4622204.3365 | 12026027.5392 | 8208010.9057 | 36708048.7725 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 69062523.7665 | 135980459.87 | 23713.7371 | 9.2775 | 7444.0742 | 14656.9887 | 151.7575 | 298.8025
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6996 | 18.8938 | 2.5092 | 4 | 6996.3621 | 13663.6845 | 142.6303 | 278.5527 | 108.0967 | 16.3665 | 88.072 | 5677681.4042 | 0 | 4066512.8732 | 0 | 0 | 0 | 2481454.7228 | 4768003.1101 | 12405366.0406 | 8466917.2275 | 37865935.3784 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 70220410.3724 | 137138346.4759 | 31622.7766 | 10.0367 | 6996.3621 | 13663.6845 | 142.6303 | 278.5527
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0936 | 19.8391 | 2.6658 | 4 | 6665.7151 | 12941.4231 | 135.8896 | 263.8284 | 107.7614 | 16.2029 | 77.6838 | 5836121.7575 | 0 | 4218647.2157 | 0 | 0 | 0 | 2447310.3563 | 4875810.9385 | 12685859.8956 | 8658360.0471 | 38722110.2106 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 71076585.2046 | 137994521.3081 | 42169.6503 | 10.663 | 6665.7151 | 12941.4231 | 135.8896 | 263.8284
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3272 | 20.5856 | 2.7918 | 4 | 6420.8802 | 12413.3032 | 130.8983 | 253.062 | 107.4773 | 16.0687 | 81.7372 | 5956515.9568 | 0 | 4337322.2925 | 0 | 0 | 0 | 2410346.6259 | 4954632.1013 | 12890936.3929 | 8798328.9704 | 39348082.3399 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 71702557.3338 | 138620493.4373 | 56234.1325 | 11.1671 | 6420.8802 | 12413.3032 | 130.8983 | 253.062
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.6085 | 21.1672 | 2.8914 | 4 | 6239.1367 | 12025.116 | 127.1932 | 245.1483 | 107.2445 | 15.9612 | 96.1131 | 6047425.5045 | 0 | 4428887.3932 | 0 | 0 | 0 | 2375223.3663 | 5012099.143 | 13040453.8471 | 8900377.7052 | 39804466.9592 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 72158941.9532 | 139076878.0566 | 74989.4209 | 11.5655 | 6239.1367 | 12025.116 | 127.1932 | 245.1483
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1176 | 21.6138 | 2.969 | 4 | 6103.9343 | 11738.7412 | 124.437 | 239.3101 | 107.059 | 15.8769 | 81.0447 | 6115521.2652 | 0 | 4498672.9119 | 0 | 0 | 0 | 2343973.7609 | 5053685.4958 | 13148653.0066 | 8974225.8548 | 40134732.2952 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 72489207.2891 | 139407143.3926 | 100000 | 11.8758 | 6103.9343 | 11738.7412 | 124.437 | 239.3101
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.042 | 21.9572 | 3.0289 | 4 | 6003.1742 | 11526.3875 | 122.3828 | 234.981 | 106.9123 | 15.811 | 89.576 | 6166908.5988 | 0 | 4552061.6733 | 0 | 0 | 0 | 2317918.9471 | 5084386.7955 | 13228531.4907 | 9028744.5616 | 40378552.067 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 72733027.061 | 139650963.1644 | 133352.1432 | 12.1158 | 6003.1742 | 11526.3875 | 122.3828 | 234.981
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5035 | 22.2187 | 3.0749 | 4 | 5927.974 | 11368.6136 | 120.8498 | 231.7646 | 106.7984 | 15.7603 | 77.5924 | 6205451.7642 | 0 | 4592538.1295 | 0 | 0 | 0 | 2296676.0899 | 5106919.7336 | 13287157.5735 | 9068758.0677 | 40557501.3584 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 72911976.3524 | 139829912.4559 | 177827.941 | 12.2996 | 5927.974 | 11368.6136 | 120.8498 | 231.7646
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.605 | 22.4162 | 3.1099 | 4 | 5871.7863 | 11251.2165 | 119.7043 | 229.3713 | 106.7111 | 15.7217 | 96.2106 | 6234220.4442 | 0 | 4623001.3475 | 0 | 0 | 0 | 2279633.5374 | 5123373.5784 | 13329967.1024 | 9097976.4509 | 40688172.4608 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73042647.4547 | 139960583.5582 | 237137.3706 | 12.4396 | 5871.7863 | 11251.2165 | 119.7043 | 229.3713
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.4307 | 22.5646 | 3.1364 | 4 | 5829.7676 | 11163.7535 | 118.8477 | 227.5882 | 106.6448 | 15.6925 | 90.5017 | 6255627.9996 | 0 | 4645813.8852 | 0 | 0 | 0 | 2266136.275 | 5135355.4823 | 13361141.5588 | 9119253.6579 | 40783328.8589 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73137803.8529 | 140055739.9564 | 316227.766 | 12.5456 | 5829.7676 | 11163.7535 | 118.8477 | 227.5882
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0614 | 22.6778 | 3.1565 | 4 | 5798.3236 | 11098.2884 | 118.2067 | 226.2536 | 106.5937 | 15.6701 | 92.5101 | 6271889.2728 | 0 | 4663226.0419 | 0 | 0 | 0 | 2255858.9235 | 5144479.9529 | 13384881.5594 | 9135456.6961 | 40855792.4464 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73210267.4404 | 140128203.5439 | 421696.5034 | 12.6261 | 5798.3236 | 11098.2884 | 118.2067 | 226.2536
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.5413 | 22.764 | 3.1718 | 4 | 5774.781 | 11049.2607 | 117.7267 | 225.2541 | 106.5545 | 15.6529 | 96.4419 | 6284210.4296 | 0 | 4676468.1637 | 0 | 0 | 0 | 2248068.993 | 5151411.5586 | 13402916.1758 | 9147765.6923 | 40910841.013 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73265316.0069 | 140183252.1104 | 562341.3252 | 12.6871 | 5774.781 | 11049.2607 | 117.7267 | 225.2541
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8922 | 22.8272 | 3.1832 | 4 | 5757.1474 | 11012.7448 | 117.3672 | 224.5097 | 106.5257 | 15.6404 | 84.955 | 6293192.3282 | 0 | 4686148.8709 | 0 | 0 | 0 | 2241902.6661 | 5156285.1074 | 13415596.15 | 9156420.0353 | 40949545.1581 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73304020.152 | 140221956.2555 | 749894.2093 | 12.7327 | 5757.1474 | 11012.7448 | 117.3672 | 224.5097
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.148 | 22.8736 | 3.1917 | 4 | 5743.9359 | 10985.5408 | 117.0979 | 223.9551 | 106.5046 | 15.6312 | 91.6324 | 6299721.7 | 0 | 4693201.0373 | 0 | 0 | 0 | 2237044.6026 | 5159687.2626 | 13424447.8598 | 9162461.5092 | 40976563.9715 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73331038.9655 | 140248975.069 | 1000000 | 12.7667 | 5743.9359 | 10985.5408 | 117.0979 | 223.9551
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.3481 | 22.9096 | 3.1981 | 4 | 5734.0352 | 10965.0358 | 116.8961 | 223.5371 | 106.4881 | 15.624 | 82.6927 | 6304819.7067 | 0 | 4698715.4435 | 0 | 0 | 0 | 2233536.2658 | 5162457.8522 | 13431656.3658 | 9167381.4626 | 40998567.0966 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73353042.0906 | 140270978.194 | 1333521.4322 | 12.7926 | 5734.0352 | 10965.0358 | 116.8961 | 223.5371
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.5159 | 22.9394 | 3.2032 | 4 | 5726.6146 | 10949.3849 | 116.7448 | 223.218 | 106.4742 | 15.6179 | 100.3119 | 6309091.4108 | 0 | 4703341.1426 | 0 | 0 | 0 | 2231261.7255 | 5165040.7688 | 13438376.5848 | 9171968.1502 | 41019079.7827 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73373554.7767 | 140291490.8802 | 1778279.41 | 12.8127 | 5726.6146 | 10949.3849 | 116.7448 | 223.218
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6233 | 22.9589 | 3.2068 | 4 | 5721.0519 | 10937.9612 | 116.6314 | 222.9851 | 106.4653 | 15.6141 | 87.8372 | 6311821.9426 | 0 | 4706301.4004 | 0 | 0 | 0 | 2229148.7776 | 5166436.127 | 13442007.0207 | 9174445.9973 | 41030161.2656 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73384636.2596 | 140302572.3631 | 2371373.7057 | 12.8271 | 5721.0519 | 10937.9612 | 116.6314 | 222.9851
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7009 | 22.9731 | 3.2095 | 4 | 5716.8817 | 10929.4482 | 116.5464 | 222.8116 | 106.4588 | 15.6113 | 83.3619 | 6313793.1126 | 0 | 4708439.8915 | 0 | 0 | 0 | 2227494.1365 | 5167393.5848 | 13444498.1295 | 9176146.2302 | 41037765.0852 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73392240.0792 | 140310176.1826 | 3162277.6602 | 12.8378 | 5716.8817 | 10929.4482 | 116.5464 | 222.8116
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7741 | 22.986 | 3.2116 | 4 | 5713.7552 | 10922.8228 | 116.4826 | 222.6765 | 106.4528 | 15.6086 | 81.0594 | 6315651.3189 | 0 | 4710456.2098 | 0 | 0 | 0 | 2226567.9322 | 5168543.4297 | 13447489.7902 | 9178188.1001 | 41046896.7808 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73401371.7748 | 140319307.8783 | 4216965.0343 | 12.8464 | 5713.7552 | 10922.8228 | 116.4826 | 222.6765
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.813 | 22.9932 | 3.2131 | 4 | 5711.411 | 10918.1172 | 116.4348 | 222.5806 | 106.4495 | 15.6072 | 83.7149 | 6316637.6806 | 0 | 4711527.4759 | 0 | 0 | 0 | 2225530.6908 | 5168941.3804 | 13448525.1763 | 9178894.7724 | 41050057.1764 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73404532.1703 | 140322468.2738 | 5623413.2519 | 12.8523 | 5711.411 | 10918.1172 | 116.4348 | 222.5806
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.8519 | 23.0002 | 3.2143 | 4 | 5709.6533 | 10914.4306 | 116.399 | 222.5054 | 106.4463 | 15.6058 | 89.7248 | 6317624.696 | 0 | 4712599.2517 | 0 | 0 | 0 | 2224958.7371 | 5169521.247 | 13450033.8702 | 9179924.487 | 41054662.289 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73409137.283 | 140327073.3864 | 7498942.0933 | 12.857 | 5709.6533 | 10914.4306 | 116.399 | 222.5054
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.8861 | 23.0062 | 3.2152 | 4 | 5708.3353 | 10911.5836 | 116.3721 | 222.4474 | 106.4434 | 15.6046 | 79.3591 | 6318494.336 | 0 | 4713543.6185 | 0 | 0 | 0 | 2224637.5157 | 5170103.4334 | 13451548.5995 | 9180958.3209 | 41059285.8239 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 73413760.8179 | 140331696.9213 | 10000000 | 12.8608 | 5708.3353 | 10911.5836 | 116.3721 | 222.4474
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.104 | [19 empty] | 100 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3264 | [19 empty] | 133.3521 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.041373 | 0.0033187 | 4 | 2576628.9695 | 7720754.2501 | 52528.0667 | 157398.0185 | 60.1901 | 14.0376 | 24.0903 | 166383.9666 | 0 | 52813.7527 | 0 | 0 | 0 | 164845.885 | 149777.0057 | 389689.0453 | 265970.7807 | 1189480.4361 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 34204278.84 | 102491602.1482 | 177.8279 | 0.013275 | 2576628.9695 | 7720754.2501 | 52528.0667 | 157398.0185
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.095702 | 0.014128 | 4 | 630166.9881 | 1838509.6735 | 12846.8064 | 37480.5065 | 79.75 | 15.973 | 44.5181 | 354606.3292 | 0 | 156389.245 | 0 | 0 | 0 | 327799.3517 | 327130.0211 | 851125.2113 | 580910.4456 | 2597960.6038 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 35612759.0077 | 103900082.3159 | 237.1374 | 0.056513 | 630166.9881 | 1838509.6735 | 12846.8064 | 37480.5065
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7427 | 0.25554 | 0.029171 | 4 | 313082.4992 | 898317.6239 | 6382.6102 | 18313.4198 | 87.1892 | 16.6095 | 50.5289 | 484520.1472 | 0 | 230129.7509 | 0 | 0 | 0 | 420802.854 | 442826.5733 | 1152143.9076 | 786361.8911 | 3516785.1242 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 36531583.5281 | 104818906.8363 | 316.2278 | 0.11668 | 313082.4992 | 898317.6239 | 6382.6102 | 18313.4198
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4157 | 0.48118 | 0.051336 | 4 | 183017.0485 | 515565.5735 | 3731.0501 | 10510.5016 | 92.9899 | 17.0687 | 59.896 | 634861.4275 | 0 | 317373.5688 | 0 | 0 | 0 | 522270.6809 | 575057.2141 | 1496180.9106 | 1021174.2149 | 4566918.0168 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 37581716.4207 | 105869039.7289 | 421.6965 | 0.20535 | 183017.0485 | 515565.5735 | 3731.0501 | 10510.5016
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5593 | 0.79089 | 0.082624 | 4 | 117459.0251 | 324080.6451 | 2394.5611 | 6606.8223 | 97.6351 | 17.4128 | 59.0824 | 812886.2375 | 0 | 423101.9061 | 0 | 0 | 0 | 638179.1823 | 730925.2571 | 1901717.5856 | 1297961.3286 | 5804771.4971 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 38819569.9011 | 107106893.2093 | 562.3413 | 0.33049 | 117459.0251 | 324080.6451 | 2394.5611 | 6606.8223
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2855 | 1.2022 | 0.12558 | 4 | 80157.174 | 216097.6447 | 1634.1124 | 4405.4428 | 101.3079 | 17.6689 | 57.3993 | 1021744.8751 | 0 | 550156.0242 | 0 | 0 | 0 | 769127.697 | 913001.1525 | 2375441.7166 | 1621287.782 | 7250759.2475 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 40265557.6514 | 108552880.9596 | 749.8942 | 0.50233 | 80157.174 | 216097.6447 | 1634.1124 | 4405.4428
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7614 | 1.7407 | 0.18352 | 4 | 57164.1194 | 150189.9729 | 1165.3679 | 3061.8257 | 104.2068 | 17.8581 | 65.3133 | 1267377.1092 | 0 | 703286.5831 | 0 | 0 | 0 | 918207.0776 | 1126659.6003 | 2931337.1703 | 2000697.8517 | 8947565.3922 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 41962363.7961 | 110249687.1043 | 1000 | 0.73407 | 57164.1194 | 150189.9729 | 1165.3679 | 3061.8257
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.2003 | 2.4397 | 0.26063 | 4 | 42169.0413 | 107672.1229 | 859.6729 | 2195.0419 | 106.4837 | 17.9936 | 50.4162 | 1556869.1147 | 0 | 888324.1756 | 0 | 0 | 0 | 1089118.3324 | 1378381.5329 | 3586266.0036 | 2447700.2378 | 10946659.397 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 43961457.8009 | 112248781.1091 | 1333.5214 | 1.0425 | 42169.0413 | 107672.1229 | 859.6729 | 2195.0419
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7567 | 3.3262 | 0.36169 | 4 | 31979.0215 | 79179.4944 | 651.9356 | 1614.1811 | 108.226 | 18.0807 | 65.1945 | 1891696.9267 | 0 | 1107854.4286 | 0 | 0 | 0 | 1278715.5296 | 1668524.0851 | 4341157.408 | 2962929.1328 | 13250877.5108 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 46265675.9147 | 114552999.2229 | 1778.2794 | 1.4468 | 31979.0215 | 79179.4944 | 651.9356 | 1614.1811
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.6487 | 4.4363 | 0.49217 | 4 | 24840.147 | 59526.8935 | 506.4 | 1213.5362 | 109.5352 | 18.1225 | 51.6475 | 2276055.9278 | 0 | 1366536.7493 | 0 | 0 | 0 | 1487003.1599 | 2000542.3764 | 5205000.8958 | 3552520.0634 | 15887659.1726 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 48902457.5766 | 117189780.8847 | 2371.3737 | 1.9687 | 24840.147 | 59526.8935 | 506.4 | 1213.5362
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.0286 | 5.7977 | 0.65726 | 4 | 19726.2768 | 45700.6588 | 402.1468 | 931.6697 | 110.4779 | 18.1173 | 64.2489 | 2709202.1176 | 0 | 1666176.1231 | 0 | 0 | 0 | 1709397.8172 | 2373062.6626 | 6174222.2659 | 4214033.5641 | 18846094.5505 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 51860892.9544 | 120148216.2626 | 3162.2777 | 2.629 | 19726.2768 | 45700.6588 | 402.1468 | 931.6697
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8971 | 7.4152 | 0.86015 | 4 | 16006.4675 | 35853.8783 | 326.3135 | 730.9298 | 111.0988 | 18.0603 | 65.1052 | 3182667.6386 | 0 | 2003534.0626 | 0 | 0 | 0 | 1935369.835 | 2777412.8991 | 7226258.6377 | 4932070.005 | 22057313.078 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 55072111.482 | 123359434.7902 | 4216.965 | 3.4406 | 16006.4675 | 35853.8783 | 326.3135 | 730.9298
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.9829 | 9.2507 | 1.0995 | 4 | 13275.9425 | 28803.0185 | 270.648 | 587.1885 | 111.4285 | 17.9473 | 69.5972 | 3677083.7162 | 0 | 2367467.5008 | 0 | 0 | 0 | 2147270.5714 | 3194810.4975 | 8312241.5688 | 5673275.6702 | 25372149.5251 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 58386947.929 | 126674271.2372 | 5623.4133 | 4.398 | 13275.9425 | 28803.0185 | 270.648 | 587.1885
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.754 | 11.2212 | 1.3672 | 4 | 11265.7351 | 23752.0937 | 229.6672 | 484.2186 | 111.4998 | 17.7804 | 67.2891 | 4166017.943 | 0 | 2740412.5346 | 0 | 0 | 0 | 2326585.0205 | 3600876.0443 | 9368740.826 | 6394358.1221 | 28596990.4906 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 61611788.8945 | 129899112.2027 | 7498.9421 | 5.469 | 11265.7351 | 23752.0937 | 229.6672 | 484.2186
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.464 | 13.2046 | 1.6488 | 4 | 9785.8205 | 20140.0643 | 199.4972 | 410.5825 | 111.356 | 17.57 | 80.4344 | 4620029.6923 | 0 | 3100443.4938 | 0 | 0 | 0 | 2457483.598 | 3969403.1458 | 10327572.7489 | 7048780.6115 | 31523713.2904 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 64538511.6944 | 132825835.0026 | 10000 | 6.5951 | 9785.8205 | 20140.0643 | 199.4972 | 410.5825
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.4017 | 15.0794 | 1.9265 | 4 | 8697.7307 | 17559.1999 | 177.315 | 357.968 | 111.0602 | 17.3353 | 75.8753 | 5017294.3475 | 0 | 3428590.535 | 0 | 0 | 0 | 2535050.0936 | 4282564.6407 | 11142354.7202 | 7604886.0491 | 34010740.3861 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 67025538.79 | 135312862.0982 | 13335.2143 | 7.7061 | 8697.7307 | 17559.1999 | 177.315 | 357.968
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0682 | 16.7552 | 2.1848 | 4 | 7898.1928 | 15712.0725 | 161.0153 | 320.3118 | 110.6824 | 17.0979 | 74.0695 | 5347906.2117 | 0 | 3713061.5756 | 0 | 0 | 0 | 2565254.1527 | 4534226.5566 | 11797127.4025 | 8051781.8589 | 36009357.758 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 69024156.1619 | 137311479.4701 | 17782.7941 | 8.7392 | 7898.1928 | 15712.0725 | 161.0153 | 320.3118
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2675 | 18.1909 | 2.4135 | 4 | 7310.2466 | 14383.8516 | 149.0293 | 293.2343 | 110.2817 | 16.875 | 86.8435 | 5613694.1471 | 0 | 3950829.515 | 0 | 0 | 0 | 2561386.9237 | 4729105.1285 | 12304161.4715 | 8397843.0295 | 37557020.2153 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 70571818.6192 | 138859141.9274 | 23713.7371 | 9.6538 | 7310.2466 | 14383.8516 | 149.0293 | 293.2343
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9519 | 19.3724 | 2.6074 | 4 | 6877.084 | 13424.4532 | 140.1987 | 273.6756 | 109.9024 | 16.6787 | 74.1765 | 5820557.7828 | 0 | 4142543.8408 | 0 | 0 | 0 | 2535507.7725 | 4874457.6645 | 12682338.9542 | 8655956.9323 | 38711362.9471 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 71726161.351 | 140013484.6592 | 31622.7766 | 10.4297 | 6877.084 | 13424.4532 | 140.1987 | 273.6756
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3085 | 20.3259 | 2.7673 | 4 | 6557.1581 | 12726.2852 | 133.6765 | 259.4425 | 109.5649 | 16.5121 | 102.6624 | 5979992.1653 | 0 | 4294928.9771 | 0 | 0 | 0 | 2500177.079 | 4982288.3064 | 12962892.1653 | 8847440.2636 | 39567718.9567 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 72582517.3606 | 140869840.6688 | 42169.6503 | 11.0692 | 6557.1581 | 12726.2852 | 133.6765 | 259.4425
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.489 | 21.0752 | 2.8956 | 4 | 6320.2403 | 12216.049 | 128.8466 | 249.0407 | 109.2808 | 16.3763 | 96.0576 | 6100503.4445 | 0 | 4413147.8252 | 0 | 0 | 0 | 2461857.485 | 5060448.4143 | 13166248.7334 | 8986235.2999 | 40188441.2024 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 73203239.6064 | 141490562.9146 | 56234.1325 | 11.5824 | 6320.2403 | 12216.049 | 128.8466 | 249.0407
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.7339 | 21.6595 | 2.9969 | 4 | 6144.358 | 11840.7621 | 125.261 | 241.39 | 109.0479 | 16.2674 | 89.9595 | 6191667.3439 | 0 | 4504504.5511 | 0 | 0 | 0 | 2425938.4301 | 5117623.0268 | 13315005.3469 | 9087764.7452 | 40642503.4439 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 73657301.8479 | 141944625.156 | 74989.4209 | 11.9878 | 6144.358 | 11840.7621 | 125.261 | 241.39
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.2307 | 22.1107 | 3.076 | 4 | 6013.5055 | 11563.5351 | 122.5934 | 235.7383 | 108.8612 | 16.1815 | 92.6935 | 6260398.5863 | 0 | 4574574.2472 | 0 | 0 | 0 | 2394526.1202 | 5159504.5919 | 13423972.5883 | 9162137.1265 | 40975113.2604 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 73989911.6643 | 142277234.9725 | 100000 | 12.304 | 6013.5055 | 11563.5351 | 122.5934 | 235.7383
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1138 | 22.4525 | 3.1368 | 4 | 5915.9807 | 11358.4895 | 120.6053 | 231.5582 | 108.7161 | 16.1156 | 90.5778 | 6311416.4634 | 0 | 4627294.9035 | 0 | 0 | 0 | 2367654.9372 | 5189482.8586 | 13501969.8887 | 9215371.8868 | 41213190.9381 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74227989.3421 | 142515312.6502 | 133352.1432 | 12.547 | 5915.9807 | 11358.4895 | 120.6053 | 231.5582
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.5681 | 22.7166 | 3.1836 | 4 | 5843.1912 | 11205.6928 | 119.1214 | 228.4432 | 108.6016 | 16.064 | 89.7663 | 6350336.407 | 0 | 4667940.5047 | 0 | 0 | 0 | 2346381.5402 | 5212216.7962 | 13561118.9311 | 9255742.3236 | 41393736.5027 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74408534.9067 | 142695858.2149 | 177827.941 | 12.7342 | 5843.1912 | 11205.6928 | 119.1214 | 228.4432
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6593 | 22.9153 | 3.2191 | 4 | 5788.8025 | 11092.0712 | 118.0126 | 226.1269 | 108.5142 | 16.0248 | 93.9575 | 6379258.6871 | 0 | 4698394.8134 | 0 | 0 | 0 | 2329218.3008 | 5228680.0025 | 13603952.8168 | 9284977.3308 | 41524481.9514 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74539280.3553 | 142826603.6635 | 237137.3706 | 12.8765 | 5788.8025 | 11092.0712 | 118.0126 | 226.1269
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4661 | 23.0628 | 3.2459 | 4 | 5748.1277 | 11007.5984 | 117.1834 | 224.4048 | 108.4487 | 15.9957 | 76.7696 | 6400490.2922 | 0 | 4720891.2197 | 0 | 0 | 0 | 2315392.0103 | 5240341.6736 | 13634294.0929 | 9305685.8752 | 41617095.1639 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74631893.5678 | 142919216.876 | 316227.766 | 12.9837 | 5748.1277 | 11007.5984 | 117.1834 | 224.4048
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.0897 | 23.1766 | 3.2664 | 4 | 5717.6887 | 10944.2446 | 116.5628 | 223.1132 | 108.3977 | 15.973 | 86.257 | 6416813.0268 | 0 | 4738267.9256 | 0 | 0 | 0 | 2305036.5145 | 5249445.8121 | 13657981.1936 | 9321852.8081 | 41689397.2806 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74704195.6845 | 142991518.9927 | 421696.5034 | 13.0655 | 5717.6887 | 10944.2446 | 116.5628 | 223.1132
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.565 | 23.2632 | 3.2819 | 4 | 5694.8981 | 10896.7831 | 116.0982 | 222.1457 | 108.3585 | 15.9557 | 93.4526 | 6429200.8649 | 0 | 4751503.9535 | 0 | 0 | 0 | 2297208.0578 | 5256386.0217 | 13676038.1955 | 9334177.0829 | 41744514.1763 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74759312.5802 | 143046635.8884 | 562341.3252 | 13.1274 | 5694.8981 | 10896.7831 | 116.0982 | 222.1457
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9056 | 23.3257 | 3.2934 | 4 | 5677.8275 | 10861.5461 | 115.7502 | 221.4273 | 108.3303 | 15.9432 | 82.3909 | 6438050.2163 | 0 | 4760985.8653 | 0 | 0 | 0 | 2290860.8387 | 5261059.7989 | 13688198.405 | 9342476.6757 | 41781631.7999 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74796430.2038 | 143083753.512 | 749894.2093 | 13.1734 | 5677.8275 | 10861.5461 | 115.7502 | 221.4273
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1808 | 23.3758 | 3.3022 | 4 | 5665.0377 | 10834.8543 | 115.4895 | 220.8832 | 108.3074 | 15.9331 | 92.896 | 6445185.0393 | 0 | 4768645.8244 | 0 | 0 | 0 | 2286459.8389 | 5265113.374 | 13698744.976 | 9349674.9272 | 41813823.9798 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74828622.3837 | 143115945.6919 | 1000000 | 13.2088 | 5665.0377 | 10834.8543 | 115.4895 | 220.8832
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.366 | 23.41 | 3.3086 | 4 | 5655.453 | 10815.2114 | 115.2941 | 220.4827 | 108.2919 | 15.9263 | 89.078 | 6449976.3076 | 0 | 4773798.625 | 0 | 0 | 0 | 2282656.0704 | 5267508.0912 | 13704975.5388 | 9353927.4143 | 41832842.0473 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74847640.4512 | 143134963.7594 | 1333521.4322 | 13.2346 | 5655.453 | 10815.2114 | 115.2941 | 220.4827
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.5272 | 23.4392 | 3.3137 | 4 | 5648.269 | 10800.1396 | 115.1476 | 220.1755 | 108.2785 | 15.9203 | 81.4448 | 6454141.0319 | 0 | 4778281.9134 | 0 | 0 | 0 | 2280263.9551 | 5269947.8912 | 13711323.3978 | 9358259.9585 | 41852218.1479 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74867016.5518 | 143154339.86 | 1778279.41 | 13.2549 | 5648.269 | 10800.1396 | 115.1476 | 220.1755
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.6413 | 23.46 | 3.3174 | 4 | 5642.8839 | 10788.956 | 115.0378 | 219.9475 | 108.2689 | 15.9161 | 96.4557 | 6457085.9463 | 0 | 4781455.3242 | 0 | 0 | 0 | 2278309.7032 | 5271571.8798 | 13715548.683 | 9361143.8025 | 41865115.339 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74879913.7429 | 143167237.0511 | 2371373.7057 | 13.2698 | 5642.8839 | 10788.956 | 115.0378 | 219.9475
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7144 | 23.4736 | 3.3201 | 4 | 5638.8467 | 10780.7736 | 114.9555 | 219.7807 | 108.2628 | 15.9134 | 88.8749 | 6458972.0884 | 0 | 4783489.6209 | 0 | 0 | 0 | 2276568.0987 | 5272421.6251 | 13717759.5462 | 9362652.762 | 41871863.7413 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74886662.1453 | 143173985.4534 | 3162277.6602 | 13.2805 | 5638.8467 | 10780.7736 | 114.9555 | 219.7807
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.783 | 23.486 | 3.3223 | 4 | 5635.8199 | 10774.4216 | 114.8938 | 219.6512 | 108.257 | 15.9109 | 89.1063 | 6460739.1656 | 0 | 4785395.7714 | 0 | 0 | 0 | 2275554.0746 | 5273458.7145 | 13720457.84 | 9364494.403 | 41880099.9692 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74894898.3731 | 143182221.6813 | 4216965.0343 | 13.2891 | 5635.8199 | 10774.4216 | 114.8938 | 219.6512
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8265 | 23.4941 | 3.3238 | 4 | 5633.5504 | 10769.7859 | 114.8475 | 219.5567 | 108.2534 | 15.9093 | 89.647 | 6461860.4102 | 0 | 4786606.0273 | 0 | 0 | 0 | 2274620.9592 | 5274004.0847 | 13721876.7814 | 9365462.8597 | 41884431.1223 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74899229.5263 | 143186552.8345 | 5623413.2519 | 13.2952 | 5633.5504 | 10769.7859 | 114.8475 | 219.5567
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8607 | 23.5004 | 3.325 | 4 | 5631.8488 | 10766.2845 | 114.8129 | 219.4853 | 108.2505 | 15.908 | 85.4299 | 6462742.9684 | 0 | 4787558.8289 | 0 | 0 | 0 | 2273955.0906 | 5274460.1863 | 13723063.4642 | 9366272.7951 | 41888053.3334 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74902851.7374 | 143190175.0456 | 7498942.0933 | 13.2999 | 5631.8488 | 10766.2845 | 114.8129 | 219.4853
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8802 | 23.5041 | 3.3258 | 4 | 5630.5728 | 10763.7593 | 114.7868 | 219.4338 | 108.2488 | 15.9073 | 88.2793 | 6463243.2398 | 0 | 4788099.2882 | 0 | 0 | 0 | 2273319.9158 | 5274618.3531 | 13723474.9818 | 9366553.6643 | 41889309.443 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 74904107.8469 | 143191431.1551 | 10000000 | 13.3031 | 5630.5728 | 10763.7593 | 114.7868 | 219.4338
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2924 | [19 empty] | 100 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9826 | [19 empty] | 133.3521 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.042656 | 0.0034108 | 4 | 2556529.7433 | 7663114.0439 | 52118.3168 | 156222.9449 | 60.4356 | 14.2817 | 25.9128 | 167979.0646 | 0 | 52573.9142 | 0 | 0 | 0 | 166380.2378 | 150903.9545 | 392621.1348 | 267971.9921 | 1198430.2979 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 34879412.2027 | 104549893.9291 | 177.8279 | 0.013643 | 2556529.7433 | 7663114.0439 | 52118.3168 | 156222.9449
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4929 | 0.10277 | 0.01504 | 4 | 604656.852 | 1762742.3563 | 12326.7478 | 35935.8872 | 81.0943 | 16.325 | 39.5376 | 368118.2506 | 0 | 162092.2097 | 0 | 0 | 0 | 339981.2751 | 339374.7768 | 882983.5539 | 602654.419 | 2695204.4851 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 36376186.3898 | 106046668.1163 | 237.1374 | 0.06016 | 604656.852 | 1762742.3563 | 12326.7478 | 35935.8872
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8593 | 0.26839 | 0.030923 | 4 | 301701.9812 | 864954.197 | 6150.603 | 17633.2612 | 88.6139 | 16.9644 | 50.4361 | 501725.5545 | 0 | 237527.6063 | 0 | 0 | 0 | 435177.1236 | 458027.8109 | 1191694.4095 | 813355.9213 | 3637508.426 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 37318490.3307 | 106988972.0571 | 316.2278 | 0.12369 | 301701.9812 | 864954.197 | 6150.603 | 17633.2612
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5861 | 0.50444 | 0.054318 | 4 | 176799.7709 | 497460.9421 | 3604.3025 | 10141.4142 | 94.5605 | 17.4319 | 53.1724 | 658509.5852 | 0 | 328022.5775 | 0 | 0 | 0 | 541447.6242 | 595912.1169 | 1550441.0898 | 1058207.9021 | 4732540.8957 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 38413522.8004 | 108084004.5269 | 421.6965 | 0.21727 | 176799.7709 | 497460.9421 | 3604.3025 | 10141.4142
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7787 | 0.82608 | 0.087299 | 4 | 113660.4964 | 313176.6855 | 2317.123 | 6384.5303 | 99.2745 | 17.7786 | 47.2186 | 842456.8629 | 0 | 436683.6863 | 0 | 0 | 0 | 660945.2931 | 756633.4785 | 1968605.1042 | 1343613.4344 | 6008937.8594 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 39689919.7641 | 109360401.4905 | 562.3413 | 0.3492 | 113660.4964 | 313176.6855 | 2317.123 | 6384.5303
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5755 | 1.2541 | 0.13257 | 4 | 77666.1739 | 209045.6736 | 1583.33 | 4261.6788 | 103.0138 | 18.0371 | 36.2849 | 1058909.4155 | 0 | 567648.0451 | 0 | 0 | 0 | 796670.1748 | 945058.7778 | 2458849.0816 | 1678215.0225 | 7505350.5173 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 41186332.422 | 110856814.1484 | 749.8942 | 0.5303 | 77666.1739 | 209045.6736 | 1583.33 | 4261.6788
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1318 | 1.813 | 0.19359 | 4 | 55448.6618 | 145421.7356 | 1130.396 | 2964.6188 | 105.9575 | 18.2273 | 37.8841 | 1312808.4474 | 0 | 725077.0748 | 0 | 0 | 0 | 950434.7824 | 1165444.9188 | 3032248.613 | 2069571.9849 | 9255585.8212 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 42936567.7259 | 112607049.4524 | 1000 | 0.77435 | 55448.6618 | 145421.7356 | 1130.396 | 2964.6188
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6607 | 2.5368 | 0.27471 | 4 | 40944.5194 | 104347.384 | 834.7094 | 2127.2626 | 108.2658 | 18.3627 | 36.1807 | 1611282.8088 | 0 | 914815.9685 | 0 | 0 | 0 | 1125865.8826 | 1424266.2174 | 3705648.5404 | 2529181.2723 | 11311060.6899 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 44992042.5946 | 114662524.321 | 1333.5214 | 1.0989 | 40944.5194 | 104347.384 | 834.7094 | 2127.2626
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3339 | 3.455 | 0.38098 | 4 | 31080.3454 | 76798.1986 | 633.6149 | 1565.6352 | 110.0352 | 18.4491 | 46.7946 | 1956824.3403 | 0 | 1140131.1082 | 0 | 0 | 0 | 1320851.0433 | 1722944.5318 | 4482748.2472 | 3059567.79 | 13683067.0608 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 47364048.9655 | 117034530.6919 | 1778.2794 | 1.5239 | 31080.3454 | 76798.1986 | 633.6149 | 1565.6352
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3797 | 4.6062 | 0.51812 | 4 | 24165.6714 | 57782.3524 | 492.6499 | 1177.9714 | 111.3665 | 18.4891 | 43.7427 | 2354023.4633 | 0 | 1406011.9429 | 0 | 0 | 0 | 1535723.261 | 2065345.8802 | 5373606.3196 | 3667596.7297 | 16402307.5966 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 50083289.5013 | 119753771.2277 | 2371.3737 | 2.0725 | 24165.6714 | 57782.3524 | 492.6499 | 1177.9714
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.9176 | 6.0136 | 0.69132 | 4 | 19210.4213 | 44405.2607 | 391.6304 | 905.2613 | 112.3211 | 18.4803 | 38.014 | 2800140.1632 | 0 | 1712998.3441 | 0 | 0 | 0 | 1763706.3319 | 2447969.4873 | 6369114.4583 | 4347051.49 | 19440980.2746 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 53121962.1793 | 122792443.9058 | 3162.2777 | 2.7653 | 19210.4213 | 44405.2607 | 391.6304 | 905.2613
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.9512 | 7.6824 | 0.90375 | 4 | 15605.3297 | 34878.0265 | 318.1358 | 711.0357 | 112.9473 | 18.4181 | 48.3458 | 3286813.0355 | 0 | 2058002.3952 | 0 | 0 | 0 | 1994599.1097 | 2862371.6707 | 7447303.9341 | 5082937.9618 | 22732028.107 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 56413010.0117 | 126083491.7382 | 4216.965 | 3.615 | 15605.3297 | 34878.0265 | 318.1358 | 711.0357
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.1692 | 9.5679 | 1.1534 | 4 | 12959.66 | 28060.3557 | 264.2002 | 572.0483 | 113.2763 | 18.2986 | 44.3747 | 3792722.2237 | 0 | 2428537.5776 | 0 | 0 | 0 | 2209224.1254 | 3287888.7314 | 8554412.0405 | 5838561.9932 | 26111346.6918 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 59792328.5965 | 129462810.323 | 5623.4133 | 4.6137 | 12959.66 | 28060.3557 | 264.2002 | 572.0483
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.0575 | 11.5882 | 1.432 | 4 | 11011.6053 | 23175.0221 | 224.4865 | 472.4542 | 113.3406 | 18.1227 | 49.6542 | 4291998.7474 | 0 | 2807678.5405 | 0 | 0 | 0 | 2390043.7741 | 3700991.2142 | 9629219.9615 | 6572140.4844 | 29392072.7221 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 63073054.6268 | 132743536.3532 | 7498.9421 | 5.7279 | 11011.6053 | 23175.0221 | 224.4865 | 472.4542
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.8085 | 13.6095 | 1.7234 | 4 | 9578.29 | 19684.9171 | 195.2664 | 401.3037 | 113.1883 | 17.904 | 65.2898 | 4752752.9001 | 0 | 3171476.9469 | 0 | 0 | 0 | 2519663.222 | 4073118.2969 | 10597418.2971 | 7232955.7429 | 32347385.4058 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 66028367.3105 | 135698849.037 | 10000 | 6.8935 | 9578.29 | 19684.9171 | 195.2664 | 401.3037
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.7512 | 15.5144 | 2.0098 | 4 | 8524.7523 | 17191.1326 | 173.7886 | 350.4645 | 112.8843 | 17.6616 | 69.0654 | 5154804.0776 | 0 | 3502190.7743 | 0 | 0 | 0 | 2595208.6213 | 4388359.3545 | 11417610.8642 | 7792754.0232 | 34850927.715 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 68531909.6197 | 138202391.3462 | 13335.2143 | 8.0392 | 8524.7523 | 17191.1326 | 173.7886 | 350.4645
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4151 | 17.2155 | 2.2754 | 4 | 7750.7262 | 15405.495 | 158.009 | 314.0619 | 112.4989 | 17.4173 | 73.2857 | 5489241.1237 | 0 | 3788779.1531 | 0 | 0 | 0 | 2623770.0549 | 4641698.2293 | 12076746.6495 | 8242627.7406 | 36862862.9511 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 70543844.8558 | 140214326.5823 | 17782.7941 | 9.1016 | 7750.7262 | 15405.495 | 158.009 | 314.0619
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5586 | 18.6642 | 2.5095 | 4 | 7181.5666 | 14122.2468 | 146.4059 | 287.9011 | 112.0942 | 17.1898 | 77.7464 | 5756441.0367 | 0 | 4026827.0555 | 0 | 0 | 0 | 2617238.6863 | 4836197.6436 | 12582794.2281 | 8588015.6113 | 38407514.2615 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 72088496.1662 | 141758977.8927 | 23713.7371 | 10.038 | 7181.5666 | 14122.2468 | 146.4059 | 287.9011
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2017 | 19.8567 | 2.7078 | 4 | 6762.2315 | 13194.6363 | 137.8572 | 268.9905 | 111.7116 | 16.9896 | 84.6202 | 5964622.3367 | 0 | 4218938.7461 | 0 | 0 | 0 | 2589661.84 | 4981556.9399 | 12960989.2998 | 8846141.5188 | 39561910.6813 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 73242892.586 | 142913374.3125 | 31622.7766 | 10.8312 | 6762.2315 | 13194.6363 | 137.8572 | 268.9905
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.505 | 20.8158 | 2.8708 | 4 | 6452.4955 | 12519.6943 | 131.5428 | 255.2309 | 111.373 | 16.8205 | 93.96 | 6124527.5457 | 0 | 4371092.1295 | 0 | 0 | 0 | 2552686.9013 | 5088839.5649 | 13240116.6833 | 9036651.6935 | 40413914.5182 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 74094896.4229 | 143765378.1494 | 42169.6503 | 11.4831 | 6452.4955 | 12519.6943 | 131.5428 | 255.2309
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2406 | 21.6641 | 3.0076 | 4 | 6222.4158 | 12013.5759 | 126.8524 | 244.913 | 111.0465 | 16.6626 | 90.8279 | 6262630.327 | 0 | 4503881.8655 | 0 | 0 | 0 | 2528400.6324 | 5185016.0017 | 13490348.0434 | 9207439.7386 | 41177716.6086 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 74858698.5133 | 144529180.2398 | 56234.1325 | 12.0305 | 6222.4158 | 12013.5759 | 126.8524 | 244.913
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4802 | 22.2562 | 3.1112 | 4 | 6051.0567 | 11649.347 | 123.359 | 237.4877 | 110.8093 | 16.5507 | 94.5268 | 6354509.659 | 0 | 4592603.7409 | 0 | 0 | 0 | 2491940.2712 | 5241230.9317 | 13636607.76 | 9307265.0005 | 41624157.3632 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 75305139.2679 | 144975620.9943 | 74989.4209 | 12.445 | 6051.0567 | 11649.347 | 123.359 | 237.4877
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9823 | 22.7149 | 3.1921 | 4 | 5923.5685 | 11380.0745 | 120.76 | 231.9982 | 110.6186 | 16.4622 | 89.7289 | 6424038.0021 | 0 | 4660836.533 | 0 | 0 | 0 | 2460386.7378 | 5282651.8964 | 13744376.6136 | 9380819.4575 | 41953109.2403 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 75634091.145 | 145304572.8715 | 100000 | 12.7683 | 5923.5685 | 11380.0745 | 120.76 | 231.9982
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.8628 | 23.0613 | 3.2541 | 4 | 5828.5499 | 11180.9978 | 118.8229 | 227.9398 | 110.4709 | 16.3945 | 99.0316 | 6475464.4511 | 0 | 4711954.3973 | 0 | 0 | 0 | 2433264.7631 | 5312066.6085 | 13820907.6606 | 9433053.4696 | 42186711.3501 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 75867693.2549 | 145538174.9813 | 133352.1432 | 13.0166 | 5828.5499 | 11180.9978 | 118.8229 | 227.9398
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3003 | 23.3265 | 3.3018 | 4 | 5757.63 | 11032.8837 | 117.3771 | 224.9203 | 110.3555 | 16.342 | 83.9641 | 6514295.8036 | 0 | 4750936.0905 | 0 | 0 | 0 | 2411485.0847 | 5333919.6217 | 13877764.7184 | 9471859.5799 | 42360260.8988 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76041242.8035 | 145711724.5299 | 177827.941 | 13.207 | 5757.63 | 11032.8837 | 117.3771 | 224.9203
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.3844 | 23.527 | 3.338 | 4 | 5704.6376 | 10922.6352 | 116.2968 | 222.6727 | 110.267 | 16.3021 | 96.0953 | 6543303.8055 | 0 | 4780280.9296 | 0 | 0 | 0 | 2394082.5908 | 5349890.2571 | 13919317.0355 | 9500219.8901 | 42487094.5086 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76168076.4133 | 145838558.1397 | 237137.3706 | 13.352 | 5704.6376 | 10922.6352 | 116.2968 | 222.6727
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.2151 | 23.6805 | 3.3656 | 4 | 5665.0066 | 10840.1921 | 115.4888 | 220.992 | 110.1984 | 16.2712 | 86.8582 | 6565372.5171 | 0 | 4802737.2611 | 0 | 0 | 0 | 2380739.2802 | 5362051.1328 | 13950957.1395 | 9521814.9112 | 42583672.2419 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76264654.1467 | 145935135.8731 | 316227.766 | 13.4624 | 5665.0066 | 10840.1921 | 115.4888 | 220.992
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8265 | 23.7939 | 3.3863 | 4 | 5635.3484 | 10778.8458 | 114.8842 | 219.7414 | 110.1474 | 16.2484 | 86.6251 | 6581524.4608 | 0 | 4819248.2807 | 0 | 0 | 0 | 2370070.8461 | 5370628.9991 | 13973274.9883 | 9537047.3016 | 42651794.8765 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76332776.7813 | 146003258.5077 | 421696.5034 | 13.5454 | 5635.3484 | 10778.8458 | 114.8842 | 219.7414
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3035 | 23.8821 | 3.4022 | 4 | 5613.1424 | 10732.7132 | 114.4315 | 218.8009 | 110.1074 | 16.2305 | 87.0895 | 6594075.4885 | 0 | 4832120.9405 | 0 | 0 | 0 | 2362259.494 | 5377497.81 | 13991146.2251 | 9549244.7879 | 42706344.746 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76387326.6507 | 146057808.3772 | 562341.3252 | 13.6087 | 5613.1424 | 10732.7132 | 114.4315 | 218.8009
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.6519 | 23.9468 | 3.414 | 4 | 5596.5095 | 10698.3586 | 114.0924 | 218.1005 | 110.078 | 16.2173 | 86.6385 | 6603211.6975 | 0 | 4841516.6835 | 0 | 0 | 0 | 2356062.0621 | 5382308.2728 | 14003662.0626 | 9557787.1042 | 42744547.8826 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76425529.7873 | 146096011.5138 | 749894.2093 | 13.6559 | 5596.5095 | 10698.3586 | 114.0924 | 218.1005
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.9077 | 23.9944 | 3.4228 | 4 | 5584.0476 | 10672.7329 | 113.8384 | 217.5781 | 110.0563 | 16.2077 | 91.5646 | 6609903.0638 | 0 | 4848411.9227 | 0 | 0 | 0 | 2351219.518 | 5385718.4568 | 14012534.6617 | 9563842.8354 | 42771630.4584 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76452612.3631 | 146123094.0896 | 1000000 | 13.6913 | 5584.0476 | 10672.7329 | 113.8384 | 217.5781
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1124 | 24.0322 | 3.4296 | 4 | 5574.7086 | 10653.3456 | 113.648 | 217.1829 | 110.0389 | 16.2 | 89.5088 | 6615248.8217 | 0 | 4853927.5376 | 0 | 0 | 0 | 2347832.5693 | 5388633.4822 | 14020118.9599 | 9569019.2748 | 42794780.6455 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76475762.5502 | 146146244.2766 | 1333521.4322 | 13.7183 | 5574.7086 | 10653.3456 | 113.648 | 217.1829
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.2561 | 24.059 | 3.4346 | 4 | 5567.7088 | 10638.9748 | 113.5053 | 216.8899 | 110.0267 | 16.1945 | 96.9528 | 6618996.7999 | 0 | 4857799.7727 | 0 | 0 | 0 | 2345052.5541 | 5390521.1594 | 14025030.3089 | 9572371.3714 | 42809771.9664 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76490753.8711 | 146161235.5975 | 1778279.41 | 13.7383 | 5567.7088 | 10638.9748 | 113.5053 | 216.8899
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.3681 | 24.0798 | 3.4384 | 4 | 5562.4617 | 10628.1412 | 113.3983 | 216.669 | 110.0171 | 16.1903 | 96.1797 | 6621916.5014 | 0 | 4860818.3689 | 0 | 0 | 0 | 2343049.552 | 5392055.9247 | 14029023.4532 | 9575096.7744 | 42821960.5746 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76502942.4793 | 146173424.2057 | 2371373.7057 | 13.7534 | 5562.4617 | 10628.1412 | 113.3983 | 216.669
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4413 | 24.0937 | 3.4411 | 4 | 5558.528 | 10620.1897 | 113.3181 | 216.5069 | 110.0108 | 16.1875 | 91.4169 | 6623820.4367 | 0 | 4862788.935 | 0 | 0 | 0 | 2341299.704 | 5392884.5395 | 14031179.3391 | 9576568.2108 | 42828541.1651 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76509523.0698 | 146180004.7963 | 3162277.6602 | 13.7643 | 5558.528 | 10620.1897 | 113.3181 | 216.5069
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5191 | 24.1078 | 3.4434 | 4 | 5555.5787 | 10613.8768 | 113.258 | 216.3782 | 110.0042 | 16.1846 | 101.424 | 6625845.9343 | 0 | 4864884.0015 | 0 | 0 | 0 | 2340490.1118 | 5394175.8186 | 14034538.9823 | 9578861.2364 | 42838796.0849 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76519777.9896 | 146190259.716 | 4216965.0343 | 13.7735 | 5555.5787 | 10613.8768 | 113.258 | 216.3782
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5534 | 24.1145 | 3.4448 | 4 | 5553.3675 | 10609.5147 | 113.2129 | 216.2893 | 110.0013 | 16.1832 | 93.8481 | 6626736.0492 | 0 | 4865806.7569 | 0 | 0 | 0 | 2339348.839 | 5394437.7416 | 14035220.4522 | 9579326.3536 | 42840876.1924 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76521858.0971 | 146192339.8235 | 5623413.2519 | 13.7794 | 5553.3675 | 10609.5147 | 113.2129 | 216.2893
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5922 | 24.1216 | 3.4461 | 4 | 5551.7094 | 10606.0416 | 113.1791 | 216.2185 | 109.9979 | 16.1818 | 98.3441 | 6627747.725 | 0 | 4866854.1559 | 0 | 0 | 0 | 2338783.2197 | 5395020.1893 | 14036735.8617 | 9580360.6517 | 42845501.8033 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76526483.708 | 146196965.4344 | 7498942.0933 | 13.7843 | 5551.7094 | 10606.0416 | 113.1791 | 216.2185
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.6265 | 24.1278 | 3.4471 | 4 | 5550.4662 | 10603.3595 | 113.1538 | 216.1638 | 109.995 | 16.1805 | 86.1711 | 6628639.1084 | 0 | 4867776.8179 | 0 | 0 | 0 | 2338470.7532 | 5395605.805 | 14038259.5137 | 9581400.5755 | 42850152.5738 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 76531134.4785 | 146201616.205 | 10000000 | 13.7882 | 5550.4662 | 10603.3595 | 113.1538 | 216.1638
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9906 | [19 empty] | 100 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1851 | [19 empty] | 133.3521 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.043931 | 0.0034983 | 4 | 2541244.1069 | 7619928.8064 | 51806.6984 | 155342.5554 | 60.6725 | 14.5246 | 25.7659 | 169550.8065 | 0 | 52330.7995 | 0 | 0 | 0 | 167912.7546 | 152019.8007 | 395524.3378 | 269953.4877 | 1207291.9868 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 35560317.4832 | 106627728.8414 | 177.8279 | 0.013993 | 2541244.1069 | 7619928.8064 | 51806.6984 | 155342.5554
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5829 | 0.10984 | 0.015994 | 4 | 580580.5734 | 1691392.5377 | 11835.9203 | 34481.3247 | 82.4208 | 16.6752 | 53.7004 | 381543.9947 | 0 | 167698.6363 | 0 | 0 | 0 | 351974.3509 | 351474.6229 | 914464.8715 | 624141.0652 | 2791297.5416 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 37144323.0379 | 108211734.3962 | 237.1374 | 0.063978 | 580580.5734 | 1691392.5377 | 11835.9203 | 34481.3247
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9861 | 0.28257 | 0.032758 | 4 | 290924.8136 | 833286.7824 | 5930.8958 | 16987.6782 | 90.0851 | 17.3229 | 40.1244 | 520144.9781 | 0 | 245550.5184 | 0 | 0 | 0 | 450794.1144 | 474430.9482 | 1234372.0081 | 842484.2594 | 3767776.8266 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 38120802.323 | 109188213.6812 | 316.2278 | 0.13103 | 290924.8136 | 833286.7824 | 5930.8958 | 16987.6782
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7519 | 0.5277 | 0.057416 | 4 | 170900.2573 | 480341.7899 | 3484.0329 | 9792.4171 | 96.1206 | 17.7942 | 42.2611 | 682071.7533 | 0 | 338525.4953 | 0 | 0 | 0 | 560325.2685 | 616559.7817 | 1604162.0782 | 1094873.5806 | 4896517.9576 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 39249543.454 | 110316954.8122 | 421.6965 | 0.22966 | 170900.2573 | 480341.7899 | 3484.0329 | 9792.4171
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9808 | 0.85986 | 0.09213 | 4 | 110051.7945 | 302897.4108 | 2243.5547 | 6174.9734 | 100.8871 | 18.1422 | 58.261 | 871011.2601 | 0 | 449536.1447 | 0 | 0 | 0 | 682269.0123 | 781098.4027 | 2032257.8184 | 1387057.7198 | 6203230.358 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 40556255.8544 | 111623667.2126 | 562.3413 | 0.36852 | 110051.7945 | 302897.4108 | 2243.5547 | 6174.9734
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8534 | 1.3054 | 0.13981 | 4 | 75297.3844 | 202380.2054 | 1535.039 | 4125.7942 | 104.7098 | 18.4044 | 46.1344 | 1095667.9951 | 0 | 584727.6914 | 0 | 0 | 0 | 823393.5912 | 976477.8183 | 2540594.98 | 1734008.2778 | 7754870.3537 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 42107895.8501 | 113175307.2083 | 749.8942 | 0.55922 | 75297.3844 | 202380.2054 | 1535.039 | 4125.7942
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4996 | 1.8864 | 0.20402 | 4 | 53816.123 | 140899.6762 | 1097.1145 | 2872.4305 | 107.7098 | 18.5964 | 59.4908 | 1358685.6934 | 0 | 746936.721 | 0 | 0 | 0 | 982726.5907 | 1204456.112 | 3133747.7355 | 2138847.2216 | 9565400.0743 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 43918425.5707 | 114985836.9289 | 1000 | 0.81608 | 53816.123 | 140899.6762 | 1097.1145 | 2872.4305
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1166 | 2.635 | 0.28929 | 4 | 39778.2828 | 101193.6683 | 810.9341 | 2062.9698 | 110.0497 | 18.7318 | 54.4826 | 1666143.9228 | 0 | 941336.9666 | 0 | 0 | 0 | 1162569.3637 | 1470319.5987 | 3825469.9918 | 2610961.8749 | 11676801.7185 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 46029827.2148 | 117097238.573 | 1333.5214 | 1.1572 | 39778.2828 | 101193.6683 | 810.9341 | 2062.9698
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9212 | 3.5876 | 0.40099 | 4 | 30223.8235 | 74531.0896 | 616.1535 | 1519.4171 | 111.8508 | 18.8176 | 43.9792 | 2023441.3321 | 0 | 1173070.0065 | 0 | 0 | 0 | 1363981.4572 | 1778592.1903 | 4627532.0398 | 3158385.7035 | 14125002.7294 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 48478028.2257 | 119545439.5839 | 1778.2794 | 1.604 | 30223.8235 | 74531.0896 | 616.1535 | 1519.4171
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.1024 | 4.7779 | 0.54492 | 4 | 23522.3593 | 56126.7191 | 479.5351 | 1144.2191 | 113.2005 | 18.8555 | 49.1337 | 2432586.8439 | 0 | 1445500.3598 | 0 | 0 | 0 | 1584312.1952 | 2130335.7656 | 5542696.6701 | 3783004.3683 | 16918436.2029 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 51271461.6992 | 122338873.0575 | 2371.3737 | 2.1797 | 23522.3593 | 56126.7191 | 479.5351 | 1144.2191
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8092 | 6.2337 | 0.72652 | 4 | 18718.0312 | 43172.7287 | 381.5924 | 880.1345 | 114.1684 | 18.8431 | 48.7431 | 2892420.1091 | 0 | 1760291.6359 | 0 | 0 | 0 | 1818553.6796 | 2523793.5156 | 6566393.0263 | 4481698.1664 | 20043150.1329 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 54396175.6293 | 125463586.9875 | 3162.2777 | 2.9061 | 18718.0312 | 43172.7287 | 381.5924 | 880.1345
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9964 | 7.953 | 0.94867 | 4 | 15222.1432 | 33950.3547 | 310.324 | 692.1239 | 114.7992 | 18.7753 | 71.9242 | 3391894.0109 | 0 | 2112608.4628 | 0 | 0 | 0 | 2053809.3324 | 2947741.6044 | 7669418.9897 | 5234536.0513 | 23410008.4515 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 57763033.9478 | 128830445.306 | 4216.965 | 3.7947 | 15222.1432 | 33950.3547 | 310.324 | 692.1239
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.3607 | 9.8914 | 1.2091 | 4 | 12656.8123 | 27351.3513 | 258.0262 | 557.5943 | 115.127 | 18.6486 | 69.1206 | 3909994.0077 | 0 | 2490275.8731 | 0 | 0 | 0 | 2271702.7538 | 3382069.3275 | 8799450.6323 | 6005805.8672 | 26859298.4616 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 61212323.958 | 132279735.3162 | 5623.4133 | 4.8363 | 12656.8123 | 27351.3513 | 258.0262 | 557.5943
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.346 | 11.9589 | 1.4984 | 4 | 10768.4156 | 22625.4714 | 219.5287 | 461.2508 | 115.1849 | 18.4642 | 83.6398 | 4418872.9159 | 0 | 2874989.5506 | 0 | 0 | 0 | 2453296.697 | 3801392.0738 | 9890442.4032 | 6750430.1685 | 30189423.809 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 64542449.3053 | 135609860.6636 | 7498.9421 | 5.9937 | 10768.4156 | 22625.4714 | 219.5287 | 461.2508
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.1534 | 14.0208 | 1.8 | 4 | 9379.4635 | 19250.0162 | 191.213 | 392.4376 | 115.024 | 18.2369 | 75.3349 | 4886984.889 | 0 | 3243046.6241 | 0 | 0 | 0 | 2582223.9908 | 4177779.6465 | 10869725.6598 | 7418811.1134 | 33178571.9236 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 67531597.42 | 138599008.7782 | 10000 | 7.1999 | 9379.4635 | 19250.0162 | 191.213 | 392.4376
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5345 | 16.0239 | 2.0995 | 4 | 8354.4351 | 16816.8901 | 170.3165 | 342.8351 | 114.6964 | 17.9761 | 73.9563 | 5309365.7233 | 0 | 3580989.5646 | 0 | 0 | 0 | 2670609.0896 | 4508776.1072 | 11730910.5538 | 8006587.4991 | 35807238.5377 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 70160264.034 | 141227675.3922 | 13335.2143 | 8.398 | 8354.4351 | 16816.8901 | 170.3165 | 342.8351
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.223 | 17.7552 | 2.3733 | 4 | 7600.519 | 15086.5049 | 154.9469 | 307.5588 | 114.2974 | 17.7227 | 74.4038 | 5647650.0768 | 0 | 3860005.9812 | 0 | 0 | 0 | 2697251.6674 | 4759914.0129 | 12384319.869 | 8452552.7829 | 37801694.3902 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 72154719.8866 | 143222131.2448 | 17782.7941 | 9.4934 | 7600.519 | 15086.5049 | 154.9469 | 307.5588
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.3808 | 19.2281 | 2.6142 | 4 | 7046.3868 | 13842.773 | 143.6501 | 282.2037 | 113.8809 | 17.4873 | 84.5887 | 5917695.0444 | 0 | 4091074.7894 | 0 | 0 | 0 | 2689109.8925 | 4952173.0932 | 12884538.5583 | 8793962.3168 | 39328553.6946 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 73681579.1909 | 144748990.5492 | 23713.7371 | 10.4566 | 7046.3868 | 13842.773 | 143.6501 | 282.2037
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.0434 | 20.4417 | 2.8179 | 4 | 6638.2241 | 12943.2811 | 135.3292 | 263.8663 | 113.4879 | 17.2802 | 91.4263 | 6128318.1483 | 0 | 4277390.1973 | 0 | 0 | 0 | 2660601.6441 | 5095860.896 | 13258384.7466 | 9049120.0221 | 40469675.6543 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 74822701.1507 | 145890112.5089 | 31622.7766 | 11.2715 | 6638.2241 | 12943.2811 | 135.3292 | 263.8663
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3512 | 21.4158 | 2.985 | 4 | 6336.7782 | 12288.8692 | 129.1838 | 250.5252 | 113.1412 | 17.1057 | 57.1062 | 6289747.4174 | 0 | 4424379.8016 | 0 | 0 | 0 | 2622693.5697 | 5201360.1076 | 13532872.0542 | 9236463.2497 | 41307516.2001 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 75660541.6965 | 146727953.0547 | 42169.6503 | 11.9399 | 6336.7782 | 12288.8692 | 129.1838 | 250.5252
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4929 | 22.1808 | 3.1188 | 4 | 6113.5383 | 11810.2824 | 124.6327 | 240.7686 | 112.85 | 16.9638 | 50.3265 | 6411778.2234 | 0 | 4538229.1266 | 0 | 0 | 0 | 2582604.9886 | 5277718.8121 | 13731541.74 | 9372059.3925 | 41913932.2831 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 76266957.7795 | 147334369.1377 | 56234.1325 | 12.4751 | 6113.5383 | 11810.2824 | 124.6327 | 240.7686
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6982 | 22.7758 | 3.2242 | 4 | 5947.7986 | 11458.2454 | 121.2539 | 233.5918 | 112.6124 | 16.8504 | 58.1282 | 6503847.5935 | 0 | 4625850.2331 | 0 | 0 | 0 | 2545271.18 | 5333237.9126 | 13875991.051 | 9470649.0154 | 42354846.9857 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 76707872.482 | 147775283.8403 | 74989.4209 | 12.8969 | 5947.7986 | 11458.2454 | 121.2539 | 233.5918
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.164 | 23.2351 | 3.3063 | 4 | 5824.4826 | 11198.082 | 118.74 | 228.288 | 112.4221 | 16.7612 | 62.0269 | 6573262.554 | 0 | 4692975.0051 | 0 | 0 | 0 | 2512888.4282 | 5373859.135 | 13981679.1393 | 9542783.3073 | 42677447.5689 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77030473.0652 | 148097884.4235 | 100000 | 13.2253 | 5824.4826 | 11198.082 | 118.74 | 228.288
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0297 | 23.584 | 3.3695 | 4 | 5732.5681 | 11005.4825 | 116.8662 | 224.3616 | 112.2739 | 16.6924 | 58.0506 | 6624962.4818 | 0 | 4743604.1598 | 0 | 0 | 0 | 2485487.3053 | 5403081.0393 | 14057708.5399 | 9594674.9355 | 42909518.4616 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77262543.958 | 148329955.3162 | 133352.1432 | 13.4778 | 5732.5681 | 11005.4825 | 116.8662 | 224.3616
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4575 | 23.8514 | 3.4179 | 4 | 5663.9618 | 10862.1394 | 115.4675 | 221.4394 | 112.158 | 16.6391 | 65.0979 | 6664050.7066 | 0 | 4782259.7416 | 0 | 0 | 0 | 2463561.8211 | 5424850.185 | 14114347.3916 | 9633332.1156 | 43082401.9615 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77435427.4578 | 148502838.8161 | 177827.941 | 13.6716 | 5663.9618 | 10862.1394 | 115.4675 | 221.4394
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.5272 | 24.0523 | 3.4547 | 4 | 5612.6962 | 10755.5443 | 114.4224 | 219.2663 | 112.0697 | 16.5988 | 70.9591 | 6693059.8065 | 0 | 4811167.2253 | 0 | 0 | 0 | 2445896.827 | 5440548.305 | 14155190.6796 | 9661208.4989 | 43207071.3423 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77560096.8386 | 148627508.1969 | 237137.3706 | 13.8187 | 5612.6962 | 10755.5443 | 114.4224 | 219.2663
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3398 | 24.205 | 3.4826 | 4 | 5574.3556 | 10675.9355 | 113.6408 | 217.6434 | 112.0019 | 16.5679 | 100.6659 | 6714942.6564 | 0 | 4833099.9758 | 0 | 0 | 0 | 2432205.0938 | 5452296.6132 | 14185757.3676 | 9682070.8916 | 43300372.5985 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77653398.0948 | 148720809.4531 | 316227.766 | 13.9305 | 5574.3556 | 10675.9355 | 113.6408 | 217.6434
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.9466 | 24.3193 | 3.5037 | 4 | 5545.6624 | 10616.5556 | 113.0558 | 216.4328 | 111.9507 | 16.5447 | 96.5258 | 6731193.1318 | 0 | 4849460.2598 | 0 | 0 | 0 | 2421482.7638 | 5460833.1006 | 14207967.5569 | 9697229.8021 | 43368166.6151 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77721192.1115 | 148788603.4697 | 421696.5034 | 14.0148 | 5545.6624 | 10616.5556 | 113.0558 | 216.4328
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.407 | 24.406 | 3.5196 | 4 | 5524.1784 | 10572.0985 | 112.6178 | 215.5265 | 111.9117 | 16.527 | 98.0071 | 6743474.6653 | 0 | 4861866.0365 | 0 | 0 | 0 | 2413341.5796 | 5467286.0897 | 14224756.9109 | 9708688.8812 | 43419414.1631 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77772439.6595 | 148839851.0177 | 562341.3252 | 14.0786 | 5524.1784 | 10572.0985 | 112.6178 | 215.5265
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.7554 | 24.4716 | 3.5317 | 4 | 5508.0863 | 10538.8008 | 112.2898 | 214.8477 | 111.8819 | 16.5136 | 103.4196 | 6752738.5063 | 0 | 4871247.3929 | 0 | 0 | 0 | 2407178.8609 | 5472154.2565 | 14237422.8821 | 9717333.6668 | 43458075.5655 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77811101.0619 | 148878512.4201 | 749894.2093 | 14.1267 | 5508.0863 | 10538.8008 | 112.2898 | 214.8477
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.0138 | 24.5203 | 3.5407 | 4 | 5496.0294 | 10513.9243 | 112.044 | 214.3406 | 111.8598 | 16.5037 | 63.9511 | 6759592.5739 | 0 | 4878202.1179 | 0 | 0 | 0 | 2402419.7129 | 5475683.6178 | 14246605.5564 | 9723601.0307 | 43486104.6096 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77839130.106 | 148906541.4642 | 1000000 | 14.1628 | 5496.0294 | 10513.9243 | 112.044 | 214.3406
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.2159 | 24.5582 | 3.5476 | 4 | 5486.9938 | 10495.1714 | 111.8598 | 213.9583 | 111.8425 | 16.4959 | 70.7353 | 6764943.9005 | 0 | 4883639.2969 | 0 | 0 | 0 | 2398997.2708 | 5478556.3826 | 14254079.9011 | 9728702.4246 | 43508919.1766 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77861944.6729 | 148929356.0312 | 1333521.4322 | 14.1903 | 5486.9938 | 10495.1714 | 111.8598 | 213.9583
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.3498 | 24.5838 | 3.5525 | 4 | 5480.2214 | 10481.3905 | 111.7217 | 213.6773 | 111.8309 | 16.4907 | 58.7459 | 6768484.7186 | 0 | 4887242.3415 | 0 | 0 | 0 | 2396011.0819 | 5480177.8754 | 14258298.6927 | 9731581.8365 | 43521796.5467 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77874822.043 | 148942233.4012 | 1778279.41 | 14.2102 | 5480.2214 | 10481.3905 | 111.7217 | 213.6773
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.4546 | 24.6037 | 3.5563 | 4 | 5475.1447 | 10470.9982 | 111.6182 | 213.4655 | 111.8219 | 16.4866 | 59.7268 | 6771253.8407 | 0 | 4890061.8661 | 0 | 0 | 0 | 2393857.9891 | 5481517.7414 | 14261784.7492 | 9733961.1417 | 43532437.3282 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77885462.8246 | 148952874.1828 | 2371373.7057 | 14.2253 | 5475.1447 | 10470.9982 | 111.6182 | 213.4655
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5519 | 24.6217 | 3.5594 | 4 | 5471.3388 | 10462.9294 | 111.5406 | 213.301 | 111.8135 | 16.4829 | 68.4634 | 6773822.3051 | 0 | 4892677.0061 | 0 | 0 | 0 | 2392654.7447 | 5483070.0819 | 14265823.6207 | 9736717.7545 | 43544765.513 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77897791.0094 | 148965202.3676 | 3162277.6602 | 14.2374 | 5471.3388 | 10462.9294 | 111.5406 | 213.301
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6056 | 24.632 | 3.5614 | 4 | 5468.4853 | 10457.1705 | 111.4825 | 213.1836 | 111.8089 | 16.4808 | 79.2961 | 6775238.7818 | 0 | 4894121.4099 | 0 | 0 | 0 | 2391316.7472 | 5483664.0062 | 14267368.8899 | 9737772.4325 | 43549482.2674 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77902507.7638 | 148969919.122 | 4216965.0343 | 14.2457 | 5468.4853 | 10457.1705 | 111.4825 | 213.1836
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6593 | 24.642 | 3.5631 | 4 | 5466.3458 | 10452.6516 | 111.4389 | 213.0914 | 111.8042 | 16.4787 | 86.8472 | 6776656.0482 | 0 | 4895565.7071 | 0 | 0 | 0 | 2390612.6268 | 5484505.409 | 14269558.0475 | 9739266.5775 | 43556164.416 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77909189.9124 | 148976601.2706 | 5623413.2519 | 14.2525 | 5466.3458 | 10452.6516 | 111.4389 | 213.0914
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6936 | 24.6485 | 3.5643 | 4 | 5464.7416 | 10449.3542 | 111.4061 | 213.0242 | 111.8013 | 16.4774 | 89.1959 | 6777559.3893 | 0 | 4896487.0134 | 0 | 0 | 0 | 2389948.3051 | 5484957.9361 | 14270735.4301 | 9740070.1653 | 43559758.2394 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77912783.7358 | 148980195.094 | 7498942.0933 | 14.2574 | 5464.7416 | 10449.3542 | 111.4061 | 213.0242
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.7176 | 24.6531 | 3.5652 | 4 | 5463.5388 | 10446.9062 | 111.3816 | 212.9743 | 111.7992 | 16.4764 | 95.2857 | 6778193.8767 | 0 | 4897134.392 | 0 | 0 | 0 | 2389413.1438 | 5485249.1509 | 14271493.1112 | 9740587.2983 | 43562070.9729 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 77915096.4692 | 148982507.8275 | 10000000 | 14.2609 | 5463.5388 | 10446.9062 | 111.3816 | 212.9743
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5748 | [19 empty] | 100 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9041 | [19 empty] | 133.3521 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | -0.045198 | 0.0035813 | 4 | 2530283.4046 | 7589741.4147 | 51583.2497 | 154727.1446 | 60.9012 | 14.7665 | 22.6457 | 171099.9935 | 0 | 52084.6682 | 0 | 0 | 0 | 169443.4548 | 153124.9655 | 398399.7499 | 271916.0156 | 1216068.8474 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 36246998.0263 | 108725110.2298 | 177.8279 | 0.014325 | 2530283.4046 | 7589741.4147 | 51583.2497 | 154727.1446
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6755 | 0.11732 | 0.016995 | 4 | 557842.2344 | 1624026.1237 | 11372.3685 | 33107.9692 | 83.7656 | 17.0268 | 49.4856 | 395412.4474 | 0 | 173503.2337 | 0 | 0 | 0 | 364371.4153 | 363981.9676 | 947006.4166 | 646351.3384 | 2890626.8189 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 37921555.9978 | 110399668.2014 | 237.1374 | 0.067979 | 557842.2344 | 1624026.1237 | 11372.3685 | 33107.9692
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1176 | 0.29754 | 0.034675 | 4 | 280711.1391 | 803271.3095 | 5722.6763 | 16375.7721 | 91.5773 | 17.6829 | 42.4272 | 539254.7809 | 0 | 253894.2675 | 0 | 0 | 0 | 467056.9416 | 491480.3361 | 1278731.018 | 872760.1951 | 3903177.5392 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 38934106.7181 | 111412218.9216 | 316.2278 | 0.1387 | 280711.1391 | 803271.3095 | 5722.6763 | 16375.7721
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9151 | 0.55115 | 0.060635 | 4 | 165298.1817 | 464129.3678 | 3369.827 | 9461.9049 | 97.6757 | 18.1559 | 53.3261 | 705715.2956 | 0 | 348982.7765 | 0 | 0 | 0 | 579094.0429 | 637178.9248 | 1657808.859 | 1131488.6109 | 5060268.5096 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 40091197.6885 | 112569309.8921 | 421.6965 | 0.24254 | 165298.1817 | 464129.3678 | 3369.827 | 9461.9049
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2003 | 0.89646 | 0.097173 | 4 | 106620.8188 | 293087.6744 | 2173.6096 | 5974.9887 | 102.5319 | 18.5079 | 47.9888 | 901374.2616 | 0 | 463342.7709 | 0 | 0 | 0 | 705405.4167 | 807347.7552 | 2100553.2491 | 1433670.7546 | 6411694.208 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 41442623.3869 | 113920735.5904 | 562.3413 | 0.38869 | 106620.8188 | 293087.6744 | 2173.6096 | 5974.9887
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1286 | 1.3573 | 0.1473 | 4 | 73043.1957 | 196056.5441 | 1489.0843 | 3996.8778 | 106.4062 | 18.7716 | 58.4697 | 1132720.7617 | 0 | 601828.0297 | 0 | 0 | 0 | 850101.8449 | 1008013.7481 | 2622645.0006 | 1790009.1029 | 8005318.4879 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 43036247.6668 | 115514359.8703 | 749.8942 | 0.58919 | 73043.1957 | 196056.5441 | 1489.0843 | 3996.8778
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8675 | 1.9611 | 0.21483 | 4 | 52261.2707 | 136604.3203 | 1065.4167 | 2784.8638 | 109.4655 | 18.9654 | 68.2141 | 1405183.1732 | 0 | 768975.6675 | 0 | 0 | 0 | 1015279.836 | 1243881.0839 | 3236323.4252 | 2208857.2375 | 9878500.4232 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 44909429.6021 | 117387541.8056 | 1000 | 0.85933 | 52261.2707 | 136604.3203 | 1065.4167 | 2784.8638
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5887 | 2.7373 | 0.30444 | 4 | 38666.7209 | 98184.8611 | 788.2734 | 2001.6312 | 111.8436 | 19.1011 | 49.5164 | 1722796.6814 | 0 | 968746.2182 | 0 | 0 | 0 | 1200745.1784 | 1517992.3504 | 3949504.7127 | 2695618.1207 | 12055403.2618 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 47086332.4407 | 119564444.6442 | 1333.5214 | 1.2177 | 38666.7209 | 98184.8611 | 788.2734 | 2001.6312
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.5083 | 3.7227 | 0.42169 | 4 | 29406.8526 | 72375.6008 | 599.4985 | 1475.4745 | 113.6701 | 19.186 | 60.4995 | 2090942.5617 | 0 | 1206269.6014 | 0 | 0 | 0 | 1407431.2688 | 1834810.9385 | 4773801.6904 | 3258217.7455 | 14571473.8064 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 49602402.9852 | 122080515.1888 | 1778.2794 | 1.6868 | 29406.8526 | 72375.6008 | 599.4985 | 1475.4745
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8406 | 4.955 | 0.5727 | 4 | 22908.3061 | 54547.1407 | 467.0168 | 1112.0172 | 115.0406 | 19.2218 | 67.8486 | 2513061.6983 | 0 | 1485890.3425 | 0 | 0 | 0 | 1634207.6209 | 2196932.2681 | 5715967.1088 | 3901265.0031 | 17447324.0416 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 52478253.2205 | 124956365.4241 | 2371.3737 | 2.2908 | 22908.3061 | 54547.1407 | 467.0168 | 1112.0172
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.7003 | 6.4576 | 0.76287 | 4 | 18247.6875 | 41999.5708 | 372.0038 | 856.2181 | 116.0196 | 19.2055 | 77.9605 | 2985890.2867 | 0 | 1807950.5327 | 0 | 0 | 0 | 1873777.7981 | 2600371.2608 | 6765632.6112 | 4617683.277 | 20651305.7665 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 55682234.9453 | 128160347.1489 | 3162.2777 | 3.0515 | 18247.6875 | 41999.5708 | 372.0038 | 856.2181
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0318 | 8.2268 | 0.99492 | 4 | 14855.8368 | 33067.8075 | 302.8563 | 674.132 | 116.6545 | 19.1322 | 39.4118 | 3497852.7494 | 0 | 2167316.449 | 0 | 0 | 0 | 2112943.9769 | 3033464.1384 | 7892451.4389 | 5386760.2807 | 24090789.0333 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 59121718.2121 | 131599830.4157 | 4216.965 | 3.9797 | 14855.8368 | 33067.8075 | 302.8563 | 674.132
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5398 | 10.2183 | 1.2663 | 4 | 12367.0713 | 26676.316 | 252.1195 | 543.8328 | 116.9811 | 18.9979 | 37.2434 | 4028164.4317 | 0 | 2552091.4844 | 0 | 0 | 0 | 2334038.9118 | 3476574.9829 | 9045334.9619 | 6173626.9745 | 27609831.7473 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 62640760.9261 | 135118873.1297 | 5623.4133 | 5.0651 | 12367.0713 | 26676.316 | 252.1195 | 543.8328
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9681 | 12.3875 | 1.5701 | 4 | 10524.9781 | 22065.6762 | 214.5659 | 449.8387 | 117.0316 | 18.7993 | 53.3444 | 4561107.3376 | 0 | 2938874.778 | 0 | 0 | 0 | 2530917.0365 | 3912050.6693 | 10178353.3696 | 6946935.319 | 31068238.5101 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 66099167.689 | 138577279.8925 | 7498.9421 | 6.2802 | 10524.9781 | 22065.6762 | 214.5659 | 449.8387
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9024 | 14.5021 | 1.8834 | 4 | 9170.8665 | 18791.3152 | 186.9605 | 383.0864 | 116.8538 | 18.5596 | 52.3811 | 5038348.6631 | 0 | 3298093.4467 | 0 | 0 | 0 | 2660442.4851 | 4288784.992 | 11158538.7985 | 7615932.015 | 34060140.4005 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 69091069.5794 | 141569181.7829 | 10000 | 7.5338 | 9170.8665 | 18791.3152 | 186.9605 | 383.0864
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.9325 | 16.4803 | 2.189 | 4 | 8177.0746 | 16454.5839 | 166.7007 | 335.4489 | 116.5248 | 18.2983 | 49.2831 | 5451694.5139 | 0 | 3621575.7397 | 0 | 0 | 0 | 2733245.6668 | 4604541.2089 | 11980071.7044 | 8176645.1041 | 36567773.9378 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 71598703.1167 | 144076815.3202 | 13335.2143 | 8.756 | 8177.0746 | 16454.5839 | 166.7007 | 335.4489
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.6157 | 18.2366 | 2.4705 | 4 | 7447.567 | 14782.065 | 151.8287 | 301.3524 | 116.1177 | 18.0376 | 56.3086 | 5793527.5467 | 0 | 3899694.8692 | 0 | 0 | 0 | 2757972.6337 | 4855966.0694 | 12634227.6168 | 8623119.9559 | 38564508.6917 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 73595437.8706 | 146073550.0741 | 17782.7941 | 9.8818 | 7447.567 | 14782.065 | 151.8287 | 301.3524
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7445 | 19.7266 | 2.7172 | 4 | 6911.4064 | 13579.919 | 140.8984 | 276.845 | 115.6953 | 17.7965 | 60.4212 | 6065645.5333 | 0 | 4129379.1233 | 0 | 0 | 0 | 2747772.1983 | 5047690.7734 | 13133055.9687 | 8963580.556 | 40087124.153 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 75118053.3319 | 147596165.5354 | 23713.7371 | 10.8687 | 6911.4064 | 13579.919 | 140.8984 | 276.845
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.354 | 20.9492 | 2.9252 | 4 | 6516.4737 | 12710.6961 | 132.8471 | 259.1247 | 115.2993 | 17.5857 | 56.0082 | 6277020.6639 | 0 | 4313800.4147 | 0 | 0 | 0 | 2717040.0325 | 5190065.8333 | 13503486.6694 | 9216407.1208 | 41217820.7345 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 76248749.9134 | 148726862.1169 | 31622.7766 | 11.7009 | 6516.4737 | 12710.6961 | 132.8471 | 259.1247
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.6157 | 21.9297 | 3.0956 | 4 | 6224.781 | 12078.0517 | 126.9006 | 246.2274 | 114.9508 | 17.4084 | 61.2108 | 6438970.3609 | 0 | 4459215.8069 | 0 | 0 | 0 | 2677521.0791 | 5294525.8263 | 13775270.1434 | 9401904.9264 | 42047408.1429 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 77078337.3218 | 149556449.5253 | 42169.6503 | 12.3825 | 6224.781 | 12078.0517 | 126.9006 | 246.2274
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.7233 | 22.7 | 3.2319 | 4 | 6008.7474 | 11615.1515 | 122.4964 | 236.7906 | 114.6584 | 17.2643 | 66.1354 | 6561491.0291 | 0 | 4571913.1978 | 0 | 0 | 0 | 2636398.2687 | 5370222.9733 | 13972218.5924 | 9536326.2897 | 42648570.3512 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 77679499.5301 | 150157611.7336 | 56234.1325 | 12.9277 | 6008.7474 | 11615.1515 | 122.4964 | 236.7906
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9091 | 23.3002 | 3.3393 | 4 | 5848.3456 | 11274.4216 | 119.2264 | 229.8443 | 114.4193 | 17.1489 | 89.4398 | 6654153.4911 | 0 | 4658844.9537 | 0 | 0 | 0 | 2598550.6507 | 5425504.1473 | 14116048.8673 | 9634493.4077 | 43087595.5178 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 78118524.6967 | 150596636.9002 | 74989.4209 | 13.3574 | 5848.3456 | 11274.4216 | 119.2264 | 229.8443
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3381 | 23.7599 | 3.4227 | 4 | 5728.9931 | 11022.924 | 116.7933 | 224.7172 | 114.2297 | 17.0589 | 93.823 | 6723405.9933 | 0 | 4724851.5289 | 0 | 0 | 0 | 2565296.0013 | 5465285.8741 | 14219552.7602 | 9705136.9414 | 43403529.0993 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 78434458.2781 | 150912570.4817 | 100000 | 13.6908 | 5728.9931 | 11022.924 | 116.7933 | 224.7172
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.1823 | 24.1101 | 3.4868 | 4 | 5640.0277 | 10836.5888 | 114.9796 | 220.9185 | 114.0815 | 16.9894 | 86.4518 | 6775177.9985 | 0 | 4774814.5748 | 0 | 0 | 0 | 2537441.4563 | 5494099.2716 | 14294519.3099 | 9756303.152 | 43632355.7631 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 78663284.942 | 151141397.1455 | 133352.1432 | 13.9473 | 5640.0277 | 10836.5888 | 114.9796 | 220.9185
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.5829 | 24.3767 | 3.5359 | 4 | 5573.6197 | 10698.056 | 113.6258 | 218.0943 | 113.9666 | 16.9359 | 89.4471 | 6814029.0812 | 0 | 4812672.4851 | 0 | 0 | 0 | 2514944.8162 | 5515242.0892 | 14349528.5843 | 9793848.1121 | 43800265.1681 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 78831194.347 | 151309306.5505 | 177827.941 | 14.1436 | 5573.6197 | 10698.056 | 113.6258 | 218.0943
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.6519 | 24.5803 | 3.5734 | 4 | 5523.9949 | 10594.7139 | 112.6141 | 215.9876 | 113.8774 | 16.8947 | 88.2288 | 6843409.5711 | 0 | 4841516.6835 | 0 | 0 | 0 | 2497336.1083 | 5531082.3215 | 14390741.6196 | 9821976.8556 | 43926063.1595 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 78956992.3384 | 151435104.542 | 237137.3706 | 14.2935 | 5523.9949 | 10594.7139 | 112.6141 | 215.9876
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4607 | 24.7344 | 3.6018 | 4 | 5486.8803 | 10517.5803 | 111.8575 | 214.4151 | 113.8091 | 16.8633 | 76.7462 | 6865482.9443 | 0 | 4863312.7228 | 0 | 0 | 0 | 2483617.2247 | 5542841.0278 | 14421335.3613 | 9842857.7129 | 44019446.9937 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79050376.1725 | 151528488.3761 | 316227.766 | 14.4072 | 5486.8803 | 10517.5803 | 111.8575 | 214.4151
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.0481 | 24.8471 | 3.623 | 4 | 5459.1041 | 10460.2953 | 111.2912 | 213.2473 | 113.7591 | 16.8403 | 66.7902 | 6881424.2061 | 0 | 4879124.2429 | 0 | 0 | 0 | 2472491.6377 | 5550885.6338 | 14442265.776 | 9857143.151 | 44083334.6476 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79114263.8265 | 151592376.03 | 421696.5034 | 14.4922 | 5459.1041 | 10460.2953 | 111.2912 | 213.2473
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5083 | 24.9349 | 3.6393 | 4 | 5438.3064 | 10417.1847 | 110.8672 | 212.3684 | 113.7196 | 16.8223 | 63.5981 | 6893868.6597 | 0 | 4891506.4628 | 0 | 0 | 0 | 2464388.2765 | 5557407.7257 | 14459234.9211 | 9868724.9412 | 44135130.987 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79166060.1659 | 151644172.3694 | 562341.3252 | 14.5571 | 5438.3064 | 10417.1847 | 110.8672 | 212.3684
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8567 | 25.0014 | 3.6515 | 4 | 5422.7281 | 10384.8926 | 110.5496 | 211.7101 | 113.6896 | 16.8086 | 72.2498 | 6903259.0438 | 0 | 4900873.5922 | 0 | 0 | 0 | 2458258.9017 | 5562332.6997 | 14472048.6933 | 9877470.6041 | 44174243.5349 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79205172.7138 | 151683284.9173 | 749894.2093 | 14.6061 | 5422.7281 | 10384.8926 | 110.5496 | 211.7101
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1003 | 25.0484 | 3.6606 | 4 | 5411.056 | 10360.9874 | 110.3117 | 211.2227 | 113.6685 | 16.799 | 80.05 | 6909807.3732 | 0 | 4907419.6249 | 0 | 0 | 0 | 2453184.1322 | 5565460.3408 | 14480186.1739 | 9883024.6017 | 44199082.2466 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79230011.4255 | 151708123.629 | 1000000 | 14.6422 | 5411.056 | 10360.9874 | 110.3117 | 211.2227
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.3024 | 25.0868 | 3.6676 | 4 | 5402.3088 | 10342.7988 | 110.1334 | 210.8519 | 113.651 | 16.791 | 61.1233 | 6915232.4798 | 0 | 4912848.6985 | 0 | 0 | 0 | 2449783.9847 | 5568367.4136 | 14487749.7809 | 9888186.9189 | 44222169.2763 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79253098.4552 | 151731210.6587 | 1333521.4322 | 14.6702 | 5402.3088 | 10342.7988 | 110.1334 | 210.8519
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.4487 | 25.1148 | 3.6728 | 4 | 5395.7525 | 10329.2517 | 109.9997 | 210.5758 | 113.6383 | 16.7852 | 60.5271 | 6919155.2311 | 0 | 4916779.1604 | 0 | 0 | 0 | 2447091.7644 | 5570380.2008 | 14492986.6404 | 9891761.1832 | 44238154.1804 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79269083.3592 | 151747195.5628 | 1778279.41 | 14.691 | 5395.7525 | 10329.2517 | 109.9997 | 210.5758
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.5607 | 25.1362 | 3.6767 | 4 | 5390.8378 | 10319.0668 | 109.8995 | 210.3681 | 113.6286 | 16.7808 | 59.8173 | 6922156.5535 | 0 | 4919788.6666 | 0 | 0 | 0 | 2445113.1364 | 5571952.759 | 14497078.1143 | 9894553.6982 | 44250642.9279 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79281572.1067 | 151759684.3103 | 2371373.7057 | 14.7067 | 5390.8378 | 10319.0668 | 109.8995 | 210.3681
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6339 | 25.1504 | 3.6795 | 4 | 5387.1532 | 10311.594 | 109.8244 | 210.2158 | 113.6222 | 16.7779 | 58.8492 | 6924113.7038 | 0 | 4921753.3025 | 0 | 0 | 0 | 2443373.9459 | 5572803.9714 | 14499292.7943 | 9896065.2628 | 44257402.9808 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79288332.1597 | 151766444.3632 | 3162277.6602 | 14.718 | 5387.1532 | 10311.594 | 109.8244 | 210.2158
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6922 | 25.1617 | 3.6817 | 4 | 5384.3908 | 10305.9415 | 109.7681 | 210.1006 | 113.6171 | 16.7756 | 90.8377 | 6925674.0247 | 0 | 4923319.897 | 0 | 0 | 0 | 2442145.2352 | 5573544.2712 | 14501218.9025 | 9897379.8712 | 44263282.2017 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79294211.3805 | 151772323.5841 | 4216965.0343 | 14.7267 | 5384.3908 | 10305.9415 | 109.7681 | 210.1006
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7434 | 25.1713 | 3.6834 | 4 | 5382.3196 | 10301.5959 | 109.7259 | 210.012 | 113.6126 | 16.7736 | 99.9365 | 6927041.0578 | 0 | 4924692.1929 | 0 | 0 | 0 | 2441389.3136 | 5574317.8001 | 14503231.4661 | 9898753.4872 | 44269425.3177 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79300354.4966 | 151778466.7001 | 5623413.2519 | 14.7335 | 5382.3196 | 10301.5959 | 109.7259 | 210.012
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7823 | 25.1787 | 3.6847 | 4 | 5380.7665 | 10298.3299 | 109.6942 | 209.9454 | 113.6092 | 16.772 | 91.0349 | 6928081.0537 | 0 | 4925736.4472 | 0 | 0 | 0 | 2440834.0083 | 5574914.0886 | 14504782.8864 | 9899812.3634 | 44274160.8475 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79305090.0264 | 151783202.2299 | 7498942.0933 | 14.7386 | 5380.7665 | 10298.3299 | 109.6942 | 209.9454
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7971 | 25.1818 | 3.6855 | 4 | 5379.602 | 10296.0918 | 109.6705 | 209.8998 | 113.6079 | 16.7714 | 94.3931 | 6928475.9797 | 0 | 4926134.2438 | 0 | 0 | 0 | 2440089.9714 | 5574933.076 | 14504832.2878 | 9899846.0809 | 44274311.6396 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 79305240.8185 | 151783353.022 | 10000000 | 14.7418 | 5379.602 | 10296.0918 | 109.6705 | 209.8998

## Water (R245fa)
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0001 | [19 empty] | 100 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.2086 | [19 empty] | 133.3521 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.4149 | [19 empty] | 177.8279 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6253 | [19 empty] | 237.1374 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4082 | [19 empty] | 316.2278 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.3461 | [19 empty] | 421.6965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1464 | [19 empty] | 562.3413 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4556 | [19 empty] | 749.8942 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3732 | [19 empty] | 1000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6039 | [19 empty] | 1333.5214 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 168.99 | [19 empty] | 1778.2794 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4716 | [19 empty] | 2371.3737 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4055 | [19 empty] | 3162.2777 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.4075 | [19 empty] | 4216.965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.3763 | [19 empty] | 5623.4133 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.4794 | [19 empty] | 7498.9421 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.4404 | [19 empty] | 10000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.5742 | [19 empty] | 13335.2143 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.366 | [19 empty] | 17782.7941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5679 | [19 empty] | 23713.7371 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.1948 | [19 empty] | 31622.7766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 178.4138 | [19 empty] | 42169.6503 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7167 | [19 empty] | 56234.1325 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1549 | [19 empty] | 74989.4209 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.9705 | [19 empty] | 100000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8331 | [19 empty] | 133352.1432 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.3931 | [19 empty] | 177827.941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7066 | [19 empty] | 237137.3706 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5714 | [19 empty] | 316227.766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.4281 | [19 empty] | 421696.5034 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.979 | [19 empty] | 562341.3252 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6409 | [19 empty] | 749894.2093 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 182.5033 | [19 empty] | 1000000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5393 | [19 empty] | 1333521.4322 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4723 | [19 empty] | 1778279.41 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4678 | [19 empty] | 2371373.7057 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4043 | [19 empty] | 3162277.6602 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8162 | [19 empty] | 4216965.0343 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6403 | [19 empty] | 5623413.2519 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.1138 | [19 empty] | 7498942.0933 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.9637 | [19 empty] | 10000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.0201 | [19 empty] | 100 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3769 | [19 empty] | 133.3521 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 160.0777 | [19 empty] | 177.8279 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1838 | [19 empty] | 237.1374 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8929 | [19 empty] | 316.2278 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7366 | [19 empty] | 421.6965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.5451 | [19 empty] | 562.3413 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1031 | [19 empty] | 749.8942 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.24 | [19 empty] | 1000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0868 | [19 empty] | 1333.5214 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8937 | [19 empty] | 1778.2794 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5045 | [19 empty] | 2371.3737 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4386 | [19 empty] | 3162.2777 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 183.5458 | [19 empty] | 4216.965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.6906 | [19 empty] | 5623.4133 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.6415 | [19 empty] | 7498.9421 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.0397 | [19 empty] | 10000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.3302 | [19 empty] | 13335.2143 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8887 | [19 empty] | 17782.7941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.3855 | [19 empty] | 23713.7371 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.688 | [19 empty] | 31622.7766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8211 | [19 empty] | 42169.6503 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.5601 | [19 empty] | 56234.1325 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7279 | [19 empty] | 74989.4209 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 183.477 | [19 empty] | 100000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.9969 | [19 empty] | 133352.1432 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.1686 | [19 empty] | 177827.941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6775 | [19 empty] | 237137.3706 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8959 | [19 empty] | 316227.766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2923 | [19 empty] | 421696.5034 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.1141 | [19 empty] | 562341.3252 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.9284 | [19 empty] | 749894.2093 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3555 | [19 empty] | 1000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4262 | [19 empty] | 1333521.4322 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.0337 | [19 empty] | 1778279.41 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 169.9893 | [19 empty] | 2371373.7057 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6328 | [19 empty] | 3162277.6602 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.404 | [19 empty] | 4216965.0343 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7121 | [19 empty] | 5623413.2519 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.1184 | [19 empty] | 7498942.0933 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5292 | [19 empty] | 10000000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.8319 | [19 empty] | 100 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9296 | [19 empty] | 133.3521 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2004 | [19 empty] | 177.8279 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6343 | [19 empty] | 237.1374 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1531 | [19 empty] | 316.2278 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 169.552 | [19 empty] | 421.6965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.363 | [19 empty] | 562.3413 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0643 | [19 empty] | 749.8942 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4169 | [19 empty] | 1000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0871 | [19 empty] | 1333.5214 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6632 | [19 empty] | 1778.2794 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7265 | [19 empty] | 2371.3737 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.2248 | [19 empty] | 3162.2777 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.3022 | [19 empty] | 4216.965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.0305 | [19 empty] | 5623.4133 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.2383 | [19 empty] | 7498.9421 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 183.5604 | [19 empty] | 10000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.3626 | [19 empty] | 13335.2143 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.4131 | [19 empty] | 17782.7941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.953 | [19 empty] | 23713.7371 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8393 | [19 empty] | 31622.7766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.0613 | [19 empty] | 42169.6503 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.7229 | [19 empty] | 56234.1325 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8372 | [19 empty] | 74989.4209 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.3025 | [19 empty] | 100000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8689 | [19 empty] | 133352.1432 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.7186 | [19 empty] | 177827.941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 181.5353 | [19 empty] | 237137.3706 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5921 | [19 empty] | 316227.766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.3393 | [19 empty] | 421696.5034 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.10338 | 1.1697e-05 | 4 | 108727335.6501 | 267746846.2678 | 2216553.8018 | 5458381.6156 | 43.5951 | 0 | 29.3463 | 30983.9153 | 708.753 | 59124.3962 | 69734.2159 | 0 | 0 | 0 | 62614.9993 | 162911.3841 | 111190.3672 | 497268.031 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5087318.987 | 12527793.5543 | 562341.3252 | 4.679e-05 | 108727335.6501 | 267746846.2678 | 2216553.8018 | 5458381.6156
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1176 | 0.14551 | 7.2463e-05 | 4 | 18092262.7779 | 43762324.1375 | 368835.2483 | 892154.1705 | 43.8741 | 0 | 57.5091 | 39558.3698 | 912.3292 | 77699.3947 | 87998.0227 | 0 | 4985.5788 | 0 | 82349.9411 | 214257.6545 | 146235.2518 | 653996.5426 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5244047.4987 | 12684522.0659 | 749894.2093 | 0.00028985 | 18092262.7779 | 43762324.1375 | 368835.2483 | 892154.1705
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3815 | 0.18307 | 0.00013904 | 4 | 9618658.8796 | 22996654.8593 | 196089.3715 | 468817.9146 | 44.0167 | 0 | 73.1074 | 46540.6226 | 1078.5428 | 93350.929 | 104274.0759 | 0 | 0 | 0 | 95645.2264 | 248849.2596 | 169844.733 | 759583.3893 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5349634.3454 | 12790108.9126 | 1000000 | 0.00055617 | 9618658.8796 | 22996654.8593 | 196089.3715 | 468817.9146
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.021 | 0.23165 | 0.00021306 | 4 | 6455019.9215 | 15185407.0038 | 131594.3122 | 309575.0616 | 44.123 | 0 | 64.3859 | 54904.7759 | 1277.9196 | 112680.4654 | 125346.3224 | 0 | 0 | 0 | 114741.6985 | 298534.3627 | 203755.8368 | 911241.3812 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5501292.3373 | 12941766.9045 | 1333521.4322 | 0.00085225 | 6455019.9215 | 15185407.0038 | 131594.3122 | 309575.0616
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9773 | 0.29019 | 0.000316 | 4 | 4492445.5128 | 10378811.3067 | 91584.5783 | 211586.1069 | 44.2354 | 0 | 50.9813 | 64353.2074 | 1503.8778 | 134919.1119 | 150658.6201 | 0 | 0 | 0 | 137059.5787 | 356600.909 | 243387.4478 | 1088482.7528 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5678533.7088 | 13119008.2761 | 1778279.41 | 0.001264 | 4492445.5128 | 10378811.3067 | 91584.5783 | 211586.1069
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.036 | 0.3515 | 0.00041757 | 4 | 3508008.9365 | 7962684.7794 | 71515.5071 | 162330.0996 | 44.3012 | 0 | 78.8049 | 73592.2016 | 1724.9671 | 157269.6696 | 177209.153 | 0 | 0 | 0 | 159820.4366 | 415819.9923 | 283805.689 | 1269242.1091 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5859293.0651 | 13299767.6324 | 2371373.7057 | 0.0016703 | 3508008.9365 | 7962684.7794 | 71515.5071 | 162330.0996
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1165 | 0.41348 | 0.00052053 | 4 | 2899904.9219 | 6473393.2616 | 59118.4842 | 131968.8775 | 44.3484 | 0 | 69.9702 | 82432.3553 | 1936.7369 | 179077.6178 | 204042.9379 | 0 | 0 | 0 | 182320.9627 | 474361.7458 | 323761.6387 | 1447933.9952 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6037984.9512 | 13478459.5185 | 3162277.6602 | 0.0020821 | 2899904.9219 | 6473393.2616 | 59118.4842 | 131968.8775
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0914 | 0.47231 | 0.00061849 | 4 | 2507945.4404 | 5515454.8982 | 51127.8601 | 112440.0083 | 44.382 | 0 | 79.2252 | 90450.7025 | 2128.9736 | 199179.8475 | 229515.0273 | 0 | 0 | 0 | 203297.0748 | 528937.2867 | 361010.5668 | 1614519.4791 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6204570.4352 | 13645045.0024 | 4216965.0343 | 0.002474 | 2507945.4404 | 5515454.8982 | 51127.8601 | 112440.0083
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.836 | 0.52428 | 0.00070517 | 4 | 2251110.9217 | 4888949.0108 | 45891.941 | 99667.8384 | 44.4056 | 0 | 241.4959 | 97280.5242 | 2292.8117 | 216523.7722 | 252016.9573 | 0 | 0 | 0 | 221564.4855 | 576465.3422 | 393449.4412 | 1759593.3343 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6349644.2903 | 13790118.8576 | 5623413.2519 | 0.0028207 | 2251110.9217 | 4888949.0108 | 45891.941 | 99667.8384
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3512 | 0.56942 | 0.00078055 | 4 | 2073624.2456 | 4456713.2894 | 42273.635 | 90856.1286 | 44.4228 | 0 | 71.4588 | 103045.3116 | 2431.1602 | 231311.0048 | 271562.2573 | 0 | 0 | 0 | 237256.3962 | 617292.475 | 421314.7983 | 1884213.4034 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6474264.3594 | 13914738.9267 | 7498942.0933 | 0.0031222 | 2073624.2456 | 4456713.2894 | 42273.635 | 90856.1286
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5887 | 0.60629 | 0.00084217 | 4 | 1951851.1371 | 4160568.7297 | 39791.1255 | 84818.8211 | 44.4349 | 0 | 68.1718 | 107649.6951 | 2541.6946 | 243213.8243 | 287524.3337 | 0 | 0 | 0 | 249962.5236 | 650351.2121 | 443878.0656 | 1985121.3491 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6575172.3051 | 14015646.8724 | 10000000 | 0.0033687 | 1951851.1371 | 4160568.7297 | 39791.1255 | 84818.8211
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.0823 | [19 empty] | 100 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4633 | [19 empty] | 133.3521 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6266 | [19 empty] | 177.8279 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1142 | [19 empty] | 237.1374 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1273 | [19 empty] | 316.2278 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.3666 | [19 empty] | 421.6965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.485 | [19 empty] | 562.3413 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7638 | [19 empty] | 749.8942 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 170.7963 | [19 empty] | 1000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1527 | [19 empty] | 1333.5214 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5307 | [19 empty] | 1778.2794 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1801 | [19 empty] | 2371.3737 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7263 | [19 empty] | 3162.2777 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.4138 | [19 empty] | 4216.965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.6308 | [19 empty] | 5623.4133 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.6525 | [19 empty] | 7498.9421 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.0421 | [19 empty] | 10000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.6142 | [19 empty] | 13335.2143 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.8449 | [19 empty] | 17782.7941 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.0182 | [19 empty] | 23713.7371 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.9008 | [19 empty] | 31622.7766 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4037 | [19 empty] | 42169.6503 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.4098 | [19 empty] | 56234.1325 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.5702 | [19 empty] | 74989.4209 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.9413 | [19 empty] | 100000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.046964 | 4.3191e-05 | 4 | 29986413.97 | 75293810.6835 | 611313.6084 | 1534966.1732 | 44.3825 | 0 | 31.2618 | 18650.2151 | 423.1142 | 31425.0912 | 44504.5698 | 0 | 6404.1919 | 0 | 39548.801 | 102897.8678 | 70229.9091 | 314083.7601 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5180580.3168 | 13008078.7249 | 133352.1432 | 0.00017276 | 29986413.97 | 75293810.6835 | 611313.6084 | 1534966.1732
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3855 | 0.1081 | 0.00015605 | 4 | 8683832.7068 | 21224242.0222 | 177031.6755 | 432684.8815 | 45.7601 | 0 | 74.1496 | 34507.8503 | 804.5143 | 61139.4343 | 69855.7637 | 0 | 12494.7006 | 0 | 69732.8827 | 181430.6566 | 123830.1511 | 553795.9537 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5420292.5104 | 13247790.9185 | 177827.941 | 0.00062418 | 8683832.7068 | 21224242.0222 | 177031.6755 | 432684.8815
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5038 | 0.14652 | 0.00028015 | 4 | 4954795.4681 | 11939885.1293 | 101010.2075 | 243410.7083 | 46.0783 | 0 | 85.2635 | 42929.0737 | 1008.4556 | 77954.5239 | 85751.5216 | 0 | 13795.2391 | 0 | 86361.1374 | 224693.9644 | 153358.2477 | 685852.1632 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5552348.7199 | 13379847.1281 | 237137.3706 | 0.0011206 | 4954795.4681 | 11939885.1293 | 101010.2075 | 243410.7083
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.848 | 0.19262 | 0.00044431 | 4 | 3209094.8766 | 7613373.6623 | 65421.7397 | 155208.92 | 46.3006 | 0 | 92.2076 | 52159.5196 | 1232.6478 | 97000.9003 | 104827.1505 | 0 | 14974.9297 | 0 | 105376.1077 | 274167.0165 | 187124.6224 | 836862.8944 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5703359.4511 | 13530857.8593 | 316227.766 | 0.0017772 | 3209094.8766 | 7613373.6623 | 65421.7397 | 155208.92
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3561 | 0.24423 | 0.00064885 | 4 | 2259881.636 | 5275813.9118 | 46070.7439 | 107554.6027 | 46.4457 | 0 | 81.761 | 61680.3074 | 1464.265 | 117272.4742 | 126196.7661 | 0 | 15852.8758 | 0 | 125762.0085 | 327206.9488 | 223325.466 | 998761.1117 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5865257.6684 | 13692756.0766 | 421696.5034 | 0.0025954 | 2259881.636 | 5275813.9118 | 46070.7439 | 107554.6027
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6218 | 0.32218 | 0.00092552 | 4 | 1648445.9338 | 3762794.1137 | 33605.8 | 76709.6476 | 46.6008 | 0 | 73.8253 | 74990.9049 | 1788.9286 | 146340.041 | 158412.6432 | 0 | 17592.6151 | 0 | 155658.8018 | 404992.2723 | 276415.5476 | 1236191.7544 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6102688.3111 | 13930186.7193 | 562341.3252 | 0.0037021 | 1648445.9338 | 3762794.1137 | 33605.8 | 76709.6476
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9117 | 0.40081 | 0.0012483 | 4 | 1268174.0001 | 2835745.7343 | 25853.4423 | 57810.5124 | 46.6906 | 0 | 78.277 | 87405.615 | 2092.0516 | 174257.8991 | 190927.2652 | 0 | 18637.1244 | 0 | 184594.7825 | 480277.7585 | 327799.4389 | 1465991.9351 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6332488.4918 | 14159986.9 | 749894.2093 | 0.0049934 | 1268174.0001 | 2835745.7343 | 25853.4423 | 57810.5124
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3944 | 0.48606 | 0.001618 | 4 | 1015831.0153 | 2225279.114 | 20709.0893 | 45365.3247 | 46.7559 | 0 | 66.0409 | 100038.3864 | 2400.8072 | 203314.5728 | 226180.7156 | 0 | 19495.9988 | 0 | 215057.8875 | 559536.5089 | 381895.1647 | 1707920.0419 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6574416.5986 | 14401915.0068 | 1000000 | 0.006472 | 1015831.0153 | 2225279.114 | 20709.0893 | 45365.3247
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9003 | 0.57212 | 0.002019 | 4 | 843530.0073 | 1812762.4316 | 17196.5002 | 36955.6141 | 46.8027 | 0 | 96.4187 | 112112.3772 | 2696.1265 | 231625.4583 | 261765.9527 | 0 | 20044.4333 | 0 | 245015.2957 | 637479.54 | 435092.8849 | 1945832.0687 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6812328.6254 | 14639827.0336 | 1333521.4322 | 0.008076 | 843530.0073 | 1812762.4316 | 17196.5002 | 36955.6141
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.387 | 0.62319 | 0.0025108 | 4 | 691314.0783 | 1470709.997 | 14093.3726 | 29982.4126 | 46.8245 | 0 | 149.0588 | 119010.7587 | 2864.9321 | 248015.8998 | 282879.3314 | 0 | 17627.2274 | 0 | 261455.2782 | 680253.0021 | 464286.6518 | 2076393.0815 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6942889.6382 | 14770388.0463 | 1778279.41 | 0.010043 | 691314.0783 | 1470709.997 | 14093.3726 | 29982.4126
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7996 | 0.74041 | 0.0029759 | 4 | 609920.2317 | 1267503.8004 | 12434.0489 | 25839.7794 | 46.8635 | 0 | 78.7172 | 134225.7791 | 3237.4051 | 284671.3157 | 331344.7649 | 0 | 19348.8849 | 0 | 301402.9784 | 784188.7235 | 535224.9173 | 2393644.7689 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7260141.3256 | 15087639.7337 | 2371373.7057 | 0.011903 | 609920.2317 | 1267503.8004 | 12434.0489 | 25839.7794
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.6755 | 0.80485 | 0.003352 | 4 | 553988.3527 | 1137780.6373 | 11293.8019 | 23195.1973 | 46.8803 | 0 | 77.3069 | 142273.4043 | 3434.4871 | 304319.9705 | 357987.0249 | 0 | 18972.6567 | 0 | 322525.142 | 839144.2605 | 572733.2005 | 2561390.1467 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7427886.7033 | 15255385.1115 | 3162277.6602 | 0.013408 | 553988.3527 | 1137780.6373 | 11293.8019 | 23195.1973
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2218 | 0.85797 | 0.0036801 | 4 | 513871.3734 | 1045620.5377 | 10475.963 | 21316.389 | 46.8923 | 0 | 101.0805 | 148760.5189 | 3593.3822 | 320281.0519 | 379948.9903 | 0 | 18457.3248 | 0 | 339706.0945 | 883845.5747 | 603242.7659 | 2697835.7032 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7564332.2599 | 15391830.6681 | 4216965.0343 | 0.01472 | 513871.3734 | 1045620.5377 | 10475.963 | 21316.389
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4741 | 0.90099 | 0.0039567 | 4 | 484855.2807 | 979429.6412 | 9884.4307 | 19966.998 | 46.9011 | 0 | 78.212 | 153925.1481 | 3719.9007 | 333063.1368 | 397735.5373 | 0 | 17901.3468 | 0 | 353474.5772 | 919668.3422 | 627692.5409 | 2807180.53 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7673677.0867 | 15501175.4949 | 5623413.2519 | 0.015827 | 484855.2807 | 979429.6412 | 9884.4307 | 19966.998
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4681 | 0.93514 | 0.0041835 | 4 | 463713.5075 | 931477.1014 | 9453.4271 | 18989.4206 | 46.9075 | 0 | 84.314 | 157971.8085 | 3819.0413 | 343123.2115 | 411855.0075 | 0 | 17357.9275 | 0 | 364309.5286 | 947858.6632 | 646933.0142 | 2893228.2022 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7759724.7589 | 15587223.1671 | 7498942.0933 | 0.016734 | 463713.5075 | 931477.1014 | 9453.4271 | 18989.4206
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2381 | 0.9616 | 0.004365 | 4 | 448213.2078 | 896521.1337 | 9137.4325 | 18276.7959 | 46.9122 | 0 | 90.0958 | 161075.4379 | 3895.0832 | 350864.9526 | 422791.3927 | 0 | 16848.0303 | 0 | 372635.2097 | 969520.3777 | 661717.5794 | 2959348.0634 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7825844.6201 | 15653343.0283 | 10000000 | 0.01746 | 448213.2078 | 896521.1337 | 9137.4325 | 18276.7959
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.6923 | [19 empty] | 100 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.2987 | [19 empty] | 133.3521 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5553 | [19 empty] | 177.8279 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7035 | [19 empty] | 237.1374 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6925 | [19 empty] | 316.2278 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.447 | [19 empty] | 421.6965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8405 | [19 empty] | 562.3413 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0945 | [19 empty] | 749.8942 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.401 | [19 empty] | 1000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.801 | [19 empty] | 1333.5214 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7805 | [19 empty] | 1778.2794 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.054 | [19 empty] | 2371.3737 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.1509 | [19 empty] | 3162.2777 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.9371 | [19 empty] | 4216.965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.87 | [19 empty] | 5623.4133 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.8786 | [19 empty] | 7498.9421 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.9135 | [19 empty] | 10000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.332 | [19 empty] | 13335.2143 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.5305 | [19 empty] | 17782.7941 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3728 | [19 empty] | 23713.7371 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7016 | [19 empty] | 31622.7766 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.053031 | 2.9066e-07 | 4 | 4737462142.9301 | 11809919311.7944 | 96579573.6754 | 240761179.269 | 46.4146 | 0 | 32.7077 | 21699.1858 | 502.0822 | 34561.7395 | 46263.3856 | 0 | 12935.6757 | 0 | 45225.2068 | 117666.7112 | 80309.9482 | 359163.9352 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5507966.1834 | 13730692.5597 | 42169.6503 | 1.1626e-06 | 4737462142.9301 | 11809919311.7944 | 96579573.6754 | 240761179.269
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.053032 | 8.2585e-05 | 4 | 16657680.1076 | 41549432.5844 | 339589.3402 | 847041.383 | 46.4147 | 0 | 32.5638 | 21699.2566 | 502.0841 | 34561.8086 | 46263.4237 | 0 | 11231.3195 | 0 | 44560.5781 | 115937.4835 | 79129.7148 | 353885.6689 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5502687.9171 | 13725414.2934 | 56234.1325 | 0.00033034 | 16657680.1076 | 41549432.5844 | 339589.3402 | 847041.383
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6452 | 0.093543 | 0.0002209 | 4 | 6407078.4839 | 15712892.0504 | 130616.9611 | 320328.5577 | 47.5929 | 0 | 57.2019 | 33139.8862 | 782.5313 | 54357.5874 | 62377.7337 | 0 | 14833.2944 | 0 | 64541.5028 | 167923.7511 | 114611.4106 | 512567.6974 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5661369.9456 | 13884096.3219 | 74989.4209 | 0.00088361 | 6407078.4839 | 15712892.0504 | 130616.9611 | 320328.5577
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.12886 | 0.00039608 | 4 | 3652532.6822 | 8842609.8688 | 74461.8191 | 180268.5627 | 48.0694 | 0 | 67.5419 | 41833.5235 | 996.8842 | 70200.7324 | 76381.5061 | 0 | 16565.5048 | 0 | 80331.4789 | 209006.0298 | 142650.91 | 637966.5697 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5786768.8179 | 14009495.1942 | 100000 | 0.0015843 | 3652532.6822 | 8842609.8688 | 74461.8191 | 180268.5627
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7085 | 0.17391 | 0.00063362 | 4 | 2343088.7084 | 5587414.7419 | 47767.0326 | 113907.0071 | 48.4169 | 0 | 85.8427 | 51900.7524 | 1245.9791 | 89197.9312 | 94241.2933 | 0 | 18395.7851 | 0 | 99442.879 | 258729.9727 | 176588.5227 | 789743.1156 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5938545.3638 | 14161271.7401 | 133352.1432 | 0.0025345 | 2343088.7084 | 5587414.7419 | 47767.0326 | 113907.0071
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1186 | 0.22882 | 0.00094576 | 4 | 1616337.4223 | 3789913.5073 | 32951.2246 | 77262.5131 | 48.6627 | 0 | 92.3065 | 63102.8712 | 1523.7709 | 111064.0508 | 116000.5613 | 0 | 20155.2459 | 0 | 121620.135 | 316430.6436 | 215970.4162 | 965867.6948 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6114669.943 | 14337396.3193 | 177827.941 | 0.003783 | 1616337.4223 | 3789913.5073 | 32951.2246 | 77262.5131
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7434 | 0.2919 | 0.0013383 | 4 | 1178410.4573 | 2714458.7275 | 24023.4911 | 55337.9127 | 48.8225 | 0 | 95.9283 | 74942.1909 | 1817.6892 | 134927.4913 | 141020.9827 | 0 | 21632.4437 | 0 | 145992.9111 | 379843.6074 | 259251.0671 | 1159428.3832 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6308230.6314 | 14530957.0077 | 237137.3706 | 0.0053532 | 1178410.4573 | 2714458.7275 | 24023.4911 | 55337.9127
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1944 | 0.38776 | 0.0018802 | 4 | 876671.2067 | 1969996.9766 | 17872.1283 | 40161.053 | 49.0027 | 0 | 77.858 | 91591.2821 | 2232.1744 | 169307.7417 | 178942.1714 | 0 | 24307.6141 | 0 | 181888.5837 | 473236.7842 | 322993.8293 | 1444500.1809 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6593302.4291 | 14816028.8054 | 316227.766 | 0.0075208 | 876671.2067 | 1969996.9766 | 17872.1283 | 40161.053
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8083 | 0.48982 | 0.0025256 | 4 | 681419.6709 | 1495350.8103 | 13891.6617 | 30484.7489 | 49.1069 | 0 | 77.3603 | 107908.8042 | 2638.5533 | 204087.8006 | 219341.7986 | 0 | 26270.7182 | 0 | 218496.5932 | 568483.3157 | 388001.5442 | 1735229.1281 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6884031.3763 | 15106757.7526 | 421696.5034 | 0.010102 | 681419.6709 | 1495350.8103 | 13891.6617 | 30484.7489
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7554 | 0.60491 | 0.0032949 | 4 | 546398.3072 | 1170294.3032 | 11139.0686 | 23858.0323 | 49.1833 | 0 | 104.9159 | 125092.9024 | 3066.8603 | 241605.5661 | 264892.0098 | 0 | 28036.9506 | 0 | 258450.7727 | 672435.8951 | 458951.3156 | 2052532.2726 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7201334.5208 | 15424060.8971 | 562341.3252 | 0.01318 | 546398.3072 | 1170294.3032 | 11139.0686 | 23858.0323
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.8908 | 0.72737 | 0.0041675 | 4 | 451666.4523 | 944929.1232 | 9207.8316 | 19263.6583 | 49.2388 | 0 | 78.0312 | 142305.1441 | 3496.1162 | 279984.1409 | 313355.4409 | 0 | 29447.1702 | 0 | 299749.3248 | 779886.2561 | 532288.3948 | 2380511.988 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7529314.2362 | 15752040.6125 | 749894.2093 | 0.01667 | 451666.4523 | 944929.1232 | 9207.8316 | 19263.6583
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.036 | 0.85023 | 0.0051029 | 4 | 384599.2384 | 787448.4892 | 7840.5757 | 16053.2026 | 49.2789 | 0 | 94.2236 | 158701.5771 | 3905.1873 | 317203.8529 | 361973.144 | 0 | 30413.2738 | 0 | 340156.8437 | 885018.3316 | 604043.1966 | 2701415.407 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7850217.6552 | 16072944.0315 | 1000000 | 0.020411 | 384599.2384 | 787448.4892 | 7840.5757 | 16053.2026
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.0197 | 0.96679 | 0.0060481 | 4 | 336813.2306 | 676702.2052 | 6866.3933 | 13795.4898 | 49.3079 | 0 | 87.9113 | 173601.5225 | 4277.0178 | 351531.017 | 408098.9418 | 0 | 30934.8112 | 0 | 377692.891 | 982679.427 | 670698.901 | 2999514.5293 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8148316.7775 | 16371043.1538 | 1333521.4322 | 0.024192 | 336813.2306 | 676702.2052 | 6866.3933 | 13795.4898
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6728 | 1.0704 | 0.0069476 | 4 | 302571.4333 | 598453.5642 | 6168.3279 | 12200.2854 | 49.3286 | 0 | 87.8702 | 186397.9704 | 4596.4064 | 381364.4414 | 449114.9002 | 0 | 31014.687 | 0 | 410470.4781 | 1067959.9849 | 728904.6341 | 3259823.5023 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8408625.7505 | 16631352.1268 | 1778279.41 | 0.027791 | 302571.4333 | 598453.5642 | 6168.3279 | 12200.2854
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.9554 | 1.1596 | 0.0077633 | 4 | 277892.0883 | 542688.0767 | 5665.2061 | 11063.4305 | 49.3437 | 0 | 99.8179 | 197110.5971 | 4863.8104 | 406573.6348 | 484406.0043 | 0 | 30815.1334 | 0 | 438269.9802 | 1140288.5869 | 778270.3912 | 3480598.1382 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8629400.3864 | 16852126.7627 | 2371373.7057 | 0.031053 | 277892.0883 | 542688.0767 | 5665.2061 | 11063.4305
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.8339 | 1.233 | 0.0084701 | 4 | 259998.0037 | 502695.2359 | 5300.411 | 10248.1223 | 49.3545 | 0 | 75.0106 | 205741.3733 | 5079.2605 | 427030.8111 | 513450.4022 | 0 | 30417.5128 | 0 | 460870.5503 | 1199090.6344 | 818403.9968 | 3660084.5414 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8808886.7896 | 17031613.1659 | 3162277.6602 | 0.033881 | 259998.0037 | 502695.2359 | 5300.411 | 10248.1223
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.3413 | 1.2919 | 0.0090621 | 4 | 246947.7915 | 473790.5637 | 5034.3648 | 9658.8615 | 49.3624 | 0 | 93.2754 | 212555.7968 | 5249.3745 | 443271.7285 | 536758.0475 | 0 | 29930.9526 | 0 | 478828.7009 | 1245814.0586 | 850293.6939 | 3802702.3533 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8951504.6015 | 17174230.9778 | 4216965.0343 | 0.036249 | 246947.7915 | 473790.5637 | 5034.3648 | 9658.8615
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.146 | 1.2452 | 0.0094751 | 4 | 232671.962 | 449627.7546 | 4743.3327 | 9166.2699 | 49.3562 | 0 | 314.5908 | 207160.1778 | 5114.679 | 430405.8643 | 518276.0726 | 0 | 23826.5024 | 0 | 462065.4855 | 1202199.6106 | 820525.937 | 3669574.3292 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8818376.5774 | 17041102.9537 | 5623413.2519 | 0.0379 | 232671.962 | 449627.7546 | 4743.3327 | 9166.2699
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.6311 | 1.3814 | 0.010196 | 4 | 224629.7576 | 426239.9082 | 4579.3814 | 8689.4771 | 49.3732 | 0 | 99.7337 | 222731.8563 | 5503.4137 | 467665.1642 | 572165.912 | 0 | 27528.3188 | 0 | 505281.9194 | 1314639.9066 | 897268.7494 | 4012785.2403 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9161587.4885 | 17384313.8648 | 7498942.0933 | 0.040785 | 224629.7576 | 426239.9082 | 4579.3814 | 8689.4771
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4741 | 1.4144 | 0.010521 | 4 | 219577.2279 | 414969.9313 | 4476.3788 | 8459.7233 | 49.3768 | 0 | 84.3873 | 226427.5682 | 5595.676 | 476564.8258 | 585200.5326 | 0 | 27279.6358 | 0 | 515216.6129 | 1340487.9414 | 914910.5643 | 4091683.357 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9240485.6052 | 17463211.9815 | 10000000 | 0.042083 | 219577.2279 | 414969.9313 | 4476.3788 | 8459.7233
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6432 | [19 empty] | 100 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.3679 | [19 empty] | 133.3521 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8433 | [19 empty] | 177.8279 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3634 | [19 empty] | 237.1374 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8209 | [19 empty] | 316.2278 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1832 | [19 empty] | 421.6965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2636 | [19 empty] | 562.3413 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7288 | [19 empty] | 749.8942 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2801 | [19 empty] | 1000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9427 | [19 empty] | 1333.5214 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6502 | [19 empty] | 1778.2794 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9449 | [19 empty] | 2371.3737 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.4088 | [19 empty] | 3162.2777 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.1885 | [19 empty] | 4216.965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.7 | [19 empty] | 5623.4133 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8569 | [19 empty] | 7498.9421 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8807 | [19 empty] | 10000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.3637 | [19 empty] | 13335.2143 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.5129 | [19 empty] | 17782.7941 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.1845 | [19 empty] | 23713.7371 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.059098 | 0.00012864 | 4 | 11318679.0462 | 28082175.1713 | 230746.582 | 572493.1248 | 48.4168 | 0 | 32.4113 | 24824.657 | 585.2951 | 37613.5635 | 47919.6558 | 0 | 14134.385 | 0 | 48780.247 | 126916.1965 | 86622.912 | 387396.9118 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5824364.9424 | 14450523.414 | 31622.7766 | 0.00051458 | 11318679.0462 | 28082175.1713 | 230746.582 | 572493.1248
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.059098 | 0.00023454 | 4 | 6202007.9884 | 15396752.7399 | 126436.3217 | 313883.6303 | 48.4169 | 0 | 31.487 | 24824.7558 | 585.2977 | 37613.6564 | 47919.7054 | 0 | 12236.3826 | 0 | 48040.1211 | 124990.5408 | 85308.6124 | 381519.0722 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5818487.1028 | 14444645.5744 | 42169.6503 | 0.00093816 | 6202007.9884 | 15396752.7399 | 126436.3217 | 313883.6303
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1614 | 0.12713 | 0.00053805 | 4 | 2824427.3096 | 6832476.1077 | 57579.771 | 139289.2671 | 50.1057 | 0 | 75.5194 | 43879.5549 | 1062.7471 | 69305.073 | 73876.6149 | 0 | 19088.5184 | 0 | 80812.8782 | 210258.5322 | 143505.7686 | 641789.6873 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6078757.7179 | 14704916.1895 | 56234.1325 | 0.0021522 | 2824427.3096 | 6832476.1077 | 57579.771 | 139289.2671
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2091 | 0.17281 | 0.00086174 | 4 | 1808559.8353 | 4311086.9607 | 36869.9385 | 87887.3389 | 50.5549 | 0 | 72.7879 | 54814.3392 | 1338.5901 | 88555.613 | 91274.1435 | 0 | 21374.2703 | 0 | 100369.2129 | 261140.1034 | 178233.4865 | 797099.759 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6234067.7895 | 14860226.2612 | 74989.4209 | 0.003447 | 1808559.8353 | 4311086.9607 | 36869.9385 | 87887.3389
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5339 | 0.23061 | 0.0012933 | 4 | 1241198.3831 | 2908726.1874 | 25303.5079 | 59298.3177 | 50.8828 | 0 | 74.9274 | 67407.7315 | 1657.0203 | 111511.3549 | 113274.7137 | 0 | 23778.5949 | 0 | 123875.472 | 322298.5677 | 219975.395 | 983778.85 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6420746.8806 | 15046905.3522 | 100000 | 0.005173 | 1241198.3831 | 2908726.1874 | 25303.5079 | 59298.3177
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1003 | 0.29897 | 0.0018499 | 4 | 896106.3452 | 2061840.4268 | 18268.3399 | 42033.4059 | 51.1057 | 0 | 77.7759 | 81044.5923 | 2002.2186 | 137218.505 | 139285.9661 | 0 | 25954.2847 | 0 | 150347.171 | 391172.4985 | 266983.2681 | 1194008.5043 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6630976.5349 | 15257135.0065 | 133352.1432 | 0.0073998 | 896106.3452 | 2061840.4268 | 18268.3399 | 42033.4059
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4561 | 0.40232 | 0.0026061 | 4 | 665536.0014 | 1493033.6097 | 13567.8516 | 30437.5096 | 51.3242 | 0 | 81.4498 | 99978.2225 | 2482.4246 | 173972.5375 | 178539.0042 | 0 | 29598.8368 | 0 | 188982.7 | 491694.2197 | 335591.4082 | 1500839.3534 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6937807.384 | 15563965.8556 | 177827.941 | 0.010424 | 665536.0014 | 1493033.6097 | 13567.8516 | 30437.5096
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8922 | 0.50909 | 0.0035404 | 4 | 511216.1699 | 1120340.6752 | 10421.8331 | 22839.66 | 51.4539 | 0 | 78.3637 | 117981.7344 | 2939.3841 | 209990.0486 | 219098.6312 | 0 | 32007.39 | 0 | 226986.7035 | 590572.841 | 403078.099 | 1802654.8318 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7239622.8624 | 15865781.334 | 237137.3706 | 0.014162 | 511216.1699 | 1120340.6752 | 10421.8331 | 22839.66
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9271 | 0.64209 | 0.004705 | 4 | 404025.4357 | 862380.7644 | 8236.605 | 17580.7983 | 51.5563 | 0 | 89.5429 | 138850.3101 | 3469.4159 | 252812.517 | 269624.4011 | 0 | 34802.5987 | 0 | 272828.1047 | 709842.7638 | 484482.2721 | 2166712.3835 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7603680.414 | 16229838.8857 | 316227.766 | 0.01882 | 404025.4357 | 862380.7644 | 8236.605 | 17580.7983
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3501 | 0.79212 | 0.0060944 | 4 | 328212.6888 | 682066.6421 | 6691.0596 | 13904.8511 | 51.6316 | 0 | 95.2791 | 160853.8998 | 4028.5471 | 299036.3794 | 326615.1985 | 0 | 37333.1051 | 0 | 322868.1807 | 840036.7767 | 573342.3612 | 2564114.4485 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8001082.4791 | 16627240.9507 | 421696.5034 | 0.024378 | 328212.6888 | 682066.6421 | 6691.0596 | 13904.8511
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.0165 | 0.95284 | 0.0076754 | 4 | 274075.9526 | 555043.7255 | 5587.409 | 11315.3171 | 51.6867 | 0 | 88.7306 | 183053.1042 | 4592.818 | 346644.4783 | 387662.3823 | 0 | 39415.2409 | 0 | 374933.5292 | 975500.1337 | 665798.8857 | 2977600.5723 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8414568.6029 | 17040727.0745 | 562341.3252 | 0.030702 | 274075.9526 | 555043.7255 | 5587.409 | 11315.3171
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7165 | 1.1151 | 0.0093763 | 4 | 235205.1858 | 465204.5135 | 4794.9759 | 9483.8232 | 51.7268 | 0 | 102.0673 | 204329.4534 | 5133.7177 | 393086.8714 | 449273.7867 | 0 | 40898.0957 | 0 | 426161.5507 | 1108784.9371 | 756768.5028 | 3384436.9154 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8821404.946 | 17447563.4176 | 749894.2093 | 0.037505 | 235205.1858 | 465204.5135 | 4794.9759 | 9483.8232
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2197 | 1.2687 | 0.011099 | 4 | 207195.4562 | 401503.7902 | 4223.9596 | 8185.1978 | 51.7558 | 0 | 82.5355 | 223626.2625 | 5624.324 | 435829.3661 | 507613.1095 | 0 | 41706.5643 | 0 | 473615.8543 | 1232251.3009 | 841036.8331 | 3761303.6148 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9198271.6454 | 17824430.117 | 1000000 | 0.044394 | 207195.4562 | 401503.7902 | 4223.9596 | 8185.1978
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3649 | 1.4066 | 0.012745 | 4 | 186945.2409 | 356151.8747 | 3811.1316 | 7260.6377 | 51.7767 | 0 | 97.2536 | 240358.5573 | 6049.7323 | 473330.5413 | 559993.8833 | 0 | 41923.6994 | 0 | 515446.0013 | 1341084.7629 | 915317.9072 | 4093505.0852 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9530473.1157 | 18156631.5874 | 1333521.4322 | 0.05098 | 186945.2409 | 356151.8747 | 3811.1316 | 7260.6377
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.0781 | 1.5256 | 0.014242 | 4 | 172249.1987 | 323668.6067 | 3511.5329 | 6598.4223 | 51.7919 | 0 | 100.4244 | 254400.19 | 6406.7232 | 505095.1965 | 605183.1178 | 0 | 41726.237 | 0 | 550996.4712 | 1433579.793 | 978447.6659 | 4375835.3946 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9812803.4251 | 18438961.8968 | 1778279.41 | 0.056969 | 172249.1987 | 323668.6067 | 3511.5329 | 6598.4223
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.3218 | 1.624 | 0.015543 | 4 | 161537.6866 | 300280.9963 | 3293.1642 | 6121.6343 | 51.8029 | 0 | 103.7637 | 265765.6497 | 6695.6643 | 530992.1105 | 642555.3444 | 0 | 41243.3085 | 0 | 580028.3102 | 1509114.6829 | 1030001.7803 | 4606396.8508 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10043364.8814 | 18669523.353 | 2371373.7057 | 0.062174 | 161537.6866 | 300280.9963 | 3293.1642 | 6121.6343
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.1271 | 1.7032 | 0.016635 | 4 | 153694.968 | 283332.1421 | 3133.2798 | 5776.109 | 51.8109 | 0 | 88.7594 | 274761.2192 | 6924.3461 | 551602.5429 | 672626.5147 | 0 | 40621.5641 | 0 | 603149.1129 | 1569270.2689 | 1071059.2038 | 4790014.7726 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10226982.8031 | 18853141.2748 | 3162277.6602 | 0.066541 | 153694.968 | 283332.1421 | 3133.2798 | 5776.109
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5498 | 1.7656 | 0.017526 | 4 | 147927.7087 | 270973.9285 | 3015.7064 | 5524.1701 | 51.8167 | 0 | 73.3482 | 281762.0377 | 7102.3107 | 567709.9788 | 696324.3071 | 0 | 39966.6916 | 0 | 621217.4771 | 1616280.4461 | 1103144.6157 | 4933507.8648 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10370475.8954 | 18996634.367 | 4216965.0343 | 0.070105 | 147927.7087 | 270973.9285 | 3015.7064 | 5524.1701
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.6681 | 1.8147 | 0.018241 | 4 | 143670.0742 | 261896.3969 | 2928.9088 | 5339.1123 | 51.821 | 0 | 88.2001 | 287213.265 | 7240.8785 | 580292.0451 | 714952.8835 | 0 | 39371.6983 | 0 | 635337.6004 | 1653018.1107 | 1128218.8267 | 5045645.3082 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10482613.3388 | 19108771.8104 | 5623413.2519 | 0.072963 | 143670.0742 | 261896.3969 | 2928.9088 | 5339.1123
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.5371 | 1.8528 | 0.018804 | 4 | 140516.4231 | 255198.7122 | 2864.6173 | 5202.5709 | 51.8242 | 0 | 101.7903 | 291418.4294 | 7347.7686 | 590021.5485 | 729427.5225 | 0 | 38858.9847 | 0 | 646258.9589 | 1681433.2452 | 1147612.7398 | 5132379.1976 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10569347.2282 | 19195505.6998 | 7498942.0933 | 0.075218 | 140516.4231 | 255198.7122 | 2864.6173 | 5202.5709
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.1903 | 1.8814 | 0.019241 | 4 | 138174.0762 | 250256.9514 | 2816.8654 | 5101.8265 | 51.8266 | 0 | 106.39 | 294562.6457 | 7427.6885 | 597309.5438 | 740309.1199 | 0 | 38403.3805 | 0 | 654424.8276 | 1702679.1604 | 1162113.5135 | 5197229.8799 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10634197.9105 | 19260356.3821 | 10000000 | 0.076962 | 138174.0762 | 250256.9514 | 2816.8654 | 5101.8265
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6712 | [19 empty] | 100 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9087 | [19 empty] | 133.3521 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.3368 | [19 empty] | 177.8279 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.3262 | [19 empty] | 237.1374 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.9969 | [19 empty] | 316.2278 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4557 | [19 empty] | 421.6965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6744 | [19 empty] | 562.3413 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9786 | [19 empty] | 749.8942 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.346 | [19 empty] | 1000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7594 | [19 empty] | 1333.5214 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1626 | [19 empty] | 1778.2794 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.973 | [19 empty] | 2371.3737 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.8427 | [19 empty] | 3162.2777 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.7707 | [19 empty] | 4216.965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.8837 | [19 empty] | 5623.4133 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.3695 | [19 empty] | 7498.9421 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.7314 | [19 empty] | 10000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8255 | [19 empty] | 13335.2143 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065194 | 7.9906e-05 | 4 | 19254653.9869 | 47531072.3844 | 392532.1654 | 968985.2011 | 50.3894 | 0 | 31.2413 | 28019.7675 | 672.6065 | 40606.3806 | 49495.6957 | 0 | 17854.6957 | 0 | 53293.167 | 138657.8886 | 94636.8581 | 423237.0597 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6154230.9636 | 15192025.6577 | 17782.7941 | 0.00031962 | 19254653.9869 | 47531072.3844 | 392532.1654 | 968985.2011
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065194 | 0.00026181 | 4 | 5869834.9436 | 14500007.0295 | 119664.5249 | 295602.256 | 50.3895 | 0 | 29.7857 | 28019.9495 | 672.6116 | 40606.5425 | 49495.7798 | 0 | 15545.6375 | 0 | 52392.8032 | 136315.3266 | 93038.0114 | 416086.662 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6147080.5658 | 15184875.26 | 23713.7371 | 0.0010472 | 5869834.9436 | 14500007.0295 | 119664.5249 | 295602.256
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065194 | 0.00039822 | 4 | 3854951.728 | 9528769.8571 | 78588.4052 | 194256.8622 | 50.3896 | 0 | 31.0466 | 28020.086 | 672.6154 | 40606.6639 | 49495.8429 | 0 | 13431.0268 | 0 | 51568.2317 | 134169.9607 | 91573.7551 | 409538.1824 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6140532.0862 | 15178326.7804 | 31622.7766 | 0.0015929 | 3854951.728 | 9528769.8571 | 78588.4052 | 194256.8622
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4197 | 0.15328 | 0.00090634 | 4 | 1785139.3506 | 4278066.3229 | 36392.4802 | 87214.1685 | 52.4503 | 0 | 60.4437 | 52925.1913 | 1309.6472 | 80303.5523 | 81827.9388 | 0 | 22815.0415 | 0 | 93280.7347 | 242697.3372 | 165645.9196 | 740805.3627 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6471799.2665 | 15509593.9606 | 42169.6503 | 0.0036254 | 1785139.3506 | 4278066.3229 | 36392.4802 | 87214.1685
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5381 | 0.20771 | 0.0013976 | 4 | 1189877.9565 | 2806564.8881 | 24257.2716 | 57215.6214 | 52.9179 | 0 | 70.8402 | 65916.2814 | 1643.9049 | 102356.0999 | 101738.7088 | 0 | 25641.5277 | 0 | 115945.6439 | 301666.7816 | 205893.7771 | 920802.7252 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6651796.629 | 15689591.3232 | 56234.1325 | 0.0055903 | 1189877.9565 | 2806564.8881 | 24257.2716 | 57215.6214
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9601 | 0.27683 | 0.0020518 | 4 | 836945.1754 | 1938128.9295 | 17062.2595 | 39511.3797 | 53.2612 | 0 | 90.4245 | 80963.3382 | 2031.9302 | 128755.9586 | 127023.8563 | 0 | 28680.6787 | 0 | 143307.7471 | 372857.3615 | 254482.8107 | 1138103.681 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6869097.5848 | 15906892.279 | 74989.4209 | 0.0082073 | 836945.1754 | 1938128.9295 | 17062.2595 | 39511.3797
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6339 | 0.35795 | 0.002892 | 4 | 614786.5543 | 1396051.4621 | 12533.2555 | 28460.3974 | 53.4876 | 0 | 69.6469 | 97155.9901 | 2449.8262 | 158110.0692 | 156725.6827 | 0 | 31422.1961 | 0 | 173886.8681 | 452417.9617 | 308784.5551 | 1380953.1491 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7111947.0529 | 16149741.7471 | 100000 | 0.011568 | 614786.5543 | 1396051.4621 | 12533.2555 | 28460.3974
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0823 | 0.47742 | 0.0040485 | 4 | 460489.3008 | 1018589.6876 | 9387.6973 | 20765.3285 | 53.7233 | 0 | 76.06 | 119161.1232 | 3019.1507 | 199027.2116 | 200353.1109 | 0 | 35740.0313 | 0 | 217347.2448 | 565492.947 | 385960.556 | 1726101.3755 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7457095.2794 | 16494889.9735 | 133352.1432 | 0.016194 | 460489.3008 | 1018589.6876 | 9387.6973 | 20765.3285
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8667 | 0.61293 | 0.0054874 | 4 | 356775.1198 | 768524.0205 | 7273.3434 | 15667.4017 | 53.8686 | 0 | 63.0192 | 142092.4843 | 3612.4786 | 243030.3963 | 249884.5557 | 0 | 39444.9378 | 0 | 264445.2926 | 688032.406 | 469596.2548 | 2100138.8061 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7831132.7099 | 16868927.404 | 177827.941 | 0.02195 | 356775.1198 | 768524.0205 | 7273.3434 | 15667.4017
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.177 | 0.77407 | 0.0072798 | 4 | 283656.8501 | 594030.3612 | 5782.7286 | 12110.1124 | 53.9769 | 0 | 99.5152 | 167414.1704 | 4267.9441 | 292891.7231 | 308775.0524 | 0 | 43127.9704 | 0 | 318425.9756 | 828479.0702 | 565453.989 | 2528835.8952 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8259829.799 | 17297624.4932 | 237137.3706 | 0.029119 | 283656.8501 | 594030.3612 | 5782.7286 | 12110.1124
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9554 | 0.95809 | 0.0094354 | 4 | 231395.3738 | 470860.7248 | 4717.3077 | 9599.1328 | 54.0573 | 0 | 92.1572 | 194425.3729 | 4967.2613 | 347356.2803 | 376016.1658 | 0 | 46554.0936 | 0 | 378034.4778 | 983568.1658 | 671305.4835 | 3002227.301 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8733221.2048 | 17771015.899 | 316227.766 | 0.037742 | 231395.3738 | 470860.7248 | 4717.3077 | 9599.1328
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0381 | 1.157 | 0.011911 | 4 | 193716.6441 | 383407.7158 | 3949.1758 | 7816.2849 | 54.1162 | 0 | 101.0206 | 221894.1945 | 5678.4709 | 403911.9188 | 448682.5292 | 0 | 49413.7547 | 0 | 440536.5386 | 1146185.7069 | 782295.2967 | 3498598.4102 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9229592.314 | 18267387.0082 | 421696.5034 | 0.047645 | 193716.6441 | 383407.7158 | 3949.1758 | 7816.2849
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2233 | 1.3609 | 0.014609 | 4 | 166430.3535 | 321096.2849 | 3392.9079 | 6545.9821 | 54.1594 | 0 | 112.9329 | 248606.5636 | 6370.0789 | 459904.7675 | 523180.0037 | 0 | 51547.7112 | 0 | 502947.5587 | 1308566.3791 | 893123.4421 | 3994246.5049 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9725240.4087 | 18763035.1028 | 562341.3252 | 0.058434 | 166430.3535 | 321096.2849 | 3392.9079 | 6545.9821
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2406 | 1.5567 | 0.017375 | 4 | 146625.2117 | 276668.5774 | 2989.1533 | 5640.2632 | 54.1908 | 0 | 89.3339 | 273134.7902 | 7005.0802 | 512095.7668 | 594696.9976 | 0 | 52798.0792 | 0 | 561494.9784 | 1460894.7554 | 997090.6889 | 4459211.1365 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10190205.0404 | 19227999.7345 | 749894.2093 | 0.069498 | 146625.2117 | 276668.5774 | 2989.1533 | 5640.2632
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9017 | 1.7351 | 0.020053 | 4 | 132223.3387 | 244897.8881 | 2695.5516 | 4992.5747 | 54.2136 | 0 | 93.438 | 294692.4354 | 7563.1082 | 558527.6478 | 659876.9893 | 0 | 53262.7656 | 0 | 613829.949 | 1597059.6135 | 1090026.0025 | 4874838.5113 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10605832.4152 | 19643627.1093 | 1000000 | 0.080212 | 132223.3387 | 244897.8881 | 2695.5516 | 4992.5747
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.0734 | 1.8897 | 0.02251 | 4 | 121725.6903 | 222102.0561 | 2481.5428 | 4527.8508 | 54.2301 | 0 | 95.1227 | 312836.5398 | 8032.7118 | 597986.8113 | 716347.0302 | 0 | 53090.7302 | 0 | 658434.5911 | 1713111.7425 | 1169233.9652 | 5229074.122 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10960068.0259 | 19997862.72 | 1333521.4322 | 0.090039 | 121725.6903 | 222102.0561 | 2481.5428 | 4527.8508
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.7212 | 2.0188 | 0.024664 | 4 | 114050.1116 | 205658.3728 | 2325.0658 | 4192.6241 | 54.2421 | 0 | 110.9168 | 327645.4017 | 8415.942 | 630436.2624 | 763490.7993 | 0 | 52508.8553 | 0 | 695173.9317 | 1808699.9705 | 1234474.8949 | 5520846.0578 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11251839.9616 | 20289634.6557 | 1778279.41 | 0.098657 | 114050.1116 | 205658.3728 | 2325.0658 | 4192.6241
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.8749 | 2.1238 | 0.026487 | 4 | 108417.8458 | 193722.1782 | 2210.2444 | 3949.2886 | 54.2507 | 0 | 93.6685 | 339482.5949 | 8722.2324 | 656525.5041 | 801838.0763 | 0 | 51730.6758 | 0 | 724736.6425 | 1885616.0799 | 1286971.7201 | 5755623.5259 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11486617.4298 | 20524412.1239 | 2371373.7057 | 0.10595 | 108417.8458 | 193722.1782 | 2210.2444 | 3949.2886
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.5728 | 2.2065 | 0.02798 | 4 | 104269.7743 | 185021.3911 | 2125.6804 | 3771.9113 | 54.257 | 0 | 94.6105 | 348690.9096 | 8960.4741 | 676911.0574 | 832069.0541 | 0 | 50865.4904 | 0 | 747823.8244 | 1945684.1914 | 1327969.4404 | 5938974.4419 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11669968.3457 | 20707763.0399 | 3162277.6602 | 0.11192 | 104269.7743 | 185021.3911 | 2125.6804 | 3771.9113
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.9151 | 2.2719 | 0.029184 | 4 | 101204.2843 | 178626.2319 | 2063.1862 | 3641.5373 | 54.2616 | 0 | 92.1801 | 355897.0296 | 9146.8971 | 692918.1488 | 855967.635 | 0 | 50073.0295 | 0 | 765961.0686 | 1992873.5803 | 1360177.168 | 6083014.5569 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11814008.4607 | 20851803.1549 | 4216965.0343 | 0.11673 | 101204.2843 | 178626.2319 | 2063.1862 | 3641.5373
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.946 | 2.3222 | 0.030132 | 4 | 98932.0022 | 173917.7855 | 2016.8627 | 3545.5493 | 54.2649 | 0 | 105.2518 | 361389.1174 | 9288.9671 | 705149.2214 | 874322.3073 | 0 | 49351.2854 | 0 | 779805.3505 | 2028893.5619 | 1384761.5456 | 6192961.3568 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11923955.2606 | 20961749.9548 | 5623413.2519 | 0.12053 | 98932.0022 | 173917.7855 | 2016.8627 | 3545.5493
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.725 | 2.3602 | 0.030867 | 4 | 97243.4147 | 170442.1901 | 1982.4385 | 3474.6946 | 54.2673 | 0 | 93.4608 | 365515.3978 | 9395.6999 | 714356.2696 | 888191.8224 | 0 | 48714.3573 | 0 | 790207.6833 | 2055958.2981 | 1403233.7842 | 6275573.3127 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12006567.2165 | 21044361.9106 | 7498942.0933 | 0.12347 | 97243.4147 | 170442.1901 | 1982.4385 | 3474.6946
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3272 | 2.3895 | 0.031438 | 4 | 95986.0041 | 167856.9254 | 1956.8045 | 3421.9905 | 54.2691 | 0 | 88.0097 | 368690.9582 | 9477.8369 | 721452.2068 | 898911.8565 | 0 | 48209.8745 | 0 | 798229.6658 | 2076829.851 | 1417479.0479 | 6339281.2976 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12070275.2014 | 21108069.8956 | 10000000 | 0.12575 | 95986.0041 | 167856.9254 | 1956.8045 | 3421.9905
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.1542 | [19 empty] | 100 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4293 | [19 empty] | 133.3521 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.081 | [19 empty] | 177.8279 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6678 | [19 empty] | 237.1374 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3976 | [19 empty] | 316.2278 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3504 | [19 empty] | 421.6965 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5475 | [19 empty] | 562.3413 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1264 | [19 empty] | 749.8942 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.562 | [19 empty] | 1000 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3205 | [19 empty] | 1333.5214 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.4393 | [19 empty] | 1778.2794 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.3833 | [19 empty] | 2371.3737 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6073 | [19 empty] | 3162.2777 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.3266 | [19 empty] | 4216.965 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.7575 | [19 empty] | 5623.4133 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.1803 | [19 empty] | 7498.9421 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7514 | [19 empty] | 10000 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071336 | 0.00015568 | 4 | 10413008.5457 | 25600684.9303 | 212283.2638 | 521904.5898 | 52.333 | 0 | 31.9701 | 31278.1656 | 763.8781 | 43555.4037 | 51006.0074 | 0 | 19811.7299 | 0 | 57101.922 | 148567.4879 | 101400.3633 | 453484.9579 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6484364.8258 | 15941999.8697 | 13335.2143 | 0.00062272 | 10413008.5457 | 25600684.9303 | 212283.2638 | 521904.5898
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071337 | 0.00039025 | 4 | 4148772.528 | 10207429.8823 | 84578.3396 | 208092.2647 | 52.3331 | 0 | 30.1312 | 31278.4206 | 763.8854 | 43555.6332 | 51006.1234 | 0 | 17201.6006 | 0 | 56084.2086 | 145919.6063 | 99593.1297 | 445402.6077 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6476282.4756 | 15933917.5195 | 17782.7941 | 0.001561 | 4148772.528 | 10207429.8823 | 84578.3396 | 208092.2647
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071337 | 0.00056617 | 4 | 2856459.2666 | 7032604.8718 | 58232.7858 | 143369.1626 | 52.3332 | 0 | 30.2985 | 31278.6119 | 763.8908 | 43555.8053 | 51006.2103 | 0 | 14839.3106 | 0 | 55163.0933 | 143523.0532 | 97957.4329 | 438087.4083 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6468967.2762 | 15926602.3201 | 23713.7371 | 0.0022647 | 2856459.2666 | 7032604.8718 | 58232.7858 | 143369.1626
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5272 | 0.17401 | 0.0012811 | 4 | 1336908.4352 | 3182539.1628 | 27254.6868 | 64880.3655 | 54.7072 | 0 | 58.2825 | 60810.5965 | 1534.4523 | 88683.0456 | 87352.1815 | 0 | 26335.0108 | 0 | 103238.9618 | 268606.6014 | 183329.5248 | 819890.3747 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6850770.2426 | 16308405.2865 | 31622.7766 | 0.0051243 | 1336908.4352 | 3182539.1628 | 27254.6868 | 64880.3655
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.665 | 0.23502 | 0.0019517 | 4 | 902961.9237 | 2114449.9269 | 18408.1002 | 43105.9218 | 55.2125 | 0 | 75.6804 | 75570.1904 | 1921.743 | 112733.0346 | 108866.1655 | 0 | 29654.027 | 0 | 128210.6126 | 333577.7144 | 227673.6444 | 1018207.1319 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7049086.9999 | 16506722.0438 | 42169.6503 | 0.0078066 | 902961.9237 | 2114449.9269 | 18408.1002 | 43105.9218
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1038 | 0.31229 | 0.0028415 | 4 | 641180.9083 | 1473294.0406 | 13071.3401 | 30035.0918 | 55.5833 | 0 | 105.146 | 92611.8871 | 2369.5606 | 141465.9746 | 136088.0781 | 0 | 33197.1388 | 0 | 158235.7293 | 411696.9091 | 280991.6 | 1256656.8776 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7287536.7455 | 16745171.7894 | 56234.1325 | 0.011366 | 641180.9083 | 1473294.0406 | 13071.3401 | 30035.0918
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8165 | 0.40397 | 0.0039842 | 4 | 474184.804 | 1067635.4164 | 9666.8986 | 21765.192 | 55.829 | 0 | 87.5302 | 111158.3033 | 2857.0877 | 173775.9989 | 168421.5956 | 0 | 36498.8939 | 0 | 192157.633 | 499954.744 | 341229.3858 | 1526053.6422 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7556933.5101 | 17014568.554 | 74989.4209 | 0.015937 | 474184.804 | 1067635.4164 | 9666.8986 | 21765.192
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3575 | 0.54106 | 0.0055705 | 4 | 356598.5729 | 781050.9976 | 7269.7442 | 15922.781 | 56.0949 | 0 | 91.0868 | 136757.9223 | 3531.8245 | 219481.0418 | 216621.2187 | 0 | 41845.3472 | 0 | 241112.5683 | 627325.4436 | 428162.5055 | 1914837.872 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7945717.7399 | 17403352.7838 | 100000 | 0.022282 | 356598.5729 | 781050.9976 | 7269.7442 | 15922.781
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2493 | 0.69651 | 0.0075498 | 4 | 277033.4884 | 590207.3957 | 5647.7024 | 12032.1761 | 56.2557 | 0 | 76.3685 | 163405.8773 | 4234.0678 | 268579.1477 | 271343.3822 | 0 | 46440.8661 | 0 | 294061.3031 | 765087.1903 | 522187.7283 | 2335339.5629 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8366219.4308 | 17823854.4747 | 133352.1432 | 0.030199 | 277033.4884 | 590207.3957 | 5647.7024 | 12032.1761
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7176 | 0.88298 | 0.010034 | 4 | 220549.2332 | 456191.0577 | 4496.1944 | 9300.0718 | 56.376 | 0 | 87.6386 | 193068.0721 | 5015.9324 | 324667.9978 | 336979.0215 | 0 | 51077.3092 | 0 | 355215.2499 | 924197.2155 | 630783.5899 | 2821004.3882 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8851884.2561 | 18309519.3 | 177827.941 | 0.040136 | 220549.2332 | 456191.0577 | 4496.1944 | 9300.0718
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.713 | 1.0978 | 0.013053 | 4 | 179893.0008 | 361038.2723 | 3667.3621 | 7360.2535 | 56.4653 | 0 | 82.028 | 224962.2902 | 5856.6752 | 386424.6112 | 412593.7782 | 0 | 55438.2714 | 0 | 423257.4942 | 1101229.1779 | 751611.5419 | 3361373.8403 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9392253.7082 | 18849888.7521 | 237137.3706 | 0.05221 | 179893.0008 | 361038.2723 | 3667.3621 | 7360.2535
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1272 | 1.3352 | 0.016575 | 4 | 150387.9806 | 293033.4185 | 3065.8624 | 5973.8826 | 56.5316 | 0 | 85.8452 | 258072.4093 | 6729.3935 | 451911.1738 | 496142.5022 | 0 | 59271.1965 | 0 | 496129.4033 | 1290826.9373 | 881015.9086 | 3940098.9245 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9970978.7924 | 19428613.8363 | 316227.766 | 0.066302 | 150387.9806 | 293033.4185 | 3065.8624 | 5973.8826
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7191 | 1.5822 | 0.020476 | 4 | 128886.7892 | 244358.1147 | 2627.5315 | 4981.5707 | 56.5803 | 0 | 94.3762 | 290680.5781 | 7588.7266 | 517609.7403 | 583062.8102 | 0 | 62205.4127 | 0 | 569847.4345 | 1482626.1327 | 1011922.8005 | 4525543.6355 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 10556423.5034 | 20014058.5473 | 421696.5034 | 0.081905 | 128886.7892 | 244358.1147 | 2627.5315 | 4981.5707
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.2427 | 1.8256 | 0.024559 | 4 | 113191.5279 | 209466.6709 | 2307.5624 | 4270.2614 | 56.6161 | 0 | 98.4343 | 321339.9276 | 8396.5159 | 580356.9318 | 668699.2611 | 0 | 64128.821 | 0 | 640739.3683 | 1667072.4027 | 1137811.1698 | 5088544.3981 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11119424.266 | 20577059.3099 | 562341.3252 | 0.098235 | 113191.5279 | 209466.6709 | 2307.5624 | 4270.2614
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4233 | 2.0505 | 0.028579 | 4 | 101724.5222 | 184455.8518 | 2073.792 | 3760.382 | 56.642 | 0 | 92.007 | 348602.2152 | 9114.6233 | 636874.7837 | 747847.0253 | 0 | 64971.8329 | 0 | 704890.0874 | 1833979.4145 | 1251728.6349 | 5598008.6171 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11628888.4851 | 21086523.529 | 749894.2093 | 0.11432 | 101724.5222 | 184455.8518 | 2073.792 | 3760.382
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.1085 | 2.2488 | 0.03233 | 4 | 93336.836 | 166471.4579 | 1902.7977 | 3393.7458 | 56.6608 | 0 | 119.7391 | 371900.1674 | 9728.1553 | 685675.1672 | 817619.4798 | 0 | 64955.6014 | 0 | 760452.6427 | 1978541.7861 | 1350395.424 | 6039268.424 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12070148.292 | 21527783.3359 | 1000000 | 0.12932 | 93336.836 | 166471.4579 | 1902.7977 | 3393.7458
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.2024 | 2.4153 | 0.035655 | 4 | 87189.3756 | 153502.5098 | 1777.4734 | 3129.3563 | 56.6742 | 0 | 109.3048 | 390987.8173 | 10230.6944 | 725982.3025 | 876196.6878 | 0 | 64286.6877 | 0 | 806396.834 | 2098079.1473 | 1431982.1293 | 6404142.3003 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12435022.1682 | 21892657.2121 | 1333521.4322 | 0.14262 | 87189.3756 | 153502.5098 | 1777.4734 | 3129.3563
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.7434 | 2.552 | 0.038499 | 4 | 82671.5954 | 144086.1992 | 1685.3723 | 2937.3921 | 56.6838 | 0 | 109.1537 | 406369.7927 | 10635.5842 | 758669.4562 | 924304.0526 | 0 | 63311.1477 | 0 | 843683.113 | 2195090.3968 | 1498194.3004 | 6700257.8435 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12731137.7115 | 22188772.7554 | 1778279.41 | 0.154 | 82671.5954 | 144086.1992 | 1685.3723 | 2937.3921
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.7728 | 2.6612 | 0.040853 | 4 | 79341.2727 | 137217.4433 | 1617.4792 | 2797.3632 | 56.6907 | 0 | 88.7721 | 418476.5304 | 10954.2025 | 784521.9636 | 962723.7987 | 0 | 62210.5239 | 0 | 873165.9374 | 2271798.6582 | 1550549.265 | 6934400.8796 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12965280.7475 | 22422915.7914 | 2371373.7057 | 0.16341 | 79341.2727 | 137217.4433 | 1617.4792 | 2797.3632
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.3682 | 2.747 | 0.042755 | 4 | 76878.7872 | 132179.8373 | 1567.2781 | 2694.6648 | 56.6956 | 0 | 103.0337 | 427887.9406 | 11201.8475 | 804693.7383 | 992923.7792 | 0 | 61134.5839 | 0 | 896158.3369 | 2331620.1652 | 1591378.6727 | 7116999.0642 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13147878.9321 | 22605513.976 | 3162277.6602 | 0.17102 | 76878.7872 | 132179.8373 | 1567.2781 | 2694.6648
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6102 | 2.8138 | 0.044266 | 4 | 75052.9137 | 128466.552 | 1530.0552 | 2618.9644 | 56.6991 | 0 | 100.6585 | 435153.0618 | 11392.9918 | 820309.4721 | 1016434.284 | 0 | 60171.1477 | 0 | 913949.7734 | 2377909.8334 | 1622972.3225 | 7258292.8866 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13289172.7545 | 22746807.7984 | 4216965.0343 | 0.17706 | 75052.9137 | 128466.552 | 1530.0552 | 2618.9644
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.5434 | 2.864 | 0.045439 | 4 | 73695.8223 | 125730.9581 | 1502.389 | 2563.1956 | 56.7016 | 0 | 117.5837 | 440576.1646 | 11535.6581 | 831990.8026 | 1034095.3737 | 0 | 59291.73 | 0 | 927220.9943 | 2412438.828 | 1646539.0708 | 7363688.6222 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13394568.4901 | 22852203.534 | 5623413.2519 | 0.18175 | 73695.8223 | 125730.9581 | 1502.389 | 2563.1956
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.2692 | 2.903 | 0.046352 | 4 | 72685.1567 | 123695.1655 | 1481.7852 | 2521.6933 | 56.7035 | 0 | 97.4093 | 444774.6738 | 11646.0999 | 841048.8591 | 1047833.5387 | 0 | 58597.1099 | 0 | 937521.1098 | 2439237.6156 | 1664829.7939 | 7445488.8007 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13476368.6686 | 22934003.7125 | 7498942.0933 | 0.18541 | 72685.1567 | 123695.1655 | 1481.7852 | 2521.6933
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8151 | 2.9324 | 0.047051 | 4 | 71931.2879 | 122183.8075 | 1466.4166 | 2490.8822 | 56.7048 | 0 | 99.3836 | 447920.2177 | 11728.8382 | 847843.449 | 1058163.3548 | 0 | 58022.7181 | 0 | 945234.6453 | 2459306.6528 | 1678527.3242 | 7506747.2 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13537627.0679 | 22995262.1118 | 10000000 | 0.1882 | 71931.2879 | 122183.8075 | 1466.4166 | 2490.8822
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.4298 | [19 empty] | 100 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.1706 | [19 empty] | 133.3521 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5898 | [19 empty] | 177.8279 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9048 | [19 empty] | 237.1374 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1806 | [19 empty] | 316.2278 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6337 | [19 empty] | 421.6965 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.96 | [19 empty] | 562.3413 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6772 | [19 empty] | 749.8942 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8289 | [19 empty] | 1000 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7313 | [19 empty] | 1333.5214 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.676 | [19 empty] | 1778.2794 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5923 | [19 empty] | 2371.3737 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.1779 | [19 empty] | 3162.2777 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.2816 | [19 empty] | 4216.965 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.1098 | [19 empty] | 5623.4133 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.1813 | [19 empty] | 7498.9421 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077439 | 0.00020021 | 4 | 8517189.9423 | 20861064.9507 | 173634.4373 | 425281.0257 | 54.248 | 0 | 35.1028 | 34581.454 | 858.7955 | 46423.2813 | 52437.8575 | 0 | 22103.5712 | 0 | 60997.9342 | 158704.1124 | 108318.8178 | 484425.8239 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6821051.7468 | 16706731.2676 | 10000 | 0.00080086 | 8517189.9423 | 20861064.9507 | 173634.4373 | 425281.0257
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077439 | 0.00050298 | 4 | 3385759.1604 | 8299310.9233 | 69023.2801 | 169192.6788 | 54.2482 | 0 | 32.7319 | 34581.8047 | 858.8057 | 46423.584 | 52438.0068 | 0 | 19141.8362 | 0 | 59843.1746 | 155699.6647 | 106268.2205 | 475255.0972 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6811881.02 | 16697560.5409 | 13335.2143 | 0.0020119 | 3385759.1604 | 8299310.9233 | 69023.2801 | 169192.6788
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.07744 | 0.00073004 | 4 | 2329898.7159 | 5715220.3905 | 47498.1367 | 116512.4981 | 54.2484 | 0 | 32.345 | 34582.0678 | 858.8133 | 46423.8112 | 52438.1188 | 0 | 16492.117 | 0 | 58810.0219 | 153011.6135 | 104433.5703 | 467050.1338 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6803676.0567 | 16689355.5776 | 17782.7941 | 0.0029202 | 2329898.7159 | 5715220.3905 | 47498.1367 | 116512.4981
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4781 | 0.18717 | 0.0016164 | 4 | 1114916.4622 | 2643841.3774 | 22729.0801 | 53898.2825 | 56.8584 | 0 | 73.087 | 66846.4667 | 1716.4246 | 93812.1812 | 89931.0153 | 0 | 29288.3673 | 0 | 109821.8375 | 285733.8935 | 195019.2536 | 872169.4395 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7208795.3624 | 17094474.8832 | 23713.7371 | 0.0064658 | 1114916.4622 | 2643841.3774 | 22729.0801 | 53898.2825
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6159 | 0.25401 | 0.0024624 | 4 | 753770.16 | 1757437.2763 | 15366.6243 | 35827.736 | 57.4361 | 0 | 87.8571 | 83410.1686 | 2159.2933 | 119705.6992 | 112684.8453 | 0 | 33215.1522 | 0 | 136958.3119 | 356337.4335 | 243207.6203 | 1087678.5243 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7424304.4472 | 17309983.968 | 31622.7766 | 0.0098496 | 753770.16 | 1757437.2763 | 15366.6243 | 35827.736
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0332 | 0.33736 | 0.0035862 | 4 | 535312.1533 | 1224466.9815 | 10913.0623 | 24962.4156 | 57.8537 | 0 | 90.1425 | 102241.2493 | 2663.5072 | 150154.6581 | 141036.8814 | 0 | 37266.8138 | 0 | 169011.6128 | 439733.5475 | 300127.1818 | 1342235.452 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7678861.3749 | 17564540.8957 | 42169.6503 | 0.014345 | 535312.1533 | 1224466.9815 | 10913.0623 | 24962.4156
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7628 | 0.43877 | 0.0050386 | 4 | 395633.1577 | 886131.7475 | 8065.5171 | 18064.9943 | 58.1385 | 0 | 101.6767 | 123241.4004 | 3225.9037 | 185240.4745 | 175562.1573 | 0 | 41295.9586 | 0 | 206140.6988 | 536335.8131 | 366060.2131 | 1637102.6195 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7973728.5424 | 17859408.0632 | 56234.1325 | 0.020154 | 395633.1577 | 886131.7475 | 8065.5171 | 18064.9943
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2675 | 0.58679 | 0.0070465 | 4 | 297600.2317 | 648331.0551 | 6066.9833 | 13217.1055 | 58.4339 | 0 | 77.2428 | 151513.6914 | 3984.9462 | 233672.3995 | 225797.6857 | 0 | 47397.992 | 0 | 258323.0188 | 672103.5055 | 458724.4529 | 2051517.6919 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8388143.6148 | 18273823.1357 | 74989.4209 | 0.028186 | 297600.2317 | 648331.0551 | 6066.9833 | 13217.1055
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1614 | 0.75729 | 0.0095712 | 4 | 230982.7477 | 489197.6268 | 4708.8957 | 9972.9553 | 58.6167 | 0 | 85.6048 | 181402.666 | 4786.9812 | 286521.8376 | 283725.8335 | 0 | 52821.4317 | 0 | 315610.9125 | 821154.8537 | 560455.0607 | 2506479.577 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8843105.4999 | 18728785.0207 | 100000 | 0.038285 | 230982.7477 | 489197.6268 | 4708.8957 | 9972.9553
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6787 | 0.96457 | 0.012768 | 4 | 183566.3839 | 377130.3183 | 3742.249 | 7688.3116 | 58.7544 | 0 | 83.403 | 215086.7835 | 5690.9224 | 347663.6681 | 354141.1523 | 0 | 58434.8557 | 0 | 382596.779 | 995438.3376 | 679407.1196 | 3038459.6183 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9375085.5411 | 19260765.062 | 133352.1432 | 0.051072 | 183566.3839 | 377130.3183 | 3742.249 | 7688.3116
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8009 | 1.2075 | 0.016703 | 4 | 149320.2178 | 297281.5041 | 3044.0946 | 6060.4856 | 58.8573 | 0 | 86.7716 | 251873.9692 | 6678.0332 | 416073.2593 | 436670.7389 | 0 | 63889.4469 | 0 | 458322.3245 | 1192460.6736 | 813878.9123 | 3639847.3579 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9976473.2808 | 19862152.8016 | 177827.941 | 0.066813 | 149320.2178 | 297281.5041 | 3044.0946 | 6060.4856
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4413 | 1.4811 | 0.021373 | 4 | 124360.9388 | 239996.1434 | 2535.2659 | 4892.646 | 58.934 | 0 | 90.5374 | 290699.4687 | 7719.5903 | 489871.4476 | 529581.4807 | 0 | 68846.4188 | 0 | 540820.1784 | 1407103.1667 | 960376.8244 | 4295018.5757 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 10631644.4986 | 20517324.0194 | 237137.3706 | 0.08549 | 124360.9388 | 239996.1434 | 2535.2659 | 4892.646
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3723 | 1.7718 | 0.026648 | 4 | 106084.0647 | 198828.9594 | 2162.6671 | 4053.3973 | 58.9906 | 0 | 105.5521 | 329659.0389 | 8764.4074 | 565367.4297 | 628322.265 | 0 | 72817.0767 | 0 | 625922.7849 | 1628522.6919 | 1111500.2 | 4970875.8945 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11307501.8174 | 21193181.3383 | 316227.766 | 0.10659 | 106084.0647 | 198828.9594 | 2162.6671 | 4053.3973
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.3292 | 2.0641 | 0.032288 | 4 | 92676.6081 | 169219.2327 | 1889.338 | 3449.7629 | 59.0322 | 0 | 96.9003 | 366934.4313 | 9763.7131 | 638798.8372 | 727585.9898 | 0 | 75560.3668 | 0 | 709270.9019 | 1845377.3953 | 1259507.991 | 5632799.6265 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11969425.5494 | 21855105.0702 | 421696.5034 | 0.12915 | 92676.6081 | 169219.2327 | 1889.338 | 3449.7629
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.046 | 2.3423 | 0.037981 | 4 | 82839.0468 | 147908.4026 | 1688.786 | 3015.3128 | 59.0627 | 0 | 109.4341 | 400964.1767 | 10675.6705 | 706765.3912 | 822047.4485 | 0 | 77050.4105 | 0 | 786826.208 | 2047160.3929 | 1397229.0331 | 6248718.7315 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 12585344.6544 | 22471024.1752 | 562341.3252 | 0.15193 | 82839.0468 | 147908.4026 | 1688.786 | 3015.3128
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.2692 | 2.5914 | 0.043395 | 4 | 75619.7833 | 132571.268 | 1541.6116 | 2702.6446 | 59.0846 | 0 | 97.6237 | 430420.3908 | 11464.7724 | 766260.0891 | 906627.601 | 0 | 77333.8106 | 0 | 854921.599 | 2224330.632 | 1518151.3617 | 6789510.2567 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13126136.1795 | 23011815.7004 | 749894.2093 | 0.17358 | 75619.7833 | 132571.268 | 1541.6116 | 2702.6446
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.8897 | 2.8049 | 0.048289 | 4 | 70317.1678 | 121496.9594 | 1433.5106 | 2476.8799 | 59.1002 | 0 | 104.1918 | 455000.9324 | 12123.0298 | 816351.5093 | 979131.8347 | 0 | 76739.7325 | 0 | 912345.3451 | 2373735.4403 | 1620123.2134 | 7245551.0375 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13582176.9604 | 23467856.4813 | 1000000 | 0.19316 | 70317.1678 | 121496.9594 | 1433.5106 | 2476.8799
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.8735 | 2.9808 | 0.052521 | 4 | 66415.2642 | 113471.0983 | 1353.965 | 2313.2618 | 59.111 | 0 | 97.7684 | 474835.8564 | 12654.031 | 857055.3349 | 1038879.8139 | 0 | 75579.548 | 0 | 959011.7878 | 2495151.9516 | 1702992.4772 | 7616160.8008 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13952786.7237 | 23838466.2446 | 1333521.4322 | 0.21008 | 66415.2642 | 113471.0983 | 1353.965 | 2313.2618
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.2876 | 3.1231 | 0.056067 | 4 | 63537.0135 | 107616.6417 | 1295.288 | 2193.9108 | 59.1187 | 0 | 116.3109 | 490623.6201 | 13076.5661 | 889629.8803 | 1087214.3403 | 0 | 74214.2556 | 0 | 996355.8783 | 2592313.6146 | 1769307.3087 | 7912735.4639 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14249361.3867 | 24135040.9076 | 1778279.41 | 0.22427 | 63537.0135 | 107616.6417 | 1295.288 | 2193.9108
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.1829 | 3.2348 | 0.05895 | 4 | 61408.1688 | 103332.4817 | 1251.8886 | 2106.5724 | 59.124 | 0 | 117.3504 | 502863.8805 | 13404.0788 | 914990.3925 | 1125156.2451 | 0 | 72789.761 | 0 | 1025389.6996 | 2667853.662 | 1820864.9432 | 8143312.6628 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14479938.5857 | 24365618.1065 | 2371373.7057 | 0.2358 | 61408.1688 | 103332.4817 | 1251.8886 | 2106.5724
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.6593 | 3.3218 | 0.06125 | 4 | 59829.5369 | 100179.3041 | 1219.706 | 2042.2906 | 59.1277 | 0 | 92.1477 | 512307.8662 | 13656.7217 | 934619.5089 | 1154707.2271 | 0 | 71473.0773 | 0 | 1047838.1164 | 2726259.8378 | 1860728.3583 | 8321590.7137 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14658216.6366 | 24543896.1574 | 3162277.6602 | 0.245 | 59829.5369 | 100179.3041 | 1219.706 | 2042.2906
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.7971 | 3.3888 | 0.063057 | 4 | 58656.2211 | 97849.5198 | 1195.7864 | 1994.7948 | 59.1303 | 0 | 112.4667 | 519533.3104 | 13849.9839 | 949673.7104 | 1177478.0072 | 0 | 70324.2174 | 0 | 1065035.0994 | 2771002.8599 | 1891266.3903 | 8458163.5789 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14794789.5017 | 24680469.0226 | 4216965.0343 | 0.25223 | 58656.2211 | 97849.5198 | 1195.7864 | 1994.7948
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.6855 | 3.4412 | 0.064471 | 4 | 57782.4642 | 96116.3955 | 1177.9737 | 1959.4627 | 59.1322 | 0 | 128.391 | 525143.9407 | 14000.0349 | 961385.0153 | 1195256.0443 | 0 | 69408.2383 | 0 | 1078425.3767 | 2805841.6146 | 1915044.5562 | 8564504.8209 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14901130.7438 | 24786810.2647 | 5623413.2519 | 0.25788 | 57782.4642 | 96116.3955 | 1177.9737 | 1959.4627
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.3387 | 3.4796 | 0.065546 | 4 | 57130.7573 | 94835.8547 | 1164.6878 | 1933.3572 | 59.1335 | 0 | 133.9125 | 529252.3599 | 14109.8998 | 969972.6016 | 1208327.3412 | 0 | 68601.4197 | 0 | 1088202.8126 | 2831280.4974 | 1932407.1165 | 8642154.0486 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14978779.9715 | 24864459.4923 | 7498942.0933 | 0.26218 | 57130.7573 | 94835.8547 | 1164.6878 | 1933.3572
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8381 | 3.509 | 0.066371 | 4 | 56644.0611 | 93880.6936 | 1154.7658 | 1913.8849 | 59.1345 | 0 | 130.0454 | 532383.1386 | 14193.615 | 976523.424 | 1218318.3229 | 0 | 67970.1151 | 0 | 1095661.5601 | 2850686.6282 | 1945652.1995 | 8701389.0033 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 15038014.9262 | 24923694.447 | 10000000 | 0.26548 | 56644.0611 | 93880.6936 | 1154.7658 | 1913.8849
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.9645 | [19 empty] | 100 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.3315 | [19 empty] | 133.3521 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8322 | [19 empty] | 177.8279 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9939 | [19 empty] | 237.1374 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.231 | [19 empty] | 316.2278 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6356 | [19 empty] | 421.6965 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4373 | [19 empty] | 562.3413 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8561 | [19 empty] | 749.8942 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1975 | [19 empty] | 1000 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8677 | [19 empty] | 1333.5214 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1212 | [19 empty] | 1778.2794 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.1401 | [19 empty] | 2371.3737 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.7515 | [19 empty] | 3162.2777 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.0736 | [19 empty] | 4216.965 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.8581 | [19 empty] | 5623.4133 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.083714 | 0.00019192 | 4 | 9333434.8281 | 22779113.6925 | 190274.6934 | 464383.0437 | 56.1349 | 0 | 37.6616 | 37950.0648 | 957.583 | 49319.4103 | 53849.692 | 0 | 24788.5132 | 0 | 65077.4527 | 169318.1828 | 115563.1389 | 516824.0379 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7165056.1066 | 17486984.2316 | 7498.9421 | 0.00076768 | 9333434.8281 | 22779113.6925 | 190274.6934 | 464383.0437
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.083715 | 0.00058313 | 4 | 3067336.4396 | 7492575.7218 | 62531.8022 | 152746.2905 | 56.1351 | 0 | 36.8121 | 37950.5465 | 957.5974 | 49319.8121 | 53849.8857 | 0 | 21412.1714 | 0 | 63761.1051 | 165893.3164 | 113225.5972 | 506370.0319 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7154602.1006 | 17476530.2256 | 10000 | 0.0023325 | 3067336.4396 | 7492575.7218 | 62531.8022 | 152746.2905
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.083715 | 0.00087652 | 4 | 2037993.2849 | 4982008.8766 | 41547.2497 | 101564.9896 | 56.1353 | 0 | 35.365 | 37950.9081 | 957.6081 | 49320.1136 | 53850.0311 | 0 | 18423.9815 | 0 | 62596.0305 | 162862.0312 | 111156.6828 | 497117.387 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7145349.4557 | 17467277.5807 | 13335.2143 | 0.0035061 | 2037993.2849 | 4982008.8766 | 41547.2497 | 101564.9896
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.19349 | 0.001882 | 4 | 1002858.1686 | 2373980.4212 | 20444.6202 | 48396.8019 | 58.9059 | 0 | 76.3674 | 71131.0482 | 1855.8092 | 96152.306 | 90143.7204 | 0 | 31740.0577 | 0 | 113498.9472 | 295300.9788 | 201548.9858 | 901371.8533 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7549603.922 | 17871532.0471 | 17782.7941 | 0.0075281 | 1002858.1686 | 2373980.4212 | 20444.6202 | 48396.8019
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4332 | 0.26419 | 0.0028882 | 4 | 673193.3714 | 1566651.8758 | 13723.9574 | 31938.3175 | 59.5821 | 0 | 86.1485 | 89234.2559 | 2348.8536 | 123276.6853 | 113424.9332 | 0 | 36238.7912 | 0 | 142164.1725 | 369882.0149 | 252452.0755 | 1129021.782 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7777253.8507 | 18099181.9757 | 23713.7371 | 0.011553 | 673193.3714 | 1566651.8758 | 13723.9574 | 31938.3175
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.824 | 0.35318 | 0.0042311 | 4 | 475537.8295 | 1085421.6497 | 9694.4819 | 22127.7885 | 60.0733 | 0 | 107.0513 | 109976.2143 | 2914.6273 | 155431.1796 | 142702.7175 | 0 | 40978.4427 | 0 | 176281.2407 | 458647.6281 | 313036.4304 | 1399968.4806 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8048200.5493 | 18370128.6743 | 31622.7766 | 0.016924 | 475537.8295 | 1085421.6497 | 9694.4819 | 22127.7885
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.505 | 0.46057 | 0.0059756 | 4 | 349692.7047 | 781525.7037 | 7128.9588 | 15932.4586 | 60.4093 | 0 | 109.8166 | 132892.8953 | 3539.7773 | 192149.7886 | 178048.899 | 0 | 45577.2448 | 0 | 215361.3559 | 560326.0714 | 382434.0573 | 1710330.0895 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8358562.1582 | 18680490.2832 | 42169.6503 | 0.023903 | 349692.7047 | 781525.7037 | 7128.9588 | 15932.4586
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9165 | 0.61564 | 0.008371 | 4 | 262500.0766 | 570764.6247 | 5351.4191 | 11635.8089 | 60.7392 | 0 | 105.61 | 163376.7782 | 4373.0846 | 242288.7674 | 228952.7019 | 0 | 52369.1659 | 0 | 269630.5942 | 701523.4973 | 478804.2018 | 2141318.7912 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8789550.8599 | 19111478.9849 | 56234.1325 | 0.033484 | 262500.0766 | 570764.6247 | 5351.4191 | 11635.8089
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7593 | 0.79802 | 0.011417 | 4 | 203030.532 | 429044.0313 | 4139.052 | 8746.6429 | 60.9522 | 0 | 104.563 | 196276.4132 | 5271.9467 | 298124.0172 | 288867.8744 | 0 | 58686.1287 | 0 | 330418.2883 | 859680.608 | 586749.6796 | 2624074.9561 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9272307.0248 | 19594235.1498 | 74989.4209 | 0.04567 | 203030.532 | 429044.0313 | 4139.052 | 8746.6429
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2307 | 1.0207 | 0.015303 | 4 | 160718.4884 | 329339.1325 | 3276.4638 | 6714.0237 | 61.1123 | 0 | 113.4863 | 233472.5678 | 6288.2711 | 362928.9068 | 362011.5524 | 0 | 65235.1093 | 0 | 401675.1989 | 1045076.4725 | 713286.1667 | 3189974.2454 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9838206.3141 | 20160134.4391 | 100000 | 0.061214 | 160718.4884 | 329339.1325 | 3276.4638 | 6714.0237
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.3723 | 1.2863 | 0.02015 | 4 | 130133.2947 | 258199.2752 | 2652.9432 | 5263.7415 | 61.2328 | 0 | 118.1216 | 274757.7284 | 7416.0919 | 436648.3598 | 449272.3449 | 0 | 71816.3818 | 0 | 483565.2537 | 1258137.5972 | 858704.7622 | 3840318.5199 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 10488550.5886 | 20810478.7136 | 133352.1432 | 0.080599 | 130133.2947 | 258199.2752 | 2652.9432 | 5263.7415
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1124 | 1.5903 | 0.025993 | 4 | 107793.5671 | 207068.9702 | 2197.5177 | 4221.381 | 61.3229 | 0 | 102.1023 | 318961.7579 | 8623.1898 | 517383.2083 | 549148.1237 | 0 | 77946.6672 | 0 | 574104.5493 | 1493702.2722 | 1019482.4933 | 4559352.2615 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 11207584.3302 | 21529512.4552 | 177827.941 | 0.10397 | 107793.5671 | 207068.9702 | 2197.5177 | 4221.381
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2844 | 1.9221 | 0.032743 | 4 | 91379.334 | 170190.4908 | 1862.8913 | 3469.5634 | 61.3898 | 0 | 119.8978 | 364385.4389 | 9863.023 | 602034.978 | 658136.7517 | 0 | 83151.5167 | 0 | 669852.9662 | 1742820.0124 | 1189510.4698 | 5319755.1566 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 11967987.2253 | 22289915.3503 | 237137.3706 | 0.13097 | 91379.334 | 170190.4908 | 1862.8913 | 3469.5634
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.6387 | 2.2657 | 0.040149 | 4 | 79289.9723 | 143562.5345 | 1616.4333 | 2926.7164 | 61.4394 | 0 | 130.0384 | 409000.6073 | 11080.1849 | 686650.9949 | 770979.8298 | 0 | 87072.5412 | 0 | 766265.8217 | 1993666.4852 | 1360718.3419 | 6085434.807 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 12733666.8757 | 23055595.0007 | 316227.766 | 0.1606 | 79289.9723 | 143562.5345 | 1616.4333 | 2926.7164
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.8445 | 2.5997 | 0.047809 | 4 | 70384.3011 | 124359.1063 | 1434.8792 | 2535.2286 | 61.4757 | 0 | 107.0744 | 450478.2725 | 12211.1841 | 766492.1464 | 880699.3648 | 0 | 89416.8511 | 0 | 857726.1494 | 2231627.4969 | 1523131.622 | 6811783.0872 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 13460015.1559 | 23781943.2809 | 421696.5034 | 0.19124 | 70384.3011 | 124359.1063 | 1434.8792 | 2535.2286
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.6387 | 2.9074 | 0.055285 | 4 | 63827.6396 | 110503.2724 | 1301.2128 | 2252.7587 | 61.5019 | 0 | 131.1517 | 487287.834 | 13214.3981 | 838219.7982 | 981746.9242 | 0 | 90286.0972 | 0 | 940194.4702 | 2446193.151 | 1669577.0898 | 7466719.7627 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 14114951.8314 | 24436879.9564 | 562341.3252 | 0.22114 | 63827.6396 | 110503.2724 | 1301.2128 | 2252.7587
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8038 | 3.1747 | 0.062174 | 4 | 59000.9743 | 100504.9019 | 1202.8147 | 2048.9284 | 61.5202 | 0 | 157.9334 | 518324.5346 | 14059.8727 | 899298.0485 | 1069525.915 | 0 | 89851.6404 | 0 | 1010513.4044 | 2629148.5934 | 1794447.9386 | 8025169.9475 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 14673402.0162 | 24995330.1412 | 749894.2093 | 0.2487 | 59000.9743 | 100504.9019 | 1202.8147 | 2048.9284
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.307 | 3.3994 | 0.068248 | 4 | 55444.7273 | 93255.0848 | 1130.3158 | 1901.131 | 61.5328 | 0 | 133.7454 | 543818.5981 | 14754.0489 | 949862.6074 | 1143343.7774 | 0 | 88629.2204 | 0 | 1068759.2183 | 2780692.2535 | 1897879.6005 | 8487739.3245 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15135971.3932 | 25457899.5182 | 1000000 | 0.27299 | 55444.7273 | 93255.0848 | 1130.3158 | 1901.131
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.1575 | 3.5822 | 0.073398 | 4 | 52819.8754 | 87977.2514 | 1076.8046 | 1793.5353 | 61.5413 | 0 | 131.5193 | 564181.8194 | 15308.2946 | 990499.2073 | 1203394.7325 | 0 | 86977.9421 | 0 | 1115541.1784 | 2902409.3172 | 1980953.9975 | 8859266.4889 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15507498.5576 | 25829426.6826 | 1333521.4322 | 0.29359 | 52819.8754 | 87977.2514 | 1076.8046 | 1793.5353
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.4297 | 3.7278 | 0.077639 | 4 | 50878.0972 | 84114.9362 | 1037.2188 | 1714.7967 | 61.5471 | 0 | 131.2135 | 580182.7849 | 15743.6572 | 1022582.7528 | 1251251.3179 | 0 | 85215.3732 | 0 | 1152440.5955 | 2998414.0315 | 2046479.1877 | 9152309.7008 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15800541.7695 | 26122469.8945 | 1778279.41 | 0.31056 | 50878.0972 | 84114.9362 | 1037.2188 | 1714.7967
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.2083 | 3.8418 | 0.08105 | 4 | 49438.2397 | 81276.256 | 1007.8654 | 1656.9264 | 61.551 | 0 | 129.2592 | 592571.3364 | 16080.6338 | 1047514.0489 | 1288704.9997 | 0 | 83525.6092 | 0 | 1181074.6849 | 3072914.0584 | 2097326.9869 | 9379712.3583 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16027944.427 | 26349872.552 | 2371373.7057 | 0.3242 | 49438.2397 | 81276.256 | 1007.8654 | 1656.9264
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.5749 | 3.9293 | 0.08374 | 4 | 48368.2113 | 79183.7911 | 986.0514 | 1614.2687 | 61.5536 | 0 | 149.1542 | 602010.3209 | 16337.3201 | 1066562.4342 | 1317475.068 | 0 | 81990.0642 | 0 | 1202906.3309 | 3129715.523 | 2136095.1537 | 9553092.2149 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16201324.2836 | 26523252.4087 | 3162277.6602 | 0.33496 | 48368.2113 | 79183.7911 | 986.0514 | 1614.2687
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.6297 | 3.9969 | 0.085842 | 4 | 47571.5017 | 77632.3997 | 969.8094 | 1582.6415 | 61.5554 | 0 | 124.2918 | 609250.4178 | 16534.1726 | 1081204.2254 | 1339679.2984 | 0 | 80703.8514 | 0 | 1219675.0666 | 3173344.3335 | 2165872.7133 | 9686264.0791 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16334496.1478 | 26656424.2728 | 4216965.0343 | 0.34337 | 47571.5017 | 77632.3997 | 969.8094 | 1582.6415
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.4339 | 4.0484 | 0.087465 | 4 | 46977.3555 | 76480.2262 | 957.6969 | 1559.1529 | 61.5567 | 0 | 120.0313 | 614743.8972 | 16683.5142 | 1092331.6303 | 1356605.7013 | 0 | 79644.8959 | 0 | 1232403.7592 | 3206461.7806 | 2188476.0515 | 9787351.2302 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16435583.2989 | 26757511.4239 | 5623413.2519 | 0.34986 | 46977.3555 | 76480.2262 | 957.6969 | 1559.1529
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.0381 | 4.087 | 0.088706 | 4 | 46533.7048 | 75624.138 | 948.6525 | 1541.7003 | 61.5575 | 0 | 135.333 | 618856.1015 | 16795.2929 | 1100671.2197 | 1369320.5358 | 0 | 78776.0981 | 0 | 1241923.5067 | 3231230.211 | 2205381.0142 | 9862953.98 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16511186.0487 | 26833114.1737 | 7498942.0933 | 0.35482 | 46533.7048 | 75624.138 | 948.6525 | 1541.7003
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.501 | 4.1167 | 0.089655 | 4 | 46202.0971 | 74984.3906 | 941.8922 | 1528.6582 | 61.5582 | 0 | 116.4671 | 621998.0783 | 16880.6914 | 1107048.9677 | 1379061.0256 | 0 | 78106.8436 | 0 | 1249207.2866 | 3250181.112 | 2218315.3935 | 9920799.3986 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16569031.4673 | 26890959.5923 | 10000000 | 0.35862 | 46202.0971 | 74984.3906 | 941.8922 | 1528.6582
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.0589 | [19 empty] | 100 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.2366 | [19 empty] | 133.3521 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0542 | [19 empty] | 177.8279 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1965 | [19 empty] | 237.1374 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8245 | [19 empty] | 316.2278 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7955 | [19 empty] | 421.6965 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9496 | [19 empty] | 562.3413 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3423 | [19 empty] | 749.8942 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8741 | [19 empty] | 1000 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.1904 | [19 empty] | 1333.5214 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.5399 | [19 empty] | 1778.2794 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8551 | [19 empty] | 2371.3737 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.0123 | [19 empty] | 3162.2777 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.9912 | [19 empty] | 4216.965 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.089945 | 0.00010752 | 4 | 17475857.1037 | 42509222.1698 | 356268.9849 | 866607.9919 | 57.994 | 0 | 35.7989 | 41351.0382 | 1059.7304 | 52141.9289 | 55195.9533 | 0 | 27937.834 | 0 | 69297.7291 | 180298.4761 | 123057.4147 | 550340.1047 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7516038.4101 | 18282419.2665 | 5623.4133 | 0.00043008 | 17475857.1037 | 42509222.1698 | 356268.9849 | 866607.9919
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.089946 | 0.00061341 | 4 | 3058363.947 | 7446319.2431 | 62348.8858 | 151803.2897 | 57.9944 | 0 | 34.6814 | 41351.7026 | 1059.7505 | 52142.4771 | 55196.212 | 0 | 24071.211 | 0 | 67790.3278 | 176376.5271 | 120380.6039 | 538368.8121 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7504067.1175 | 18270447.9739 | 7498.9421 | 0.0024536 | 3058363.947 | 7446319.2431 | 62348.8858 | 151803.2897
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.089947 | 0.0009928 | 4 | 1886983.2406 | 4598102.7647 | 38468.7057 | 93738.5443 | 57.9946 | 0 | 35.0144 | 41352.2013 | 1059.7657 | 52142.8885 | 55196.4062 | 0 | 20682.8639 | 0 | 66469.309 | 172939.5073 | 118034.7673 | 527877.7092 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7493576.0146 | 18259956.871 | 10000 | 0.0039712 | 1886983.2406 | 4598102.7647 | 38468.7057 | 93738.5443
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1297 | 0.19509 | 0.0020553 | 4 | 958606.5265 | 2268197.4183 | 19542.4907 | 46240.2723 | 60.8561 | 0 | 74.2403 | 74090.5167 | 1961.9636 | 96608.6286 | 88896.1099 | 0 | 33923.0525 | 0 | 115237.3058 | 299823.8312 | 204635.9256 | 915177.3337 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7880875.6391 | 18647256.4955 | 13335.2143 | 0.0082212 | 958606.5265 | 2268197.4183 | 19542.4907 | 46240.2723
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 0.27216 | 0.0032024 | 4 | 634735.8917 | 1475236.1692 | 12939.9497 | 30074.6847 | 61.6882 | 0 | 53.4938 | 94539.2652 | 2529.3066 | 125989.4856 | 113503.8897 | 0 | 39560.1354 | 0 | 146687.6121 | 381651.077 | 260484.7022 | 1164945.4739 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8130643.7792 | 18897024.6356 | 17782.7941 | 0.012809 | 634735.8917 | 1475236.1692 | 12939.9497 | 30074.6847
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4802 | 0.35755 | 0.0047269 | 4 | 443701.1627 | 1013126.9257 | 9045.4484 | 20653.9627 | 62.2222 | 0 | 90.8488 | 115158.7851 | 3102.2377 | 156649.2724 | 140733.8069 | 0 | 43973.6656 | 0 | 179250.9294 | 466374.1489 | 318309.9396 | 1423552.7856 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8389251.091 | 19155631.9474 | 23713.7371 | 0.018907 | 443701.1627 | 1013126.9257 | 9045.4484 | 20653.9627
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1197 | 0.47101 | 0.0067362 | 4 | 323531.6639 | 723102.2847 | 6595.6306 | 14741.4181 | 62.6363 | 0 | 80.3885 | 140264.7215 | 3799.8613 | 195214.5375 | 176901.1408 | 0 | 49424.789 | 0 | 220585.9696 | 573919.4444 | 391711.8137 | 1751822.2778 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8717520.5832 | 19483901.4396 | 31622.7766 | 0.026945 | 323531.6639 | 723102.2847 | 6595.6306 | 14741.4181
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4561 | 0.63346 | 0.0094769 | 4 | 241856.2461 | 525871.1937 | 4930.5667 | 10720.5956 | 63.0137 | 0 | 82.3987 | 173249.4689 | 4717.8022 | 247348.5849 | 228579.5519 | 0 | 57231.0776 | 0 | 277339.3293 | 721580.0447 | 492493.2075 | 2202539.067 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9168237.3724 | 19934618.2287 | 42169.6503 | 0.037908 | 241856.2461 | 525871.1937 | 4930.5667 | 10720.5956
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0897 | 0.81656 | 0.012969 | 4 | 186015.2553 | 393557.3931 | 3792.1726 | 8023.1998 | 63.256 | 0 | 79.8823 | 207376.5718 | 5666.9517 | 302990.6473 | 286825.1805 | 0 | 63702.4912 | 0 | 337959.1186 | 879300.3017 | 600140.5237 | 2683961.7865 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9649660.0919 | 20416040.9483 | 56234.1325 | 0.051876 | 186015.2553 | 393557.3931 | 3792.1726 | 8023.1998
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4413 | 1.0496 | 0.017476 | 4 | 146470.1671 | 300486.1168 | 2985.9925 | 6125.8159 | 63.4453 | 0 | 86.0755 | 247590.592 | 6785.1578 | 370327.3738 | 360951.0302 | 0 | 71152.9855 | 0 | 412154.7844 | 1072342.2044 | 731895.5889 | 3273199.717 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10238898.0224 | 21005278.8788 | 74989.4209 | 0.069904 | 146470.1671 | 300486.1168 | 2985.9925 | 6125.8159
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5 | 1.3319 | 0.023162 | 4 | 117921.0116 | 234126.8449 | 2403.9793 | 4772.9924 | 63.5885 | 0 | 90.766 | 292821.2135 | 8042.4093 | 448001.8033 | 450722.8692 | 0 | 78832.2058 | 0 | 498583.9955 | 1297213.2826 | 885374.7204 | 3959592.4996 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10925290.805 | 21691671.6614 | 100000 | 0.092649 | 117921.0116 | 234126.8449 | 2403.9793 | 4772.9924
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.2427 | 1.6618 | 0.030135 | 4 | 97054.3921 | 186372.8864 | 1978.5851 | 3799.4634 | 63.6961 | 0 | 100.7597 | 342152.3454 | 9412.966 | 534718.5245 | 555633.5606 | 0 | 86262.7844 | 0 | 595990.2706 | 1550644.4296 | 1058346.6858 | 4733161.567 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 11698859.8724 | 22465240.7287 | 133352.1432 | 0.12054 | 97054.3921 | 186372.8864 | 1978.5851 | 3799.4634
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5292 | 2.0296 | 0.038356 | 4 | 81687.6015 | 151861.5456 | 1665.3122 | 3095.903 | 63.7763 | 0 | 84.2058 | 393789.151 | 10846.754 | 627421.431 | 672583.9074 | 0 | 92808.0094 | 0 | 701005.2086 | 1823871.7568 | 1244829.9508 | 5567156.169 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 12532854.4744 | 23299235.3308 | 177827.941 | 0.15342 | 81687.6015 | 151861.5456 | 1665.3122 | 3095.903
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.1661 | 2.4218 | 0.047619 | 4 | 70330.6978 | 126854.7518 | 1433.7864 | 2586.1057 | 63.8361 | 0 | 78.9467 | 445853.6022 | 12291.5275 | 722646.435 | 797298.5143 | 0 | 98102.0862 | 0 | 809714.9444 | 2106712.1901 | 1437874.3583 | 6430493.6581 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 13396191.9635 | 24162572.8199 | 237137.3706 | 0.19047 | 70330.6978 | 126854.7518 | 1433.7864 | 2586.1057
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.825 | 2.8157 | 0.057484 | 4 | 61932.0367 | 108755.8139 | 1262.5683 | 2217.1344 | 63.8802 | 0 | 87.1709 | 495650.1617 | 13672.5064 | 815193.3309 | 922514.0498 | 0 | 101691.3787 | 0 | 916001.3567 | 2383247.6323 | 1626615.4799 | 7274585.8962 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 14240284.2016 | 25006665.058 | 316227.766 | 0.22993 | 61932.0367 | 108755.8139 | 1262.5683 | 2217.1344
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.1723 | 3.1879 | 0.06738 | 4 | 55726.8222 | 95673.3182 | 1136.0666 | 1950.43 | 63.912 | 0 | 111.9771 | 540824.6762 | 14924.5284 | 900283.8584 | 1040834.1676 | 0 | 103435.3641 | 0 | 1014118.0119 | 2638527.0427 | 1800848.923 | 8053796.5721 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15019494.8775 | 25785875.7339 | 421696.5034 | 0.26952 | 55726.8222 | 95673.3182 | 1136.0666 | 1950.43
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.9318 | 3.519 | 0.076734 | 4 | 51146.8723 | 86223.7171 | 1042.6982 | 1757.7871 | 63.9341 | 0 | 100.3556 | 579713.1821 | 16001.6772 | 974341.6342 | 1146133.4185 | 0 | 103459.1748 | 0 | 1099663.1439 | 2861097.9285 | 1952758.1259 | 8733168.2851 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15698866.5905 | 26465247.4468 | 562341.3252 | 0.30694 | 51146.8723 | 86223.7171 | 1042.6982 | 1757.7871
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.0197 | 3.8034 | 0.085166 | 4 | 47766.9451 | 79370.9965 | 973.7938 | 1618.0851 | 63.9491 | 0 | 93.8254 | 612231.1837 | 16901.8503 | 1036815.8392 | 1236553.0319 | 0 | 102356.3045 | 0 | 1171894.7018 | 3049029.6253 | 2081025.3706 | 9306807.9073 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 16272506.2127 | 27038887.069 | 749894.2093 | 0.34066 | 47766.9451 | 79370.9965 | 973.7938 | 1618.0851
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.3714 | 4.0364 | 0.092421 | 4 | 45270.2259 | 74393.4371 | 922.8948 | 1516.6108 | 63.9588 | 0 | 100.4671 | 638333.1971 | 17624.0301 | 1087314.496 | 1310661.5669 | 0 | 100465.5306 | 0 | 1230215.5401 | 3200768.4834 | 2184590.2591 | 9769973.1033 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 16735671.4087 | 27502052.265 | 1000000 | 0.36968 | 45270.2259 | 74393.4371 | 922.8948 | 1516.6108
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.0755 | 4.2243 | 0.098479 | 4 | 43422.7318 | 70754.4029 | 885.2311 | 1442.4242 | 63.9651 | 0 | 112.2474 | 659048.8389 | 18196.9157 | 1127610.8423 | 1370433.2514 | 0 | 98322.5448 | 0 | 1276708.8333 | 3321734.4953 | 2267152.0478 | 10139207.7695 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17104906.0749 | 27871286.9312 | 1333521.4322 | 0.39392 | 43422.7318 | 70754.4029 | 885.2311 | 1442.4242
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.195 | 4.3714 | 0.10339 | 4 | 42052.8136 | 68086.4493 | 857.3035 | 1388.0344 | 63.9691 | 0 | 112.9112 | 675080.2009 | 18640.0853 | 1158926.5357 | 1417264.7638 | 0 | 96141.0612 | 0 | 1312760.5323 | 3415533.6208 | 2331171.8784 | 10425518.6784 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17391216.9838 | 28157597.8402 | 1778279.41 | 0.41356 | 42052.8136 | 68086.4493 | 857.3035 | 1388.0344
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.8493 | 4.4862 | 0.1073 | 4 | 41034.9197 | 66118.6017 | 836.5523 | 1347.9171 | 63.9716 | 0 | 106.921 | 687472.8965 | 18982.5584 | 1183212.4014 | 1453808.9854 | 0 | 94165.1911 | 0 | 1340680.3928 | 3488175.3707 | 2380751.3653 | 10647249.1616 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17612947.4669 | 28379328.3233 | 2371373.7057 | 0.42922 | 41034.9197 | 66118.6017 | 836.5523 | 1347.9171
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.123 | 4.5746 | 0.11038 | 4 | 40277.1775 | 64662.882 | 821.1047 | 1318.2403 | 63.9733 | 0 | 118.617 | 696943.4074 | 19244.2099 | 1201817.3041 | 1481936.4465 | 0 | 92452.0297 | 0 | 1362033.4251 | 3543731.5806 | 2418669.6201 | 10816828.0234 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17782526.3288 | 28548907.1852 | 3162277.6602 | 0.4415 | 40277.1775 | 64662.882 | 821.1047 | 1318.2403
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.0996 | 4.6423 | 0.11276 | 4 | 39712.2012 | 63582.1522 | 809.5869 | 1296.2082 | 63.9743 | 0 | 121.8693 | 704164.7139 | 19443.6801 | 1216030.1051 | 1503500.0703 | 0 | 91032.1199 | 0 | 1378326.5688 | 3586122.9984 | 2447602.6338 | 10946222.8902 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17911921.1956 | 28678302.052 | 4216965.0343 | 0.45104 | 39712.2012 | 63582.1522 | 809.5869 | 1296.2082
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.8307 | 4.693 | 0.11458 | 4 | 39290.4041 | 62780.5429 | 800.988 | 1279.8663 | 63.975 | 0 | 121.3081 | 709547.3326 | 19592.3381 | 1226638.9221 | 1519638.5147 | 0 | 89843.4418 | 0 | 1390451.6142 | 3617669.8793 | 2469134.0283 | 11042516.0711 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18008214.3765 | 28774595.2329 | 5623413.2519 | 0.45834 | 39290.4041 | 62780.5429 | 800.988 | 1279.8663
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.3908 | 4.7318 | 0.11598 | 4 | 38975.1755 | 62181.9615 | 794.5617 | 1267.6634 | 63.9755 | 0 | 100.6019 | 713658.3688 | 19705.8638 | 1234750.0729 | 1532001.9778 | 0 | 88918.1969 | 0 | 1399723.4473 | 3641793.2871 | 2485598.7498 | 11116149.9644 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18081848.2698 | 28848229.1262 | 7498942.0933 | 0.46393 | 38975.1755 | 62181.9615 | 794.5617 | 1267.6634
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8124 | 4.7611 | 0.11705 | 4 | 38739.3997 | 61735.5246 | 789.7551 | 1258.5622 | 63.9758 | 0 | 102.4809 | 716744.9908 | 19791.0927 | 1240844.8966 | 1541305.9868 | 0 | 88188.0664 | 0 | 1406681.263 | 3659896.0963 | 2497954.2891 | 11171406.6818 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18137104.9872 | 28903485.8435 | 10000000 | 0.46818 | 38739.3997 | 61735.5246 | 789.7551 | 1258.5622
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4216 | [19 empty] | 100 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7734 | [19 empty] | 133.3521 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.3645 | [19 empty] | 177.8279 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5285 | [19 empty] | 237.1374 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1272 | [19 empty] | 316.2278 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3042 | [19 empty] | 421.6965 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8468 | [19 empty] | 562.3413 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8931 | [19 empty] | 749.8942 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3212 | [19 empty] | 1000 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.451 | [19 empty] | 1333.5214 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4987 | [19 empty] | 1778.2794 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8732 | [19 empty] | 2371.3737 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8383 | [19 empty] | 3162.2777 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.8519 | [19 empty] | 4216.965 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.096181 | 0.0005687 | 4 | 3455500.7971 | 8387345.2516 | 70445.0577 | 170987.3777 | 59.8263 | 0 | 34.3829 | 44785.977 | 1165.224 | 54918.4456 | 56494.1223 | 0 | 27187.8596 | 0 | 71975.1351 | 187264.5374 | 127811.8947 | 571603.1957 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7860627.8287 | 19079665.5436 | 5623.4133 | 0.0022748 | 3455500.7971 | 8387345.2516 | 70445.0577 | 170987.3777
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.12142 | 0.0012084 | 4 | 1644720.1004 | 3965741.9879 | 33529.8439 | 80847.0145 | 60.9247 | 0 | 290.2224 | 53562.5252 | 1410.1255 | 66102.4966 | 64379.3211 | 0 | 27959.8059 | 0 | 83231.567 | 216551.4641 | 147800.824 | 660998.1293 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7950022.7623 | 19169060.4772 | 7498.9421 | 0.0048337 | 1644720.1004 | 3965741.9879 | 33529.8439 | 80847.0145
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8667 | 0.1897 | 0.0021188 | 4 | 966841.5924 | 2290593.4592 | 19710.3736 | 46696.8459 | 62.6448 | 0 | 61.3224 | 74936.2018 | 2010.8626 | 94306.0012 | 85620.3741 | 0 | 35364.0519 | 0 | 113972.6217 | 296533.3828 | 202390.1269 | 905133.6231 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8194158.256 | 19413195.9709 | 10000 | 0.0084752 | 966841.5924 | 2290593.4592 | 19710.3736 | 46696.8459
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 0.26135 | 0.0033618 | 4 | 626698.2733 | 1460997.4036 | 12776.092 | 29784.4082 | 63.588 | 0 | 79.0219 | 94839.9688 | 2572.2336 | 121754.5601 | 107796.6649 | 0 | 40571.9545 | 0 | 143338.799 | 372938.1521 | 254537.9519 | 1138350.2849 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8427374.9179 | 19646412.6328 | 13335.2143 | 0.013447 | 626698.2733 | 1460997.4036 | 12776.092 | 29784.4082
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0586 | 0.35355 | 0.0050389 | 4 | 432149.963 | 988768.558 | 8809.9615 | 20157.3845 | 64.2892 | 0 | 86.8814 | 118095.2151 | 3229.4576 | 154948.6796 | 136286.3838 | 0 | 46317.9643 | 0 | 178962.3031 | 465623.2025 | 317797.4033 | 1421260.6093 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8710285.2422 | 19929322.9571 | 17782.7941 | 0.020156 | 432149.963 | 988768.558 | 8809.9615 | 20157.3845
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.623 | 0.47049 | 0.0072643 | 4 | 311463.5876 | 697564.1669 | 6349.6065 | 14220.7891 | 64.8024 | 0 | 82.2227 | 145023.5511 | 3991.2326 | 194655.1432 | 172420.3083 | 0 | 52563.2767 | 0 | 221774.8697 | 577012.7186 | 393823.0369 | 1761264.1371 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9050288.77 | 20269326.4849 | 23713.7371 | 0.029057 | 311463.5876 | 697564.1669 | 6349.6065 | 14220.7891
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1551 | 0.58459 | 0.010093 | 4 | 231852.6477 | 509754.5481 | 4726.6298 | 10392.036 | 65.086 | 0 | 51.1709 | 169263.4861 | 4676.154 | 231519.8458 | 207723.4654 | 0 | 55468.1015 | 0 | 260773.9106 | 678480.2233 | 463076.6938 | 2070981.8804 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9360006.5134 | 20579044.2283 | 31622.7766 | 0.04037 | 231852.6477 | 509754.5481 | 4726.6298 | 10392.036
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.264 | 0.81894 | 0.014148 | 4 | 176529.3824 | 374771.8706 | 3598.7902 | 7640.2315 | 65.5243 | 0 | 80.5996 | 215209.0931 | 5978.0216 | 303068.9134 | 279899.7582 | 0 | 67976.278 | 0 | 340131.5051 | 884952.4057 | 603998.2008 | 2701214.1759 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9990238.8088 | 21209276.5238 | 42169.6503 | 0.056592 | 176529.3824 | 374771.8706 | 3598.7902 | 7640.2315
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.246 | 1.0429 | 0.019109 | 4 | 138072.4365 | 284848.7781 | 2814.7934 | 5807.0276 | 65.7394 | 0 | 49.7302 | 255344.702 | 7113.6406 | 367663.7796 | 348967.2204 | 0 | 74979.6345 | 0 | 411086.9011 | 1069563.7911 | 729999.2648 | 3264718.9341 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10553743.567 | 21772781.282 | 56234.1325 | 0.076436 | 138072.4365 | 284848.7781 | 2814.7934 | 5807.0276
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3501 | 1.3512 | 0.025604 | 4 | 110375.5917 | 219917.7141 | 2250.1557 | 4483.3201 | 65.9225 | 0 | 94.3801 | 306545.1615 | 8561.6719 | 452235.0397 | 444033.928 | 0 | 85055.0054 | 0 | 505608.0145 | 1315488.3393 | 897847.8222 | 4015374.9826 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 11304399.6155 | 22523437.3304 | 74989.4209 | 0.10242 | 110375.5917 | 219917.7141 | 2250.1557 | 4483.3201
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9787 | 1.6989 | 0.033588 | 4 | 90178.5501 | 173684.5043 | 1838.4117 | 3540.7935 | 66.0517 | 0 | 69.911 | 360208.9697 | 10078.5294 | 543084.2616 | 551228.2752 | 0 | 93708.7083 | 0 | 607740.4102 | 1581215.8828 | 1079212.3307 | 4826477.368 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 12115502.0009 | 23334539.7159 | 100000 | 0.13435 | 90178.5501 | 173684.5043 | 1838.4117 | 3540.7935
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2723 | 2.0965 | 0.043199 | 4 | 75296.3832 | 140222.675 | 1535.0186 | 2858.6289 | 66.1486 | 0 | 104.6838 | 417676.0551 | 11701.8834 | 642517.1956 | 673792.1049 | 0 | 101732.9605 | 0 | 720493.8778 | 1874577.2763 | 1279437.5098 | 5721928.8632 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 13010953.4962 | 24229991.2111 | 133352.1432 | 0.1728 | 75296.3832 | 140222.675 | 1535.0186 | 2858.6289
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0723 | 2.5322 | 0.054306 | 4 | 64272.8054 | 115920.4426 | 1310.2881 | 2363.195 | 66.2214 | 0 | 113.6794 | 477017.5454 | 13376.9447 | 747235.3953 | 808095.292 | 0 | 108598.2011 | 0 | 840186.1176 | 2185991.9322 | 1491984.4113 | 6672485.8396 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 13961510.4726 | 25180548.1875 | 177827.941 | 0.21722 | 64272.8054 | 115920.4426 | 1310.2881 | 2363.195
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.0823 | 2.9837 | 0.066491 | 4 | 56093.4268 | 98276.0625 | 1143.5404 | 2003.4905 | 66.2753 | 0 | 86.8631 | 535379.5701 | 15023.1229 | 852014.2033 | 947273.3784 | 0 | 113709.7445 | 0 | 960726.0075 | 2499611.9994 | 1706036.5515 | 7629774.5775 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 14918799.2104 | 26137836.9254 | 237137.3706 | 0.26596 | 56093.4268 | 98276.0625 | 1143.5404 | 2003.4905
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9212 | 3.4224 | 0.079081 | 4 | 50028.8135 | 85495.7524 | 1019.905 | 1742.9466 | 66.3144 | 0 | 105.4615 | 589606.2111 | 16551.5122 | 950805.4474 | 1082491.9188 | 0 | 116625.6241 | 0 | 1074871.4783 | 2796595.1001 | 1908733.6201 | 8536280.912 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 15825305.545 | 27044343.2599 | 316227.766 | 0.31632 | 50028.8135 | 85495.7524 | 1019.905 | 1742.9466
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.2996 | 3.8264 | 0.09136 | 4 | 45539.4836 | 76239.5788 | 928.384 | 1554.2469 | 66.3416 | 0 | 112.301 | 637733.2766 | 17906.9676 | 1039559.8712 | 1207030.2791 | 0 | 117514.8143 | 0 | 1177700.6314 | 3064135.4634 | 2091335.4155 | 9352916.7192 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 16641941.3521 | 27860979.0671 | 421696.5034 | 0.36544 | 45539.4836 | 76239.5788 | 928.384 | 1554.2469
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.9944 | 4.1789 | 0.10268 | 4 | 42219.9538 | 69534.978 | 860.7109 | 1417.5646 | 66.3598 | 0 | 102.2026 | 678486.7628 | 19053.9072 | 1115468.5649 | 1315704.4835 | 0 | 116703.7282 | 0 | 1265712.8042 | 3293125.0832 | 2247625.5362 | 10051880.8703 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 17340905.5032 | 28559943.2181 | 562341.3252 | 0.41073 | 42219.9538 | 69534.978 | 860.7109 | 1417.5646
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.9307 | 4.4742 | 0.11264 | 4 | 39765.3159 | 64664.8198 | 810.6698 | 1318.2798 | 66.3713 | 0 | 118.8495 | 711838.5887 | 19991.8885 | 1178088.5918 | 1406786.3809 | 0 | 114767.7713 | 0 | 1338274.5563 | 3481915.8776 | 2376479.1327 | 10628142.7878 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 17917167.4208 | 29136205.1357 | 749894.2093 | 0.45057 | 39765.3159 | 64664.8198 | 810.6698 | 1318.2798
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1218 | 4.7135 | 0.12107 | 4 | 37948.274 | 61114.6871 | 773.6269 | 1245.9056 | 66.3783 | 0 | 121.3788 | 738366.6045 | 20737.4952 | 1228210.828 | 1480591.8744 | 0 | 112225.363 | 0 | 1396251.5444 | 3632760.1079 | 2479433.4194 | 11088577.2368 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 18377601.8697 | 29596639.5846 | 1000000 | 0.48428 | 37948.274 | 61114.6871 | 773.6269 | 1245.9056
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.6723 | 4.9045 | 0.12801 | 4 | 36600.9452 | 58511.066 | 746.1598 | 1192.8272 | 66.3824 | 0 | 136.6061 | 759258.1206 | 21324.3676 | 1267877.4361 | 1539555.6708 | 0 | 109590.2891 | 0 | 1442066.2948 | 3751960.6907 | 2560790.2665 | 11452423.1363 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 18741447.7692 | 29960485.4841 | 1333521.4322 | 0.51205 | 36600.9452 | 58511.066 | 746.1598 | 1192.8272
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.6675 | 5.0539 | 0.13359 | 4 | 35600.0264 | 56595.2154 | 725.7547 | 1153.77 | 66.3848 | 0 | 110.6976 | 775415.3999 | 21778.048 | 1298671.7249 | 1585662.4142 | 0 | 107082.9759 | 0 | 1477558.1195 | 3844303.1382 | 2623815.8843 | 11734287.705 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19023312.3379 | 30242350.0529 | 1778279.41 | 0.53436 | 35600.0264 | 56595.2154 | 725.7547 | 1153.77
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1996 | 5.1685 | 0.13798 | 4 | 34855.1095 | 55181.6828 | 710.5686 | 1124.9532 | 66.3861 | 0 | 123.1328 | 787715.5987 | 22123.3026 | 1322182.6986 | 1621056.6432 | 0 | 104818.7414 | 0 | 1504579.824 | 3914608.0703 | 2671800.4451 | 11948885.324 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19237909.957 | 30456947.6719 | 2371373.7057 | 0.55194 | 34855.1095 | 55181.6828 | 710.5686 | 1124.9532
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.3787 | 5.2567 | 0.14142 | 4 | 34299.8361 | 54133.3239 | 699.2486 | 1103.581 | 66.3868 | 0 | 102.9217 | 797119.6214 | 22387.1904 | 1340197.364 | 1648288.1546 | 0 | 102913.5734 | 0 | 1525253.3025 | 3968396.2205 | 2708511.9629 | 12113067.3896 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19402092.0226 | 30621129.7375 | 3162277.6602 | 0.56566 | 34299.8361 | 54133.3239 | 699.2486 | 1103.581
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.2802 | 5.3241 | 0.14407 | 4 | 33885.3761 | 53353.8378 | 690.7992 | 1087.6901 | 66.3871 | 0 | 114.6281 | 804273.3591 | 22587.8885 | 1353924.2224 | 1669102.614 | 0 | 101357.4062 | 0 | 1540985.7412 | 4009328.7989 | 2736449.2887 | 12238009.3191 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19527033.952 | 30746071.667 | 4216965.0343 | 0.57627 | 33885.3761 | 53353.8378 | 690.7992 | 1087.6901
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9723 | 5.3758 | 0.14611 | 4 | 33575.6882 | 52772.1531 | 684.4858 | 1075.8317 | 66.3873 | 0 | 126.0338 | 809745.3264 | 22741.3783 | 1364437.3932 | 1685081.5895 | 0 | 100134.5876 | 0 | 1553034.7072 | 4040677.737 | 2757845.5832 | 12333698.3024 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19622722.9354 | 30841760.6503 | 5623413.2519 | 0.58443 | 33575.6882 | 52772.1531 | 684.4858 | 1075.8317
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.4936 | 5.4148 | 0.14766 | 4 | 33344.0913 | 52338.6378 | 679.7644 | 1066.9939 | 66.3874 | 0 | 100.0275 | 813854.1401 | 22856.6163 | 1372339.1747 | 1697112.8537 | 0 | 99160.8068 | 0 | 1562076.2007 | 4064201.8483 | 2773901.2725 | 12405502.913 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19694527.5459 | 30913565.2609 | 7498942.0933 | 0.59065 | 33344.0913 | 52338.6378 | 679.7644 | 1066.9939
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.8855 | 5.444 | 0.14884 | 4 | 33170.7798 | 52015.0804 | 676.2312 | 1060.3978 | 66.3874 | 0 | 118.2786 | 816937.0002 | 22943.0713 | 1378272.1984 | 1706158.4854 | 0 | 98396.9604 | 0 | 1568856.0091 | 4081841.519 | 2785940.7102 | 12459345.954 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19748370.5869 | 30967408.3018 | 10000000 | 0.59535 | 33170.7798 | 52015.0804 | 676.2312 | 1060.3978
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.4845 | [19 empty] | 100 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7174 | [19 empty] | 133.3521 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2885 | [19 empty] | 177.8279 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0822 | [19 empty] | 237.1374 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0334 | [19 empty] | 316.2278 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1376 | [19 empty] | 421.6965 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1684 | [19 empty] | 562.3413 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5295 | [19 empty] | 749.8942 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1954 | [19 empty] | 1000 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5846 | [19 empty] | 1333.5214 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.2595 | [19 empty] | 1778.2794 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9877 | [19 empty] | 2371.3737 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.1476 | [19 empty] | 3162.2777 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10236 | 0.00041753 | 4 | 4924505.4202 | 11918035.7959 | 100392.7039 | 242965.28 | 61.6313 | 0 | 35.451 | 48241.545 | 1273.8248 | 57625.988 | 57737.379 | 0 | 30845.6302 | 0 | 76332.5031 | 198601.5152 | 135549.615 | 606208.0002 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8224419.0516 | 19904317.7523 | 4216.965 | 0.0016701 | 4924505.4202 | 11918035.7959 | 100392.7039 | 242965.28
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10237 | 0.0010534 | 4 | 1948608.6999 | 4720545.9028 | 39725.024 | 96234.7132 | 61.6318 | 0 | 219.6162 | 48242.4713 | 1273.8543 | 57626.6929 | 57737.7 | 0 | 26415.0891 | 0 | 74605.365 | 194107.856 | 132482.6003 | 592491.6289 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8210702.6803 | 19890601.381 | 5623.4133 | 0.0042136 | 1948608.6999 | 4720545.9028 | 39725.024 | 96234.7132
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.13244 | 0.0018609 | 4 | 1117364.2488 | 2686495.7945 | 22778.9816 | 54767.8505 | 62.938 | 0 | 291.7926 | 58826.7023 | 1574.6337 | 70727.0702 | 66877.0496 | 0 | 27658.3986 | 0 | 88008.9032 | 228981.113 | 156284.3147 | 698938.1853 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8317149.2367 | 19997047.9374 | 7498.9421 | 0.0074435 | 1117364.2488 | 2686495.7945 | 22778.9816 | 54767.8505
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4781 | 0.25203 | 0.0033791 | 4 | 646300.3527 | 1510425.2462 | 13175.7069 | 30792.0616 | 65.4199 | 0 | 75.7808 | 95131.2506 | 2613.9546 | 118068.7137 | 102910.6112 | 0 | 42070.4957 | 0 | 140710.0601 | 366098.7127 | 249869.894 | 1117473.6926 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8735684.7439 | 20415583.4446 | 10000 | 0.013516 | 646300.3527 | 1510425.2462 | 13175.7069 | 30792.0616
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6159 | 0.34352 | 0.0051615 | 4 | 436855.7879 | 1002579.4226 | 8905.8961 | 20438.9376 | 66.268 | 0 | 86.7727 | 119262.2354 | 3307.7419 | 151151.4721 | 130378.1422 | 0 | 48265.4484 | 0 | 176422.3656 | 459014.8062 | 313287.037 | 1401089.249 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9019300.3003 | 20699199.001 | 13335.2143 | 0.020646 | 436855.7879 | 1002579.4226 | 8905.8961 | 20438.9376
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0527 | 0.459 | 0.00754 | 4 | 310258.6681 | 697522.5161 | 6325.0426 | 14219.94 | 66.8902 | 0 | 94.0305 | 147035.8256 | 4107.4298 | 190479.8426 | 165007.2803 | 0 | 54901.6965 | 0 | 218997.5092 | 569786.5963 | 388891.0599 | 1739207.2402 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9357418.2916 | 21037316.9923 | 17782.7941 | 0.03016 | 310258.6681 | 697522.5161 | 6325.0426 | 14219.94
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7971 | 0.59881 | 0.010627 | 4 | 229260.184 | 504030.6982 | 4673.7789 | 10275.3475 | 67.3138 | 0 | 87.2087 | 177832.8132 | 4993.6229 | 235537.478 | 206980.09 | 0 | 61439.3471 | 0 | 267845.507 | 696879.0665 | 475634.2823 | 2127142.2069 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9745353.2583 | 21425251.959 | 23713.7371 | 0.042508 | 229260.184 | 504030.6982 | 4673.7789 | 10275.3475
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3186 | 0.80267 | 0.014908 | 4 | 172535.3187 | 368395.8291 | 3517.3658 | 7510.2473 | 67.7466 | 0 | 81.1308 | 219244.0396 | 6188.15 | 297637.6273 | 267965.6092 | 0 | 71250.6844 | 0 | 336291.5831 | 874961.7163 | 597179.35 | 2670718.7598 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10288929.8112 | 21968828.5119 | 31622.7766 | 0.059634 | 172535.3187 | 368395.8291 | 3517.3658 | 7510.2473
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3077 | 1.0436 | 0.020361 | 4 | 133825.7286 | 277238.4284 | 2728.2185 | 5651.8804 | 68.0219 | 0 | 69.0323 | 264109.0678 | 7480.4077 | 367090.2754 | 340117.4475 | 0 | 80496.1309 | 0 | 413124.3984 | 1074864.9413 | 733617.4087 | 3280900.0777 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10899111.129 | 22579009.8297 | 42169.6503 | 0.081443 | 133825.7286 | 277238.4284 | 2728.2185 | 5651.8804
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9734 | 1.3392 | 0.027357 | 4 | 106154.3416 | 212891.6319 | 2164.0998 | 4340.0839 | 68.2287 | 0 | 96.1993 | 315041.4689 | 8946.5182 | 448066.4751 | 428624.7416 | 0 | 90108.7235 | 0 | 503407.2916 | 1309762.5098 | 893939.8259 | 3997897.5546 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 11616108.606 | 23296007.3067 | 56234.1325 | 0.10943 | 106154.3416 | 212891.6319 | 2164.0998 | 4340.0839
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.4124 | 1.6972 | 0.036182 | 4 | 86029.9364 | 166733.1984 | 1753.8366 | 3399.0818 | 68.3857 | 0 | 73.158 | 372370.0159 | 10595.5794 | 541498.6201 | 535810.3499 | 0 | 100010.4792 | 0 | 608511.1674 | 1583221.2347 | 1080581.0246 | 4832598.4712 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 12450809.5225 | 24130708.2232 | 74989.4209 | 0.14473 | 86029.9364 | 166733.1984 | 1753.8366 | 3399.0818
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.741 | 2.0464 | 0.046464 | 4 | 71166.3405 | 134010.2777 | 1450.8221 | 2731.9808 | 68.4875 | 0 | 129.0305 | 424857.2402 | 12104.2635 | 628871.6759 | 640341.9869 | 0 | 104607.4758 | 0 | 706205.2305 | 1837401.1471 | 1254064.0377 | 5608453.0574 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 13226664.1088 | 24906562.8095 | 100000 | 0.18586 | 71166.3405 | 134010.2777 | 1450.8221 | 2731.9808
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.7 | 2.6886 | 0.060859 | 4 | 60160.1911 | 108139.8365 | 1226.4469 | 2204.5768 | 68.6083 | 0 | 67.6352 | 514897.9506 | 14689.9229 | 782246.4511 | 832565.8835 | 0 | 124336.2349 | 0 | 884807.2128 | 2302086.8687 | 1571221.5911 | 7026852.1156 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 14645063.1669 | 26324961.8677 | 133352.1432 | 0.24343 | 60160.1911 | 108139.8365 | 1226.4469 | 2204.5768
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6667 | 3.0895 | 0.074284 | 4 | 52070.8663 | 91378.9718 | 1061.535 | 1862.8839 | 68.6593 | 0 | 83.9839 | 567816.8788 | 16208.1484 | 874190.6978 | 952533.5649 | 0 | 125038.5798 | 0 | 988957.2692 | 2573063.9514 | 1756169.018 | 7853978.1084 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 15472189.1598 | 27152087.8605 | 177827.941 | 0.29714 | 52070.8663 | 91378.9718 | 1061.535 | 1862.8839
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.9466 | 3.5963 | 0.089741 | 4 | 45994.2556 | 78532.1778 | 937.6551 | 1600.9847 | 68.708 | 0 | 97.5325 | 631896.2906 | 18045.1303 | 987113.2866 | 1104225.5376 | 0 | 129653.1403 | 0 | 1119664.0203 | 2913136.1061 | 1988275.2514 | 8892008.763 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 16510219.8144 | 28190118.5151 | 237137.3706 | 0.35896 | 45994.2556 | 78532.1778 | 937.6551 | 1600.9847
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.8929 | 4.0762 | 0.10528 | 4 | 41481.357 | 69215.9274 | 845.6536 | 1411.0603 | 68.7421 | 0 | 94.615 | 690116.7969 | 19712.6819 | 1091106.2943 | 1247841.7079 | 0 | 131747.1116 | 0 | 1240404.5911 | 3227278.3041 | 2202683.7565 | 9850891.2442 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 17469102.2956 | 29149000.9963 | 316227.766 | 0.42113 | 41481.357 | 69215.9274 | 845.6536 | 1411.0603
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.2307 | 4.5067 | 0.12004 | 4 | 38136.2266 | 62461.4006 | 777.4586 | 1273.3601 | 68.7647 | 0 | 106.8236 | 740621.2218 | 21157.9448 | 1182332.7928 | 1376717.2234 | 0 | 131635.6292 | 0 | 1346461.2767 | 3503216.0447 | 2391016.9344 | 10693159.0678 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 18311370.1192 | 29991268.8199 | 421696.5034 | 0.48016 | 38136.2266 | 62461.4006 | 777.4586 | 1273.3601
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8003 | 4.8749 | 0.13334 | 4 | 35659.053 | 57558.0772 | 726.958 | 1173.3993 | 68.7787 | 0 | 104.4774 | 782673.848 | 22360.3087 | 1258988.2162 | 1486990.9516 | 0 | 129871.2523 | 0 | 1435544.985 | 3734993.5801 | 2549209.8649 | 11400633.0068 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19018844.0582 | 30698742.7589 | 562341.3252 | 0.53335 | 35659.053 | 57558.0772 | 726.958 | 1173.3993
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5787 | 5.1791 | 0.14483 | 4 | 33824.1319 | 53986.1147 | 689.5507 | 1100.58 | 68.7868 | 0 | 94.7435 | 816685.7516 | 23332.0006 | 1321439.9271 | 1578119.4617 | 0 | 127142.9099 | 0 | 1508020.8198 | 3923560.8356 | 2677910.8914 | 11976212.5977 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19594423.6491 | 31274322.3498 | 749894.2093 | 0.5793 | 33824.1319 | 53986.1147 | 689.5507 | 1100.58
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.6138 | 5.4231 | 0.15441 | 4 | 32463.36 | 51374.1447 | 661.8095 | 1047.3314 | 68.7911 | 0 | 125.3607 | 843537.0332 | 24098.5855 | 1371026.8405 | 1651276.2497 | 0 | 124000.2022 | 0 | 1565436.1754 | 4072943.8132 | 2779867.8431 | 12432186.7428 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20050397.7941 | 31730296.4948 | 1000000 | 0.61763 | 32463.36 | 51374.1447 | 661.8095 | 1047.3314
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.0085 | 5.6156 | 0.1622 | 4 | 31452.5926 | 49455.2066 | 641.2036 | 1008.2113 | 68.7932 | 0 | 133.0266 | 864440.893 | 24695.0267 | 1409802.6426 | 1708966.5299 | 0 | 120877.3727 | 0 | 1610225.1613 | 4189475.5671 | 2859403.1597 | 12787886.353 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20406097.4043 | 32085996.1051 | 1333521.4322 | 0.64879 | 31452.5926 | 49455.2066 | 641.2036 | 1008.2113
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8797 | 5.7658 | 0.16841 | 4 | 30700.5336 | 48038.602 | 625.8719 | 979.3319 | 68.794 | 0 | 131.8846 | 880608.215 | 25156.1015 | 1439895.432 | 1754026.2145 | 0 | 118049.5026 | 0 | 1644916.8316 | 4279736.177 | 2921007.8806 | 13063396.3549 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20681607.4062 | 32361506.1069 | 1778279.41 | 0.67366 | 30700.5336 | 48038.602 | 625.8719 | 979.3319
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.307 | 5.8803 | 0.17327 | 4 | 30140.0883 | 46991.8748 | 614.4465 | 957.9929 | 68.7942 | 0 | 118.3892 | 892843.5106 | 25504.9062 | 1462729.0989 | 1788382.3887 | 0 | 115546.3034 | 0 | 1671152.421 | 4347995.799 | 2967596.4752 | 13271750.9029 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20889961.9543 | 32569860.655 | 2371373.7057 | 0.6931 | 30140.0883 | 46991.8748 | 614.4465 | 957.9929
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.4077 | 5.9686 | 0.17706 | 4 | 29721.8723 | 46213.6147 | 605.9206 | 942.127 | 68.7941 | 0 | 120.6472 | 902222.8249 | 25772.2126 | 1480267.6999 | 1814867.9018 | 0 | 113493.3179 | 0 | 1691283.3432 | 4400372.3292 | 3003344.5333 | 13431624.1627 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21049835.2141 | 32729733.9148 | 3162277.6602 | 0.70823 | 29721.8723 | 46213.6147 | 605.9206 | 942.127
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2554 | 6.0365 | 0.17998 | 4 | 29409.4446 | 45633.231 | 599.5513 | 930.2951 | 68.7938 | 0 | 139.5409 | 909414.1324 | 25977.1139 | 1493735.3491 | 1835262.2834 | 0 | 111863.6291 | 0 | 1706738.4781 | 4440583.4197 | 3030789.4288 | 13554363.8345 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21172574.8858 | 32852473.5865 | 4216965.0343 | 0.71992 | 29409.4446 | 45633.231 | 599.5513 | 930.2951
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.8887 | 6.0873 | 0.1822 | 4 | 29175.8385 | 45201.7249 | 594.7889 | 921.4983 | 68.7935 | 0 | 115.6514 | 914767.8226 | 26129.6287 | 1503773.0987 | 1850494.4766 | 0 | 110532.8811 | 0 | 1718222.184 | 4470461.6669 | 3051181.9465 | 13645563.705 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21263774.7563 | 32943673.457 | 5623413.2519 | 0.72881 | 29175.8385 | 45201.7249 | 594.7889 | 921.4983
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.3614 | 6.1251 | 0.18389 | 4 | 29001.047 | 44880.3115 | 591.2256 | 914.9459 | 68.7932 | 0 | 130.7441 | 918753.5185 | 26243.157 | 1511252.3582 | 1861861.7762 | 0 | 109468.7977 | 0 | 1726756.0469 | 4492665.0278 | 3066336.1965 | 13713336.8788 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21331547.9301 | 33011446.6308 | 7498942.0933 | 0.73554 | 29001.047 | 44880.3115 | 591.2256 | 914.9459
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.7272 | 6.1544 | 0.18517 | 4 | 28870.1927 | 44638.995 | 588.5579 | 910.0263 | 68.793 | 0 | 114.0245 | 921832.2437 | 26330.8421 | 1517033.397 | 1870658.3121 | 0 | 108677.4215 | 0 | 1733367.5644 | 4509866.84 | 3078076.7868 | 13765843.4076 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21384054.459 | 33063953.1597 | 10000000 | 0.7407 | 28870.1927 | 44638.995 | 588.5579 | 910.0263
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.531 | [19 empty] | 100 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4172 | [19 empty] | 133.3521 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.875 | [19 empty] | 177.8279 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6566 | [19 empty] | 237.1374 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1637 | [19 empty] | 316.2278 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1317 | [19 empty] | 421.6965 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4133 | [19 empty] | 562.3413 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9823 | [19 empty] | 749.8942 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9462 | [19 empty] | 1000 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.3509 | [19 empty] | 1333.5214 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7602 | [19 empty] | 1778.2794 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.1433 | [19 empty] | 2371.3737 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10863 | 0.00011787 | 4 | 18231639.7202 | 43998620.0506 | 371676.6358 | 896971.3823 | 63.4098 | 0 | 34.2414 | 51731.8972 | 1385.6362 | 60330.0513 | 58958.3785 | 0 | 35146.3384 | 0 | 80945.3977 | 210603.3205 | 143741.0937 | 642842.1137 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8596099.6743 | 20745063.488 | 3162.2777 | 0.00047149 | 18231639.7202 | 43998620.0506 | 371676.6358 | 896971.3823
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10863 | 0.00094206 | 4 | 2277000.8657 | 5501041.6211 | 46419.7425 | 112146.1742 | 63.4104 | 0 | 35.4732 | 51733.1825 | 1385.6776 | 60331.0609 | 58958.8306 | 0 | 30038.7792 | 0 | 78954.537 | 205423.5096 | 140205.7663 | 627031.3438 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8580288.9044 | 20729252.7181 | 4216.965 | 0.0037682 | 2277000.8657 | 5501041.6211 | 46419.7425 | 112146.1742
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10863 | 0.0015601 | 4 | 1372725.3535 | 3319495.7421 | 27984.8631 | 67672.4107 | 63.4109 | 0 | 218.2312 | 51734.1477 | 1385.7087 | 60331.8192 | 58959.1702 | 0 | 25614.91 | 0 | 77230.0447 | 200936.7344 | 137143.45 | 613335.9849 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8566593.5455 | 20715557.3593 | 5623.4133 | 0.0062406 | 1372725.3535 | 3319495.7421 | 27984.8631 | 67672.4107
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1102 | 0.23725 | 0.0032463 | 4 | 695522.1468 | 1631129.0579 | 14179.1597 | 33252.7721 | 67.0859 | 0 | 65.5339 | 93501.4915 | 2598.959 | 112326.7216 | 96745.0996 | 0 | 42935.4378 | 0 | 135762.0067 | 353224.8929 | 241083.2474 | 1078177.8566 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9031435.4173 | 21180399.231 | 7498.9421 | 0.012985 | 695522.1468 | 1631129.0579 | 14179.1597 | 33252.7721
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.136 | 0.32523 | 0.0050849 | 4 | 457642.5118 | 1054943.3788 | 9329.6616 | 21506.4477 | 68.1144 | 0 | 83.0051 | 117936.8207 | 3313.921 | 144432.3836 | 122459.1934 | 0 | 49370.1492 | 0 | 170629.8625 | 443943.9013 | 303000.8348 | 1355087.0665 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9308344.6272 | 21457308.4409 | 10000 | 0.02034 | 457642.5118 | 1054943.3788 | 9329.6616 | 21506.4477
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4607 | 0.4392 | 0.0075613 | 4 | 318944.7501 | 720625.8988 | 6502.1201 | 14690.9337 | 68.8862 | 0 | 90.8162 | 146700.879 | 4156.6966 | 183544.3099 | 155709.4239 | 0 | 56605.201 | 0 | 213219.439 | 554753.243 | 378630.4874 | 1693319.6798 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9646577.2405 | 21795541.0542 | 13335.2143 | 0.030245 | 318944.7501 | 720625.8988 | 6502.1201 | 14690.9337
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1003 | 0.58014 | 0.010822 | 4 | 231986.1244 | 512646.7228 | 4729.3509 | 10450.9969 | 69.4342 | 0 | 79.3331 | 179198.5063 | 5108.9143 | 229202.6955 | 196824.3335 | 0 | 64047.7923 | 0 | 263009.0743 | 684295.6608 | 467045.8494 | 2088732.8265 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10041990.3871 | 22190954.2008 | 17782.7941 | 0.043287 | 231986.1244 | 512646.7228 | 4729.3509 | 10450.9969
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4413 | 0.78237 | 0.015279 | 4 | 173194.4195 | 371974.3196 | 3530.8025 | 7583.1996 | 69.93 | 0 | 102.5613 | 221964.1718 | 6363.6044 | 291022.6918 | 255689.3588 | 0 | 74739.2666 | 0 | 331413.8464 | 862270.8461 | 588517.5704 | 2631981.3564 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10585238.9171 | 22734202.7308 | 23713.7371 | 0.061118 | 173194.4195 | 371974.3196 | 3530.8025 | 7583.1996
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0897 | 1.0109 | 0.020983 | 4 | 133025.2435 | 277769.7633 | 2711.8995 | 5662.7123 | 70.2507 | 0 | 81.1973 | 266342.4758 | 7664.5231 | 357145.5651 | 322235.667 | 0 | 83679.6935 | 0 | 404456.4905 | 1052312.823 | 718225.1245 | 3212062.3626 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11165319.9232 | 23314283.7369 | 31622.7766 | 0.083934 | 133025.2435 | 277769.7633 | 2711.8995 | 5662.7123
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4996 | 1.3052 | 0.028403 | 4 | 104586.5033 | 211519.279 | 2132.1373 | 4312.1066 | 70.5029 | 0 | 100.2019 | 319207.975 | 9213.2131 | 438049.9222 | 407918.3492 | 0 | 94198.6139 | 0 | 494749.3486 | 1287236.318 | 878565.2371 | 3929138.9769 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11882396.5376 | 24031360.3513 | 42169.6503 | 0.11361 | 104586.5033 | 211519.279 | 2132.1373 | 4312.1066
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6802 | 1.6661 | 0.037866 | 4 | 84019.7368 | 164229.8977 | 1712.856 | 3348.0486 | 70.6945 | 0 | 89.4842 | 379328.2758 | 10973.0345 | 532437.1566 | 512974.6632 | 0 | 105239.2941 | 0 | 600971.4454 | 1563604.4248 | 1067192.1488 | 4772720.4432 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 12725978.0039 | 24874941.8176 | 56234.1325 | 0.15146 | 84019.7368 | 164229.8977 | 1712.856 | 3348.0486
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6519 | 2.0954 | 0.049656 | 4 | 68929.4845 | 130095.5225 | 1405.2208 | 2652.1732 | 70.839 | 0 | 82.9187 | 445939.6311 | 12921.0917 | 639532.9467 | 637924.7175 | 0 | 116194.7483 | 0 | 722480.1228 | 1879745.0784 | 1282964.6409 | 5737702.9775 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 13690960.5382 | 25839924.3519 | 74989.4209 | 0.19862 | 68929.4845 | 130095.5225 | 1405.2208 | 2652.1732
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.377 | 2.5899 | 0.06391 | 4 | 57749.6027 | 105273.3062 | 1177.3038 | 2146.1387 | 70.9481 | 0 | 104.899 | 517774.7135 | 15019.8831 | 757574.9725 | 781823.5 | 0 | 126482.5701 | 0 | 857483.4993 | 2230996.1711 | 1522700.7292 | 6809856.0388 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 14763113.5994 | 26912077.4132 | 100000 | 0.25564 | 57749.6027 | 105273.3062 | 1177.3038 | 2146.1387
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6936 | 3.1356 | 0.080471 | 4 | 49421.7952 | 87165.1809 | 1007.5301 | 1776.9801 | 71.0302 | 0 | 90.3384 | 592445.4856 | 17199.3613 | 882713.383 | 940609.5407 | 0 | 135369.1433 | 0 | 1001651.3965 | 2606091.4666 | 1778710.9758 | 7954790.7529 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 15908048.3135 | 28057012.1272 | 133352.1432 | 0.32188 | 49421.7952 | 87165.1809 | 1007.5301 | 1776.9801
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.2829 | 3.7049 | 0.098751 | 4 | 43208.3728 | 73965.0034 | 880.8611 | 1507.8766 | 71.0911 | 0 | 107.3526 | 666332.4565 | 19353.8172 | 1008700.9743 | 1106266.3815 | 0 | 142012.3211 | 0 | 1147639.7207 | 2985923.1401 | 2037953.8977 | 9114182.7091 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 17067440.2697 | 29216404.0834 | 177827.941 | 0.395 | 43208.3728 | 73965.0034 | 880.8611 | 1507.8766
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.7332 | 4.2621 | 0.11776 | 4 | 38578.0714 | 64369.4486 | 786.4662 | 1312.2583 | 71.1343 | 0 | 124.3317 | 735437.9555 | 21366.8262 | 1128300.7472 | 1268412.2893 | 0 | 145807.2848 | 0 | 1286736.7902 | 3347825.1821 | 2284959.4777 | 10218846.553 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 18172104.1136 | 30321067.9273 | 237137.3706 | 0.47105 | 38578.0714 | 64369.4486 | 786.4662 | 1312.2583
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.7165 | 4.7787 | 0.13642 | 4 | 35135.7346 | 57399.8395 | 716.2895 | 1170.1734 | 71.1632 | 0 | 113.6337 | 797124.0257 | 23161.8516 | 1236407.0534 | 1418768.9698 | 0 | 146918.8538 | 0 | 1412728.4942 | 3675629.7513 | 2508692.8319 | 11219431.8317 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 19172689.3923 | 31321653.206 | 316227.766 | 0.54567 | 35135.7346 | 57399.8395 | 716.2895 | 1170.1734
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.9512 | 5.2302 | 0.15369 | 4 | 32581.4609 | 52343.9308 | 664.2172 | 1067.1018 | 71.181 | 0 | 114.6055 | 849410.7286 | 24681.7825 | 1328995.851 | 1550242.1553 | 0 | 145662.9588 | 0 | 1520607.4557 | 3956308.6803 | 2700261.9683 | 12076171.5806 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 20029429.1412 | 32178392.9549 | 421696.5034 | 0.61475 | 32581.4609 | 52343.9308 | 664.2172 | 1067.1018
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3628 | 5.6103 | 0.16895 | 4 | 30687.4181 | 48664.8228 | 625.6045 | 992.0982 | 71.1908 | 0 | 125.0145 | 892365.6708 | 25929.2161 | 1405701.1828 | 1660965.5879 | 0 | 142894.0072 | 0 | 1609863.7092 | 4188535.143 | 2858761.3009 | 12785015.8179 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 20738273.3785 | 32887237.1922 | 562341.3252 | 0.67579 | 30687.4181 | 48664.8228 | 625.6045 | 992.0982
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.9755 | 5.9212 | 0.18193 | 4 | 29282.2637 | 45976.3857 | 596.9586 | 937.2908 | 71.1956 | 0 | 129.3142 | 926836.2063 | 26929.3682 | 1467669.3416 | 1751571.7369 | 0 | 139390.5906 | 0 | 1681834.925 | 4375789.4831 | 2986566.2357 | 13356587.8874 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21309845.448 | 33458809.2617 | 749894.2093 | 0.72774 | 29282.2637 | 45976.3857 | 596.9586 | 937.2908
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8527 | 6.1685 | 0.19264 | 4 | 28238.5457 | 44005.3042 | 575.6809 | 897.1076 | 71.1974 | 0 | 129.9617 | 953857.333 | 27712.7787 | 1516501.7604 | 1823682.0401 | 0 | 135663.8911 | 0 | 1738392.9433 | 4522941.8449 | 3087000.7463 | 13805753.3378 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21759010.8984 | 33907974.7121 | 1000000 | 0.77054 | 28238.5457 | 44005.3042 | 575.6809 | 897.1076
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1176 | 6.3629 | 0.20127 | 4 | 27462.1296 | 42552.717 | 559.8527 | 867.4947 | 71.1975 | 0 | 133.0991 | 974869.5939 | 28321.5908 | 1554630.2928 | 1880413.8048 | 0 | 132152.86 | 0 | 1782451.3755 | 4637572.848 | 3165238.7613 | 14155651.1271 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22108908.6877 | 34257872.5014 | 1333521.4322 | 0.80507 | 27462.1296 | 42552.717 | 559.8527 | 867.4947
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.8498 | 6.5115 | 0.20806 | 4 | 26883.6879 | 41481.5474 | 548.0603 | 845.6575 | 71.1969 | 0 | 113.3025 | 990789.4792 | 28782.6207 | 1583608.7177 | 1923778.7255 | 0 | 128939.0973 | 0 | 1815800.4697 | 4724340.3503 | 3224459.3646 | 14420498.8249 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22373756.3855 | 34522720.1992 | 1778279.41 | 0.83224 | 26883.6879 | 41481.5474 | 548.0603 | 845.6575
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.1922 | 6.6266 | 0.21338 | 4 | 26452.1568 | 40685.8966 | 539.263 | 829.437 | 71.196 | 0 | 128.6672 | 1003040.2486 | 29137.2527 | 1605961.4728 | 1957373.3755 | 0 | 126259.8687 | 0 | 1841491.1651 | 4791182.2699 | 3270080.3481 | 14624526.0013 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22577783.562 | 34726747.3757 | 2371373.7057 | 0.85353 | 26452.1568 | 40685.8966 | 539.263 | 829.437
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.223 | 6.7149 | 0.21751 | 4 | 26129.8564 | 40093.7518 | 532.6925 | 817.3654 | 71.1951 | 0 | 127.5946 | 1012395.6155 | 29407.984 | 1623062.3927 | 1983159.399 | 0 | 124079.4504 | 0 | 1861120.8882 | 4842254.7828 | 3304938.3877 | 14780418.9003 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22733676.461 | 34882640.2747 | 3162277.6602 | 0.87003 | 26129.8564 | 40093.7518 | 532.6925 | 817.3654
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79 | 6.7815 | 0.22066 | 4 | 25888.9148 | 39653.2783 | 527.7805 | 808.3857 | 71.1943 | 0 | 132.7457 | 1019418.9535 | 29611.18 | 1635918.2572 | 2002592.4108 | 0 | 122303.5436 | 0 | 1875839.2946 | 4880549.057 | 3331075.0167 | 14897307.7135 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22850565.2741 | 34999529.0878 | 4216965.0343 | 0.88264 | 25888.9148 | 39653.2783 | 527.7805 | 808.3857
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.5823 | 6.8313 | 0.22305 | 4 | 25708.6624 | 39325.2373 | 524.1059 | 801.6982 | 71.1936 | 0 | 120.2982 | 1024666.1869 | 29762.9625 | 1645532.9775 | 2017152.9082 | 0 | 120878.7651 | 0 | 1886817.5821 | 4909112.309 | 3350570.0231 | 14984493.7143 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22937751.2749 | 35086715.0886 | 5623413.2519 | 0.89222 | 25708.6624 | 39325.2373 | 524.1059 | 801.6982
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.0427 | 6.8707 | 0.22491 | 4 | 25573.7355 | 39078.1272 | 521.3552 | 796.6605 | 71.193 | 0 | 127.5728 | 1028805.7028 | 29882.6858 | 1653123.9681 | 2028664.8386 | 0 | 119847.1314 | 0 | 1895526.4874 | 4931771.0943 | 3366035.1096 | 15053657.0179 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23006914.5786 | 35155878.3923 | 7498942.0933 | 0.89963 | 25573.7355 | 39078.1272 | 521.3552 | 796.6605
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.3787 | 6.8995 | 0.22629 | 4 | 25472.6926 | 38894.4651 | 519.2953 | 792.9163 | 71.1925 | 0 | 112.3778 | 1031821.0065 | 29969.885 | 1658656.7238 | 2037064.3739 | 0 | 119007.5835 | 0 | 1901842.6334 | 4948204.4104 | 3377251.1855 | 15103817.802 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23057075.3626 | 35206039.1763 | 10000000 | 0.90517 | 25472.6926 | 38894.4651 | 519.2953 | 792.9163
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.5745 | [19 empty] | 100 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2855 | [19 empty] | 133.3521 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3058 | [19 empty] | 177.8279 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9328 | [19 empty] | 237.1374 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0728 | [19 empty] | 316.2278 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7797 | [19 empty] | 421.6965 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1504 | [19 empty] | 562.3413 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3345 | [19 empty] | 749.8942 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4786 | [19 empty] | 1000 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.087 | [19 empty] | 1333.5214 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.683 | [19 empty] | 1778.2794 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.3314 | [19 empty] | 2371.3737 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.11498 | 0.00068558 | 4 | 3266487.6583 | 7870707.8846 | 66591.7692 | 160455.0261 | 65.163 | 0 | 37.4315 | 55256.0925 | 1500.6093 | 63034.2494 | 60161.8161 | 0 | 34295.6396 | 0 | 83556.8787 | 217397.8585 | 148378.5055 | 663581.6496 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 8957745.8104 | 21583978.8643 | 3162.2777 | 0.0027423 | 3266487.6583 | 7870707.8846 | 66591.7692 | 160455.0261
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.15116 | 0.0016381 | 4 | 1386681.6441 | 3313646.2226 | 28269.3809 | 67553.1603 | 66.7541 | 0 | 303.7355 | 68241.2562 | 1881.987 | 78343.8395 | 70568.0794 | 0 | 36649.971 | 0 | 99717.2019 | 259443.7045 | 177075.6594 | 791921.6989 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9086085.8596 | 21712318.9135 | 4216.965 | 0.0065524 | 1386681.6441 | 3313646.2226 | 28269.3809 | 67553.1603
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7398 | 0.21816 | 0.0029747 | 4 | 783064.652 | 1844198.567 | 15963.8321 | 37596.4823 | 68.5408 | 0 | 82.1796 | 90082.0844 | 2528.5164 | 104895.7021 | 89730.9204 | 0 | 43176.465 | 0 | 128861.3384 | 335270.7695 | 228829.1893 | 1023374.9854 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9317539.1462 | 21943772.2 | 5623.4133 | 0.011899 | 783064.652 | 1844198.567 | 15963.8321 | 37596.4823
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.30188 | 0.0048228 | 4 | 496925.7576 | 1151438.7315 | 10130.5037 | 23473.636 | 69.8028 | 0 | 77.5037 | 114638.5161 | 3258.7884 | 135866.5138 | 113577.9807 | 0 | 49817.5508 | 0 | 162692.1464 | 423291.5923 | 288905.2095 | 1292048.298 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9586212.4588 | 22212445.5127 | 7498.9421 | 0.019291 | 496925.7576 | 1151438.7315 | 10130.5037 | 23473.636
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8593 | 0.41217 | 0.0073345 | 4 | 338105.2594 | 768476.0546 | 6892.733 | 15666.4238 | 70.7625 | 0 | 88.7595 | 143970.6176 | 4133.1641 | 174153.1972 | 144925.2239 | 0 | 57534.1003 | 0 | 204639.3582 | 532429.6327 | 363394.1647 | 1625179.4587 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9919343.6195 | 22545576.6734 | 10000 | 0.029338 | 338105.2594 | 768476.0546 | 6892.733 | 15666.4238
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3622 | 0.5501 | 0.010679 | 4 | 241419.0875 | 537017.7599 | 4921.6546 | 10947.8334 | 71.4568 | 0 | 110.8519 | 177395.7757 | 5130.1833 | 219257.8633 | 184091.1837 | 0 | 65617.1269 | 0 | 254081.9318 | 661069.0673 | 451193.222 | 2017836.354 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10312000.5148 | 22938233.5687 | 13335.2143 | 0.042714 | 241419.0875 | 537017.7599 | 4921.6546 | 10947.8334
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1675 | 0.71513 | 0.014988 | 4 | 179413.2571 | 390012.3632 | 3657.5819 | 7950.9296 | 71.9164 | 0 | 90.9155 | 214031.9253 | 6221.3381 | 270353.2717 | 231014.2145 | 0 | 73392.0688 | 0 | 310054.9991 | 806699.5067 | 550588.9894 | 2462356.3135 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10756520.4743 | 23382753.5282 | 17782.7941 | 0.059954 | 179413.2571 | 390012.3632 | 3657.5819 | 7950.9296
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8593 | 0.964 | 0.021066 | 4 | 135313.4038 | 285157.9826 | 2758.5468 | 5813.3312 | 72.4285 | 0 | 82.4012 | 265068.1444 | 7746.5337 | 343150.7758 | 301439.1089 | 0 | 85948.9262 | 0 | 391307.8608 | 1018102.7854 | 694876.071 | 3107640.2062 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 11401804.367 | 24028037.4209 | 23713.7371 | 0.084262 | 135313.4038 | 285157.9826 | 2758.5468 | 5813.3312
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9922 | 1.2524 | 0.028743 | 4 | 105329.0407 | 215147.4847 | 2147.275 | 4386.0725 | 72.738 | 0 | 92.5788 | 319231.6461 | 9361.4574 | 422959.379 | 383186.1644 | 0 | 97290.1356 | 0 | 480491.2252 | 1250139.6056 | 853245.9686 | 3815905.582 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 12110069.7427 | 24736302.7966 | 31622.7766 | 0.11497 | 105329.0407 | 215147.4847 | 2147.275 | 4386.0725
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8554 | 1.6081 | 0.038615 | 4 | 83815.8828 | 165559.8713 | 1708.7001 | 3375.1619 | 72.972 | 0 | 124.6969 | 381068.3444 | 11203.5696 | 516499.4008 | 483998.5567 | 0 | 109236.6558 | 0 | 585782.5457 | 1524086.0233 | 1040220.0277 | 4652095.124 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 12946259.2848 | 25572492.3387 | 42169.6503 | 0.15446 | 83815.8828 | 165559.8713 | 1708.7001 | 3375.1619
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.5307 | 2.0388 | 0.051086 | 4 | 68111.9289 | 129901.5916 | 1388.5538 | 2648.2197 | 73.1494 | 0 | 103.2301 | 450643.0612 | 13274.0151 | 624376.4405 | 606029.3851 | 0 | 121471.0698 | 0 | 708159.6489 | 1842486.143 | 1257534.6519 | 5623974.4156 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 13918138.5764 | 26544371.6303 | 56234.1325 | 0.20434 | 68111.9289 | 129901.5916 | 1388.5538 | 2648.2197
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0406 | 2.5465 | 0.066458 | 4 | 56506.5324 | 104003.6169 | 1151.9621 | 2120.2544 | 73.2839 | 0 | 116.2495 | 527216.1757 | 15550.2646 | 745845.6742 | 749864.26 | 0 | 133469.189 | 0 | 847058.7698 | 2203873.1633 | 1504188.719 | 6727066.2156 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 15021230.3764 | 27647463.4303 | 74989.4209 | 0.26583 | 56506.5324 | 104003.6169 | 1151.9621 | 2120.2544
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.2692 | 3.1206 | 0.084749 | 4 | 47862.7279 | 85108.5731 | 975.7464 | 1735.0534 | 73.3853 | 0 | 105.6572 | 608491.0256 | 17963.6243 | 877482.7772 | 912478.3321 | 0 | 144291.9638 | 0 | 998676.012 | 2598350.1266 | 1773427.3522 | 7931161.2139 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 16225325.3747 | 28851558.4286 | 100000 | 0.339 | 47862.7279 | 85108.5731 | 975.7464 | 1735.0534
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.0024 | 3.7412 | 0.10559 | 4 | 41401.0472 | 71295.2371 | 844.0163 | 1453.4498 | 73.4614 | 0 | 140.4717 | 691503.4086 | 20425.866 | 1014455.2543 | 1088280.846 | 0 | 153174.4429 | 0 | 1157457.529 | 3011467.0632 | 2055388.1501 | 9192152.5602 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 17486316.721 | 30112549.7749 | 133352.1432 | 0.42236 | 41401.0472 | 71295.2371 | 844.0163 | 1453.4498
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.8554 | 4.3729 | 0.12806 | 4 | 36570.3241 | 61219.0232 | 745.5355 | 1248.0326 | 73.5165 | 0 | 131.0563 | 771882.4058 | 22807.3379 | 1149256.33 | 1267210.1876 | 0 | 159213.7984 | 0 | 1314444.3233 | 3419914.4996 | 2334161.9182 | 10438890.8009 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 18733054.9616 | 31359288.0155 | 177827.941 | 0.51225 | 36570.3241 | 61219.0232 | 745.5355 | 1248.0326
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.4324 | 4.9788 | 0.1509 | 4 | 32966.9705 | 53885.324 | 672.0763 | 1098.5252 | 73.5542 | 0 | 121.0009 | 845786.9772 | 24994.4362 | 1274940.7051 | 1438883.7342 | 0 | 162121.5979 | 0 | 1461223.7058 | 3801804.3442 | 2594809.5842 | 11604565.0848 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 19898729.2456 | 32524962.2994 | 237137.3706 | 0.6036 | 32966.9705 | 53885.324 | 672.0763 | 1098.5252
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3593 | 5.5244 | 0.17272 | 4 | 30286.2411 | 48561.6169 | 617.426 | 989.9942 | 73.5775 | 0 | 118.2674 | 910035.466 | 26893.4874 | 1385492.7575 | 1593499.6865 | 0 | 161958.6155 | 0 | 1590373.205 | 4137824.8491 | 2824150.4833 | 12630228.5503 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 20924392.7111 | 33550625.765 | 316227.766 | 0.69089 | 30286.2411 | 48561.6169 | 617.426 | 989.9942
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4749 | 5.9946 | 0.19254 | 4 | 28295.2475 | 44689.8142 | 576.8369 | 911.0623 | 73.5903 | 0 | 142.6018 | 963881.5222 | 28483.1754 | 1479043.9652 | 1726847.809 | 0 | 159587.3653 | 0 | 1699559.0965 | 4421904.1415 | 3018040.4376 | 13497347.5126 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 21791511.6734 | 34417744.7273 | 421696.5034 | 0.77015 | 28295.2475 | 44689.8142 | 576.8369 | 911.0623
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.7138 | 6.3837 | 0.20973 | 4 | 26817.0587 | 41867.8707 | 546.702 | 853.5332 | 73.596 | 0 | 147.1862 | 1007457.575 | 29768.2452 | 1555344.3274 | 1837246.7392 | 0 | 155812.4118 | 0 | 1788395.4265 | 4653038.0494 | 3175794.0791 | 14202856.8537 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 22497021.0145 | 35123254.0684 | 562341.3252 | 0.83891 | 26817.0587 | 41867.8707 | 546.702 | 853.5332
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.1554 | 6.6991 | 0.22417 | 4 | 25718.8784 | 39800.0906 | 524.3141 | 811.3787 | 73.5976 | 0 | 174.4472 | 1042183.2447 | 30791.3197 | 1616525.1523 | 1926804.7955 | 0 | 151545.9501 | 0 | 1859461.6803 | 4837937.864 | 3301992.0019 | 14767242.0085 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23061406.1692 | 35687639.2231 | 749894.2093 | 0.89667 | 25718.8784 | 39800.0906 | 524.3141 | 811.3787
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.8692 | 6.9475 | 0.23593 | 4 | 24902.034 | 38281.2179 | 507.6616 | 780.4144 | 73.5969 | 0 | 140.5853 | 1069170.0049 | 31585.7406 | 1664302.0496 | 1997369.9611 | 0 | 147224.5828 | 0 | 1914764.4122 | 4981824.2283 | 3400197.4021 | 15206438.3816 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23500602.5424 | 36126835.5963 | 1000000 | 0.94372 | 24902.034 | 38281.2179 | 507.6616 | 780.4144
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.0035 | 7.1426 | 0.24536 | 4 | 24293.6136 | 37158.6283 | 495.2582 | 757.5289 | 73.5953 | 0 | 117.812 | 1090156.4532 | 32203.1126 | 1701595.643 | 2052828.7499 | 0 | 143323.7678 | 0 | 1957842.0133 | 5093903.3099 | 3476693.6783 | 15548546.7278 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23842710.8885 | 36468943.9424 | 1333521.4322 | 0.98144 | 24293.6136 | 37158.6283 | 495.2582 | 757.5289
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.6406 | 7.2921 | 0.25276 | 4 | 23839.8361 | 36328.356 | 486.0073 | 740.6027 | 73.5933 | 0 | 156.3508 | 1106116.4657 | 32672.3661 | 1730038.9314 | 2095346.2631 | 0 | 139882.7107 | 0 | 1990582.1274 | 5179086.371 | 3534832.8678 | 15808558.1033 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24102722.2641 | 36728955.318 | 1778279.41 | 1.011 | 23839.8361 | 36328.356 | 486.0073 | 740.6027
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8929 | 7.4064 | 0.2585 | 4 | 23501.0025 | 35711.9604 | 479.0997 | 728.0366 | 73.5915 | 0 | 125.1024 | 1118245.1782 | 33028.8223 | 1751701.5742 | 2127854.5806 | 0 | 136996.5418 | 0 | 2015452.4119 | 5243793.7495 | 3578996.9833 | 16006069.8418 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24300234.0025 | 36926467.0564 | 2371373.7057 | 1.034 | 23501.0025 | 35711.9604 | 479.0997 | 728.0366
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.8519 | 7.4939 | 0.26294 | 4 | 23247.7531 | 35252.7499 | 473.9369 | 718.675 | 73.5899 | 0 | 170.8244 | 1127487.2417 | 33300.3526 | 1768235.9604 | 2152740.3594 | 0 | 134669.3859 | 0 | 2034408.987 | 5293114.8696 | 3612659.6611 | 16156616.8178 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24450780.9786 | 37077014.0325 | 3162277.6602 | 1.0517 | 23247.7531 | 35252.7499 | 473.9369 | 718.675
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.5661 | 7.559 | 0.2663 | 4 | 23058.3243 | 34911.5038 | 470.0751 | 711.7182 | 73.5885 | 0 | 136.5137 | 1134344.786 | 33501.7757 | 1780519.7383 | 2171269.4592 | 0 | 132760.4192 | 0 | 2048434.5096 | 5329606.4022 | 3637565.8819 | 16268002.972 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24562167.1328 | 37188400.1867 | 4216965.0343 | 1.0652 | 23058.3243 | 34911.5038 | 470.0751 | 711.7182
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.1165 | 7.6092 | 0.26889 | 4 | 22916.5469 | 34655.8444 | 467.1848 | 706.5063 | 73.5874 | 0 | 169.3464 | 1139615.3214 | 33656.5549 | 1789969.6485 | 2185547.5306 | 0 | 131304.6845 | 0 | 2059236.5586 | 5357711.1179 | 3656747.9279 | 16353789.3443 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24647953.505 | 37274186.5589 | 5623413.2519 | 1.0756 | 22916.5469 | 34655.8444 | 467.1848 | 706.5063
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.5381 | 7.6476 | 0.27086 | 4 | 22810.3843 | 34464.2529 | 465.0205 | 702.6004 | 73.5865 | 0 | 168.3936 | 1143642.9615 | 33774.8167 | 1797196.3078 | 2196480.2802 | 0 | 130199.4603 | 0 | 2067504.5924 | 5379222.8459 | 3671430.1243 | 16419451.3891 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24713615.5499 | 37339848.6038 | 7498942.0933 | 1.0834 | 22810.3843 | 34464.2529 | 465.0205 | 702.6004
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.8398 | 7.6751 | 0.27232 | 4 | 22730.8617 | 34322.2542 | 463.3994 | 699.7056 | 73.5859 | 0 | 168.1494 | 1146521.2272 | 33859.3206 | 1802363.4637 | 2204304.6829 | 0 | 129284.611 | 0 | 2073369.9891 | 5394483.4049 | 3681845.7694 | 16466032.4686 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24760196.6294 | 37386429.6833 | 10000000 | 1.0893 | 22730.8617 | 34322.2542 | 463.3994 | 699.7056
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7354 | [19 empty] | 100 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5573 | [19 empty] | 133.3521 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4275 | [19 empty] | 177.8279 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8659 | [19 empty] | 237.1374 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4313 | [19 empty] | 316.2278 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4217 | [19 empty] | 421.6965 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6554 | [19 empty] | 562.3413 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6855 | [19 empty] | 749.8942 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4371 | [19 empty] | 1000 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.1572 | [19 empty] | 1333.5214 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.3618 | [19 empty] | 1778.2794 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.12133 | 0.00020644 | 4 | 11315307.5763 | 27193764.9719 | 230677.85 | 554381.6812 | 66.8898 | 0 | 36.6294 | 58796.3256 | 1618.3882 | 65702.517 | 61330.9943 | 0 | 39441.3084 | 0 | 88486.9181 | 230224.8097 | 157133.1632 | 702734.4245 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9343665.2762 | 22455371.6975 | 2371.3737 | 0.00082575 | 11315307.5763 | 27193764.9719 | 230677.85 | 554381.6812
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.13176 | 0.0012917 | 4 | 1812983.7173 | 4350587.992 | 36960.1253 | 88692.6208 | 67.4299 | 0 | 245.9376 | 62703.911 | 1734.84 | 70147.5681 | 64265.983 | 0 | 35771.1202 | 0 | 91503.1347 | 238072.3865 | 162489.2957 | 726688.239 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9367619.0908 | 22479325.5121 | 3162.2777 | 0.005167 | 1812983.7173 | 4350587.992 | 36960.1253 | 88692.6208
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.18772 | 0.0025681 | 4 | 931224.852 | 2207627.4728 | 18984.2782 | 45005.4721 | 69.4991 | 0 | 342.9799 | 82294.1816 | 2322.1704 | 92933.1453 | 79930.4721 | 0 | 41163.5337 | 0 | 116470.9662 | 303033.5626 | 206826.6332 | 924974.665 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9565905.5167 | 22677611.938 | 4216.965 | 0.010272 | 931224.852 | 2207627.4728 | 18984.2782 | 45005.4721
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0862 | 0.26446 | 0.0043688 | 4 | 561942.6945 | 1312241.1674 | 11455.9619 | 26751.8111 | 71.1315 | 0 | 69.675 | 106481.2285 | 3052.3382 | 122072.3397 | 101290.0692 | 0 | 47827.7538 | 0 | 148482.2544 | 386320.3682 | 263671.5894 | 1179197.9413 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9820128.793 | 22931835.2143 | 5623.4133 | 0.017475 | 561942.6945 | 1312241.1674 | 11455.9619 | 26751.8111
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 0.37733 | 0.0068283 | 4 | 372452.0948 | 852501.6515 | 7592.9397 | 17379.3993 | 72.4681 | 0 | 103.4889 | 138432.9969 | 4020.6572 | 162024.349 | 132593.1955 | 0 | 57541.4455 | 0 | 192898.9312 | 501883.4499 | 342545.7672 | 1531940.7923 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10172871.644 | 23284578.0653 | 7498.9421 | 0.027313 | 372452.0948 | 852501.6515 | 7592.9397 | 17379.3993
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4996 | 0.49963 | 0.010183 | 4 | 258407.5627 | 580305.9368 | 5267.9877 | 11830.3214 | 73.2973 | 0 | 109.0581 | 169852.5992 | 4974.4024 | 202676.8489 | 166455.9479 | 0 | 64527.6249 | 0 | 237310.0951 | 617432.1885 | 421410.1556 | 1884639.8625 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10525570.7143 | 23637277.1356 | 10000 | 0.040732 | 258407.5627 | 580305.9368 | 5267.9877 | 11830.3214
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3198 | 0.67713 | 0.014629 | 4 | 188265.0648 | 412341.9937 | 3838.038 | 8406.1493 | 73.9827 | 0 | 90.0711 | 211439.4574 | 6236.1143 | 258320.5978 | 215591.0683 | 0 | 75308.0283 | 0 | 299089.1537 | 778168.6264 | 531116.0773 | 2375269.1235 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11016199.9753 | 24127906.3965 | 13335.2143 | 0.058514 | 188265.0648 | 412341.9937 | 3838.038 | 8406.1493
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6607 | 0.90689 | 0.020644 | 4 | 140687.8879 | 299470.4617 | 2868.1129 | 6105.1104 | 74.5436 | 0 | 94.2384 | 260729.641 | 7733.7461 | 326174.4286 | 279013.699 | 0 | 87387.0202 | 0 | 374805.0286 | 975165.8014 | 665570.6971 | 2976580.062 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11617510.9138 | 24729217.335 | 17782.7941 | 0.082576 | 140687.8879 | 299470.4617 | 2868.1129 | 6105.1104
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4964 | 1.1847 | 0.028413 | 4 | 108285.5759 | 223651.5017 | 2207.5479 | 4559.4384 | 74.924 | 0 | 111.3238 | 315393.7941 | 9392.1878 | 403786.9113 | 355748.5946 | 0 | 99330.7507 | 0 | 461624.373 | 1201051.9264 | 819742.6189 | 3666071.1569 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 12307002.0087 | 25418708.4299 | 23713.7371 | 0.11365 | 108285.5759 | 223651.5017 | 2207.5479 | 4559.4384
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9749 | 1.5251 | 0.038407 | 4 | 85350.2427 | 170698.174 | 1739.9801 | 3479.9132 | 75.2086 | 0 | 101.4785 | 377266.3863 | 11266.8811 | 494085.9637 | 449320.5762 | 0 | 111639.3218 | 0 | 562995.8604 | 1464799.7423 | 999755.9227 | 4471130.6545 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 13112061.5063 | 26223767.9276 | 31622.7766 | 0.15363 | 85350.2427 | 170698.174 | 1739.9801 | 3479.9132
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2844 | 1.9468 | 0.051184 | 4 | 68713.3872 | 132755.1083 | 1400.8153 | 2706.3924 | 75.4275 | 0 | 116.5359 | 448373.5776 | 13418.8718 | 600528.4559 | 565051.1423 | 0 | 124902.3662 | 0 | 683387.0214 | 1778032.8476 | 1213543.9534 | 5427238.2362 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 14068169.088 | 27179875.5092 | 42169.6503 | 0.20474 | 68713.3872 | 132755.1083 | 1400.8153 | 2706.3924
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4607 | 2.4534 | 0.06719 | 4 | 56451.894 | 105237.7738 | 1150.8482 | 2145.4144 | 75.5941 | 0 | 104.6179 | 527941.2496 | 15824.1532 | 722487.7512 | 704071.0068 | 0 | 138349.0311 | 0 | 822382.5449 | 2139670.688 | 1460369.2104 | 6531095.6353 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 15172026.487 | 28283732.9083 | 56234.1325 | 0.26876 | 56451.894 | 105237.7738 | 1150.8482 | 2145.4144
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4855 | 3.0431 | 0.086689 | 4 | 47325.2605 | 85137.8508 | 964.7894 | 1735.6502 | 75.7205 | 0 | 80.2431 | 614615.5545 | 18441.133 | 858279.6336 | 865886.0945 | 0 | 151239.2571 | 0 | 978300.0523 | 2545336.0593 | 1737244.1619 | 7769341.9462 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 16410272.7979 | 29521979.2192 | 74989.4209 | 0.34676 | 47325.2605 | 85137.8508 | 964.7894 | 1735.6502
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.1844 | 3.699 | 0.10953 | 4 | 40492.9978 | 70420.3797 | 825.5045 | 1435.6147 | 75.8157 | 0 | 122.4436 | 705324.1759 | 21176.6276 | 1003239.658 | 1045817.4563 | 0 | 162450.0005 | 0 | 1145823.0881 | 2981196.6346 | 2034727.9606 | 9099755.6015 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 17740686.4533 | 30852392.8746 | 100000 | 0.43812 | 40492.9978 | 70420.3797 | 825.5045 | 1435.6147
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.2755 | 4.3933 | 0.13505 | 4 | 35369.3351 | 59642.0716 | 721.0517 | 1215.8843 | 75.8861 | 0 | 115.9239 | 796286.1095 | 23916.4463 | 1151187.8562 | 1236290.3996 | 0 | 171107.2219 | 0 | 1317727.333 | 3428456.2175 | 2339991.8162 | 10464963.4 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 19105894.2518 | 32217600.6731 | 133352.1432 | 0.54018 | 35369.3351 | 59642.0716 | 721.0517 | 1215.8843
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.313 | 5.0822 | 0.16192 | 4 | 31532.6962 | 51777.4124 | 642.8367 | 1055.5526 | 75.9355 | 0 | 114.9202 | 882392.4781 | 26506.7626 | 1293403.0731 | 1425299.7801 | 0 | 176269.8999 | 0 | 1483510.0775 | 3859788.912 | 2634385.2432 | 11781556.2265 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 20422487.0782 | 33534193.4995 | 177827.941 | 0.64766 | 31532.6962 | 51777.4124 | 642.8367 | 1055.5526
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.9218 | 5.7285 | 0.1886 | 4 | 28668.4687 | 46048.6058 | 584.4455 | 938.7631 | 75.9671 | 0 | 138.4634 | 960057.7356 | 28840.0601 | 1423369.7353 | 1602744.3316 | 0 | 177986.0746 | 0 | 1635269.1955 | 4254635.0068 | 2903875.8162 | 12986777.9556 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 21627708.8074 | 34739415.2286 | 237137.3706 | 0.75441 | 28668.4687 | 46048.6058 | 584.4455 | 938.7631
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.7561 | 6.2984 | 0.21355 | 4 | 26535.9722 | 41885.6795 | 540.9717 | 853.8962 | 75.9846 | 0 | 137.1778 | 1026354.5814 | 30829.132 | 1535536.3533 | 1759317.874 | 0 | 176513.7902 | 0 | 1766135.175 | 4595121.4413 | 3136264.804 | 14026073.1513 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 22667004.0031 | 35778710.4244 | 316227.766 | 0.8542 | 26535.9722 | 41885.6795 | 540.9717 | 853.8962
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.7332 | 6.7837 | 0.23583 | 4 | 24950.5418 | 38850.1236 | 508.6505 | 792.0123 | 75.9924 | 0 | 132.4416 | 1081385.2219 | 32478.0499 | 1629482.2631 | 1892813.486 | 0 | 173046.6733 | 0 | 1875590.2208 | 4879901.018 | 3330632.7167 | 14895329.6497 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 23536260.5014 | 36647966.9227 | 421696.5034 | 0.94332 | 24950.5418 | 38850.1236 | 508.6505 | 792.0123
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.8204 | 7.1816 | 0.2549 | 4 | 23772.0088 | 36631.7631 | 484.6246 | 746.788 | 75.9942 | 0 | 143.5661 | 1125595.769 | 33801.1994 | 1705504.3731 | 2002371.4928 | 0 | 168422.656 | 0 | 1963921.2412 | 5109720.2141 | 3487489.0404 | 15596825.986 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 24237756.8378 | 37349463.2591 | 562341.3252 | 1.0196 | 23772.0088 | 36631.7631 | 484.6246 | 746.788
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0996 | 7.5004 | 0.27072 | 4 | 22895.3162 | 35003.6896 | 466.752 | 713.5976 | 75.9928 | 0 | 138.7027 | 1160462.5936 | 34843.6469 | 1765802.8546 | 2090226.4426 | 0 | 163463.1786 | 0 | 2033771.4994 | 5291456.2575 | 3611527.6243 | 16151554.0975 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 24792484.9492 | 37904191.3705 | 749894.2093 | 1.0829 | 22895.3162 | 35003.6896 | 466.752 | 713.5976
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.6749 | 7.7504 | 0.2835 | 4 | 22242.4187 | 33804.8397 | 453.4418 | 689.1574 | 75.9899 | 0 | 123.2071 | 1187480.9107 | 35650.7586 | 1812736.3974 | 2159186.9868 | 0 | 158662.2701 | 0 | 2087949.7562 | 5432416.9682 | 3707736.2058 | 16581820.2537 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25222751.1054 | 38334457.5267 | 1000000 | 1.134 | 22242.4187 | 33804.8397 | 453.4418 | 689.1574
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.6692 | 7.9438 | 0.29363 | 4 | 21755.5887 | 32918.9739 | 443.5171 | 671.0978 | 75.9866 | 0 | 134.9747 | 1208191.4271 | 36269.0183 | 1848835.8995 | 2212570.1422 | 0 | 154329.9921 | 0 | 2129476.6269 | 5540461.3674 | 3781478.7284 | 16911613.2019 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25552544.0537 | 38664250.475 | 1333521.4322 | 1.1745 | 21755.5887 | 32918.9739 | 443.5171 | 671.0978
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.2091 | 8.093 | 0.30157 | 4 | 21392.1681 | 32261.5724 | 436.1083 | 657.6958 | 75.9835 | 0 | 148.1057 | 1224058.0828 | 36742.4219 | 1876564.7676 | 2253775.2114 | 0 | 150650.2404 | 0 | 2161298.3824 | 5623255.0477 | 3837987.1164 | 17164331.2707 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25805262.1224 | 38916968.5437 | 1778279.41 | 1.2063 | 21392.1681 | 32261.5724 | 436.1083 | 657.6958
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3929 | 8.2076 | 0.30774 | 4 | 21120.6043 | 31772.2872 | 430.5721 | 647.721 | 75.9807 | 0 | 151.0276 | 1236182.5285 | 37104.0188 | 1897796.117 | 2285442.0168 | 0 | 147637.5 | 0 | 2185623.2506 | 5686543.3652 | 3881182.6935 | 17357511.4905 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25998442.3423 | 39110148.7636 | 2371373.7057 | 1.231 | 21120.6043 | 31772.2872 | 430.5721 | 647.721
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.2897 | 8.2943 | 0.31247 | 4 | 20917.5154 | 31408.0433 | 426.4318 | 640.2954 | 75.9784 | 0 | 142.3775 | 1245326.7645 | 37376.6455 | 1913833.1198 | 2309428.4625 | 0 | 145191.6632 | 0 | 2203951.0956 | 5734228.6582 | 3913728.8859 | 17503065.2951 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26143996.1468 | 39255702.5681 | 3162277.6602 | 1.2499 | 20917.5154 | 31408.0433 | 426.4318 | 640.2954
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9741 | 8.3605 | 0.31609 | 4 | 20765.5374 | 31135.9145 | 423.3336 | 634.7477 | 75.9766 | 0 | 136.0423 | 1252281.2061 | 37583.9336 | 1926043.7325 | 2327730.4057 | 0 | 143275.213 | 0 | 2217896.6515 | 5770512.134 | 3938493.1036 | 17613816.38 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26254747.2318 | 39366453.6531 | 4216965.0343 | 1.2643 | 20765.5374 | 31135.9145 | 423.3336 | 634.7477
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.4734 | 8.4088 | 0.3188 | 4 | 20651.7501 | 30933.9049 | 421.0139 | 630.6295 | 75.9752 | 0 | 148.1549 | 1257342.3722 | 37734.761 | 1934937.7694 | 2341082.2628 | 0 | 141701.179 | 0 | 2227991.3544 | 5796776.4802 | 3956419.0596 | 17693985.2386 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26334916.0903 | 39446622.5116 | 5623413.2519 | 1.2752 | 20651.7501 | 30933.9049 | 421.0139 | 630.6295
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.8561 | 8.4458 | 0.32087 | 4 | 20566.5238 | 30782.4153 | 419.2764 | 627.5412 | 75.974 | 0 | 143.2737 | 1261213.491 | 37850.1077 | 1941744.8637 | 2351313.0933 | 0 | 140510.9406 | 0 | 2235726.6735 | 5816902.1939 | 3970155.2728 | 17755416.6365 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26396347.4883 | 39508053.9095 | 7498942.0933 | 1.2835 | 20566.5238 | 30782.4153 | 419.2764 | 627.5412
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.1534 | 8.4745 | 0.32245 | 4 | 20502.6706 | 30668.4169 | 417.9747 | 625.2172 | 75.9731 | 0 | 132.8605 | 1264216.5182 | 37939.5783 | 1947028.0685 | 2359260.6848 | 0 | 139636.6039 | 0 | 2241751.767 | 5832578.2511 | 3980854.5039 | 17803265.9757 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26444196.8275 | 39555903.2488 | 10000000 | 1.2898 | 20502.6706 | 30668.4169 | 417.9747 | 625.2172
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.8655 | [19 empty] | 100 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4849 | [19 empty] | 133.3521 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.856 | [19 empty] | 177.8279 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8903 | [19 empty] | 237.1374 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2572 | [19 empty] | 316.2278 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3627 | [19 empty] | 421.6965 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6525 | [19 empty] | 562.3413 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.5348 | [19 empty] | 749.8942 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6118 | [19 empty] | 1000 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.8179 | [19 empty] | 1333.5214 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.9051 | [19 empty] | 1778.2794 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.12759 | 0.00083982 | 4 | 2892375.2389 | 6942460.3205 | 58964.9815 | 141531.444 | 68.5924 | 0 | 34.5152 | 62339.3881 | 1738.9047 | 68293.6886 | 62451.7777 | 0 | 38528.3727 | 0 | 91007.3314 | 236782.4082 | 161608.859 | 722750.7305 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9716308.3641 | 23321692.28 | 2371.3737 | 0.0033593 | 2892375.2389 | 6942460.3205 | 58964.9815 | 141531.444
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.14061 | 0.0019787 | 4 | 1231841.7975 | 2950799.8328 | 25112.7612 | 60156.0458 | 69.2665 | 0 | 249.8034 | 67255.1328 | 1887.7828 | 73769.1324 | 66029.4268 | 0 | 35258.4614 | 0 | 95237.9751 | 247789.6752 | 169121.5449 | 756349.1315 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9749906.7651 | 23355290.681 | 3162.2777 | 0.0079149 | 1231841.7975 | 2950799.8328 | 25112.7612 | 60156.0458
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7398 | 0.24365 | 0.0037808 | 4 | 668928.3407 | 1568574.6101 | 13637.009 | 31977.5151 | 72.4954 | 0 | 98.2546 | 102390.7626 | 2961.912 | 114186.5187 | 94128.8719 | 0 | 48804.8317 | 0 | 141364.4298 | 367801.2485 | 251031.9097 | 1122670.4848 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10116228.1185 | 23721612.0344 | 4216.965 | 0.015123 | 668928.3407 | 1568574.6101 | 13637.009 | 31977.5151
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6903 | 0.34155 | 0.0061754 | 4 | 422105.6334 | 972891.2674 | 8605.1943 | 19833.7044 | 74.0021 | 0 | 95.6586 | 131682.8946 | 3863.9254 | 149411.2098 | 120659.4637 | 0 | 57115.5547 | 0 | 180465.8888 | 469535.224 | 320467.4384 | 1433201.5993 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10426759.2329 | 24032143.1488 | 5623.4133 | 0.024702 | 422105.6334 | 972891.2674 | 8605.1943 | 19833.7044
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8593 | 0.46245 | 0.0094139 | 4 | 286403.6663 | 647713.6338 | 5838.7261 | 13204.5185 | 75.0776 | 0 | 96.1458 | 164459.5552 | 4875.4308 | 190220.1376 | 153282.3045 | 0 | 65473.6959 | 0 | 225541.3383 | 586812.2975 | 400511.4508 | 1791176.2106 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10784733.8443 | 24390117.7602 | 7498.9421 | 0.037656 | 286403.6663 | 647713.6338 | 5838.7261 | 13204.5185
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3622 | 0.61737 | 0.013684 | 4 | 204919.2158 | 453491.0576 | 4177.5554 | 9245.0286 | 75.8873 | 0 | 109.7668 | 202713.6873 | 6055.2839 | 239524.5849 | 194420.9572 | 0 | 74867.7325 | 0 | 279857.0759 | 728130.7049 | 496964.1677 | 2222534.1943 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11216091.8279 | 24821475.7438 | 10000 | 0.054734 | 204919.2158 | 453491.0576 | 4177.5554 | 9245.0286
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1649 | 0.8025 | 0.019188 | 4 | 152477.1811 | 329742.6455 | 3108.4536 | 6722.2498 | 76.4259 | 0 | 112.8354 | 244594.2836 | 7344.451 | 295308.1938 | 243622.8519 | 0 | 83869.4557 | 0 | 341148.3021 | 887597.9028 | 605803.807 | 2709289.248 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11702846.8816 | 25308230.7975 | 13335.2143 | 0.076751 | 152477.1811 | 329742.6455 | 3108.4536 | 6722.2498
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9176 | 1.0885 | 0.026978 | 4 | 115155.9638 | 241236.3347 | 2347.6101 | 4917.929 | 77.0296 | 0 | 94.0746 | 304267.405 | 9187.0597 | 376663.5611 | 319084.9636 | 0 | 99188.3539 | 0 | 432272.6239 | 1124684.696 | 767620.415 | 3432969.0782 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 12426526.7118 | 26031910.6277 | 17782.7941 | 0.10791 | 115155.9638 | 241236.3347 | 2347.6101 | 4917.929
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0688 | 1.4153 | 0.036894 | 4 | 89514.3619 | 181706.7952 | 1824.8713 | 3704.3388 | 77.3896 | 0 | 207.637 | 366812.8972 | 11115.345 | 464576.0285 | 406417.3746 | 0 | 112480.4076 | 0 | 530946.8006 | 1381414.6631 | 942843.8928 | 4216607.4094 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13210165.043 | 26815548.9589 | 23713.7371 | 0.14758 | 89514.3619 | 181706.7952 | 1824.8713 | 3704.3388
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.064 | 1.7262 | 0.048954 | 4 | 71026.5105 | 140507.3901 | 1447.9715 | 2864.4332 | 77.6102 | 0 | 179.3869 | 422315.795 | 12824.8378 | 544436.6784 | 489441.9681 | 0 | 117703.7692 | 0 | 618821.9889 | 1610047.8772 | 1098890.7593 | 4914483.6737 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13908041.3073 | 27513425.2232 | 31622.7766 | 0.19581 | 71026.5105 | 140507.3901 | 1447.9715 | 2864.4332
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9206 | 2.3341 | 0.066356 | 4 | 57523.6148 | 108782.9897 | 1172.6967 | 2217.6884 | 77.8773 | 0 | 84.0554 | 522902.0036 | 15918.9921 | 692899.5327 | 651802.3204 | 0 | 142302.7325 | 0 | 790071.9767 | 2055605.2174 | 1402992.7993 | 6274495.5748 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 15268053.2085 | 28873437.1244 | 42169.6503 | 0.26542 | 57523.6148 | 108782.9897 | 1172.6967 | 2217.6884
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5204 | 2.9153 | 0.086482 | 4 | 47676.843 | 87006.7547 | 971.9569 | 1773.7504 | 78.0319 | 0 | 98.9041 | 611884.4627 | 18651.8702 | 827680.7139 | 806808.0195 | 0 | 156241.8186 | 0 | 944294.0851 | 2456859.5081 | 1676857.0977 | 7499277.5758 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 16492835.2094 | 30098219.1253 | 56234.1325 | 0.34593 | 47676.843 | 87006.7547 | 971.9569 | 1773.7504
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.0346 | 3.5907 | 0.11072 | 4 | 40338.8906 | 71059.9343 | 822.3628 | 1448.6529 | 78.1511 | 0 | 103.5981 | 708835.183 | 21624.2828 | 977746.0512 | 986204.3824 | 0 | 169827.0377 | 0 | 1117052.4055 | 2906341.2201 | 1983637.602 | 8871268.1647 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 17864825.7983 | 31470209.7142 | 74989.4209 | 0.44287 | 40338.8906 | 71059.9343 | 822.3628 | 1448.6529
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.1498 | 4.3286 | 0.13864 | 4 | 34827.4802 | 59361.2871 | 710.0053 | 1210.1601 | 78.2404 | 0 | 99.0494 | 808746.2034 | 24683.4669 | 1135350.4824 | 1182159.8737 | 0 | 181125.0271 | 0 | 1299505.3709 | 3381046.4098 | 2307633.6482 | 10320250.4823 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 19313808.1159 | 32919192.0318 | 100000 | 0.55456 | 34827.4802 | 59361.2871 | 710.0053 | 1210.1601
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.5286 | 5.0938 | 0.16922 | 4 | 30687.3846 | 50787.9395 | 625.6038 | 1035.3808 | 78.305 | 0 | 123.8973 | 907138.5097 | 27692.1315 | 1293180.3005 | 1385367.2366 | 0 | 189246.2529 | 0 | 1483023.5282 | 3858523.0104 | 2633521.2393 | 11777692.209 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 20771249.8426 | 34376633.7585 | 133352.1432 | 0.67687 | 30687.3846 | 50787.9395 | 625.6038 | 1035.3808
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.6929 | 5.8362 | 0.20071 | 4 | 27585.493 | 44531.924 | 562.3676 | 907.8435 | 78.3479 | 0 | 110.8126 | 998474.7304 | 30481.0781 | 1441838.5798 | 1582637.6621 | 0 | 193349.9036 | 0 | 1656244.962 | 4309209.6487 | 2941124.1306 | 13153360.6952 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 22146918.3289 | 35752302.2448 | 177827.941 | 0.80285 | 27585.493 | 44531.924 | 562.3676 | 907.8435
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.2681 | 6.5167 | 0.23129 | 4 | 25269.2383 | 39975.3562 | 515.1476 | 814.9517 | 78.373 | 0 | 115.5757 | 1079166.1331 | 32941.3117 | 1574808.0901 | 1763632.8196 | 0 | 193666.3884 | 0 | 1811243.7498 | 4712484.6997 | 3216367.6394 | 14384310.8318 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 23377868.4654 | 36983252.3813 | 237137.3706 | 0.92515 | 25269.2383 | 39975.3562 | 515.1476 | 814.9517
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1024 | 7.1196 | 0.26033 | 4 | 23472.5982 | 36537.9808 | 478.5207 | 744.8762 | 78.3847 | 0 | 109.1178 | 1148521.0959 | 35052.7235 | 1690291.4808 | 1924165.9424 | 0 | 189994.0854 | 0 | 1945329.8779 | 5061349.3003 | 3454474.8978 | 15449179.4041 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 24442737.0377 | 38048120.9536 | 316227.766 | 1.0413 | 23472.5982 | 36537.9808 | 478.5207 | 744.8762
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.8157 | 7.6056 | 0.28404 | 4 | 22260.2391 | 34235.0872 | 453.8051 | 697.9286 | 78.3875 | 0 | 131.26 | 1203134.0188 | 36712.9979 | 1781996.7427 | 2053797.3965 | 0 | 186346.7139 | 0 | 2052175.2692 | 5339339.0915 | 3644208.6424 | 16297710.8729 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 25291268.5066 | 38896652.4225 | 421696.5034 | 1.1362 | 22260.2391 | 34235.0872 | 453.8051 | 697.9286
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.7233 | 8.0079 | 0.30487 | 4 | 21305.0354 | 32461.892 | 434.332 | 661.7796 | 78.3855 | 0 | 155.5445 | 1247509.4733 | 38060.3905 | 1857007.6998 | 2161220.1954 | 0 | 180791.5731 | 0 | 2138989.8395 | 5565212.7953 | 3798372.0865 | 16987164.0534 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 25980721.687 | 39586105.6029 | 562341.3252 | 1.2195 | 21305.0354 | 32461.892 | 434.332 | 661.7796
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8392 | 8.3281 | 0.32198 | 4 | 20593.7193 | 31157.6208 | 419.8308 | 635.1902 | 78.3812 | 0 | 121.7229 | 1282336.6859 | 39116.7519 | 1916190.2946 | 2246847.3423 | 0 | 175154.2565 | 0 | 2207261.6792 | 5742842.1176 | 3919607.7489 | 17529356.8769 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 26522914.5105 | 40128298.4264 | 749894.2093 | 1.2879 | 20593.7193 | 31157.6208 | 419.8308 | 635.1902
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.2823 | 8.5789 | 0.33572 | 4 | 20063.4523 | 30194.8177 | 409.0206 | 615.5622 | 78.3763 | 0 | 136.6835 | 1309308.9664 | 39934.1535 | 1962213.4561 | 2313962.2277 | 0 | 169908.9521 | 0 | 2260177.8248 | 5880519.0738 | 4013575.1004 | 17949599.7548 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 26943157.3884 | 40548541.3043 | 1000000 | 1.3429 | 20063.4523 | 30194.8177 | 409.0206 | 615.5622
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.1823 | 8.7736 | 0.3466 | 4 | 19667.7147 | 29481.2657 | 400.953 | 601.0155 | 78.3714 | 0 | 156.7976 | 1330086.8884 | 40563.3961 | 1997779.581 | 2366141.8968 | 0 | 165337.5628 | 0 | 2300964.6368 | 5986637.9921 | 4086003.4427 | 18273515.3967 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27267073.0303 | 40872456.9462 | 1333521.4322 | 1.3864 | 19667.7147 | 29481.2657 | 400.953 | 601.0155
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6197 | 8.9209 | 0.35502 | 4 | 19372.079 | 28952.8228 | 394.926 | 590.2425 | 78.3672 | 0 | 123.5441 | 1345694.3113 | 41035.7967 | 2024559.7448 | 2405611.5638 | 0 | 161383.9409 | 0 | 2331531.2894 | 6066166.1521 | 4140283.0461 | 18516265.8449 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27509823.4785 | 41115207.3944 | 1778279.41 | 1.4201 | 19372.079 | 28952.8228 | 394.926 | 590.2425
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.7381 | 9.0353 | 0.36157 | 4 | 19151.0367 | 28558.1011 | 390.4198 | 582.1955 | 78.3637 | 0 | 135.8084 | 1357770.3076 | 41401.1544 | 2045318.5063 | 2436312.7299 | 0 | 158250.1425 | 0 | 2355230.6079 | 6127826.9175 | 4182367.7854 | 18704478.1516 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27698035.7852 | 41303419.7011 | 2371373.7057 | 1.4463 | 19151.0367 | 28558.1011 | 390.4198 | 582.1955
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.5734 | 9.1208 | 0.36656 | 4 | 18985.6529 | 28264.7129 | 387.0482 | 576.2144 | 78.3608 | 0 | 134.0168 | 1366753.1223 | 41672.8393 | 2060781.624 | 2459242.0113 | 0 | 155675.553 | 0 | 2372808.8085 | 6173561.7897 | 4213582.7755 | 18844078.5236 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27837636.1572 | 41443020.0731 | 3162277.6602 | 1.4662 | 18985.6529 | 28264.7129 | 387.0482 | 576.2144
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.1996 | 9.1848 | 0.37035 | 4 | 18861.8459 | 28046.045 | 384.5242 | 571.7566 | 78.3586 | 0 | 131.5803 | 1373466.3226 | 41875.8296 | 2072349.8298 | 2476429.2814 | 0 | 153620.8688 | 0 | 2385919.4315 | 6207672.9415 | 4236864.3375 | 18948198.8426 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27941756.4763 | 41547140.3922 | 4216965.0343 | 1.4814 | 18861.8459 | 28046.045 | 384.5242 | 571.7566
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.6741 | 9.2333 | 0.37323 | 4 | 18769.1247 | 27882.509 | 382.634 | 568.4227 | 78.3568 | 0 | 138.7414 | 1378540.5684 | 42029.2333 | 2081100.6158 | 2489449.6459 | 0 | 152030.2432 | 0 | 2395828.6196 | 6233454.6162 | 4254460.8602 | 19026894.4026 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28020452.0363 | 41625835.9522 | 5623413.2519 | 1.4929 | 18769.1247 | 27882.509 | 382.634 | 568.4227
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.0445 | 9.2711 | 0.37544 | 4 | 18699.6618 | 27759.3933 | 381.2179 | 565.9128 | 78.3554 | 0 | 126.0188 | 1382495.517 | 42148.7814 | 2087925.1939 | 2499615.3472 | 0 | 150862.1084 | 0 | 2403588.3097 | 6253643.7381 | 4268240.3508 | 19088519.3466 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28082076.9802 | 41687460.8961 | 7498942.0933 | 1.5017 | 18699.6618 | 27759.3933 | 381.2179 | 565.9128
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.3197 | 9.2992 | 0.3771 | 4 | 18647.6106 | 27667.47 | 380.1568 | 564.0388 | 78.3543 | 0 | 137.5735 | 1385429.9645 | 42237.4726 | 2092991.1306 | 2507167.8664 | 0 | 149950.7986 | 0 | 2409333.1207 | 6268590.5579 | 4278441.8624 | 19134142.7737 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28127700.4073 | 41733084.3232 | 10000000 | 1.5084 | 18647.6106 | 27667.47 | 380.1568 | 564.0388
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.0019 | [19 empty] | 100 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0236 | [19 empty] | 133.3521 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5514 | [19 empty] | 177.8279 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1514 | [19 empty] | 237.1374 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0067 | [19 empty] | 316.2278 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7726 | [19 empty] | 421.6965 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8023 | [19 empty] | 562.3413 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9593 | [19 empty] | 749.8942 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.0962 | [19 empty] | 1000 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.4134 | [19 empty] | 1333.5214 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.13386 | 0.00015838 | 4 | 15967527.2425 | 38235478.5327 | 325519.6405 | 779481.9472 | 70.269 | 0 | 34.2893 | 65893.9465 | 1862.0812 | 70856.6736 | 63548.5272 | 0 | 44430.0496 | 0 | 96170.5985 | 250216.1699 | 170777.6774 | 763755.724 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10115800.2303 | 24223065.768 | 1778.2794 | 0.00063352 | 15967527.2425 | 38235478.5327 | 325519.6405 | 779481.9472
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.14346 | 0.0015045 | 4 | 1683865.9269 | 4027999.5946 | 34327.8845 | 82116.22 | 70.7833 | 0 | 254.0138 | 69571.6076 | 1975.2336 | 74858.3768 | 66128.6866 | 0 | 39836.1185 | 0 | 98424.309 | 256079.8625 | 174779.7681 | 781653.9627 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10133698.469 | 24240964.0068 | 2371.3737 | 0.0060181 | 1683865.9269 | 4027999.5946 | 34327.8845 | 82116.22
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3321 | 0.21234 | 0.0030995 | 4 | 837022.2421 | 1974878.6111 | 17063.8306 | 40260.5717 | 73.3822 | 0 | 388.988 | 94157.0978 | 2737.36 | 102207.9357 | 84531.7513 | 0 | 47448.5918 | 0 | 129122.2673 | 335949.6528 | 229292.5411 | 1025447.1979 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10377491.7042 | 24484757.2419 | 3162.2777 | 0.012398 | 837022.2421 | 1974878.6111 | 17063.8306 | 40260.5717
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1297 | 0.29888 | 0.0053491 | 4 | 498191.2348 | 1157517.006 | 10156.3022 | 23597.5498 | 75.2205 | 0 | 83.6981 | 121811.8761 | 3601.0469 | 134137.2145 | 107396.4542 | 0 | 55203.3778 | 0 | 164638.4881 | 428355.5741 | 292361.4812 | 1307505.513 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10659550.0194 | 24766815.5571 | 4216.965 | 0.021397 | 498191.2348 | 1157517.006 | 10156.3022 | 23597.5498
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1702 | 0.41168 | 0.0083808 | 4 | 328166.658 | 748989.0978 | 6690.1212 | 15269.1558 | 76.6114 | 0 | 81.3496 | 154299.304 | 4617.8164 | 173100.2993 | 136371.4484 | 0 | 64054.9644 | 0 | 207653.0947 | 540270.7568 | 368745.893 | 1649113.577 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11001158.0834 | 25108423.6211 | 5623.4133 | 0.033523 | 328166.658 | 748989.0978 | 6690.1212 | 15269.1558
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5922 | 0.56699 | 0.012558 | 4 | 227881.9747 | 508727.646 | 4645.6823 | 10371.1012 | 77.7012 | 0 | 103.1952 | 194925.9771 | 5892.8685 | 223411.4402 | 176807.078 | 0 | 75297.7884 | 0 | 263770.7093 | 686277.2788 | 468398.3444 | 2094781.4845 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11446825.9909 | 25554091.5286 | 7498.9421 | 0.050231 | 227881.9747 | 508727.646 | 4645.6823 | 10371.1012
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1735 | 0.73927 | 0.017963 | 4 | 165713.6112 | 362049.8723 | 3378.2961 | 7380.8764 | 78.3964 | 0 | 82.1189 | 236048.0601 | 7182.0753 | 276080.9387 | 221335.8626 | 0 | 84246.7196 | 0 | 321708.526 | 837019.593 | 571283.0713 | 2554904.8466 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11906949.3529 | 26014214.8906 | 10000 | 0.071853 | 165713.6112 | 362049.8723 | 3378.2961 | 7380.8764
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5339 | 0.99732 | 0.025357 | 4 | 123905.6201 | 262990.6076 | 2525.9837 | 5361.4193 | 79.066 | 0 | 113.5674 | 292598.0869 | 8955.6011 | 350614.6525 | 287223.1116 | 0 | 98815.8831 | 0 | 404900.8607 | 1053468.9829 | 719014.2275 | 3215591.4062 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12567635.9126 | 26674901.4503 | 13335.2143 | 0.10143 | 123905.6201 | 262990.6076 | 2525.9837 | 5361.4193
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2944 | 1.2991 | 0.034904 | 4 | 95240.6557 | 196284.3641 | 1941.6096 | 4001.5223 | 79.5091 | 0 | 92.292 | 353269.375 | 10855.8458 | 433023.6077 | 364536.4729 | 0 | 112031.8602 | 0 | 496749.6931 | 1292440.804 | 882117.4057 | 3945025.0644 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 13297069.5708 | 27404335.1085 | 17782.7941 | 0.13962 | 95240.6557 | 196284.3641 | 1941.6096 | 4001.5223
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7897 | 1.6813 | 0.047337 | 4 | 74887.7592 | 149392.8847 | 1526.6883 | 3045.576 | 79.8505 | 0 | 111.2881 | 424286.9971 | 13077.6476 | 532105.64 | 462438.0117 | 0 | 126785.9263 | 0 | 607890.7468 | 1581607.0278 | 1079479.2952 | 4827671.2925 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 14179715.7989 | 28286981.3366 | 23713.7371 | 0.18935 | 74887.7592 | 149392.8847 | 1526.6883 | 3045.576
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1406 | 2.1574 | 0.063358 | 4 | 60107.0168 | 115771.8154 | 1225.3628 | 2360.1651 | 80.1122 | 0 | 110.9278 | 506303.6278 | 15640.9902 | 649441.7809 | 584641.6808 | 0 | 142758.3788 | 0 | 740526.7188 | 1926698.6194 | 1315011.3974 | 5881023.1941 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 15233067.7004 | 29340333.2382 | 31622.7766 | 0.25343 | 60107.0168 | 115771.8154 | 1225.3628 | 2360.1651
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3681 | 2.7299 | 0.083558 | 4 | 49211.8275 | 91419.6485 | 1003.2497 | 1863.7132 | 80.3097 | 0 | 116.3869 | 598075.4003 | 18506.1095 | 783861.1811 | 731891.964 | 0 | 158790.0693 | 0 | 893538.6424 | 2324804.2577 | 1586726.6758 | 7096194.3001 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 16448238.8065 | 30555504.3442 | 42169.6503 | 0.33423 | 49211.8275 | 91419.6485 | 1003.2497 | 1863.7132
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.046 | 3.2423 | 0.10644 | 4 | 41037.2055 | 74171.2268 | 836.5989 | 1512.0808 | 80.4294 | 0 | 295.496 | 675422.8282 | 20917.8763 | 899416.3893 | 863672.7428 | 0 | 162283.317 | 0 | 1022468.1299 | 2660252.3371 | 1815676.8828 | 8120110.5035 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 17472155.0098 | 31579420.5475 | 56234.1325 | 0.42576 | 41037.2055 | 74171.2268 | 836.5989 | 1512.0808
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.7009 | 4.1906 | 0.13866 | 4 | 34929.858 | 60363.9882 | 712.0924 | 1230.6015 | 80.5767 | 0 | 98.041 | 809652.0524 | 25097.2255 | 1104186.0641 | 1107520.4918 | 0 | 189349.7793 | 0 | 1261964.1891 | 3283371.9556 | 2240968.8262 | 10022110.5841 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 19374155.0904 | 33481420.6281 | 74989.4209 | 0.55466 | 34929.858 | 60363.9882 | 712.0924 | 1230.6015
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.1964 | 5.0119 | 0.17222 | 4 | 30394.2526 | 50873.3626 | 619.6279 | 1037.1223 | 80.66 | 0 | 124.9284 | 918732.7604 | 28488.0827 | 1274066.1918 | 1318706.7025 | 0 | 200539.0366 | 0 | 1458807.7818 | 3795518.6057 | 2590519.4385 | 11585378.5999 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 20937423.1063 | 35044688.644 | 100000 | 0.68886 | 30394.2526 | 50873.3626 | 619.6279 | 1037.1223
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.7823 | 5.8427 | 0.20817 | 4 | 26988.034 | 43930.3642 | 550.1876 | 895.5799 | 80.718 | 0 | 107.2628 | 1023792.6336 | 31748.9939 | 1440328.3283 | 1532388.0425 | 0 | 207725.5205 | 0 | 1652033.5723 | 4298252.4765 | 2933645.6355 | 13119915.2032 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 22471959.7095 | 36579225.2472 | 133352.1432 | 0.83266 | 26988.034 | 43930.3642 | 550.1876 | 895.5799
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.9977 | 6.632 | 0.24441 | 4 | 24437.9578 | 38868.1596 | 498.2008 | 792.38 | 80.7537 | 0 | 125.9626 | 1119524.631 | 34715.4733 | 1593951.8159 | 1735506.7819 | 0 | 210463.763 | 0 | 1830723.3614 | 4763166.6533 | 3250959.1142 | 14539011.5941 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 23891056.1004 | 37998321.6381 | 177827.941 | 0.97762 | 24437.9578 | 38868.1596 | 498.2008 | 792.38
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.4823 | 7.3401 | 0.27884 | 4 | 22534.8629 | 35183.2068 | 459.4037 | 717.2573 | 80.7717 | 0 | 123.0801 | 1202492.8767 | 37281.9728 | 1728678.5506 | 1917871.652 | 0 | 209189.0394 | 0 | 1987250.4957 | 5170418.1487 | 3528916.6279 | 15782099.3638 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 25134143.8702 | 39241409.4079 | 237137.3706 | 1.1153 | 22534.8629 | 35183.2068 | 459.4037 | 717.2573
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0628 | 7.9482 | 0.30993 | 4 | 21117.3985 | 32496.6186 | 430.5067 | 662.4875 | 80.7774 | 0 | 153.496 | 1271784.4993 | 39421.7386 | 1842310.3054 | 2074625.4269 | 0 | 205065.9753 | 0 | 2118951.0988 | 5513076.1024 | 3762787.7223 | 16828022.869 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 26180067.3753 | 40287332.9131 | 316227.766 | 1.2397 | 21117.3985 | 32496.6186 | 430.5067 | 662.4875
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.6844 | 8.4506 | 0.33682 | 4 | 20062.2954 | 30533.3432 | 408.997 | 622.4635 | 80.7756 | 0 | 139.0803 | 1327794.8409 | 41148.641 | 1934900.8092 | 2204282.6647 | 0 | 199240.1705 | 0 | 2225873.1793 | 5791265.4231 | 3952657.6499 | 17677163.3786 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 27029207.8849 | 41136473.4226 | 421696.5034 | 1.3473 | 20062.2954 | 30533.3432 | 408.997 | 622.4635
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.4381 | 8.8578 | 0.35934 | 4 | 19276.641 | 29091.2168 | 392.9804 | 593.0638 | 80.77 | 0 | 135.7512 | 1372419.7071 | 42522.6071 | 2009143.8061 | 2309471.1241 | 0 | 192917.4203 | 0 | 2311325.1192 | 6013593.8423 | 4104401.3644 | 18355794.9906 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 27707839.4969 | 41815105.0346 | 562341.3252 | 1.4374 | 19276.641 | 29091.2168 | 392.9804 | 593.0638
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3929 | 9.1777 | 0.37764 | 4 | 18691.1131 | 28030.1551 | 381.0436 | 571.4326 | 80.7631 | 0 | 136.2589 | 1407021.4528 | 43586.7329 | 2067001.6267 | 2392187.846 | 0 | 186625.2853 | 0 | 2377604.948 | 6186040.3609 | 4222099.6568 | 18882167.9094 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28234212.4158 | 42341477.9535 | 749894.2093 | 1.5106 | 18691.1131 | 28030.1551 | 381.0436 | 571.4326
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6929 | 9.4263 | 0.39222 | 4 | 18254.2764 | 27246.1056 | 372.1381 | 555.4487 | 80.7563 | 0 | 114.5216 | 1433645.0324 | 44404.7318 | 2111692.5684 | 2456520.8017 | 0 | 180885.5825 | 0 | 2428587.9995 | 6318687.8029 | 4312634.2615 | 19287058.7806 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28639103.2869 | 42746368.8247 | 1000000 | 1.5689 | 18254.2764 | 27246.1056 | 372.1381 | 555.4487
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4808 | 9.6194 | 0.40371 | 4 | 17928.039 | 26663.9752 | 365.4873 | 543.5812 | 80.7501 | 0 | 138.1802 | 1454156.8591 | 45034.4768 | 2146227.4984 | 2506494.7461 | 0 | 175992.2977 | 0 | 2467883.2924 | 6420926.0944 | 4382413.9963 | 19599129.2611 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28951173.7675 | 43058439.3052 | 1333521.4322 | 1.6149 | 17928.039 | 26663.9752 | 365.4873 | 543.5812
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.8445 | 9.7664 | 0.41262 | 4 | 17684.1806 | 26231.5876 | 360.5159 | 534.7664 | 80.7449 | 0 | 150.6992 | 1469695.4285 | 45511.2538 | 2172449.2425 | 2544589.8922 | 0 | 171886.0094 | 0 | 2497611.4123 | 6498272.5643 | 4435204.5513 | 19835220.3543 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29187264.8607 | 43294530.3984 | 1778279.41 | 1.6505 | 17684.1806 | 26231.5876 | 360.5159 | 534.7664
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.8728 | 9.8773 | 0.41944 | 4 | 17501.7646 | 25910.0948 | 356.7971 | 528.2123 | 80.7407 | 0 | 140.5665 | 1481352.8434 | 45868.7813 | 2192155.5495 | 2573304.6724 | 0 | 168505.4803 | 0 | 2519863.0575 | 6556166.7807 | 4474718.5436 | 20011935.7087 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29363980.215 | 43471245.7527 | 2371373.7057 | 1.6778 | 17501.7646 | 25910.0948 | 356.7971 | 528.2123
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.6498 | 9.9609 | 0.42465 | 4 | 17365.2298 | 25670.3985 | 354.0137 | 523.3258 | 80.7373 | 0 | 126.9407 | 1490127.2713 | 46137.7959 | 2207007.6389 | 2594994.4122 | 0 | 165803.6656 | 0 | 2536587.6057 | 6599680.6244 | 4504417.636 | 20144756.6499 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29496801.1563 | 43604066.694 | 3162277.6602 | 1.6986 | 17365.2298 | 25670.3985 | 354.0137 | 523.3258
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.254 | 10.026 | 0.42866 | 4 | 17262.9891 | 25490.4396 | 351.9294 | 519.6571 | 80.7346 | 0 | 139.9815 | 1496929.9779 | 46346.3041 | 2218533.7186 | 2611855.3848 | 0 | 163765.5434 | 0 | 2549598.0622 | 6633531.1634 | 4527521.3244 | 20248081.4788 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29600125.9851 | 43707391.5228 | 4216965.0343 | 1.7147 | 17262.9891 | 25490.4396 | 351.9294 | 519.6571
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7 | 10.074 | 0.43168 | 4 | 17186.4019 | 25356.4254 | 350.368 | 516.925 | 80.7326 | 0 | 141.2915 | 1501940.8987 | 46499.8613 | 2227030.3209 | 2624300.5934 | 0 | 162137.3895 | 0 | 2559144.5349 | 6658369.127 | 4544473.745 | 20323896.4707 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29675940.977 | 43783206.5148 | 5623413.2519 | 1.7267 | 17186.4019 | 25356.4254 | 350.368 | 516.925
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.0387 | 10.1104 | 0.43396 | 4 | 17129.0161 | 25256.0068 | 349.1982 | 514.8779 | 80.731 | 0 | 150.1057 | 1505740.0472 | 46616.2666 | 2233475.8449 | 2633750.5257 | 0 | 160898.3799 | 0 | 2566387.6151 | 6677214.1359 | 4557335.8508 | 20381418.6661 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29733463.1724 | 43840728.7102 | 7498942.0933 | 1.7359 | 17129.0161 | 25256.0068 | 349.1982 | 514.8779
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.2823 | 10.1366 | 0.43566 | 4 | 17086.0091 | 25181.4327 | 348.3214 | 513.3576 | 80.7299 | 0 | 132.3164 | 1508468.4575 | 46699.855 | 2238106.7254 | 2640544.7611 | 0 | 159897.8021 | 0 | 2571549.8644 | 6690645.2499 | 4566502.862 | 20422415.5775 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29774460.0838 | 43881725.6215 | 10000000 | 1.7426 | 17086.0091 | 25181.4327 | 348.3214 | 513.3576
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.7112 | [19 empty] | 100 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.8873 | [19 empty] | 133.3521 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7534 | [19 empty] | 177.8279 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2491 | [19 empty] | 237.1374 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.405 | [19 empty] | 316.2278 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5024 | [19 empty] | 421.6965 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1784 | [19 empty] | 562.3413 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5846 | [19 empty] | 749.8942 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.952 | [19 empty] | 1000 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5141 | [19 empty] | 1333.5214 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.14012 | 0.00085807 | 4 | 3059111.8128 | 7317913.8386 | 62364.1321 | 149185.5718 | 71.9225 | 0 | 33.6736 | 69458.6148 | 1987.9605 | 73385.6016 | 64619.5594 | 0 | 43450.093 | 0 | 98631.7134 | 256619.4862 | 175148.0723 | 783301.1012 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10499692.5711 | 25117043.8578 | 1778.2794 | 0.0034323 | 3059111.8128 | 7317913.8386 | 62364.1321 | 149185.5718
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9626 | 0.1809 | 0.0023497 | 4 | 1132016.1469 | 2687250.7906 | 23077.6803 | 54783.2421 | 73.8452 | 0 | 309.2471 | 84790.2637 | 2468.8619 | 89871.1823 | 75317.6281 | 0 | 45625.9984 | 0 | 116248.8344 | 302455.6212 | 206432.1763 | 923210.5663 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10639602.0362 | 25256953.323 | 2371.3737 | 0.0093988 | 1132016.1469 | 2687250.7906 | 23077.6803 | 54783.2421
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6452 | 0.25826 | 0.0043954 | 4 | 619960.5497 | 1451368.92 | 12638.7344 | 29588.1186 | 76.1444 | 0 | 68.756 | 111247.4255 | 3304.8586 | 119250.8087 | 95047.5682 | 0 | 53231.0453 | 0 | 149011.8654 | 387698.3074 | 264612.0612 | 1183403.9403 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10899795.4102 | 25517146.6969 | 3162.2777 | 0.017581 | 619960.5497 | 1451368.92 | 12638.7344 | 29588.1186
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6024 | 0.36781 | 0.0072793 | 4 | 386185.8834 | 888202.669 | 7872.9216 | 18107.2128 | 77.9844 | 0 | 95.265 | 144918.2854 | 4375.5534 | 157994.4962 | 122901.2962 | 0 | 63241.6395 | 0 | 192438.1956 | 500684.7104 | 341727.6029 | 1528281.7795 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11244673.2495 | 25862024.5362 | 4216.965 | 0.029117 | 386185.8834 | 888202.669 | 7872.9216 | 18107.2128
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.49899 | 0.01112 | 4 | 261370.4365 | 590005.8977 | 5328.3899 | 12028.0683 | 79.2541 | 0 | 65.8643 | 181275.8411 | 5532.7643 | 201452.2176 | 155361.0115 | 0 | 72757.7808 | 0 | 240388.05 | 625440.3957 | 426875.9216 | 1909083.9827 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11625475.4526 | 26242826.7394 | 5623.4133 | 0.044479 | 261370.4365 | 590005.8977 | 5328.3899 | 12028.0683
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2696 | 0.67349 | 0.016317 | 4 | 185468.7903 | 409429.2911 | 3781.0322 | 8346.7699 | 80.2341 | 0 | 111.767 | 225388.2636 | 6938.5762 | 255867.41 | 198843.0332 | 0 | 84194.5278 | 0 | 300780.4062 | 782568.9184 | 534119.367 | 2388700.5025 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12105091.9724 | 26722443.2591 | 7498.9421 | 0.065268 | 185468.7903 | 409429.2911 | 3781.0322 | 8346.7699
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0601 | 0.87883 | 0.023084 | 4 | 136860.6662 | 295165.1498 | 2790.0898 | 6017.3408 | 80.8764 | 0 | 111.2455 | 272956.638 | 8453.31 | 316399.3208 | 250567.1718 | 0 | 94685.9491 | 0 | 367794.332 | 956925.4068 | 653121.253 | 2920903.3813 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12637294.8513 | 27254646.138 | 10000 | 0.092337 | 136860.6662 | 295165.1498 | 2790.0898 | 6017.3408
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6741 | 1.1812 | 0.032474 | 4 | 103051.9405 | 215582.7296 | 2100.8532 | 4394.9455 | 81.5531 | 0 | 89.4315 | 337481.9549 | 10511.6326 | 400623.7729 | 325360.4404 | 0 | 110843.1408 | 0 | 462080.1672 | 1202237.8094 | 820552.0084 | 3669690.9266 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 13386082.3966 | 28003433.6833 | 13335.2143 | 0.1299 | 103051.9405 | 215582.7296 | 2100.8532 | 4394.9455
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7681 | 1.5376 | 0.044425 | 4 | 80020.766 | 162278.8432 | 1631.3316 | 3308.2737 | 81.9793 | 0 | 90.1961 | 407171.3266 | 12727.9594 | 494545.5752 | 413566.6064 | 0 | 125982.2071 | 0 | 567057.5332 | 1475367.3818 | 1006968.5538 | 4503387.1435 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 14219778.6135 | 28837129.9002 | 17782.7941 | 0.1777 | 80020.766 | 162278.8432 | 1631.3316 | 3308.2737
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6534 | 1.9854 | 0.059951 | 4 | 63473.5405 | 124429.1259 | 1293.994 | 2536.656 | 82.3059 | 0 | 98.177 | 488200.1188 | 15302.3642 | 606607.4663 | 524620.9072 | 0 | 142577.2009 | 0 | 693150.1424 | 1803434.4858 | 1230881.0934 | 5504773.779 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 15221165.2489 | 29838516.5356 | 23713.7371 | 0.2398 | 63473.5405 | 124429.1259 | 1293.994 | 2536.656
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4038 | 2.5332 | 0.079756 | 4 | 51384.561 | 97203.4195 | 1047.5438 | 1981.6232 | 82.5535 | 0 | 120.6471 | 580173.0733 | 18220.3631 | 737006.8689 | 660434.8765 | 0 | 159802.5839 | 0 | 840698.7286 | 2187325.6408 | 1492894.6949 | 6676556.83 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 16392948.3 | 31010299.5867 | 31622.7766 | 0.31902 | 51384.561 | 97203.4195 | 1047.5438 | 1981.6232
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0944 | 3.1895 | 0.10453 | 4 | 42428.5678 | 77388.3845 | 864.9637 | 1577.6669 | 82.7417 | 0 | 107.2316 | 682868.6452 | 21473.7065 | 886032.7848 | 823136.3485 | 0 | 177101.0352 | 0 | 1010338.8829 | 2628694.5243 | 1794138.0271 | 8023783.9544 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 17740175.4244 | 32357526.7111 | 42169.6503 | 0.41812 | 42428.5678 | 77388.3845 | 864.9637 | 1577.6669
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.7102 | 3.9527 | 0.13468 | 4 | 35728.5863 | 62861.964 | 728.3756 | 1281.5262 | 82.8849 | 0 | 109.5701 | 794680.6536 | 25010.5263 | 1051811.1579 | 1012308.1441 | 0 | 193557.478 | 0 | 1200173.5043 | 3122605.2688 | 2131242.2591 | 9531388.9921 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 19247780.462 | 33865131.7488 | 56234.1325 | 0.53872 | 35728.5863 | 62861.964 | 728.3756 | 1281.5262
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.441 | 4.4985 | 0.16498 | 4 | 30680.4157 | 52830.0274 | 625.4618 | 1077.0116 | 82.9586 | 0 | 531.5919 | 870727.7213 | 27413.0571 | 1166413.9792 | 1147583.1777 | 0 | 187891.7275 | 0 | 1326011.5685 | 3450010.0988 | 2354702.7831 | 10530754.1131 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 20247145.5831 | 34864496.8698 | 74989.4209 | 0.65994 | 30680.4157 | 52830.0274 | 625.4618 | 1077.0116
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.213 | 5.7419 | 0.2107 | 4 | 26821.4715 | 44165.3678 | 546.792 | 900.3708 | 83.0735 | 0 | 119.4434 | 1034580.2886 | 32582.7816 | 1417749.468 | 1456402.7633 | 0 | 219988.7376 | 0 | 1622908.5752 | 4222475.2085 | 2881926.093 | 12888613.9158 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 22605005.3857 | 37222356.6724 | 100000 | 0.8428 | 26821.4715 | 44165.3678 | 546.792 | 900.3708
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.9427 | 6.6335 | 0.25222 | 4 | 23988.7558 | 38477.1758 | 489.0432 | 784.4093 | 83.1241 | 0 | 129.8861 | 1145591.7547 | 36078.5606 | 1591219.3424 | 1678127.278 | 0 | 225977.6732 | 0 | 1824027.8975 | 4745746.4297 | 3239069.4536 | 14485838.3898 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 24202229.8597 | 38819581.1465 | 133352.1432 | 1.0089 | 23988.7558 | 38477.1758 | 489.0432 | 784.4093
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.1434 | 7.4627 | 0.29321 | 4 | 21869.0947 | 34332.4648 | 445.8311 | 699.9137 | 83.1522 | 0 | 147.4711 | 1244842.105 | 39198.0524 | 1748394.5356 | 1884445.4993 | 0 | 227105.5286 | 0 | 2006154.4312 | 5219602.3111 | 3562485.8294 | 15932228.2928 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 25648619.7627 | 40265971.0494 | 177827.941 | 1.1728 | 21869.0947 | 34332.4648 | 445.8311 | 699.9137
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.5313 | 8.1965 | 0.33148 | 4 | 20287.5338 | 31311.8305 | 413.5888 | 638.334 | 83.1631 | 0 | 129.1195 | 1329893.062 | 41865.995 | 1884618.7452 | 2067203.4482 | 0 | 224328.839 | 0 | 2163684.9349 | 5629464.3677 | 3842225.1049 | 17183284.497 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 26899675.9669 | 41517027.2536 | 237137.3706 | 1.3259 | 20287.5338 | 31311.8305 | 413.5888 | 638.334
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9487 | 8.8172 | 0.36549 | 4 | 19109.2518 | 29107.7696 | 389.5679 | 593.4013 | 83.1629 | 0 | 125.1832 | 1399991.8205 | 44060.7338 | 1997955.2824 | 2221930.4097 | 0 | 218826.3503 | 0 | 2294278.1927 | 5969241.2362 | 4074129.7993 | 18220413.8247 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 27936805.2947 | 42554156.5814 | 316227.766 | 1.462 | 19109.2518 | 29107.7696 | 389.5679 | 593.4013
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.3649 | 9.3219 | 0.39529 | 4 | 18189.1202 | 27433.731 | 370.8098 | 559.2737 | 83.1567 | 0 | 149.0918 | 1455844.1679 | 45806.4434 | 2088945.9338 | 2347855.7519 | 0 | 210155.7199 | 0 | 2397957.1266 | 6238992.5548 | 4258240.6171 | 19043798.3154 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 28760189.7854 | 43377541.0721 | 421696.5034 | 1.5812 | 18189.1202 | 27433.731 | 370.8098 | 559.2737
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.9756 | 9.7336 | 0.41861 | 4 | 17577.6826 | 26307.3972 | 358.3448 | 536.3119 | 83.1477 | 0 | 130.0588 | 1500684.6768 | 47205.8881 | 2162441.979 | 2450654.2388 | 0 | 204755.6399 | 0 | 2482639.5448 | 6459318.8361 | 4408617.8314 | 19716318.6348 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 29432710.1047 | 44050061.3914 | 562341.3252 | 1.6744 | 17577.6826 | 26307.3972 | 358.3448 | 536.3119
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.777 | 10.0524 | 0.43801 | 4 | 17089.9074 | 25432.8611 | 348.4009 | 518.4833 | 83.1384 | 0 | 145.0766 | 1534983.8687 | 48275.0297 | 2218928.8409 | 2530309.6049 | 0 | 197850.4035 | 0 | 2546835.6216 | 6626343.8595 | 4522615.8419 | 20226143.0705 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 29942534.5405 | 44559885.8272 | 749894.2093 | 1.7521 | 17089.9074 | 25432.8611 | 348.4009 | 518.4833
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.9714 | 10.3016 | 0.45346 | 4 | 16725.7364 | 24784.5408 | 340.9768 | 505.2664 | 83.1298 | 0 | 128.1973 | 1561558.7009 | 49102.575 | 2262855.8042 | 2592637.9656 | 0 | 191793.486 | 0 | 2596599.9273 | 6755820.375 | 4610986.2242 | 20621355.0581 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30337746.528 | 44955097.8147 | 1000000 | 1.8138 | 16725.7364 | 24784.5408 | 340.9768 | 505.2664
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.6427 | 10.4912 | 0.46548 | 4 | 16453.5977 | 24304.2179 | 335.4288 | 495.4744 | 83.1224 | 0 | 143.3512 | 1581631.0777 | 49727.1425 | 2296128.3582 | 2640070.6097 | 0 | 186540.1715 | 0 | 2634097.9703 | 6853382.5908 | 4677574.4412 | 20919152.3619 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30635543.8319 | 45252895.1186 | 1333521.4322 | 1.8619 | 16453.5977 | 24304.2179 | 335.4288 | 495.4744
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.9339 | 10.6375 | 0.47483 | 4 | 16250.0734 | 23946.1338 | 331.2797 | 488.1743 | 83.1163 | 0 | 125.6788 | 1597038.7252 | 50206.2707 | 2321723.5379 | 2676687.874 | 0 | 182278.4094 | 0 | 2662894.5787 | 6928305.459 | 4728710.8382 | 21147845.6932 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30864237.1631 | 45481588.4498 | 1778279.41 | 1.8993 | 16250.0734 | 23946.1338 | 331.2797 | 488.1743
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9083 | 10.7479 | 0.48199 | 4 | 16097.7666 | 23679.5932 | 328.1747 | 482.7405 | 83.1114 | 0 | 134.3728 | 1608610.6382 | 50565.9496 | 2340978.3423 | 2704308.1747 | 0 | 178806.4871 | 0 | 2684475.1409 | 6984453.6551 | 4767033.1357 | 21319231.5237 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31035622.9937 | 45652974.2804 | 2371373.7057 | 1.9279 | 16097.7666 | 23679.5932 | 328.1747 | 482.7405
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6512 | 10.8319 | 0.48746 | 4 | 15983.7313 | 23480.4024 | 325.85 | 478.6798 | 83.1075 | 0 | 127.9361 | 1617400.8627 | 50839.0691 | 2355622.7519 | 2725357.2909 | 0 | 176082.2835 | 0 | 2700867.8806 | 7027104.2012 | 4796143.0099 | 21449417.3498 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31165808.8197 | 45783160.1065 | 3162277.6602 | 1.9498 | 15983.7313 | 23480.4024 | 325.85 | 478.6798
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1971 | 10.8937 | 0.49157 | 4 | 15898.3176 | 23332.2946 | 324.1087 | 475.6604 | 83.1046 | 0 | 137.2388 | 1623841.5083 | 51039.1303 | 2366362.7648 | 2740817.5851 | 0 | 173877.041 | 0 | 2712815.8315 | 7058190.3185 | 4817359.9237 | 21544304.1031 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31260695.5731 | 45878046.8598 | 4216965.0343 | 1.9663 | 15898.3176 | 23332.2946 | 324.1087 | 475.6604
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.6233 | 10.9419 | 0.49473 | 4 | 15834.3231 | 23220.8224 | 322.8041 | 473.3879 | 83.1023 | 0 | 156.9348 | 1628860.0644 | 51194.986 | 2374737.2263 | 2752886.2133 | 0 | 172245.9301 | 0 | 2722170.5238 | 7082529.309 | 4833971.7848 | 21618596.0375 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31334987.5075 | 45952338.7942 | 5623413.2519 | 1.9789 | 15834.3231 | 23220.8224 | 322.8041 | 473.3879
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.9398 | 10.9776 | 0.49711 | 4 | 15786.3659 | 23137.6036 | 321.8264 | 471.6913 | 83.1005 | 0 | 136.6572 | 1632581.8015 | 51310.5494 | 2380951.0031 | 2761848.7021 | 0 | 170972.1887 | 0 | 2729089.0555 | 7100529.9093 | 4846257.5644 | 21673540.774 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31389932.2439 | 46007283.5307 | 7498942.0933 | 1.9884 | 15786.3659 | 23137.6036 | 321.8264 | 471.6913
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1787 | 11.0046 | 0.4989 | 4 | 15750.4209 | 23075.253 | 321.0936 | 470.4202 | 83.0991 | 0 | 117.5913 | 1635387.6824 | 51397.6643 | 2385637.5413 | 2768612.6839 | 0 | 170004.4696 | 0 | 2734305.6162 | 7114102.33 | 4855521.0204 | 21714969.008 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31431360.478 | 46048711.7647 | 10000000 | 1.9956 | 15750.4209 | 23075.253 | 321.0936 | 470.4202
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.2094 | [19 empty] | 100 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.869 | [19 empty] | 133.3521 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9356 | [19 empty] | 177.8279 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0571 | [19 empty] | 237.1374 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6499 | [19 empty] | 316.2278 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3669 | [19 empty] | 421.6965 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8865 | [19 empty] | 562.3413 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1694 | [19 empty] | 749.8942 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9323 | [19 empty] | 1000 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2707 | [19 empty] | 1333.5214 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.14781 | 0.0015734 | 4 | 1731135.9262 | 4136030.0389 | 35291.5474 | 84318.5667 | 73.636 | 0 | 244.5099 | 73604.7625 | 2134.712 | 76476.1509 | 66042.458 | 0 | 42819.0859 | 0 | 101820.096 | 264915.0037 | 180809.9335 | 808622.2026 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 10895220.727 | 26030861.8899 | 1778.2794 | 0.0062937 | 1731135.9262 | 4136030.0389 | 35291.5474 | 84318.5667
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.21896 | 0.0033923 | 4 | 821395.4845 | 1936849.2322 | 16745.258 | 39485.2914 | 76.6626 | 0 | 346.5384 | 99827.5881 | 2970.9378 | 104455.8387 | 83756.2322 | 0 | 50890.0729 | 0 | 133341.2611 | 346926.6094 | 236784.5395 | 1058953.0796 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11145551.604 | 26281192.767 | 2371.3737 | 0.013569 | 821395.4845 | 1936849.2322 | 16745.258 | 39485.2914
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9982 | 0.3125 | 0.0059935 | 4 | 477556.3635 | 1108892.0293 | 9735.6324 | 22606.2639 | 78.9046 | 0 | 75.6693 | 130681.1962 | 3964.1002 | 138580.3309 | 106747.6857 | 0 | 59880.1326 | 0 | 171542.8438 | 446319.2912 | 304622.0872 | 1362337.6677 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11448936.1921 | 26584577.355 | 3162.2777 | 0.023974 | 477556.3635 | 1108892.0293 | 9735.6324 | 22606.2639
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0823 | 0.44292 | 0.0096048 | 4 | 308277.2305 | 702236.2126 | 6284.6483 | 14316.035 | 80.6632 | 0 | 102.1181 | 169315.1011 | 5213.3109 | 182915.2033 | 138484.5913 | 0 | 71415.3664 | 0 | 221263.9935 | 575683.5236 | 392915.834 | 1757206.9241 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11843805.4485 | 26979446.6114 | 4216.965 | 0.038419 | 308277.2305 | 702236.2126 | 6284.6483 | 14316.035
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3292 | 0.5933 | 0.014428 | 4 | 212514.3641 | 474773.5857 | 4332.3928 | 9678.9017 | 81.834 | 0 | 93.5561 | 209686.5857 | 6520.3156 | 230890.1961 | 174721.4394 | 0 | 81430.7682 | 0 | 274267.229 | 713587.0699 | 487037.838 | 2178141.442 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12264739.9664 | 27400381.1294 | 5623.4133 | 0.057713 | 212514.3641 | 474773.5857 | 4332.3928 | 9678.9017
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9734 | 0.79158 | 0.020845 | 4 | 153392.5663 | 334914.4684 | 3127.1149 | 6827.6844 | 82.7354 | 0 | 108.554 | 258334.4399 | 8094.6989 | 290580.4091 | 222406.082 | 0 | 93475.489 | 0 | 340427.5364 | 885722.6184 | 604523.8868 | 2703565.1606 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12790163.6849 | 27925804.8479 | 7498.9421 | 0.083382 | 153392.5663 | 334914.4684 | 3127.1149 | 6827.6844
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3977 | 1.0863 | 0.029776 | 4 | 113671.4575 | 240748.5966 | 2317.3464 | 4907.9858 | 83.5454 | 0 | 108.9312 | 324515.1286 | 10241.1182 | 374055.2412 | 294012.5712 | 0 | 111823.5858 | 0 | 434712.5816 | 1131032.9654 | 771953.2393 | 3452346.4313 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 13538944.9556 | 28674586.1186 | 10000 | 0.11911 | 113671.4575 | 240748.5966 | 2317.3464 | 4907.9858
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9434 | 1.396 | 0.04115 | 4 | 86714.9753 | 178669.7733 | 1767.8021 | 3642.425 | 84.0376 | 0 | 111.9344 | 388354.6833 | 12309.4171 | 456979.7157 | 369495.8243 | 0 | 124565.8092 | 0 | 527165.1253 | 1371575.5197 | 936128.4752 | 4186574.5698 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 14273173.0942 | 29408814.2572 | 13335.2143 | 0.1646 | 86714.9753 | 178669.7733 | 1767.8021 | 3642.425
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.3876 | 1.8139 | 0.056028 | 4 | 67920.3678 | 135456.4479 | 1384.6486 | 2761.4629 | 84.4455 | 0 | 113.0085 | 467915.3264 | 14880.1358 | 563314.2649 | 470196.8198 | 0 | 141667.5089 | 0 | 646609.8818 | 1682346.2744 | 1148235.9011 | 5135166.113 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 15221764.6374 | 30357405.8004 | 17782.7941 | 0.22411 | 67920.3678 | 135456.4479 | 1384.6486 | 2761.4629
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6413 | 2.3303 | 0.075188 | 4 | 54332.0534 | 104657.9985 | 1107.6324 | 2133.5949 | 84.7545 | 0 | 97.7125 | 558940.5345 | 17816.9854 | 688139.6571 | 594575.9095 | 0 | 159699.2338 | 0 | 787477.2049 | 2048854.1534 | 1398385.0594 | 6253888.7381 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 16340487.2624 | 31476128.4254 | 23713.7371 | 0.30075 | 54332.0534 | 104657.9985 | 1107.6324 | 2133.5949
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8151 | 2.9585 | 0.099483 | 4 | 44338.4774 | 82374.1534 | 903.8998 | 1679.3085 | 84.9897 | 0 | 112.2197 | 661893.3056 | 21133.5039 | 832771.0669 | 745867.8973 | 0 | 178280.9536 | 0 | 951579.2236 | 2475813.9441 | 1689793.8897 | 7557133.7847 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 17643732.309 | 32779373.472 | 31622.7766 | 0.39793 | 44338.4774 | 82374.1534 | 903.8998 | 1679.3085
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9908 | 3.7086 | 0.12969 | 4 | 36893.315 | 66069.8128 | 752.1201 | 1346.9225 | 85.1697 | 0 | 88.3596 | 776654.2558 | 24824.8971 | 997644.2831 | 926606.0067 | 0 | 196933.9061 | 0 | 1139838.706 | 2965626.5001 | 2024101.0238 | 9052229.5788 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 19138828.1031 | 34274469.2661 | 42169.6503 | 0.51876 | 36893.315 | 66069.8128 | 752.1201 | 1346.9225
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.0749 | 4.5692 | 0.16604 | 4 | 31303.0663 | 54092.2931 | 638.1553 | 1102.7446 | 85.3061 | 0 | 104.1755 | 900145.389 | 28790.7683 | 1178788.5993 | 1133950.3818 | 0 | 214152.6412 | 0 | 1347772.834 | 3506628.448 | 2393345.9697 | 10703575.0314 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 20790173.5557 | 35925814.7187 | 56234.1325 | 0.66416 | 31303.0663 | 54092.2931 | 638.1553 | 1102.7446
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.846 | 5.5134 | 0.20801 | 4 | 27088.669 | 45279.3271 | 552.2392 | 923.0803 | 85.4077 | 0 | 132.0517 | 1027942.3942 | 32888.3017 | 1369813.1197 | 1361406.0465 | 0 | 228506.7703 | 0 | 1568017.0867 | 4079658.8149 | 2784450.9698 | 12452683.5038 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 22539282.0282 | 37674923.1912 | 74989.4209 | 0.83206 | 27088.669 | 45279.3271 | 552.2392 | 923.0803
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.8944 | 6.4907 | 0.25398 | 4 | 23912.1607 | 38810.7526 | 487.4817 | 791.2097 | 85.4787 | 0 | 121.6604 | 1153567.0369 | 36909.2605 | 1560774.5832 | 1596941.0964 | 0 | 238460.1864 | 0 | 1788794.3437 | 4654075.9502 | 3176502.4677 | 14206024.9249 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 24292623.4493 | 39428264.6123 | 100000 | 1.0159 | 23912.1607 | 38810.7526 | 487.4817 | 791.2097
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.0307 | 7.4775 | 0.30274 | 4 | 21482.0774 | 33980.9181 | 437.9412 | 692.747 | 85.5234 | 0 | 124.0809 | 1274775.791 | 40781.3429 | 1747818.35 | 1834947.5833 | 0 | 244108.6554 | 0 | 2005548.3718 | 5218025.469 | 3561409.6023 | 15927415.1658 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 26014013.6902 | 41149654.8532 | 133352.1432 | 1.211 | 21482.0774 | 33980.9181 | 437.9412 | 692.747
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.2191 | 8.3475 | 0.34869 | 4 | 19710.0933 | 30561.945 | 401.8169 | 623.0466 | 85.5433 | 0 | 130.5423 | 1377654.9931 | 44060.9612 | 1908656.0029 | 2045074.8987 | 0 | 243754.7338 | 0 | 2191488.62 | 5701803.8532 | 3891598.2901 | 17404092.3531 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 27490690.8775 | 42626332.0405 | 177827.941 | 1.3948 | 19710.0933 | 30561.945 | 401.8169 | 623.0466
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.4749 | 9.1026 | 0.39081 | 4 | 18387.2459 | 28069.3975 | 374.8489 | 572.2326 | 85.547 | 0 | 120.1679 | 1464297.3347 | 46817.2392 | 2045569.7762 | 2227782.5518 | 0 | 239352.8059 | 0 | 2349289.6861 | 6112369.8576 | 4171818.0244 | 18657297.276 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 28743895.8003 | 43879536.9633 | 237137.3706 | 1.5633 | 18387.2459 | 28069.3975 | 374.8489 | 572.2326
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.742 | 9.7366 | 0.4278 | 4 | 17400.954 | 26245.9733 | 354.742 | 535.0597 | 85.5409 | 0 | 120.7926 | 1535316.8793 | 49072.1203 | 2158789.7387 | 2381471.4714 | 0 | 232595.0573 | 0 | 2479325.6542 | 6450696.7725 | 4402733.0958 | 19690000.7895 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 29776599.3138 | 44912240.4768 | 316227.766 | 1.7112 | 17400.954 | 26245.9733 | 354.742 | 535.0597
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.0339 | 10.2519 | 0.45906 | 4 | 16665.7018 | 24908.3698 | 339.7529 | 507.7908 | 85.5301 | 0 | 119.5993 | 1591959.4647 | 50867.4224 | 2249733.6286 | 2506599.1735 | 0 | 224734.9165 | 0 | 2583318.8962 | 6721265.8564 | 4587402.0552 | 20515881.4134 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 30602479.9378 | 45738121.1007 | 421696.5034 | 1.8363 | 16665.7018 | 24908.3698 | 339.7529 | 507.7908
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4445 | 10.6604 | 0.4847 | 4 | 16117.3055 | 23924.0148 | 328.5731 | 487.7234 | 85.518 | 0 | 104.2657 | 1636217.6914 | 52268.147 | 2321193.2521 | 2605955.9385 | 0 | 216746.7505 | 0 | 2664628.894 | 6932817.7916 | 4731790.598 | 21161619.0631 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 31248217.5875 | 46383858.7504 | 562341.3252 | 1.9388 | 16117.3055 | 23924.0148 | 328.5731 | 487.7234
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.124 | 10.9808 | 0.5053 | 4 | 15707.9431 | 23196.3583 | 320.2277 | 472.8891 | 85.5064 | 0 | 147.4824 | 1670535.3627 | 53352.9622 | 2376845.5608 | 2683961.9687 | 0 | 209376.0862 | 0 | 2727688.0568 | 7096884.7982 | 4843769.7011 | 21662414.4968 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 31749013.0212 | 46884654.1841 | 749894.2093 | 2.0212 | 15707.9431 | 23196.3583 | 320.2277 | 472.8891
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.1897 | 11.2273 | 0.52153 | 4 | 15402.0997 | 22657.4861 | 313.9926 | 461.9035 | 85.4961 | 0 | 137.4011 | 1696727.778 | 54180.136 | 2419464.7672 | 2744069.7332 | 0 | 202863.9475 | 0 | 2775749.4811 | 7221930.7654 | 4929116.1432 | 22044102.7516 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32130701.2759 | 47266342.4389 | 1000000 | 2.0861 | 15402.0997 | 22657.4861 | 313.9926 | 461.9035
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7903 | 11.4181 | 0.53423 | 4 | 15173.4156 | 22256.3635 | 309.3306 | 453.7261 | 85.4875 | 0 | 140.2976 | 1716867.4883 | 54815.681 | 2452320.1075 | 2790625.2984 | 0 | 197459.3665 | 0 | 2812714.2972 | 7318105.6344 | 4994757.4675 | 22337665.3407 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32424263.8651 | 47559905.0281 | 1333521.4322 | 2.1369 | 15173.4156 | 22256.3635 | 309.3306 | 453.7261
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.9935 | 11.5614 | 0.54396 | 4 | 15002.3103 | 21958.4813 | 305.8424 | 447.6533 | 85.4806 | 0 | 123.0188 | 1731917.7892 | 55290.3419 | 2476921.098 | 2825608.7041 | 0 | 192940.0111 | 0 | 2840244.3983 | 7389733.3101 | 5043644.828 | 22556300.4808 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32642899.0051 | 47778540.1681 | 1778279.41 | 2.1759 | 15002.3103 | 21958.4813 | 305.8424 | 447.6533
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.9144 | 11.671 | 0.55145 | 4 | 14874.2177 | 21735.9717 | 303.231 | 443.1172 | 85.475 | 0 | 137.1015 | 1743386.3797 | 55651.8794 | 2495695.3225 | 2852377.6468 | 0 | 189361.4316 | 0 | 2861224.3374 | 7444318.8081 | 5080900.552 | 22722916.3575 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32809514.8818 | 47945156.0448 | 2371373.7057 | 2.2058 | 14874.2177 | 21735.9717 | 303.231 | 443.1172
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.613 | 11.754 | 0.55716 | 4 | 14778.285 | 21569.7258 | 301.2753 | 439.728 | 85.4707 | 0 | 143.4799 | 1752056.876 | 55925.1151 | 2509905.0594 | 2872679.4296 | 0 | 186550.1307 | 0 | 2877075.4782 | 7485560.2249 | 5109048.6664 | 22848800.9803 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32935399.5047 | 48071040.6677 | 3162277.6602 | 2.2286 | 14778.285 | 21569.7258 | 301.2753 | 439.728
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.142 | 11.8169 | 0.5615 | 4 | 14706.4149 | 21445.379 | 299.8102 | 437.1931 | 85.4674 | 0 | 144.9255 | 1758606.0298 | 56131.4461 | 2520647.3764 | 2888050.683 | 0 | 184369.8955 | 0 | 2889044.118 | 7516700.1706 | 5130302.3192 | 22943852.0386 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33030450.563 | 48166091.726 | 4216965.0343 | 2.246 | 14706.4149 | 21445.379 | 299.8102 | 437.1931
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5339 | 11.8635 | 0.56476 | 4 | 14652.5589 | 21352.6364 | 298.7122 | 435.3024 | 85.4648 | 0 | 162.7933 | 1763449.0516 | 56283.9951 | 2528596.2812 | 2899437.8279 | 0 | 182652.8215 | 0 | 2897863.7912 | 7539647.151 | 5145964.1048 | 23013895.0244 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33100493.5488 | 48236134.7118 | 5623413.2519 | 2.259 | 14652.5589 | 21352.6364 | 298.7122 | 435.3024
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.8387 | 11.8997 | 0.56725 | 4 | 14612.1944 | 21282.797 | 297.8893 | 433.8786 | 85.4628 | 0 | 157.3457 | 1767210.9584 | 56402.4727 | 2534773.7143 | 2908294.8796 | 0 | 181389.5727 | 0 | 2904747.9231 | 7557558.2502 | 5158188.7981 | 23068566.5692 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33155165.0936 | 48290806.2565 | 7498942.0933 | 2.269 | 14612.1944 | 21282.797 | 297.8893 | 433.8786
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.048 | 11.9246 | 0.56906 | 4 | 14581.9376 | 21231.3281 | 297.2725 | 432.8293 | 85.4615 | 0 | 160.4459 | 1769790.877 | 56483.7154 | 2539011.7335 | 2914375.1323 | 0 | 180322.5936 | 0 | 2909393.7802 | 7569645.8173 | 5166438.811 | 23105462.4602 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33192060.9845 | 48327702.1475 | 10000000 | 2.2762 | 14581.9376 | 21231.3281 | 297.2725 | 432.8293
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.6031 | [19 empty] | 100 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0783 | [19 empty] | 133.3521 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6795 | [19 empty] | 177.8279 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3779 | [19 empty] | 237.1374 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5405 | [19 empty] | 316.2278 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9768 | [19 empty] | 421.6965 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4835 | [19 empty] | 562.3413 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8317 | [19 empty] | 749.8942 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4845 | [19 empty] | 1000 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.15256 | 0.00064788 | 4 | 4363678.8053 | 10407309.2074 | 88959.4948 | 212167.0751 | 75.1565 | 0 | 33.5475 | 76580.6504 | 2246.4294 | 78330.3444 | 66649.1403 | 0 | 49292.2593 | 0 | 106508.5413 | 277113.3765 | 189135.5736 | 845856.3152 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11308521.9849 | 26970657.1513 | 1333.5214 | 0.0025915 | 4363678.8053 | 10407309.2074 | 88959.4948 | 212167.0751
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.17787 | 0.0023858 | 4 | 1192869.7726 | 2834053.9279 | 24318.2638 | 57776.0227 | 76.4894 | 0 | 287.046 | 86350.9107 | 2560.9344 | 88466.4201 | 72689.1812 | 0 | 47331.3065 | 0 | 115985.5136 | 301770.5145 | 205964.5769 | 921119.3578 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11383785.0275 | 27045920.1939 | 1778.2794 | 0.0095432 | 1192869.7726 | 2834053.9279 | 24318.2638 | 57776.0227
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.26489 | 0.0046937 | 4 | 622077.6605 | 1456290.8835 | 12681.8945 | 29688.4594 | 79.5061 | 0 | 417.7717 | 117286.2401 | 3566.5676 | 121357.2059 | 93503.7555 | 0 | 57111.5947 | 0 | 153201.8919 | 398599.8966 | 272052.6198 | 1216679.772 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11679345.4417 | 27341480.6081 | 2371.3737 | 0.018775 | 622077.6605 | 1456290.8835 | 12681.8945 | 29688.4594
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3808 | 0.37476 | 0.0079514 | 4 | 377996.3075 | 870429.5524 | 7705.966 | 17744.8838 | 81.6319 | 0 | 71.0914 | 152246.1425 | 4712.102 | 159902.5064 | 119543.5219 | 0 | 67181.8581 | 0 | 196398.5911 | 510988.8471 | 348760.3879 | 1559733.957 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12022399.6267 | 27684534.7931 | 3162.2777 | 0.031806 | 377996.3075 | 870429.5524 | 7705.966 | 17744.8838
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5964 | 0.52844 | 0.012445 | 4 | 250532.0861 | 565161.1429 | 5107.4354 | 11521.5743 | 83.3086 | 0 | 101.9934 | 196251.829 | 6159.0087 | 210215.2153 | 155644.2812 | 0 | 80285.7045 | 0 | 252936.8551 | 658089.8126 | 449159.8195 | 2008742.526 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12471408.1957 | 28133543.3621 | 4216.965 | 0.04978 | 250532.0861 | 565161.1429 | 5107.4354 | 11521.5743
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9944 | 0.70625 | 0.018495 | 4 | 175108.6209 | 386810.9699 | 3569.8261 | 7885.6648 | 84.4197 | 0 | 100.1949 | 242569.5295 | 7685.4634 | 264868.483 | 197839.6172 | 0 | 91684.3382 | 0 | 313812.4982 | 816475.7485 | 557261.4752 | 2492197.1531 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12954862.8228 | 28616997.9892 | 5623.4133 | 0.073982 | 175108.6209 | 386810.9699 | 3569.8261 | 7885.6648
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7434 | 0.92754 | 0.026337 | 4 | 128342.868 | 277012.4761 | 2616.443 | 5647.274 | 85.2174 | 0 | 115.3708 | 295253.8047 | 9416.6801 | 329200.1317 | 249656.6232 | 0 | 103823.5768 | 0 | 385066.8184 | 1001864.8734 | 683793.3624 | 3058075.8707 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 13520741.5404 | 29182876.7068 | 7498.9421 | 0.10535 | 128342.868 | 277012.4761 | 2616.443 | 5647.274
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2844 | 1.252 | 0.037248 | 4 | 96080.6469 | 201202.1841 | 1958.7339 | 4101.7787 | 86.003 | 0 | 114.2829 | 366374.4505 | 11759.4454 | 418235.4194 | 325298.2673 | 0 | 122163.5979 | 0 | 485094.1604 | 1262115.4988 | 861419.7618 | 3852460.6014 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 14315126.2711 | 29977261.4375 | 10000 | 0.14899 | 96080.6469 | 201202.1841 | 1958.7339 | 4101.7787
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3077 | 1.6375 | 0.051303 | 4 | 74100.9966 | 150423.0857 | 1510.649 | 3066.5781 | 86.5134 | 0 | 81.7107 | 443822.1146 | 14305.1556 | 518200.9235 | 415699.2178 | 0 | 139547.789 | 0 | 597314.3282 | 1554089.356 | 1060697.9188 | 4743676.8035 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 15206342.4732 | 30868477.6396 | 13335.2143 | 0.20521 | 74100.9966 | 150423.0857 | 1510.649 | 3066.5781
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0855 | 2.1194 | 0.069564 | 4 | 58462.7378 | 114749.19 | 1191.842 | 2339.3174 | 86.9011 | 0 | 115.6894 | 533274.2765 | 17241.0797 | 636779.6903 | 528676.8462 | 0 | 158281.3449 | 0 | 730958.7627 | 1901804.7603 | 1298020.8271 | 5805037.5877 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 16267703.2574 | 31929838.4238 | 17782.7941 | 0.27826 | 58462.7378 | 114749.19 | 1191.842 | 2339.3174
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7413 | 2.7135 | 0.092979 | 4 | 47100.2901 | 89212.5271 | 960.2031 | 1818.718 | 87.1962 | 0 | 91.3733 | 635503.4227 | 20590.6477 | 775761.3323 | 667811.7379 | 0 | 178027.134 | 0 | 888300.7671 | 2311176.3803 | 1577425.3695 | 7054596.7914 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 17517262.4611 | 33179397.6275 | 23713.7371 | 0.37191 | 47100.2901 | 89212.5271 | 960.2031 | 1818.718
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3561 | 3.43 | 0.12246 | 4 | 38707.0615 | 70680.0943 | 789.0958 | 1440.9093 | 87.4206 | 0 | 112.7162 | 750290.9045 | 24345.2337 | 935543.3143 | 835563.6788 | 0 | 198030.8959 | 0 | 1070071.8706 | 2784107.5055 | 1900210.5802 | 8498163.9836 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 18960829.6533 | 34622964.8197 | 31622.7766 | 0.48985 | 38707.0615 | 70680.0943 | 789.0958 | 1440.9093
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.9844 | 4.276 | 0.15878 | 4 | 32433.7665 | 57094.5597 | 661.2062 | 1163.9498 | 87.5923 | 0 | 141.2105 | 877014.4004 | 28483.1953 | 1115846.6062 | 1033613.79 | 0 | 217652.7754 | 0 | 1276318.1992 | 3320718.1455 | 2266458.3683 | 10136105.4803 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 20598771.15 | 36260906.3164 | 42169.6503 | 0.6351 | 32433.7665 | 57094.5597 | 661.2062 | 1163.9498
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.5165 | 5.2376 | 0.20202 | 4 | 27711.0911 | 47093.4132 | 564.9281 | 960.0629 | 87.7223 | 0 | 135.7345 | 1012342.1775 | 32894.6244 | 1312307.469 | 1258687.0139 | 0 | 235451.5979 | 0 | 1502156.3243 | 3908302.6211 | 2667496.8465 | 11929638.6746 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 22392304.3443 | 38054439.5107 | 56234.1325 | 0.80806 | 27711.0911 | 47093.4132 | 564.9281 | 960.0629
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.6212 | 6.2722 | 0.25113 | 4 | 24146.3524 | 39737.7954 | 492.2561 | 810.1087 | 87.817 | 0 | 134.6055 | 1149960.405 | 37372.8595 | 1515760.3124 | 1500853.4615 | 0 | 249407.1557 | 0 | 1736808.1357 | 4518818.5007 | 3084186.4792 | 13793167.3097 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 24255832.9794 | 39917968.1458 | 74989.4209 | 1.0045 | 24146.3524 | 39737.7954 | 492.2561 | 810.1087
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.8696 | 7.3242 | 0.30397 | 4 | 21459.5013 | 34340.9285 | 437.481 | 700.0863 | 87.8799 | 0 | 147.4782 | 1283128.4023 | 41697.9035 | 1715855.7491 | 1747226.6114 | 0 | 258267.9713 | 0 | 1968008.8887 | 5120355.4342 | 3494747.7966 | 15629288.7571 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 26091954.4268 | 41754089.5932 | 100000 | 1.2159 | 21459.5013 | 34340.9285 | 437.481 | 700.0863
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.128 | 8.1211 | 0.35306 | 4 | 19409.6618 | 30499.9297 | 395.6922 | 621.7823 | 87.9092 | 0 | 365.576 | 1380198.7013 | 44844.4607 | 1863612.6657 | 1934040.2268 | 0 | 249397.6229 | 0 | 2134116.5342 | 5552533.4545 | 3789718.1758 | 16948461.842 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 27411127.5116 | 43073262.678 | 133352.1432 | 1.4122 | 19409.6618 | 30499.9297 | 395.6922 | 621.7823
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.1749 | 9.2701 | 0.40991 | 4 | 17903.7161 | 27455.8121 | 364.9915 | 559.7239 | 87.9267 | 0 | 156.7015 | 1515188.9745 | 49210.0356 | 2071689.8626 | 2203802.3948 | 0 | 260106.2609 | 0 | 2378999.0361 | 6189667.4921 | 4224575.2483 | 18893239.3049 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 29355904.9746 | 45018040.141 | 177827.941 | 1.6397 | 17903.7161 | 27455.8121 | 364.9915 | 559.7239
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.2922 | 10.0443 | 0.45585 | 4 | 16786.3451 | 25375.8392 | 342.2124 | 517.3208 | 87.9231 | 0 | 121.3441 | 1603218.6065 | 52049.5058 | 2209002.0039 | 2385957.942 | 0 | 254133.3716 | 0 | 2536700.9577 | 6599975.5429 | 4504618.924 | 20145656.8545 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 30608322.5242 | 46270457.6906 | 237137.3706 | 1.8234 | 16786.3451 | 25375.8392 | 342.2124 | 517.3208
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3734 | 10.6855 | 0.49562 | 4 | 15952.8729 | 23853.1546 | 325.2209 | 486.2788 | 87.9115 | 0 | 139.9414 | 1674494.5707 | 54343.7457 | 2321121.1909 | 2537070.4122 | 0 | 245976.9098 | 0 | 2664872.6634 | 6933452.0296 | 4732223.4784 | 21163555.0006 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 31626220.6703 | 47288355.8367 | 316227.766 | 1.9825 | 15952.8729 | 23853.1546 | 325.2209 | 486.2788
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4808 | 11.2023 | 0.52889 | 4 | 15331.134 | 22734.4612 | 312.5459 | 463.4727 | 87.8967 | 0 | 135.4658 | 1730951.358 | 56157.6587 | 2410530.4624 | 2659083.4713 | 0 | 237035.6322 | 0 | 2766565.8472 | 7198036.8338 | 4912808.044 | 21971169.3077 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 32433834.9774 | 48095970.1438 | 421696.5034 | 2.1156 | 15331.134 | 22734.4612 | 312.5459 | 463.4727
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4381 | 11.5735 | 0.55583 | 4 | 14839.6382 | 21884.0693 | 302.5261 | 446.1364 | 87.8831 | 0 | 145.0399 | 1770982.324 | 57441.9365 | 2474250.6403 | 2746848.248 | 0 | 224931.7393 | 0 | 2837037.4064 | 7381389.3751 | 5037949.9209 | 22530831.5905 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 32993497.2602 | 48655632.4266 | 562341.3252 | 2.2233 | 14839.6382 | 21884.0693 | 302.5261 | 446.1364
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3003 | 11.932 | 0.57771 | 4 | 14520.4265 | 21298.092 | 296.0185 | 434.1904 | 87.8677 | 0 | 148.9748 | 1809247.5213 | 58668.0237 | 2535414.0245 | 2831720.7691 | 0 | 220519.6292 | 0 | 2907672.2874 | 7565166.8463 | 5163381.8213 | 23091790.9228 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33554456.5925 | 49216591.7589 | 749894.2093 | 2.3108 | 14520.4265 | 21298.092 | 296.0185 | 434.1904
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.2519 | 12.1761 | 0.59467 | 4 | 14261.2867 | 20845.6635 | 290.7356 | 424.967 | 87.856 | 0 | 118.5678 | 1835076.1309 | 59494.7449 | 2576839.4568 | 2889552.2246 | 0 | 213616.5792 | 0 | 2954085.8632 | 7685925.4497 | 5245802.0494 | 23460392.4988 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33923058.1685 | 49585193.3349 | 1000000 | 2.3787 | 14261.2867 | 20845.6635 | 290.7356 | 424.967
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7593 | 12.3643 | 0.60789 | 4 | 14067.4277 | 20508.6416 | 286.7835 | 418.0964 | 87.8463 | 0 | 133.1217 | 1854881.5464 | 60128.1843 | 2608681.9015 | 2934195.9543 | 0 | 207933.3654 | 0 | 2989670.1712 | 7778508.5199 | 5308991.8972 | 23742991.5403 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34205657.21 | 49867792.3764 | 1333521.4322 | 2.4316 | 14067.4277 | 20508.6416 | 286.7835 | 418.0964
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.8971 | 12.5063 | 0.61802 | 4 | 13922.3214 | 20257.9123 | 283.8254 | 412.9849 | 87.8387 | 0 | 148.0533 | 1869748.7012 | 60603.3966 | 2632629.1219 | 2967879.2849 | 0 | 203259.5289 | 0 | 3016306.8131 | 7847811.5982 | 5356292.6722 | 23954531.1172 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34417196.7869 | 50079331.9533 | 1778279.41 | 2.4721 | 13922.3214 | 20257.9123 | 283.8254 | 412.9849
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.7667 | 12.6147 | 0.6258 | 4 | 13813.6578 | 20070.5303 | 281.6101 | 409.1649 | 87.8326 | 0 | 131.7734 | 1881064.6288 | 60964.9313 | 2650881.771 | 2993615.4743 | 0 | 199575.1186 | 0 | 3036579.7503 | 7900557.6222 | 5392292.9174 | 24115532.214 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34578197.8837 | 50240333.0501 | 2371373.7057 | 2.5032 | 13813.6578 | 20070.5303 | 281.6101 | 409.1649
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4272 | 12.6969 | 0.63173 | 4 | 13732.2562 | 19930.4158 | 279.9506 | 406.3085 | 87.8278 | 0 | 137.7835 | 1889632.2141 | 61238.5619 | 2664716.0644 | 3013157.8566 | 0 | 196699.4426 | 0 | 3051923.2144 | 7940478.1684 | 5419539.5105 | 24237385.0329 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34700050.7026 | 50362185.869 | 3162277.6602 | 2.5269 | 13732.2562 | 19930.4158 | 279.9506 | 406.3085
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9265 | 12.7591 | 0.63622 | 4 | 13671.2611 | 19825.5994 | 278.7071 | 404.1717 | 87.8242 | 0 | 130.0487 | 1896094.0901 | 61444.8849 | 2675158.635 | 3027929.6565 | 0 | 194472.7585 | 0 | 3063489.0098 | 7970569.9954 | 5440077.8007 | 24329236.8309 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34791902.5006 | 50454037.667 | 4216965.0343 | 2.5449 | 13671.2611 | 19825.5994 | 278.7071 | 404.1717
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2944 | 12.8049 | 0.63959 | 4 | 13625.5476 | 19747.4771 | 277.7752 | 402.579 | 87.8214 | 0 | 138.9258 | 1900845.6927 | 61596.5693 | 2682841.9938 | 3038809.6564 | 0 | 192713.447 | 0 | 3071954.8701 | 7992596.4273 | 5455111.2931 | 24396469.9497 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34859135.6194 | 50521270.7858 | 5623413.2519 | 2.5584 | 13625.5476 | 19747.4771 | 277.7752 | 402.579
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5696 | 12.8392 | 0.64213 | 4 | 13591.2822 | 19689.0423 | 277.0767 | 401.3878 | 87.8194 | 0 | 151.8115 | 1904396.3015 | 61709.8974 | 2688585.9061 | 3046949.5657 | 0 | 191360.185 | 0 | 3078270.7238 | 8009028.9831 | 5466326.8501 | 24446628.4128 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34909294.0825 | 50571429.2489 | 7498942.0933 | 2.5685 | 13591.2822 | 19689.0423 | 277.0767 | 401.3878
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.7935 | 12.867 | 0.6441 | 4 | 13565.5951 | 19644.6384 | 276.553 | 400.4825 | 87.8177 | 0 | 139.7185 | 1907282.3668 | 61802.0043 | 2693256.3632 | 3053572.1597 | 0 | 190423.7255 | 0 | 3083471.2816 | 8022559.7678 | 5475561.8886 | 24487929.5575 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34950595.2272 | 50612730.3936 | 10000000 | 2.5764 | 13565.5951 | 19644.6384 | 276.553 | 400.4825
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7752 | [19 empty] | 100 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8239 | [19 empty] | 133.3521 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9256 | [19 empty] | 177.8279 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1784 | [19 empty] | 237.1374 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1132 | [19 empty] | 316.2278 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6712 | [19 empty] | 421.6965 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9968 | [19 empty] | 562.3413 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4337 | [19 empty] | 749.8942 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.1002 | [19 empty] | 1000 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.15842 | 0.0013974 | 4 | 2094451.3265 | 4992209.7816 | 42698.2232 | 101772.9489 | 76.7392 | 0 | 32.0988 | 79948.0578 | 2371.8371 | 80624.1242 | 67203.7556 | 0 | 48230.2047 | 0 | 108567.412 | 282470.1357 | 192791.6718 | 862207.1988 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11706800.1046 | 27903633.4017 | 1333.5214 | 0.0055894 | 2094451.3265 | 4992209.7816 | 42698.2232 | 101772.9489
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.21774 | 0.0034056 | 4 | 874276.1241 | 2063250.6495 | 17823.3013 | 42062.1552 | 79.5275 | 0 | 337.2484 | 102471.9587 | 3110.3446 | 103740.4469 | 81126.1177 | 0 | 53486.1764 | 0 | 134134.6672 | 348990.8893 | 238193.453 | 1065254.0537 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11909846.9596 | 28106680.2566 | 1778.2794 | 0.013623 | 874276.1241 | 2063250.6495 | 17823.3013 | 42062.1552
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.31877 | 0.0062913 | 4 | 486356.4115 | 1129979.1843 | 9915.0333 | 23036.1541 | 82.3362 | 0 | 84.2792 | 137028.5024 | 4255.0085 | 140406.9462 | 104404.8725 | 0 | 64179.7875 | 0 | 175607.2957 | 456894.1615 | 311839.6534 | 1394616.2279 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12239209.1337 | 28436042.4308 | 2371.3737 | 0.025165 | 486356.4115 | 1129979.1843 | 9915.0333 | 23036.1541
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 0.44789 | 0.01037 | 4 | 304469.0578 | 694944.9023 | 6207.0136 | 14167.3918 | 84.3499 | 0 | 91.7098 | 176763.7913 | 5581.4713 | 184002.5563 | 134387.9601 | 0 | 75485.0209 | 0 | 224726.112 | 584691.2457 | 399063.7894 | 1784701.947 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12629294.8529 | 28826128.1499 | 3162.2777 | 0.04148 | 304469.0578 | 694944.9023 | 6207.0136 | 14167.3918
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0781 | 0.61646 | 0.015867 | 4 | 206443.4351 | 461634.1521 | 4208.6287 | 9411.0366 | 85.8646 | 0 | 99.5486 | 223576.3136 | 7145.9471 | 237300.1527 | 172668.7971 | 0 | 88430.1064 | 0 | 284357.3136 | 739839.4002 | 504955.5928 | 2258273.6235 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13102866.5293 | 29299699.8264 | 4216.965 | 0.06347 | 206443.4351 | 461634.1521 | 4208.6287 | 9411.0366
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6787 | 0.82955 | 0.023261 | 4 | 146872.6799 | 320950.0919 | 2994.1982 | 6543.0017 | 86.9623 | 0 | 87.577 | 277489.4501 | 8949.8292 | 300651.5526 | 221437.1896 | 0 | 102281.24 | 0 | 355215.612 | 924198.1577 | 630784.233 | 2821007.2643 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13665600.1702 | 29862433.4672 | 5623.4133 | 0.093044 | 146872.6799 | 320950.0919 | 2994.1982 | 6543.0017
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2346 | 1.1708 | 0.033473 | 4 | 108500.2822 | 229469.0049 | 2211.925 | 4678.036 | 87.9666 | 0 | 93.6868 | 355787.3208 | 11569.2505 | 395764.5582 | 299245.6351 | 0 | 126688.8436 | 0 | 463731.6872 | 1206534.7257 | 823484.7421 | 3682806.7632 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 14527399.6691 | 30724232.9661 | 7498.9421 | 0.13389 | 108500.2822 | 229469.0049 | 2211.925 | 4678.036
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4272 | 1.4644 | 0.046335 | 4 | 82025.9391 | 169414.8877 | 1672.2097 | 3453.7516 | 88.4916 | 0 | 86.3365 | 417742.3172 | 13641.3002 | 473148.4527 | 366200.1834 | 0 | 136401.4866 | 0 | 548782.1586 | 1427818.606 | 974515.5374 | 4358250.0421 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 15202842.948 | 31399676.245 | 10000 | 0.18534 | 82025.9391 | 169414.8877 | 1672.2097 | 3453.7516
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7445 | 1.9083 | 0.063476 | 4 | 63799.1427 | 127590.1624 | 1300.6318 | 2601.098 | 88.9783 | 0 | 86.5928 | 504649.7932 | 16542.3875 | 584544.4004 | 467470.3816 | 0 | 155519.0491 | 0 | 674203.1446 | 1754138.2842 | 1197235.4229 | 5354302.8634 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 16198895.7693 | 32395729.0663 | 13335.2143 | 0.2539 | 63799.1427 | 127590.1624 | 1300.6318 | 2601.098
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.8714 | 2.4607 | 0.08566 | 4 | 50724.9922 | 97995.8708 | 1034.0976 | 1997.7784 | 89.3484 | 0 | 85.5666 | 604707.7328 | 19877.1882 | 716165.3328 | 593456.9218 | 0 | 175969.869 | 0 | 822969.0474 | 2141196.6471 | 1461410.7089 | 6535753.448 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 17380346.3538 | 33577179.6509 | 17782.7941 | 0.34264 | 50724.9922 | 97995.8708 | 1034.0976 | 1997.7784
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9138 | 3.1358 | 0.11395 | 4 | 41160.9956 | 76697.4448 | 839.1226 | 1563.5812 | 89.6298 | 0 | 117.095 | 718275.1762 | 23655.6126 | 869261.9663 | 747412.0645 | 0 | 197143.5845 | 0 | 996741.8776 | 2593317.9055 | 1769992.7579 | 7915800.945 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 18760393.8509 | 34957227.1479 | 23713.7371 | 0.45578 | 41160.9956 | 76697.4448 | 839.1226 | 1563.5812
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30 | 3.9509 | 0.14943 | 4 | 34060.9091 | 61159.4919 | 694.3777 | 1246.819 | 89.8458 | 0 | 109.677 | 846089.3841 | 27900.3927 | 1045569.3708 | 933253.9743 | 0 | 218819.595 | 0 | 1197936.7596 | 3116785.7178 | 2127270.2959 | 9513625.4901 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 20358218.3959 | 36555051.693 | 31622.7766 | 0.5977 | 34060.9091 | 61159.4919 | 694.3777 | 1246.819
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0855 | 4.9001 | 0.19267 | 4 | 28735.2066 | 49750.9857 | 585.8061 | 1014.2411 | 90.01 | 0 | 119.1075 | 985440.7657 | 32519.9917 | 1241937.1333 | 1149621.4742 | 0 | 239388.4593 | 0 | 1423074.0514 | 3702546.7692 | 2527064.2497 | 11301592.8945 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 22146185.8004 | 38343019.0975 | 42169.6503 | 0.7707 | 28735.2066 | 49750.9857 | 585.8061 | 1014.2411
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0197 | 5.963 | 0.24351 | 4 | 24717.6708 | 41346.4669 | 503.9032 | 842.9037 | 90.1333 | 0 | 112.2746 | 1132314.5457 | 37379.7079 | 1453006.7009 | 1391789.971 | 0 | 257355.5797 | 0 | 1666020.137 | 4334642.6487 | 2958482.6758 | 13230991.9666 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 24075584.8725 | 40272418.1695 | 56234.1325 | 0.97402 | 24717.6708 | 41346.4669 | 503.9032 | 842.9037
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.4339 | 7.0898 | 0.30038 | 4 | 21682.3521 | 35162.4447 | 442.0241 | 716.834 | 90.2205 | 0 | 116.0699 | 1279765.3083 | 42249.13 | 1668668.1514 | 1648559.3708 | 0 | 270772.6649 | 0 | 1914905.7039 | 4982191.8403 | 3400448.3048 | 15207560.4743 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 26052153.3802 | 42248986.6772 | 74989.4209 | 1.2015 | 21682.3521 | 35162.4447 | 442.0241 | 716.834
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.8138 | 8.2104 | 0.36037 | 4 | 19394.8252 | 30630.9879 | 395.3897 | 624.4541 | 90.2742 | 0 | 130.695 | 1419611.7634 | 46857.3629 | 1876447.1588 | 1904138.243 | 0 | 278125.4023 | 0 | 2154820.1729 | 5606400.0755 | 3826483.2515 | 17112883.4304 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 27957476.3363 | 44154309.6333 | 100000 | 1.4415 | 19394.8252 | 30630.9879 | 395.3897 | 624.4541
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.6749 | 9.2591 | 0.4199 | 4 | 17677.4993 | 27320.672 | 360.3797 | 556.9689 | 90.299 | 0 | 129.7738 | 1545321.4945 | 50989.6978 | 2065816.3918 | 2143658.5719 | 0 | 279227.052 | 0 | 2373155.1511 | 6174462.9021 | 4214197.8032 | 18846829.0644 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 29691421.9703 | 45888255.2674 | 133352.1432 | 1.6796 | 17677.4993 | 27320.672 | 360.3797 | 556.9689
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0265 | 10.2366 | 0.47771 | 4 | 16365.5711 | 24841.7845 | 333.6343 | 506.4334 | 90.3022 | 0 | 144.4837 | 1658597.5459 | 54703.6589 | 2238531.6469 | 2367360.4849 | 0 | 276222.873 | 0 | 2572212.3218 | 6692368.828 | 4567679.2395 | 20427676.5989 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 31272269.5048 | 47469102.8018 | 177827.941 | 1.9109 | 16365.5711 | 24841.7845 | 333.6343 | 506.4334
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9728 | 11.0246 | 0.52734 | 4 | 15415.0329 | 23093.5307 | 314.2563 | 470.7929 | 90.2916 | 0 | 137.0646 | 1747436.181 | 57609.057 | 2375365.5381 | 2548042.1473 | 0 | 268551.1224 | 0 | 2728831.5779 | 7099860.0053 | 4845800.3412 | 21671495.9702 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 32516088.876 | 48712922.1731 | 237137.3706 | 2.1094 | 15415.0329 | 23093.5307 | 314.2563 | 470.7929
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.887 | 11.6736 | 0.56989 | 4 | 14705.6083 | 21810.7919 | 299.7937 | 444.6425 | 90.2746 | 0 | 143.0757 | 1819093.02 | 59947.3444 | 2486624.0928 | 2697160.3286 | 0 | 259150.9176 | 0 | 2855570.5243 | 7429608.7462 | 5070860.6325 | 22678015.6063 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 33522608.5122 | 49719441.8092 | 316227.766 | 2.2796 | 14705.6083 | 21810.7919 | 299.7937 | 444.6425
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.8324 | 12.1931 | 0.60518 | 4 | 14176.0418 | 20867.0108 | 288.9978 | 425.4022 | 90.2558 | 0 | 146.4111 | 1875523.0926 | 61785.2409 | 2574804.3805 | 2816736.1389 | 0 | 249271.8845 | 0 | 2955467.0876 | 7689519.1123 | 5248254.7979 | 23471361.7352 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 34315954.6411 | 50512787.9381 | 421696.5034 | 2.4207 | 14176.0418 | 20867.0108 | 288.9978 | 425.4022
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9413 | 12.6014 | 0.63371 | 4 | 13780.5023 | 20170.1734 | 280.9342 | 411.1963 | 90.2379 | 0 | 128.6582 | 1919322.1566 | 63209.4957 | 2643592.3128 | 2910861.0692 | 0 | 239859.7106 | 0 | 3032969.4505 | 7891164.3627 | 5385881.8247 | 24086860.3828 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 34931453.2887 | 51128286.5857 | 562341.3252 | 2.5348 | 13780.5023 | 20170.1734 | 280.9342 | 411.1963
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.365 | 12.9191 | 0.65639 | 4 | 13484.8562 | 19653.7545 | 274.907 | 400.6684 | 90.2221 | 0 | 158.0558 | 1953071.0021 | 64305.536 | 2696803.6593 | 2984177.8178 | 0 | 231490.5103 | 0 | 3092640.9249 | 8046417.2988 | 5491845.1438 | 24560751.8929 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 35405344.7988 | 51602178.0958 | 749894.2093 | 2.6256 | 13484.8562 | 19653.7545 | 274.907 | 400.6684
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2332 | 13.1635 | 0.67415 | 4 | 13263.7221 | 19270.1216 | 270.3989 | 392.8475 | 90.2089 | 0 | 152.3767 | 1978854.1704 | 65142.0315 | 2737578.2549 | 3040656.2162 | 0 | 224352.3318 | 0 | 3138167.3719 | 8164867.7751 | 5572690.0277 | 24922308.1796 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 35766901.0855 | 51963734.3825 | 1000000 | 2.6966 | 13263.7221 | 19270.1216 | 270.3989 | 392.8475
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6487 | 13.3485 | 0.68784 | 4 | 13098.2214 | 18985.0348 | 267.025 | 387.0356 | 90.1983 | 0 | 145.1814 | 1998254.8982 | 65770.9621 | 2768329.8417 | 3083421.7382 | 0 | 218374.3516 | 0 | 3172319.1988 | 8253723.8232 | 5633336.1064 | 25193530.9203 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36038123.8262 | 52234957.1232 | 1333521.4322 | 2.7514 | 13098.2214 | 18985.0348 | 267.025 | 387.0356
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.7398 | 13.4909 | 0.69842 | 4 | 12974.2978 | 18771.9321 | 264.4986 | 382.6912 | 90.1898 | 0 | 152.0245 | 2013133.2243 | 66252.9927 | 2791954.2358 | 3116374.9331 | 0 | 213635.597 | 0 | 3198526.8833 | 8321910.8422 | 5679875.148 | 25401663.8563 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36246256.7621 | 52443090.0592 | 1778279.41 | 2.7937 | 12974.2978 | 18771.9321 | 264.4986 | 382.6912
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.5512 | 13.5968 | 0.70644 | 4 | 12881.4715 | 18613.3545 | 262.6062 | 379.4584 | 90.1833 | 0 | 141.0423 | 2024154.561 | 66609.8969 | 2809477.4968 | 3140873.4885 | 0 | 209789.9211 | 0 | 3217853.0921 | 8372193.6732 | 5714194.2133 | 25555146.3429 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36399739.2488 | 52596572.5458 | 2371373.7057 | 2.8257 | 12881.4715 | 18613.3545 | 262.6062 | 379.4584
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.1749 | 13.678 | 0.71257 | 4 | 12811.9191 | 18494.4612 | 261.1883 | 377.0346 | 90.1782 | 0 | 160.4661 | 2032599.9299 | 66883.2869 | 2822918.4649 | 3159696.8537 | 0 | 206843.9522 | 0 | 3232687.5702 | 8410789.9422 | 5740536.96 | 25672956.9599 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36517549.8658 | 52714383.1629 | 3162277.6602 | 2.8503 | 12811.9191 | 18494.4612 | 261.1883 | 377.0346
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.6501 | 13.74 | 0.71724 | 4 | 12759.7941 | 18405.3556 | 260.1257 | 375.2181 | 90.1742 | 0 | 151.207 | 2039021.7728 | 67091.1155 | 2833146.7176 | 3174039.6424 | 0 | 204591.8365 | 0 | 3243977.5231 | 8440164.0839 | 5760585.4153 | 25762618.1073 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36607211.0132 | 52804044.3102 | 4216965.0343 | 2.8689 | 12759.7941 | 18405.3556 | 260.1257 | 375.2181
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.9861 | 13.7837 | 0.72067 | 4 | 12720.7237 | 18339.4025 | 259.3292 | 373.8735 | 90.1714 | 0 | 133.7964 | 2043554.2654 | 67237.7694 | 2840369.8303 | 3184178.1635 | 0 | 202736.6957 | 0 | 3251849.9225 | 8460646.4521 | 5774565.0525 | 25825138.1513 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36669731.0572 | 52866564.3543 | 5623413.2519 | 2.8827 | 12720.7237 | 18339.4025 | 259.3292 | 373.8735
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.2567 | 13.819 | 0.72333 | 4 | 12691.4349 | 18289.4099 | 258.7321 | 372.8544 | 90.169 | 0 | 146.7053 | 2047200.0316 | 67355.7148 | 2846182.2356 | 3192342.3906 | 0 | 201423.2647 | 0 | 3258256.4186 | 8477314.8408 | 5785941.5703 | 25876016.467 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36720609.3729 | 52917442.67 | 7498942.0933 | 2.8933 | 12691.4349 | 18289.4099 | 258.7321 | 372.8544
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4466 | 13.8437 | 0.72528 | 4 | 12669.477 | 18252.4149 | 258.2844 | 372.1002 | 90.1674 | 0 | 139.28 | 2049755.4566 | 67438.3764 | 2850257.6376 | 3198069.9146 | 0 | 200347.4503 | 0 | 3262688.8459 | 8488847.1075 | 5793812.5793 | 25911217.3683 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36755810.2742 | 52952643.5713 | 10000000 | 2.9011 | 12669.477 | 18252.4149 | 258.2844 | 372.1002
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8984 | [19 empty] | 100 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2992 | [19 empty] | 133.3521 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8583 | [19 empty] | 177.8279 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6416 | [19 empty] | 237.1374 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.541 | [19 empty] | 316.2278 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.659 | [19 empty] | 421.6965 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.7067 | [19 empty] | 562.3413 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.2709 | [19 empty] | 749.8942 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.16452 | 7.9191e-05 | 4 | 38326943.4342 | 91173247.9565 | 781346.5829 | 1858689.9805 | 78.2971 | 0 | 30.1246 | 83454.3302 | 2504.5538 | 82987.2995 | 68051.0897 | 0 | 56218.627 | 0 | 114354.201 | 297526.1738 | 203067.7272 | 908164.0022 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12140544.2351 | 28880279.79 | 1000 | 0.00031676 | 38326943.4342 | 91173247.9565 | 781346.5829 | 1858689.9805
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.17134 | 0.0021867 | 4 | 1387846.9322 | 3301624.1436 | 28293.1369 | 67308.0739 | 78.6987 | 0 | 260.4346 | 86163.7199 | 2594.0026 | 85699.5522 | 69562.0444 | 0 | 48841.2421 | 0 | 114215.6189 | 297165.6115 | 202821.636 | 907063.4276 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12139443.6605 | 28879179.2154 | 1333.5214 | 0.008747 | 1387846.9322 | 3301624.1436 | 28293.1369 | 67308.0739
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3321 | 0.26336 | 0.0046651 | 4 | 667504.0947 | 1564585.9621 | 13607.9738 | 31896.2011 | 82.4946 | 0 | 391.6194 | 120273.8803 | 3732.1406 | 120501.1748 | 90290.2036 | 0 | 60193.18 | 0 | 154046.3259 | 400796.9409 | 273552.1477 | 1223385.9938 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12455766.2267 | 29195501.7816 | 1778.2794 | 0.01866 | 667504.0947 | 1564585.9621 | 13607.9738 | 31896.2011
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1808 | 0.38024 | 0.0082688 | 4 | 387710.6799 | 893819.5841 | 7904.0066 | 18221.7212 | 85.1192 | 0 | 92.6137 | 158901.959 | 5036.633 | 161314.2477 | 116677.9818 | 0 | 71844.0647 | 0 | 200372.2056 | 521327.3769 | 355816.6469 | 1591291.1154 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12823671.3484 | 29563406.9032 | 2371.3737 | 0.033075 | 387710.6799 | 893819.5841 | 7904.0066 | 18221.7212
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2823 | 0.53295 | 0.013248 | 4 | 250388.4859 | 566272.5796 | 5104.508 | 11544.2325 | 87.0585 | 0 | 77.888 | 204266.5772 | 6575.928 | 211011.3259 | 150726.3429 | 0 | 84946.8555 | 0 | 256435.5415 | 667192.6769 | 455372.7114 | 2036527.9595 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13268908.1924 | 30008643.7473 | 3162.2777 | 0.052993 | 250388.4859 | 566272.5796 | 5104.508 | 11544.2325
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6628 | 0.72528 | 0.02 | 4 | 172399.9096 | 381645.1438 | 3514.6053 | 7780.3525 | 88.4627 | 0 | 113.1304 | 256081.2582 | 8337.7592 | 269698.1509 | 193574.0447 | 0 | 98753.4761 | 0 | 322313.4287 | 838593.426 | 572357.2446 | 2559708.7885 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13792089.0214 | 30531824.5763 | 4216.965 | 0.080001 | 172399.9096 | 381645.1438 | 3514.6053 | 7780.3525
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3561 | 0.96121 | 0.028916 | 4 | 124453.0112 | 269181.7466 | 2537.143 | 5487.634 | 89.4536 | 0 | 99.2069 | 314134.9596 | 10310.6827 | 337585.7357 | 246230.7701 | 0 | 112709.3394 | 0 | 398178.8801 | 1035979.7684 | 707077.4792 | 3162207.6151 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 14394587.8481 | 31134323.4029 | 5623.4133 | 0.11566 | 124453.0112 | 269181.7466 | 2537.143 | 5487.634
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7339 | 1.2949 | 0.04116 | 4 | 92360.3779 | 194035.2363 | 1882.8912 | 3955.6707 | 90.3525 | 0 | 82.4754 | 389526.2568 | 12876.5207 | 428163.8273 | 320320.23 | 0 | 132127.3969 | 0 | 500375.5504 | 1301874.5409 | 888556.125 | 3973820.448 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 15206200.6809 | 31945936.2358 | 7498.9421 | 0.16464 | 92360.3779 | 194035.2363 | 1882.8912 | 3955.6707
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6233 | 1.6997 | 0.057029 | 4 | 70727.9105 | 144110.0693 | 1441.8841 | 2937.8787 | 90.9666 | 0 | 92.5824 | 473313.8246 | 15720.6224 | 532010.2483 | 410162.6897 | 0 | 151444.9156 | 0 | 617234.3972 | 1605917.2894 | 1096071.5483 | 4901875.5356 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 16134255.7685 | 32873991.3234 | 10000 | 0.22812 | 70727.9105 | 144110.0693 | 1441.8841 | 2937.8787
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2307 | 2.2055 | 0.07772 | 4 | 55445.9296 | 109292.4778 | 1130.3403 | 2228.075 | 91.4312 | 0 | 111.9906 | 569975.9306 | 18997.2925 | 655035.2608 | 522522.3034 | 0 | 172144.377 | 0 | 756083.3141 | 1967173.6892 | 1342636.4643 | 6004568.6318 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 17236948.8647 | 33976684.4196 | 13335.2143 | 0.31088 | 55445.9296 | 109292.4778 | 1130.3403 | 2228.075
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.7324 | 2.837 | 0.10444 | 4 | 44403.7463 | 84472.6482 | 905.2304 | 1722.0892 | 91.7875 | 0 | 104.1531 | 681755.5815 | 22779.6717 | 800969.4639 | 662770.9139 | 0 | 194572.395 | 0 | 921510.7301 | 2397581.8919 | 1636398.9066 | 7318339.5546 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 18550719.7875 | 35290455.3424 | 17782.7941 | 0.41777 | 44403.7463 | 84472.6482 | 905.2304 | 1722.0892
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1964 | 3.6036 | 0.13833 | 4 | 36280.4031 | 66532.7158 | 739.6251 | 1356.3594 | 92.058 | 0 | 138.2638 | 807909.0586 | 27040.3261 | 969676.4782 | 832976.4077 | 0 | 217482.9686 | 0 | 1113483.2433 | 2897054.9922 | 1977299.5607 | 8842923.0352 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 20075303.2682 | 36815038.823 | 23713.7371 | 0.55334 | 36280.4031 | 66532.7158 | 739.6251 | 1356.3594
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.7151 | 4.5183 | 0.18048 | 4 | 30223.8805 | 53411.2722 | 616.1547 | 1088.861 | 92.2649 | 0 | 110.9324 | 948409.706 | 31776.2599 | 1161842.3426 | 1035911.7614 | 0 | 240322.649 | 0 | 1333122.4603 | 3468511.1808 | 2367330.1517 | 10587226.5116 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 21819606.7445 | 38559342.2994 | 31622.7766 | 0.72193 | 30223.8805 | 53411.2722 | 616.1547 | 1088.861
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.7083 | 5.6401 | 0.23282 | 4 | 25646.14 | 43620.9067 | 522.8313 | 889.2712 | 92.4303 | 0 | 62.1309 | 1109722.1018 | 37203.2218 | 1387217.9652 | 1284775.2007 | 0 | 265872.9943 | 0 | 1593068.6787 | 4144837.9186 | 2828937.0474 | 12651635.1285 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 23884015.3614 | 40623750.9163 | 42169.6503 | 0.93129 | 25646.14 | 43620.9067 | 522.8313 | 889.2712
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.664 | 6.7566 | 0.29098 | 4 | 22207.4971 | 36589.5504 | 452.7299 | 745.9275 | 92.5401 | 0 | 80.4447 | 1261075.9846 | 42285.276 | 1602728.5201 | 1532458.5477 | 0 | 280355.4525 | 0 | 1840372.4745 | 4788271.6664 | 3268093.8015 | 14615641.7234 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 25848021.9563 | 42587757.5112 | 56234.1325 | 1.1639 | 22207.4971 | 36589.5504 | 452.7299 | 745.9275
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.3165 | 7.9699 | 0.35599 | 4 | 19608.5746 | 31364.4551 | 399.7473 | 639.4068 | 92.6183 | 0 | 85.2556 | 1417361.7666 | 47521.9493 | 1828995.6961 | 1801745.2246 | 0 | 292750.7768 | 0 | 2101466.4112 | 5467584.5319 | 3731738.7907 | 16689165.1471 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 27921545.38 | 44661280.9349 | 74989.4209 | 1.4239 | 19608.5746 | 31364.4551 | 399.7473 | 639.4068
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.787 | 9.1554 | 0.42332 | 4 | 17650.2218 | 27536.2741 | 359.8236 | 561.3642 | 92.6618 | 0 | 92.0197 | 1563290.3954 | 52399.5863 | 2043508.7029 | 2065156.4185 | 0 | 298456.3591 | 0 | 2348896.4702 | 6111346.7907 | 4171119.7602 | 18654174.4833 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 29886554.7162 | 46626290.2711 | 100000 | 1.6933 | 17650.2218 | 27536.2741 | 359.8236 | 561.3642
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.5964 | 10.2451 | 0.48893 | 4 | 16180.4344 | 24739.8903 | 329.86 | 504.3561 | 92.6768 | 0 | 98.9183 | 1692409.7889 | 56703.7393 | 2235858.2822 | 2307716.6801 | 0 | 297572.5807 | 0 | 2570201.8178 | 6687137.909 | 4564109.0298 | 20411709.8279 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 31644090.0608 | 48383825.6157 | 133352.1432 | 1.9557 | 16180.4344 | 24739.8903 | 329.86 | 504.3561
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.4714 | 11.2011 | 0.54954 | 4 | 15080.64 | 22695.9402 | 307.4392 | 462.6874 | 92.6718 | 0 | 68.8414 | 1802188.3691 | 60353.1302 | 2401265.9562 | 2520942.0022 | 0 | 291665.663 | 0 | 2759801.897 | 7180438.4229 | 4900796.7669 | 21917452.2074 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 33149832.4403 | 49889567.9952 | 177827.941 | 2.1982 | 15080.64 | 22695.9402 | 307.4392 | 462.6874
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6003 | 12.0501 | 0.605 | 4 | 14241.4156 | 21158.6593 | 290.3305 | 431.3479 | 92.6541 | 0 | 71.0561 | 1897215.1409 | 63503.7249 | 2545839.9019 | 2710737.527 | 0 | 283496.5395 | 0 | 2925309.2054 | 7611054.4889 | 5194701.0802 | 23231857.6087 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 34464237.8416 | 51203973.3965 | 237137.3706 | 2.42 | 14241.4156 | 21158.6593 | 290.3305 | 431.3479
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.3138 | 12.7008 | 0.65002 | 4 | 13634.2073 | 20072.3925 | 277.9518 | 409.2029 | 92.6326 | 0 | 85.9711 | 1968577.6313 | 65864.1016 | 2655269.8569 | 2856488.2525 | 0 | 272830.7619 | 0 | 3049421.9357 | 7933970.3542 | 5415097.7935 | 24217520.6877 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 35449900.9206 | 52189636.4755 | 316227.766 | 2.6001 | 13634.2073 | 20072.3925 | 277.9518 | 409.2029
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.0922 | 13.2207 | 0.68711 | 4 | 13180.7203 | 19271.3547 | 268.7068 | 392.8726 | 92.6107 | 0 | 76.5603 | 2024752.4766 | 67718.5055 | 2741933.3741 | 2973180.7118 | 0 | 262151.9627 | 0 | 3147197.442 | 8188362.1651 | 5588725.4317 | 24994022.0696 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 36226402.3026 | 52966137.8574 | 421696.5034 | 2.7484 | 13180.7203 | 19271.3547 | 268.7068 | 392.8726
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0493 | 13.6267 | 0.71689 | 4 | 12841.8433 | 18679.4617 | 261.7983 | 380.8061 | 92.5907 | 0 | 94.7608 | 2068096.846 | 69147.0641 | 2809120.445 | 3064411.9045 | 0 | 252159.5025 | 0 | 3222544.9472 | 8384400.9178 | 5722525.9086 | 25592407.5357 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 36824787.7686 | 53564523.3235 | 562341.3252 | 2.8676 | 12841.8433 | 18679.4617 | 261.7983 | 380.8061
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.3051 | 13.6617 | 0.73195 | 4 | 12572.1233 | 18289.6676 | 256.2997 | 372.8596 | 92.5888 | 0 | 94.5349 | 2071817.3318 | 69269.5512 | 2814902.7667 | 3072297.1753 | 0 | 229378.1646 | 0 | 3220489.3459 | 8379052.6649 | 5718875.6161 | 25576082.6164 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 36808462.8493 | 53548198.4042 | 749894.2093 | 2.9278 | 12572.1233 | 18289.6676 | 256.2997 | 372.8596
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.1102 | 14.1825 | 0.7588 | 4 | 12398.8382 | 17914.0225 | 252.7671 | 365.2016 | 92.5595 | 0 | 86.4555 | 2126760.3799 | 71077.1919 | 2900498.3938 | 3189555.8118 | 0 | 236008.7798 | 0 | 3324321.2173 | 8649201.8953 | 5903258.0169 | 26400681.6866 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 37633061.9195 | 54372797.4744 | 1000000 | 3.0352 | 12398.8382 | 17914.0225 | 252.7671 | 365.2016
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4527 | 14.3659 | 0.77296 | 4 | 12256.8947 | 17671.0482 | 249.8734 | 360.2482 | 92.5483 | 0 | 93.7606 | 2145939.0132 | 71707.3437 | 2930484.151 | 3230888.3538 | 0 | 229919.5537 | 0 | 3357485.982 | 8735489.8101 | 5962151.2917 | 26664065.4991 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 37896445.732 | 54636181.2869 | 1333521.4322 | 3.0918 | 12256.8947 | 17671.0482 | 249.8734 | 360.2482
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.464 | 14.5039 | 0.78377 | 4 | 12150.5864 | 17490.045 | 247.7061 | 356.5582 | 92.5395 | 0 | 87.8805 | 2160317.6134 | 72179.4971 | 2953001.4933 | 3262012.7565 | 0 | 224985.0028 | 0 | 3382273.5816 | 8799982.0596 | 6006168.5772 | 26860920.5815 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38093300.8144 | 54833036.3693 | 1778279.41 | 3.1351 | 12150.5864 | 17490.045 | 247.7061 | 356.5582
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.2307 | 14.6084 | 0.79202 | 4 | 12070.9413 | 17354.8 | 246.0825 | 353.8011 | 92.5327 | 0 | 109.4141 | 2171178.9411 | 72535.9899 | 2970031.4317 | 3285601.3819 | 0 | 221099.9778 | 0 | 3400974.6118 | 8848638.304 | 6039377.4638 | 27009438.1021 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38241818.335 | 54981553.8899 | 2371373.7057 | 3.1681 | 12070.9413 | 17354.8 | 246.0825 | 353.8011
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8102 | 14.6874 | 0.79829 | 4 | 12011.2573 | 17253.6578 | 244.8657 | 351.7392 | 92.5274 | 0 | 104.9183 | 2179367.0415 | 72804.6478 | 2982881.743 | 3303428.6886 | 0 | 218077.0466 | 0 | 3415058.0753 | 8885280.5872 | 6064386.5751 | 27121284.4051 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38353664.638 | 55093400.1929 | 3162277.6602 | 3.1931 | 12011.2573 | 17253.6578 | 244.8657 | 351.7392
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.2512 | 14.7475 | 0.80305 | 4 | 11966.5236 | 17177.8517 | 243.9538 | 350.1937 | 92.5234 | 0 | 105.6927 | 2185584.6648 | 73008.599 | 2992646.4154 | 3316991.3561 | 0 | 215768.5818 | 0 | 3425759.8506 | 8913124.4114 | 6083390.5572 | 27206274.4362 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38438654.6691 | 55178390.224 | 4216965.0343 | 3.2122 | 11966.5236 | 17177.8517 | 243.9538 | 350.1937
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5802 | 14.7923 | 0.80662 | 4 | 11932.9908 | 17121.1934 | 243.2702 | 349.0387 | 92.5203 | 0 | 106.7422 | 2190215.1748 | 73160.4589 | 2999922.3854 | 3327106.3719 | 0 | 213981.1152 | 0 | 3433710.3474 | 8933809.9732 | 6097508.8781 | 27269414.705 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38501794.9379 | 55241530.4928 | 5623413.2519 | 3.2265 | 11932.9908 | 17121.1934 | 243.2702 | 349.0387
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.8313 | 14.8264 | 0.80934 | 4 | 11907.8519 | 17078.6439 | 242.7577 | 348.1713 | 92.518 | 0 | 113.3397 | 2193746.4776 | 73276.2523 | 3005473.3505 | 3334828.4723 | 0 | 212641.0617 | 0 | 3439786.5896 | 8949619.1089 | 6108298.9381 | 27317670.251 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38550050.4839 | 55289786.0388 | 7498942.0933 | 3.2374 | 11907.8519 | 17078.6439 | 242.7577 | 348.1713
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0166 | 14.8516 | 0.81137 | 4 | 11889.0043 | 17046.8734 | 242.3734 | 347.5236 | 92.5162 | 0 | 106.7984 | 2196348.4747 | 73361.5634 | 3009564.7355 | 3340522.9905 | 0 | 211602.6383 | 0 | 3444246.1569 | 8961221.9882 | 6116218.1417 | 27353086.6892 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38585466.9221 | 55325202.477 | 10000000 | 3.2455 | 11889.0043 | 17046.8734 | 242.3734 | 347.5236
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.8803 | [19 empty] | 100 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2196 | [19 empty] | 133.3521 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7034 | [19 empty] | 177.8279 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4652 | [19 empty] | 237.1374 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0605 | [19 empty] | 316.2278 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6884 | [19 empty] | 421.6965 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2564 | [19 empty] | 562.3413 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.0295 | [19 empty] | 749.8942 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.17031 | 0.0008897 | 4 | 3526349.7136 | 8384964.1347 | 71889.4087 | 170938.8354 | 79.8346 | 0 | 30.7048 | 86776.5444 | 2632.257 | 85207.1467 | 68491.7847 | 0 | 55075.5654 | 0 | 116291.4863 | 302566.5927 | 206507.9167 | 923549.294 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12549576.9448 | 29840418.8847 | 1000 | 0.0035588 | 3526349.7136 | 8384964.1347 | 71889.4087 | 170938.8354
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.20748 | 0.0031287 | 4 | 1012039.1066 | 2393659.6286 | 20631.7861 | 48797.9892 | 81.7912 | 0 | 295.4486 | 101357.5598 | 3122.9312 | 99626.8543 | 76793.7976 | 0 | 54731.699 | 0 | 130896.8083 | 340566.6446 | 232443.7329 | 1039540.0277 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12665567.6785 | 29956409.6185 | 1333.5214 | 0.012515 | 1012039.1066 | 2393659.6286 | 20631.7861 | 48797.9892
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.3127 | 0.0062291 | 4 | 522329.2181 | 1216287.8655 | 10648.3876 | 24795.6733 | 85.3306 | 0 | 427.2959 | 139060.4325 | 4406.732 | 137928.5907 | 100006.4395 | 0 | 66883.2826 | 0 | 174831.3361 | 454875.2738 | 310461.7211 | 1388453.8083 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13014481.4592 | 30305323.3991 | 1778.2794 | 0.024916 | 522329.2181 | 1216287.8655 | 10648.3876 | 24795.6733
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.44926 | 0.010633 | 4 | 315765.5989 | 722305.8714 | 6437.3088 | 14725.1822 | 87.8585 | 0 | 77.7644 | 182723.9011 | 5907.3207 | 183942.1926 | 129801.9297 | 0 | 80080.8882 | 0 | 227157.9306 | 591018.3389 | 403382.1605 | 1804014.6623 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13430042.3131 | 30720884.2531 | 2371.3737 | 0.042532 | 315765.5989 | 722305.8714 | 6437.3088 | 14725.1822
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.62354 | 0.016713 | 4 | 208252.5015 | 466891.2022 | 4245.5089 | 9518.2087 | 89.6852 | 0 | 61.4976 | 232988.0467 | 7642.8957 | 238746.9322 | 167818.1425 | 0 | 94213.1771 | 0 | 289149.5858 | 752307.9094 | 513465.6065 | 2296332.2959 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13922359.9468 | 31213201.8867 | 3162.2777 | 0.066853 | 208252.5015 | 466891.2022 | 4245.5089 | 9518.2087
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.265 | 0.84449 | 0.024884 | 4 | 145732.5438 | 319448.0476 | 2970.955 | 6512.3805 | 91.0209 | 0 | 98.373 | 290845.6083 | 9642.0148 | 303996.5285 | 215778.5351 | 0 | 109438.1342 | 0 | 362583.3202 | 943367.423 | 643867.6505 | 2879519.2146 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14505546.8654 | 31796388.8054 | 4216.965 | 0.099535 | 145732.5438 | 319448.0476 | 2970.955 | 6512.3805
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0601 | 1.1056 | 0.035501 | 4 | 106700.2519 | 228464.8732 | 2175.229 | 4657.5655 | 91.9112 | 0 | 97.5683 | 353403.6068 | 11799.5946 | 376846.7068 | 272650.5274 | 0 | 123611.5703 | 0 | 443941.6823 | 1155045.1924 | 788342.0776 | 3525640.9582 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 15151668.609 | 32442510.549 | 5623.4133 | 0.142 | 106700.2519 | 228464.8732 | 2175.229 | 4657.5655
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7324 | 1.4988 | 0.050508 | 4 | 79607.5741 | 165192.5219 | 1622.9081 | 3367.673 | 92.8433 | 0 | 52.1356 | 440193.354 | 14802.3039 | 480362.6752 | 357532.2742 | 0 | 146189.9527 | 0 | 561241.4184 | 1460235.0441 | 996640.4224 | 4457197.4448 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 16083225.0956 | 33374067.0356 | 7498.9421 | 0.20203 | 79607.5741 | 165192.5219 | 1622.9081 | 3367.673
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8802 | 1.9607 | 0.069586 | 4 | 61485.0593 | 123605.272 | 1253.4561 | 2519.8607 | 93.4312 | 0 | 48.812 | 533531.3272 | 18021.085 | 595248.5583 | 457751.907 | 0 | 167346.7721 | 0 | 691040.8633 | 1797946.5744 | 1227135.4811 | 5488022.5684 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 17114050.2192 | 34404892.1592 | 10000 | 0.27834 | 61485.0593 | 123605.272 | 1253.4561 | 2519.8607
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8165 | 2.5387 | 0.09441 | 4 | 48569.5895 | 94356.0431 | 990.1568 | 1923.5756 | 93.8786 | 0 | 58.9322 | 641486.6808 | 21737.6388 | 731667.2418 | 583255.3065 | 0 | 190174.2918 | 0 | 845645.2523 | 2200195.4808 | 1501678.6251 | 6715840.5179 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 18341868.1687 | 35632710.1086 | 13335.2143 | 0.37764 | 48569.5895 | 94356.0431 | 990.1568 | 1923.5756
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6427 | 3.2475 | 0.12621 | 4 | 39175.7887 | 73426.7116 | 798.6514 | 1496.9028 | 94.2179 | 0 | 54.1077 | 764243.7582 | 25955.3604 | 890712.9633 | 736931.2344 | 0 | 213851.6923 | 0 | 1026361.0534 | 2670380.9253 | 1822589.8524 | 8151026.8398 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 19777054.4906 | 37067896.4305 | 17782.7941 | 0.50483 | 39175.7887 | 73426.7116 | 798.6514 | 1496.9028
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5204 | 4.1107 | 0.16641 | 4 | 32224.2654 | 58199.9265 | 656.9352 | 1186.4842 | 94.4787 | 0 | 56.4842 | 903443.8091 | 30728.459 | 1075336.1114 | 923987.5522 | 0 | 238421.3389 | 0 | 1237047.7355 | 3218544.4544 | 2196722.7246 | 9824232.1852 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 21450259.836 | 38741101.7759 | 23713.7371 | 0.66566 | 32224.2654 | 58199.9265 | 656.9352 | 1186.4842
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 5.1331 | 0.2161 | 4 | 27015.4571 | 47019.0539 | 550.7466 | 958.547 | 94.6782 | 0 | 59.9226 | 1057553.0101 | 36002.3581 | 1284250.8019 | 1145510.3887 | 0 | 262544.8319 | 0 | 1476485.9424 | 3841513.5532 | 2621911.9352 | 11725772.8215 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 23351800.4723 | 40642642.4123 | 31622.7766 | 0.86439 | 27015.4571 | 47019.0539 | 550.7466 | 958.547
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.4339 | 6.3017 | 0.27556 | 4 | 23082.4071 | 38769.206 | 470.5661 | 790.3627 | 94.8292 | 0 | 57.6473 | 1222981.9323 | 41652.4666 | 1513079.485 | 1398683.5684 | 0 | 284540.2805 | 0 | 1739765.7158 | 4526513.5174 | 3089438.4862 | 13816655.4521 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 25442683.1029 | 42733525.0429 | 42169.6503 | 1.1023 | 23082.4071 | 38769.206 | 470.5661 | 790.3627
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.087 | 7.5726 | 0.34366 | 4 | 20104.1661 | 32682.5981 | 409.8506 | 666.279 | 94.938 | 0 | 74.3776 | 1392905.2769 | 47443.884 | 1752494.4435 | 1674075.2204 | 0 | 302178.4439 | 0 | 2015947.9348 | 5245082.9986 | 3579876.9222 | 16010005.1243 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 27636032.7751 | 44926874.7151 | 56234.1325 | 1.3746 | 20104.1661 | 32682.5981 | 409.8506 | 666.279
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.9318 | 8.8699 | 0.41733 | 4 | 17852.4435 | 28210.5776 | 363.9462 | 575.1108 | 95.0067 | 0 | 64.2285 | 1557790.9767 | 53049.976 | 1988718.7723 | 1955382.4405 | 0 | 313182.7965 | 0 | 2288568.7352 | 5954386.399 | 4063991.0677 | 18175071.1639 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 29801098.8147 | 47091940.7547 | 74989.4209 | 1.6693 | 17852.4435 | 28210.5776 | 363.9462 | 575.1108
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4554 | 10.1169 | 0.49237 | 4 | 16156.6316 | 24936.0256 | 329.3748 | 508.3546 | 95.0392 | 0 | 78.122 | 1709503.7767 | 58193.618 | 2209340.6729 | 2226101.6958 | 0 | 316874.2441 | 0 | 2542805.4629 | 6615858.2133 | 4515459.1729 | 20194136.8564 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 31820164.5072 | 49111006.4471 | 100000 | 1.9695 | 16156.6316 | 24936.0256 | 329.3748 | 508.3546
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.1922 | 11.2447 | 0.56431 | 4 | 14884.2669 | 22544.3991 | 303.4359 | 459.5981 | 95.0432 | 0 | 74.1803 | 1841811.1689 | 62665.8055 | 2404260.3941 | 2471467.5649 | 0 | 313660.5415 | 0 | 2766607.5352 | 7198145.2975 | 4912882.0726 | 21971500.3803 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 33597528.0311 | 50888369.971 | 133352.1432 | 2.2573 | 14884.2669 | 22544.3991 | 303.4359 | 459.5981
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.9324 | 12.2232 | 0.62992 | 4 | 13932.144 | 20794.4749 | 284.0256 | 423.9235 | 95.0287 | 0 | 82.5675 | 1953250.3598 | 66421.2717 | 2570260.8422 | 2684867.0248 | 0 | 305607.8524 | 0 | 2956358.8669 | 7691839.339 | 5249838.4004 | 23478443.9572 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 35104471.608 | 52395313.5479 | 177827.941 | 2.5197 | 13932.144 | 20794.4749 | 284.0256 | 423.9235
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.9176 | 13.0885 | 0.6895 | 4 | 13203.5681 | 19472.9303 | 269.1726 | 396.982 | 95.0028 | 0 | 76.0526 | 2049427.0416 | 69653.0732 | 2714879.614 | 2874038.5344 | 0 | 295637.1108 | 0 | 3121417.7959 | 8121288.814 | 5542946.4913 | 24789288.4752 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 36415316.126 | 53706158.066 | 237137.3706 | 2.758 | 13203.5681 | 19472.9303 | 269.1726 | 396.982
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.464 | 13.7433 | 0.73723 | 4 | 12677.6954 | 18541.1571 | 258.452 | 377.9866 | 94.9755 | 0 | 74.0689 | 2120813.1826 | 72045.6009 | 2823051.4093 | 3017444.1676 | 0 | 283497.9329 | 0 | 3243572.3944 | 8439110.022 | 5759865.9964 | 25759400.706 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 37385428.3568 | 54676270.2968 | 316227.766 | 2.9489 | 12677.6954 | 18541.1571 | 258.452 | 377.9866
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0734 | 14.2614 | 0.7762 | 4 | 12284.7132 | 17853.7511 | 250.4405 | 363.9729 | 94.9494 | 0 | 79.2315 | 2176505.435 | 73908.2562 | 2907936.9675 | 3131124.5261 | 0 | 271578.6424 | 0 | 3338810.9926 | 8686901.3185 | 5928988.6479 | 26515754.7863 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 38141782.4372 | 55432624.3771 | 421696.5034 | 3.1048 | 12284.7132 | 17853.7511 | 250.4405 | 363.9729
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9117 | 14.6677 | 0.80745 | 4 | 11990.8724 | 17344.4068 | 244.4502 | 353.5892 | 94.9263 | 0 | 75.5762 | 2219706.9511 | 75350.7027 | 2974085.8751 | 3220409.2119 | 0 | 260807.5723 | 0 | 3412640.5221 | 8878990.6097 | 6060093.5361 | 27102084.981 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 38728112.6318 | 56018954.5717 | 562341.3252 | 3.2298 | 11990.8724 | 17344.4068 | 244.4502 | 353.5892
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0971 | 14.9799 | 0.83199 | 4 | 11771.0293 | 16966.6348 | 239.9684 | 345.8878 | 94.9069 | 0 | 73.2624 | 2252623.0643 | 76448.2439 | 3024664.6507 | 3289088.1711 | 0 | 251396.4098 | 0 | 3468746.0105 | 9024965.5816 | 6159724.4539 | 27547656.5857 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39173684.2365 | 56464526.1764 | 749894.2093 | 3.328 | 11771.0293 | 16966.6348 | 239.9684 | 345.8878
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7749 | 15.2192 | 0.85109 | 4 | 11606.4594 | 16685.5119 | 236.6134 | 340.1567 | 94.8911 | 0 | 91.1976 | 2277692.1265 | 77283.2503 | 3063290.0747 | 3341774.8007 | 0 | 243534.1095 | 0 | 3511394.0011 | 9135926.9049 | 6235457.8371 | 27886353.1047 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39512380.7556 | 56803222.6955 | 1000000 | 3.4043 | 11606.4594 | 16685.5119 | 236.6134 | 340.1567
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.0466 | 15.4003 | 0.86576 | 4 | 11483.2108 | 16476.1828 | 234.1008 | 335.8893 | 94.8787 | 0 | 78.9793 | 2296578.3051 | 77911.7995 | 3092449.16 | 3381685.6349 | 0 | 237084.1221 | 0 | 3543426.5184 | 9219268.9443 | 6292340.4915 | 28140744.9759 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39766772.6267 | 57057614.5667 | 1333521.4322 | 3.463 | 11483.2108 | 16476.1828 | 234.1008 | 335.8893
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0166 | 15.5383 | 0.87701 | 4 | 11390.8762 | 16319.7849 | 232.2184 | 332.7009 | 94.8689 | 0 | 79.6022 | 2310917.1964 | 78388.7105 | 3114622.1014 | 3412112.9258 | 0 | 231966.3785 | 0 | 3567722.8519 | 9282483.0201 | 6335485.3972 | 28333698.5817 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39959726.2325 | 57250568.1725 | 1778279.41 | 3.508 | 11390.8762 | 16319.7849 | 232.2184 | 332.7009
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7445 | 15.6417 | 0.88555 | 4 | 11321.6836 | 16203.0791 | 230.8078 | 330.3217 | 94.8614 | 0 | 79.5417 | 2321640.3306 | 78745.19 | 3131223.4187 | 3434938.8584 | 0 | 227905.6134 | 0 | 3585836.8304 | 9329611.8763 | 6367651.8099 | 28477553.9278 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40103581.5786 | 57394423.5185 | 2371373.7057 | 3.5422 | 11321.6836 | 16203.0791 | 230.8078 | 330.3217
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.2929 | 15.7197 | 0.89202 | 4 | 11269.8229 | 16115.8179 | 229.7506 | 328.5427 | 94.8556 | 0 | 68.3232 | 2329698.2856 | 79012.9709 | 3143709.6298 | 3452131.7813 | 0 | 224744.0333 | 0 | 3599425.7134 | 9364967.3625 | 6391782.6557 | 28585472.4326 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40211500.0834 | 57502342.0233 | 3162277.6602 | 3.5681 | 11269.8229 | 16115.8179 | 229.7506 | 328.5427
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6996 | 15.7774 | 0.89688 | 4 | 11230.9474 | 16050.6914 | 228.9581 | 327.2151 | 94.8513 | 0 | 77.9805 | 2335662.6903 | 79211.1249 | 3152957.92 | 3464880.1075 | 0 | 222268.3011 | 0 | 3609442.256 | 9391028.3518 | 6409569.8164 | 28665020.568 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40291048.2188 | 57581890.1588 | 4216965.0343 | 3.5875 | 11230.9474 | 16050.6914 | 228.9581 | 327.2151
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.024 | 15.8235 | 0.90064 | 4 | 11201.8028 | 16001.4183 | 228.3639 | 326.2106 | 94.8479 | 0 | 80.995 | 2340411.4088 | 79368.8581 | 3160324.8829 | 3475043.5047 | 0 | 220487.3348 | 0 | 3617498.0358 | 9411987.8384 | 6423875.0967 | 28728996.9603 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40355024.6111 | 57645866.551 | 5623413.2519 | 3.6025 | 11201.8028 | 16001.4183 | 228.3639 | 326.2106
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2527 | 15.8559 | 0.90339 | 4 | 11179.9518 | 15964.9289 | 227.9184 | 325.4667 | 94.8454 | 0 | 79.8292 | 2343756.9991 | 79479.9668 | 3165517.1134 | 3482211.1849 | 0 | 219036.7817 | 0 | 3623100.7979 | 9426565.076 | 6433824.3609 | 28773492.2808 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40399519.9316 | 57690361.8716 | 7498942.0933 | 3.6136 | 11179.9518 | 15964.9289 | 227.9184 | 325.4667
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.4307 | 15.8812 | 0.9055 | 4 | 11163.5682 | 15937.4196 | 227.5844 | 324.9059 | 94.8435 | 0 | 79.2183 | 2346358.0649 | 79566.3397 | 3169554.9935 | 3487787.8798 | 0 | 217974.6079 | 0 | 3627484.3355 | 9437970.1416 | 6441608.5525 | 28808304.9154 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40434332.5662 | 57725174.5061 | 10000000 | 3.622 | 11163.5682 | 15937.4196 | 227.5844 | 324.9059
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6868 | [19 empty] | 100 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.96 | [19 empty] | 133.3521 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7687 | [19 empty] | 177.8279 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0514 | [19 empty] | 237.1374 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4551 | [19 empty] | 316.2278 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4326 | [19 empty] | 421.6965 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2592 | [19 empty] | 562.3413 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0611 | [19 empty] | 749.8942 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.17628 | 0.0017281 | 4 | 1875789.9915 | 4458199.6335 | 38240.5162 | 90886.4297 | 81.35 | 0 | 30.5019 | 90222.7599 | 2766.8911 | 87481.5571 | 69189.8439 | 0 | 53935.4403 | 0 | 118402.632 | 308059.3608 | 210256.8437 | 940315.3289 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 12965850.4885 | 30816002.9407 | 1000 | 0.0069122 | 1875789.9915 | 4458199.6335 | 38240.5162 | 90886.4297
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0987 | 0.24942 | 0.0043164 | 4 | 765324.8615 | 1799184.295 | 15602.1825 | 36678.8054 | 84.837 | 0 | 340.1548 | 118433.0733 | 3732.9776 | 115151.5748 | 85066.2944 | 0 | 61252.7401 | 0 | 149618.2975 | 389276.1191 | 265688.9501 | 1188220.0268 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13213755.1864 | 31063907.6386 | 1333.5214 | 0.017266 | 765324.8615 | 1799184.295 | 15602.1825 | 36678.8054
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.925 | 0.37277 | 0.0081198 | 4 | 418994.3955 | 968581.8831 | 8541.7675 | 19745.8518 | 88.2186 | 0 | 76.4292 | 161071.3461 | 5212.732 | 158383.7872 | 111433.8558 | 0 | 75015.7359 | 0 | 199335.8082 | 518630.8836 | 353976.2349 | 1583060.3836 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13608595.5432 | 31458747.9954 | 1778.2794 | 0.032479 | 418994.3955 | 968581.8831 | 8541.7675 | 19745.8518
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9534 | 0.52825 | 0.013486 | 4 | 260757.7655 | 591665.0155 | 5315.8997 | 12061.8916 | 90.5764 | 0 | 70.0114 | 209205.3946 | 6897.1369 | 208936.7152 | 144611.573 | 0 | 89171.1902 | 0 | 256940.5839 | 668506.6935 | 456269.5547 | 2040538.842 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14066074.0015 | 31916226.4537 | 2371.3737 | 0.053943 | 260757.7655 | 591665.0155 | 5315.8997 | 12061.8916
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4024 | 0.74866 | 0.02095 | 4 | 175093.9046 | 388102.9558 | 3569.5261 | 7912.0037 | 92.4416 | 0 | 59.0443 | 270595.3653 | 9052.1369 | 275764.9059 | 191399.0414 | 0 | 107922.9132 | 0 | 333346.4015 | 867298.9578 | 591949.3599 | 2647329.082 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14672864.2415 | 32523016.6937 | 3162.2777 | 0.0838 | 175093.9046 | 388102.9558 | 3569.5261 | 7912.0037
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8614 | 0.97109 | 0.030603 | 4 | 124451.0171 | 270271.6077 | 2537.1023 | 5509.8523 | 93.5299 | 0 | 60.9999 | 327098.6504 | 11036.0583 | 339269.8198 | 238668.1269 | 0 | 119919.5477 | 0 | 404036.9592 | 1051221.2884 | 717480.1298 | 3208730.5804 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 15234265.74 | 33084418.1922 | 4216.965 | 0.12241 | 124451.0171 | 270271.6077 | 2537.1023 | 5509.8523
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3124 | 1.3466 | 0.044063 | 4 | 91651.0134 | 192926.8044 | 1868.4299 | 3933.0739 | 94.6538 | 0 | 51.4908 | 414449.5117 | 14105.4871 | 440308.4274 | 318353.8819 | 0 | 145648.1262 | 0 | 519817.5194 | 1352458.5562 | 923080.7549 | 4128222.2648 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 16153757.4244 | 34003909.8766 | 5623.4133 | 0.17625 | 91651.0134 | 192926.8044 | 1868.4299 | 3933.0739
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7802 | 1.725 | 0.061332 | 4 | 69323.5162 | 142083.2982 | 1413.2536 | 2896.5602 | 95.3217 | 0 | 85.396 | 495168.7951 | 16937.369 | 536479.7315 | 398374.4452 | 0 | 161431.822 | 0 | 627272.9435 | 1632035.5276 | 1113897.7826 | 4981598.4165 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 17007133.576 | 34857286.0282 | 7498.9421 | 0.24533 | 69323.5162 | 142083.2982 | 1413.2536 | 2896.5602
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2024 | 2.2495 | 0.084119 | 4 | 53929.2004 | 106979.6139 | 1099.4197 | 2180.9241 | 95.887 | 0 | 122.6211 | 598701.4158 | 20562.0784 | 663153.6936 | 509220.2543 | 0 | 184405.9054 | 0 | 770656.9055 | 2005091.1847 | 1368515.9341 | 6120307.3719 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 18145842.5315 | 35995994.9837 | 10000 | 0.33648 | 53929.2004 | 106979.6139 | 1099.4197 | 2180.9241
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4755 | 2.905 | 0.11368 | 4 | 42887.0488 | 82143.827 | 874.3105 | 1674.613 | 96.3182 | 0 | 107.4336 | 718385.3331 | 24744.3951 | 813421.255 | 647787.9595 | 0 | 209189.6478 | 0 | 941276.1503 | 2449007.4608 | 1671497.914 | 7475310.1156 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 19500845.2751 | 37350997.7274 | 13335.2143 | 0.4547 | 42887.0488 | 82143.827 | 874.3105 | 1674.613
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7102 | 3.7083 | 0.15145 | 4 | 34807.2835 | 64273.4427 | 709.5936 | 1310.3011 | 96.6462 | 0 | 107.1429 | 854562.4886 | 29493.4396 | 988623.2758 | 817605.6263 | 0 | 234948.4939 | 0 | 1140840.9964 | 2968234.2541 | 2025880.8695 | 9060189.4442 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 21085724.6038 | 38935877.056 | 17782.7941 | 0.60578 | 34807.2835 | 64273.4427 | 709.5936 | 1310.3011
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.0445 | 4.6806 | 0.19896 | 4 | 28803.4347 | 51233.0257 | 587.197 | 1044.4545 | 96.898 | 0 | 81.5481 | 1008166.5888 | 34839.1522 | 1190834.2149 | 1023118.0691 | 0 | 261357.8312 | 0 | 1372143.1839 | 3570035.0994 | 2436622.3122 | 10897116.4518 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 22922651.6113 | 40772804.0635 | 23713.7371 | 0.79583 | 28803.4347 | 51233.0257 | 587.197 | 1044.4545
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4452 | 5.8168 | 0.25709 | 4 | 24292.9792 | 41651.0096 | 495.2452 | 849.1122 | 97.0894 | 0 | 95.8011 | 1176140.6666 | 40672.6747 | 1416744.6685 | 1263107.8918 | 0 | 286453.2038 | 0 | 1631416.4511 | 4244610.9562 | 2897034.1956 | 12956180.7082 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 24981715.8677 | 42831868.32 | 31622.7766 | 1.0284 | 24292.9792 | 41651.0096 | 495.2452 | 849.1122
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.8297 | 7.1039 | 0.32596 | 4 | 20881.859 | 34572.1159 | 425.7049 | 704.7993 | 97.2331 | 0 | 112.567 | 1355117.6988 | 46875.0667 | 1662239.0361 | 1534850.8625 | 0 | 308957.8114 | 0 | 1914135.7855 | 4980188.6706 | 3399081.1003 | 15201446.0319 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 27226981.1915 | 45077133.6437 | 42169.6503 | 1.3039 | 20881.859 | 34572.1159 | 425.7049 | 704.7993
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.7749 | 8.4761 | 0.40355 | 4 | 18297.6341 | 29355.8123 | 373.022 | 598.4579 | 97.3326 | 0 | 145.4626 | 1535647.8587 | 53116.8909 | 1914343.6844 | 1824685.3323 | 0 | 325787.1716 | 0 | 2204896.5658 | 5736688.5777 | 3915407.8314 | 17510573.9129 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 29536109.0724 | 47386261.5246 | 56234.1325 | 1.6142 | 18297.6341 | 29355.8123 | 373.022 | 598.4579
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.7755 | 9.8542 | 0.48609 | 4 | 16344.7254 | 25525.1107 | 333.2093 | 520.3639 | 97.39 | 0 | 152.6304 | 1708333.4336 | 59071.3932 | 2159436.1184 | 2116100.87 | 0 | 335229.1538 | 0 | 2487486.678 | 6471930.0824 | 4417225.2661 | 19754812.9955 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 31780348.1551 | 49630500.6073 | 74989.4209 | 1.9444 | 16344.7254 | 25525.1107 | 333.2093 | 520.3639
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.2823 | 11.1525 | 0.56863 | 4 | 14874.7856 | 22722.7086 | 303.2426 | 463.2332 | 97.4109 | 0 | 149.7833 | 1864397.0611 | 64436.1821 | 2384158.6956 | 2391186.1564 | 0 | 336660.4769 | 0 | 2745927.0431 | 7144338.8991 | 4876158.1001 | 21807262.6144 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 33832797.774 | 51682950.2262 | 100000 | 2.2745 | 14874.7856 | 22722.7086 | 303.2426 | 463.2332
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.9239 | 12.3141 | 0.64663 | 4 | 13772.1988 | 20673.4602 | 280.7649 | 421.4565 | 97.4048 | 0 | 171.1653 | 1999283.5837 | 69057.9134 | 2580838.7524 | 2637907.5174 | 0 | 331383.1297 | 0 | 2971203.6496 | 7730462.4187 | 5276199.4459 | 23596336.4108 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 35621871.5703 | 53472024.0225 | 133352.1432 | 2.5865 | 13772.1988 | 20673.4602 | 280.7649 | 421.4565
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.5017 | 13.3096 | 0.71679 | 4 | 12946.9485 | 19172.6745 | 263.9411 | 390.8609 | 97.3822 | 0 | 146.3641 | 2111692.9843 | 72897.2536 | 2746493.0164 | 2849924.09 | 0 | 321473.4272 | 0 | 3159967.5009 | 8221587.2388 | 5611402.2272 | 25095437.7384 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 37120972.898 | 54971125.3502 | 177827.941 | 2.8672 | 12946.9485 | 19172.6745 | 263.9411 | 390.8609
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.587 | 13.9255 | 0.77114 | 4 | 12315.3945 | 18102.2935 | 251.066 | 369.0397 | 97.3607 | 0 | 319.373 | 2179880.4056 | 75220.198 | 2847763.3227 | 2981410.0226 | 0 | 298082.4145 | 0 | 3269118.9817 | 8505577.0018 | 5805231.0759 | 25962283.4227 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 37987818.5823 | 55837971.0345 | 237137.3706 | 3.0846 | 12315.3945 | 18102.2935 | 251.066 | 369.0397
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.723 | 14.8471 | 0.83032 | 4 | 11856.9276 | 17231.3777 | 241.7195 | 351.2849 | 97.3184 | 0 | 150.0844 | 2280078.744 | 78624.8917 | 2997658.9654 | 3178605.4781 | 0 | 297004.7945 | 0 | 3444469.4208 | 8961802.875 | 6116614.6088 | 27354859.7785 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 39380394.938 | 57230547.3902 | 316227.766 | 3.3213 | 11856.9276 | 17231.3777 | 241.7195 | 351.2849
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2017 | 15.3675 | 0.87109 | 4 | 11515.7834 | 16638.7015 | 234.7648 | 339.2024 | 97.2892 | 0 | 140.4404 | 2335738.4538 | 80511.3166 | 3081493.9649 | 3290232.5916 | 0 | 284493.0969 | 0 | 3538263.0753 | 9205834.7244 | 6283171.3604 | 28099738.5839 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 40125273.7435 | 57975426.1957 | 421696.5034 | 3.4844 | 11515.7834 | 16638.7015 | 234.7648 | 339.2024
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.9083 | 15.7714 | 0.90351 | 4 | 11260.5333 | 16199.6214 | 229.5612 | 330.2512 | 97.2641 | 0 | 127.7738 | 2378488.9229 | 81957.7509 | 3146163.7743 | 3376993.5289 | 0 | 273206.4868 | 0 | 3610156.0808 | 9392885.5775 | 6410837.4112 | 28670689.5333 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 40696224.6928 | 58546377.145 | 562341.3252 | 3.6141 | 11260.5333 | 16199.6214 | 229.5612 | 330.2512
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9929 | 16.0817 | 0.92892 | 4 | 11069.454 | 15873.4587 | 225.6658 | 323.6019 | 97.2433 | 0 | 162.192 | 2411089.2926 | 83059.2727 | 3195643.6558 | 3443758.7847 | 0 | 263494.271 | 0 | 3664847.658 | 9535181.8424 | 6507957.5358 | 29105032.313 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41130567.4726 | 58980719.9248 | 749894.2093 | 3.7157 | 11069.454 | 15873.4587 | 225.6658 | 323.6019
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5935 | 16.3196 | 0.94865 | 4 | 10926.3495 | 15630.4558 | 222.7484 | 318.648 | 97.2265 | 0 | 147.094 | 2435933.4609 | 83897.8357 | 3233447.682 | 3494992.9376 | 0 | 255462.4601 | 0 | 3706456.4068 | 9643439.2717 | 6581845.4558 | 29435475.5105 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41461010.6701 | 59311163.1223 | 1000000 | 3.7946 | 10926.3495 | 15630.4558 | 222.7484 | 318.648
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8117 | 16.5004 | 0.96381 | 4 | 10819.137 | 15449.2225 | 220.5627 | 314.9533 | 97.2133 | 0 | 154.8209 | 2454732.3119 | 84531.8315 | 3262108.5904 | 3533964.8727 | 0 | 248953.0259 | 0 | 3737873.3466 | 9725179.7047 | 6637634.9809 | 29684978.6645 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41710513.8241 | 59560666.2763 | 1333521.4322 | 3.8553 | 10819.137 | 15449.2225 | 220.5627 | 314.9533
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.713 | 16.634 | 0.97528 | 4 | 10738.7932 | 15314.4617 | 218.9248 | 312.206 | 97.2032 | 0 | 145.7375 | 2468580.6813 | 84998.5795 | 3283252.8583 | 3562787.3813 | 0 | 243633.198 | 0 | 3760868.5523 | 9785008.513 | 6678469.3719 | 29867599.1355 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41893134.2951 | 59743286.7473 | 1778279.41 | 3.9011 | 10738.7932 | 15314.4617 | 218.9248 | 312.206
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4124 | 16.7377 | 0.98409 | 4 | 10678.5728 | 15213.2425 | 217.6972 | 310.1425 | 97.1953 | 0 | 133.8109 | 2479292.0428 | 85359.427 | 3299625.3931 | 3585146.9223 | 0 | 239583.5801 | 0 | 3778712.8725 | 9831435.7736 | 6710156.9313 | 30009312.9426 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42034848.1022 | 59885000.5544 | 2371373.7057 | 3.9364 | 10678.5728 | 15213.2425 | 217.6972 | 310.1425
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.9387 | 16.8156 | 0.99077 | 4 | 10633.4294 | 15137.5485 | 216.7768 | 308.5994 | 97.1892 | 0 | 158.8609 | 2487333.7098 | 85630.2383 | 3311927.6123 | 3601971.6374 | 0 | 236435.2231 | 0 | 3792086.3841 | 9866230.9076 | 6733905.3252 | 30115521.0378 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42141056.1974 | 59991208.6496 | 3162277.6602 | 3.9631 | 10633.4294 | 15137.5485 | 216.7768 | 308.5994
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3332 | 16.874 | 0.9958 | 4 | 10599.5849 | 15080.9359 | 216.0869 | 307.4453 | 97.1846 | 0 | 148.8894 | 2493349.6598 | 85832.7756 | 3321136.7008 | 3614579.5609 | 0 | 234001.2064 | 0 | 3802070.9623 | 9892208.732 | 6751635.7242 | 30194815.322 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42220350.4816 | 60070502.9338 | 4216965.0343 | 3.9832 | 10599.5849 | 15080.9359 | 216.0869 | 307.4453
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.6233 | 16.9169 | 0.99956 | 4 | 10574.2097 | 15038.7099 | 215.5696 | 306.5844 | 97.1812 | 0 | 144.0724 | 2497766.3595 | 85981.4406 | 3327900.8876 | 3623847.5724 | 0 | 232097.3582 | 0 | 3809361.5111 | 9911177.2445 | 6764582.1237 | 30252714.4977 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42278249.6572 | 60128402.1095 | 5623413.2519 | 3.9982 | 10574.2097 | 15038.7099 | 215.5696 | 306.5844
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.8519 | 16.9507 | 1.0025 | 4 | 10555.1833 | 15006.8095 | 215.1817 | 305.9341 | 97.1785 | 0 | 153.4981 | 2501243.3576 | 86098.4578 | 3333227.7883 | 3631150.6042 | 0 | 230717.3031 | 0 | 3815150.6293 | 9926239.3423 | 6774862.315 | 30298689.7975 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42324224.9571 | 60174377.4093 | 7498942.0933 | 4.0098 | 10555.1833 | 15006.8095 | 215.1817 | 305.9341
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0176 | 16.9753 | 1.0046 | 4 | 10540.9169 | 14983.0554 | 214.8908 | 305.4499 | 97.1765 | 0 | 142.0519 | 2503763.011 | 86183.2455 | 3337089.0583 | 3636446.7183 | 0 | 229632.7045 | 0 | 3819314.7477 | 9937073.5242 | 6782256.8667 | 30331759.8762 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42357295.0357 | 60207447.488 | 10000000 | 4.0184 | 10540.9169 | 14983.0554 | 214.8908 | 305.4499
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9936 | [19 empty] | 100 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.604 | [19 empty] | 133.3521 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2998 | [19 empty] | 177.8279 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5944 | [19 empty] | 237.1374 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6932 | [19 empty] | 316.2278 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.537 | [19 empty] | 421.6965 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5784 | [19 empty] | 562.3413 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8301 | [19 empty] | 749.8942 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.2018 | 0.0025979 | 4 | 1295702.5267 | 3068064.6324 | 26414.6486 | 62546.6474 | 83.9663 | 0 | 282.0314 | 101536.8252 | 3175.1613 | 97265.704 | 74052.2781 | 0 | 57656.4953 | 0 | 130137.7209 | 338591.6549 | 231095.7618 | 1033511.6015 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13464414.3607 | 31882081.4524 | 1000 | 0.010392 | 1295702.5267 | 3068064.6324 | 26414.6486 | 62546.6474
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.30036 | 0.0057604 | 4 | 598633.2581 | 1397961.2268 | 12203.9487 | 28499.3305 | 87.9251 | 0 | 396.6595 | 138368.1143 | 4460.9963 | 133281.2554 | 94703.0372 | 0 | 69082.5377 | 0 | 171559.4169 | 446362.4112 | 304651.5175 | 1362469.2866 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13793372.0458 | 32211039.1374 | 1333.5214 | 0.023041 | 598633.2581 | 1397961.2268 | 12203.9487 | 28499.3305
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.254 | 0.43861 | 0.010397 | 4 | 341929.7828 | 784789.5084 | 6970.7011 | 15998.9956 | 91.0195 | 0 | 77.0578 | 184567.6731 | 6095.3227 | 179993.1337 | 123644.1523 | 0 | 83400.5679 | 0 | 225303.3314 | 586193.0522 | 400088.8032 | 1789286.0364 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14220188.7956 | 32637855.8873 | 1778.2794 | 0.041588 | 341929.7828 | 784789.5084 | 6970.7011 | 15998.9956
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 0.61348 | 0.016874 | 4 | 218059.0004 | 490931.1459 | 4445.4277 | 10008.2954 | 93.2302 | 0 | 57.2118 | 237121.6168 | 7966.3013 | 235008.08 | 160027.9055 | 0 | 98310.5094 | 0 | 287989.421 | 749289.3988 | 511405.411 | 2287118.6438 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14718021.403 | 33135688.4947 | 2371.3737 | 0.067496 | 218059.0004 | 490931.1459 | 4445.4277 | 10008.2954
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.846 | 0.84984 | 0.025644 | 4 | 149642.5095 | 329193.4651 | 3050.665 | 6711.0541 | 94.9333 | 0 | 51.2134 | 301418.2139 | 10261.591 | 304600.9733 | 209257.6816 | 0 | 116866.6173 | 0 | 367537.9801 | 956258.4317 | 652666.0288 | 2918867.5177 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 15349770.2769 | 33767437.3686 | 3162.2777 | 0.10258 | 149642.5095 | 329193.4651 | 3050.665 | 6711.0541
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.507 | 1.1136 | 0.037218 | 4 | 107483.6456 | 231199.464 | 2191.1995 | 4713.3138 | 96.0231 | 0 | 100.1018 | 366859.7058 | 12594.0178 | 377824.3499 | 263899.2448 | 0 | 131543.4451 | 0 | 449561.0978 | 1169665.7587 | 798320.9146 | 3570268.5346 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 16001171.2938 | 34418838.3854 | 4216.965 | 0.14887 | 107483.6456 | 231199.464 | 2191.1995 | 4713.3138
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.936 | 1.5029 | 0.053186 | 4 | 79544.498 | 166116.2889 | 1621.6222 | 3386.5052 | 97.0755 | 0 | 108.8423 | 455746.3227 | 15768.8495 | 479847.7858 | 344267.4911 | 0 | 154604.955 | 0 | 565591.8076 | 1471553.8645 | 1004365.7499 | 4491746.8261 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 16922649.5853 | 35340316.677 | 5623.4133 | 0.21274 | 79544.498 | 166116.2889 | 1621.6222 | 3386.5052
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8861 | 1.9746 | 0.073843 | 4 | 60846.9102 | 123201.062 | 1240.4466 | 2511.6203 | 97.7909 | 0 | 87.5241 | 554346.5779 | 19279.3944 | 596612.7537 | 441424.5534 | 0 | 177524.2349 | 0 | 697783.1305 | 1815488.5707 | 1239108.254 | 5541567.4695 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 17972470.2287 | 36390137.3204 | 7498.9421 | 0.29537 | 60846.9102 | 123201.062 | 1240.4466 | 2511.6203
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6009 | 2.569 | 0.10086 | 4 | 47666.2921 | 93319.4213 | 971.7418 | 1902.4426 | 98.336 | 0 | 100.3748 | 669058.3752 | 23356.7669 | 736117.9738 | 564017.6613 | 0 | 202596.2331 | 0 | 856107.334 | 2227415.6712 | 1520256.9644 | 6798926.9798 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 19229829.739 | 37647496.8307 | 10000 | 0.40343 | 47666.2921 | 93319.4213 | 971.7418 | 1902.4426
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1929 | 3.3043 | 0.13572 | 4 | 38150.2946 | 72076.7722 | 777.7454 | 1469.3825 | 98.7497 | 0 | 110.4609 | 800474.5152 | 28018.746 | 900026.1845 | 715717.5531 | 0 | 229017.7718 | 0 | 1042569.3606 | 2712551.6158 | 1851372.2151 | 8279747.9621 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 20710650.7213 | 39128317.813 | 13335.2143 | 0.54287 | 38150.2946 | 72076.7722 | 777.7454 | 1469.3825
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8102 | 4.2039 | 0.18009 | 4 | 31152.2245 | 56719.0017 | 635.0802 | 1156.2936 | 99.0662 | 0 | 103.5022 | 949953.465 | 33309.9732 | 1090981.1602 | 901267.2712 | 0 | 256506.6237 | 0 | 1260487.2124 | 3279529.1652 | 2238346.0428 | 10010380.9138 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 22441283.673 | 40858950.7647 | 17782.7941 | 0.72037 | 31152.2245 | 56719.0017 | 635.0802 | 1156.2936
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.5628 | 5.2856 | 0.23556 | 4 | 25931.6029 | 45478.2053 | 528.6508 | 927.1347 | 99.3092 | 0 | 140.2456 | 1117613.0812 | 39231.4489 | 1310045.463 | 1124145.5403 | 0 | 284330.7257 | 0 | 1511392.8411 | 3932334.1431 | 2683898.8541 | 12002992.0974 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 24433894.8566 | 42851561.9482 | 23713.7371 | 0.94224 | 25931.6029 | 45478.2053 | 528.6508 | 927.1347
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.4239 | 6.545 | 0.30303 | 4 | 21996.0236 | 37190.6103 | 448.4187 | 758.1809 | 99.4942 | 0 | 141.2719 | 1300553.2202 | 45678.8069 | 1554112.6186 | 1383634.827 | 0 | 310711.855 | 0 | 1791929.6178 | 4662233.2903 | 3182070.02 | 14230924.2559 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 26661827.0151 | 45079494.1068 | 31622.7766 | 1.2121 | 21996.0236 | 37190.6103 | 448.4187 | 758.1809
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.1741 | 7.9467 | 0.38193 | 4 | 19014.129 | 31069.6871 | 387.6287 | 633.3976 | 99.63 | 0 | 124.9193 | 1492328.2035 | 52422.443 | 1814921.5646 | 1672448.9569 | 0 | 333147.8435 | 0 | 2092454.9145 | 5444138.466 | 3715736.3689 | 16617598.7609 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 29048501.5201 | 47466168.6118 | 42169.6503 | 1.5277 | 19014.129 | 31069.6871 | 387.6287 | 633.3976
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.3823 | 9.42 | 0.46957 | 4 | 16754.5965 | 26560.1851 | 341.5651 | 541.4653 | 99.7194 | 0 | 159.7472 | 1683361.3798 | 59122.787 | 2079316.3468 | 1976234.3327 | 0 | 349012.7061 | 0 | 2397348.5454 | 6237409.1514 | 4257159.9118 | 19038965.1611 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 31469867.9203 | 49887535.012 | 56234.1325 | 1.8783 | 16754.5965 | 26560.1851 | 341.5651 | 541.4653
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.4614 | 10.869 | 0.56112 | 4 | 15047.9285 | 23253.7305 | 306.7724 | 474.0587 | 99.7646 | 0 | 152.1036 | 1862628.4691 | 65391.3686 | 2331392.7792 | 2275446.0444 | 0 | 356312.341 | 0 | 2687556.6909 | 6992471.2159 | 4772505.2858 | 21343704.1948 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 33774606.954 | 52192274.0457 | 74989.4209 | 2.2445 | 15047.9285 | 23253.7305 | 306.7724 | 474.0587
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9487 | 12.2183 | 0.65134 | 4 | 13763.9837 | 20833.1618 | 280.5974 | 424.7122 | 99.7734 | 0 | 144.2541 | 2023060.6747 | 70982.1911 | 2560185.1791 | 2554716.2227 | 0 | 355518.8997 | 0 | 2950140.6352 | 7675660.7759 | 5238796.1986 | 23429060.777 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 35859963.5362 | 54277630.6279 | 100000 | 2.6053 | 13763.9837 | 20833.1618 | 280.5974 | 424.7122
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.466 | 13.4081 | 0.73533 | 4 | 12801.0623 | 19062.7923 | 260.967 | 388.6208 | 99.7569 | 0 | 158.9559 | 2159936.7035 | 75735.2607 | 2757779.3802 | 2801606.9107 | 0 | 347944.6593 | 0 | 3175771.1366 | 8262705.0572 | 5639465.9832 | 25220945.0914 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 37651847.8505 | 56069514.9422 | 133352.1432 | 2.9413 | 12801.0623 | 19062.7923 | 260.967 | 388.6208
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.8922 | 14.4203 | 0.81008 | 4 | 12080.2055 | 17764.1322 | 246.2713 | 362.1459 | 99.7261 | 0 | 167.6226 | 2273342.2793 | 79659.9694 | 2923181.7096 | 3012253.0041 | 0 | 336194.4202 | 0 | 3363606.2393 | 8751413.4641 | 5973019.5128 | 26712670.5989 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 39143573.3581 | 57561240.4498 | 177827.941 | 3.2403 | 12080.2055 | 17764.1322 | 246.2713 | 362.1459
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1787 | 15.2493 | 0.87388 | 4 | 11540.9539 | 16809.881 | 235.278 | 342.6922 | 99.6901 | 0 | 141.2955 | 2364284.735 | 82797.6689 | 3056945.0255 | 3185223.2741 | 0 | 322214.1585 | 0 | 3514471.2962 | 9143933.3955 | 6240922.4315 | 27910791.9853 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 40341694.7445 | 58759361.8361 | 237137.3706 | 3.4955 | 11540.9539 | 16809.881 | 235.278 | 342.6922
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7756 | 15.9672 | 0.92956 | 4 | 11125.9824 | 16079.3161 | 226.8182 | 327.7986 | 99.6514 | 0 | 153.2473 | 2441716.5507 | 85461.9971 | 3171635.398 | 3335377.8044 | 0 | 308967.1731 | 0 | 3643831.9801 | 9480503.3595 | 6470638.3477 | 28938132.6106 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 41369035.3698 | 59786702.4615 | 316227.766 | 3.7182 | 11125.9824 | 16079.3161 | 226.8182 | 327.7986
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.0982 | 16.4842 | 0.97189 | 4 | 10827.6956 | 15565.2653 | 220.7372 | 317.319 | 99.6194 | 0 | 134.5095 | 2496759.2438 | 87351.6231 | 3253619.4674 | 3443756.083 | 0 | 295578.049 | 0 | 3735055.1418 | 9717847.3139 | 6632630.4735 | 29662597.3956 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42093500.1548 | 60511167.2465 | 421696.5034 | 3.8876 | 10827.6956 | 15565.2653 | 220.7372 | 317.319
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.6922 | 16.8868 | 1.0055 | 4 | 10604.4049 | 15183.5854 | 216.1851 | 309.5379 | 99.5921 | 0 | 160.4652 | 2539207.1149 | 88806.3235 | 3317105.3943 | 3528276.1923 | 0 | 283792.4154 | 0 | 3805303.1018 | 9900618.0958 | 6757375.2878 | 30220483.9258 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42651386.685 | 61069053.7767 | 562341.3252 | 4.022 | 10604.4049 | 15183.5854 | 216.1851 | 309.5379
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6802 | 17.1947 | 1.0317 | 4 | 10437.1816 | 14899.9788 | 212.7761 | 303.7562 | 99.5699 | 0 | 147.0467 | 2571430.5727 | 89909.1041 | 3365453.0858 | 3592990.6485 | 0 | 273707.6225 | 0 | 3858461.5031 | 10038925.3518 | 6851772.8319 | 30642650.7205 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43073553.4796 | 61491220.5713 | 749894.2093 | 4.1269 | 10437.1816 | 14899.9788 | 212.7761 | 303.7562
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1882 | 17.4278 | 1.0519 | 4 | 10311.9015 | 14688.9427 | 210.2221 | 299.454 | 99.5523 | 0 | 137.4484 | 2595700.2622 | 90738.7929 | 3401955.3288 | 3642049.084 | 0 | 265317.0863 | 0 | 3898346.6161 | 10142698.2343 | 6922599.9565 | 30959405.361 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43390308.1202 | 61807975.2119 | 1000000 | 4.2078 | 10311.9015 | 14688.9427 | 210.2221 | 299.454
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.537 | 17.0177 | 1.0449 | 4 | 10212.3637 | 14619.0632 | 208.1928 | 298.0294 | 99.5825 | 0 | 159.1621 | 2552918.6556 | 89275.5634 | 3337670.3726 | 3555775.7452 | 0 | 231516.6076 | 0 | 3809191.2083 | 9910734.1514 | 6764279.7036 | 30251362.0076 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42682264.7667 | 61099931.8584 | 1333521.4322 | 4.1795 | 10212.3637 | 14619.0632 | 208.1928 | 298.0294
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0299 | 17.7121 | 1.0794 | 4 | 10135.6024 | 14401.4306 | 206.628 | 293.5926 | 99.5299 | 0 | 146.4936 | 2625137.0607 | 91744.091 | 3446330.9462 | 3701919.4374 | 0 | 250104.3419 | 0 | 3944941.9921 | 10263929.8446 | 7005343.0216 | 31329450.7356 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43760353.4948 | 62178020.5865 | 1778279.41 | 4.3175 | 10135.6024 | 14401.4306 | 206.628 | 293.5926
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.8749 | 17.8424 | 1.0884 | 4 | 10094.8945 | 14325.4257 | 205.7981 | 292.0432 | 99.5193 | 0 | 160.2561 | 2638569.2443 | 92202.4089 | 3466618.2887 | 3729375.9959 | 0 | 249132.6218 | 0 | 3968600.4383 | 10325484.2685 | 7047355.1807 | 31517338.4471 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43948241.2063 | 62365908.298 | 2371373.7057 | 4.3535 | 10094.8945 | 14325.4257 | 205.7981 | 292.0432
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3802 | 17.9202 | 1.0952 | 4 | 10055.3439 | 14259.3335 | 204.9918 | 290.6958 | 99.5129 | 0 | 244.3292 | 2646579.0265 | 92475.6004 | 3478726.7627 | 3745788.2123 | 0 | 245969.3597 | 0 | 3981720.195 | 10359619.1843 | 7070652.9622 | 31621531.3032 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44052434.0624 | 62470101.1541 | 3162277.6602 | 4.381 | 10055.3439 | 14259.3335 | 204.9918 | 290.6958
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7567 | 17.9782 | 1.1004 | 4 | 10025.6897 | 14209.9414 | 204.3872 | 289.6889 | 99.5081 | 0 | 168.0777 | 2652537.9409 | 92678.7853 | 3487740.4028 | 3758017.8583 | 0 | 243514.0112 | 0 | 3991450.7094 | 10384935.9868 | 7087932.2001 | 31698807.8947 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44129710.6539 | 62547377.7456 | 4216965.0343 | 4.4017 | 10025.6897 | 14209.9414 | 204.3872 | 289.6889
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.0346 | 18.0209 | 1.1043 | 4 | 10003.4545 | 14173.0721 | 203.934 | 288.9372 | 99.5045 | 0 | 159.237 | 2656928.5624 | 92828.4634 | 3494384.8038 | 3767039.6518 | 0 | 241603.4432 | 0 | 3998586.1206 | 10403500.863 | 7100603.1096 | 31755475.0179 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44186377.7771 | 62604044.8688 | 5623413.2519 | 4.4171 | 10003.4545 | 14173.0721 | 203.934 | 288.9372
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2413 | 18.0527 | 1.1072 | 4 | 9986.7818 | 14145.497 | 203.5941 | 288.3751 | 99.5018 | 0 | 179.8743 | 2660191.8251 | 92939.6921 | 3499324.808 | 3773750.9005 | 0 | 240137.4908 | 0 | 4003874.4394 | 10417259.9838 | 7109993.9923 | 31797473.132 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44228375.8912 | 62646042.9829 | 7498942.0933 | 4.4287 | 9986.7818 | 14145.497 | 203.5941 | 288.3751
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.405 | 18.0779 | 1.1094 | 4 | 9974.2796 | 14124.6366 | 203.3392 | 287.9498 | 99.4997 | 0 | 168.5984 | 2662775.0533 | 93027.7317 | 3503236.3315 | 3779067.1052 | 0 | 239083.917 | 0 | 4008104.1541 | 10428264.8337 | 7117505.0284 | 31831064.1549 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44261966.9141 | 62679634.0058 | 10000000 | 4.4376 | 9974.2796 | 14124.6366 | 203.3392 | 287.9498
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6325 | [19 empty] | 100 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3102 | [19 empty] | 133.3521 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2611 | [19 empty] | 177.8279 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4306 | [19 empty] | 237.1374 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6802 | [19 empty] | 316.2278 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0938 | [19 empty] | 421.6965 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.3146 | [19 empty] | 562.3413 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.18809 | 0.00085813 | 4 | 4034021.7006 | 9567388.4283 | 82238.9888 | 195044.154 | 84.3131 | 0 | 29.3749 | 97033.0959 | 3039.0738 | 91917.2254 | 70427.7745 | 0 | 61975.1467 | 0 | 126513.0034 | 329160.8834 | 224659.0665 | 1004725.2695 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13846855.7192 | 32840241.5776 | 749.8942 | 0.0034325 | 4034021.7006 | 9567388.4283 | 82238.9888 | 195044.154
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.23295 | 0.0036296 | 4 | 963353.4472 | 2271594.4062 | 19639.2631 | 46309.5245 | 86.7248 | 0 | 309.3439 | 114885.5824 | 3665.138 | 108863.9894 | 79651.6199 | 0 | 62321.5454 | 0 | 144061.2713 | 374817.8769 | 255820.9027 | 1144087.9261 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13986218.3757 | 32979604.2341 | 1000 | 0.014518 | 963353.4472 | 2271594.4062 | 19639.2631 | 46309.5245
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.35518 | 0.0075192 | 4 | 478295.6767 | 1109790.1249 | 9750.7043 | 22624.5728 | 90.8605 | 0 | 433.8311 | 159273.4613 | 5246.0042 | 152056.4431 | 104852.7606 | 0 | 76920.4443 | 0 | 194356.1543 | 505674.8455 | 345133.4726 | 1543513.5859 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14385644.0355 | 33379029.8939 | 1333.5214 | 0.030077 | 478295.6767 | 1109790.1249 | 9750.7043 | 22624.5728
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5855 | 0.50953 | 0.013108 | 4 | 283147.0083 | 645381.9147 | 5772.3347 | 13156.9833 | 93.7394 | 0 | 40.4702 | 209308.3561 | 7048.6168 | 202490.1605 | 136452.1538 | 0 | 91844.7251 | 0 | 252386.1648 | 656657.0292 | 448181.9154 | 2004369.1215 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14846499.5712 | 33839885.4295 | 1778.2794 | 0.052434 | 283147.0083 | 645381.9147 | 5772.3347 | 13156.9833
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8035 | 0.71065 | 0.020836 | 4 | 184823.2082 | 412719.6363 | 3767.8711 | 8413.848 | 95.8771 | 0 | 49.5513 | 268083.9959 | 9177.0614 | 263798.4423 | 177356.8103 | 0 | 108587.0827 | 0 | 322531.3231 | 839160.3425 | 572744.1768 | 2561439.235 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15403569.6847 | 34396955.5431 | 2371.3737 | 0.083342 | 184823.2082 | 412719.6363 | 3767.8711 | 8413.848
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3233 | 0.96253 | 0.031237 | 4 | 128481.2037 | 280491.8655 | 2619.2631 | 5718.2061 | 97.4235 | 0 | 90.6241 | 334905.9091 | 11599.4177 | 335865.6792 | 228345.3328 | 0 | 126106.4895 | 0 | 404360.9031 | 1052064.1239 | 718055.3823 | 3211303.2376 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16053433.6873 | 35046819.5457 | 3162.2777 | 0.12495 | 128481.2037 | 280491.8655 | 2619.2631 | 5718.2061
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1332 | 1.2615 | 0.044734 | 4 | 93749.0117 | 199894.0829 | 1911.2004 | 4075.1113 | 98.4634 | 0 | 101.2007 | 407450.6459 | 14222.7286 | 416688.2611 | 288885.7125 | 0 | 142629.1066 | 0 | 495251.8174 | 1288543.6387 | 879457.5103 | 3933129.4211 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16775259.8708 | 35768645.7292 | 4216.965 | 0.17894 | 93749.0117 | 199894.0829 | 1911.2004 | 4075.1113
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8593 | 1.7179 | 0.063868 | 4 | 69798.0492 | 144144.5602 | 1422.9276 | 2938.5818 | 99.5632 | 0 | 81.5672 | 509451.891 | 17925.9974 | 532997.7291 | 380664.4891 | 0 | 169824.0563 | 0 | 628237.0235 | 1634543.866 | 1115609.7751 | 4989254.8275 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 17831385.2772 | 36824771.1355 | 5623.4133 | 0.25547 | 69798.0492 | 144144.5602 | 1422.9276 | 2938.5818
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0434 | 2.2488 | 0.088256 | 4 | 53773.5158 | 107575.5354 | 1096.2459 | 2193.0728 | 100.2502 | 0 | 107.381 | 617992.6141 | 21850.6091 | 660794.7101 | 487630.3102 | 0 | 194518.3488 | 0 | 773286.771 | 2011933.5553 | 1373185.9926 | 6141192.9112 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 18983323.3609 | 37976709.2192 | 7498.9421 | 0.35302 | 53773.5158 | 107575.5354 | 1096.2459 | 2193.0728
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.0406 | 2.9158 | 0.12004 | 4 | 42399.7123 | 81954.8002 | 864.3755 | 1670.7595 | 100.7748 | 0 | 112.9791 | 744015.8464 | 26398.9068 | 813100.6968 | 622119.659 | 0 | 221410.0744 | 0 | 946547.6216 | 2462722.7477 | 1680858.8792 | 7517174.4319 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 20359304.8816 | 39352690.7399 | 10000 | 0.48018 | 42399.7123 | 81954.8002 | 864.3755 | 1670.7595
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9787 | 3.7402 | 0.16092 | 4 | 34145.7367 | 63653.181 | 696.107 | 1297.6562 | 101.1748 | 0 | 85.6068 | 888389.4954 | 31597.4561 | 992011.9897 | 788179.2778 | 0 | 249801.986 | 0 | 1150492.28 | 2993344.914 | 2043019.4109 | 9136836.81 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 21978967.2596 | 40972353.118 | 13335.2143 | 0.64368 | 34145.7367 | 63653.181 | 696.107 | 1297.6562
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.0151 | 4.7481 | 0.21279 | 4 | 28046.2922 | 50361.5 | 571.7616 | 1026.6873 | 101.4819 | 0 | 102.0274 | 1052611.3729 | 37496.7658 | 1200385.4219 | 991056.0893 | 0 | 279416.6591 | 0 | 1388776.8605 | 3613312.5138 | 2466160.0368 | 11029215.7202 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 23871346.1699 | 42864732.0283 | 17782.7941 | 0.85114 | 28046.2922 | 50361.5 | 571.7616 | 1026.6873
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.1964 | 5.9476 | 0.27718 | 4 | 23476.5671 | 40607.7707 | 478.6016 | 827.8443 | 101.7166 | 0 | 136.0495 | 1235147.6855 | 44039.3965 | 1437146.2132 | 1232444.1559 | 0 | 308661.3104 | 0 | 1660401.117 | 4320023.1113 | 2948504.541 | 13186367.5307 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 26028497.9804 | 45021883.8388 | 23713.7371 | 1.1087 | 23476.5671 | 40607.7707 | 478.6016 | 827.8443
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.4667 | 7.3291 | 0.35478 | 4 | 20022.8327 | 33406.7035 | 408.1925 | 681.0408 | 101.8942 | 0 | 107.7287 | 1432427.9403 | 51094.7255 | 1698294.1283 | 1510449.0203 | 0 | 335663.4803 | 0 | 1960892.4249 | 5101839.8554 | 3482110.5336 | 15572772.1087 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 28414902.5583 | 47408288.4167 | 31622.7766 | 1.4191 | 20022.8327 | 33406.7035 | 408.1925 | 681.0408
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.5628 | 8.8479 | 0.44449 | 4 | 17402.8953 | 28085.6069 | 354.7816 | 572.5631 | 102.0211 | 0 | 145.4233 | 1637031.8071 | 58394.5071 | 1974251.5872 | 1816198.8965 | 0 | 357830.2255 | 0 | 2279045.7391 | 5929609.5166 | 4047080.3364 | 18099442.6155 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 30941573.0652 | 49934958.9236 | 42169.6503 | 1.778 | 17402.8953 | 28085.6069 | 354.7816 | 572.5631
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.9781 | 10.4173 | 0.54261 | 4 | 15417.5088 | 24168.4141 | 314.3068 | 492.7058 | 102.0988 | 0 | 128.5001 | 1837745.1074 | 65535.7317 | 2249618.0616 | 2132607.0854 | 0 | 372254.4784 | 0 | 2596526.5812 | 6755629.5434 | 4610855.9777 | 20620772.5669 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 33462903.0165 | 52456288.8749 | 56234.1325 | 2.1704 | 15417.5088 | 24168.4141 | 314.3068 | 492.7058
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.1233 | 11.9368 | 0.64348 | 4 | 13918.9446 | 21298.068 | 283.7565 | 434.1899 | 102.131 | 0 | 130.9214 | 2023473.9961 | 72121.0754 | 2508431.4517 | 2439451.6597 | 0 | 377396.899 | 0 | 2894141.2819 | 7529961.9455 | 5139353.7531 | 22984332.0624 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 35826462.512 | 54819848.3704 | 74989.4209 | 2.5739 | 13918.9446 | 21298.068 | 283.7565 | 434.1899
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5218 | 13.3259 | 0.7412 | 4 | 12792.1201 | 19198.4328 | 260.7847 | 391.386 | 102.1275 | 0 | 169.026 | 2186933.5266 | 77894.789 | 2739379.0478 | 2720632.1581 | 0 | 373899.2344 | 0 | 3158508.1148 | 8217790.2156 | 5608810.6809 | 25083847.7672 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 37925978.2169 | 56919364.0753 | 100000 | 2.9648 | 12792.1201 | 19198.4328 | 260.7847 | 391.386
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9233 | 14.544 | 0.83121 | 4 | 11947.1173 | 17659.7209 | 243.5581 | 360.0173 | 102.1005 | 0 | 142.6819 | 2325839.19 | 82782.2665 | 2937988.0893 | 2967824.0484 | 0 | 364190.4027 | 0 | 3384663.3588 | 8806199.7697 | 6010412.2922 | 26879899.4177 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 39722029.8674 | 58715415.7257 | 133352.1432 | 3.3248 | 11947.1173 | 17659.7209 | 243.5581 | 360.0173
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.1519 | 15.5638 | 0.91018 | 4 | 11314.3834 | 16531.3042 | 230.659 | 337.013 | 102.062 | 0 | 133.7144 | 2439245.418 | 86757.999 | 3101767.5616 | 3175333.1872 | 0 | 350312.9297 | 0 | 3569832.6672 | 9287972.3267 | 6339231.9617 | 28350454.0511 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 41192584.5008 | 60185970.3591 | 177827.941 | 3.6407 | 11314.3834 | 16531.3042 | 230.659 | 337.013
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2675 | 16.3975 | 0.97715 | 4 | 10840.8452 | 15700.2207 | 221.0053 | 320.0702 | 102.0202 | 0 | 153.5076 | 2530125.2164 | 89933.6988 | 3234091.9431 | 3345376.3535 | 0 | 334876.5237 | 0 | 3718417.4569 | 9674559.4705 | 6603085.6309 | 29530466.2938 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 42372596.7435 | 61365982.6018 | 237137.3706 | 3.9086 | 10840.8452 | 15700.2207 | 221.0053 | 320.0702
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4721 | 17.08 | 1.0339 | 4 | 10474.9223 | 15067.3589 | 213.5455 | 307.1685 | 101.9795 | 0 | 156.9632 | 2603369.6573 | 92486.3903 | 3341430.4107 | 3484947.5022 | 0 | 318750.0175 | 0 | 3837983.7514 | 9985646.4424 | 6815408.8814 | 30480023.0531 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 43322153.5028 | 62315539.3612 | 316227.766 | 4.1358 | 10474.9223 | 15067.3589 | 213.5455 | 307.1685
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.924 | 17.6382 | 1.0795 | 4 | 10212.7534 | 14611.4172 | 208.2008 | 297.8735 | 101.942 | 0 | 167.5039 | 2662553.4091 | 94544.5086 | 3428615.7911 | 3599426.6698 | 0 | 306521.4535 | 0 | 3935748.1145 | 10240009.2611 | 6989016.7318 | 31256435.9396 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 44098566.3892 | 63091952.2476 | 421696.5034 | 4.318 | 10212.7534 | 14611.4172 | 208.2008 | 297.8735
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3964 | 18.0369 | 1.1142 | 4 | 10016.4398 | 14278.2265 | 204.1987 | 291.081 | 101.9129 | 0 | 159.3133 | 2704427.0755 | 95997.9573 | 3490556.1893 | 3681328.4529 | 0 | 294158.8562 | 0 | 4003922.7272 | 10417385.6186 | 7110079.7406 | 31797856.6176 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 44639987.0672 | 63633372.9256 | 562341.3252 | 4.4567 | 10016.4398 | 14278.2265 | 204.1987 | 291.081
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2944 | 18.3423 | 1.1412 | 4 | 9869.365 | 14030.2918 | 201.2004 | 286.0265 | 101.8893 | 0 | 139.274 | 2736282.1526 | 97102.1127 | 3537819.7367 | 3744141.9521 | 0 | 283727.6634 | 0 | 4055638.7108 | 10551939.9996 | 7201915.8704 | 32208568.1984 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45050698.6481 | 64044084.5064 | 749894.2093 | 4.5647 | 9869.365 | 14030.2918 | 201.2004 | 286.0265
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.746 | 18.5755 | 1.162 | 4 | 9759.1466 | 13845.3703 | 198.9534 | 282.2566 | 101.8705 | 0 | 168.2961 | 2760479.8058 | 97939.9357 | 3573805.1252 | 3792151.542 | 0 | 275202.7852 | 0 | 4094835.8856 | 10653923.0081 | 7271521.3692 | 32519859.4568 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45361989.9065 | 64355375.7648 | 1000000 | 4.6482 | 9759.1466 | 13845.3703 | 198.9534 | 282.2566
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.8345 | 18.7502 | 1.1779 | 4 | 9676.5303 | 13707.6265 | 197.2692 | 279.4485 | 101.8561 | 0 | 157.4108 | 2778530.3427 | 98564.3976 | 3600696.0178 | 3828132.1847 | 0 | 268266.1768 | 0 | 4123933.7567 | 10729629.6997 | 7323192.7419 | 32750945.3179 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45593075.7675 | 64586461.6259 | 1333521.4322 | 4.7117 | 9676.5303 | 13707.6265 | 197.2692 | 279.4485
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.6628 | 18.8829 | 1.1901 | 4 | 9614.5942 | 13604.5773 | 196.0065 | 277.3477 | 101.8449 | 0 | 164.1873 | 2792211.8525 | 99037.4117 | 3621105.073 | 3855499.5556 | 0 | 262824.6263 | 0 | 4145964.6224 | 10786949.4933 | 7362314.6788 | 32925907.3136 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45768037.7632 | 64761423.6216 | 1778279.41 | 4.7603 | 9614.5942 | 13604.5773 | 196.0065 | 277.3477
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5715 | 18.7079 | 1.1889 | 4 | 9558.9024 | 13552.7103 | 194.8712 | 276.2903 | 101.8595 | 0 | 168.0632 | 2774169.1283 | 98413.471 | 3594199.4674 | 3819436.2741 | 0 | 244796.058 | 0 | 4107095.6156 | 10685820.3105 | 7293291.9336 | 32617222.2586 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45459352.7082 | 64452738.5666 | 2371373.7057 | 4.7557 | 9558.9024 | 13552.7103 | 194.8712 | 276.2903
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4 | 19.161 | 1.2113 | 4 | 9526.2696 | 13446.4018 | 194.2059 | 274.1231 | 101.8208 | 0 | 132.7023 | 2820762.1131 | 100023.7053 | 3663766.4282 | 3912868.6694 | 0 | 258393.3027 | 0 | 4194767.5453 | 10913924.6877 | 7448977.8581 | 33313484.3098 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46155614.7594 | 65149000.6178 | 3162277.6602 | 4.8451 | 9526.2696 | 13446.4018 | 194.2059 | 274.1231
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5 | 19.4964 | 1.2277 | 4 | 9503.5967 | 13371.3115 | 193.7437 | 272.5923 | 101.7907 | 0 | 144.4575 | 2855011.1534 | 101205.3847 | 3715076.0368 | 3982162.6823 | 0 | 268372.7534 | 0 | 4259512.9241 | 11082378.8824 | 7563951.3073 | 33827671.1244 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46669801.5741 | 65663187.4325 | 4216965.0343 | 4.9108 | 9503.5967 | 13371.3115 | 193.7437 | 272.5923
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120 | 19.7356 | 1.2395 | 4 | 9486.4588 | 13317.25 | 193.3943 | 271.4902 | 101.7685 | 0 | 156.2252 | 2879297.7329 | 102042.3088 | 3751550.3062 | 4031618.9253 | 0 | 275120.1865 | 0 | 4305455.4893 | 11201912.0127 | 7645535.125 | 34192532.0867 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 47034662.5363 | 66028048.3947 | 5623413.2519 | 4.9581 | 9486.4588 | 13317.25 | 193.3943 | 271.4902
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.5756 | 19.189 | 1.2184 | 4 | 9472.9705 | 13370.1106 | 193.1193 | 272.5678 | 101.8183 | 0 | 150.3577 | 2823630.5169 | 100122.6607 | 3668061.6388 | 3918660.9923 | 0 | 249388.827 | 0 | 4196347.2079 | 10918034.6458 | 7451782.9889 | 33326029.4782 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46168159.9278 | 65161545.7862 | 7498942.0933 | 4.8737 | 9472.9705 | 13370.1106 | 193.1193 | 272.5678
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7239 | 19.2127 | 1.2206 | 4 | 9461.9616 | 13351.983 | 192.8949 | 272.1982 | 101.8161 | 0 | 161.0402 | 2826057.1294 | 100206.4212 | 3671693.479 | 3923557.5515 | 0 | 248273.1146 | 0 | 4200217.2013 | 10928103.5748 | 7458655.2399 | 33356763.7117 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46198894.1613 | 65192280.0197 | 10000000 | 4.8826 | 9461.9616 | 13351.983 | 192.8949 | 272.1982
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2466 | [19 empty] | 100 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2385 | [19 empty] | 133.3521 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4573 | [19 empty] | 177.8279 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8557 | [19 empty] | 237.1374 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4894 | [19 empty] | 316.2278 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6976 | [19 empty] | 421.6965 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8764 | [19 empty] | 562.3413 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.19383 | 0.0017548 | 4 | 2034238.7699 | 4823341.1994 | 41470.7088 | 98330.3344 | 85.7642 | 0 | 28.9931 | 100344.362 | 3174.3266 | 94048.1908 | 70863.1151 | 0 | 60745.6436 | 0 | 128378.4989 | 334014.52 | 227971.7732 | 1019540.4301 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14278758.6612 | 33856067.4134 | 749.8942 | 0.0070192 | 2034238.7699 | 4823341.1994 | 41470.7088 | 98330.3344
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0987 | 0.27609 | 0.004919 | 4 | 739707.6952 | 1734687.9212 | 15079.9419 | 35363.9596 | 89.79 | 0 | 342.9357 | 132638.4123 | 4327.9748 | 124408.9584 | 87648.9905 | 0 | 69193.9972 | 0 | 163105.15 | 424366.1427 | 289638.6123 | 1295328.2382 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14554546.4693 | 34131855.2215 | 1000 | 0.019676 | 739707.6952 | 1734687.9212 | 15079.9419 | 35363.9596
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9056 | 0.41216 | 0.0096221 | 4 | 389321.0038 | 897976.897 | 7936.8353 | 18306.4736 | 93.6469 | 0 | 45.3048 | 180561.5007 | 6067.8847 | 170905.1454 | 115057.1993 | 0 | 84382.8719 | 0 | 217220.0948 | 565162.1287 | 385734.7657 | 1725091.5912 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14984309.8222 | 34561618.5745 | 1333.5214 | 0.038488 | 389321.0038 | 897976.897 | 7936.8353 | 18306.4736
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9534 | 0.5913 | 0.016297 | 4 | 237840.4079 | 538153.129 | 4848.6984 | 10970.9794 | 96.4654 | 0 | 68.1969 | 236987.3229 | 8136.7643 | 227613.0568 | 150840.643 | 0 | 101431.1546 | 0 | 282753.4873 | 735666.5731 | 502107.5526 | 2245536.5547 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15504754.7857 | 35082063.538 | 1778.2794 | 0.06519 | 237840.4079 | 538153.129 | 4848.6984 | 10970.9794
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2614 | 0.81642 | 0.025438 | 4 | 158321.2242 | 350724.1924 | 3227.5923 | 7149.9871 | 98.486 | 0 | 88.9819 | 300967.8711 | 10491.2852 | 294179.8744 | 195412.3583 | 0 | 119189.2821 | 0 | 358893.8617 | 933768.2089 | 637315.9896 | 2850218.7314 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16109436.9624 | 35686745.7146 | 2371.3737 | 0.10175 | 158321.2242 | 350724.1924 | 3227.5923 | 7149.9871
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8808 | 1.0958 | 0.037651 | 4 | 111616.6958 | 241608.1865 | 2275.4573 | 4925.5097 | 99.9383 | 0 | 105.3973 | 373261.8766 | 13152.9932 | 371862.378 | 250640.3745 | 0 | 137505.4439 | 0 | 447104.9959 | 1163275.4854 | 793959.4217 | 3550762.9694 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16809981.2004 | 36387289.9527 | 3162.2777 | 0.1506 | 111616.6958 | 241608.1865 | 2275.4573 | 4925.5097
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3272 | 1.5202 | 0.054574 | 4 | 81656.6206 | 171339.4258 | 1664.6807 | 3492.9859 | 101.2506 | 0 | 86.6188 | 473367.2568 | 16842.1249 | 482716.3922 | 334400.1107 | 0 | 166888.0764 | 0 | 574943.4447 | 1495884.9061 | 1020972.1858 | 4566014.4974 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 17825232.7285 | 37402541.4807 | 4216.965 | 0.2183 | 81656.6206 | 171339.4258 | 1664.6807 | 3492.9859
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8339 | 1.9555 | 0.076173 | 4 | 61652.086 | 125904.7108 | 1256.8612 | 2566.7378 | 102.0413 | 0 | 86.4457 | 567494.4842 | 20304.1889 | 590106.1203 | 420087.5109 | 0 | 186080.279 | 0 | 695788.3075 | 1810298.4503 | 1235565.8902 | 5525725.2314 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 18784943.4624 | 38362252.2147 | 5623.4133 | 0.30469 | 61652.086 | 125904.7108 | 1256.8612 | 2566.7378
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2755 | 2.5535 | 0.10484 | 4 | 47812.8563 | 94494.9976 | 974.7297 | 1926.4083 | 102.7041 | 0 | 111.7383 | 687134.1291 | 24698.0047 | 730154.3262 | 538137.1458 | 0 | 212878.5485 | 0 | 855270.8401 | 2225239.2859 | 1518771.5367 | 6792283.8169 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 20051502.0479 | 39628810.8002 | 7498.9421 | 0.41937 | 47812.8563 | 94494.9976 | 974.7297 | 1926.4083
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5681 | 3.2998 | 0.14204 | 4 | 37936.1834 | 72393.8304 | 773.3804 | 1475.8462 | 103.2091 | 0 | 102.4022 | 825211.2711 | 29757.0762 | 896051.0625 | 685327.316 | 0 | 241651.8624 | 0 | 1044419.4494 | 2717365.1674 | 1854657.563 | 8294440.7678 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 21553658.9989 | 41130967.7511 | 10000 | 0.56816 | 37936.1834 | 72393.8304 | 773.3804 | 1475.8462
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8734 | 4.2226 | 0.18976 | 4 | 30729.3282 | 56522.1846 | 626.4589 | 1152.2812 | 103.5962 | 0 | 119.2997 | 983626.7216 | 35547.0397 | 1091133.6275 | 867153.1985 | 0 | 272184.2563 | 0 | 1267361.489 | 3297414.6229 | 2250553.2352 | 10064974.1908 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 23324192.4218 | 42901501.1741 | 13335.2143 | 0.75902 | 30729.3282 | 56522.1846 | 626.4589 | 1152.2812
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.3003 | 5.3408 | 0.24996 | 4 | 25378.8613 | 44959.176 | 517.3824 | 916.5536 | 103.8925 | 0 | 91.4964 | 1162430.1022 | 42067.0073 | 1316452.0569 | 1087450.7976 | 0 | 303371.1187 | 0 | 1525590.7223 | 3969274.1176 | 2709111.1457 | 12115747.0684 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 25374965.2994 | 44952274.0516 | 17782.7941 | 0.99985 | 25378.8613 | 44959.176 | 517.3824 | 916.5536
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.9102 | 6.665 | 0.32427 | 4 | 21357.6005 | 36450.8435 | 435.4036 | 743.0997 | 104.1194 | 0 | 98.7385 | 1360455.107 | 49271.5916 | 1571404.3736 | 1348259.4125 | 0 | 333944.8148 | 0 | 1818700.7668 | 4731886.3283 | 3229609.6496 | 14443532.0442 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 27702750.2752 | 47280059.0274 | 23713.7371 | 1.2971 | 21357.6005 | 36450.8435 | 435.4036 | 743.0997
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.5802 | 8.1735 | 0.41298 | 4 | 18312.2737 | 30163.5191 | 373.3205 | 614.9241 | 104.2891 | 0 | 114.4285 | 1572411.3637 | 56965.0982 | 1849773.7384 | 1645333.2455 | 0 | 361406.3467 | 0 | 2139497.0191 | 5566532.3724 | 3799272.725 | 16991191.9089 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 30250410.1399 | 49827718.8922 | 31622.7766 | 1.6519 | 18312.2737 | 30163.5191 | 373.3205 | 614.9241
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.983 | 9.8081 | 0.51419 | 4 | 16000.7185 | 25519.1777 | 326.1963 | 520.243 | 104.4058 | 0 | 141.478 | 1789395.5151 | 64820.0868 | 2140032.8481 | 1967391.9957 | 0 | 382891.9415 | 0 | 2474367.631 | 6437797.0132 | 4393928.745 | 19650625.7764 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 32909844.0075 | 52487152.7597 | 42169.6503 | 2.0568 | 16000.7185 | 25519.1777 | 326.1963 | 520.243
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.542 | 11.4659 | 0.62307 | 4 | 14249.8124 | 22104.9897 | 290.5017 | 450.6401 | 104.4704 | 0 | 137.6865 | 1998641.6003 | 72370.4549 | 2424702.7818 | 2294464.7532 | 0 | 395320.9648 | 0 | 2802345.2164 | 7291127.4131 | 4976344.2771 | 22255317.4615 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 35514535.6925 | 55091844.4448 | 56234.1325 | 2.4923 | 14249.8124 | 22104.9897 | 290.5017 | 450.6401
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.6964 | 13.0473 | 0.73329 | 4 | 12928.7671 | 19603.2716 | 263.5704 | 399.6392 | 104.4889 | 0 | 166.7373 | 2189766.2393 | 79240.7684 | 2688712.6318 | 2607162.0571 | 0 | 397904.4376 | 0 | 3105486.5923 | 8079839.0904 | 5514656.2033 | 24662768.0202 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 37921986.2513 | 57499295.0035 | 74989.4209 | 2.9331 | 12928.7671 | 19603.2716 | 263.5704 | 399.6392
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.025 | 14.479 | 0.8387 | 4 | 11935.62 | 17771.2531 | 243.3238 | 362.291 | 104.4728 | 0 | 140.4675 | 2356594.6622 | 85213.1085 | 2922282.1346 | 2891031.1367 | 0 | 391975.2441 | 0 | 3372367.5516 | 8774208.6016 | 5988577.6625 | 26782250.1019 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 40041468.3329 | 59618777.0852 | 100000 | 3.3548 | 11935.62 | 17771.2531 | 243.3238 | 362.291
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.2749 | 15.7184 | 0.93453 | 4 | 11190.7731 | 16427.9939 | 228.139 | 334.9069 | 104.4357 | 0 | 149.3896 | 2496784.7363 | 90211.323 | 3120837.298 | 3137550.0165 | 0 | 379927.0372 | 0 | 3597871.0602 | 9360922.4739 | 6389021.9362 | 28573125.8812 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 41832344.1122 | 61409652.8644 | 133352.1432 | 3.7381 | 11190.7731 | 16427.9939 | 228.139 | 334.9069
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.3501 | 16.7516 | 1.0179 | 4 | 10632.8391 | 15440.9931 | 216.7648 | 314.7855 | 104.3895 | 0 | 166.1082 | 2610879.2481 | 94263.7315 | 3283999.2563 | 3343652.3484 | 0 | 364311.8209 | 0 | 3781871.498 | 9839653.8693 | 6715765.9505 | 30034397.723 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 43293615.954 | 62870924.7062 | 177827.941 | 4.0717 | 10632.8391 | 15440.9931 | 216.7648 | 314.7855
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2929 | 17.5881 | 1.088 | 4 | 10215.0844 | 14713.6503 | 208.2483 | 299.9577 | 104.3423 | 0 | 161.5113 | 2701538.4911 | 97473.0421 | 3414669.8194 | 3510986.4673 | 0 | 347419.2024 | 0 | 3928113.9387 | 10220146.7015 | 6975460.1268 | 31195807.7893 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 44455026.0203 | 64032334.7725 | 237137.3706 | 4.3519 | 10215.0844 | 14713.6503 | 208.2483 | 299.9577
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.2272 | 18.2512 | 1.1452 | 4 | 9902.2679 | 14175.9698 | 201.8711 | 288.9963 | 104.2989 | 0 | 153.381 | 2772361.6117 | 99973.1181 | 3517391.6018 | 3643943.2561 | 0 | 330953.9311 | 0 | 4042203.1724 | 10516983.4846 | 7178057.3306 | 32101867.5064 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 45361085.7374 | 64938394.4897 | 316227.766 | 4.5809 | 9902.2679 | 14175.9698 | 201.8711 | 288.9963
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.6593 | 18.8276 | 1.1943 | 4 | 9659.5728 | 13757.5498 | 196.9235 | 280.4663 | 104.2572 | 0 | 162.1353 | 2833205.0654 | 102115.7742 | 3606093.8522 | 3759750.337 | 0 | 317132.3766 | 0 | 4141135.9881 | 10774386.3773 | 7353740.094 | 32887559.8648 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 46146778.0959 | 65724086.8481 | 421696.5034 | 4.7773 | 9659.5728 | 13757.5498 | 196.9235 | 280.4663
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0176 | 19.2225 | 1.23 | 4 | 9486.2614 | 13465.3665 | 193.3903 | 274.5097 | 104.2263 | 0 | 140.8589 | 2874512.3167 | 103567.567 | 3666560.8207 | 3839226.1565 | 0 | 304223.9998 | 0 | 4207355.4357 | 10946675.7964 | 7471331.1627 | 33413453.2556 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 46672671.4866 | 66249980.2388 | 562341.3252 | 4.92 | 9486.2614 | 13465.3665 | 193.3903 | 274.5097
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.8345 | 19.526 | 1.2578 | 4 | 9356.3751 | 13247.5805 | 190.7424 | 270.0698 | 104.2014 | 0 | 161.2043 | 2906062.523 | 104674.8449 | 3712879.7491 | 3900396.8552 | 0 | 293489.674 | 0 | 4257826.422 | 11077990.9498 | 7560956.4532 | 33814277.4711 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47073495.7021 | 66650804.4544 | 749894.2093 | 5.0312 | 9356.3751 | 13247.5805 | 190.7424 | 270.0698
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.1964 | 19.7532 | 1.279 | 4 | 9259.0108 | 13085.6049 | 188.7575 | 266.7678 | 104.1821 | 0 | 170.1785 | 2929557.8047 | 105498.5123 | 3747449.7693 | 3946215.894 | 0 | 284576.2459 | 0 | 4295186.3083 | 11175193.7102 | 7627299.3345 | 34110977.5792 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47370195.8102 | 66947504.5625 | 1000000 | 5.1161 | 9259.0108 | 13085.6049 | 188.7575 | 266.7678
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.2512 | 19.9289 | 1.2954 | 4 | 9186.0138 | 12964.1742 | 187.2693 | 264.2922 | 104.1668 | 0 | 149.3019 | 2947665.8561 | 106132.7812 | 3774138.0065 | 3981684.4679 | 0 | 277616.1365 | 0 | 4324022.5268 | 11250219.6358 | 7678506.0703 | 34339985.4811 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47599203.7121 | 67176512.4644 | 1333521.4322 | 5.1817 | 9186.0138 | 12964.1742 | 187.2693 | 264.2922
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0406 | 20.0603 | 1.3078 | 4 | 9131.2799 | 12873.5627 | 186.1535 | 262.445 | 104.1552 | 0 | 155.8979 | 2961166.0776 | 106605.3409 | 3794060.6501 | 4008216.2411 | 0 | 272077.5973 | 0 | 4345429.1038 | 11305915.1579 | 7716519.4086 | 34509989.5773 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47769207.8083 | 67346516.5606 | 1778279.41 | 5.2314 | 9131.2799 | 12873.5627 | 186.1535 | 262.445
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.6324 | 20.1587 | 1.3172 | 4 | 9090.2373 | 12805.8459 | 185.3168 | 261.0645 | 104.1463 | 0 | 148.4291 | 2971258.2045 | 106958.4289 | 3808968.2099 | 4028099.7998 | 0 | 267742.466 | 0 | 4361380.5726 | 11347417.6077 | 7744845.6834 | 34636670.9728 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47895889.2038 | 67473197.9561 | 2371373.7057 | 5.2689 | 9090.2373 | 12805.8459 | 185.3168 | 261.0645
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.0734 | 20.232 | 1.3243 | 4 | 9059.4603 | 12755.2476 | 184.6894 | 260.033 | 104.1396 | 0 | 159.1262 | 2978763.0984 | 107220.9008 | 3820062.02 | 4042913.6033 | 0 | 264366.7688 | 0 | 4373197.2926 | 11378162.2892 | 7765829.5602 | 34730515.5332 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47989733.7642 | 67567042.5165 | 3162277.6602 | 5.2972 | 9059.4603 | 12755.2476 | 184.6894 | 260.033
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1125 | 19.9057 | 1.3141 | 4 | 9028.9677 | 12753.4025 | 184.0677 | 259.9954 | 104.1686 | 0 | 169.2734 | 2945276.458 | 106048.9512 | 3770621.5073 | 3977013.9778 | 0 | 243437.1168 | 0 | 4306535.2243 | 11204721.2618 | 7647452.4952 | 34201106.9923 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47460325.2234 | 67037633.9756 | 4216965.0343 | 5.2565 | 9028.9677 | 12753.4025 | 184.0677 | 259.9954
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.5713 | 20.1485 | 1.327 | 4 | 9010.2899 | 12698.5557 | 183.6869 | 258.8772 | 104.1471 | 0 | 144.6303 | 2970212.2321 | 106921.7767 | 3807425.4587 | 4026043.916 | 0 | 250053.7213 | 0 | 4352656.2708 | 11324718.7642 | 7729353.2562 | 34567385.396 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47826603.627 | 67403912.3793 | 5623413.2519 | 5.308 | 9010.2899 | 12698.5557 | 183.6869 | 258.8772
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.673 | 20.3316 | 1.3366 | 4 | 8996.8754 | 12658.5176 | 183.4135 | 258.061 | 104.1305 | 0 | 148.7025 | 2988945.6298 | 107576.9018 | 3835124.0747 | 4063048.6784 | 0 | 255080.5496 | 0 | 4387412.5754 | 11415147.5391 | 7791072.7533 | 34843408.7022 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48102626.9332 | 67679935.6855 | 7498942.0933 | 5.3466 | 8996.8754 | 12658.5176 | 183.4135 | 258.061
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120 | 20.5518 | 1.3466 | 4 | 8993.4722 | 12628.0412 | 183.3441 | 257.4397 | 104.11 | 0 | 150.2415 | 3011399.589 | 108361.438 | 3868380.2595 | 4107597.9687 | 0 | 263803.7159 | 0 | 4430221.7587 | 11526528.2528 | 7867092.379 | 35183385.3617 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48442603.5927 | 68019912.345 | 10000000 | 5.3864 | 8993.4722 | 12628.0412 | 183.3441 | 257.4397
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6604 | [19 empty] | 100 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4608 | [19 empty] | 133.3521 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1519 | [19 empty] | 177.8279 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2656 | [19 empty] | 237.1374 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9086 | [19 empty] | 316.2278 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7306 | [19 empty] | 421.6965 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8453 | [19 empty] | 562.3413 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.19968 | 0.0026704 | 4 | 1377808.0326 | 3266034.3005 | 28088.4804 | 66582.5269 | 87.1947 | 0 | 30.5126 | 103727.6763 | 3314.6313 | 96202.3885 | 71450.6296 | 0 | 59518.0303 | 0 | 130343.2088 | 339126.2923 | 231460.6628 | 1035143.5199 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14717309.6232 | 34886745.3965 | 749.8942 | 0.010682 | 1377808.0326 | 3266034.3005 | 28088.4804 | 66582.5269
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.3222 | 0.0064901 | 4 | 582930.3869 | 1359861.3044 | 11883.8244 | 27722.612 | 92.7188 | 0 | 379.4109 | 151139.8195 | 5037.3376 | 140446.9397 | 95860.4566 | 0 | 75975.213 | 0 | 182699.3089 | 475346.125 | 324433.4977 | 1450938.698 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15133104.8013 | 35302540.5746 | 1000 | 0.02596 | 582930.3869 | 1359861.3044 | 11883.8244 | 27722.612
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.48121 | 0.012111 | 4 | 322464.2184 | 738797.9397 | 6573.8693 | 15061.3953 | 96.5029 | 0 | 74.0175 | 205476.9049 | 7047.7957 | 193022.0964 | 127200.246 | 0 | 93526.5321 | 0 | 244246.6943 | 635479.7967 | 433728.019 | 1939728.0851 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15621894.1883 | 35791329.9617 | 1333.5214 | 0.048445 | 322464.2184 | 738797.9397 | 6573.8693 | 15061.3953
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3166 | 0.67743 | 0.019993 | 4 | 202240.7379 | 454452.1534 | 4122.951 | 9264.6218 | 99.1142 | 0 | 82.2806 | 265547.0009 | 9287.685 | 253260.8234 | 165357.6253 | 0 | 110839.0863 | 0 | 313673.9662 | 816115.3165 | 557015.473 | 2491096.9766 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16173263.0799 | 36342698.8532 | 1778.2794 | 0.07997 | 202240.7379 | 454452.1534 | 4122.951 | 9264.6218
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7218 | 0.92929 | 0.030754 | 4 | 136827.3753 | 300784.9167 | 2789.4111 | 6131.9074 | 101.0498 | 0 | 96.1627 | 335410.6505 | 11901.3535 | 325658.3794 | 214169.2331 | 0 | 129832.1236 | 0 | 396618.9786 | 1031921.2247 | 704307.4397 | 3149819.3831 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16831985.4864 | 37001421.2597 | 2371.3737 | 0.12302 | 136827.3753 | 300784.9167 | 2789.4111 | 6131.9074
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4681 | 1.2425 | 0.045019 | 4 | 97724.9494 | 209729.2392 | 1992.2553 | 4275.6142 | 102.4302 | 0 | 92.9951 | 414572.7943 | 14860.4604 | 410415.5308 | 274816.3491 | 0 | 149643.3096 | 0 | 493080.2933 | 1282893.7784 | 875601.3646 | 3915883.8804 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 17598049.9837 | 37767485.757 | 3162.2777 | 0.18008 | 97724.9494 | 209729.2392 | 1992.2553 | 4275.6142
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8971 | 1.6821 | 0.064725 | 4 | 71915.6914 | 149820.562 | 1466.0986 | 3054.2948 | 103.6647 | 0 | 96.4557 | 516530.922 | 18680.9716 | 522495.7865 | 359714.6923 | 0 | 176467.6403 | 0 | 621617.105 | 1617320.1959 | 1103854.2663 | 4936681.5798 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 18618847.6831 | 38788283.4564 | 4216.965 | 0.2589 | 71915.6914 | 149820.562 | 1466.0986 | 3054.2948
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8324 | 2.2124 | 0.090265 | 4 | 54767.593 | 110629.2199 | 1116.5115 | 2255.3263 | 104.5044 | 0 | 94.4833 | 629124.7003 | 22886.6019 | 650154.7099 | 462023.8679 | 0 | 202796.9623 | 0 | 767124.8685 | 1995901.5488 | 1362243.8188 | 6092257.0783 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 19774423.1815 | 39943858.9549 | 5623.4133 | 0.36106 | 54767.593 | 110629.2199 | 1116.5115 | 2255.3263
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5324 | 2.8812 | 0.12367 | 4 | 42768.6968 | 83541.8187 | 871.8977 | 1703.113 | 105.1455 | 0 | 104.5123 | 760146.752 | 27770.2985 | 802747.9563 | 590933.1689 | 0 | 231646.35 | 0 | 941165.365 | 2448719.2202 | 1671301.1839 | 7474430.2947 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 21156596.3979 | 41326032.1713 | 7498.9421 | 0.49467 | 42768.6968 | 83541.8187 | 871.8977 | 1703.113
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1345 | 3.7136 | 0.16688 | 4 | 34144.1513 | 64359.5901 | 696.0747 | 1312.0573 | 105.6346 | 0 | 97.6922 | 911081.6644 | 33382.2528 | 983092.9694 | 751204.8694 | 0 | 262478.5927 | 0 | 1147083.736 | 2984476.5817 | 2036966.5919 | 9109767.2582 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 22791933.3614 | 42961369.1347 | 10000 | 0.66752 | 34144.1513 | 64359.5901 | 696.0747 | 1312.0573
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8102 | 4.7405 | 0.22217 | 4 | 27813.4067 | 50509.7141 | 567.0139 | 1029.7088 | 106.0103 | 0 | 99.0378 | 1084071.9727 | 39798.9079 | 1194818.0786 | 948909.9075 | 0 | 295125.7501 | 0 | 1389462.6006 | 3615096.6687 | 2467377.7592 | 11034661.6453 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 24716827.7485 | 44886263.5219 | 13335.2143 | 0.88867 | 27813.4067 | 50509.7141 | 567.0139 | 1029.7088
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.6554 | 5.9797 | 0.29166 | 4 | 23090.6928 | 40378.9435 | 470.735 | 823.1794 | 106.298 | 0 | 132.8436 | 1278728.575 | 47003.5864 | 1438450.379 | 1187760.54 | 0 | 328210.7122 | 0 | 1669259.9791 | 4343072.0534 | 2964235.9176 | 13256721.7428 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 26938887.846 | 47108323.6194 | 17782.7941 | 1.1667 | 23090.6928 | 40378.9435 | 470.735 | 823.1794
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.6823 | 7.4332 | 0.3768 | 4 | 19530.925 | 32912.8467 | 398.1643 | 670.9729 | 106.5172 | 0 | 121.8637 | 1492472.768 | 54895.8577 | 1711673.8569 | 1467875.1383 | 0 | 359892.5427 | 0 | 1983855.9638 | 5161586.2731 | 3522888.6914 | 15755141.0919 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 29437307.1951 | 49606742.9685 | 23713.7371 | 1.5072 | 19530.925 | 32912.8467 | 398.1643 | 670.9729
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.742 | 9.0734 | 0.4775 | 4 | 16830.8988 | 27390.7608 | 343.1206 | 558.3977 | 106.6784 | 0 | 127.3518 | 1719371.8742 | 63252.752 | 2007435.3656 | 1783993.6611 | 0 | 387682.6008 | 0 | 2325077.139 | 6049373.7767 | 4128821.9048 | 18465009.0742 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 32147175.1774 | 52316610.9508 | 31622.7766 | 1.91 | 16830.8988 | 27390.7608 | 343.1206 | 558.3977
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3936 | 10.8182 | 0.59069 | 4 | 14781.0765 | 23317.4131 | 301.3322 | 475.357 | 106.7833 | 0 | 122.7688 | 1947758.2133 | 71639.4648 | 2310561.4196 | 2120536.1007 | 0 | 407896.9325 | 0 | 2674772.9311 | 6959210.4953 | 4749804.1605 | 21242179.7179 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 34924345.8212 | 55093781.5945 | 42169.6503 | 2.3628 | 14781.0765 | 23317.4131 | 301.3322 | 475.357
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.0692 | 12.562 | 0.71066 | 4 | 13229.2795 | 20324.6205 | 269.6968 | 414.3449 | 106.8338 | 0 | 122.9622 | 2165135.5462 | 79592.9369 | 2603901.1937 | 2457410.3943 | 0 | 418155.5441 | 0 | 3012436.2899 | 7837741.2907 | 5349419.4804 | 23923792.6761 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 37605958.7793 | 57775394.5527 | 56234.1325 | 2.8426 | 13229.2795 | 20324.6205 | 269.6968 | 414.3449
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.2191 | 14.2034 | 0.83034 | 4 | 12059.1252 | 18131.7469 | 245.8416 | 369.6402 | 106.838 | 0 | 145.3506 | 2361361.3739 | 86742.3644 | 2872693.4668 | 2775255.0795 | 0 | 418160.0641 | 0 | 3320542.816 | 8639371.2702 | 5896548.4132 | 26370674.8481 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 40052840.9514 | 60222276.7247 | 74989.4209 | 3.3214 | 12059.1252 | 18131.7469 | 245.8416 | 369.6402
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.446 | 15.6709 | 0.94326 | 4 | 11179.6228 | 16525.2811 | 227.9117 | 336.8902 | 106.8094 | 0 | 158.8851 | 2530787.8575 | 92887.9118 | 3107852.2953 | 3060259.5528 | 0 | 409625.4373 | 0 | 3588551.0913 | 9336673.8266 | 6372471.7361 | 28499109.7087 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 42181275.812 | 62350711.5853 | 100000 | 3.773 | 11179.6228 | 16525.2811 | 227.9117 | 336.8902
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.5346 | 16.9279 | 1.0447 | 4 | 10519.9334 | 15346.5051 | 214.4631 | 312.8593 | 106.7625 | 0 | 147.187 | 2671844.7179 | 97982.1939 | 3305850.0253 | 3305127.2234 | 0 | 395236.0915 | 0 | 3812655.6983 | 9919748.0437 | 6770431.8703 | 30278875.8644 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 43961041.9676 | 64130477.741 | 133352.1432 | 4.1788 | 10519.9334 | 15346.5051 | 214.4631 | 312.8593
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4272 | 17.967 | 1.1321 | 4 | 10025.6154 | 14479.4598 | 204.3857 | 295.1834 | 106.7091 | 0 | 154.479 | 2785830.3664 | 102082.4434 | 3467351.1595 | 3508129.7356 | 0 | 377707.2707 | 0 | 3994029.3805 | 10391645.16 | 7092511.3486 | 31719286.8647 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 45401452.9679 | 65570888.7413 | 177827.941 | 4.5285 | 10025.6154 | 14479.4598 | 204.3857 | 295.1834
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1964 | 18.8038 | 1.205 | 4 | 9655.3234 | 13839.6977 | 196.8368 | 282.141 | 106.6569 | 0 | 192.7173 | 2876005.018 | 105314.9692 | 3596087.8917 | 3672035.7278 | 0 | 359383.4356 | 0 | 4137442.5465 | 10764776.7998 | 7347181.3599 | 32858227.7484 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 46540393.8517 | 66709829.625 | 237137.3706 | 4.8202 | 9655.3234 | 13839.6977 | 196.8368 | 282.141
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9897 | 19.4665 | 1.2644 | 4 | 9377.9139 | 13365.9443 | 191.1815 | 272.4829 | 106.61 | 0 | 166.421 | 2946440.8222 | 107832.5981 | 3697254.1069 | 3802132.6621 | 0 | 341982.1596 | 0 | 4249300.5161 | 11055808.2914 | 7545816.333 | 33746567.4893 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 47428733.5925 | 67598169.3659 | 316227.766 | 5.0575 | 9377.9139 | 13365.9443 | 191.1815 | 272.4829
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3053 | 20.0436 | 1.3153 | 4 | 9161.5782 | 12995.1928 | 186.7712 | 264.9246 | 106.5652 | 0 | 177.745 | 3007101.9771 | 109995.5208 | 3784814.4604 | 3915647.0345 | 0 | 327406.3104 | 0 | 4346536.4683 | 11308796.2932 | 7718485.8426 | 34518783.9073 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 48200950.0105 | 68370385.7839 | 421696.5034 | 5.2612 | 9161.5782 | 12995.1928 | 186.7712 | 264.9246
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5682 | 20.4363 | 1.352 | 4 | 9007.8257 | 12737.3915 | 183.6367 | 259.669 | 106.5327 | 0 | 157.1004 | 3048022.3696 | 111451.5962 | 3844113.8678 | 3993008.2944 | 0 | 314075.9019 | 0 | 4411162.0917 | 11476938.9088 | 7833246.6328 | 35032019.6633 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 48714185.7665 | 68883621.5399 | 562341.3252 | 5.408 | 9007.8257 | 12737.3915 | 183.6367 | 259.669
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.2977 | 20.7358 | 1.3804 | 4 | 8892.5613 | 12545.3351 | 181.2869 | 255.7536 | 106.5067 | 0 | 160.3122 | 3079040.454 | 112553.7022 | 3889189.2032 | 4052073.7383 | 0 | 302978.0805 | 0 | 4459975.7194 | 11603941.9552 | 7919928.8216 | 35419681.6742 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49101847.7775 | 69271283.5508 | 749894.2093 | 5.5217 | 8892.5613 | 12545.3351 | 181.2869 | 255.7536
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.6083 | 20.9624 | 1.4022 | 4 | 8806.1361 | 12402.1144 | 179.525 | 252.8339 | 106.4865 | 0 | 140.8538 | 3102397.8341 | 113382.677 | 3923204.3026 | 4096795.2885 | 0 | 293936.2348 | 0 | 4496589.3714 | 11699203.1671 | 7984946.5561 | 35710455.4315 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49392621.5347 | 69562057.308 | 1000000 | 5.6089 | 8806.1361 | 12402.1144 | 179.525 | 252.8339
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5876 | 21.1314 | 1.4188 | 4 | 8741.3276 | 12295.3716 | 178.2038 | 250.6578 | 106.471 | 0 | 150.7137 | 3119767.3052 | 113998.6038 | 3948539.863 | 4130188.7849 | 0 | 286635.9066 | 0 | 4523660.8808 | 11769637.6813 | 8033019.5593 | 35925448.5848 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49607614.6881 | 69777050.4614 | 1333521.4322 | 5.6751 | 8741.3276 | 12295.3716 | 178.2038 | 250.6578
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.3381 | 21.2609 | 1.4314 | 4 | 8692.7263 | 12215.3445 | 177.213 | 249.0263 | 106.459 | 0 | 152.6557 | 3133032.0792 | 114468.6698 | 3967911.5678 | 4155769.612 | 0 | 280989.0332 | 0 | 4544346.6752 | 11823457.8752 | 8069752.9476 | 36089728.4602 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49771894.5634 | 69941330.3368 | 1778279.41 | 5.7257 | 8692.7263 | 12215.3445 | 177.213 | 249.0263
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8982 | 21.3574 | 1.441 | 4 | 8656.278 | 12155.5653 | 176.4699 | 247.8076 | 106.4499 | 0 | 137.6032 | 3142905.2768 | 114818.3727 | 3982343.4998 | 4174854.4297 | 0 | 276563.034 | 0 | 4559678.999 | 11863349.4368 | 8096979.758 | 36211492.8068 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49893658.91 | 70063094.6834 | 2371373.7057 | 5.7639 | 8656.278 | 12155.5653 | 176.4699 | 247.8076
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3339 | 21.4324 | 1.4483 | 4 | 8628.9437 | 12110.5487 | 175.9127 | 246.8899 | 106.4427 | 0 | 154.9734 | 3150570.0265 | 115089.7517 | 3993555.0182 | 4189696.4547 | 0 | 273260.6631 | 0 | 4571647.0465 | 11894487.8413 | 8118232.359 | 36306539.161 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49988705.2642 | 70158141.0376 | 3162277.6602 | 5.7931 | 8628.9437 | 12110.5487 | 175.9127 | 246.8899
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.648 | 21.4865 | 1.4537 | 4 | 8608.4445 | 12077.081 | 175.4948 | 246.2076 | 106.4375 | 0 | 174.4628 | 3156087.2585 | 115285.0377 | 4001629.571 | 4200394.4015 | 0 | 270633.1463 | 0 | 4580171.4719 | 11916666.6476 | 8133369.85 | 36374237.3846 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50056403.4878 | 70225839.2612 | 4216965.0343 | 5.8148 | 8608.4445 | 12077.081 | 175.4948 | 246.2076
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8844 | 21.5272 | 1.4578 | 4 | 8593.0712 | 12052.0006 | 175.1814 | 245.6963 | 106.4336 | 0 | 181.0474 | 3160233.459 | 115431.7641 | 4007699.9376 | 4208441.7783 | 0 | 268635.501 | 0 | 4586572.5516 | 11933320.9438 | 8144736.7494 | 36425072.6848 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50107238.788 | 70276674.5614 | 5623413.2519 | 5.8311 | 8593.0712 | 12052.0006 | 175.1814 | 245.6963
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0696 | 21.559 | 1.4609 | 4 | 8581.5424 | 12033.0649 | 174.9463 | 245.3103 | 106.4305 | 0 | 169.937 | 3163480.2067 | 115546.6427 | 4012454.7965 | 4214748.0298 | 0 | 267177.9797 | 0 | 4591628.9856 | 11946476.7479 | 8153715.856 | 36465229.2449 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50147395.3481 | 70316831.1215 | 7498942.0933 | 5.8436 | 8581.5424 | 12033.0649 | 174.9463 | 245.3103
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2009 | 21.5816 | 1.4632 | 4 | 8572.8966 | 12019.0128 | 174.7701 | 245.0238 | 106.4284 | 0 | 160.23 | 3165780.7871 | 115628.0325 | 4015824.7751 | 4219219.1029 | 0 | 266018.1725 | 0 | 4595163.6394 | 11955673.1919 | 8159992.618 | 36493300.3195 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50175466.4227 | 70344902.1961 | 10000000 | 5.8528 | 8572.8966 | 12019.0128 | 174.7701 | 245.0238
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5624 | [19 empty] | 100 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1596 | [19 empty] | 133.3521 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.069 | [19 empty] | 177.8279 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0329 | [19 empty] | 237.1374 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9996 | [19 empty] | 316.2278 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.7445 | [19 empty] | 421.6965 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.2055 | 0.00038474 | 4 | 9875807.3425 | 23371830.9801 | 201331.6907 | 476466.3873 | 88.6011 | 0 | 29.3635 | 107092.4178 | 3456.1608 | 98328.4408 | 72027.7859 | 0 | 70194.8052 | 0 | 136928.8481 | 356260.7749 | 243155.2993 | 1087444.5328 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15198418.5991 | 35968185.5208 | 562.3413 | 0.001539 | 9875807.3425 | 23371830.9801 | 201331.6907 | 476466.3873
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.24194 | 0.0037528 | 4 | 1019306.1797 | 2402917.0123 | 20779.9352 | 48986.7135 | 90.679 | 0 | 279.4072 | 121967.3662 | 3998.9114 | 111860.5717 | 79216.5228 | 0 | 67204.9235 | 0 | 149856.8353 | 389896.7455 | 266112.5404 | 1190114.4168 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15301088.4831 | 36070855.4048 | 749.8942 | 0.015011 | 1019306.1797 | 2402917.0123 | 20779.9352 | 48986.7135
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.37856 | 0.0083432 | 4 | 471883.4967 | 1094237.486 | 9619.9833 | 22307.5112 | 95.736 | 0 | 372.5362 | 173002.0511 | 5893.3666 | 159403.8367 | 105852.1028 | 0 | 84431.0813 | 0 | 206147.151 | 536352.6003 | 366071.6707 | 1637153.8604 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15748127.9268 | 36517894.8484 | 1000 | 0.033373 | 471883.4967 | 1094237.486 | 9619.9833 | 22307.5112
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5124 | 0.55237 | 0.015004 | 4 | 270985.7145 | 617045.1898 | 5524.4103 | 12579.3008 | 99.2314 | 0 | 65.9656 | 230644.983 | 8064.298 | 215091.4482 | 139134.2034 | 0 | 102204.3112 | 0 | 271104.3051 | 705357.7907 | 481421.1858 | 2153022.5253 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16263996.5916 | 37033763.5133 | 1333.5214 | 0.060018 | 270985.7145 | 617045.1898 | 5524.4103 | 12579.3008
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7038 | 0.77335 | 0.024279 | 4 | 173691.6121 | 387554.3792 | 3540.9384 | 7900.8202 | 101.7493 | 0 | 71.9982 | 296582.5794 | 10564.6912 | 281007.7527 | 181145.6717 | 0 | 120997.7834 | 0 | 347216.4066 | 903385.866 | 616579.4163 | 2757480.1672 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16868454.2335 | 37638221.1552 | 1778.2794 | 0.097117 | 173691.6121 | 387554.3792 | 3540.9384 | 7900.8202
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2313 | 1.0583 | 0.036903 | 4 | 119202.6254 | 259908.9767 | 2430.1068 | 5298.596 | 103.619 | 0 | 87.1309 | 373709.633 | 13497.3182 | 360648.3018 | 235323.8841 | 0 | 141886.0543 | 0 | 438775.4247 | 1141603.6497 | 779167.9485 | 3484612.2143 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 17595586.2806 | 38365353.2023 | 2371.3737 | 0.14761 | 119202.6254 | 259908.9767 | 2430.1068 | 5298.596
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0406 | 1.3949 | 0.05334 | 4 | 86221.3495 | 183568.2641 | 1757.7388 | 3742.2874 | 104.8719 | 0 | 95.9713 | 456881.5243 | 16652.5332 | 449400.8168 | 299232.016 | 0 | 161336.8127 | 0 | 539566.4441 | 1403841.2073 | 958150.47 | 4285061.8243 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 18396035.8906 | 39165802.8123 | 3162.2777 | 0.21336 | 86221.3495 | 183568.2641 | 1757.7388 | 3742.2874
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7324 | 1.9021 | 0.076537 | 4 | 63853.9911 | 131696.6023 | 1301.75 | 2684.8134 | 106.1497 | 0 | 88.3036 | 572144.8885 | 21041.0427 | 575426.519 | 394717.6637 | 0 | 192319.2799 | 0 | 684703.2636 | 1781457.4398 | 1215881.308 | 5437691.4052 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 19548665.4715 | 40318432.3931 | 4216.965 | 0.30615 | 63853.9911 | 131696.6023 | 1301.75 | 2684.8134
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8996 | 2.4973 | 0.1063 | 4 | 48956.1523 | 97803.3942 | 998.0374 | 1993.8545 | 106.9634 | 0 | 89.9885 | 695876.2669 | 25734.183 | 715019.314 | 507287.0287 | 0 | 220937.0712 | 0 | 844293.0069 | 2196677.2155 | 1499277.3368 | 6705101.4229 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 20816075.4892 | 41585842.4109 | 5623.4133 | 0.4252 | 48956.1523 | 97803.3942 | 998.0374 | 1993.8545
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8554 | 3.2413 | 0.14508 | 4 | 38457.8013 | 74247.322 | 784.0143 | 1513.6321 | 107.5813 | 0 | 112.1457 | 838703.486 | 31139.6878 | 880458.4563 | 647925.361 | 0 | 251629.8682 | 0 | 1033444.1751 | 2688809.755 | 1835167.9073 | 8207278.6966 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 22318252.7629 | 43088019.6846 | 7498.9421 | 0.58033 | 38457.8013 | 74247.322 | 784.0143 | 1513.6321
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.7741 | 4.1667 | 0.19514 | 4 | 30870.4659 | 57478.8679 | 629.3362 | 1171.7845 | 108.0549 | 0 | 80.1096 | 1003364.8727 | 37356.2892 | 1076014.6766 | 822784.5301 | 0 | 284509.968 | 0 | 1257371.8313 | 3271423.5825 | 2232813.8161 | 9985639.5665 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 24096613.6328 | 44866380.5545 | 10000 | 0.78057 | 30870.4659 | 57478.8679 | 629.3362 | 1171.7845
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8176 | 5.3036 | 0.2589 | 4 | 25280.8647 | 45336.5316 | 515.3846 | 924.2465 | 108.4191 | 0 | 93.7892 | 1191449.8413 | 44438.7101 | 1304758.6952 | 1037267.7629 | 0 | 319098.2857 | 0 | 1519835.1852 | 3954299.3907 | 2698890.5869 | 12070038.4581 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 26181012.5244 | 46950779.446 | 13335.2143 | 1.0356 | 25280.8647 | 45336.5316 | 515.3846 | 924.2465
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.0649 | 6.6675 | 0.33857 | 4 | 21097.7291 | 36433.9069 | 430.1057 | 742.7545 | 108.6981 | 0 | 123.3336 | 1402008.8872 | 52347.8156 | 1566580.822 | 1294505.624 | 0 | 353743.3642 | 0 | 1820982.74 | 4737823.5546 | 3233661.9286 | 14461654.7361 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 28572628.8024 | 49342395.7241 | 17782.7941 | 1.3543 | 21097.7291 | 36433.9069 | 430.1057 | 742.7545
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.523 | 8.2594 | 0.43559 | 4 | 17935.4447 | 29855.804 | 365.6383 | 608.6509 | 108.9101 | 0 | 109.6548 | 1632349.4889 | 60978.4965 | 1858986.1885 | 1594739.2941 | 0 | 386669.3403 | 0 | 2158151.8953 | 5615068.5337 | 3832399.6523 | 17139342.8897 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 31250316.956 | 52020083.8776 | 23713.7371 | 1.7424 | 17935.4447 | 29855.804 | 365.6383 | 608.6509
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.9332 | 10.0296 | 0.54901 | 4 | 15533.4127 | 24991.1617 | 316.6696 | 509.4786 | 109.0616 | 0 | 122.1393 | 1873601.2329 | 69993.2509 | 2171184.3748 | 1928679.7494 | 0 | 414296.0359 | 0 | 2518524.3111 | 6552683.6372 | 4472341.2266 | 20001303.8189 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 34112277.8852 | 54882044.8068 | 31622.7766 | 2.1961 | 15533.4127 | 24991.1617 | 316.6696 | 509.4786
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.8035 | 11.8827 | 0.6747 | 4 | 13709.4726 | 21405.4096 | 279.4861 | 436.3782 | 109.1533 | 0 | 113.4297 | 2112902.258 | 78905.4694 | 2486412.247 | 2278636.3092 | 0 | 432948.9538 | 0 | 2882024.0426 | 7498435.3743 | 5117836.2204 | 22888100.8747 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 36999074.941 | 57768841.8626 | 42169.6503 | 2.6988 | 13709.4726 | 21405.4096 | 279.4861 | 436.3782
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.5575 | 13.7071 | 0.80594 | 4 | 12329.1648 | 18771.8431 | 251.3467 | 382.6894 | 109.1886 | 0 | 155.479 | 2337638.8053 | 87241.691 | 2787315.9346 | 2623924.3622 | 0 | 440734.7508 | 0 | 3227973.6621 | 8398525.3204 | 5732166.1036 | 25635520.63 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 39746494.6963 | 60516261.6179 | 56234.1325 | 3.2238 | 12329.1648 | 18771.8431 | 251.3467 | 382.6894
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.6755 | 15.4036 | 0.93512 | 4 | 11288.645 | 16841.3312 | 230.1343 | 343.3333 | 109.1781 | 0 | 151.1638 | 2538383.2196 | 94654.1032 | 3060064.5534 | 2945987.7106 | 0 | 438013.1367 | 0 | 3540070.0622 | 9210536.1336 | 6286380.1688 | 28114089.088 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 42225063.1543 | 62994830.076 | 74989.4209 | 3.7405 | 11288.645 | 16841.3312 | 230.1343 | 343.3333
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.7802 | 16.9025 | 1.0554 | 4 | 10506.6035 | 15426.2594 | 214.1913 | 314.4852 | 109.1373 | 0 | 154.8329 | 2709920.3733 | 100958.1963 | 3296136.4225 | 3231534.888 | 0 | 426787.7081 | 0 | 3808481.6594 | 9908888.0508 | 6763019.702 | 30245727.0005 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 44356701.0668 | 65126467.9884 | 100000 | 4.2218 | 10506.6035 | 15426.2594 | 214.1913 | 314.4852
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7056 | 18.1753 | 1.1624 | 4 | 9919.8882 | 14386.7394 | 202.2303 | 293.2931 | 109.0809 | 0 | 154.094 | 2851710.7887 | 106145.5246 | 3493405.9198 | 3474908.3931 | 0 | 410110.2621 | 0 | 4031149.5464 | 10488224.2173 | 7158428.5397 | 32014083.1916 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 46125057.2579 | 66894824.1795 | 133352.1432 | 4.6498 | 9919.8882 | 14386.7394 | 202.2303 | 293.2931
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4332 | 19.2221 | 1.2539 | 4 | 9480.0874 | 13620.9907 | 193.2644 | 277.6823 | 109.0205 | 0 | 156.6154 | 2965823.5257 | 110303.2341 | 3653604.4153 | 3675711.2587 | 0 | 390846.8407 | 0 | 4210552.8171 | 10954994.7269 | 7477009.0037 | 33438845.8221 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 47549819.8884 | 68319586.8101 | 177827.941 | 5.0158 | 9480.0874 | 13620.9907 | 193.2644 | 277.6823
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0493 | 20.0614 | 1.3298 | 4 | 9150.4989 | 13055.2733 | 186.5453 | 266.1494 | 108.9634 | 0 | 163.6233 | 3055793.1987 | 113569.586 | 3780839.2551 | 3837188.4859 | 0 | 371258.9073 | 0 | 4351873.2788 | 11322681.5796 | 7727962.8359 | 34561167.1273 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 48672141.1936 | 69441908.1152 | 237137.3706 | 5.3191 | 9150.4989 | 13055.2733 | 186.5453 | 266.1494
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.6887 | 20.7203 | 1.391 | 4 | 8903.4806 | 12636.3275 | 181.5095 | 257.6086 | 108.9132 | 0 | 143.5509 | 3125507.4196 | 116093.0515 | 3880004.4232 | 3964263.3042 | 0 | 352809.5346 | 0 | 4461084.3159 | 11606826.2958 | 7921897.4433 | 35428485.7881 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 49539459.8544 | 70309226.776 | 316227.766 | 5.5641 | 8903.4806 | 12636.3275 | 181.5095 | 257.6086
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.646 | 20.5316 | 1.4091 | 4 | 8716.1014 | 12401.0855 | 177.6895 | 252.8129 | 108.9276 | 0 | 707.57 | 3105618.7805 | 115373.4817 | 3851675.4284 | 3927865.332 | 0 | 304903.2624 | 0 | 4409120.1511 | 11471626.1984 | 7829620.5987 | 35015803.2333 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 49126777.2996 | 69896544.2212 | 421696.5034 | 5.6363 | 8716.1014 | 12401.0855 | 177.6895 | 252.8129
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0601 | 21.6881 | 1.4814 | 4 | 8572.8871 | 12077.8829 | 174.7699 | 246.224 | 108.8314 | 0 | 164.4336 | 3226497.7361 | 119736.5444 | 4024561.8335 | 4151434.8648 | 0 | 323716.9171 | 0 | 4619919.6794 | 12020083.3298 | 8203953.8606 | 36689904.7656 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 50800878.8319 | 71570645.7535 | 562341.3252 | 5.9258 | 8572.8871 | 12077.8829 | 174.7699 | 246.224
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6996 | 21.9824 | 1.5104 | 4 | 8470.1959 | 11907.9087 | 172.6764 | 242.7588 | 108.8046 | 0 | 154.3001 | 3256877.8721 | 120829.6243 | 4068262.8497 | 4208471.8173 | 0 | 312207.0621 | 0 | 4666993.1979 | 12142558.9691 | 8287546.0011 | 37063747.3936 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51174721.4599 | 71944488.3816 | 749894.2093 | 6.0417 | 8470.1959 | 11907.9087 | 172.6764 | 242.7588
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9519 | 22.2067 | 1.5327 | 4 | 8393.1818 | 11780.8904 | 171.1064 | 240.1694 | 108.7836 | 0 | 130.7542 | 3279944.1192 | 121658.6157 | 4101510.0037 | 4252005.5721 | 0 | 302965.6257 | 0 | 4702652.7352 | 12235337.7702 | 8350869.4392 | 37346943.881 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51457917.9473 | 72227684.869 | 1000000 | 6.1309 | 8393.1818 | 11780.8904 | 171.1064 | 240.1694
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9038 | 22.3771 | 1.5498 | 4 | 8335.4212 | 11685.8912 | 169.9288 | 238.2327 | 108.7673 | 0 | 182.2195 | 3297398.6143 | 122285.3792 | 4126707.203 | 4285079.868 | 0 | 295662.6922 | 0 | 4729582.1651 | 12305402.623 | 8398690.1409 | 37560808.6857 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51671782.752 | 72441549.6737 | 1333521.4322 | 6.1991 | 8335.4212 | 11685.8912 | 169.9288 | 238.2327
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.6102 | 22.5033 | 1.5626 | 4 | 8292.0998 | 11615.0474 | 169.0457 | 236.7885 | 108.755 | 0 | 154.2698 | 3310308.0485 | 122748.6303 | 4145364.8167 | 4309615.3881 | 0 | 289850.4753 | 0 | 4749376.07 | 12356902.3031 | 8433839.7308 | 37718005.4628 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51828979.5291 | 72598746.4507 | 1778279.41 | 6.2504 | 8292.0998 | 11615.0474 | 169.0457 | 236.7885
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1561 | 22.6008 | 1.5724 | 4 | 8259.6081 | 11561.7897 | 168.3833 | 235.7027 | 108.7455 | 0 | 161.9958 | 3320256.9577 | 123105.4672 | 4159756.1737 | 4328566.7885 | 0 | 285451.6748 | 0 | 4764683.4541 | 12396728.9767 | 8461022.2539 | 37839571.7466 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51950545.8129 | 72720312.7346 | 2371373.7057 | 6.2897 | 8259.6081 | 11561.7897 | 168.3833 | 235.7027
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.5628 | 22.6735 | 1.5798 | 4 | 8235.2393 | 11521.9799 | 167.8865 | 234.8911 | 108.7383 | 0 | 175.6181 | 3327656.1123 | 123370.7504 | 4170466.3818 | 4342685.5035 | 0 | 282038.3658 | 0 | 4776024.6743 | 12426236.5053 | 8481161.7485 | 37929640.0418 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52040614.1081 | 72810381.0298 | 3162277.6602 | 6.3193 | 8235.2393 | 11521.9799 | 167.8865 | 234.8911
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8601 | 22.7265 | 1.5853 | 4 | 8216.9629 | 11492.3044 | 167.5139 | 234.2862 | 108.733 | 0 | 166.6495 | 3333056.2088 | 123564.3051 | 4178286.858 | 4353002.8908 | 0 | 279364.7912 | 0 | 4784237.271 | 12447603.9972 | 8495745.5008 | 37994861.8229 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52105835.8892 | 72875602.8108 | 4216965.0343 | 6.3413 | 8216.9629 | 11492.3044 | 167.5139 | 234.2862
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.077 | 22.7652 | 1.5894 | 4 | 8203.2563 | 11470.1782 | 167.2345 | 233.8351 | 108.7291 | 0 | 170.8691 | 3336991.7241 | 123705.3349 | 4183988.3935 | 4360529.105 | 0 | 277282.2108 | 0 | 4790173.7397 | 12463049.4709 | 8506287.3539 | 38042007.3329 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52152981.3992 | 72922748.3208 | 5623413.2519 | 6.3576 | 8203.2563 | 11470.1782 | 167.2345 | 233.8351
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.2498 | 22.796 | 1.5926 | 4 | 8192.9767 | 11453.4266 | 167.0249 | 233.4936 | 108.726 | 0 | 134.6652 | 3340125.4266 | 123817.6151 | 4188529.5006 | 4366526.0381 | 0 | 275780.6592 | 0 | 4794963.9035 | 12475512.4945 | 8514793.6236 | 38080049.2613 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52191023.3276 | 72960790.2492 | 7498942.0933 | 6.3702 | 8192.9767 | 11453.4266 | 167.0249 | 233.4936
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3935 | 22.8217 | 1.595 | 4 | 8185.2679 | 11440.6348 | 166.8678 | 233.2328 | 108.7234 | 0 | 145.7512 | 3342729.8157 | 123910.9205 | 4192304.313 | 4371512.6489 | 0 | 274752.8244 | 0 | 4799032.1038 | 12486097.1172 | 8522017.8462 | 38112357.5897 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52223331.656 | 72993098.5777 | 10000000 | 6.3802 | 8185.2679 | 11440.6348 | 166.8678 | 233.2328
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5176 | [19 empty] | 100 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4293 | [19 empty] | 133.3521 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5821 | [19 empty] | 177.8279 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3262 | [19 empty] | 237.1374 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8049 | [19 empty] | 316.2278 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1894 | [19 empty] | 421.6965 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.21133 | 0.0013793 | 4 | 2836189.7948 | 6710916.1384 | 57819.5652 | 136811.1027 | 89.9911 | 0 | 28.4206 | 110470.7011 | 3600.4224 | 100440.3859 | 72629.2823 | 0 | 68874.2246 | 0 | 138845.8563 | 361248.437 | 246559.4812 | 1102668.7908 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15648310.911 | 37026613.1082 | 562.3413 | 0.0055174 | 2836189.7948 | 6710916.1384 | 57819.5652 | 136811.1027
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.28498 | 0.0050695 | 4 | 783479.0365 | 1837739.4252 | 15972.2799 | 37464.8039 | 93.8388 | 0 | 301.0825 | 140082.2415 | 4699.9327 | 127198.3111 | 86869.0824 | 0 | 74357.8522 | 0 | 168950.8937 | 439575.5688 | 300019.3581 | 1341753.2404 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15887395.3607 | 37265697.5578 | 749.8942 | 0.020278 | 783479.0365 | 1837739.4252 | 15972.2799 | 37464.8039
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.44114 | 0.010538 | 4 | 388640.3113 | 895800.1756 | 7922.9584 | 18262.0982 | 98.6902 | 0 | 77.7371 | 196568.8544 | 6838.1303 | 179752.8228 | 116469.3367 | 0 | 93382.3961 | 0 | 231274.5007 | 601728.81 | 410692.2771 | 1836707.1282 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16382349.2485 | 37760651.4456 | 1000 | 0.042153 | 388640.3113 | 895800.1756 | 7922.9584 | 18262.0982
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8413 | 0.634 | 0.01838 | 4 | 230375.3149 | 521156.5323 | 4696.5124 | 10624.4808 | 101.9724 | 0 | 67.4215 | 258712.531 | 9220.5333 | 239670.5843 | 152551.5316 | 0 | 112014.1322 | 0 | 301146.0319 | 783520.2014 | 534768.6372 | 2391604.1829 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16937246.3031 | 38315548.5003 | 1333.5214 | 0.07352 | 230375.3149 | 521156.5323 | 4696.5124 | 10624.4808
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1371 | 0.88413 | 0.02927 | 4 | 150360.7592 | 332955.5889 | 3065.3075 | 6787.75 | 104.4006 | 0 | 73.7808 | 331447.2016 | 12026.3164 | 312154.049 | 199262.65 | 0 | 132654.8576 | 0 | 385142.5791 | 1002061.9873 | 683927.8967 | 3058677.5378 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 17604319.6581 | 38982621.8552 | 1778.2794 | 0.11708 | 150360.7592 | 332955.5889 | 3065.3075 | 6787.75
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7501 | 1.1964 | 0.043879 | 4 | 104713.0206 | 226516.1884 | 2134.7166 | 4617.8389 | 106.1512 | 0 | 82.0504 | 413898.3346 | 15209.457 | 397090.8053 | 257193.5128 | 0 | 154181.7886 | 0 | 482653.8203 | 1255766.2345 | 857086.2585 | 3833080.2115 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 18378722.3318 | 39757024.5289 | 2371.3737 | 0.17552 | 104713.0206 | 226516.1884 | 2134.7166 | 4617.8389
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2781 | 1.6888 | 0.064239 | 4 | 76061.3601 | 159259.1094 | 1550.6137 | 3246.7124 | 107.7453 | 0 | 87.2468 | 531958.488 | 19772.4353 | 522580.8204 | 348674.3452 | 0 | 190995.3818 | 0 | 629452.7736 | 1637706.9983 | 1117768.6779 | 4998909.9205 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 19544552.0407 | 40922854.2379 | 3162.2777 | 0.25696 | 76061.3601 | 159259.1094 | 1550.6137 | 3246.7124
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5903 | 2.14 | 0.090005 | 4 | 56978.4947 | 116359.2981 | 1161.5837 | 2372.1417 | 108.6196 | 0 | 91.1399 | 631213.0585 | 23603.6668 | 631167.8758 | 432139.8374 | 0 | 208672.8588 | 0 | 751450.9459 | 1955121.2175 | 1334410.4047 | 5967779.8653 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 20513421.9855 | 41891724.1827 | 4216.965 | 0.36002 | 56978.4947 | 116359.2981 | 1161.5837 | 2372.1417
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.966 | 2.7986 | 0.12435 | 4 | 43994.3357 | 86975.2227 | 896.884 | 1773.1076 | 109.4052 | 0 | 97.2332 | 765380.8792 | 28768.8512 | 781837.299 | 553818.1903 | 0 | 238983.7654 | 0 | 923827.7042 | 2403610.1832 | 1640513.3393 | 7336740.2117 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 21882382.3319 | 43260684.5291 | 5623.4133 | 0.49739 | 43994.3357 | 86975.2227 | 896.884 | 1773.1076
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.2346 | 3.632 | 0.16915 | 4 | 34773.5202 | 66369.7573 | 708.9052 | 1353.0373 | 110.0104 | 0 | 92.9097 | 922288.8034 | 34794.6056 | 962705.0846 | 707714.8382 | 0 | 272626.8937 | 0 | 1131050.788 | 2942762.1398 | 2008495.6282 | 8982438.7815 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 23528080.9017 | 44906383.0989 | 7498.9421 | 0.67661 | 34773.5202 | 66369.7573 | 708.9052 | 1353.0373
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.5009 | 4.6611 | 0.22685 | 4 | 28061.6943 | 51622.1618 | 572.0756 | 1052.3876 | 110.4711 | 0 | 101.021 | 1102005.2278 | 41681.9413 | 1174941.7133 | 898118.2342 | 0 | 307983.3564 | 0 | 1374644.8845 | 3576544.0109 | 2441064.7781 | 10916984.1465 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 25462626.2667 | 46840928.4639 | 10000 | 0.90738 | 28061.6943 | 51622.1618 | 572.0756 | 1052.3876
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9176 | 5.9154 | 0.30001 | 4 | 23093.2146 | 40907.7676 | 470.7864 | 833.9602 | 110.824 | 0 | 92.299 | 1305863.264 | 49474.3754 | 1421351.2442 | 1130154.3326 | 0 | 344440.0744 | 0 | 1658000.4834 | 4313777.155 | 2944241.5476 | 13167302.4766 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 27712944.5968 | 49091246.794 | 13335.2143 | 1.2 | 23093.2146 | 40907.7676 | 470.7864 | 833.9602
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5741 | 7.4125 | 0.39097 | 4 | 19364.0109 | 33033.9518 | 394.7616 | 673.4418 | 111.0946 | 0 | 95.8683 | 1533172.6052 | 58140.9764 | 1702160.8507 | 1407045.5069 | 0 | 380616.0856 | 0 | 1981643.0497 | 5155828.7244 | 3518959.0461 | 15737566.845 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 30283208.9652 | 51661511.1624 | 17782.7941 | 1.5639 | 19364.0109 | 33033.9518 | 394.7616 | 673.4418
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4339 | 9.1449 | 0.50087 | 4 | 16539.592 | 27210.1098 | 337.182 | 554.7149 | 111.2981 | 0 | 124.3259 | 1779962.2574 | 67525.5136 | 2013298.2942 | 1727424.655 | 0 | 414302.6629 | 0 | 2340980.2194 | 6090750.3298 | 4157062.2525 | 18591306.1848 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 33136948.305 | 54515250.5021 | 23713.7371 | 2.0035 | 16539.592 | 27210.1098 | 337.182 | 554.7149
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.1534 | 11.0436 | 0.6278 | 4 | 14392.8494 | 22905.9666 | 293.4177 | 466.9691 | 111.4383 | 0 | 125.1392 | 2035056.6405 | 77196.879 | 2341038.4811 | 2078723.2236 | 0 | 441245.1299 | 0 | 2719571.5382 | 7075767.2814 | 4829356.5621 | 21597955.7359 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 36143597.8561 | 57521900.0533 | 31622.7766 | 2.5112 | 14392.8494 | 22905.9666 | 293.4177 | 466.9691
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.2117 | 13.0032 | 0.76655 | 4 | 12763.3852 | 19735.6644 | 260.1989 | 402.3382 | 111.5153 | 0 | 139.3158 | 2284890.465 | 86633.6235 | 2667696.7038 | 2441788.3231 | 0 | 458045.7974 | 0 | 3096231.416 | 8055759.02 | 5498221.0604 | 24589266.4092 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 39134908.5294 | 60513210.7265 | 42169.6503 | 3.0662 | 12763.3852 | 19735.6644 | 260.1989 | 402.3382
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.005 | 14.9025 | 0.90924 | 4 | 11531.0868 | 17409.1387 | 235.0768 | 354.9088 | 111.5346 | 0 | 145.867 | 2516220.134 | 95332.131 | 2975068.5471 | 2794490.193 | 0 | 463041.004 | 0 | 3449219.2836 | 8974161.0436 | 6125049.3129 | 27392581.6492 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 41938223.7694 | 63316525.9666 | 56234.1325 | 3.637 | 11531.0868 | 17409.1387 | 235.0768 | 354.9088
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.0519 | 16.6465 | 1.0478 | 4 | 10602.5419 | 15703.3955 | 216.1472 | 320.135 | 111.5093 | 0 | 145.8792 | 2720578.1263 | 102978.0255 | 3250552.5775 | 3119352.2247 | 0 | 457318.1183 | 0 | 3763803.8382 | 9792645.5247 | 6683681.7894 | 29890910.2246 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 44436552.3449 | 65814854.542 | 74989.4209 | 4.1911 | 10602.5419 | 15703.3955 | 216.1472 | 320.135
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.025 | 18.1734 | 1.1754 | 4 | 9904.7044 | 14451.8542 | 201.9208 | 294.6206 | 111.4563 | 0 | 152.1357 | 2893859.097 | 109428.1974 | 3487103.383 | 3404730.2952 | 0 | 443412.0606 | 0 | 4032027.883 | 10490509.4688 | 7159988.2709 | 32021058.6558 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 46566700.7761 | 67945002.9732 | 100000 | 4.7015 | 9904.7044 | 14451.8542 | 201.9208 | 294.6206
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7802 | 19.4587 | 1.2877 | 4 | 9381.0452 | 13531.6622 | 191.2453 | 275.8612 | 111.3909 | 0 | 158.8532 | 3035985.951 | 114693.2278 | 3683203.6269 | 3645738.8434 | 0 | 424449.4368 | 0 | 4252587.7235 | 11064360.9309 | 7551653.6852 | 33772673.4255 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 48318315.5458 | 69696617.7429 | 133352.1432 | 5.1506 | 9381.0452 | 13531.6622 | 191.2453 | 275.8612
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.3413 | 20.5103 | 1.383 | 4 | 8988.359 | 12852.8712 | 183.2399 | 262.0232 | 111.3239 | 0 | 187.0574 | 3149923.2019 | 118895.8252 | 3841797.4402 | 3843562.8995 | 0 | 403477.2517 | 0 | 4429486.0812 | 11524614.1709 | 7865785.9788 | 35177542.8494 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 49723184.9696 | 71101487.1668 | 177827.941 | 5.532 | 8988.359 | 12852.8712 | 183.2399 | 262.0232
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.7802 | 21.3454 | 1.4613 | 4 | 8693.9394 | 12351.3137 | 177.2377 | 251.7982 | 111.2625 | 0 | 159.8447 | 3238956.0044 | 122167.7443 | 3966606.937 | 4001068.1488 | 0 | 382444.7204 | 0 | 4567384.9864 | 11883398.8352 | 8110663.8844 | 36272691.2609 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 50818333.3812 | 72196635.5783 | 237137.3706 | 5.8453 | 8693.9394 | 12351.3137 | 177.2377 | 251.7982
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2903 | 22.0029 | 1.5245 | 4 | 8473.1787 | 11979.0596 | 172.7372 | 244.2093 | 111.2091 | 0 | 178.2156 | 3308190.6113 | 124704.3612 | 4064208.405 | 4125354.2424 | 0 | 363144.7597 | 0 | 4674384.9281 | 12161790.7346 | 8300672.0762 | 37122450.1185 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 51668092.2387 | 73046394.4359 | 316227.766 | 6.0978 | 8473.1787 | 11979.0596 | 172.7372 | 244.2093
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0017 | 22.5089 | 1.5742 | 4 | 8307.6221 | 11702.6261 | 169.3621 | 238.5739 | 111.1651 | 0 | 168.7012 | 3360978.1034 | 126633.6501 | 4138950.8774 | 4221194.0425 | 0 | 346066.1514 | 0 | 4755590.9017 | 12373072.0203 | 8444875.8951 | 37767361.642 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 52313003.7622 | 73691305.9593 | 421696.5034 | 6.297 | 8307.6221 | 11702.6261 | 169.3621 | 238.5739
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.605 | 22.8074 | 1.6101 | 4 | 8176.9751 | 11496.4574 | 166.6987 | 234.3708 | 111.138 | 0 | 145.7934 | 3391910.4822 | 127762.1932 | 4182882.3099 | 4277794.6888 | 0 | 326081.1153 | 0 | 4799508.0078 | 12487335.3219 | 8522862.9463 | 38116137.0654 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 52661779.1856 | 74040081.3828 | 562341.3252 | 6.4403 | 8176.9751 | 11496.4574 | 166.6987 | 234.3708
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0307 | 23.2579 | 1.647 | 4 | 8084.9294 | 11329.8724 | 164.8222 | 230.9748 | 111.0955 | 0 | 171.9485 | 3438328.4511 | 129453.0562 | 4248989.0963 | 4363335.5817 | 0 | 321102.4213 | 0 | 4875471.3566 | 12684976.3731 | 8657757.0249 | 38719413.3612 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53265055.4814 | 74643357.6786 | 749894.2093 | 6.5882 | 8084.9294 | 11329.8724 | 164.8222 | 230.9748
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2339 | 23.4809 | 1.6698 | 4 | 8016.0486 | 11216.7255 | 163.418 | 228.6681 | 111.0737 | 0 | 175.4098 | 3461175.7637 | 130283.9986 | 4281612.8977 | 4405718.2194 | 0 | 311719.7208 | 0 | 4910299.1341 | 12775591.106 | 8719603.442 | 38996004.2821 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53541646.4024 | 74919948.5995 | 1000000 | 6.6793 | 8016.0486 | 11216.7255 | 163.418 | 228.6681
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.1307 | 23.6469 | 1.6871 | 4 | 7964.3794 | 11132.3562 | 162.3646 | 226.9481 | 111.0571 | 0 | 164.6435 | 3478131.3206 | 130900.1146 | 4305859.7526 | 4437289.3093 | 0 | 304189.7635 | 0 | 4935984.4017 | 12842418.9035 | 8765214.7869 | 39199988.3527 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53745630.473 | 75123932.6701 | 1333521.4322 | 6.7483 | 7964.3794 | 11132.3562 | 162.3646 | 226.9481
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8151 | 23.7734 | 1.7002 | 4 | 7925.6217 | 11069.1078 | 161.5745 | 225.6587 | 111.0443 | 0 | 153.7704 | 3491028.3716 | 131368.4431 | 4324323.3675 | 4461370.8913 | 0 | 298370.5685 | 0 | 4955520.0404 | 12893246.6281 | 8799905.7534 | 39355134.0639 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53900776.1841 | 75279078.3813 | 1778279.41 | 6.8008 | 7925.6217 | 11069.1078 | 161.5745 | 225.6587
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3144 | 23.8657 | 1.71 | 4 | 7896.5502 | 11022.0202 | 160.9819 | 224.6988 | 111.0349 | 0 | 162.0731 | 3500415.0908 | 131709.127 | 4337772.8545 | 4478934.9485 | 0 | 293741.0292 | 0 | 4969603.4895 | 12929888.874 | 8824914.8391 | 39466980.2528 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54012622.373 | 75390924.5701 | 2371373.7057 | 6.84 | 7896.5502 | 11022.0202 | 160.9819 | 224.6988
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6971 | 23.9363 | 1.7175 | 4 | 7874.7448 | 10986.6425 | 160.5373 | 223.9776 | 111.0276 | 0 | 157.2407 | 3507595.2291 | 131969.6273 | 4348067.0663 | 4492391.0371 | 0 | 290243.7874 | 0 | 4980404.0314 | 12957989.6685 | 8844094.2088 | 39552754.656 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54098396.7763 | 75476698.9734 | 3162277.6602 | 6.8699 | 7874.7448 | 10986.6425 | 160.5373 | 223.9776
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.9944 | 23.9912 | 1.7232 | 4 | 7858.3902 | 10959.9855 | 160.2039 | 223.4341 | 111.022 | 0 | 150.7827 | 3513165.5969 | 132171.6666 | 4356057.1128 | 4502842.7315 | 0 | 287650.8287 | 0 | 4988836.2953 | 12979928.6893 | 8859068.0413 | 39619720.9625 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54165363.0827 | 75543665.2798 | 4216965.0343 | 6.8927 | 7858.3902 | 10959.9855 | 160.2039 | 223.4341
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.2159 | 24.0321 | 1.7274 | 4 | 7846.1242 | 10940.0393 | 159.9539 | 223.0275 | 111.0177 | 0 | 173.0151 | 3517311.8358 | 132322.0184 | 4362006.5993 | 4510629.4898 | 0 | 285665.3626 | 0 | 4995094.7693 | 12996211.9548 | 8870181.7046 | 39669423.7346 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54215065.8549 | 75593368.052 | 5623413.2519 | 6.9098 | 7846.1242 | 10940.0393 | 159.9539 | 223.0275
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3692 | 24.0604 | 1.7305 | 4 | 7836.9249 | 10925.294 | 159.7663 | 222.7269 | 111.0148 | 0 | 141.5939 | 3520180.4312 | 132426.0211 | 4366123.947 | 4516020.5407 | 0 | 284058.6832 | 0 | 4999335.753 | 13007246.1246 | 8877712.7522 | 39703104.2531 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54248746.3733 | 75627048.5705 | 7498942.0933 | 6.9222 | 7836.9249 | 10925.294 | 159.7663 | 222.7269
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.4935 | 24.0833 | 1.733 | 4 | 7830.0259 | 10914.097 | 159.6257 | 222.4986 | 111.0124 | 0 | 145.1761 | 3522503.4048 | 132510.2334 | 4369458.748 | 4520388.1931 | 0 | 282917.4085 | 0 | 5002833.4152 | 13016346.3242 | 8883923.8254 | 39730881.5525 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54276523.6728 | 75654825.8699 | 10000000 | 6.9318 | 7830.0259 | 10914.097 | 159.6257 | 222.4986
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2188 | [19 empty] | 100 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2798 | [19 empty] | 133.3521 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1223 | [19 empty] | 177.8279 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.118 | [19 empty] | 237.1374 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2476 | [19 empty] | 316.2278 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.3031 | [19 empty] | 421.6965 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.21712 | 0.0023727 | 4 | 1696744.6682 | 4014215.4333 | 34590.4351 | 81835.2112 | 91.3614 | 0 | 30.1644 | 113818.2866 | 3745.1487 | 102527.3142 | 73182.924 | 0 | 67555.5519 | 0 | 140723.3979 | 366133.4151 | 249893.5791 | 1117579.6175 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16103749.8825 | 38098791.4824 | 562.3413 | 0.009491 | 1696744.6682 | 4014215.4333 | 34590.4351 | 81835.2112
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.33458 | 0.0066479 | 4 | 620393.5757 | 1447535.3626 | 12647.5622 | 29509.9663 | 96.9877 | 0 | 339.7616 | 160316.3159 | 5502.3948 | 144268.8185 | 95424.3209 | 0 | 82372.3479 | 0 | 190274.8372 | 495056.0957 | 337885.9577 | 1511101.0887 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16497271.3538 | 38492312.9537 | 749.8942 | 0.026592 | 620393.5757 | 1447535.3626 | 12647.5622 | 29509.9663
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0862 | 0.50506 | 0.013099 | 4 | 324825.2615 | 744602.1331 | 6622.0023 | 15179.7216 | 101.4846 | 0 | 61.7013 | 220197.4462 | 7812.3475 | 199881.8175 | 126931.1944 | 0 | 101789.0517 | 0 | 256078.6243 | 666264.0515 | 454738.9055 | 2033693.4385 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17019863.7035 | 39014905.3034 | 1000 | 0.052397 | 324825.2615 | 744602.1331 | 6622.0023 | 15179.7216
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1749 | 0.72162 | 0.022298 | 4 | 197631.6975 | 444234.3338 | 4028.9895 | 9056.3178 | 104.6554 | 0 | 93.2964 | 288252.5973 | 10468.0423 | 265289.2451 | 166715.9411 | 0 | 121979.162 | 0 | 332554.9452 | 865239.751 | 590543.909 | 2641043.593 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17627213.858 | 39622255.4579 | 1333.5214 | 0.089192 | 197631.6975 | 444234.3338 | 4028.9895 | 9056.3178
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5781 | 1.003 | 0.034961 | 4 | 131280.0309 | 288562.3537 | 2676.321 | 5882.7339 | 107.0078 | 0 | 75.613 | 368058.0715 | 13596.4989 | 344624.8608 | 218064.7915 | 0 | 144555.3622 | 0 | 424670.8381 | 1104906.4088 | 754121.3276 | 3372598.1594 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 18358768.4245 | 40353810.0243 | 1778.2794 | 0.13984 | 131280.0309 | 288562.3537 | 2676.321 | 5882.7339
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2519 | 1.3392 | 0.051781 | 4 | 92557.6959 | 198751.2749 | 1886.9138 | 4051.8136 | 108.6295 | 0 | 51.5937 | 454929.414 | 17003.3091 | 433792.921 | 279413.3764 | 0 | 165921.8046 | 0 | 526913.7218 | 1370921.4192 | 935682.0382 | 4184578.0042 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 19170748.2693 | 41165789.8692 | 2371.3737 | 0.20712 | 92557.6959 | 198751.2749 | 1886.9138 | 4051.8136
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6413 | 1.8229 | 0.07498 | 4 | 67617.2177 | 140953.696 | 1378.4684 | 2873.5317 | 110.0894 | 0 | 76.2197 | 569351.2009 | 21497.299 | 554567.8874 | 366966.4882 | 0 | 196729.1664 | 0 | 666553.6963 | 1734235.9888 | 1183651.6974 | 5293553.4243 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 20279723.6893 | 42274765.2892 | 3162.2777 | 0.29992 | 67617.2177 | 140953.696 | 1378.4684 | 2873.5317
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5159 | 2.4049 | 0.10526 | 4 | 51135.7152 | 103374.7398 | 1042.4707 | 2107.4339 | 111.0886 | 0 | 102.6604 | 695424.9469 | 26438.409 | 691673.7665 | 472778.15 | 0 | 226629.926 | 0 | 824048.6274 | 2144005.4928 | 1463327.8038 | 6544327.1224 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 21530497.3874 | 43525538.9873 | 4216.965 | 0.42105 | 51135.7152 | 103374.7398 | 1042.4707 | 2107.4339
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1381 | 3.139 | 0.14494 | 4 | 39713.1291 | 77651.4423 | 809.6059 | 1583.0297 | 111.8501 | 0 | 99.0687 | 842037.6499 | 32170.8203 | 855502.5604 | 606126.5752 | 0 | 259311.5479 | 0 | 1012108.17 | 2633297.8463 | 1797279.889 | 8037835.059 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 23024005.3241 | 45019046.9239 | 5623.4133 | 0.57976 | 39713.1291 | 77651.4423 | 809.6059 | 1583.0297
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6593 | 4.0556 | 0.1964 | 4 | 31561.1674 | 59559.3706 | 643.4171 | 1214.1983 | 112.4322 | 0 | 101.727 | 1011388.912 | 38774.7169 | 1049667.8136 | 772347.6098 | 0 | 294462.4744 | 0 | 1234990.1954 | 3213191.1572 | 2193068.9892 | 9807891.8685 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 24794062.1336 | 46789103.7334 | 7498.9421 | 0.78559 | 31561.1674 | 59559.3706 | 643.4171 | 1214.1983
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2649 | 5.1925 | 0.2625 | 4 | 25605.6177 | 46553.6639 | 522.0052 | 949.0594 | 112.88 | 0 | 111.7383 | 1206366.5777 | 46357.6516 | 1278704.9434 | 978392.9126 | 0 | 332043.1674 | 0 | 1498327.4486 | 3898340.6719 | 2660697.6115 | 11899230.9846 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 26885401.2497 | 48880442.8495 | 10000 | 1.05 | 25605.6177 | 46553.6639 | 522.0052 | 949.0594
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.0707 | 6.5733 | 0.34603 | 4 | 21176.3791 | 37067.1829 | 431.7091 | 755.6647 | 113.2234 | 0 | 108.668 | 1426976.7725 | 54916.0366 | 1543808.071 | 1228758.6326 | 0 | 370550.5358 | 0 | 1803753.9189 | 4692997.6962 | 3203067.3591 | 14324829.0227 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 29310999.2878 | 51306040.8876 | 13335.2143 | 1.3841 | 21176.3791 | 37067.1829 | 431.7091 | 755.6647
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.1487 | 8.2128 | 0.44936 | 4 | 17840.8257 | 30077.5614 | 363.7094 | 613.1718 | 113.4862 | 0 | 112.5023 | 1671909.1115 | 64393.645 | 1844490.2836 | 1526050.3499 | 0 | 408364.6862 | 0 | 2150931.1497 | 5596281.635 | 3819577.2079 | 17081998.0689 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 32068168.3339 | 54063209.9338 | 17782.7941 | 1.7975 | 17840.8257 | 30077.5614 | 363.7094 | 613.1718
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.3787 | 10.0858 | 0.57301 | 4 | 15309.752 | 24906.1031 | 312.11 | 507.7446 | 113.6803 | 0 | 110.3352 | 1934732.6284 | 74535.3895 | 2173641.5282 | 1865706.5043 | 0 | 442330.7065 | 0 | 2531469.2352 | 6586363.6742 | 4495328.5439 | 20104108.21 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 35090278.475 | 57085320.0749 | 23713.7371 | 2.292 | 15309.752 | 24906.1031 | 312.11 | 507.7446
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3787 | 12.1119 | 0.71412 | 4 | 13385.0404 | 21085.0618 | 272.8722 | 429.8475 | 113.8077 | 0 | 116.3205 | 2203248.6847 | 84862.5717 | 2516238.955 | 2233428.5523 | 0 | 468250.7655 | 0 | 2927351.5164 | 7616368.1632 | 5198327.7721 | 23248076.9808 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 38234247.2459 | 60229288.8457 | 31622.7766 | 2.8565 | 13385.0404 | 21085.0618 | 272.8722 | 429.8475
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5808 | 14.172 | 0.8662 | 4 | 11924.6352 | 18272.7442 | 243.0998 | 372.5146 | 113.8688 | 0 | 138.2683 | 2462688.0509 | 94799.1679 | 2853037.837 | 2607952.3547 | 0 | 482769.9609 | 0 | 3315486.4748 | 8626215.7078 | 5887569.4716 | 26330519.0256 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 41316689.2906 | 63311730.8905 | 42169.6503 | 3.4648 | 11924.6352 | 18272.7442 | 243.0998 | 372.5146
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.3929 | 16.1429 | 1.0205 | 4 | 10820.7313 | 16209.1076 | 220.5952 | 330.4446 | 113.8715 | 0 | 139.9576 | 2700160.9166 | 103849.2884 | 3166256.0733 | 2967221.0984 | 0 | 484870.4087 | 0 | 3674719.5363 | 9560866.4447 | 6525487.8047 | 29183431.571 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 44169601.836 | 66164643.4359 | 56234.1325 | 4.0819 | 10820.7313 | 16209.1076 | 220.5952 | 330.4446
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.3575 | 17.9317 | 1.1684 | 4 | 9989.1314 | 14695.4929 | 203.642 | 299.5875 | 113.8314 | 0 | 170.3735 | 2907815.4375 | 111720.2353 | 3444062.3589 | 3294402.3196 | 0 | 476143.9049 | 0 | 3991316.26 | 10384586.1769 | 7087693.4476 | 31697740.1407 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 46683910.4058 | 68678952.0056 | 74989.4209 | 4.6735 | 9989.1314 | 14695.4929 | 203.642 | 299.5875
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.1844 | 19.4825 | 1.303 | 4 | 9364.1136 | 13584.0297 | 190.9001 | 276.9288 | 113.7666 | 0 | 183.4205 | 3082405.4102 | 118302.1226 | 3680530.272 | 3579076.9971 | 0 | 459504.6595 | 0 | 4258729.5899 | 11080340.8074 | 7562560.2793 | 33821450.138 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 48807620.403 | 70802662.0029 | 100000 | 5.2122 | 9364.1136 | 13584.0297 | 190.9001 | 276.9288
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.7887 | 20.7822 | 1.4207 | 4 | 8894.9695 | 12765.4684 | 181.336 | 260.2413 | 113.6922 | 0 | 145.1097 | 3225149.2115 | 123656.2623 | 3875886.0394 | 3818489.8776 | 0 | 438485.5541 | 0 | 4477850.1085 | 11650447.4489 | 7951669.7766 | 35561634.2789 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 50547804.5439 | 72542846.1438 | 133352.1432 | 5.6827 | 8894.9695 | 12765.4684 | 181.336 | 260.2413
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1555 | 21.8319 | 1.5195 | 4 | 8543.0276 | 12161.8478 | 174.1612 | 247.9357 | 113.6194 | 0 | 152.4299 | 3338199.2164 | 127877.7005 | 4031930.0056 | 4012457.9985 | 0 | 415585.752 | 0 | 4651159.7624 | 12101363.6178 | 8259429.3273 | 36938003.3804 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 51924173.6454 | 73919215.2453 | 177827.941 | 6.078 | 8543.0276 | 12161.8478 | 174.1612 | 247.9357
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.4667 | 22.6706 | 1.6006 | 4 | 8279.0464 | 11714.4682 | 168.7796 | 238.8153 | 113.5533 | 0 | 160.0009 | 3427167.7001 | 131187.3282 | 4155579.533 | 4167877.5348 | 0 | 393524.0862 | 0 | 4787381.1111 | 12455783.6242 | 8501328.2643 | 38019829.1818 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 53005999.4469 | 75001041.0467 | 237137.3706 | 6.4024 | 8279.0464 | 11714.4682 | 168.7796 | 238.8153
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8313 | 23.3223 | 1.6654 | 4 | 8081.0304 | 11382.7615 | 164.7427 | 232.053 | 113.4973 | 0 | 179.6087 | 3495487.988 | 133720.9196 | 4251048.9688 | 4288915.931 | 0 | 373222.8672 | 0 | 4891534.7031 | 12726769.9057 | 8686281.9696 | 38846983.253 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 53833153.518 | 75828195.1179 | 316227.766 | 6.6617 | 8081.0304 | 11382.7615 | 164.7427 | 232.053
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4307 | 23.8241 | 1.7164 | 4 | 7932.479 | 11136.1313 | 161.7143 | 227.0251 | 113.4514 | 0 | 166.6074 | 3547612.279 | 135649.0804 | 4324194.1708 | 4382264.403 | 0 | 355498.4295 | 0 | 4970635.1614 | 12932573.0725 | 8826746.8598 | 39475173.4564 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 54461343.7214 | 76456385.3213 | 421696.5034 | 6.8656 | 7932.479 | 11136.1313 | 161.7143 | 227.0251
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.425 | 24.2079 | 1.7561 | 4 | 7821.0257 | 10952.3363 | 159.4422 | 223.2782 | 113.4147 | 0 | 173.9826 | 3587222.3266 | 137111.4449 | 4379959.131 | 4453789.9326 | 0 | 340603.4835 | 0 | 5030487.6643 | 13088297.0075 | 8933031.6453 | 39950502.6358 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 54936672.9008 | 76931714.5007 | 562341.3252 | 7.0242 | 7821.0257 | 10952.3363 | 159.4422 | 223.2782
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3204 | 24.5719 | 1.7912 | 4 | 7731.8648 | 10801.7654 | 157.6245 | 220.2086 | 113.3787 | 0 | 163.5632 | 3624568.9013 | 138488.0298 | 4432678.1936 | 4521689.9352 | 0 | 329822.4928 | 0 | 5088426.5455 | 13239042.0917 | 9035918.2627 | 40410634.4526 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 55396804.7176 | 77391846.3175 | 749894.2093 | 7.1647 | 7731.8648 | 10801.7654 | 157.6245 | 220.2086
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.4607 | 24.7904 | 1.8143 | 4 | 7670.0421 | 10700.8422 | 156.3642 | 218.1511 | 113.3564 | 0 | 157.9798 | 3646892.9274 | 139309.7076 | 4464261.7808 | 4562503.84 | 0 | 320168.4338 | 0 | 5121923.309 | 13326193.7991 | 9095401.0938 | 40676654.8916 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 55662825.1566 | 77657866.7565 | 1000000 | 7.2572 | 7670.0421 | 10700.8422 | 156.3642 | 218.1511
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3233 | 24.9555 | 1.8319 | 4 | 7623.6609 | 10625.361 | 155.4186 | 216.6124 | 113.3393 | 0 | 160.9931 | 3663707.897 | 139928.0619 | 4488085.057 | 4593355.4555 | 0 | 312557.462 | 0 | 5147077.234 | 13391639.1522 | 9140068.892 | 40876419.2115 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 55862589.4765 | 77857631.0764 | 1333521.4322 | 7.3275 | 7623.6609 | 10625.361 | 155.4186 | 216.6124
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9734 | 25.0798 | 1.8452 | 4 | 7588.8661 | 10568.8819 | 154.7093 | 215.461 | 113.3263 | 0 | 158.1946 | 3676341.8617 | 140392.3482 | 4506003.9445 | 4616598.1942 | 0 | 306621.9486 | 0 | 5165923.7359 | 13440673.8842 | 9173536.1042 | 41026092.0215 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56012262.2866 | 78007303.8864 | 1778279.41 | 7.3808 | 7588.8661 | 10568.8819 | 154.7093 | 215.461
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.4487 | 25.1706 | 1.8552 | 4 | 7562.7648 | 10526.8083 | 154.1772 | 214.6032 | 113.3166 | 0 | 144.4401 | 3685556.0004 | 140730.7844 | 4519082.9936 | 4633583.5274 | 0 | 301921.8218 | 0 | 5179541.2998 | 13476103.992 | 9197717.8808 | 41134238.3001 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56120408.5652 | 78115450.165 | 2371373.7057 | 7.4206 | 7562.7648 | 10526.8083 | 154.1772 | 214.6032
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8165 | 25.2409 | 1.8628 | 4 | 7543.1862 | 10495.1385 | 153.7781 | 213.9576 | 113.3092 | 0 | 153.3685 | 3692675.032 | 140992.1691 | 4529194.1118 | 4646726.1838 | 0 | 298404.1474 | 0 | 5190116.7412 | 13503619.1213 | 9216497.5219 | 41218225.0285 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56204395.2936 | 78199436.8935 | 3162277.6602 | 7.451 | 7543.1862 | 10495.1385 | 153.7781 | 213.9576
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0944 | 25.2939 | 1.8685 | 4 | 7528.501 | 10471.3898 | 153.4787 | 213.4734 | 113.3035 | 0 | 144.9999 | 3698044.873 | 141189.2724 | 4536824.3535 | 4656650.9168 | 0 | 295732.7577 | 0 | 5198092.4476 | 13524370.2733 | 9230660.6096 | 41281565.5039 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56267735.7689 | 78262777.3688 | 4216965.0343 | 7.474 | 7528.501 | 10471.3898 | 153.4787 | 213.4734
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.2964 | 25.3325 | 1.8727 | 4 | 7517.4867 | 10453.6902 | 153.2541 | 213.1126 | 113.2993 | 0 | 161.1548 | 3701946.3916 | 141332.4475 | 4542370.1271 | 4663868.0673 | 0 | 293649.7707 | 0 | 5203835.0536 | 13539311.3561 | 9240858.2056 | 41327171.4194 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56313341.6844 | 78308383.2843 | 5623413.2519 | 7.491 | 7517.4867 | 10453.6902 | 153.2541 | 213.1126
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4498 | 25.3618 | 1.876 | 4 | 7509.226 | 10440.399 | 153.0857 | 212.8417 | 113.2961 | 0 | 133.0419 | 3704905.7399 | 141441.0302 | 4546577.7132 | 4669345.776 | 0 | 292086.6336 | 0 | 5208199.1882 | 13550665.9392 | 9248607.9418 | 41361829.962 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56348000.2271 | 78343041.8269 | 7498942.0933 | 7.5038 | 7509.226 | 10440.399 | 153.0857 | 212.8417
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5741 | 25.3855 | 1.8785 | 4 | 7503.0306 | 10430.3012 | 152.9594 | 212.6358 | 113.2936 | 0 | 141.5516 | 3707302.2055 | 141528.9505 | 4549985.6033 | 4673783.6291 | 0 | 290980.7804 | 0 | 5211796.6559 | 13560025.812 | 9254996.2474 | 41390399.8841 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56376570.1492 | 78371611.749 | 10000000 | 7.5138 | 7503.0306 | 10430.3012 | 152.9594 | 212.6358
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6556 | [19 empty] | 100 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6892 | [19 empty] | 133.3521 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6047 | [19 empty] | 177.8279 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4054 | [19 empty] | 237.1374 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2664 | [19 empty] | 316.2278 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5586 | [19 empty] | 421.6965 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.22288 | 0.0033829 | 4 | 1224141.975 | 2895763.0603 | 24955.7899 | 59034.0468 | 92.7124 | 0 | 25.4387 | 117156.8544 | 3891.617 | 104587.5606 | 73737.7159 | 0 | 66190.1442 | 0 | 142569.9179 | 370937.6813 | 253172.5895 | 1132244.0809 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16564802.5816 | 39184787.7114 | 562.3413 | 0.013532 | 1224141.975 | 2895763.0603 | 24955.7899 | 59034.0468
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.39117 | 0.0085053 | 4 | 503531.9702 | 1168412.0251 | 10265.1803 | 23819.6595 | 100.1114 | 0 | 371.4207 | 182686.6409 | 6410.8239 | 163094.8932 | 104817.1001 | 0 | 91275.9591 | 0 | 213831.3127 | 556345.2128 | 379717.0395 | 1698178.9821 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17130737.4828 | 39750722.6126 | 749.8942 | 0.034021 | 503531.9702 | 1168412.0251 | 10265.1803 | 23819.6595
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.364 | 0.57786 | 0.016095 | 4 | 274707.6186 | 626065.3672 | 5600.2864 | 12763.1893 | 104.2866 | 0 | 78.2156 | 246409.3312 | 8916.2492 | 222151.1299 | 138700.4855 | 0 | 111171.818 | 0 | 283666.1154 | 738041.0443 | 503728.178 | 2252784.3514 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17685342.8521 | 40305327.9819 | 1000 | 0.064379 | 274707.6186 | 626065.3672 | 5600.2864 | 12763.1893
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5381 | 0.8205 | 0.026802 | 4 | 171144.6588 | 382135.38 | 3489.0154 | 7790.3466 | 107.3408 | 0 | 82.1322 | 320714.7663 | 11865.7061 | 293411.4485 | 182323.2964 | 0 | 133032.5014 | 0 | 367125.6103 | 955185.5301 | 651933.7514 | 2915592.6103 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 18348151.111 | 40968136.2408 | 1333.5214 | 0.10721 | 171144.6588 | 382135.38 | 3489.0154 | 7790.3466
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9996 | 1.1245 | 0.041393 | 4 | 115459.5107 | 252076.1859 | 2353.7983 | 5138.914 | 109.5461 | 0 | 75.4095 | 404993.7752 | 15223.2012 | 376943.6797 | 236644.4138 | 0 | 155758.1029 | 0 | 463929.6374 | 1207049.7514 | 823836.2577 | 3684378.8193 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 19116937.32 | 41736922.4497 | 1778.2794 | 0.16557 | 115459.5107 | 252076.1859 | 2353.7983 | 5138.914
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7977 | 1.4986 | 0.06068 | 4 | 82402.7137 | 175595.7154 | 1679.8908 | 3579.7562 | 111.1003 | 0 | 83.5299 | 499612.9391 | 18989.5047 | 473771.7728 | 303656.171 | 0 | 178949.6077 | 0 | 575242.1982 | 1496662.2013 | 1021502.7057 | 4568387.1005 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 20000945.6012 | 42620930.731 | 2371.3737 | 0.24272 | 82402.7137 | 175595.7154 | 1679.8908 | 3579.7562
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3723 | 2.0405 | 0.087635 | 4 | 60530.0798 | 125059.1217 | 1233.9875 | 2549.4994 | 112.5685 | 0 | 94.7346 | 625435.8101 | 24014.9087 | 605850.0523 | 400120.5282 | 0 | 212566.5204 | 0 | 728515.2497 | 1895447.2406 | 1293681.6893 | 5785631.9992 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 21218190.4999 | 43838175.6297 | 3162.2777 | 0.35054 | 60530.0798 | 125059.1217 | 1233.9875 | 2549.4994
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4586 | 2.6886 | 0.12245 | 4 | 46102.3613 | 92284.6835 | 939.859 | 1881.3481 | 113.5426 | 0 | 82.0489 | 763047.5341 | 29489.9852 | 754888.2102 | 515545.6426 | 0 | 244964.279 | 0 | 900094.9039 | 2341862.3052 | 1598369.1438 | 7148262.0041 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 22580820.5048 | 45200805.6346 | 4216.965 | 0.4898 | 46102.3613 | 92284.6835 | 939.859 | 1881.3481
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3218 | 3.5005 | 0.16794 | 4 | 36019.9672 | 69692.4683 | 734.3158 | 1420.7752 | 114.2817 | 0 | 105.775 | 922144.7476 | 35804.9621 | 931839.8725 | 660110.4168 | 0 | 279823.3016 | 0 | 1103592.0872 | 2871320.233 | 1959735.0588 | 8764370.6795 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 24196929.1802 | 46816914.31 | 5623.4133 | 0.67176 | 36019.9672 | 69692.4683 | 734.3158 | 1420.7752
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.148 | 4.5154 | 0.22686 | 4 | 28779.1846 | 53705.9469 | 586.7026 | 1094.8684 | 114.8488 | 0 | 100.8194 | 1106252.6595 | 43092.2968 | 1141869.1994 | 840587.69 | 0 | 317491.8824 | 0 | 1345224.554 | 3499998.3459 | 2388820.7889 | 10683337.4168 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 26115895.9175 | 48735881.0473 | 7498.9421 | 0.90746 | 28779.1846 | 53705.9469 | 586.7026 | 1094.8684
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0944 | 5.7663 | 0.3023 | 4 | 23461.9551 | 42168.714 | 478.3037 | 859.6663 | 115.2839 | 0 | 95.8234 | 1317114.5356 | 51418.1174 | 1388167.4607 | 1063159.4483 | 0 | 357180.4288 | 0 | 1629045.5964 | 4238442.4786 | 2892824.0829 | 12937352.1487 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 28369910.6494 | 50989895.7792 | 10000 | 1.2092 | 23461.9551 | 42168.714 | 478.3037 | 859.6663
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.295 | 7.2816 | 0.39728 | 4 | 19493.9204 | 33728.1341 | 397.4099 | 687.5936 | 115.6183 | 0 | 111.8308 | 1555258.4606 | 60796.7172 | 1672630.4828 | 1332810.8649 | 0 | 397715.6355 | 0 | 1957492.7428 | 5092994.5798 | 3476073.4513 | 15545772.935 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 30978331.4357 | 53598316.5655 | 13335.2143 | 1.5891 | 19493.9204 | 33728.1341 | 397.4099 | 687.5936
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.7823 | 9.0679 | 0.51404 | 4 | 16498.0989 | 27499.1427 | 336.3361 | 560.6072 | 115.8729 | 0 | 111.2164 | 1818025.3693 | 71116.8705 | 1993188.0174 | 1650678.8226 | 0 | 436889.836 | 0 | 2328260.5772 | 6057656.4299 | 4134474.9858 | 18490290.9086 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 33922849.4093 | 56542834.5391 | 17782.7941 | 2.0562 | 16498.0989 | 27499.1427 | 336.3361 | 560.6072
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.3607 | 11.083 | 0.65235 | 4 | 14221.5894 | 22890.2028 | 289.9263 | 466.6477 | 116.0565 | 0 | 115.1404 | 2096760.7142 | 82031.5454 | 2339976.1142 | 2009361.0922 | 0 | 470790.5305 | 0 | 2729578.7986 | 7101804.1205 | 4847127.2397 | 21677430.1553 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 37109988.656 | 59729973.7858 | 23713.7371 | 2.6094 | 14221.5894 | 22890.2028 | 289.9263 | 466.6477
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.6165 | 13.2363 | 0.80836 | 4 | 12490.1925 | 19485.8085 | 254.6295 | 397.2446 | 116.1696 | 0 | 130.0333 | 2378402.051 | 93019.3141 | 2696884.8612 | 2393069.4348 | 0 | 495398.648 | 0 | 3142141.9806 | 8175208.8915 | 5579748.0522 | 24953873.2333 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 40386431.734 | 63006416.8638 | 31622.7766 | 3.2335 | 12490.1925 | 19485.8085 | 254.6295 | 397.2446
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.9324 | 15.3931 | 0.97413 | 4 | 11177.1491 | 16982.3366 | 227.8613 | 346.2079 | 116.2135 | 0 | 146.0271 | 2646851.0345 | 103443.6469 | 3042960.6692 | 2778185.7587 | 0 | 507357.5805 | 0 | 3540731.489 | 9212257.0306 | 6287554.7163 | 28119341.9257 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 43551900.4264 | 66171885.5562 | 42169.6503 | 3.8965 | 11177.1491 | 16982.3366 | 227.8613 | 346.2079
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.7233 | 17.4277 | 1.1399 | 4 | 10185.1106 | 15145.8902 | 207.6373 | 308.7695 | 116.1991 | 0 | 149.9208 | 2889499.6485 | 112814.6917 | 3360722.081 | 3142553.236 | 0 | 506230.08 | 0 | 3904609.6975 | 10158993.4874 | 6933721.8016 | 31009144.7238 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 46441703.2245 | 69061688.3543 | 56234.1325 | 4.5598 | 10185.1106 | 15145.8902 | 207.6373 | 308.7695
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.5977 | 19.2587 | 1.2971 | 4 | 9437.9151 | 13797.5598 | 192.4047 | 281.2819 | 116.1443 | 0 | 162.3469 | 3100160.5071 | 120902.9504 | 3640477.5938 | 3471590.2684 | 0 | 494524.3131 | 0 | 4222785.6968 | 10986822.1707 | 7498731.8881 | 33535995.3885 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 48968553.8892 | 71588539.019 | 74989.4209 | 5.1885 | 9437.9151 | 13797.5598 | 192.4047 | 281.2819
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.266 | 20.829 | 1.4387 | 4 | 8876.2711 | 12806.9824 | 180.9548 | 261.0877 | 116.0681 | 0 | 163.9504 | 3275593.447 | 127600.0011 | 3876283.2892 | 3754815.0739 | 0 | 475111.4987 | 0 | 4488667.2909 | 11678591.5386 | 7970878.6962 | 35647540.8357 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 51080099.3364 | 73700084.4662 | 100000 | 5.7547 | 8876.2711 | 12806.9824 | 180.9548 | 261.0877
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.6922 | 22.1357 | 1.5612 | 4 | 8454.5662 | 12076.6805 | 172.3578 | 246.1995 | 115.9854 | 0 | 168.1628 | 3418164.1205 | 133013.7648 | 4069872.2343 | 3991321.2567 | 0 | 451843.0551 | 0 | 4705043.6283 | 12241558.3836 | 8355115.1357 | 37365931.579 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 52798490.0797 | 75418475.2095 | 133352.1432 | 6.245 | 8454.5662 | 12076.6805 | 172.3578 | 246.1995
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9056 | 23.1892 | 1.6637 | 4 | 8138.0823 | 11537.1783 | 165.9058 | 235.201 | 115.9066 | 0 | 152.5338 | 3530989.4978 | 137278.1251 | 4224351.8622 | 4182668.476 | 0 | 427397.8035 | 0 | 4876047.4482 | 12686475.2453 | 8658780.0359 | 38723988.4941 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 54156546.9948 | 76776532.1246 | 177827.941 | 6.6547 | 8138.0823 | 11537.1783 | 165.9058 | 235.201
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.064 | 24.0251 | 1.7472 | 4 | 7900.6017 | 11137.1886 | 161.0645 | 227.0467 | 115.8366 | 0 | 171.2971 | 3619211.2829 | 140599.5207 | 4345953.155 | 4334896.0614 | 0 | 404098.687 | 0 | 5009455.8958 | 13033576.6601 | 8895683.8838 | 39783475.1468 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 55216033.6475 | 77836018.7773 | 237137.3706 | 6.9888 | 7900.6017 | 11137.1886 | 161.0645 | 227.0467
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.3038 | 24.6735 | 1.8137 | 4 | 7722.3973 | 10840.3027 | 157.4315 | 220.9942 | 115.7778 | 0 | 180.5189 | 3686879.2381 | 143138.9423 | 4439716.1612 | 4453240.2236 | 0 | 382958.0534 | 0 | 5111313.7212 | 13298589.828 | 9076560.8163 | 40592396.9842 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 56024955.4849 | 78644940.6147 | 316227.766 | 7.2549 | 7722.3973 | 10840.3027 | 157.4315 | 220.9942
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.7882 | 25.1689 | 1.8657 | 4 | 7588.6648 | 10619.6165 | 154.7052 | 216.4952 | 115.7303 | 0 | 161.9879 | 3738148.7823 | 145058.0662 | 4511047.1041 | 4543835.7618 | 0 | 364543.5883 | 0 | 5188026.988 | 13498182.0122 | 9212786.5832 | 41201628.886 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 56634187.3867 | 79254172.5165 | 421696.5034 | 7.463 | 7588.6648 | 10619.6165 | 154.7052 | 216.4952
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.7102 | 25.5511 | 1.9063 | 4 | 7488.3022 | 10454.77 | 152.6592 | 213.1346 | 115.6922 | 0 | 160.7597 | 3777447.2643 | 146526.1469 | 4565894.581 | 4613828.0707 | 0 | 349330.0687 | 0 | 5246680.1914 | 13650785.6158 | 9316941.6784 | 41667433.6173 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 57099992.118 | 79719977.2478 | 562341.3252 | 7.6252 | 7488.3022 | 10454.77 | 152.6592 | 213.1346
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.7358 | 25.3573 | 1.9143 | 4 | 7409.2283 | 10363.3683 | 151.0471 | 211.2713 | 115.7113 | 0 | 165.8903 | 3757539.0238 | 145782.3525 | 4538104.0434 | 4578340.0222 | 0 | 314705.9689 | 0 | 5200443.8502 | 13530488.1405 | 9234836.1796 | 41300239.5809 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 56732798.0816 | 79352783.2114 | 749894.2093 | 7.657 | 7409.2283 | 10363.3683 | 151.0471 | 211.2713
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.6339 | 26.1308 | 1.9659 | 4 | 7351.6591 | 10228.1767 | 149.8735 | 208.5152 | 115.632 | 0 | 143.3131 | 3836630.3295 | 148732.2331 | 4648775.6134 | 4720139.5005 | 0 | 328316.5312 | 0 | 5336211.741 | 13883728.3425 | 9475929.8759 | 42378464.1671 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 57811022.6678 | 80431007.7976 | 1000000 | 7.8637 | 7351.6591 | 10228.1767 | 149.8735 | 208.5152
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4498 | 26.2922 | 1.9837 | 4 | 7309.8898 | 10160.6215 | 149.022 | 207.138 | 115.6146 | 0 | 136.0005 | 3853014.6744 | 149341.8451 | 4671783.6254 | 4749770.7065 | 0 | 320508.3912 | 0 | 5360323.5046 | 13946462.2055 | 9518747.0264 | 42569951.9792 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58002510.4799 | 80622495.6097 | 1333521.4322 | 7.9348 | 7309.8898 | 10160.6215 | 149.022 | 207.138
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0681 | 26.4143 | 1.9972 | 4 | 7278.5516 | 10110.0097 | 148.3831 | 206.1062 | 115.6014 | 0 | 170.7215 | 3865394.4817 | 149802.146 | 4689186.0282 | 4772216.5666 | 0 | 314463.3255 | 0 | 5378514.3938 | 13993791.1676 | 9551050.0155 | 42714418.1249 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58146976.6256 | 80766961.7554 | 1778279.41 | 7.9888 | 7278.5516 | 10110.0097 | 148.3831 | 206.1062
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5286 | 26.5052 | 2.0074 | 4 | 7255.0416 | 10072.1793 | 147.9038 | 205.335 | 115.5914 | 0 | 177.326 | 3874592.3976 | 150143.9611 | 4702125.6538 | 4788925.2758 | 0 | 309760.1879 | 0 | 5391963.5157 | 14028783.024 | 9574932.6766 | 42821226.6924 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58253785.1931 | 80873770.3229 | 2371373.7057 | 8.0294 | 7255.0416 | 10072.1793 | 147.9038 | 205.335
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.877 | 26.574 | 2.015 | 4 | 7237.4057 | 10043.8097 | 147.5443 | 204.7566 | 115.5838 | 0 | 181.9928 | 3881540.1022 | 150402.0532 | 4711905.3348 | 4801564.3284 | 0 | 306176.7068 | 0 | 5402119.5249 | 14055206.8768 | 9592967.499 | 42901882.4263 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58334440.927 | 80954426.0568 | 3162277.6602 | 8.0601 | 7237.4057 | 10043.8097 | 147.5443 | 204.7566
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1398 | 26.6258 | 2.0208 | 4 | 7224.1771 | 10022.5374 | 147.2746 | 204.323 | 115.5781 | 0 | 172.6246 | 3886775.0201 | 150596.4618 | 4719277.2968 | 4811097.8027 | 0 | 303455.1919 | 0 | 5409768.6916 | 14075108.4394 | 9606550.7244 | 42962629.6287 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58395188.1294 | 81015173.2592 | 4216965.0343 | 8.0833 | 7224.1771 | 10022.5374 | 147.2746 | 204.323
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.325 | 26.6623 | 2.0251 | 4 | 7214.2549 | 10006.763 | 147.0723 | 204.0014 | 115.574 | 0 | 163.302 | 3890460.4018 | 150733.293 | 4724468.922 | 4817814.8936 | 0 | 301287.1465 | 0 | 5415058.2162 | 14088870.6974 | 9615943.7483 | 43004637.3187 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58437195.8194 | 81057180.9492 | 5623413.2519 | 8.1002 | 7214.2549 | 10006.763 | 147.0723 | 204.0014
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4862 | 26.6941 | 2.0285 | 4 | 7206.8131 | 9994.6339 | 146.9206 | 203.7541 | 115.5704 | 0 | 153.8177 | 3893664.6882 | 150852.2475 | 4728983.7604 | 4823658.285 | 0 | 299832.9868 | 0 | 5419826.8675 | 14101277.7499 | 9624411.8166 | 43042508.4019 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58475066.9026 | 81095052.0324 | 7498942.0933 | 8.1139 | 7206.8131 | 9994.6339 | 146.9206 | 203.7541
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.6003 | 26.7166 | 2.031 | 4 | 7201.2319 | 9985.6361 | 146.8069 | 203.5707 | 115.5679 | 0 | 177.127 | 3895931.9021 | 150936.4019 | 4732178.9447 | 4827794.9341 | 0 | 298676.9001 | 0 | 5423152.4423 | 14109930.2134 | 9630317.3007 | 43068919.0393 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58501477.54 | 81121462.6698 | 10000000 | 8.1238 | 7201.2319 | 9985.6361 | 146.8069 | 203.5707
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9991 | [19 empty] | 100 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2055 | [19 empty] | 133.3521 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1372 | [19 empty] | 177.8279 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8183 | [19 empty] | 237.1374 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4079 | [19 empty] | 316.2278 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.2287 | 0.00042526 | 4 | 10037730.129 | 23707610.9156 | 204632.7057 | 483311.7154 | 94.0392 | 0 | 25.3366 | 120519.7384 | 4041.039 | 106653.1844 | 74371.9779 | 0 | 78580.4863 | 0 | 149824.9062 | 389813.6726 | 266055.8414 | 1189860.8462 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17074667.6734 | 40327800.4604 | 421.6965 | 0.001701 | 10037730.129 | 23707610.9156 | 204632.7057 | 483311.7154
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.28218 | 0.0046711 | 4 | 922382.3033 | 2166912.2107 | 18804.0109 | 44175.4364 | 97.0807 | 0 | 281.4523 | 142597.172 | 4890.3931 | 125884.7122 | 84190.5852 | 0 | 78059.5714 | 0 | 169892.7493 | 442026.0838 | 301691.8849 | 1349233.1519 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17234039.9791 | 40487172.766 | 562.3413 | 0.018684 | 922382.3033 | 2166912.2107 | 18804.0109 | 44175.4364
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6627 | 0.44734 | 0.010692 | 4 | 415303.6298 | 958985.3503 | 8466.5262 | 19550.2135 | 102.9917 | 0 | 424.1099 | 204523.9877 | 7325.2005 | 181182.3845 | 113902.565 | 0 | 99288.9867 | 0 | 236427.0185 | 615134.6043 | 419842.0072 | 1877626.7544 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17762433.5816 | 41015566.3686 | 749.8942 | 0.04277 | 415303.6298 | 958985.3503 | 8466.5262 | 19550.2135
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.6579 | 0.019545 | 4 | 235000.8621 | 532438.0363 | 4790.8104 | 10854.4695 | 107.056 | 0 | 73.5144 | 274542.4894 | 10127.8924 | 245942.9261 | 151273.156 | 0 | 121135.0219 | 0 | 313178.3794 | 814825.9015 | 556135.4208 | 2487161.1874 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 18371968.0146 | 41625100.8016 | 1000 | 0.078178 | 235000.8621 | 532438.0363 | 4790.8104 | 10854.4695
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8891 | 0.92226 | 0.031902 | 4 | 149477.0403 | 331699.9204 | 3047.2916 | 6762.1515 | 109.9474 | 0 | 62.6651 | 353595.2807 | 13318.4989 | 321569.9988 | 197768.4974 | 0 | 143591.8617 | 0 | 401639.2136 | 1044982.8462 | 713222.2648 | 3189688.4618 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 19074495.2891 | 42327628.076 | 1333.5214 | 0.12761 | 149477.0403 | 331699.9204 | 3047.2916 | 6762.1515
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4749 | 1.2645 | 0.048759 | 4 | 102147.3902 | 221371.5585 | 2082.4127 | 4512.9586 | 112.1044 | 0 | 66.3429 | 446455.0435 | 17079.0443 | 413288.3343 | 258055.0184 | 0 | 168768.1903 | 0 | 508421.796 | 1322809.2216 | 902844.4748 | 4037721.1233 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 19922527.9506 | 43175660.7375 | 1778.2794 | 0.19504 | 102147.3902 | 221371.5585 | 2082.4127 | 4512.9586
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3377 | 1.6652 | 0.070615 | 4 | 73798.4507 | 156121.6179 | 1504.4812 | 3182.7504 | 113.527 | 0 | 64.8014 | 545645.387 | 21083.7101 | 514564.8759 | 328509.4775 | 0 | 191751.2261 | 0 | 624606.3239 | 1625097.5303 | 1109162.4568 | 4960420.9875 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 20845227.8147 | 44098360.6016 | 2371.3737 | 0.28246 | 73798.4507 | 156121.6179 | 1504.4812 | 3182.7504
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.154 | 2.2809 | 0.10189 | 4 | 54477.4016 | 111534.6426 | 1110.5955 | 2273.7846 | 115.0451 | 0 | 80.0061 | 685995.9606 | 26782.5136 | 661129.0066 | 435861.6624 | 0 | 229759.4022 | 0 | 795416.1327 | 2069509.615 | 1412482.8364 | 6316937.1295 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 22201743.9567 | 45454876.7436 | 3162.2777 | 0.40754 | 54477.4016 | 111534.6426 | 1110.5955 | 2273.7846
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4332 | 2.9946 | 0.14173 | 4 | 41751.583 | 82767.0464 | 851.1625 | 1687.3182 | 115.987 | 0 | 84.4058 | 834705.8096 | 32792.4866 | 821435.8268 | 560769.3557 | 0 | 264026.2506 | 0 | 980354.5944 | 2550681.5563 | 1740892.5735 | 7785658.4536 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 23670465.2808 | 46923598.0677 | 4216.965 | 0.56694 | 41751.583 | 82767.0464 | 851.1625 | 1687.3182
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5741 | 3.897 | 0.19385 | 4 | 32798.1046 | 62787.0148 | 668.6337 | 1279.9982 | 116.7098 | 0 | 80.6111 | 1008320.1872 | 39790.7048 | 1013587.9533 | 718747.8883 | 0 | 301816.2544 | 0 | 1202082.5653 | 3127572.2538 | 2134632.3284 | 9546550.1354 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 25431356.9626 | 48684489.7495 | 5623.4133 | 0.77539 | 32798.1046 | 62787.0148 | 668.6337 | 1279.9982
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.6897 | 5.0122 | 0.26102 | 4 | 26336.1524 | 48607.3231 | 536.8981 | 990.926 | 117.2594 | 0 | 100.994 | 1207105.7486 | 47780.3604 | 1239176.5982 | 913727.147 | 0 | 341511.6341 | 0 | 1462227.5804 | 3804416.2202 | 2596592.2432 | 11612537.5321 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 27497344.3594 | 50750477.1463 | 7498.9421 | 1.0441 | 26336.1524 | 48607.3231 | 536.8981 | 990.926
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.9897 | 6.3859 | 0.34674 | 4 | 21574.2914 | 38339.7413 | 439.8211 | 781.6075 | 117.683 | 0 | 96.1884 | 1434760.3717 | 56903.6083 | 1503698.1081 | 1153623.1826 | 0 | 383427.7374 | 0 | 1767641.0732 | 4599039.4794 | 3138938.9455 | 14038032.5063 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 29922839.3335 | 53175972.1204 | 10000 | 1.387 | 21574.2914 | 38339.7413 | 439.8211 | 781.6075
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5802 | 8.0416 | 0.45419 | 4 | 18008.127 | 30807.4969 | 367.12 | 628.0525 | 118.0084 | 0 | 103.5381 | 1690782.4514 | 67135.3104 | 1807833.8632 | 1442721.3579 | 0 | 425788.4131 | 0 | 2119361.9444 | 5514145.0385 | 3763517.2932 | 16831285.6722 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 32716092.4994 | 55969225.2863 | 13335.2143 | 1.8167 | 18008.127 | 30807.4969 | 367.12 | 628.0525
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.4741 | 9.982 | 0.58553 | 4 | 15307.9037 | 25236.1328 | 312.0723 | 514.4727 | 118.2545 | 0 | 97.2245 | 1971923.4322 | 78341.4778 | 2148736.3239 | 1781853.4021 | 0 | 466207.0494 | 0 | 2514354.0573 | 6541833.4922 | 4464935.7797 | 19968185.0146 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 35852991.8418 | 59106124.6287 | 17782.7941 | 2.3421 | 15307.9037 | 25236.1328 | 312.0723 | 514.4727
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.3808 | 12.1414 | 0.73945 | 4 | 13254.0137 | 21115.665 | 270.201 | 430.4714 | 118.4263 | 0 | 142.4806 | 2266465.6038 | 90043.7649 | 2512883.2704 | 2159429.9875 | 0 | 499722.8887 | 0 | 2936132.751 | 7639215.1344 | 5213921.2994 | 23317814.7001 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 39202621.5273 | 62455754.3142 | 23713.7371 | 2.9578 | 13254.0137 | 21115.665 | 270.201 | 430.4714
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.8413 | 14.4153 | 0.91079 | 4 | 11692.1202 | 18074.7683 | 238.3597 | 368.4786 | 118.5233 | 0 | 155.9129 | 2560123.2501 | 101662.8928 | 2882600.3784 | 2557536.415 | 0 | 522390.3976 | 0 | 3363482.2002 | 8751090.7399 | 5972799.2469 | 26711685.5209 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 42596492.3481 | 65849625.135 | 31622.7766 | 3.6432 | 11692.1202 | 18074.7683 | 238.3597 | 368.4786
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.2387 | 16.6641 | 1.0905 | 4 | 10508.1926 | 15839.1444 | 214.2237 | 322.9024 | 118.549 | 0 | 150.3062 | 2836886.4849 | 112557.0057 | 3237012.3305 | 2952219.1669 | 0 | 531500.2096 | 0 | 3771368.3271 | 9812326.7731 | 6697114.6458 | 29950984.9437 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 45835791.7709 | 69088924.5578 | 42169.6503 | 4.3619 | 10508.1926 | 15839.1444 | 214.2237 | 322.9024
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.005 | 18.7621 | 1.268 | 4 | 9614.0238 | 14198.6652 | 195.9949 | 289.459 | 118.5173 | 0 | 150.3497 | 3084626.7468 | 122250.775 | 3559213.5186 | 3321638.2316 | 0 | 527213.2476 | 0 | 4139827.5827 | 10770982.1748 | 7351416.6558 | 32877168.933 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 48761975.7603 | 72015108.5472 | 56234.1325 | 5.072 | 9614.0238 | 14198.6652 | 195.9949 | 289.459
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.7519 | 20.6267 | 1.4342 | 4 | 8940.5895 | 12994.0054 | 182.266 | 264.9004 | 118.448 | 0 | 150.2964 | 3297320.2425 | 130521.4303 | 3839661.3206 | 3651179.3215 | 0 | 512237.2744 | 0 | 4458058.6398 | 11598954.1073 | 7916524.5129 | 35404456.8494 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 51289263.6766 | 74542396.4635 | 74989.4209 | 5.7367 | 8940.5895 | 12994.0054 | 182.266 | 264.9004
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.2823 | 22.2193 | 1.5827 | 4 | 8434.3014 | 12107.4029 | 171.9446 | 246.8258 | 118.3605 | 0 | 150.7285 | 3473941.0472 | 137347.9403 | 4075316.9867 | 3933745.3197 | 0 | 490324.101 | 0 | 4723163.404 | 12288702.3232 | 8387291.8431 | 37509832.9652 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 53394639.7924 | 76647772.5793 | 100000 | 6.3307 | 8434.3014 | 12107.4029 | 171.9446 | 246.8258
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.5233 | 23.5296 | 1.7099 | 4 | 8054.0394 | 11453.7261 | 164.1925 | 233.4997 | 118.27 | 0 | 167.7173 | 3616001.5024 | 142808.4628 | 4266745.6325 | 4167051.1581 | 0 | 464769.9491 | 0 | 4936376.9149 | 12843440.1424 | 8765911.8035 | 39203105.5657 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 55087912.3929 | 78341045.1799 | 133352.1432 | 6.8398 | 8054.0394 | 11453.7261 | 164.1925 | 233.4997
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5728 | 24.583 | 1.8157 | 4 | 7768.5528 | 10970.1593 | 158.3725 | 223.6415 | 118.1857 | 0 | 169.8079 | 3728187.5162 | 147100.0751 | 4419142.6728 | 4355195.0199 | 0 | 438700.7796 | 0 | 5104447.1647 | 13280724.4566 | 9064367.3332 | 40537865.018 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 56422671.8452 | 79675804.6321 | 177827.941 | 7.263 | 7768.5528 | 10970.1593 | 158.3725 | 223.6415
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.583 | 25.4149 | 1.9016 | 4 | 7554.2465 | 10611.3628 | 154.0035 | 216.327 | 118.112 | 0 | 173.6239 | 3815578.5896 | 150429.7768 | 4538627.1688 | 4504198.5511 | 0 | 414198.6845 | 0 | 5234982.7806 | 13620351.3526 | 9296169.6684 | 41574536.5725 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 57459343.3998 | 80712476.1867 | 237137.3706 | 7.6062 | 7554.2465 | 10611.3628 | 154.0035 | 216.327
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.7003 | 26.0588 | 1.9696 | 4 | 7393.3718 | 10344.8152 | 150.7239 | 210.8931 | 118.0508 | 0 | 192.5399 | 3882492.6536 | 152970.952 | 4630581.488 | 4619764.8901 | 0 | 392223.518 | 0 | 5334433.0656 | 13879100.5941 | 9472771.3425 | 42364338.5039 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 58249145.3311 | 81502278.1181 | 316227.766 | 7.8786 | 7393.3718 | 10344.8152 | 150.7239 | 210.8931
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.1124 | 26.5552 | 2.023 | 4 | 7272.606 | 10146.1641 | 148.2619 | 206.8433 | 118.0011 | 0 | 163.9825 | 3933667.1077 | 154909.3362 | 4701184.5675 | 4709026.1602 | 0 | 373464.9673 | 0 | 5410178.3341 | 14076174.2453 | 9607278.1589 | 42965882.8771 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 58850689.7043 | 82103822.4913 | 421696.5034 | 8.0921 | 7272.606 | 10146.1641 | 148.2619 | 206.8433
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9493 | 26.9323 | 2.0643 | 4 | 7181.9383 | 9998.0387 | 146.4135 | 203.8235 | 117.9619 | 0 | 173.0754 | 3972319.913 | 156371.2252 | 4754649.5975 | 4777071.9114 | 0 | 357802.5393 | 0 | 5467103.9227 | 14224282.9497 | 9708365.393 | 43417967.4519 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 59302774.2791 | 82555907.066 | 562341.3252 | 8.2572 | 7181.9383 | 9998.0387 | 146.4135 | 203.8235
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.3325 | 27.2157 | 2.0959 | 4 | 7113.8823 | 9887.5894 | 145.0261 | 201.5719 | 117.9317 | 0 | 164.1757 | 4001227.0289 | 157462.8504 | 4794725.2666 | 4828259.6474 | 0 | 344972.1205 | 0 | 5509392.2964 | 14334308.6235 | 9783460.1762 | 43753808.01 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 59638614.8372 | 82891747.6242 | 749894.2093 | 8.3834 | 7113.8823 | 9887.5894 | 145.0261 | 201.5719
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.446 | 27.034 | 2.1005 | 4 | 7059.0307 | 9826.6512 | 143.9079 | 200.3296 | 117.9508 | 0 | 414.0838 | 3982697.4635 | 156762.9027 | 4769039.6229 | 4795446.4802 | 0 | 316252.063 | 0 | 5467877.4276 | 14226295.4508 | 9709738.9663 | 43424110.377 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 59308917.2042 | 82562049.9911 | 1000000 | 8.4019 | 7059.0307 | 9826.6512 | 143.9079 | 200.3296
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.5567 | 27.6703 | 2.1434 | 4 | 7020.1226 | 9732.2508 | 143.1147 | 198.4051 | 117.8819 | 0 | 174.465 | 4047373.4897 | 159202.6002 | 4858859.7612 | 4910492.9382 | 0 | 328366.8425 | 0 | 5578675.2964 | 14514568.7776 | 9906491.4353 | 44304031.141 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60188837.9682 | 83441970.7551 | 1333521.4322 | 8.5738 | 7020.1226 | 9732.2508 | 143.1147 | 198.4051
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1487 | 27.791 | 2.1571 | 4 | 6991.8085 | 9686.701 | 142.5375 | 197.4765 | 117.8683 | 0 | 164.8539 | 4059579.356 | 159662.0805 | 4875859.188 | 4932357.6734 | 0 | 322244.6522 | 0 | 5596384.1506 | 14560643.5835 | 9937938.4371 | 44444669.1213 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60329475.9485 | 83582608.7354 | 1778279.41 | 8.6286 | 6991.8085 | 9686.701 | 142.5375 | 197.4765
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5897 | 27.8809 | 2.1675 | 4 | 6970.5658 | 9652.6451 | 142.1044 | 196.7822 | 117.8582 | 0 | 166.8787 | 4068652.8529 | 160003.4688 | 4888505.4313 | 4948641.4604 | 0 | 317491.591 | 0 | 5609484.9737 | 14594729.2379 | 9961202.5966 | 44548711.6125 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60433518.4397 | 83686651.2266 | 2371373.7057 | 8.6698 | 6970.5658 | 9652.6451 | 142.1044 | 196.7822
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9233 | 27.9488 | 2.1752 | 4 | 6954.6299 | 9627.104 | 141.7795 | 196.2615 | 117.8504 | 0 | 187.7192 | 4075504.935 | 160261.1778 | 4898060.8255 | 4960955.5827 | 0 | 313872.8615 | 0 | 5619375.5992 | 14620462.6166 | 9978766.1563 | 44627259.7545 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60512066.5817 | 83765199.3686 | 3162277.6602 | 8.701 | 6954.6299 | 9627.104 | 141.7795 | 196.2615
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1692 | 27.9989 | 2.1811 | 4 | 6942.676 | 9608.0243 | 141.5358 | 195.8726 | 117.8447 | 0 | 153.5745 | 4080551.7691 | 160450.9346 | 4905101.7097 | 4970034.9237 | 0 | 311077.631 | 0 | 5626614.6175 | 14639297.0575 | 9991621.0492 | 44684749.6922 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60569556.5194 | 83822689.3064 | 4216965.0343 | 8.7242 | 6942.676 | 9608.0243 | 141.5358 | 195.8726
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3519 | 28.0361 | 2.1854 | 4 | 6933.7097 | 9593.7511 | 141.3531 | 195.5816 | 117.8404 | 0 | 164.5912 | 4084295.0084 | 160591.6465 | 4910325.5545 | 4976774.2793 | 0 | 308939.3707 | 0 | 5631961.0852 | 14653207.4696 | 10001115.1913 | 44727209.6054 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60612016.4327 | 83865149.2196 | 5623413.2519 | 8.7416 | 6933.7097 | 9593.7511 | 141.3531 | 195.5816
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.4936 | 28.0649 | 2.1887 | 4 | 6926.9847 | 9582.992 | 141.216 | 195.3623 | 117.8371 | 0 | 158.6559 | 4087197.4855 | 160700.7368 | 4914376.9778 | 4982002.8533 | 0 | 307362.1823 | 0 | 5636139.6919 | 14664079.3471 | 10008535.4711 | 44760394.7457 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60645201.573 | 83898334.3599 | 7498942.0933 | 8.7549 | 6926.9847 | 9582.992 | 141.216 | 195.3623
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5908 | 28.0847 | 2.1911 | 4 | 6921.941 | 9575.0437 | 141.1131 | 195.2002 | 117.8348 | 0 | 157.9403 | 4089188.2399 | 160775.5484 | 4917156.3269 | 4985590.7492 | 0 | 306092.8676 | 0 | 5638933.4555 | 14671348.1469 | 10013496.5763 | 44782581.9107 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60667388.7379 | 83920521.5248 | 10000000 | 8.7645 | 6921.941 | 9575.0437 | 141.1131 | 195.2002
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1079 | [19 empty] | 100 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5444 | [19 empty] | 133.3521 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.356 | [19 empty] | 177.8279 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0245 | [19 empty] | 237.1374 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0464 | [19 empty] | 316.2278 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.23442 | 0.0015102 | 4 | 2904749.5038 | 6860257.2159 | 59217.2476 | 139855.6225 | 95.3522 | 0 | 28.7765 | 123838.9064 | 4190.6857 | 108671.1402 | 74926.554 | 0 | 77147.7589 | 0 | 151622.2676 | 394490.0383 | 269247.5571 | 1204134.9083 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17547050.1529 | 41441534.7241 | 421.6965 | 0.0060408 | 2904749.5038 | 6860257.2159 | 59217.2476 | 139855.6225
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.33061 | 0.0061605 | 4 | 724760.1577 | 1694419.0135 | 14775.2161 | 34543.0235 | 100.3803 | 0 | 317.4908 | 162909.4941 | 5720.0421 | 142531.8684 | 92141.1059 | 0 | 86401.4843 | 0 | 190984.5579 | 496902.6434 | 339146.2645 | 1516737.4605 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17859652.7051 | 41754137.2764 | 562.3413 | 0.024642 | 724760.1577 | 1694419.0135 | 14775.2161 | 34543.0235
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8961 | 0.51096 | 0.013228 | 4 | 348090.231 | 799672.3564 | 7096.2902 | 16302.4026 | 105.8799 | 0 | 461.5371 | 228595.4579 | 8354.6286 | 201092.5216 | 123887.0417 | 0 | 108186.9817 | 0 | 261345.4863 | 679967.346 | 464091.6856 | 2075521.1495 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 18418436.3941 | 42312920.9653 | 749.8942 | 0.052913 | 348090.231 | 799672.3564 | 7096.2902 | 16302.4026
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9534 | 0.74363 | 0.023492 | 4 | 202990.6842 | 457278.4225 | 4138.2397 | 9322.2392 | 109.7701 | 0 | 68.45 | 304056.4163 | 11429.5147 | 270727.0646 | 164357.0928 | 0 | 131299.4536 | 0 | 343929.1214 | 894833.0244 | 610741.9261 | 2731373.614 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19074288.8586 | 42968773.4298 | 1000 | 0.093966 | 202990.6842 | 457278.4225 | 4138.2397 | 9322.2392
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2808 | 1.039 | 0.037772 | 4 | 131327.43 | 289478.3895 | 2677.2873 | 5901.4085 | 112.5773 | 0 | 78.1264 | 390393.8057 | 14974.3298 | 353076.9021 | 215541.6882 | 0 | 155689.7459 | 0 | 440573.824 | 1146282.7159 | 782361.5073 | 3498894.5189 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19841809.7635 | 43736294.3348 | 1333.5214 | 0.15109 | 131327.43 | 289478.3895 | 2677.2873 | 5901.4085
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9354 | 1.4086 | 0.056978 | 4 | 90973.9364 | 195813.8938 | 1854.6267 | 3991.9311 | 114.6063 | 0 | 71.2409 | 488508.4665 | 19009.1383 | 449750.8206 | 279318.1734 | 0 | 181221.1812 | 0 | 552945.0342 | 1438649.5544 | 981907.8822 | 4391310.251 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 20734225.4955 | 44628710.0668 | 1778.2794 | 0.22791 | 90973.9364 | 195813.8938 | 1854.6267 | 3991.9311
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3829 | 1.9593 | 0.083664 | 4 | 65729.0129 | 137129.033 | 1339.9748 | 2795.5608 | 116.4032 | 0 | 87.998 | 621635.7259 | 24495.1371 | 584868.1128 | 374137.7397 | 0 | 220264.2069 | 0 | 711906.3597 | 1852234.316 | 1264187.9803 | 5653729.5784 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 21996644.823 | 45891129.3942 | 2371.3737 | 0.33466 | 65729.0129 | 137129.033 | 1339.9748 | 2795.5608
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9628 | 2.5407 | 0.11793 | 4 | 49229.2331 | 99882.0218 | 1003.6045 | 2036.2301 | 117.5101 | 0 | 99.1906 | 750324.6098 | 29787.1684 | 719439.2829 | 474111.3678 | 0 | 247671.408 | 0 | 866320.1964 | 2253987.4444 | 1538392.7456 | 6880034.2235 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 23222949.4681 | 47117434.0394 | 3162.2777 | 0.47173 | 49229.2331 | 99882.0218 | 1003.6045 | 2036.2301
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.466 | 3.3306 | 0.16341 | 4 | 37963.5244 | 74518.4539 | 773.9378 | 1519.1595 | 118.4279 | 0 | 82.9018 | 911813.1192 | 36411.8691 | 892849.5884 | 609841.0232 | 0 | 284511.3749 | 0 | 1066816.5202 | 2775637.7514 | 1894429.799 | 8472311.0454 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 24815226.29 | 48709710.8613 | 4216.965 | 0.65366 | 37963.5244 | 74518.4539 | 773.9378 | 1519.1595
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8434 | 4.3186 | 0.22264 | 4 | 29984.7813 | 56816.0273 | 611.2803 | 1158.2716 | 119.1272 | 0 | 102.7018 | 1098510.8497 | 44051.8921 | 1098545.6244 | 779659.3048 | 0 | 324111.9909 | 0 | 1304503.0682 | 3394049.393 | 2316508.4515 | 10359940.5746 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 26702855.8192 | 50597340.3904 | 5623.4133 | 0.89055 | 29984.7813 | 56816.0273 | 611.2803 | 1158.2716
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2903 | 5.548 | 0.29895 | 4 | 24197.4045 | 44179.2092 | 493.2968 | 900.6529 | 119.6649 | 0 | 105.8815 | 1313922.7724 | 52840.9397 | 1341794.9033 | 990543.3836 | 0 | 366640.2239 | 0 | 1585639.4669 | 4125508.6335 | 2815744.4131 | 12592634.7362 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 28935549.9808 | 52830034.5521 | 7498.9421 | 1.1958 | 24197.4045 | 44179.2092 | 493.2968 | 900.6529
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.9628 | 7.0547 | 0.39605 | 4 | 19912.0707 | 34995.1204 | 405.9345 | 713.4229 | 120.0781 | 0 | 111.1842 | 1559566.1158 | 62834.9371 | 1625685.503 | 1249025.9736 | 0 | 411002.7913 | 0 | 1914164.9751 | 4980264.6161 | 3399132.9347 | 15201677.8468 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 31544593.0914 | 55439077.6627 | 10000 | 1.5842 | 19912.0707 | 34995.1204 | 405.9345 | 713.4229
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.936 | 8.8563 | 0.51711 | 4 | 16691.8296 | 28243.7418 | 340.2855 | 575.7869 | 120.3941 | 0 | 110.7865 | 1833873.7601 | 73964.4879 | 1949654.8496 | 1558332.2626 | 0 | 454924.4351 | 0 | 2289592.4202 | 5957049.8174 | 4065808.9055 | 18183200.9384 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 34526116.183 | 58420600.7542 | 13335.2143 | 2.0684 | 16691.8296 | 28243.7418 | 340.2855 | 575.7869
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.1996 | 10.9492 | 0.66395 | 4 | 14249.9402 | 23247.053 | 290.5043 | 473.9226 | 120.6304 | 0 | 127.4197 | 2132728.0093 | 86053.8716 | 2309887.2199 | 1917682.5688 | 0 | 495927.9558 | 0 | 2707489.0539 | 7044331.136 | 4807900.7468 | 21502000.5623 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 37844915.8069 | 61739400.3782 | 17782.7941 | 2.6558 | 14249.9402 | 23247.053 | 290.5043 | 473.9226
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.4165 | 13.2543 | 0.83433 | 4 | 12391.238 | 19551.0313 | 252.6121 | 398.5742 | 120.789 | 0 | 133.9252 | 2442944.1018 | 98558.2401 | 2691047.5007 | 2313722.9027 | 0 | 528799.6705 | 0 | 3149278.2422 | 8193775.9803 | 5592420.4718 | 25010547.1101 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 41353462.3547 | 65247946.9259 | 23713.7371 | 3.3373 | 12391.238 | 19551.0313 | 252.6121 | 398.5742
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.0692 | 15.6492 | 1.0216 | 4 | 10978.1214 | 16825.2826 | 223.8039 | 343.0061 | 120.8686 | 0 | 116.4121 | 2748494.1583 | 110817.9226 | 3073307.709 | 2725897.5941 | 0 | 549411.6668 | 0 | 3591092.3298 | 9343285.6079 | 6376984.4127 | 28519291.4013 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 44862206.6459 | 68756691.2172 | 31622.7766 | 4.0865 | 10978.1214 | 16825.2826 | 223.8039 | 343.0061
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5024 | 17.9811 | 1.2152 | 4 | 9907.484 | 14823.089 | 201.9775 | 302.1887 | 120.8753 | 0 | 163.2037 | 3032393.2067 | 122144.0966 | 3434500.2973 | 3128351.7182 | 0 | 555201.0658 | 0 | 4006310.25 | 10423597.4632 | 7114319.4522 | 31816817.5499 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 48159732.7945 | 72054217.3658 | 42169.6503 | 4.8609 | 9907.484 | 14823.089 | 201.9775 | 302.1887
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.2271 | 20.1384 | 1.4044 | 4 | 9099.1105 | 13352.5385 | 185.4977 | 272.2096 | 120.826 | 0 | 151.2637 | 3284744.3235 | 132147.1268 | 3760502.1582 | 3502022.2597 | 0 | 547679.5108 | 0 | 4378567.1978 | 11392133.681 | 7775365.3222 | 34773161.5801 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 51116076.8247 | 75010561.3959 | 56234.1325 | 5.6177 | 9099.1105 | 13352.5385 | 185.4977 | 272.2096
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.8434 | 22.0341 | 1.5795 | 4 | 8490.2959 | 12272.3057 | 173.0862 | 250.1876 | 120.7425 | 0 | 172.4212 | 3499228.11 | 140593.0117 | 4041351.6135 | 3831684.3404 | 0 | 529490.8715 | 0 | 4696515.6994 | 12219370.4619 | 8339971.4232 | 37298205.5315 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 53641120.7761 | 77535605.3473 | 74989.4209 | 6.3179 | 8490.2959 | 12272.3057 | 173.0862 | 250.1876
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.2124 | 23.6421 | 1.7345 | 4 | 8032.4942 | 11476.4007 | 163.7533 | 233.962 | 120.6443 | 0 | 156.928 | 3676303.3512 | 147521.8357 | 4275915.1998 | 4112438.8071 | 0 | 504916.9274 | 0 | 4959667.4872 | 12904037.4341 | 8807270.7002 | 39388071.7426 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 55730986.9872 | 79625471.5584 | 100000 | 6.9382 | 8032.4942 | 11476.4007 | 163.7533 | 233.962
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.2876 | 24.9578 | 1.8665 | 4 | 7688.5364 | 10888.9452 | 156.7412 | 221.9859 | 120.5462 | 0 | 185.2203 | 3818089.3957 | 153038.2101 | 4465552.9419 | 4343007.5379 | 0 | 477300.9299 | 0 | 5170225.7161 | 13451866.7541 | 9181175.4679 | 41060256.9535 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 57403172.1981 | 81297656.7694 | 133352.1432 | 7.4661 | 7688.5364 | 10888.9452 | 156.7412 | 221.9859
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.1844 | 26.0113 | 1.9756 | 4 | 7430.2094 | 10453.9051 | 151.4749 | 213.117 | 120.4566 | 0 | 186.8528 | 3929709.122 | 157359.5924 | 4616019.0391 | 4528228.279 | 0 | 449722.9342 | 0 | 5335605.197 | 13882150.2395 | 9474852.7882 | 42373647.1915 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 58716562.4361 | 82611047.0073 | 177827.941 | 7.9024 | 7430.2094 | 10453.9051 | 151.4749 | 213.117
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0501 | 26.8385 | 2.0636 | 4 | 7236.2198 | 10130.9991 | 147.5201 | 206.5341 | 120.3795 | 0 | 188.5346 | 4016193.5218 | 160694.1444 | 4733334.5133 | 4674041.3466 | 0 | 424045.0986 | 0 | 5463240.3636 | 14214230.7614 | 9701504.5679 | 43387284.3176 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 59730199.5622 | 83624684.1334 | 237137.3706 | 8.2543 | 7236.2198 | 10130.9991 | 147.5201 | 206.5341
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0392 | 27.4752 | 2.133 | 4 | 7090.5499 | 9891.0586 | 144.5505 | 201.6426 | 120.3162 | 0 | 171.4717 | 4082095.2648 | 163226.6772 | 4823169.5427 | 4786529.8806 | 0 | 401168.2611 | 0 | 5559913.9543 | 14465755.614 | 9873175.4481 | 44155034.6428 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 60497949.8874 | 84392434.4587 | 316227.766 | 8.5322 | 7090.5499 | 9891.0586 | 144.5505 | 201.6426
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3561 | 27.9669 | 2.1875 | 4 | 6981.1677 | 9712.0112 | 142.3205 | 197.9925 | 120.2649 | 0 | 167.9186 | 4132604.6927 | 165162.5982 | 4892284.6513 | 4873565.4147 | 0 | 381854.371 | 0 | 5633733.9739 | 14657820.1623 | 10004263.4488 | 44741289.3128 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61084204.5574 | 84978689.1287 | 421696.5034 | 8.7499 | 6981.1677 | 9712.0112 | 142.3205 | 197.9925
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.107 | 28.3376 | 2.2293 | 4 | 6899.0393 | 9578.6306 | 140.6462 | 195.2733 | 120.225 | 0 | 192.9359 | 4170448.0177 | 166610.065 | 4944219.7281 | 4939248.7539 | 0 | 365713.2021 | 0 | 5688633.5091 | 14800657.4914 | 10101752.861 | 45177283.6283 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61520198.8729 | 85414683.4442 | 562341.3252 | 8.9172 | 6899.0393 | 9578.6306 | 140.6462 | 195.2733
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4371 | 28.6185 | 2.2614 | 4 | 6837.3808 | 9478.9632 | 139.3893 | 193.2415 | 120.194 | 0 | 184.1045 | 4199007.1745 | 167700.6942 | 4983500.5435 | 4989089.1892 | 0 | 352667.8435 | 0 | 5729866.5235 | 14907937.3369 | 10174973.5599 | 45504742.8651 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61847658.1097 | 85742142.681 | 749894.2093 | 9.0455 | 6837.3808 | 9478.9632 | 139.3893 | 193.2415
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4434 | 28.8307 | 2.2858 | 4 | 6791.0961 | 9404.4249 | 138.4457 | 191.7219 | 120.1701 | 0 | 187.8762 | 4220507.0449 | 168520.7422 | 5013121.8163 | 5026765.4024 | 0 | 342302.3822 | 0 | 5760774.7813 | 14988354.2836 | 10229859.7784 | 45750206.2314 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62093121.476 | 85987606.0472 | 1000000 | 9.1433 | 6791.0961 | 9404.4249 | 138.4457 | 191.7219
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2035 | 28.9907 | 2.3044 | 4 | 6756.3561 | 9348.6302 | 137.7375 | 190.5845 | 120.1518 | 0 | 148.8659 | 4236687.262 | 169137.3108 | 5035442.6264 | 5055208.4259 | 0 | 334183.1649 | 0 | 5783956.9281 | 15048669.4742 | 10271026.1354 | 45934311.3277 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62277226.5723 | 86171711.1435 | 1333521.4322 | 9.2176 | 6756.3561 | 9348.6302 | 137.7375 | 190.5845
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1561 | 29.1912 | 2.3239 | 4 | 6726.213 | 9296.7179 | 137.1229 | 189.5262 | 120.1288 | 0 | 170.5456 | 4256900.276 | 169907.0564 | 5063355.2931 | 5090835.0728 | 0 | 329479.2462 | 0 | 5815086.0084 | 15129660.9556 | 10326304.4857 | 46181528.3942 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62524443.6388 | 86418928.2101 | 1778279.41 | 9.2956 | 6726.213 | 9296.7179 | 137.1229 | 189.5262
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5628 | 29.2766 | 2.3342 | 4 | 6706.9659 | 9266.1755 | 136.7306 | 188.9035 | 120.1188 | 0 | 184.8075 | 4265500.8181 | 170234.2455 | 5075246.6543 | 5106036.7951 | 0 | 324535.787 | 0 | 5827206.177 | 15161195.1482 | 10347827.22 | 46277782.8452 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62620698.0898 | 86515182.6611 | 2371373.7057 | 9.3367 | 6706.9659 | 9266.1755 | 136.7306 | 188.9035
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8944 | 29.3463 | 2.3422 | 4 | 6692.5263 | 9242.9727 | 136.4362 | 188.4305 | 120.1106 | 0 | 163.838 | 4272500.9237 | 170500.4531 | 5084930.1253 | 5118425.2172 | 0 | 320988.9298 | 0 | 5837264.8031 | 15187365.63 | 10365689.1116 | 46357665.1937 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62700580.4383 | 86595065.0096 | 3162277.6602 | 9.3687 | 6692.5263 | 9242.9727 | 136.4362 | 188.4305
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1307 | 29.3959 | 2.3481 | 4 | 6681.6944 | 9225.74 | 136.2154 | 188.0792 | 120.1048 | 0 | 171.8699 | 4277484.5196 | 170689.913 | 5091827.058 | 5127254.0114 | 0 | 318175.8889 | 0 | 5844318.2424 | 15205717.2323 | 10378214.4573 | 46413681.3228 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62756596.5674 | 86651081.1387 | 4216965.0343 | 9.3923 | 6681.6944 | 9225.74 | 136.2154 | 188.0792
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3009 | 29.4316 | 2.3524 | 4 | 6673.5695 | 9212.9112 | 136.0497 | 187.8177 | 120.1006 | 0 | 165.3112 | 4281070.9333 | 170826.2244 | 5096791.932 | 5133612.306 | 0 | 315978.9742 | 0 | 5849329.3443 | 15218755.0913 | 10387113.064 | 46453477.8694 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62796393.114 | 86690877.6853 | 5623413.2519 | 9.4097 | 6673.5695 | 9212.9112 | 136.0497 | 187.8177
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4324 | 29.4592 | 2.3557 | 4 | 6667.4754 | 9203.2486 | 135.9255 | 187.6207 | 120.0973 | 0 | 166.4837 | 4283839.838 | 170931.4483 | 5100625.8835 | 5138523.7739 | 0 | 314351.5867 | 0 | 5853226.2869 | 15228894.1366 | 10394033.1707 | 46484426.1246 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62827341.3692 | 86721825.9404 | 7498942.0933 | 9.423 | 6667.4754 | 9203.2486 | 135.9255 | 187.6207
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5445 | 29.4827 | 2.3584 | 4 | 6662.9048 | 9195.842 | 135.8323 | 187.4697 | 120.0945 | 0 | 166.8635 | 4286198.2857 | 171021.0669 | 5103891.9373 | 5142708.6678 | 0 | 313243.0239 | 0 | 5856654.5628 | 15237813.8074 | 10400121.0293 | 46511652.3812 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62854567.6258 | 86749052.1971 | 10000000 | 9.4335 | 6662.9048 | 9195.842 | 135.8323 | 187.4697
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6737 | [19 empty] | 100 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5824 | [19 empty] | 133.3521 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2439 | [19 empty] | 177.8279 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8548 | [19 empty] | 237.1374 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8573 | [19 empty] | 316.2278 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.24012 | 0.0025897 | 4 | 1740109.8538 | 4109539.7814 | 35474.493 | 83778.527 | 96.6468 | 0 | 29.2562 | 127136.3038 | 4341.1225 | 110669.6518 | 75458.6286 | 0 | 75731.4457 | 0 | 153401.4895 | 399119.2086 | 272407.061 | 1218264.9116 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18025148.6644 | 42569189.1472 | 421.6965 | 0.010359 | 1740109.8538 | 4109539.7814 | 35474.493 | 83778.527
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.38216 | 0.0079331 | 4 | 582888.1729 | 1356358.1391 | 11882.9638 | 27651.1953 | 103.5153 | 0 | 352.0608 | 184020.5544 | 6606.9906 | 159676.5774 | 100437.6079 | 0 | 94755.556 | 0 | 212743.9417 | 553516.0965 | 377786.1095 | 1689543.4339 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18496427.1868 | 43040467.6696 | 562.3413 | 0.031732 | 582888.1729 | 1356358.1391 | 11882.9638 | 27651.1953
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1295 | 0.57839 | 0.016171 | 4 | 295074.6765 | 674520.202 | 6015.4964 | 13751.0067 | 108.6797 | 0 | 505.1656 | 253621.4772 | 9453.1016 | 221596.7693 | 134302.2296 | 0 | 117070.7087 | 0 | 287057.2717 | 746864.1374 | 509750.1203 | 2279715.8158 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19086599.5686 | 43630640.0514 | 749.8942 | 0.064684 | 295074.6765 | 674520.202 | 6015.4964 | 13751.0067
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.8382 | 0.028028 | 4 | 176623.9163 | 395545.4498 | 3600.7174 | 8063.729 | 112.4673 | 0 | 80.5833 | 335919.6752 | 12866.1448 | 297357.0624 | 178681.6975 | 0 | 142169.6865 | 0 | 377127.7639 | 981209.082 | 669695.3603 | 2995026.4726 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19801910.2254 | 44345950.7082 | 1000 | 0.11211 | 176623.9163 | 395545.4498 | 3600.7174 | 8063.729
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6977 | 1.1679 | 0.044406 | 4 | 116193.928 | 254373.2572 | 2368.7704 | 5185.7429 | 115.196 | 0 | 71.4969 | 430059.1317 | 16794.998 | 386959.4063 | 234669.1247 | 0 | 168745.6519 | 0 | 482519.0419 | 1255415.5687 | 856846.9219 | 3832009.845 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 20638893.5979 | 45182934.0807 | 1333.5214 | 0.17762 | 116193.928 | 254373.2572 | 2368.7704 | 5185.7429
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4151 | 1.5648 | 0.066226 | 4 | 81442.2912 | 174095.1495 | 1660.3113 | 3549.1651 | 117.0881 | 0 | 65.3644 | 533272.4857 | 21107.5007 | 488347.5386 | 302216.1443 | 0 | 194304.3306 | 0 | 600306.72 | 1561874.9456 | 1066011.7437 | 4767441.4092 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 21574325.162 | 46118365.6448 | 1778.2794 | 0.2649 | 81442.2912 | 174095.1495 | 1660.3113 | 3549.1651
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8628 | 2.136 | 0.096489 | 4 | 59205.6327 | 122798.2428 | 1206.9869 | 2503.4083 | 118.8004 | 0 | 100.7458 | 669265.9212 | 26803.7865 | 625637.266 | 398718.2476 | 0 | 230971.3917 | 0 | 761044.679 | 1980082.1431 | 1351446.7493 | 6043970.1843 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 22850853.9372 | 47394894.42 | 2371.3737 | 0.38596 | 59205.6327 | 122798.2428 | 1206.9869 | 2503.4083
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8083 | 2.8224 | 0.13584 | 4 | 44691.8298 | 89862.2032 | 911.1034 | 1831.9626 | 119.9677 | 0 | 81.0201 | 818735.2673 | 33045.0937 | 781225.7815 | 514543.6186 | 0 | 266567.2024 | 0 | 941505.6158 | 2449604.4829 | 1671905.3939 | 7477132.4562 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 24284016.2091 | 48828056.6919 | 3162.2777 | 0.54337 | 44691.8298 | 89862.2032 | 911.1034 | 1831.9626
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5332 | 3.6921 | 0.18757 | 4 | 34657.0276 | 67370.396 | 706.5304 | 1373.4366 | 120.8603 | 0 | 85.2047 | 993330.4903 | 40319.0231 | 967899.3087 | 661546.42 | 0 | 305804.9419 | 0 | 1157871.0718 | 3012543.0168 | 2056122.5106 | 9195436.7833 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 26002320.5362 | 50546361.019 | 4216.965 | 0.75028 | 34657.0276 | 67370.396 | 706.5304 | 1373.4366
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1882 | 4.7798 | 0.25482 | 4 | 27510.6809 | 51590.8481 | 560.8424 | 1051.7492 | 121.5422 | 0 | 75.3912 | 1195329.4512 | 48712.875 | 1189422.6657 | 845469.4681 | 0 | 348070.7099 | 0 | 1414532.0163 | 3680322.1461 | 2511895.4877 | 11233754.8202 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 28040638.573 | 52584679.0558 | 5623.4133 | 1.0193 | 27510.6809 | 51590.8481 | 560.8424 | 1051.7492
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.9345 | 6.1232 | 0.34118 | 4 | 22300.8625 | 40285.7284 | 454.6332 | 821.2791 | 122.0642 | 0 | 94.5595 | 1426854.381 | 58305.2509 | 1449543.7083 | 1072484.7683 | 0 | 392587.1174 | 0 | 1715912.3381 | 4464451.9216 | 3047080.1718 | 13627219.6574 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 30434103.4102 | 54978143.893 | 7498.9421 | 1.3647 | 22300.8625 | 40285.7284 | 454.6332 | 821.2791
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.9675 | 7.767 | 0.4506 | 4 | 18434.1393 | 32051.4638 | 375.8049 | 653.4124 | 122.4671 | 0 | 98.064 | 1690596.3002 | 69196.3298 | 1752801.3124 | 1349499.6802 | 0 | 439069.1825 | 0 | 2067453.494 | 5379089.8983 | 3671339.3848 | 16419045.5822 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 33225929.335 | 57769969.8178 | 10000 | 1.8024 | 18434.1393 | 32051.4638 | 375.8049 | 653.4124
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.3324 | 9.7227 | 0.58634 | 4 | 15520.2482 | 25985.1988 | 316.4013 | 529.7434 | 122.7745 | 0 | 119.3336 | 1983874.3956 | 81271.6986 | 2097328.2503 | 1679019.9267 | 0 | 484636.7382 | 0 | 2467191.0937 | 6419125.1353 | 4381184.8046 | 19593632.043 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 36400515.7958 | 60944556.2786 | 13335.2143 | 2.3454 | 15520.2482 | 25985.1988 | 316.4013 | 529.7434
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.977 | 11.9767 | 0.74979 | 4 | 13306.0852 | 21489.6734 | 271.2625 | 438.0961 | 123.0007 | 0 | 142.3686 | 2301175.4479 | 94294.9686 | 2477649.7578 | 2058896.911 | 0 | 526345.0665 | 0 | 2908761.2392 | 7568000.0754 | 5165315.5583 | 23100439.0246 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 39907322.7774 | 64451363.2602 | 17782.7941 | 2.9992 | 13306.0852 | 21489.6734 | 271.2625 | 438.0961
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.4787 | 14.4267 | 0.93744 | 4 | 11618.9661 | 18164.4358 | 236.8683 | 370.3066 | 123.1443 | 0 | 110.4422 | 2626668.9985 | 107606.2381 | 2875154.0696 | 2472821.1241 | 0 | 558187.6006 | 0 | 3369770.832 | 8767452.4699 | 5983966.4638 | 26761627.7965 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 43568511.5494 | 68112552.0322 | 23713.7371 | 3.7498 | 11618.9661 | 18164.4358 | 236.8683 | 370.3066
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.2675 | 16.9329 | 1.1409 | 4 | 10336.8806 | 15715.0995 | 210.7313 | 320.3736 | 123.2048 | 0 | 156.1895 | 2942691.43 | 120463.2253 | 3268080.288 | 2897051.0928 | 0 | 576047.32 | 0 | 3823690.0089 | 9948457.0564 | 6790026.3614 | 30366506.7828 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 47173390.5356 | 71717431.0184 | 31622.7766 | 4.5636 | 10336.8806 | 15715.0995 | 210.7313 | 320.3736
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.7233 | 19.3457 | 1.3486 | 4 | 9366.0234 | 13915.8633 | 190.9391 | 283.6937 | 123.1919 | 0 | 141.7001 | 3233402.2636 | 132215.7147 | 3635627.4901 | 3306709.0787 | 0 | 578459.0044 | 0 | 4245701.285 | 11046443.8306 | 7539424.8961 | 33717983.5632 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 50524867.316 | 75068907.7988 | 42169.6503 | 5.3945 | 9366.0234 | 13915.8633 | 190.9391 | 283.6937
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.3555 | 21.5504 | 1.5491 | 4 | 8633.1798 | 12594.3077 | 175.999 | 256.752 | 123.1254 | 0 | 139.2946 | 3488958.5573 | 142474.8363 | 3963666.9439 | 3682429.8986 | 0 | 567235.3387 | 0 | 4619458.5741 | 12018883.6287 | 8203135.0399 | 36686242.8175 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 53493126.5704 | 78037167.0532 | 56234.1325 | 6.1962 | 8633.1798 | 12594.3077 | 175.999 | 256.752
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.8519 | 23.4784 | 1.733 | 4 | 8081.2397 | 11621.9952 | 164.747 | 236.9301 | 123.0279 | 0 | 155.1011 | 3705357.8003 | 151100.4424 | 4245181.1654 | 4012288.1575 | 0 | 546056.4602 | 0 | 4937393.7701 | 12846085.791 | 8767717.513 | 39211181.0999 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 56018064.8528 | 80562105.3356 | 74989.4209 | 6.9319 | 8081.2397 | 11621.9952 | 164.747 | 236.9301
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.0823 | 25.1056 | 1.8947 | 4 | 7666.0132 | 10904.4647 | 156.282 | 222.3023 | 122.919 | 0 | 154.7613 | 3883353.1488 | 158151.0308 | 4479307.3363 | 4292332.189 | 0 | 519117.8723 | 0 | 5199582.0151 | 13528245.8223 | 9233305.7514 | 41293395.1658 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 58100278.9187 | 82644319.4015 | 100000 | 7.5789 | 7666.0132 | 10904.4647 | 156.282 | 222.3023
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9944 | 26.4262 | 2.0313 | 4 | 7353.9219 | 10374.5885 | 149.9196 | 211.5 | 122.8136 | 0 | 162.285 | 4024861.3487 | 163724.6543 | 4667163.5865 | 4520745.4199 | 0 | 489488.845 | 0 | 5407733.7032 | 14069813.817 | 9602937.0359 | 42946468.4105 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 59753352.1633 | 84297392.6461 | 133352.1432 | 8.1254 | 7353.9219 | 10374.5885 | 149.9196 | 211.5
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.742 | 27.4797 | 2.1437 | 4 | 7119.4549 | 9981.8126 | 145.1397 | 203.4928 | 122.7189 | 0 | 173.7619 | 4135941.1254 | 168078.0603 | 4815745.284 | 4703667.5515 | 0 | 460435.5781 | 0 | 5570708.3637 | 14493840.453 | 9892343.9278 | 44240760.3438 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 61047644.0967 | 85591684.5795 | 177827.941 | 8.5748 | 7119.4549 | 9981.8126 | 145.1397 | 203.4928
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4667 | 28.3018 | 2.2338 | 4 | 6943.3303 | 9690.2172 | 141.5492 | 197.5482 | 122.6386 | 0 | 159.1494 | 4221534.5772 | 171418.814 | 4930927.4009 | 4846854.0901 | 0 | 433591.846 | 0 | 5695687.424 | 14819010.3311 | 10114279.0512 | 45233303.5344 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 62040187.2872 | 86584227.77 | 237137.3706 | 8.9352 | 6943.3303 | 9690.2172 | 141.5492 | 197.5482
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3561 | 28.9367 | 2.3049 | 4 | 6811.0398 | 9473.1798 | 138.8523 | 193.1236 | 122.5728 | 0 | 168.2244 | 4287008.2325 | 173965.8094 | 5019450.3457 | 4957725.7182 | 0 | 410044.9516 | 0 | 5790796.0724 | 15066463.5247 | 10283170.9404 | 45988625.5948 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 62795509.3476 | 87339549.8304 | 316227.766 | 9.2197 | 6811.0398 | 9473.1798 | 138.8523 | 193.1236
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5675 | 29.421 | 2.3602 | 4 | 6711.6816 | 9311.4568 | 136.8267 | 189.8266 | 122.5204 | 0 | 192.7768 | 4336580.6952 | 175889.1741 | 5086718.7338 | 5042459.5138 | 0 | 390047.4478 | 0 | 5862361.2703 | 15252661.4896 | 10410254.8775 | 46556973.202 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 63363856.9549 | 87907897.4377 | 421696.5034 | 9.4408 | 6711.6816 | 9311.4568 | 136.8267 | 189.8266
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2413 | 29.7865 | 2.4027 | 4 | 6637.0657 | 9190.8636 | 135.3056 | 187.3682 | 122.4796 | 0 | 170.3676 | 4373795.0389 | 177330.1129 | 5137358.1811 | 5106523.244 | 0 | 373473.0319 | 0 | 5915707.0474 | 15391456.259 | 10504985.1596 | 46980628.0748 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 63787511.8277 | 88331552.3105 | 562341.3252 | 9.6108 | 6637.0657 | 9190.8636 | 135.3056 | 187.3682
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5176 | 30.0646 | 2.4353 | 4 | 6581.039 | 9100.6455 | 134.1634 | 185.529 | 122.4479 | 0 | 174.0119 | 4401995.9219 | 178420.3404 | 5175813.7496 | 5155332.2714 | 0 | 360181.4708 | 0 | 5955980.064 | 15496238.3872 | 10576501.1151 | 47300463.3203 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64107347.0731 | 88651387.5559 | 749894.2093 | 9.7412 | 6581.039 | 9100.6455 | 134.1634 | 185.529
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4728 | 30.2725 | 2.46 | 4 | 6538.9775 | 9033.2756 | 133.3059 | 184.1555 | 122.4238 | 0 | 168.3003 | 4423000.7681 | 179231.3972 | 5204502.6144 | 5191834.9145 | 0 | 349557.0644 | 0 | 5985769.4359 | 15573744.222 | 10629400.4399 | 47537040.8564 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64343924.6092 | 88887965.092 | 1000000 | 9.8401 | 6538.9775 | 9033.2756 | 133.3059 | 184.1555
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.2085 | 30.4323 | 2.4789 | 4 | 6507.4057 | 8982.6645 | 132.6623 | 183.1238 | 122.405 | 0 | 179.4391 | 4439121.4311 | 179853.2961 | 5226547.2208 | 5219935.733 | 0 | 341387.0091 | 0 | 6008669.4291 | 15633325.307 | 10670065.7547 | 47718905.1808 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64525788.9337 | 89069829.4165 | 1333521.4322 | 9.9157 | 6507.4057 | 8982.6645 | 132.6623 | 183.1238
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.646 | 29.8744 | 2.4565 | 4 | 6481.7055 | 8979.5848 | 132.1383 | 183.061 | 122.4689 | 0 | 599.6695 | 4382704.9477 | 177673.8077 | 5149526.6155 | 5121981.2701 | 0 | 304762.3628 | 0 | 5903293.1115 | 15359157.7442 | 10482940.7595 | 46882040.619 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 63688924.3718 | 88232964.8546 | 1778279.41 | 9.826 | 6481.7055 | 8979.5848 | 132.1383 | 183.061
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1185 | 30.4127 | 2.4925 | 4 | 6462.3777 | 8924.1712 | 131.7443 | 181.9313 | 122.4071 | 0 | 161.9567 | 4437137.8731 | 179776.5379 | 5223841.0635 | 5216491.8802 | 0 | 318604.8281 | 0 | 5996582.3513 | 15601877.2099 | 10648601.7823 | 47622913.5262 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64429797.279 | 88973837.7618 | 2371373.7057 | 9.97 | 6462.3777 | 8924.1712 | 131.7443 | 181.9313
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.787 | 30.7756 | 2.517 | 4 | 6448.6936 | 8886.4797 | 131.4653 | 181.1629 | 122.3658 | 0 | 308.0184 | 4473665.5665 | 181186.582 | 5273797.1777 | 5280246.7481 | 0 | 327335.7198 | 0 | 6059130.3997 | 15764614.4015 | 10759673.2595 | 48119649.8548 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64926533.6076 | 89470574.0904 | 3162277.6602 | 10.0682 | 6448.6936 | 8886.4797 | 131.4653 | 181.1629
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4358 | 31.1358 | 2.5404 | 4 | 6438.3126 | 8853.694 | 131.2537 | 180.4945 | 122.3295 | 0 | 187.8419 | 4509886.9627 | 182589.3958 | 5323247.4162 | 5343361.5235 | 0 | 337532.7403 | 0 | 6121681.035 | 15927358.3236 | 10870749.3303 | 48616406.7274 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65423290.4802 | 89967330.963 | 4216965.0343 | 10.1616 | 6438.3126 | 8853.694 | 131.2537 | 180.4945
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7964 | 31.2145 | 2.5472 | 4 | 6430.8337 | 8839.7164 | 131.1012 | 180.2096 | 122.3214 | 0 | 199.5272 | 4517777.8483 | 182894.7112 | 5334034.4509 | 5357157.9858 | 0 | 337135.9564 | 0 | 6134310.3715 | 15960217.2666 | 10893176.2341 | 48716704.8248 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65523588.5777 | 90067629.0605 | 5623413.2519 | 10.189 | 6430.8337 | 8839.7164 | 131.1012 | 180.2096
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9233 | 31.2421 | 2.5507 | 4 | 6425.2279 | 8830.8859 | 130.987 | 180.0296 | 122.3186 | 0 | 189.7592 | 4520550.5426 | 183001.9491 | 5337826.5491 | 5362011.0604 | 0 | 335503.6084 | 0 | 6138168.5468 | 15970255.4472 | 10900027.4986 | 48747345.2023 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65554228.9551 | 90098269.4379 | 7498942.0933 | 10.2026 | 6425.2279 | 8830.8859 | 130.987 | 180.0296
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.0204 | 31.2633 | 2.5532 | 4 | 6421.0235 | 8824.2442 | 130.9012 | 179.8942 | 122.3164 | 0 | 185.8291 | 4522670.9501 | 183083.9517 | 5340726.9232 | 5365723.727 | 0 | 334289.617 | 0 | 6141133.1159 | 15977968.6479 | 10905291.9166 | 48770888.8494 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65577772.6022 | 90121813.085 | 10000000 | 10.213 | 6421.0235 | 8824.2442 | 130.9012 | 179.8942
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5939 | [19 empty] | 100 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.454 | [19 empty] | 133.3521 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1304 | [19 empty] | 177.8279 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0176 | [19 empty] | 237.1374 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0994 | [19 empty] | 316.2278 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.24576 | 0.003665 | 4 | 1262543.2587 | 2981641.2975 | 25738.652 | 60784.7908 | 97.9232 | 0 | 29.1182 | 130396.5581 | 4491.7168 | 112635.4808 | 75944.8318 | 0 | 74316.737 | 0 | 155136.2766 | 403632.7688 | 275487.6585 | 1232042.0283 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18508754.3803 | 43710554.9018 | 421.6965 | 0.01466 | 1262543.2587 | 2981641.2975 | 25738.652 | 60784.7908
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.43672 | 0.0099962 | 4 | 478767.5422 | 1109054.2198 | 9760.3239 | 22609.5704 | 106.5206 | 0 | 392.5358 | 205852.4409 | 7548.7702 | 177271.6036 | 108900.8274 | 0 | 103104.3474 | 0 | 235044.4159 | 611537.356 | 417386.8113 | 1866646.5728 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19143358.9248 | 44345159.4463 | 562.3413 | 0.039985 | 478767.5422 | 1109054.2198 | 9760.3239 | 22609.5704
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4017 | 0.65862 | 0.019563 | 4 | 252960.8841 | 575024.17 | 5156.9498 | 11722.6455 | 111.5629 | 0 | 551.668 | 282515.4464 | 10743.9191 | 245353.316 | 146489.0889 | 0 | 127795.9744 | 0 | 317030.1205 | 824847.3416 | 562975.2596 | 2517750.4665 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19794462.8184 | 44996263.34 | 749.8942 | 0.078251 | 252960.8841 | 575024.17 | 5156.9498 | 11722.6455
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5648 | 0.93382 | 0.033129 | 4 | 154927.6995 | 345106.1658 | 3158.4107 | 7035.456 | 115.0698 | 0 | 75.2617 | 367699.2315 | 14338.2176 | 323594.7279 | 192631.3952 | 0 | 152272.6219 | 0 | 409709.1157 | 1065979.0761 | 727552.6231 | 3253777.0091 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 20530489.361 | 45732289.8826 | 1000 | 0.13252 | 154927.6995 | 345106.1658 | 3158.4107 | 7035.456
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.058 | 1.2902 | 0.051791 | 4 | 103374.8024 | 225026.5764 | 2107.4352 | 4587.4711 | 117.6927 | 0 | 77.5244 | 467591.0736 | 18577.4073 | 418305.4354 | 252263.1883 | 0 | 179533.1255 | 0 | 521145.3898 | 1355913.4025 | 925438.7585 | 4138767.7809 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 21415480.1329 | 46617280.6544 | 1333.5214 | 0.20716 | 103374.8024 | 225026.5764 | 2107.4352 | 4587.4711
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9 | 1.7298 | 0.076461 | 4 | 73345.503 | 155746.6335 | 1495.2473 | 3175.1058 | 119.5363 | 0 | 68.7567 | 579766.3735 | 23333.6759 | 528206.5671 | 325713.8147 | 0 | 207515.1457 | 0 | 649168.875 | 1689004.2499 | 1152780.1061 | 5155488.8079 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 22432201.1598 | 47634001.6814 | 1778.2794 | 0.30584 | 73345.503 | 155746.6335 | 1495.2473 | 3175.1058
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5622 | 2.3736 | 0.11121 | 4 | 53607.8407 | 110263.6494 | 1092.8683 | 2247.8736 | 121.2846 | 0 | 83.3979 | 730372.78 | 29748.683 | 679535.5252 | 432691.7391 | 0 | 248653.6414 | 0 | 827190.9238 | 2152181.1036 | 1468907.8261 | 6569282.2223 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 23845994.5743 | 49047795.0958 | 2371.3737 | 0.44482 | 53607.8407 | 110263.6494 | 1092.8683 | 2247.8736
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6755 | 3.1246 | 0.15586 | 4 | 40714.7297 | 81139.6158 | 830.0248 | 1654.1408 | 122.4135 | 0 | 80.1636 | 890938.6383 | 36558.5051 | 846028.0937 | 557525.0947 | 0 | 286037.042 | 0 | 1020664.0758 | 2655558.5582 | 1812473.2822 | 8105783.2899 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 25382495.6419 | 50584296.1635 | 3162.2777 | 0.62342 | 40714.7297 | 81139.6158 | 830.0248 | 1654.1408
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6392 | 4.0814 | 0.21442 | 4 | 31755.4171 | 61139.7022 | 647.3771 | 1246.4155 | 123.2855 | 0 | 72.5838 | 1079619.8474 | 44538.8933 | 1046961.3853 | 716191.663 | 0 | 328026.8633 | 0 | 1253982.0744 | 3262604.1305 | 2226794.3588 | 9958719.216 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 27235431.5679 | 52437232.0895 | 4216.965 | 0.85766 | 31755.4171 | 61139.7022 | 647.3771 | 1246.4155
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.587 | 5.2772 | 0.29051 | 4 | 25329.6762 | 47017.1274 | 516.3797 | 958.5077 | 123.9517 | 0 | 99.6943 | 1297957.4716 | 53752.6083 | 1285296.1689 | 915055.2349 | 0 | 373196.2443 | 0 | 1530850.5139 | 3982959.0166 | 2718451.3705 | 12157518.629 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 29434230.9809 | 54636031.5025 | 5623.4133 | 1.162 | 25329.6762 | 47017.1274 | 516.3797 | 958.5077
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.6324 | 6.7382 | 0.38758 | 4 | 20630.5418 | 36886.2387 | 420.5815 | 751.9759 | 124.4584 | 0 | 94.0802 | 1545577.8454 | 64162.0894 | 1562309.7511 | 1157019.6406 | 0 | 419515.0737 | 0 | 1851947.9161 | 4818388.5909 | 3288649.2213 | 14707570.1286 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 31984282.4805 | 57186083.0021 | 7498.9421 | 1.5503 | 20630.5418 | 36886.2387 | 420.5815 | 751.9759
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.0332 | 8.5274 | 0.51044 | 4 | 17125.3385 | 29468.4916 | 349.1232 | 600.7551 | 124.8515 | 0 | 105.4406 | 1828222.5374 | 76007.6714 | 1885696.0756 | 1453185.1112 | 0 | 468135.5865 | 0 | 2227386.323 | 5795202.3128 | 3955344.658 | 17689180.2759 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 34965892.6279 | 60167693.1495 | 10000 | 2.0418 | 17125.3385 | 29468.4916 | 349.1232 | 600.7551
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8151 | 10.6509 | 0.6623 | 4 | 14476.4459 | 23989.4882 | 295.1219 | 489.0582 | 125.1508 | 0 | 108.323 | 2142041.6947 | 89122.5593 | 2252369.3227 | 1804886.5716 | 0 | 515691.0766 | 0 | 2653603.3778 | 6904131.66 | 4712211.7237 | 21074057.9865 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 38350770.3384 | 63552570.86 | 13335.2143 | 2.6492 | 14476.4459 | 23989.4882 | 295.1219 | 489.0582
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.7808 | 13.0591 | 0.84321 | 4 | 12460.91 | 19932.8937 | 254.0325 | 406.359 | 125.3645 | 0 | 124.0443 | 2476466.4969 | 103053.0993 | 2650915.3443 | 2204083.0089 | 0 | 557057.2938 | 0 | 3116714.3448 | 8109051.3993 | 5534594.2043 | 24751935.1916 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 42028647.5436 | 67230448.0652 | 17782.7941 | 3.3728 | 12460.91 | 19932.8937 | 254.0325 | 406.359
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5332 | 15.6506 | 1.0487 | 4 | 10925.7725 | 16933.8082 | 222.7367 | 345.2186 | 125.4914 | 0 | 149.5371 | 2816418.6653 | 117151.8819 | 3063739.839 | 2634249.7855 | 0 | 587391.4343 | 0 | 3595391.1264 | 9354470.1947 | 6384618.123 | 28553431.0502 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 45830143.4021 | 71031943.9237 | 23713.7371 | 4.1947 | 10925.7725 | 16933.8082 | 222.7367 | 345.2186
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.4345 | 18.2645 | 1.2686 | 4 | 9759.5064 | 14726.0952 | 198.9607 | 300.2114 | 125.5318 | 0 | 139.45 | 3142312.1484 | 130590.833 | 3466586.2679 | 3069290.8857 | 0 | 602261.0336 | 0 | 4060306.0557 | 10564083.4737 | 7210204.041 | 32245634.739 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 49522347.0909 | 74724147.6125 | 31622.7766 | 5.0743 | 9759.5064 | 14726.0952 | 198.9607 | 300.2114
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.9 | 20.7556 | 1.4905 | 4 | 8876.6183 | 13103.6531 | 180.9619 | 267.1357 | 125.4989 | 0 | 149.5405 | 3439470.1685 | 142761.6564 | 3840019.2695 | 3485461.5709 | 0 | 601240.5631 | 0 | 4488491.759 | 11678134.8408 | 7970566.9905 | 35646146.8187 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 52922859.1706 | 78124659.6922 | 42169.6503 | 5.9621 | 8876.6183 | 13103.6531 | 180.9619 | 267.1357
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.4681 | 23.0133 | 1.7025 | 4 | 8210.2421 | 11910.8886 | 167.3769 | 242.8196 | 125.4148 | 0 | 166.5071 | 3698904.3358 | 153309.1537 | 4170941.6849 | 3864359.5832 | 0 | 586736.1682 | 0 | 4864957.8611 | 12657622.4144 | 8639087.386 | 38635918.5873 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 55912630.9393 | 81114431.4608 | 56234.1325 | 6.8101 | 8210.2421 | 11910.8886 | 167.3769 | 242.8196
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.8091 | 24.9637 | 1.8949 | 4 | 7708.3092 | 11033.2945 | 157.1443 | 224.9286 | 125.3039 | 0 | 174.2924 | 3916199.067 | 162078.5282 | 4451754.1462 | 4193232.2925 | 0 | 562244.274 | 0 | 5181348.2401 | 13480805.28 | 9200926.6065 | 41148588.4345 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 58425300.7864 | 83627101.308 | 74989.4209 | 7.5795 | 7708.3092 | 11033.2945 | 157.1443 | 224.9286
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.8466 | 26.5951 | 2.0625 | 4 | 7330.7066 | 10385.5209 | 149.4464 | 211.7229 | 125.1856 | 0 | 177.507 | 4093462.9874 | 169183.3045 | 4683388.7976 | 4469566.0532 | 0 | 532437.846 | 0 | 5439735.2056 | 14153075.1618 | 9659764.6146 | 43200613.9707 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 60477326.3226 | 85679126.8442 | 100000 | 8.2499 | 7330.7066 | 10385.5209 | 149.4464 | 211.7229
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.5935 | 27.917 | 2.2033 | 4 | 7046.8264 | 9906.4101 | 143.6591 | 201.9556 | 125.0734 | 0 | 164.1241 | 4234270.1972 | 174792.531 | 4869082.5236 | 4694397.1145 | 0 | 500822.6126 | 0 | 5644612.3417 | 14686123.444 | 10023581.0202 | 44827681.7847 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 62104394.1367 | 87306194.6582 | 133352.1432 | 8.8131 | 7046.8264 | 9906.4101 | 143.6591 | 201.9556
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2144 | 28.9728 | 2.3188 | 4 | 6833.462 | 9550.5954 | 139.3094 | 194.7018 | 124.9736 | 0 | 189.6457 | 4345012.0184 | 179182.058 | 5016194.3879 | 4874721.0117 | 0 | 470537.8974 | 0 | 5805402.4756 | 15104466.3896 | 10309108.6767 | 46104624.9151 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 63381337.2671 | 88583137.7886 | 177827.941 | 9.2751 | 6833.462 | 9550.5954 | 139.3094 | 194.7018
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8102 | 29.79 | 2.4109 | 4 | 6673.1071 | 9286.4359 | 136.0403 | 189.3166 | 124.8903 | 0 | 164.4484 | 4429731.2993 | 182527.964 | 5129345.2406 | 5014963.7329 | 0 | 442644.2471 | 0 | 5927692.8687 | 15422640.9074 | 10526269.3229 | 47075815.5829 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 64352527.9349 | 89554328.4565 | 237137.3706 | 9.6436 | 6673.1071 | 9286.4359 | 136.0403 | 189.3166
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5823 | 30.4171 | 2.4832 | 4 | 6552.6277 | 9089.8396 | 133.5842 | 185.3087 | 124.8227 | 0 | 182.1147 | 4494162.7554 | 185064.1225 | 5215790.7303 | 5122884.3173 | 0 | 418256.9866 | 0 | 6020101.9757 | 15663070.4481 | 10690367.4247 | 47809698.7605 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 65086411.1125 | 90288211.634 | 316227.766 | 9.9329 | 6552.6277 | 9089.8396 | 133.5842 | 185.3087
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7166 | 30.8983 | 2.5395 | 4 | 6462.1188 | 8943.0743 | 131.739 | 182.3167 | 124.7688 | 0 | 190.2594 | 4543255.4068 | 186991.4246 | 5281887.6758 | 5205858.2564 | 0 | 397826.9199 | 0 | 6090169.6766 | 15845372.2328 | 10814792.1387 | 48366153.7316 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 65642866.0836 | 90844666.6051 | 421696.5034 | 10.1581 | 6462.1188 | 8943.0743 | 131.739 | 182.3167
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.3265 | 31.2603 | 2.5827 | 4 | 6394.1354 | 8833.6363 | 130.3531 | 180.0856 | 124.7271 | 0 | 193.7503 | 4579992.952 | 188430.7241 | 5331482.9698 | 5268378.7157 | 0 | 380928.6782 | 0 | 6142193.4755 | 15980727.4862 | 10907174.8804 | 48779309.8819 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 66056022.2339 | 91257822.7554 | 562341.3252 | 10.3307 | 6394.1354 | 8833.6363 | 130.3531 | 180.0856
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5445 | 31.5336 | 2.6156 | 4 | 6343.081 | 8751.8377 | 129.3123 | 178.418 | 124.6949 | 0 | 181.5909 | 4607620.4075 | 189511.41 | 5368855.5353 | 5315639.8359 | 0 | 367335.7539 | 0 | 6181095.5476 | 16081942.6979 | 10976256.3422 | 49088257.5303 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 66364969.8822 | 91566770.4038 | 749894.2093 | 10.4626 | 6343.081 | 8751.8377 | 129.3123 | 178.418
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9876 | 32.0835 | 2.6601 | 4 | 6304.3578 | 8672.8538 | 128.5229 | 176.8079 | 124.6358 | 0 | 201.7285 | 4663100.1224 | 191686.7423 | 5443840.1927 | 5410557.0748 | 0 | 370972.7906 | 0 | 6271261.1999 | 16316535.2296 | 11136370.5654 | 49804323.9177 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67081036.2697 | 92282836.7912 | 1000000 | 10.6404 | 6304.3578 | 8672.8538 | 128.5229 | 176.8079
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7233 | 32.2493 | 2.6799 | 4 | 6275.2148 | 8626.1976 | 127.9287 | 175.8567 | 124.6188 | 0 | 217.2148 | 4679782.5566 | 192341.3987 | 5466392.3363 | 5439151.7538 | 0 | 362962.8839 | 0 | 6294846.0624 | 16377898.204 | 11178252.0564 | 49991627.2521 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67268339.604 | 92470140.1256 | 1333521.4322 | 10.7197 | 6275.2148 | 8626.1976 | 127.9287 | 175.8567
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.2787 | 32.3744 | 2.6949 | 4 | 6253.3419 | 8591.2364 | 127.4828 | 175.144 | 124.6059 | 0 | 176.2365 | 4692348.9806 | 192834.2601 | 5483393.6528 | 5460736.3295 | 0 | 356779.8876 | 0 | 6312576.3131 | 16424028.6793 | 11209737.0537 | 50132435.1567 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67409147.5087 | 92610948.0302 | 1778279.41 | 10.7797 | 6253.3419 | 8591.2364 | 127.4828 | 175.144
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6855 | 32.4659 | 2.7061 | 4 | 6236.9283 | 8565.164 | 127.1482 | 174.6125 | 124.5964 | 0 | 194.1238 | 4701533.7625 | 193194.3379 | 5495827.3156 | 5476537.2715 | 0 | 351926.3516 | 0 | 6325417.4252 | 16457438.6189 | 11232540.0239 | 50234415.1071 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67511127.459 | 92712927.9806 | 2371373.7057 | 10.8244 | 6236.9283 | 8565.164 | 127.1482 | 174.6125
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.995 | 32.5355 | 2.7146 | 4 | 6224.6132 | 8545.5835 | 126.8972 | 174.2133 | 124.5891 | 0 | 194.218 | 4708513.5191 | 193467.8867 | 5505280.0885 | 5488558.6317 | 0 | 348257.8902 | 0 | 6335190.4263 | 16482865.9629 | 11249894.7087 | 50312029.114 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67588741.4659 | 92790541.9875 | 3162277.6602 | 10.8583 | 6224.6132 | 8545.5835 | 126.8972 | 174.2133
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2339 | 32.5892 | 2.721 | 4 | 6215.3744 | 8530.8372 | 126.7088 | 173.9127 | 124.5835 | 0 | 177.1716 | 4713896.6574 | 193678.813 | 5512572.9296 | 5497838.1761 | 0 | 345531.0205 | 0 | 6342771.8627 | 16502591.3054 | 11263357.6602 | 50372238.425 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67648950.7769 | 92850751.2985 | 4216965.0343 | 10.8841 | 6215.3744 | 8530.8372 | 126.7088 | 173.9127
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.3971 | 32.6259 | 2.7257 | 4 | 6208.4441 | 8519.9587 | 126.5675 | 173.6909 | 124.5797 | 0 | 190.8714 | 4717569.8649 | 193822.7093 | 5517550.5934 | 5504174.5523 | 0 | 343310.6295 | 0 | 6347807.0562 | 16515691.8461 | 11272299.0485 | 50412226.3002 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67688938.6521 | 92890739.1737 | 5623413.2519 | 10.9027 | 6208.4441 | 8519.9587 | 126.5675 | 173.6909
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3775 | 32.1712 | 2.7027 | 4 | 6200.5819 | 8531.7323 | 126.4072 | 173.9309 | 124.6264 | 0 | 177.7577 | 4671917.5664 | 192032.2419 | 5455773.036 | 5425699.3673 | 0 | 319477.9209 | 0 | 6265311.0517 | 16301054.1645 | 11125804.4205 | 49757069.7693 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67033782.1213 | 92235582.6428 | 7498942.0933 | 10.8109 | 6200.5819 | 8531.7323 | 126.4072 | 173.9309
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.887 | 32.286 | 2.7108 | 4 | 6196.4449 | 8520.66 | 126.3229 | 173.7052 | 124.6147 | 0 | 410.2336 | 4683466.3506 | 192485.4561 | 5471387.2199 | 5445504.4499 | 0 | 322154.4641 | 0 | 6284849.1968 | 16351888.4103 | 11160499.8377 | 49912235.3853 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67188947.7373 | 92390748.2588 | 10000000 | 10.8431 | 6196.4449 | 8520.66 | 126.3229 | 173.7052
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.187 | [19 empty] | 100 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6744 | [19 empty] | 133.3521 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1121 | [19 empty] | 177.8279 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4075 | [19 empty] | 237.1374 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.058 | [19 empty] | 316.2278 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.31171 | 0.0050356 | 4 | 954401.809 | 2238633.8606 | 19456.7718 | 45637.5792 | 102.684 | 0 | 284.2901 | 158909.0393 | 5664.6073 | 135740.6665 | 86839.8564 | 0 | 88017.4518 | 0 | 185316.9323 | 482156.6442 | 329081.817 | 1471727.015 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19224128.0569 | 45091892.7444 | 421.6965 | 0.020143 | 954401.809 | 2238633.8606 | 19456.7718 | 45637.5792
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.49442 | 0.012392 | 4 | 399466.0356 | 921318.5553 | 8143.6555 | 18782.3249 | 109.4216 | 0 | 424.1527 | 228484.723 | 8551.0169 | 195357.7246 | 117649.1077 | 0 | 111438.4928 | 0 | 257977.6154 | 671204.8367 | 458111.0929 | 2048774.61 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19801175.6519 | 45668940.3394 | 562.3413 | 0.049569 | 399466.0356 | 921318.5553 | 8143.6555 | 18782.3249
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.499 | 0.70079 | 0.023206 | 4 | 219603.1759 | 498280.1296 | 4476.9078 | 10158.1144 | 113.7072 | 0 | 559.4681 | 298735.3879 | 11529.8664 | 257443.1838 | 152011.1606 | 0 | 130042.9135 | 0 | 331407.3798 | 862254.0212 | 588506.087 | 2631930.0002 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 20384331.0421 | 46252095.7297 | 749.8942 | 0.092823 | 219603.1759 | 498280.1296 | 4476.9078 | 10158.1144
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6379 | 0.97942 | 0.038427 | 4 | 137380.583 | 305672.3882 | 2800.689 | 6231.5451 | 117.1345 | 0 | 73.0025 | 384635.0434 | 15213.9865 | 335679.5979 | 198100.7638 | 0 | 152515.8996 | 0 | 423596.6636 | 1102111.6271 | 752213.8316 | 3364067.4135 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 21116468.4555 | 46984233.143 | 1000 | 0.15371 | 137380.583 | 305672.3882 | 2800.689 | 6231.5451
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1654 | 1.3559 | 0.059345 | 4 | 92848.4551 | 201820.9446 | 1892.8413 | 4114.3929 | 119.8363 | 0 | 59.8115 | 489856.2055 | 19749.2929 | 434628.8255 | 259958.8549 | 0 | 180213.5821 | 0 | 539918.6368 | 1404757.5404 | 958775.8862 | 4287858.8243 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 22040259.8663 | 47908024.5538 | 1333.5214 | 0.23738 | 92848.4551 | 201820.9446 | 1892.8413 | 4114.3929
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1922 | 1.8557 | 0.087303 | 4 | 66407.6457 | 140482.3776 | 1353.8097 | 2863.9233 | 121.8201 | 0 | 67.2113 | 616550.4546 | 25205.3549 | 557868.1395 | 342369.8768 | 0 | 213731.7259 | 0 | 684732.9652 | 1781534.7173 | 1215934.0514 | 5437927.2856 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 23190328.3275 | 49058093.015 | 1778.2794 | 0.34921 | 66407.6457 | 140482.3776 | 1353.8097 | 2863.9233
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8984 | 2.5328 | 0.12631 | 4 | 48789.671 | 99986.9022 | 994.6434 | 2038.3682 | 123.5858 | 0 | 86.5012 | 773701.0444 | 32010.1763 | 714605.1896 | 452724.8674 | 0 | 254392.3231 | 0 | 868699.1043 | 2260176.8748 | 1542617.159 | 6898926.7389 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 24651327.7808 | 50519092.4683 | 2371.3737 | 0.50526 | 48789.671 | 99986.9022 | 994.6434 | 2038.3682
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4721 | 3.4236 | 0.17758 | 4 | 37254.2457 | 73672.3016 | 759.4782 | 1501.9095 | 124.8247 | 0 | 84.4843 | 961885.2955 | 40113.1704 | 908679.5204 | 597962.781 | 0 | 303305.194 | 0 | 1096658.9249 | 2853281.5669 | 1947423.2985 | 8709309.7515 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 26461710.7935 | 52329475.481 | 3162.2777 | 0.7103 | 37254.2457 | 73672.3016 | 759.4782 | 1501.9095
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.777 | 4.4978 | 0.24405 | 4 | 29204.6804 | 55703.1255 | 595.3769 | 1135.5836 | 125.7027 | 0 | 89.6237 | 1170336.3969 | 49064.6777 | 1129702.6167 | 773046.5586 | 0 | 350987.6435 | 0 | 1354523.7785 | 3524193.0205 | 2405334.1514 | 10757188.8438 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 28509589.8858 | 54377354.5733 | 4216.965 | 0.9762 | 29204.6804 | 55703.1255 | 595.3769 | 1135.5836
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9922 | 5.8004 | 0.32959 | 4 | 23406.4327 | 43027.6665 | 477.1718 | 877.1772 | 126.3513 | 0 | 85.2428 | 1404267.2724 | 59083.5463 | 1384008.9705 | 985653.8535 | 0 | 398348.6628 | 0 | 1650231.2991 | 4293563.3314 | 2930445.1976 | 13105602.1336 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 30858003.1755 | 56725767.863 | 5623.4133 | 1.3184 | 23406.4327 | 43027.6665 | 477.1718 | 877.1772
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.4112 | 7.4048 | 0.43901 | 4 | 19140.2565 | 33870.8809 | 390.2 | 690.5037 | 126.8495 | 0 | 93.2916 | 1672056.5661 | 70519.1017 | 1682018.4377 | 1247655.4479 | 0 | 448065.3135 | 0 | 1996922.7981 | 5195583.4954 | 3546092.4942 | 15858913.6544 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 33611314.6964 | 59479079.3839 | 7498.9421 | 1.7561 | 19140.2565 | 33870.8809 | 390.2 | 690.5037
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.2038 | 9.3536 | 0.57695 | 4 | 15948.148 | 27156.9776 | 325.1246 | 553.6317 | 127.2333 | 0 | 120.1563 | 1975458.8529 | 83439.6137 | 2027162.7127 | 1566317.586 | 0 | 499127.3847 | 0 | 2399087.3985 | 6241933.2904 | 4260247.7296 | 19052774.5686 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 36805175.6105 | 62672940.298 | 10000 | 2.3078 | 15948.148 | 27156.9776 | 325.1246 | 553.6317
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3561 | 11.6429 | 0.74623 | 4 | 13532.5449 | 22198.7312 | 275.8792 | 452.5512 | 127.5221 | 0 | 107.5632 | 2309122.3077 | 97605.8843 | 2414702.4864 | 1940906.3922 | 0 | 547685.4446 | 0 | 2850908.781 | 7417479.8462 | 5062582.409 | 22640993.5515 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 40393394.5934 | 66261159.2809 | 13335.2143 | 2.9849 | 13532.5449 | 22198.7312 | 275.8792 | 452.5512
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.6481 | 14.2142 | 0.94609 | 4 | 11694.2931 | 18529.7445 | 238.404 | 377.7539 | 127.722 | 0 | 115.051 | 2661600.5899 | 112514.54 | 2832249.8096 | 2361827.1444 | 0 | 588723.7866 | 0 | 3337197.1895 | 8682702.5339 | 5926122.8911 | 26502938.485 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 44255339.527 | 70123104.2145 | 17782.7941 | 3.7844 | 11694.2931 | 18529.7445 | 238.404 | 377.7539
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.6077 | 16.9429 | 1.1703 | 4 | 10294.9506 | 15820.9496 | 209.8765 | 322.5315 | 127.8301 | 0 | 130.568 | 3015309.8638 | 127400.5222 | 3259193.3914 | 2809055.2427 | 0 | 616880.9946 | 0 | 3832857.6057 | 9972309.2629 | 6806305.9824 | 30439312.8656 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 48191713.9075 | 74059478.595 | 23713.7371 | 4.6811 | 10294.9506 | 15820.9496 | 209.8765 | 322.5315
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.5823 | 19.6585 | 1.4071 | 4 | 9232.7044 | 13828.7538 | 188.2212 | 281.9179 | 127.8492 | 0 | 133.8369 | 3350261.2325 | 141405.9949 | 3670752.0668 | 3255119.5306 | 0 | 628268.8523 | 0 | 4307864.9941 | 11208181.05 | 7649813.8717 | 34211667.5929 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 51964068.6348 | 77831833.3223 | 31622.7766 | 5.6283 | 9232.7044 | 13828.7538 | 188.2212 | 281.9179
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.0297 | 22.2221 | 1.6433 | 4 | 8428.9987 | 12364.2645 | 171.8365 | 252.0623 | 127.7959 | 0 | 152.1221 | 3653144.8741 | 153974.3012 | 4049113.6207 | 3677475.9758 | 0 | 623549.4866 | 0 | 4741330.7208 | 12335969.9548 | 8419552.973 | 37654111.907 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 55406512.949 | 81274277.6365 | 42169.6503 | 6.5733 | 8428.9987 | 12364.2645 | 171.8365 | 252.0623
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.4696 | 24.5165 | 1.8662 | 4 | 7822.4817 | 11287.7599 | 159.4719 | 230.1163 | 127.695 | 0 | 170.6916 | 3914534.8913 | 164732.6683 | 4380553.0682 | 4056766.278 | 0 | 605106.381 | 0 | 5117460.3818 | 13314582.1781 | 9087475.9239 | 40641211.7706 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 58393612.8125 | 84261377.5 | 56234.1325 | 7.4648 | 7822.4817 | 11287.7599 | 159.4719 | 230.1163
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.6667 | 26.4894 | 2.0668 | 4 | 7365.5654 | 10494.5055 | 150.157 | 213.9447 | 127.5711 | 0 | 157.0049 | 4132669.8004 | 173638.8013 | 4660779.4826 | 4384075.1242 | 0 | 577516.2202 | 0 | 5432184.9772 | 14133431.0163 | 9646357.0816 | 43140652.5039 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 60893053.5458 | 86760818.2333 | 74989.4209 | 8.2673 | 7365.5654 | 10494.5055 | 150.157 | 213.9447
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5339 | 28.1272 | 2.2401 | 4 | 7021.7095 | 9908.5913 | 143.147 | 202 | 127.4435 | 0 | 162.919 | 4309405.6783 | 180801.0943 | 4890354.5282 | 4656682.5411 | 0 | 545122.8792 | 0 | 5687123.0212 | 14796727.5119 | 10099070.5692 | 45165287.8235 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 62917688.8655 | 88785453.553 | 100000 | 8.9605 | 7021.7095 | 9908.5913 | 143.147 | 202
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.1144 | 29.4472 | 2.3848 | 4 | 6763.0877 | 9474.8465 | 137.8747 | 193.1576 | 127.325 | 0 | 192.0074 | 4449145.0997 | 186427.0452 | 5073543.6384 | 4877069.0887 | 0 | 511524.411 | 0 | 5888106.6204 | 15319645.6095 | 10455972.9157 | 46761434.4286 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 64513835.4706 | 90381600.1581 | 133352.1432 | 9.5391 | 6763.0877 | 9474.8465 | 137.8747 | 193.1576
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5534 | 30.49 | 2.5024 | 4 | 6568.6324 | 9152.8959 | 133.9105 | 186.5942 | 127.2218 | 0 | 167.0498 | 4557884.0201 | 190780.6611 | 5217152.2841 | 5051607.1841 | 0 | 479465.9814 | 0 | 6043787.151 | 15724694.4157 | 10732427.0489 | 47997798.7464 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 65750199.7883 | 91617964.4758 | 177827.941 | 10.0097 | 6568.6324 | 9152.8959 | 133.9105 | 186.5942
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0144 | 31.2984 | 2.596 | 4 | 6422.4491 | 8913.5334 | 130.9303 | 181.7144 | 127.136 | 0 | 197.6623 | 4641213.8958 | 194101.7827 | 5327851.7524 | 5187208.9561 | 0 | 450460.6427 | 0 | 6162326.4416 | 16033109.3341 | 10942926.568 | 48939199.3733 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 66691600.4153 | 92559365.1028 | 237137.3706 | 10.3841 | 6422.4491 | 8913.5334 | 130.9303 | 181.7144
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7017 | 31.9232 | 2.6696 | 4 | 6312.5716 | 8734.9802 | 128.6903 | 178.0744 | 127.0662 | 0 | 183.0867 | 4705049.6262 | 196636.672 | 5413044.3519 | 5292194.9261 | 0 | 425532.6662 | 0 | 6252658.7145 | 16268135.3786 | 11103336.6726 | 49656589.0082 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 67408990.0501 | 93276754.7376 | 316227.766 | 10.6785 | 6312.5716 | 8734.9802 | 128.6903 | 178.0744
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.746 | 32.3969 | 2.7265 | 4 | 6229.9991 | 8601.8665 | 127.007 | 175.3607 | 127.0114 | 0 | 189.6354 | 4753108.684 | 198539.5781 | 5477410.1397 | 5371878.4808 | 0 | 404529.0729 | 0 | 6320131.7226 | 16443686.305 | 11223153.7871 | 50192437.7703 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 67944838.8122 | 93812603.4997 | 421696.5034 | 10.9061 | 6229.9991 | 8601.8665 | 127.007 | 175.3607
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8561 | 33.118 | 2.7909 | 4 | 6167.6736 | 8484.8527 | 125.7364 | 172.9752 | 126.9313 | 0 | 192.2085 | 4825970.8205 | 201428.2786 | 5575040.0915 | 5493660.9453 | 0 | 402469.4069 | 0 | 6434442.1217 | 16741098.5151 | 11426143.7317 | 51100253.9113 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 68852654.9533 | 94720419.6408 | 562341.3252 | 11.1635 | 6167.6736 | 8484.8527 | 125.7364 | 172.9752
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1083 | 33.409 | 2.8258 | 4 | 6120.4455 | 8408.9874 | 124.7736 | 171.4286 | 126.9014 | 0 | 188.1939 | 4855287.8089 | 202592.8187 | 5614312.0448 | 5542788.4643 | 0 | 389405.9443 | 0 | 6475710.9616 | 16848471.571 | 11499428.0487 | 51427997.6623 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69180398.7042 | 95048163.3917 | 749894.2093 | 11.3032 | 6120.4455 | 8408.9874 | 124.7736 | 171.4286
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.0487 | 33.6272 | 2.8523 | 4 | 6084.9787 | 8352.2707 | 124.0505 | 170.2723 | 126.8787 | 0 | 182.8206 | 4877211.745 | 203462.7988 | 5643721.0292 | 5579653.5017 | 0 | 379033.14 | 0 | 6506402.0637 | 16928323.5232 | 11553928.6469 | 51671736.4485 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69424137.4904 | 95291902.1779 | 1000000 | 11.4091 | 6084.9787 | 8352.2707 | 124.0505 | 170.2723
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7527 | 33.7904 | 2.8723 | 4 | 6058.3515 | 8309.8529 | 123.5077 | 169.4076 | 126.8616 | 0 | 199.7827 | 4893574.9961 | 204111.6199 | 5665693.5561 | 5607239.0292 | 0 | 370894.2386 | 0 | 6529190.2416 | 16987613.6875 | 11594395.4023 | 51852712.7713 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69605113.8133 | 95472878.5008 | 1333521.4322 | 11.4891 | 6058.3515 | 8309.8529 | 123.5077 | 169.4076
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.2667 | 33.9095 | 2.8872 | 4 | 6038.3654 | 8278.2435 | 123.1002 | 168.7632 | 126.849 | 0 | 177.0949 | 4905493.9864 | 204583.9446 | 5681710.7315 | 5627370.7951 | 0 | 364450.1345 | 0 | 6545607.7409 | 17030328.6531 | 11623549.244 | 51983095.2302 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69735496.2721 | 95603260.9596 | 1778279.41 | 11.5487 | 6038.3654 | 8278.2435 | 123.1002 | 168.7632
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6734 | 34.0037 | 2.8987 | 4 | 6023.367 | 8254.3491 | 122.7945 | 168.2761 | 126.839 | 0 | 186.4469 | 4914910.0204 | 204956.9291 | 5694371.427 | 5643297.26 | 0 | 359706.2851 | 0 | 6558724.3494 | 17064455.3778 | 11646841.4348 | 52087263.0836 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69839664.1256 | 95707428.8131 | 2371373.7057 | 11.5948 | 6023.367 | 8254.3491 | 122.7945 | 168.2761
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.9707 | 34.0725 | 2.9073 | 4 | 6012.1134 | 8236.5275 | 122.5651 | 167.9128 | 126.8317 | 0 | 176.4371 | 4921782.8643 | 205229.0794 | 5703616.7518 | 5654935.0381 | 0 | 356004.7887 | 0 | 6568211.7237 | 17089139.5795 | 11663688.9097 | 52162608.7352 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69915009.7771 | 95782774.4646 | 3162277.6602 | 11.629 | 6012.1134 | 8236.5275 | 122.5651 | 167.9128
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.1876 | 34.1227 | 2.9136 | 4 | 6003.6706 | 8223.234 | 122.3929 | 167.6417 | 126.8263 | 0 | 181.1956 | 4926792.1084 | 205427.3844 | 5710357.4066 | 5663424.0914 | 0 | 353130.6411 | 0 | 6575061.3364 | 17106960.8669 | 11675852.3045 | 52217006.1397 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69969407.1816 | 95837171.8692 | 4216965.0343 | 11.6544 | 6003.6706 | 8223.234 | 122.3929 | 167.6417
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3534 | 34.1611 | 2.9184 | 4 | 5997.3373 | 8213.2383 | 122.2638 | 167.438 | 126.8222 | 0 | 164.6154 | 4930618.1671 | 205578.8233 | 5715507.1206 | 5669911.8121 | 0 | 350983.3702 | 0 | 6580313.7244 | 17120626.5029 | 11685179.3819 | 52258718.9024 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 70011119.9443 | 95878884.6319 | 5623413.2519 | 11.6737 | 5997.3373 | 8213.2383 | 122.2638 | 167.438
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4823 | 34.1909 | 2.9221 | 4 | 5992.5867 | 8205.6985 | 122.167 | 167.2843 | 126.819 | 0 | 200.6215 | 4933591.7594 | 205696.5062 | 5719510.1441 | 5674956.2413 | 0 | 349405.193 | 0 | 6584432.3391 | 17131342.2936 | 11692493.1292 | 52291427.6058 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 70043828.6477 | 95911593.3352 | 7498942.0933 | 11.6884 | 5992.5867 | 8205.6985 | 122.167 | 167.2843
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.5702 | 34.2112 | 2.9247 | 4 | 5989.0236 | 8200.1344 | 122.0943 | 167.1708 | 126.8168 | 0 | 178.5916 | 4935620.3027 | 205776.7762 | 5722241.4095 | 5678398.8198 | 0 | 348129.6159 | 0 | 6587165.1004 | 17138452.3778 | 11697345.9078 | 52313130.3101 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 70065531.352 | 95933296.0395 | 10000000 | 11.699 | 5989.0236 | 8200.1344 | 122.0943 | 167.1708
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9861 | [19 empty] | 100 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4532 | [19 empty] | 133.3521 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8228 | [19 empty] | 177.8279 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.417 | [19 empty] | 237.1374 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5309 | [19 empty] | 316.2278 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.35607 | 0.0066081 | 4 | 751244.0575 | 1755382.6901 | 15315.1262 | 35785.8505 | 105.7979 | 0 | 306.0442 | 177860.2645 | 6481.3071 | 150638.835 | 93685.7783 | 0 | 95455.4397 | 0 | 204407.4335 | 531826.2123 | 362982.3178 | 1623337.5881 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19857287.4108 | 46399220.3915 | 421.6965 | 0.026433 | 751244.0575 | 1755382.6901 | 15315.1262 | 35785.8505
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7016 | 0.52172 | 0.014971 | 4 | 339981.5868 | 783191.1732 | 6930.9845 | 15966.4114 | 111.4016 | 0 | 414.6076 | 240050.0985 | 9108.0094 | 203648.1083 | 121171.0243 | 0 | 112469.0565 | 0 | 267714.0558 | 696537.0575 | 475400.8541 | 2126098.2643 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20360048.0871 | 46901981.0678 | 562.3413 | 0.059886 | 339981.5868 | 783191.1732 | 6930.9845 | 15966.4114
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5573 | 0.73479 | 0.027029 | 4 | 193800.3096 | 439291.9874 | 3950.8814 | 8955.5613 | 115.6973 | 0 | 578.5809 | 312308.9688 | 12219.9451 | 267008.9577 | 156061.8708 | 0 | 130353.7138 | 0 | 342401.8479 | 890859.372 | 608029.8267 | 2719244.5029 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20953194.3257 | 47495127.3063 | 749.8942 | 0.10812 | 193800.3096 | 439291.9874 | 3950.8814 | 8955.5613
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7279 | 1.0306 | 0.044056 | 4 | 123263.3519 | 273878.1116 | 2512.8902 | 5583.3758 | 119.2359 | 0 | 82.9727 | 403197.67 | 16179.6802 | 349130.534 | 204234.8731 | 0 | 153419.1759 | 0 | 439203.1539 | 1142716.5134 | 779927.5009 | 3488009.1013 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 21721958.924 | 48263891.9047 | 1000 | 0.17622 | 123263.3519 | 273878.1116 | 2512.8902 | 5583.3758
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2775 | 1.4254 | 0.067393 | 4 | 84129.6664 | 182589.5249 | 1715.097 | 3722.3344 | 121.9832 | 0 | 61.1004 | 513164.6213 | 20997.2092 | 451676.4406 | 268294.5793 | 0 | 181002.2689 | 0 | 559702.6965 | 1456231.6055 | 993907.9933 | 4444977.4146 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 22678927.2373 | 49220860.218 | 1333.5214 | 0.26957 | 84129.6664 | 182589.5249 | 1715.097 | 3722.3344
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3238 | 1.9457 | 0.098364 | 4 | 60642.1228 | 128100.498 | 1236.2717 | 2611.5019 | 123.9861 | 0 | 69.0961 | 644616.7175 | 26745.8729 | 578542.4732 | 352510.4325 | 0 | 214059.8014 | 0 | 708425.366 | 1843177.4843 | 1258006.5065 | 5626084.6542 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 23860034.4769 | 50401967.4576 | 1778.2794 | 0.39346 | 60642.1228 | 128100.498 | 1236.2717 | 2611.5019
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0912 | 2.6611 | 0.14183 | 4 | 44745.4556 | 91531.4173 | 912.1966 | 1865.9917 | 125.8185 | 0 | 77.3869 | 810142.6109 | 34026.1284 | 742305.7119 | 466830.7197 | 0 | 255318.472 | 0 | 900363.2207 | 2342560.4105 | 1598845.6149 | 7150392.8891 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 25384342.7118 | 51926275.6925 | 2371.3737 | 0.56731 | 44745.4556 | 91531.4173 | 912.1966 | 1865.9917
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7279 | 3.5983 | 0.19897 | 4 | 34260.5265 | 67609.2939 | 698.4472 | 1378.3069 | 127.0861 | 0 | 88.2361 | 1007633.7063 | 42673.7315 | 944111.6127 | 617815.9329 | 0 | 304427.2725 | 0 | 1137498.2798 | 2959537.1909 | 2019944.9452 | 9033642.6717 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 27267592.4945 | 53809525.4752 | 3162.2777 | 0.79589 | 34260.5265 | 67609.2939 | 698.4472 | 1378.3069
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5838 | 4.8521 | 0.27542 | 4 | 26915.5586 | 51007.6231 | 548.7101 | 1039.8594 | 128.0584 | 0 | 69.6427 | 1249480.6572 | 53239.9835 | 1198380.5204 | 820615.6574 | 0 | 364966.1399 | 0 | 1437806.3538 | 3740877.1979 | 2553225.5549 | 11418592.065 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 29652541.8878 | 56194474.8684 | 4216.965 | 1.1017 | 26915.5586 | 51007.6231 | 548.7101 | 1039.8594
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.466 | 6.3705 | 0.37346 | 4 | 21666.4637 | 39434.214 | 441.7002 | 803.9198 | 128.7478 | 0 | 82.9769 | 1518549.0452 | 64944.335 | 1489326.4378 | 1064836.5009 | 0 | 425090.5044 | 0 | 1779471.2611 | 4629819.2016 | 3159946.7384 | 14131984.0244 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 32365933.8472 | 58907866.8278 | 5623.4133 | 1.4938 | 21666.4637 | 39434.214 | 441.7002 | 803.9198
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2406 | 8.1202 | 0.49618 | 4 | 17794.0936 | 31167.1665 | 362.7567 | 635.3848 | 129.2353 | 0 | 95.7686 | 1806132.1021 | 77415.7701 | 1807838.1654 | 1346353.0261 | 0 | 477635.4744 | 0 | 2150996.0698 | 5596450.5437 | 3819692.4916 | 17082513.6432 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 35316463.4659 | 61858396.4466 | 7498.9421 | 1.9847 | 17794.0936 | 31167.1665 | 362.7567 | 635.3848
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.3964 | 10.2274 | 0.64999 | 4 | 14887.8936 | 25096.4448 | 303.5098 | 511.625 | 129.6089 | 0 | 111.7609 | 2129369.219 | 91391.8987 | 2173719.9449 | 1685496.2185 | 0 | 530439.0526 | 0 | 2578062.3702 | 6707589.4539 | 4578067.6294 | 20474135.7873 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 38708085.61 | 65250018.5907 | 10000 | 2.6 | 14887.8936 | 25096.4448 | 303.5098 | 511.625
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.9165 | 12.6866 | 0.83756 | 4 | 12683.9497 | 20606.3346 | 258.5795 | 420.088 | 129.8871 | 0 | 111.6389 | 2482846.9426 | 106624.4954 | 2582169.4255 | 2081343.4775 | 0 | 579888.5689 | 0 | 3054820.4348 | 7948016.1416 | 5424684.3321 | 24260393.8184 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 42494343.6412 | 69036276.6218 | 13335.2143 | 3.3502 | 12683.9497 | 20606.3346 | 258.5795 | 420.088
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.5102 | 15.4187 | 1.0569 | 4 | 11004.8485 | 17282.8403 | 224.3487 | 352.3341 | 130.0719 | 0 | 113.7382 | 2852569.5289 | 122491.7384 | 3017808.7679 | 2521515.2452 | 0 | 620180.6691 | 0 | 3562480.7203 | 9268844.069 | 6326176.5328 | 28292067.2717 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 46526017.0945 | 73067950.0751 | 17782.7941 | 4.2278 | 11004.8485 | 17282.8403 | 224.3487 | 352.3341
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.648 | 18.2791 | 1.3001 | 4 | 9726.5278 | 14830.3704 | 198.2884 | 302.3372 | 130.1597 | 0 | 140.4582 | 3219055.5899 | 138133.5884 | 3457745.7281 | 2983284.9736 | 0 | 645779.2886 | 0 | 4073159.6758 | 10597525.9565 | 7233029.2227 | 32347714.0236 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 50581663.8464 | 77123596.8271 | 23713.7371 | 5.2004 | 9726.5278 | 14830.3704 | 198.2884 | 302.3372
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.7144 | 21.1016 | 1.5543 | 4 | 8756.399 | 13025.6486 | 178.511 | 265.5455 | 130.1568 | 0 | 165.0014 | 3563559.8309 | 152733.9516 | 3878656.298 | 3440269.2499 | 0 | 654039.4417 | 0 | 4558810.9211 | 11861090.876 | 8095438.2439 | 36204598.813 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 54438548.6357 | 80980481.6164 | 31622.7766 | 6.217 | 8756.399 | 13025.6486 | 178.511 | 265.5455
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.1165 | 23.7308 | 1.8047 | 4 | 8022.4992 | 11699.2952 | 163.5495 | 238.506 | 130.083 | 0 | 162.7791 | 3871344.5967 | 165672.4955 | 4260894.5321 | 3867615.6207 | 0 | 645370.9988 | 0 | 4996250.3151 | 12999218.4481 | 8872233.698 | 39678600.7051 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 57912550.5278 | 84454483.5085 | 42169.6503 | 7.2188 | 8022.4992 | 11699.2952 | 163.5495 | 238.506
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.4586 | 26.0686 | 2.0389 | 4 | 7468.6366 | 10723.1064 | 152.2583 | 218.605 | 129.965 | 0 | 155.049 | 4135581.2612 | 176686.1311 | 4593892.4433 | 4249303.4682 | 0 | 623438.9892 | 0 | 5373771.8943 | 13981452.1567 | 9542628.3871 | 42676754.731 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 60910704.5538 | 87452637.5345 | 56234.1325 | 8.1555 | 7468.6366 | 10723.1064 | 152.2583 | 218.605
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4977 | 28.0607 | 2.2477 | 4 | 7051.2962 | 10003.3647 | 143.7502 | 203.9321 | 129.8283 | 0 | 173.7956 | 4354339.9056 | 185729.2743 | 4873105.1324 | 4576128.0773 | 0 | 592642.0612 | 0 | 5686958.3358 | 14796299.0342 | 10098778.1244 | 45163979.945 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 63397929.7678 | 89939862.7485 | 74989.4209 | 8.991 | 7051.2962 | 10003.3647 | 143.7502 | 203.9321
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2038 | 29.7072 | 2.4271 | 4 | 6737.1469 | 9471.1115 | 137.3459 | 193.0814 | 129.6915 | 0 | 193.9308 | 4530995.222 | 192976.7218 | 5101019.3861 | 4847419.2172 | 0 | 557779.9691 | 0 | 5939774.3013 | 15454074.3168 | 10547723.2707 | 47171762.4051 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 65405712.2279 | 91947645.2086 | 100000 | 9.7082 | 6737.1469 | 9471.1115 | 137.3459 | 193.0814
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.6165 | 31.0254 | 2.5758 | 4 | 6500.8036 | 9076.9273 | 132.5277 | 185.0454 | 129.567 | 0 | 191.2965 | 4669850.8877 | 198635.75 | 5281760.5056 | 5065446.6746 | 0 | 522171.8177 | 0 | 6137767.5979 | 15969212.2604 | 10899315.5022 | 48744160.9962 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 66978110.8189 | 93520043.7996 | 133352.1432 | 10.3031 | 6500.8036 | 9076.9273 | 132.5277 | 185.0454
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.9233 | 32.0671 | 2.6964 | 4 | 6323.0511 | 8783.9172 | 128.9039 | 179.072 | 129.4593 | 0 | 195.1945 | 4778019.3242 | 203019.603 | 5423565.8547 | 5238300.6444 | 0 | 488802.1606 | 0 | 6291365.9589 | 16368843.6885 | 11172072.1635 | 49963989.3978 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 68197939.2205 | 94739872.2012 | 177827.941 | 10.7856 | 6323.0511 | 8783.9172 | 128.9039 | 179.072
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2607 | 32.8699 | 2.7919 | 4 | 6189.3923 | 8566.0793 | 126.1791 | 174.6311 | 129.3709 | 0 | 185.9207 | 4860457.7907 | 206345.4651 | 5532251.7981 | 5371857.1849 | 0 | 458746.5409 | 0 | 6407566.924 | 16671174.7637 | 11378419.3346 | 50886819.8019 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 69120769.6247 | 95662702.6054 | 237137.3706 | 11.1676 | 6189.3923 | 8566.0793 | 126.1791 | 174.6311
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8406 | 33.4877 | 2.8667 | 4 | 6088.9087 | 8403.5692 | 124.1306 | 171.3181 | 129.2996 | 0 | 191.0799 | 4923367.7362 | 208874.2719 | 5615556.4585 | 5474857.9575 | 0 | 433013.294 | 0 | 6495711.1901 | 16900508.063 | 11534944.0237 | 51586832.9951 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 69820782.8178 | 96362715.7985 | 316227.766 | 11.4669 | 6088.9087 | 8403.5692 | 124.1306 | 171.3181
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4091 | 34.3423 | 2.947 | 4 | 6012.8881 | 8264.523 | 122.5809 | 168.4835 | 129.2056 | 0 | 202.9838 | 5009878.8448 | 212352.4851 | 5730293.7775 | 5617341.5108 | 0 | 427472.4466 | 0 | 6628962.2352 | 17247199.9489 | 11771568.3597 | 52645069.6084 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 70879019.4312 | 97420952.4119 | 421696.5034 | 11.7878 | 6012.8881 | 8264.523 | 122.5809 | 168.4835
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.9903 | 34.7214 | 2.9932 | 4 | 5955.3526 | 8172.1799 | 121.4079 | 166.6009 | 129.1664 | 0 | 204.0346 | 5048082.8911 | 213889.8984 | 5780999.9632 | 5680511.7208 | 0 | 410763.7194 | 0 | 6682356.7952 | 17386121.6412 | 11866385.2692 | 53069111.8985 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71303061.7212 | 97844994.7019 | 562341.3252 | 11.9729 | 5955.3526 | 8172.1799 | 121.4079 | 166.6009
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1741 | 35.0048 | 3.0284 | 4 | 5912.1276 | 8103.2352 | 120.5267 | 165.1954 | 129.1365 | 0 | 184.4943 | 5076534.5108 | 215033.3025 | 5818828.5217 | 5727761.5588 | 0 | 397264.7235 | 0 | 6721814.8208 | 17488783.3299 | 11936453.9812 | 53382474.7492 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71616424.572 | 98158357.5527 | 749894.2093 | 12.1135 | 5912.1276 | 8103.2352 | 120.5267 | 165.1954
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0755 | 35.2203 | 3.0552 | 4 | 5879.6642 | 8051.547 | 119.8649 | 164.1417 | 129.1136 | 0 | 193.9391 | 5098116.5446 | 215899.7485 | 5847561.2316 | 5763720.1509 | 0 | 386709.7942 | 0 | 6751682.9132 | 17566493.9796 | 11989493.0964 | 53619677.4589 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71853627.2817 | 98395560.2624 | 1000000 | 12.2207 | 5879.6642 | 8051.547 | 119.8649 | 164.1417
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7601 | 35.3838 | 3.0756 | 4 | 5855.2904 | 8012.7851 | 119.368 | 163.3515 | 129.0961 | 0 | 197.0125 | 5114457.3721 | 216555.2661 | 5869337.9597 | 5791013.6545 | 0 | 378542.8381 | 0 | 6774263.7653 | 17625244.7247 | 12029591.6872 | 53799007.2676 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72032957.0903 | 98574890.071 | 1333521.4322 | 12.3022 | 5855.2904 | 8012.7851 | 119.368 | 163.3515
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2546 | 35.5018 | 3.0907 | 4 | 5836.9947 | 7983.9486 | 118.995 | 162.7636 | 129.0834 | 0 | 177.1621 | 5126235.6922 | 217027.4716 | 5885046.3594 | 5810723.2719 | 0 | 372032.5389 | 0 | 6790315.4802 | 17667007.9944 | 12058095.9769 | 53926484.7854 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72160434.6082 | 98702367.5889 | 1778279.41 | 12.3626 | 5836.9947 | 7983.9486 | 118.995 | 162.7636
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6419 | 35.5942 | 3.1023 | 4 | 5823.2643 | 7962.1874 | 118.7151 | 162.32 | 129.0733 | 0 | 187.3247 | 5135444.6651 | 217396.5144 | 5897334.7692 | 5826154.2215 | 0 | 367199.8654 | 0 | 6802976.7139 | 17699949.9271 | 12080579.5228 | 54027036.1993 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72260986.022 | 98802919.0027 | 2371373.7057 | 12.409 | 5823.2643 | 7962.1874 | 118.7151 | 162.32
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9346 | 35.664 | 3.111 | 4 | 5812.962 | 7945.8615 | 118.5051 | 161.9871 | 129.0658 | 0 | 172.4369 | 5142394.5015 | 217674.931 | 5906612.5476 | 5837811.9238 | 0 | 363531.9614 | 0 | 6812530.0875 | 17724805.8456 | 12097544.198 | 54102905.9964 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72336855.8192 | 98878788.7999 | 3162277.6602 | 12.4441 | 5812.962 | 7945.8615 | 118.5051 | 161.9871
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1413 | 35.7132 | 3.1174 | 4 | 5805.2326 | 7933.75 | 118.3475 | 161.7402 | 129.0604 | 0 | 199.2493 | 5147298.2703 | 217871.3249 | 5913161.1264 | 5846044.2654 | 0 | 360615.558 | 0 | 6819146.3126 | 17742019.9061 | 12109293.148 | 54155449.9117 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72389399.7345 | 98931332.7152 | 4216965.0343 | 12.4697 | 5805.2326 | 7933.75 | 118.3475 | 161.7402
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.305 | 35.7522 | 3.1224 | 4 | 5799.4344 | 7924.5871 | 118.2293 | 161.5534 | 129.0561 | 0 | 184.0207 | 5151180.4847 | 218026.7813 | 5918346.6169 | 5852565.1891 | 0 | 358494.4339 | 0 | 6824459.2673 | 17755843.1245 | 12118727.7785 | 54197643.6762 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72431593.499 | 98973526.4797 | 5623413.2519 | 12.4894 | 5799.4344 | 7924.5871 | 118.2293 | 161.5534
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.4145 | 35.7783 | 3.1259 | 4 | 5795.0852 | 7917.8468 | 118.1406 | 161.416 | 129.0533 | 0 | 164.9057 | 5153773.9866 | 218130.6131 | 5921811.5177 | 5856923.6387 | 0 | 356757.7862 | 0 | 6827885.0415 | 17764756.2861 | 12124811.1945 | 54224850.0642 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72458799.887 | 99000732.8676 | 7498942.0933 | 12.5035 | 5795.0852 | 7917.8468 | 118.1406 | 161.416
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.5117 | 35.8015 | 3.1287 | 4 | 5791.823 | 7912.6475 | 118.0741 | 161.31 | 129.0507 | 0 | 180.1965 | 5156077.5088 | 218222.8336 | 5924889.2197 | 5860795.6161 | 0 | 355600.4716 | 0 | 6831078.4034 | 17773064.7589 | 12130481.8979 | 54250210.71 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72484160.5328 | 99026093.5134 | 10000000 | 12.5149 | 5791.823 | 7912.6475 | 118.0741 | 161.31
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9802 | [19 empty] | 100 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2535 | [19 empty] | 133.3521 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9821 | [19 empty] | 177.8279 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6483 | [19 empty] | 237.1374 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1755 | [19 empty] | 316.2278 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.37896 | 0.0083695 | 4 | 609840.1869 | 1423044.7747 | 12432.4171 | 29010.6925 | 107.822 | 0 | 310.1676 | 188128.5816 | 6953.4667 | 158100.5426 | 96866.3698 | 0 | 97130.2412 | 0 | 213399.8888 | 555222.7364 | 378950.9263 | 1694752.7535 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20416111.448 | 47640416.849 | 421.6965 | 0.033478 | 609840.1869 | 1423044.7747 | 12432.4171 | 29010.6925
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7405 | 0.54499 | 0.017665 | 4 | 295926.1044 | 681209.2504 | 6032.8539 | 13887.372 | 113.2549 | 0 | 427.2774 | 250166.6812 | 9613.7918 | 210603.4386 | 123930.8927 | 0 | 112418.4644 | 0 | 275625.9748 | 717122.2478 | 489450.6695 | 2188932.1608 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20910290.8552 | 48134596.2563 | 562.3413 | 0.070661 | 295926.1044 | 681209.2504 | 6032.8539 | 13887.372
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 0.77497 | 0.031158 | 4 | 172871.1678 | 391309.7326 | 3524.2126 | 7977.3782 | 117.7616 | 0 | 592.2598 | 327886.5346 | 13013.6853 | 278218.7876 | 161066.4349 | 0 | 131531.3025 | 0 | 355569.5305 | 925118.9809 | 631412.7138 | 2823817.9699 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 21545176.6643 | 48769482.0654 | 749.8942 | 0.12463 | 172871.1678 | 391309.7326 | 3524.2126 | 7977.3782
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8205 | 1.0842 | 0.050044 | 4 | 111591.8667 | 247592.8304 | 2274.9511 | 5047.5147 | 121.3413 | 0 | 81.1162 | 422487.442 | 17201.4665 | 363045.2083 | 210651.5572 | 0 | 154358.432 | 0 | 455420.2013 | 1184909.9443 | 808725.3845 | 3616799.6361 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 22338158.3305 | 49562463.7316 | 1000 | 0.20018 | 111591.8667 | 247592.8304 | 2274.9511 | 5047.5147
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 1.4959 | 0.075824 | 4 | 76897.784 | 166658.9413 | 1567.6653 | 3397.5679 | 124.1238 | 0 | 77.927 | 536736.3935 | 22286.2563 | 468765.804 | 276299.7818 | 0 | 181589.8901 | 0 | 579414.469 | 1507517.5942 | 1028911.7344 | 4601521.9233 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 23322880.6178 | 50547186.0188 | 1333.5214 | 0.3033 | 76897.784 | 166658.9413 | 1567.6653 | 3397.5679
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4869 | 2.0465 | 0.11011 | 4 | 55758.6767 | 117572.283 | 1136.716 | 2396.87 | 126.1709 | 0 | 79.4145 | 675223.7729 | 28432.3278 | 601506.9927 | 363744.9927 | 0 | 215406.3591 | 0 | 734882.6336 | 1912013.8676 | 1304988.7526 | 5836199.6991 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 24557558.3935 | 51781863.7946 | 1778.2794 | 0.44043 | 55758.6767 | 117572.283 | 1136.716 | 2396.87
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.281 | 2.7946 | 0.15848 | 4 | 41229.6705 | 84176.2547 | 840.5226 | 1716.0468 | 128.0471 | 0 | 80.1749 | 848067.1272 | 36178.2599 | 770733.8321 | 482878.2893 | 0 | 256062.2444 | 0 | 933628.7036 | 2429110.3733 | 1657917.743 | 7414576.5729 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 26135935.2673 | 53360240.6684 | 2371.3737 | 0.63391 | 41229.6705 | 84176.2547 | 840.5226 | 1716.0468
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9863 | 3.7803 | 0.22175 | 4 | 31672.5717 | 62365.6384 | 645.6882 | 1271.4079 | 129.3454 | 0 | 81.6761 | 1055128.4725 | 45391.1578 | 980598.5179 | 639213.5844 | 0 | 305495.2158 | 0 | 1180072.5099 | 3070306.6046 | 2095547.3461 | 9371753.4091 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 28093112.1035 | 55317417.5046 | 3162.2777 | 0.88699 | 31672.5717 | 62365.6384 | 645.6882 | 1271.4079
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9025 | 5.0902 | 0.30607 | 4 | 24954.7177 | 47191.602 | 508.7357 | 962.0646 | 130.3359 | 0 | 93.7181 | 1306954.7723 | 56565.9395 | 1243255.6287 | 847253.1184 | 0 | 365597.0394 | 0 | 1489654.3343 | 3875775.0077 | 2645296.082 | 11830351.9223 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 30551710.6167 | 57776016.0178 | 4216.965 | 1.2243 | 24954.7177 | 47191.602 | 508.7357 | 962.0646
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4212 | 6.8288 | 0.41789 | 4 | 20126.3184 | 36412.9374 | 410.3022 | 742.327 | 131.0902 | 0 | 78.1219 | 1613266.5958 | 70108.614 | 1571902.6891 | 1123351.4648 | 0 | 438958.7374 | 0 | 1878859.3594 | 4888406.6461 | 3336437.9827 | 14921292.0893 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 33642650.7838 | 60866956.1848 | 5623.4133 | 1.6716 | 20126.3184 | 36412.9374 | 410.3022 | 742.327
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0971 | 8.8758 | 0.55849 | 4 | 16593.1131 | 28779.7159 | 338.2731 | 586.7134 | 131.6149 | 0 | 89.0724 | 1945677.4946 | 84746.0085 | 1938057.7076 | 1447479.5161 | 0 | 507637.6361 | 0 | 2310203.3615 | 6010675.2587 | 4102409.3711 | 18346886.354 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 37068245.0485 | 64292550.4496 | 7498.9421 | 2.234 | 16593.1131 | 28779.7159 | 338.2731 | 586.7134
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.6233 | 11.1503 | 0.72938 | 4 | 13938.1345 | 23269.4237 | 284.1477 | 474.3787 | 131.979 | 0 | 95.8599 | 2289606.5534 | 99839.6033 | 2325550.307 | 1807583.4702 | 0 | 562261.4599 | 0 | 2763088.1436 | 7188988.5622 | 4906632.4127 | 21943550.5122 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 40664909.2067 | 67889214.6077 | 10000 | 2.9175 | 13938.1345 | 23269.4237 | 284.1477 | 474.3787
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.5176 | 13.789 | 0.93666 | 4 | 11919.844 | 19186.1307 | 243.0021 | 391.1352 | 132.2462 | 0 | 106.8212 | 2663874.7041 | 116213.7358 | 2755763.8982 | 2226068.2117 | 0 | 612674.0541 | 0 | 3266091.8955 | 8497701.1446 | 5799855.6415 | 25938243.2854 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 44659601.9799 | 71883907.3809 | 13335.2143 | 3.7467 | 11919.844 | 19186.1307 | 243.0021 | 391.1352
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.3996 | 16.6844 | 1.1766 | 4 | 10381.6273 | 16166.067 | 211.6435 | 329.5671 | 132.4141 | 0 | 123.1878 | 3050877.5623 | 133067.8879 | 3209335.5175 | 2685784.4946 | 0 | 651969.4458 | 0 | 3795103.6142 | 9874081.1212 | 6739263.2573 | 30139482.9008 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 48860841.5952 | 76085146.9963 | 17782.7941 | 4.7065 | 10381.6273 | 16166.067 | 211.6435 | 329.5671
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.6977 | 19.6754 | 1.4393 | 4 | 9211.0055 | 13939.6237 | 187.7788 | 284.1781 | 132.4802 | 0 | 150.0453 | 3429767.8505 | 149466.8852 | 3661727.4373 | 3161715.6748 | 0 | 674753.8117 | 0 | 4320198.3472 | 11240269.9048 | 7671715.1745 | 34309615.0859 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 53030973.7804 | 80255279.1815 | 23713.7371 | 5.7573 | 9211.0055 | 13939.6237 | 187.7788 | 284.1781
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.789 | 22.589 | 1.7105 | 4 | 8322.9744 | 12301.8828 | 169.6751 | 250.7905 | 132.4545 | 0 | 163.2378 | 3781802.5445 | 164585.7491 | 4089508.5409 | 3626884.1503 | 0 | 679029.502 | 0 | 4813306.0899 | 12523235.101 | 8547365.2832 | 38225716.9609 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 56947075.6554 | 84171381.0564 | 31622.7766 | 6.8422 | 8322.9744 | 12301.8828 | 169.6751 | 250.7905
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1346 | 25.2804 | 1.9751 | 4 | 7651.319 | 11097.3254 | 155.9825 | 226.234 | 132.3603 | 0 | 162.1968 | 4094068.1744 | 177879.3609 | 4475171.2934 | 4058416.9495 | 0 | 666386.5738 | 0 | 5254049.7173 | 13669959.6105 | 9330028.3238 | 41725960.0035 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 60447318.698 | 87671624.099 | 42169.6503 | 7.9002 | 7651.319 | 11097.3254 | 155.9825 | 226.234
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.3498 | 27.6529 | 2.22 | 4 | 7144.4223 | 10210.2092 | 145.6487 | 208.1489 | 132.2259 | 0 | 152.6408 | 4360110.4365 | 189102.7159 | 4808553.3334 | 4440555.3683 | 0 | 640723.8739 | 0 | 5631227.8339 | 14651299.7002 | 9999813.0995 | 44721386.3615 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 63442745.056 | 90667050.4571 | 56234.1325 | 8.88 | 7144.4223 | 10210.2092 | 145.6487 | 208.1489
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2427 | 29.6641 | 2.4368 | 4 | 6762.4155 | 9555.4027 | 137.861 | 194.7998 | 132.0768 | 0 | 180.1796 | 4579436.1034 | 198274.6617 | 5086880.0576 | 4765989.606 | 0 | 606941.6828 | 0 | 5942633.6235 | 15461513.6866 | 10552800.7934 | 47194470.2151 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 65915828.9095 | 93140134.3106 | 74989.4209 | 9.7474 | 6762.4155 | 9555.4027 | 137.861 | 194.7998
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8003 | 31.3195 | 2.622 | 4 | 6474.736 | 9070.5361 | 131.9963 | 184.9151 | 131.931 | 0 | 167.7342 | 4756005.3005 | 205603.6384 | 5313262.3803 | 5035383.7923 | 0 | 569800.4906 | 0 | 6193221.6848 | 16113492.4194 | 10997789.6754 | 49184559.3815 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 67905918.076 | 95130223.477 | 100000 | 10.4878 | 6474.736 | 9070.5361 | 131.9963 | 184.9151
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0649 | 32.6378 | 2.7747 | 4 | 6258.2044 | 8711.1416 | 127.582 | 177.5884 | 131.8004 | 0 | 189.0465 | 4894216.0205 | 211305.276 | 5491919.9513 | 5251209.5233 | 0 | 532408.9127 | 0 | 6388613.2767 | 16621861.2611 | 11344761.8558 | 50736296.0774 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 69457654.7718 | 96681960.1729 | 133352.1432 | 11.0987 | 6258.2044 | 8711.1416 | 127.582 | 177.5884
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2324 | 33.6743 | 2.8979 | 4 | 6095.3083 | 8443.9042 | 124.2611 | 172.1404 | 131.6889 | 0 | 186.4497 | 5001400.272 | 215702.3396 | 5631426.4093 | 5421522.9956 | 0 | 497657.3791 | 0 | 6539406.6643 | 17014194.7237 | 11612537.5056 | 51933848.2891 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 70655206.9835 | 97879512.3846 | 177827.941 | 11.5917 | 6095.3083 | 8443.9042 | 124.2611 | 172.1404
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4682 | 34.4746 | 2.9954 | 4 | 5972.7904 | 8244.9547 | 121.7634 | 168.0846 | 131.5976 | 0 | 171.9157 | 5083289.6142 | 219046.4677 | 5738589.8154 | 5553422.861 | 0 | 466765.5746 | 0 | 6653834.5898 | 17311912.7135 | 11815736.1512 | 52842597.7873 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 71563956.4818 | 98788261.8828 | 237137.3706 | 11.9817 | 5972.7904 | 8244.9547 | 121.7634 | 168.0846
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5749 | 35.4891 | 3.0953 | 4 | 5880.1412 | 8079.0103 | 119.8746 | 164.7016 | 131.4852 | 0 | 186.1487 | 5186279.1705 | 223248.4313 | 5873732.6609 | 5720738.7297 | 0 | 456940.2059 | 0 | 6809766.2873 | 17717615.0045 | 12092636.3012 | 54080956.7914 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 72802315.4858 | 100026620.8869 | 316227.766 | 12.381 | 5880.1412 | 8079.0103 | 119.8746 | 164.7016
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.5823 | 35.9854 | 3.1565 | 4 | 5809.8976 | 7966.0909 | 118.4426 | 162.3995 | 131.4336 | 0 | 185.7771 | 5236388.866 | 225294.4617 | 5939560.5405 | 5802556.7963 | 0 | 436012.2416 | 0 | 6879527.0334 | 17899118.1557 | 12216515.9314 | 54634974.0265 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 73356332.721 | 100580638.122 | 421696.5034 | 12.6261 | 5809.8976 | 7966.0909 | 118.4426 | 162.3995
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.1 | 36.3599 | 3.2034 | 4 | 5757.1006 | 7881.7293 | 117.3663 | 160.6797 | 131.3938 | 0 | 199.6994 | 5274023.8995 | 226828.4561 | 5989110.0887 | 5864356.0542 | 0 | 418933.8849 | 0 | 6931568.4296 | 18034519.1935 | 12308929.9219 | 55048269.9284 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 73769628.6229 | 100993934.0239 | 562341.3252 | 12.8137 | 5757.1006 | 7881.7293 | 117.3663 | 160.6797
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2593 | 36.6454 | 3.2393 | 4 | 5717.4322 | 7818.4989 | 116.5576 | 159.3907 | 131.3631 | 0 | 199.0269 | 5302626.3177 | 227992.7311 | 6026830.4984 | 5911524.7889 | 0 | 405423.8152 | 0 | 6971015.279 | 18137151.8041 | 12378978.7875 | 55361544.022 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74082902.7165 | 101307208.1175 | 749894.2093 | 12.9574 | 5717.4322 | 7818.4989 | 116.5576 | 159.3907
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1218 | 36.8576 | 3.2664 | 4 | 5687.6382 | 7771.2764 | 115.9502 | 158.428 | 131.3401 | 0 | 199.8358 | 5323827.2347 | 228854.8415 | 6054825.4692 | 5946601.0706 | 0 | 394672.0286 | 0 | 7000024.4514 | 18212627.7201 | 12430492.651 | 55591925.4671 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74313284.1616 | 101537589.5626 | 1000000 | 13.0658 | 5687.6382 | 7771.2764 | 115.9502 | 158.428
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7675 | 37.0163 | 3.2869 | 4 | 5665.2673 | 7735.9437 | 115.4941 | 157.7077 | 131.3227 | 0 | 198.5991 | 5339652.3847 | 229497.86 | 6075741.7365 | 5972846.4964 | 0 | 386271.0026 | 0 | 7021563.6973 | 18268668.4196 | 12468741.5799 | 55762983.177 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74484341.8714 | 101708647.2725 | 1333521.4322 | 13.1475 | 5665.2673 | 7735.9437 | 115.4941 | 157.7077
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2576 | 37.1366 | 3.3024 | 4 | 5648.4746 | 7709.43 | 115.1518 | 157.1672 | 131.3094 | 0 | 187.7566 | 5351638.7547 | 229984.6202 | 6091595.4624 | 5992761.3376 | 0 | 379840.3321 | 0 | 7037869.9977 | 18311094.0684 | 12497697.957 | 55892482.53 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74613841.2244 | 101838146.6255 | 1778279.41 | 13.2096 | 5648.4746 | 7709.43 | 115.1518 | 157.1672
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.6124 | 37.2237 | 3.3139 | 4 | 5635.8719 | 7689.6858 | 114.8949 | 156.7646 | 131.2998 | 0 | 198.877 | 5360302.2103 | 230336.2812 | 6103060.3514 | 6007174.9885 | 0 | 374776.4809 | 0 | 7049503.6218 | 18341362.3719 | 12518356.6962 | 55984873.0023 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74706231.6967 | 101930537.0978 | 2371373.7057 | 13.2555 | 5635.8719 | 7689.6858 | 114.8949 | 156.7646
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.883 | 37.2901 | 3.3226 | 4 | 5626.4161 | 7674.8492 | 114.7021 | 156.4622 | 131.2924 | 0 | 208 | 5366902.5273 | 230604.1222 | 6111798.1242 | 6018166.483 | 0 | 370962.4349 | 0 | 7058389.1397 | 18364480.6669 | 12534135.4075 | 56055438.9056 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74776797.6001 | 102001103.0011 | 3162277.6602 | 13.2903 | 5626.4161 | 7674.8492 | 114.7021 | 156.4622
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.0728 | 37.3367 | 3.3289 | 4 | 5619.3219 | 7663.8494 | 114.5575 | 156.2379 | 131.2872 | 0 | 202.0768 | 5371528.9865 | 230791.8129 | 6117924.7516 | 6025876.9273 | 0 | 367931.2046 | 0 | 7064480.9363 | 18380330.272 | 12544953.0887 | 56103817.98 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74825176.6744 | 102049482.0755 | 4216965.0343 | 13.3157 | 5619.3219 | 7663.8494 | 114.5575 | 156.2379
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.236 | 37.3767 | 3.334 | 4 | 5614.0001 | 7655.4129 | 114.449 | 156.0659 | 131.2828 | 0 | 215.1061 | 5375503.2091 | 230953.0264 | 6123188.5184 | 6032503.4084 | 0 | 365851.0646 | 0 | 7069919.6985 | 18394480.8156 | 12554611.1254 | 56147010.8664 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74868369.5608 | 102092674.9619 | 5623413.2519 | 13.336 | 5614.0001 | 7655.4129 | 114.449 | 156.0659
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.348 | 37.4042 | 3.3377 | 4 | 5610.0081 | 7649.1828 | 114.3676 | 155.9389 | 131.2797 | 0 | 212.6645 | 5378230.8717 | 231063.6523 | 6126802.0009 | 6037053.7088 | 0 | 364173.2617 | 0 | 7073556.1632 | 18403942.1509 | 12561068.6812 | 56175890.4907 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74897249.1852 | 102121554.5862 | 7498942.0933 | 13.3506 | 5610.0081 | 7649.1828 | 114.3676 | 155.9389
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4406 | 37.4269 | 3.3405 | 4 | 5607.014 | 7644.4335 | 114.3066 | 155.8421 | 131.2772 | 0 | 204.3571 | 5380484.4849 | 231155.0471 | 6129787.758 | 6040814.1735 | 0 | 362996.598 | 0 | 7076642.844 | 18411973.061 | 12566549.9423 | 56200403.9087 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74921762.6031 | 102146068.0042 | 10000000 | 13.3622 | 5607.014 | 7644.4335 | 114.3066 | 155.8421
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4827 | [19 empty] | 100 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.725 | [19 empty] | 133.3521 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3354 | [19 empty] | 177.8279 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2627 | [19 empty] | 237.1374 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.26812 | 0.0033608 | 4 | 1528558.6845 | 3605052.3701 | 31161.7363 | 73493.8688 | 102.8461 | 0 | 27.7199 | 143344.3452 | 5109.0885 | 120315.9926 | 77985.8906 | 0 | 84017.1996 | 0 | 168001.2815 | 437104.8726 | 298333.0571 | 1334211.7277 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20548839.3847 | 48463721.3334 | 316.2278 | 0.013443 | 1528558.6845 | 3605052.3701 | 31161.7363 | 73493.8688
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.3976 | 0.010219 | 4 | 512865.6436 | 1195768.5109 | 10455.4598 | 24377.3585 | 109.6413 | 0 | 331.2726 | 196691.4398 | 7361.7868 | 164077.0044 | 99172.1816 | 0 | 97610.0612 | 0 | 220315.8648 | 573216.6873 | 391232.1675 | 1749677.1937 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20964304.8507 | 48879186.7993 | 421.6965 | 0.040877 | 512865.6436 | 1195768.5109 | 10455.4598 | 24377.3585
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7989 | 0.574 | 0.020578 | 4 | 261009.9044 | 600151.4035 | 5321.0399 | 12234.8981 | 115.232 | 0 | 447.4792 | 262325.2455 | 10219.7579 | 219214.3434 | 127552.8782 | 0 | 113339.8553 | 0 | 285734.3113 | 743422.0658 | 507400.8357 | 2269209.2929 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21483836.9499 | 49398718.8986 | 562.3413 | 0.08231 | 261009.9044 | 600151.4035 | 5321.0399 | 12234.8981
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7124 | 0.81628 | 0.035544 | 4 | 155756.3667 | 352098.9597 | 3175.3042 | 7178.0135 | 119.822 | 0 | 50.3739 | 343825.9559 | 13841.9116 | 289602.9258 | 166095.3497 | 0 | 132611.8223 | 0 | 368931.4065 | 959883.8414 | 655140.4454 | 2929933.6585 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22144561.3155 | 50059443.2642 | 749.8942 | 0.14217 | 155756.3667 | 352098.9597 | 3175.3042 | 7178.0135
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9131 | 1.1395 | 0.056372 | 4 | 101833.726 | 225630.3097 | 2076.0182 | 4599.7791 | 123.4445 | 0 | 78.0623 | 442253.541 | 18268.7108 | 377217.7406 | 217100.073 | 0 | 155216.2376 | 0 | 471921.9582 | 1227844.1307 | 838028.8489 | 3747851.2408 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22962478.8978 | 50877360.8464 | 1000 | 0.22549 | 101833.726 | 225630.3097 | 2076.0182 | 4599.7791
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5138 | 1.5733 | 0.084802 | 4 | 70715.1411 | 153009.392 | 1441.6238 | 3119.3034 | 126.2849 | 0 | 63.7291 | 562089.8048 | 23684.4972 | 487348.6332 | 285006.5393 | 0 | 182760.0761 | 0 | 600946.9247 | 1563540.627 | 1067148.6055 | 4772525.7078 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 23987153.3648 | 51902035.3135 | 1333.5214 | 0.33921 | 70715.1411 | 153009.392 | 1441.6238 | 3119.3034
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 2.1475 | 0.12266 | 4 | 51486.4049 | 108379.1122 | 1049.62 | 2209.4548 | 128.3443 | 0 | 66.3971 | 706188.4391 | 30193.4643 | 624196.004 | 375916.6988 | 0 | 216076.1688 | 0 | 761502.6023 | 1981273.5655 | 1352259.9195 | 6047606.8623 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 25262234.5194 | 53177116.468 | 1778.2794 | 0.49066 | 51486.4049 | 108379.1122 | 1049.62 | 2209.4548
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4831 | 2.9345 | 0.17596 | 4 | 38221.684 | 77882.9025 | 779.2007 | 1587.7483 | 130.2787 | 0 | 92.3861 | 887364.872 | 38443.2833 | 800238.8093 | 498803.9364 | 0 | 257045.3735 | 0 | 967939.547 | 2518380.1497 | 1718846.1997 | 7687062.1709 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 26901689.8279 | 54816571.7765 | 2371.3737 | 0.70383 | 38221.684 | 77882.9025 | 779.2007 | 1587.7483
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2421 | 3.9669 | 0.24563 | 4 | 29442.2563 | 57853.8265 | 600.2202 | 1179.4285 | 131.6013 | 0 | 87.2697 | 1103547.2891 | 48219.5311 | 1017578.2619 | 660311.0733 | 0 | 306322.7743 | 0 | 1223031.7826 | 3182077.82 | 2171833.4973 | 9712922.0295 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 28927549.6865 | 56842431.6352 | 3162.2777 | 0.98252 | 29442.2563 | 57853.8265 | 600.2202 | 1179.4285
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2527 | 5.3444 | 0.33855 | 4 | 23247.7708 | 43861.0608 | 473.9373 | 894.1671 | 132.6153 | 0 | 87.0604 | 1367514.9071 | 60121.3775 | 1290708.084 | 875670.9656 | 0 | 366885.623 | 0 | 1544751.3733 | 4019126.2013 | 2743136.2172 | 12267914.749 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 31482542.406 | 59397424.3547 | 4216.965 | 1.3542 | 23247.7708 | 43861.0608 | 473.9373 | 894.1671
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8622 | 7.1636 | 0.46157 | 4 | 18782.8318 | 33902.2173 | 382.9134 | 691.1426 | 133.3838 | 0 | 79.7624 | 1687121.2362 | 74484.2036 | 1630739.8159 | 1160485.9521 | 0 | 440000.3122 | 0 | 1947204.2928 | 5066226.1433 | 3457803.4434 | 15464065.3995 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 34678693.0565 | 62593575.0052 | 5623.4133 | 1.8463 | 18782.8318 | 33902.2173 | 382.9134 | 691.1426
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5199 | 9.5483 | 0.62302 | 4 | 15511.2218 | 26712.6826 | 316.2172 | 544.5742 | 133.9654 | 0 | 91.577 | 2071928.3012 | 91710.3261 | 2051392.7987 | 1533861.3485 | 0 | 527797.9059 | 0 | 2447909.3653 | 6368958.0334 | 4346944.7268 | 19440502.8059 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 38655130.4629 | 66570012.4115 | 7498.9421 | 2.4921 | 15511.2218 | 26712.6826 | 316.2172 | 544.5742
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.9324 | 12.1407 | 0.81672 | 4 | 13076.0898 | 21620.9039 | 266.5738 | 440.7714 | 134.3453 | 0 | 93.7451 | 2459360.0717 | 108985.4821 | 2485359.805 | 1939151.931 | 0 | 595603.5644 | 0 | 2959499.7332 | 7700011.2288 | 5255415.8831 | 23503387.6992 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 42718015.3563 | 70632897.3049 | 10000 | 3.2669 | 13076.0898 | 21620.9039 | 266.5738 | 440.7714
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.1512 | 14.9527 | 1.0446 | 4 | 11225.0799 | 17905.6831 | 228.8384 | 365.0316 | 134.5988 | 0 | 103.9174 | 2853034.2386 | 126469.7556 | 2935605.4944 | 2378924.1045 | 0 | 645930.9363 | 0 | 3486586.1665 | 9071382.0081 | 6191404.6188 | 27689337.3229 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 46903964.9799 | 74818846.9286 | 13335.2143 | 4.1785 | 11225.0799 | 17905.6831 | 228.8384 | 365.0316
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.287 | 18.0079 | 1.3059 | 4 | 9813.9263 | 15157.8542 | 200.0702 | 309.0134 | 134.7478 | 0 | 131.7202 | 3256502.8995 | 144298.3966 | 3406040.8901 | 2857401.9115 | 0 | 683640.3287 | 0 | 4035674.9263 | 10499998.3275 | 7166464.6119 | 32050022.2921 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 51264649.9491 | 79179531.8977 | 17782.7941 | 5.2237 | 9813.9263 | 15157.8542 | 200.0702 | 309.0134
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.7233 | 21.127 | 1.5887 | 4 | 8740.2744 | 13132.8847 | 178.1823 | 267.7316 | 134.7909 | 0 | 164.0248 | 3647327.7663 | 161451.2773 | 3870231.7157 | 3347245.4779 | 0 | 703330.6696 | 0 | 4574538.8937 | 11902011.8343 | 8123367.6388 | 36329505.2737 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 55544132.9307 | 83459014.8793 | 23713.7371 | 6.355 | 8740.2744 | 13132.8847 | 178.1823 | 267.7316
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.8387 | 24.1325 | 1.8774 | 4 | 7926.029 | 11643.2234 | 161.5828 | 237.3629 | 134.7419 | 0 | 180.6111 | 4006972.1366 | 177104.3093 | 4304900.0118 | 3821177.0295 | 0 | 703695.3539 | 0 | 5075401.048 | 13205152.419 | 9012787.8647 | 40307190.1728 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 59521817.8298 | 87436699.7785 | 31622.7766 | 7.5097 | 7926.029 | 11643.2234 | 161.5828 | 237.3629
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.1166 | 26.8829 | 2.1561 | 4 | 7310.2332 | 10546.9958 | 149.029 | 215.0148 | 134.6272 | 0 | 172.6528 | 4323375.52 | 190748.1049 | 4693480.069 | 4257009.0699 | 0 | 687012.8229 | 0 | 5519133.9789 | 14359654.483 | 9800759.2461 | 43831173.2949 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 63045800.9519 | 90960682.9005 | 42169.6503 | 8.6243 | 7310.2332 | 10546.9958 | 149.029 | 215.0148
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.2003 | 29.2873 | 2.4118 | 4 | 6845.4482 | 9739.0789 | 139.5537 | 198.5443 | 134.4767 | 0 | 158.6337 | 4591022.533 | 202180.786 | 5026902.5876 | 4640005.0581 | 0 | 657628.8312 | 0 | 5895918.5204 | 15339970.5708 | 10469845.1194 | 46823474.0064 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 66038101.6634 | 93952983.612 | 56234.1325 | 9.647 | 6845.4482 | 9739.0789 | 139.5537 | 198.5443
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9345 | 31.3128 | 2.6364 | 4 | 6495.1007 | 9142.1772 | 132.4114 | 186.3756 | 134.3157 | 0 | 180.1835 | 4810522.3146 | 211472.7701 | 5303734.2524 | 4964312.3597 | 0 | 620761.4797 | 0 | 6205213.2388 | 16144691.9831 | 11019084.0187 | 49279792.4171 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 68494420.0741 | 96409302.0228 | 74989.4209 | 10.5456 | 6495.1007 | 9142.1772 | 132.4114 | 186.3756
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.305 | 32.9652 | 2.8266 | 4 | 6231.2278 | 8700.2141 | 127.032 | 177.3656 | 134.1622 | 0 | 192.1516 | 4985768.4581 | 218831.3941 | 5527050.9623 | 5230115.1108 | 0 | 580939.805 | 0 | 6451655.2348 | 16785883.5045 | 11456710.4072 | 51236954.8769 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 70451582.5339 | 98366464.4825 | 100000 | 11.3062 | 6231.2278 | 8700.2141 | 127.032 | 177.3656
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4102 | 34.2785 | 2.9827 | 4 | 6032.5851 | 8372.3113 | 122.9824 | 170.6809 | 134.0265 | 0 | 186.6491 | 5122705.9664 | 224541.3926 | 5703031.3626 | 5442225.953 | 0 | 541662.3475 | 0 | 6643325.1386 | 17284569.2772 | 11797073.6941 | 52759135.1319 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 71973762.7889 | 99888644.7376 | 133352.1432 | 11.9308 | 6032.5851 | 8372.3113 | 122.9824 | 170.6809
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.425 | 35.3034 | 3.1079 | 4 | 5883.1084 | 8128.5581 | 119.9351 | 165.7117 | 133.912 | 0 | 182.5651 | 5228147.1661 | 228910.6184 | 5839497.1577 | 5607912.7953 | 0 | 505388.9846 | 0 | 6789844.1216 | 17665781.6158 | 12057258.9483 | 53922741.4077 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 73137369.0647 | 101052251.0133 | 177827.941 | 12.4318 | 5883.1084 | 8128.5581 | 119.9351 | 165.7117
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1922 | 36.5154 | 3.2318 | 4 | 5770.3657 | 7929.7652 | 117.6367 | 161.659 | 133.7751 | 0 | 194.5954 | 5351470.206 | 234003.4523 | 5999885.5283 | 5804020.4984 | 0 | 490898.7068 | 0 | 6973308.5728 | 18143118.4842 | 12383051.1693 | 55379756.6182 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 74594384.2752 | 102509266.2239 | 237137.3706 | 12.9272 | 5770.3657 | 7929.7652 | 117.6367 | 161.659
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7332 | 37.1623 | 3.3122 | 4 | 5684.5306 | 7791.4986 | 115.8868 | 158.8402 | 133.7078 | 0 | 196.3385 | 5416888.13 | 236708.7207 | 6085054.724 | 5908640.5671 | 0 | 465145.1373 | 0 | 7063850.5389 | 18378690.1072 | 12543833.6425 | 56098811.5677 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 75313439.2247 | 103228321.1733 | 316227.766 | 13.2488 | 5684.5306 | 7791.4986 | 115.8868 | 158.8402
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.6823 | 37.6571 | 3.3745 | 4 | 5619.9748 | 7688.0766 | 114.5708 | 156.7318 | 133.6551 | 0 | 180.531 | 5466636.3632 | 238761.1126 | 6150009.3141 | 5988757.655 | 0 | 443917.0664 | 0 | 7132351.7894 | 18556916.3095 | 12665476.6877 | 56642826.2979 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 75857453.9549 | 103772335.9036 | 421696.5034 | 13.4978 | 5619.9748 | 7688.0766 | 114.5708 | 156.7318
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1561 | 38.0305 | 3.4221 | 4 | 5571.4454 | 7610.7759 | 113.5814 | 155.156 | 133.6145 | 0 | 183.2123 | 5504008.1031 | 240300.0786 | 6198911.3404 | 6049262.5266 | 0 | 426659.6015 | 0 | 7183465.2436 | 18689903.0324 | 12756242.8587 | 57048752.7849 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 76263380.4419 | 104178262.3906 | 562341.3252 | 13.6883 | 5571.4454 | 7610.7759 | 113.5814 | 155.156
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2498 | 38.3071 | 3.458 | 4 | 5534.9789 | 7553.1086 | 112.838 | 153.9803 | 133.5841 | 0 | 167.0904 | 5531606.3362 | 241434.9842 | 6235084.0818 | 6094121.7248 | 0 | 412706.9337 | 0 | 7220832.0837 | 18787123.8854 | 12822598.0886 | 57345508.1183 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 76560135.7753 | 104475017.724 | 749894.2093 | 13.8321 | 5534.9789 | 7553.1086 | 112.838 | 153.9803
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.0922 | 38.5199 | 3.4856 | 4 | 5507.5872 | 7509.7672 | 112.2796 | 153.0968 | 133.5605 | 0 | 206.6395 | 5552786.0778 | 242305.0395 | 6262878.3525 | 6128650.1957 | 0 | 401943.6504 | 0 | 7249539.6932 | 18861815.1967 | 12873576.4433 | 57573494.6491 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 76788122.3061 | 104703004.2548 | 1000000 | 13.9422 | 5507.5872 | 7509.7672 | 112.2796 | 153.0968
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.7159 | 38.6772 | 3.5062 | 4 | 5487.0187 | 7477.3955 | 111.8603 | 152.4368 | 133.5429 | 0 | 227.1828 | 5568420.2368 | 242946.7633 | 6283414.5376 | 6154195.5948 | 0 | 393471.0882 | 0 | 7270554.8061 | 18916492.2096 | 12910894.6281 | 57740389.8645 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 76955017.5215 | 104869899.4701 | 1333521.4322 | 14.0249 | 5487.0187 | 7477.3955 | 111.8603 | 152.4368
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.1787 | 38.794 | 3.5217 | 4 | 5471.5781 | 7453.1923 | 111.5455 | 151.9434 | 133.5298 | 0 | 193.309 | 5580000.4013 | 243421.7985 | 6298636.2873 | 6173148.6664 | 0 | 386882.3517 | 0 | 7286014.907 | 18956716.2209 | 12938348.3424 | 57863168.9755 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77077796.6325 | 104992678.5812 | 1778279.41 | 14.0869 | 5471.5781 | 7453.1923 | 111.5455 | 151.9434
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5271 | 38.8818 | 3.5334 | 4 | 5459.9896 | 7435.0472 | 111.3093 | 151.5735 | 133.5199 | 0 | 197.6552 | 5588702.9287 | 243778.6296 | 6310081.4157 | 6187409.637 | 0 | 381847.5106 | 0 | 7297609.8474 | 18986883.8773 | 12958938.3877 | 57955252.2339 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77169879.8909 | 105084761.8396 | 2371373.7057 | 14.1337 | 5459.9896 | 7435.0472 | 111.3093 | 151.5735
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.7829 | 38.9462 | 3.5421 | 4 | 5451.2938 | 7421.4969 | 111.132 | 151.2973 | 133.5126 | 0 | 204.4969 | 5595084.6171 | 244040.208 | 6318477.6254 | 6197877.2436 | 0 | 377952.2854 | 0 | 7306038.472 | 19008813.4296 | 12973905.7577 | 58022189.6388 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77236817.2958 | 105151699.2445 | 3162277.6602 | 14.1685 | 5451.2938 | 7421.4969 | 111.132 | 151.2973
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.983 | 38.9966 | 3.5488 | 4 | 5444.7696 | 7411.2687 | 110.999 | 151.0887 | 133.5069 | 0 | 205.5434 | 5600071.4282 | 244244.5655 | 6325040.4356 | 6206062.3669 | 0 | 375082.4466 | 0 | 7312695.4847 | 19026133.611 | 12985727.1375 | 58075057.4759 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77289685.1329 | 105204567.0815 | 4216965.0343 | 14.1952 | 5444.7696 | 7411.2687 | 110.999 | 151.0887
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1339 | 39.0346 | 3.5538 | 4 | 5439.8752 | 7403.5932 | 110.8992 | 150.9323 | 133.5025 | 0 | 191.8619 | 5603832.1313 | 244398.6482 | 6329990.7485 | 6212238.3011 | 0 | 372920.1295 | 0 | 7317718.1839 | 19039201.6441 | 12994646.3385 | 58114946.1252 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77329573.7822 | 105244455.7308 | 5623413.2519 | 14.2153 | 5439.8752 | 7403.5932 | 110.8992 | 150.9323
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2387 | 39.061 | 3.5575 | 4 | 5436.2039 | 7397.9115 | 110.8244 | 150.8164 | 133.4995 | 0 | 220.5446 | 5606442.1429 | 244505.5646 | 6333427.0557 | 6216526.443 | 0 | 371198.7901 | 0 | 7321118.9986 | 19048049.8663 | 13000685.4321 | 58141954.2934 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77356581.9504 | 105271463.899 | 7498942.0933 | 14.2299 | 5436.2039 | 7397.9115 | 110.8244 | 150.8164
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.3165 | 39.0806 | 3.5602 | 4 | 5433.4503 | 7393.6586 | 110.7682 | 150.7297 | 133.4973 | 0 | 208.121 | 5608378.3652 | 244584.8714 | 6335976.5722 | 6219708.4899 | 0 | 369892.7974 | 0 | 7323631.0275 | 19054585.6502 | 13005146.2388 | 58161904.0126 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77376531.6696 | 105291413.6182 | 10000000 | 14.2408 | 5433.4503 | 7393.6586 | 110.7682 | 150.7297
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.158 | [19 empty] | 100 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7427 | [19 empty] | 133.3521 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3506 | [19 empty] | 177.8279 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0443 | [19 empty] | 237.1374 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.27368 | 0.0045254 | 4 | 1163494.2876 | 2744219.5313 | 23719.4048 | 55944.627 | 104.0359 | 0 | 28.3205 | 146551.5917 | 5266.4737 | 122199.4276 | 78494.3685 | 0 | 82504.6024 | 0 | 169656.4209 | 441411.2059 | 301272.2181 | 1347356.3089 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21061113.0193 | 49674775.6427 | 316.2278 | 0.018102 | 1163494.2876 | 2744219.5313 | 23719.4048 | 55944.627
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1765 | 0.42207 | 0.01227 | 4 | 438813.7135 | 1021793.6471 | 8945.8111 | 20830.6456 | 111.6609 | 0 | 347.4273 | 207537.2797 | 7878.1906 | 171852.0329 | 102459.6774 | 0 | 99174.771 | 0 | 229671.7611 | 597558.8102 | 407846.1666 | 1823978.6894 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21537735.3999 | 50151398.0233 | 421.6965 | 0.049082 | 438813.7135 | 1021793.6471 | 8945.8111 | 20830.6456
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8572 | 0.60404 | 0.023692 | 4 | 232839.449 | 534776.864 | 4746.7471 | 10902.1497 | 117.2075 | 0 | 449.9965 | 274864.2544 | 10856.7648 | 228023.9658 | 131338.6366 | 0 | 114204.609 | 0 | 296122.41 | 770449.7677 | 525847.7976 | 2351708.206 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22065464.9164 | 50679127.5398 | 562.3413 | 0.094767 | 232839.449 | 534776.864 | 4746.7471 | 10902.1497
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7754 | 0.85526 | 0.040127 | 4 | 141684.296 | 319952.3078 | 2888.426 | 6522.6606 | 121.8247 | 0 | 67.7815 | 359028.5696 | 14656.3818 | 300191.4765 | 170766.3939 | 0 | 132959.2667 | 0 | 381264.8145 | 991972.8391 | 677041.8457 | 3027881.5877 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22741638.2981 | 51355300.9215 | 749.8942 | 0.16051 | 141684.296 | 319952.3078 | 2888.426 | 6522.6606
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0058 | 1.1964 | 0.06304 | 4 | 93571.0944 | 207045.9979 | 1907.5733 | 4220.9127 | 125.5455 | 0 | 77.5273 | 462480.393 | 19380.651 | 391660.2232 | 223529.1335 | 0 | 155992.3112 | 0 | 488686.6577 | 1271462.4398 | 867799.2411 | 3880991.0506 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 23594747.761 | 52208410.3844 | 1000 | 0.25216 | 93571.0944 | 207045.9979 | 1907.5733 | 4220.9127
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 1.65 | 0.094343 | 4 | 65335.8157 | 141159.137 | 1331.959 | 2877.7199 | 128.4232 | 0 | 65.92 | 587482.4242 | 25130.4006 | 505516.0653 | 294255.3593 | 0 | 183289.4425 | 0 | 622312.7398 | 1619130.0952 | 1105089.5598 | 4942206.0867 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 24655962.7971 | 53269625.4206 | 1333.5214 | 0.37737 | 65335.8157 | 141159.137 | 1331.959 | 2877.7199
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7944 | 2.2556 | 0.13598 | 4 | 47771.2629 | 100375.7729 | 973.8818 | 2046.2959 | 130.5387 | 0 | 59.6074 | 738838.7363 | 32075.6908 | 648222.0535 | 388408.9083 | 0 | 217123.3879 | 0 | 789620.8229 | 2054431.4077 | 1402191.6501 | 6270912.6575 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 25984669.3679 | 54598331.9913 | 1778.2794 | 0.54394 | 47771.2629 | 100375.7729 | 973.8818 | 2046.2959
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6754 | 3.0763 | 0.19429 | 4 | 35608.8811 | 72427.954 | 725.9352 | 1476.5418 | 132.5031 | 0 | 75.5783 | 927100.0841 | 40788.069 | 829771.558 | 514581.5421 | 0 | 257588.535 | 0 | 1002233.6174 | 2607606.2862 | 1779744.8713 | 7959414.5631 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 27673171.2735 | 56286833.897 | 2371.3737 | 0.77714 | 35608.8811 | 72427.954 | 725.9352 | 1476.5418
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5199 | 4.166 | 0.27105 | 4 | 27476.2241 | 53867.3594 | 560.14 | 1098.159 | 133.8603 | 0 | 85.9109 | 1154638.5546 | 51254.441 | 1056606.0294 | 683191.8554 | 0 | 307635.0161 | 0 | 1268797.0997 | 3301149.7874 | 2253102.5617 | 10076375.3456 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 29790132.056 | 58403794.6794 | 3162.2777 | 1.0842 | 27476.2241 | 53867.3594 | 560.14 | 1098.159
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6011 | 5.6075 | 0.37293 | 4 | 21742.0095 | 40923.8629 | 443.2403 | 834.2883 | 134.8915 | 0 | 91.0159 | 1429931.8081 | 63870.3027 | 1339212.8697 | 905538.2052 | 0 | 367956.8277 | 0 | 1601538.9052 | 4166875.7106 | 2843978.2932 | 12718902.9226 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 32432659.633 | 61046322.2564 | 4216.965 | 1.4917 | 21742.0095 | 40923.8629 | 443.2403 | 834.2883
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3032 | 7.5082 | 0.50732 | 4 | 17606.1696 | 31706.677 | 358.9256 | 646.3835 | 135.6746 | 0 | 83.7928 | 1762615.0051 | 79047.6748 | 1690620.1064 | 1197239.1751 | 0 | 440807.8779 | 0 | 2016428.6373 | 5246333.6879 | 3580730.5434 | 16013822.7078 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 35727579.4183 | 64341242.0417 | 5623.4133 | 2.0293 | 17606.1696 | 31706.677 | 358.9256 | 646.3835
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.1117 | 10.0088 | 0.68401 | 4 | 14563.0301 | 25021.0462 | 296.8871 | 510.0879 | 136.2693 | 0 | 81.2073 | 2164800.486 | 97331.6442 | 2126921.1145 | 1581641.755 | 0 | 529073.8154 | 0 | 2534909.8379 | 6595315.4166 | 4501438.292 | 20131432.3615 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 39845189.072 | 68458851.6954 | 7498.9421 | 2.7361 | 14563.0301 | 25021.0462 | 296.8871 | 510.0879
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.2837 | 13.1823 | 0.91066 | 4 | 12302.985 | 20158.2259 | 250.813 | 410.9527 | 136.7061 | 0 | 95.2176 | 2635188.7787 | 118638.1182 | 2650404.45 | 2070592.0482 | 0 | 629566.306 | 0 | 3160711.9834 | 8223524.2296 | 5612724.2632 | 25101350.1773 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 44815106.8877 | 73428769.5111 | 10000 | 3.6426 | 12302.985 | 20158.2259 | 250.813 | 410.9527
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.8313 | 16.1747 | 1.1604 | 4 | 10599.0364 | 16763.646 | 216.0757 | 341.7496 | 136.9448 | 0 | 116.044 | 3048855.6262 | 137289.3633 | 3121164.5616 | 2531871.0375 | 0 | 679816.6089 | 0 | 3712408.907 | 9658926.4563 | 6592415.7775 | 29482748.3382 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 49196505.0486 | 77810167.6721 | 13335.2143 | 4.6416 | 10599.0364 | 16763.646 | 216.0757 | 341.7496
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1855 | 19.3834 | 1.4435 | 4 | 9300.3686 | 14255.9211 | 189.6006 | 290.6262 | 137.0729 | 0 | 122.1842 | 3467683.5531 | 156065.4383 | 3607073.1889 | 3027185.8538 | 0 | 715306.591 | 0 | 4279592.7038 | 11134622.35 | 7599608.5475 | 33987138.2262 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 53700894.9367 | 82314557.5601 | 17782.7941 | 5.7741 | 9300.3686 | 14255.9211 | 189.6006 | 290.6262
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.7265 | 22.6225 | 1.7465 | 4 | 8312.8553 | 12408.7521 | 169.4688 | 252.9692 | 137.0918 | 0 | 158.8416 | 3869267.586 | 173932.2144 | 4081667.294 | 3528636.233 | 0 | 731435.5692 | 0 | 4830126.1697 | 12566997.4984 | 8577234.0186 | 38359296.5834 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 58073053.2938 | 86686715.9172 | 23713.7371 | 6.9859 | 8312.8553 | 12408.7521 | 169.4688 | 252.9692
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.8324 | 25.71 | 2.0522 | 4 | 7564.2359 | 11049.9224 | 154.2072 | 225.2676 | 137.0193 | 0 | 159.8902 | 4235231.7472 | 190065.8127 | 4521763.0936 | 4008619.3656 | 0 | 727514.0801 | 0 | 5336445.6987 | 13884337.0524 | 9476345.3328 | 42380322.183 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 62094078.8934 | 90707741.5169 | 31622.7766 | 8.2089 | 7564.2359 | 11049.9224 | 154.2072 | 225.2676
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0176 | 28.51 | 2.3444 | 4 | 6998.1797 | 10049.5217 | 142.6674 | 204.8731 | 136.8847 | 0 | 151.5514 | 4554632.7455 | 204005.6456 | 4912057.7706 | 4445842.6642 | 0 | 706590.9845 | 0 | 5781020.6261 | 15041029.8187 | 10265811.9135 | 45910992.1687 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 65624748.8791 | 94238411.5025 | 42169.6503 | 9.3774 | 6998.1797 | 10049.5217 | 142.6674 | 204.8731
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.9628 | 30.9408 | 2.6101 | 4 | 6570.9062 | 9311.5997 | 133.9568 | 189.8296 | 136.7187 | 0 | 181.8264 | 4823197.935 | 215608.6659 | 5244930.3679 | 4827203.9824 | 0 | 673519.273 | 0 | 6155939.4874 | 16016491.7895 | 10931584.7523 | 48888476.2534 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 68602232.9639 | 97215895.5873 | 56234.1325 | 10.4403 | 6570.9062 | 9311.5997 | 133.9568 | 189.8296
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5487 | 32.9796 | 2.842 | 4 | 6248.7574 | 8765.7868 | 127.3894 | 178.7024 | 136.5463 | 0 | 165.8935 | 5042651.0012 | 224999.6354 | 5520284.6624 | 5148540.5065 | 0 | 633783.2587 | 0 | 6462401.0351 | 16813841.8725 | 11475792.5679 | 51322294.5398 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 71036051.2502 | 99649713.8736 | 74989.4209 | 11.368 | 6248.7574 | 8765.7868 | 127.3894 | 178.7024
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.7554 | 34.6313 | 3.037 | 4 | 6006.0464 | 8361.4896 | 122.4414 | 170.4603 | 136.3852 | 0 | 192.2803 | 5216758.8829 | 232386.6086 | 5740998.1018 | 5409951.9487 | 0 | 591595.719 | 0 | 6704759.5917 | 17444409.1224 | 11906167.6728 | 53247027.6477 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 72960784.3581 | 101574446.9816 | 100000 | 12.1479 | 6006.0464 | 8361.4896 | 122.4414 | 170.4603
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.7077 | 35.938 | 3.1962 | 4 | 5823.2705 | 8061.3419 | 118.7152 | 164.3414 | 136.2445 | 0 | 179.1518 | 5352261.5342 | 238093.6291 | 5914216.3586 | 5617513.3424 | 0 | 550521.9829 | 0 | 6892316.6704 | 17932394.1678 | 12239227.4934 | 54736545.1788 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 74450301.8892 | 103063964.5126 | 133352.1432 | 12.785 | 5823.2705 | 8061.3419 | 118.7152 | 164.3414
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.6124 | 36.9611 | 3.3239 | 4 | 5685.6715 | 7837.7715 | 115.9101 | 159.7836 | 136.1261 | 0 | 185.6752 | 5457001.9455 | 242478.0879 | 6049013.1758 | 5780507.9712 | 0 | 513174.5402 | 0 | 7036448.531 | 18307395.7036 | 12495173.7471 | 55881193.7021 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 75594950.4126 | 104208613.036 | 177827.941 | 13.2957 | 5685.6715 | 7837.7715 | 115.9101 | 159.7836
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4554 | 38.231 | 3.4544 | 4 | 5580.7995 | 7651.6375 | 113.7721 | 155.989 | 135.9899 | 0 | 202.1437 | 5585960.6267 | 247881.1396 | 6215284.0763 | 5982914.555 | 0 | 500041.6168 | 0 | 7227511.9856 | 18804503.6199 | 12834460.1145 | 57398557.7344 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 77112314.4448 | 105725977.0682 | 237137.3706 | 13.8174 | 5580.7995 | 7651.6375 | 113.7721 | 155.989
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.9233 | 38.8776 | 3.5364 | 4 | 5501.6694 | 7524.4594 | 112.159 | 153.3963 | 135.921 | 0 | 213.5046 | 5651173.6197 | 250614.3391 | 6299512.7376 | 6086962.9248 | 0 | 473805.2991 | 0 | 7317206.8789 | 19037871.3335 | 12993738.3742 | 58110885.507 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 77824642.2175 | 106438304.8409 | 316227.766 | 14.1456 | 5501.6694 | 7524.4594 | 112.159 | 153.3963
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7823 | 39.3633 | 3.5993 | 4 | 5442.1534 | 7429.5935 | 110.9457 | 151.4623 | 135.8681 | 0 | 182.0253 | 5699898.9323 | 252651.821 | 6362616.8822 | 6165262.9638 | 0 | 451911.4765 | 0 | 7383613.4096 | 19210647.5044 | 13111661.6611 | 58638264.6509 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 78352021.3613 | 106965683.9848 | 421696.5034 | 14.3972 | 5442.1534 | 7429.5935 | 110.9457 | 151.4623
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1971 | 39.7322 | 3.6475 | 4 | 5397.4108 | 7358.577 | 110.0335 | 150.0145 | 135.8272 | 0 | 213.1441 | 5736752.4898 | 254190.1805 | 6410443.7105 | 6224805.1716 | 0 | 434290.6016 | 0 | 7433588.0401 | 19340671.2416 | 13200405.5335 | 59035146.9692 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 78748903.6796 | 107362566.303 | 562341.3252 | 14.5901 | 5397.4108 | 7358.577 | 110.0335 | 150.0145
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.2714 | 40.0119 | 3.6843 | 4 | 5363.7887 | 7305.3717 | 109.3481 | 148.9299 | 135.7959 | 0 | 195.0809 | 5764605.7792 | 255351.2869 | 6446646.6881 | 6269990.2148 | 0 | 420354.5132 | 0 | 7471209.9081 | 19438555.625 | 13267213.6364 | 59333927.6517 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79047684.3621 | 107661346.9856 | 749894.2093 | 14.7373 | 5363.7887 | 7305.3717 | 109.3481 | 148.9299
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.0607 | 40.2171 | 3.7119 | 4 | 5338.5329 | 7265.701 | 108.8332 | 148.1211 | 135.7726 | 0 | 205.1758 | 5785000.5387 | 256200.5983 | 6473186.4957 | 6303177.5309 | 0 | 409211.6165 | 0 | 7498442.9443 | 19509410.3989 | 13315573.4755 | 59550203.5989 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79263960.3093 | 107877622.9328 | 1000000 | 14.8475 | 5338.5329 | 7265.701 | 108.8332 | 148.1211
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6481 | 40.3697 | 3.7326 | 4 | 5319.5679 | 7236.037 | 108.4466 | 147.5164 | 135.7552 | 0 | 194.4021 | 5800135.3148 | 256830.386 | 6492898.5502 | 6327861.3601 | 0 | 400499.0811 | 0 | 7518507.63 | 19561614.5952 | 13351203.9122 | 59709550.8296 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79423307.54 | 108036970.1635 | 1333521.4322 | 14.9304 | 5319.5679 | 7236.037 | 108.4466 | 147.5164
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1083 | 40.4892 | 3.7485 | 4 | 5305.3307 | 7213.6494 | 108.1563 | 147.06 | 135.7415 | 0 | 209.2557 | 5811973.3691 | 257322.7202 | 6508326.6901 | 6347200.9006 | 0 | 393999.6599 | 0 | 7534341.1026 | 19602810.0432 | 13379320.6519 | 59835295.1378 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79549051.8482 | 108162714.4716 | 1778279.41 | 14.9942 | 5305.3307 | 7213.6494 | 108.1563 | 147.06
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.4445 | 40.5764 | 3.7604 | 4 | 5294.6453 | 7196.9505 | 107.9385 | 146.7196 | 135.7315 | 0 | 180.7205 | 5820606.4535 | 257681.5988 | 6519583.6533 | 6361323.2612 | 0 | 388924.9882 | 0 | 7545766.7824 | 19632537.3183 | 13399610.128 | 59926034.1837 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79639790.8941 | 108253453.5175 | 2371373.7057 | 15.0416 | 5294.6453 | 7196.9505 | 107.9385 | 146.7196
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.7003 | 40.6428 | 3.7694 | 4 | 5286.6271 | 7184.4048 | 107.775 | 146.4638 | 135.7239 | 0 | 192.5525 | 5827167.786 | 257954.2676 | 6528142.3172 | 6372066.8311 | 0 | 385099.2543 | 0 | 7554467.8779 | 19655175.7838 | 13415061.3459 | 59995135.4638 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79708892.1742 | 108322554.7976 | 3162277.6602 | 15.0775 | 5286.6271 | 7184.4048 | 107.775 | 146.4638
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8855 | 40.6908 | 3.776 | 4 | 5280.6112 | 7175.0558 | 107.6524 | 146.2732 | 135.7183 | 0 | 185.9727 | 5831914.9727 | 258151.4934 | 6534336.4031 | 6379845.7457 | 0 | 382124.8925 | 0 | 7560685.6679 | 19671353.198 | 13426102.7635 | 60044515.1367 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79758271.8472 | 108371934.4706 | 4216965.0343 | 15.104 | 5280.6112 | 7175.0558 | 107.6524 | 146.2732
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.0144 | 40.7242 | 3.7808 | 4 | 5276.0982 | 7168.13 | 107.5604 | 146.132 | 135.7145 | 0 | 218.8435 | 5835216.5419 | 258288.6287 | 6538645.2622 | 6385258.9643 | 0 | 379766.8789 | 0 | 7564898.7476 | 19682314.7673 | 13433584.2598 | 60077974.0507 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79791730.7612 | 108405393.3846 | 5623413.2519 | 15.1232 | 5276.0982 | 7168.13 | 107.5604 | 146.132
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1265 | 40.7533 | 3.7847 | 4 | 5272.7129 | 7162.8098 | 107.4914 | 146.0236 | 135.7111 | 0 | 215.7374 | 5838085.8308 | 258407.8046 | 6542390.2703 | 6389964.6667 | 0 | 378153.6751 | 0 | 7568730.8765 | 19692285.1805 | 13440389.2717 | 60108407.5761 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79822164.2866 | 108435826.91 | 7498942.0933 | 15.1387 | 5272.7129 | 7162.8098 | 107.4914 | 146.0236
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1996 | 40.7722 | 3.7874 | 4 | 5270.1737 | 7158.911 | 107.4396 | 145.9441 | 135.7089 | 0 | 202.5829 | 5839958.2155 | 258485.5588 | 6544834.5526 | 6393036.7232 | 0 | 376820.1777 | 0 | 7571122.7388 | 19698508.3157 | 13444636.6893 | 60127402.9716 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79841159.6821 | 108454822.3055 | 10000000 | 15.1496 | 5270.1737 | 7158.911 | 107.4396 | 145.9441
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8621 | [19 empty] | 100 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8245 | [19 empty] | 133.3521 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.737 | [19 empty] | 177.8279 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1188 | [19 empty] | 237.1374 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.27914 | 0.0056836 | 4 | 949172.5641 | 2238877.3144 | 19350.1666 | 45642.5424 | 105.2093 | 0 | 27.7107 | 149717.1126 | 5423.99 | 124038.8734 | 78961.5563 | 0 | 80992.9729 | 0 | 171262.457 | 445589.7825 | 304124.1825 | 1360110.9272 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21578856.7819 | 50899504.2074 | 316.2278 | 0.022734 | 949172.5641 | 2238877.3144 | 19350.1666 | 45642.5424
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.44211 | 0.014384 | 4 | 384122.6268 | 893734.9269 | 7830.8593 | 18219.9954 | 113.478 | 0 | 346.5126 | 216635.1228 | 8327.7425 | 178119.9018 | 104936.8327 | 0 | 99559.8609 | 0 | 236955.9896 | 616510.8787 | 420781.3427 | 1881827.6716 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22100573.5263 | 51421220.9517 | 421.6965 | 0.057535 | 384122.6268 | 893734.9269 | 7830.8593 | 18219.9954
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9155 | 0.63503 | 0.02699 | 4 | 209841.5936 | 481431.3151 | 4277.9047 | 9814.6285 | 119.1814 | 0 | 452.9674 | 287707.3897 | 11520.4398 | 237008.0312 | 135133.2869 | 0 | 115009.5848 | 0 | 306687.7056 | 797938.4997 | 544609.422 | 2435614.3595 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22654360.2143 | 51975007.6397 | 562.3413 | 0.10796 | 209841.5936 | 481431.3151 | 4277.9047 | 9814.6285
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8459 | 0.8973 | 0.04499 | 4 | 129760.6463 | 292690.3602 | 2645.3463 | 5966.8889 | 123.8552 | 0 | 75.3691 | 375196.3705 | 15533.1488 | 311500.1374 | 175668.2901 | 0 | 133589.6532 | 0 | 394480.1641 | 1026356.4679 | 700509.3788 | 3132833.611 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 23351579.4657 | 52672226.8911 | 749.8942 | 0.17996 | 129760.6463 | 292690.3602 | 2645.3463 | 5966.8889
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0984 | 1.2557 | 0.070179 | 4 | 86346.5249 | 190795.6862 | 1760.2907 | 3889.6281 | 127.6443 | 0 | 78.6197 | 483520.1883 | 20563.863 | 406520.9292 | 230677.3838 | 0 | 156701.4832 | 0 | 506213.7005 | 1317064.21 | 898923.3863 | 4020185.1444 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 24238930.9991 | 53559578.4245 | 1000 | 0.28072 | 86346.5249 | 190795.6862 | 1760.2907 | 3889.6281
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7379 | 1.7286 | 0.10431 | 4 | 60711.4234 | 130982.459 | 1237.6845 | 2670.2546 | 130.5584 | 0 | 64.8241 | 613332.2569 | 26630.9247 | 523925.9328 | 303258.1572 | 0 | 183717.0626 | 0 | 643837.0903 | 1675132.0399 | 1143312.0378 | 5113145.5023 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 25331891.357 | 54652538.7824 | 1333.5214 | 0.41725 | 60711.4234 | 130982.459 | 1237.6845 | 2670.2546
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9474 | 2.3656 | 0.1501 | 4 | 44492.769 | 93327.8041 | 907.0453 | 1902.6135 | 132.7559 | 0 | 81.735 | 772080.4405 | 34040.0016 | 672394.6966 | 400710.2428 | 0 | 217728.1347 | 0 | 817811.8713 | 2127778.7328 | 1452252.7066 | 6494796.8267 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 26713542.6814 | 56034190.1069 | 1778.2794 | 0.6004 | 44492.769 | 93327.8041 | 907.0453 | 1902.6135
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8922 | 3.2302 | 0.21393 | 4 | 33276.1374 | 67540.5612 | 678.3791 | 1376.9057 | 134.7363 | 0 | 71.9922 | 969660.7523 | 43335.2122 | 861524.7494 | 532349.188 | 0 | 258784.664 | 0 | 1039605.2807 | 2704839.688 | 1846108.6659 | 8256208.2004 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 28474954.0551 | 57795601.4806 | 2371.3737 | 0.85572 | 33276.1374 | 67540.5612 | 678.3791 | 1376.9057
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7757 | 4.3631 | 0.29725 | 4 | 25772.8673 | 50432.5707 | 525.4148 | 1028.1362 | 136.1106 | 0 | 86.4286 | 1205147.0733 | 54328.5839 | 1094788.2172 | 703659.1053 | 0 | 308112.4323 | 0 | 1312753.8107 | 3415516.1326 | 2331159.9423 | 10425465.2977 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 30644211.1524 | 59964858.5778 | 3162.2777 | 1.189 | 25772.8673 | 50432.5707 | 525.4148 | 1028.1362
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9495 | 5.8765 | 0.40873 | 4 | 20422.4603 | 38356.4861 | 416.3395 | 781.9488 | 137.1649 | 0 | 97.2765 | 1493357.5754 | 67757.5266 | 1388288.8499 | 934048.5388 | 0 | 368794.0352 | 0 | 1658376.1451 | 4314754.5499 | 2944908.6396 | 13170285.8606 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 33389031.7153 | 62709679.1408 | 4216.965 | 1.6349 | 20422.4603 | 38356.4861 | 416.3395 | 781.9488
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.7831 | 7.8768 | 0.55613 | 4 | 16553.2756 | 29733.9043 | 337.4609 | 606.1659 | 137.9658 | 0 | 93.7935 | 1842532.0336 | 83961.929 | 1754012.1004 | 1238160.3063 | 0 | 442354.632 | 0 | 2090798.1905 | 5439828.01 | 3712794.3941 | 16604441.5958 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 36823187.4505 | 66143834.8759 | 5623.4133 | 2.2245 | 16553.2756 | 29733.9043 | 337.4609 | 606.1659
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.7185 | 10.4927 | 0.74907 | 4 | 13711.4582 | 23497.15 | 279.5266 | 479.0212 | 138.571 | 0 | 78.7759 | 2262009.0007 | 103349.1321 | 2205404.3817 | 1635231.6257 | 0 | 530485.7842 | 0 | 2627227.1705 | 6835506.1793 | 4665373.423 | 20864586.6973 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 41083332.5521 | 70403979.9775 | 7498.9421 | 2.9963 | 13711.4582 | 23497.15 | 279.5266 | 479.0212
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.2849 | 13.8794 | 0.99849 | 4 | 11600.5216 | 18941.7452 | 236.4923 | 386.1531 | 139.022 | 0 | 77.1961 | 2762052.6776 | 126360.7999 | 2757692.8087 | 2149317.9609 | 0 | 635729.6206 | 0 | 3288150.0084 | 8555091.8296 | 5839025.9633 | 26113421.669 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 46332167.5238 | 75652814.9492 | 10000 | 3.994 | 11600.5216 | 18941.7452 | 236.4923 | 386.1531
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.5233 | 17.4577 | 1.2859 | 4 | 10025.4605 | 15725.7883 | 204.3826 | 320.5915 | 139.2832 | 0 | 103.7429 | 3252683.0932 | 148829.0419 | 3312534.6735 | 2693674.3241 | 0 | 713823.0518 | 0 | 3947402.232 | 10270330.8841 | 7009711.8626 | 31348989.1631 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 51567735.0179 | 80888382.4433 | 13335.2143 | 5.1437 | 10025.4605 | 15725.7883 | 204.3826 | 320.5915
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.0696 | 20.8172 | 1.5916 | 4 | 8829.0285 | 13434.4962 | 179.9917 | 273.8804 | 139.3888 | 0 | 136.0388 | 3686310.8347 | 168553.0052 | 3813105.4665 | 3205711.514 | 0 | 746660.8014 | 0 | 4531933.2325 | 11791160.6436 | 8047709.4234 | 35991144.9214 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 56209890.7761 | 85530538.2015 | 17782.7941 | 6.3665 | 8829.0285 | 13434.4962 | 179.9917 | 273.8804
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.689 | 24.1715 | 1.9151 | 4 | 7919.7132 | 11747.2933 | 161.4541 | 239.4845 | 139.3826 | 0 | 164.4154 | 4097977.3621 | 187120.573 | 4297199.1391 | 3718485.3869 | 0 | 758890.9782 | 0 | 5093272.6414 | 13251650.6389 | 9044523.8553 | 40449120.575 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 60667866.4297 | 89988513.8551 | 23713.7371 | 7.6604 | 7919.7132 | 11747.2933 | 161.4541 | 239.4845
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7903 | 27.343 | 2.2383 | 4 | 7230.6093 | 10505.5248 | 147.4058 | 214.1693 | 139.2863 | 0 | 162.2271 | 4470468.2774 | 203753.4577 | 4742932.1533 | 4205250.6792 | 0 | 750853.8376 | 0 | 5605570.778 | 14584545.3036 | 9954251.8522 | 44517626.3388 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 64736372.1935 | 94057019.619 | 31622.7766 | 8.9531 | 7230.6093 | 10505.5248 | 147.4058 | 214.1693
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.8823 | 30.1922 | 2.544 | 4 | 6709.562 | 9590.9398 | 136.7835 | 195.5243 | 139.1317 | 0 | 176.9256 | 4792840.0538 | 217993.5792 | 5134895.7618 | 4644567.5523 | 0 | 725761.38 | 0 | 6051262.7476 | 15744144.3846 | 10745702.0523 | 48057167.5116 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 68275913.3663 | 97596560.7917 | 42169.6503 | 10.1759 | 6709.562 | 9590.9398 | 136.7835 | 195.5243
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7102 | 32.6551 | 2.8202 | 4 | 6316.1838 | 8915.3785 | 128.7639 | 181.752 | 138.95 | 0 | 176.246 | 5063002.1894 | 229801.8527 | 5468015.6199 | 5026390.7384 | 0 | 689326.6713 | 0 | 6425849.458 | 16718742.1667 | 11410885.0645 | 51032013.7609 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 71250759.6156 | 100571407.041 | 56234.1325 | 11.2807 | 6316.1838 | 8915.3785 | 128.7639 | 181.752
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.1233 | 34.7009 | 3.0593 | 4 | 6019.4568 | 8415.5067 | 122.7148 | 171.5615 | 138.7668 | 0 | 194.4025 | 5281900.9263 | 239280.7098 | 5741090.2588 | 5345864.5111 | 0 | 646444.0814 | 0 | 6729286.39 | 17508222.8204 | 11949721.8329 | 53441811.5306 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 73660557.3853 | 102981204.8107 | 74989.4209 | 12.2371 | 6019.4568 | 8415.5067 | 122.7148 | 171.5615
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1667 | 36.3523 | 3.2592 | 4 | 5795.8478 | 8044.8816 | 118.1562 | 164.0058 | 138.5984 | 0 | 191.6439 | 5455081.8327 | 246714.7366 | 5959303.0606 | 5605006.6515 | 0 | 601886.5724 | 0 | 6968517.2129 | 18130652.3486 | 12374542.7756 | 55341705.1907 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 75560451.0454 | 104881098.4708 | 100000 | 13.037 | 5795.8478 | 8044.8816 | 118.1562 | 164.0058
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.9735 | 37.6548 | 3.4219 | 4 | 5627.4163 | 7769.5235 | 114.7225 | 158.3922 | 138.4527 | 0 | 171.3844 | 5589534.9955 | 252443.5728 | 6130100.8871 | 5810251.5865 | 0 | 559070.3976 | 0 | 7153146.5614 | 18611020.0407 | 12702403.596 | 56807971.6377 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 77026717.4924 | 106347364.9179 | 133352.1432 | 13.6878 | 5627.4163 | 7769.5235 | 114.7225 | 158.3922
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5151 | 39.151 | 3.5817 | 4 | 5499.7821 | 7546.3149 | 112.1205 | 153.8418 | 138.2867 | 0 | 195.4142 | 5742123.599 | 258925.2953 | 6324898.1604 | 6046457.8192 | 0 | 540012.7545 | 0 | 7375842.8751 | 19190430.1675 | 13097862.9132 | 58576553.5841 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 78795299.4388 | 108115946.8642 | 177827.941 | 14.327 | 5499.7821 | 7546.3149 | 112.1205 | 153.8418
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.624 | 39.9897 | 3.6887 | 4 | 5402.8199 | 7390.0245 | 110.1438 | 150.6556 | 138.1979 | 0 | 206.0932 | 5826920.2046 | 262525.3636 | 6433446.8952 | 6178924.5027 | 0 | 508217.4141 | 0 | 7491913.4084 | 19492421.8858 | 13303978.4663 | 59498348.1408 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 79717093.9955 | 109037741.4209 | 237137.3706 | 14.7547 | 5402.8199 | 7390.0245 | 110.1438 | 150.6556
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.0038 | 40.6295 | 3.7717 | 4 | 5329.8401 | 7273.303 | 108.656 | 148.2761 | 138.1282 | 0 | 218.0467 | 5891151.9259 | 265243.8495 | 6515960.4571 | 6280150.6569 | 0 | 481329.3959 | 0 | 7579196.1513 | 19719513.6787 | 13458973.2812 | 60191519.3966 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 80410265.2513 | 109730912.6767 | 316227.766 | 15.0868 | 5329.8401 | 7273.303 | 108.656 | 148.2761
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8085 | 41.1134 | 3.8355 | 4 | 5274.9412 | 7186.0876 | 107.5368 | 146.4981 | 138.0743 | 0 | 231.2383 | 5939470.4332 | 267283.9054 | 6578198.583 | 6356807.6217 | 0 | 459139.7218 | 0 | 7644351.1034 | 19889033.499 | 13574674.0419 | 60708958.9094 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 80927704.7641 | 110248352.1896 | 421696.5034 | 15.3419 | 5274.9412 | 7186.0876 | 107.5368 | 146.4981
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1682 | 41.4772 | 3.8841 | 4 | 5233.6642 | 7120.8883 | 106.6953 | 145.1689 | 138.0332 | 0 | 204.6431 | 5975655.2477 | 268808.8419 | 6624902.4959 | 6414503.805 | 0 | 441184.8538 | 0 | 7692771.5453 | 20015013.5563 | 13660658.0196 | 61093498.3654 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 81312244.2201 | 110632891.6456 | 562341.3252 | 15.5364 | 5233.6642 | 7120.8883 | 106.6953 | 145.1689
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1861 | 41.7491 | 3.9209 | 4 | 5202.6433 | 7072.1441 | 106.0629 | 144.1752 | 138.0021 | 0 | 196.5318 | 6002622.6921 | 269943.7349 | 6659762.8979 | 6457665.4801 | 0 | 426861.7561 | 0 | 7728574.0589 | 20108164.3526 | 13724235.3521 | 61377830.3248 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 81596576.1796 | 110917223.605 | 749894.2093 | 15.6837 | 5202.6433 | 7072.1441 | 106.0629 | 144.1752
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.9755 | 41.9595 | 3.9492 | 4 | 5179.3373 | 7035.4608 | 105.5878 | 143.4274 | 137.9778 | 0 | 205.8355 | 6023438.6282 | 270818.6495 | 6686705.9157 | 6490995.183 | 0 | 415904.2983 | 0 | 7756266.4432 | 20180214.2561 | 13773410.8917 | 61597754.2658 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 81816500.1205 | 111137147.5459 | 1000000 | 15.7967 | 5179.3373 | 7035.4608 | 105.5878 | 143.4274
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.546 | 42.1113 | 3.9701 | 4 | 5161.8351 | 7008.1648 | 105.231 | 142.8709 | 137.9602 | 0 | 216.7021 | 6038440.1893 | 271448.6364 | 6706140.796 | 6515060.9368 | 0 | 407153.7199 | 0 | 7775915.2685 | 20231336.4692 | 13808302.8526 | 61753798.8687 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 81972544.7234 | 111293192.1489 | 1333521.4322 | 15.8805 | 5161.8351 | 7008.1648 | 105.231 | 142.8709
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.9696 | 42.224 | 3.9858 | 4 | 5148.6954 | 6987.7489 | 104.9631 | 142.4547 | 137.947 | 0 | 211.7715 | 6049557.4301 | 271915.2191 | 6720552.7852 | 6532923.0291 | 0 | 400371.1008 | 0 | 7790374.6301 | 20268956.762 | 13833979.4755 | 61868630.4321 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82087376.2868 | 111408023.7122 | 1778279.41 | 15.9433 | 5148.6954 | 6987.7489 | 104.9631 | 142.4547
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.301 | 42.3122 | 3.9979 | 4 | 5138.8332 | 6972.3408 | 104.7621 | 142.1406 | 137.9367 | 0 | 191.466 | 6058242.3442 | 272279.5642 | 6731816.862 | 6546892.9378 | 0 | 395335.3636 | 0 | 7801781.158 | 20298634.2077 | 13854234.942 | 61959217.3795 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82177963.2342 | 111498610.6596 | 2371373.7057 | 15.9916 | 5138.8332 | 6972.3408 | 104.7621 | 142.1406
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5445 | 42.3769 | 4.0069 | 4 | 5131.4326 | 6960.8314 | 104.6112 | 141.906 | 137.9291 | 0 | 177.1085 | 6064618.7393 | 272546.9665 | 6740090.0175 | 6557158.8249 | 0 | 391446.592 | 0 | 7810085.8447 | 20320241.2989 | 13868982.2257 | 62025170.5094 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82243916.3641 | 111564563.7895 | 3162277.6602 | 16.0275 | 5131.4326 | 6960.8314 | 104.6112 | 141.906
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.7077 | 42.4203 | 4.0133 | 4 | 5125.8799 | 6952.357 | 104.498 | 141.7332 | 137.924 | 0 | 190.1374 | 6068886.4584 | 272725.8782 | 6745629.0268 | 6564034.7731 | 0 | 388281.7183 | 0 | 7815427.5634 | 20334139.3553 | 13878467.9348 | 62067592.7084 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82286338.5631 | 111606985.9885 | 4216965.0343 | 16.0531 | 5125.8799 | 6952.357 | 104.498 | 141.7332
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8586 | 42.4604 | 4.0186 | 4 | 5121.7143 | 6945.7789 | 104.4131 | 141.5991 | 137.9193 | 0 | 200.7802 | 6072833.3563 | 272891.3358 | 6750752.1462 | 6570395.8168 | 0 | 386205.5817 | 0 | 7820700.5124 | 20347858.4869 | 13887831.524 | 62109468.76 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82328214.6147 | 111648862.0402 | 5623413.2519 | 16.0743 | 5121.7143 | 6945.7789 | 104.4131 | 141.5991
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.9512 | 42.485 | 4.0222 | 4 | 5118.5896 | 6941.0087 | 104.3494 | 141.5018 | 137.9164 | 0 | 191.4751 | 6075253.0068 | 272992.739 | 6753893.6942 | 6574297.5757 | 0 | 384410.0938 | 0 | 7823730.3727 | 20355741.5619 | 13893211.8847 | 62133530.9286 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82352276.7833 | 111672924.2088 | 7498942.0933 | 16.0889 | 5118.5896 | 6941.0087 | 104.3494 | 141.5018
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.0218 | 42.5037 | 4.025 | 4 | 5116.2458 | 6937.4232 | 104.3016 | 141.4288 | 137.9141 | 0 | 211.3951 | 6077096.0118 | 273069.9694 | 6756286.7881 | 6577270.1841 | 0 | 383069.7983 | 0 | 7826049.1732 | 20361774.6052 | 13897329.5607 | 62151946.0907 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82370691.9454 | 111691339.3708 | 10000000 | 16.0998 | 5116.2458 | 6937.4232 | 104.3016 | 141.4288
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7453 | [19 empty] | 100 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6837 | [19 empty] | 133.3521 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2217 | [19 empty] | 177.8279 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2351 | [19 empty] | 237.1374 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.31894 | 0.0073499 | 4 | 756105.0096 | 1777742.8096 | 15414.2233 | 36241.6917 | 108.5532 | 0 | 255.9428 | 167712.5218 | 6221.6569 | 137655.2992 | 84929.6728 | 0 | 87670.807 | 0 | 188834.0835 | 491307.55 | 335327.4983 | 1499659.0895 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22229254.1793 | 52265090.5339 | 316.2278 | 0.0294 | 756105.0096 | 1777742.8096 | 15414.2233 | 36241.6917
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.46276 | 0.016617 | 4 | 341066.6729 | 792943.4531 | 6953.1055 | 16165.2248 | 115.2939 | 0 | 343.8593 | 225957.6647 | 8796.1522 | 184504.3838 | 107459.8177 | 0 | 99899.9527 | 0 | 244381.0088 | 635829.2554 | 433966.5318 | 1940794.7671 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22670389.857 | 52706226.2116 | 421.6965 | 0.066469 | 341066.6729 | 792943.4531 | 6953.1055 | 16165.2248
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9739 | 0.66701 | 0.030488 | 4 | 190656.1866 | 436948.861 | 3886.7842 | 8907.7935 | 121.1537 | 0 | 449.4285 | 300891.169 | 12214.5251 | 246168.3034 | 139005.9824 | 0 | 115754.4706 | 0 | 317473.4357 | 826000.7569 | 563762.4892 | 2521271.1323 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23250866.2222 | 53286702.5768 | 562.3413 | 0.12195 | 190656.1866 | 436948.861 | 3886.7842 | 8907.7935
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 0.94132 | 0.050118 | 4 | 119571.3844 | 269396.1986 | 2437.6244 | 5492.0059 | 125.8941 | 0 | 69.9889 | 391938.5974 | 16454.0904 | 323220.919 | 180606.4472 | 0 | 134269.7015 | 0 | 408131.0047 | 1061873.155 | 724750.2476 | 3241244.1629 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23970839.2528 | 54006675.6074 | 749.8942 | 0.20047 | 119571.3844 | 269396.1986 | 2437.6244 | 5492.0059
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1884 | 1.3159 | 0.077649 | 4 | 80132.2095 | 176835.5601 | 1633.6035 | 3605.0321 | 129.7349 | 0 | 88.7881 | 504796.3941 | 21785.9227 | 421429.6222 | 237666.294 | 0 | 157215.7776 | 0 | 523728.6642 | 1362634.5526 | 930026.0815 | 4159283.309 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 24888878.3988 | 54924714.7535 | 1000 | 0.3106 | 80132.2095 | 176835.5601 | 1633.6035 | 3605.0321
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8622 | 1.8131 | 0.1149 | 4 | 56624.8893 | 121975.6743 | 1154.375 | 2486.6391 | 132.707 | 0 | 69.4319 | 640713.1554 | 28240.3953 | 543526.1582 | 312826.5302 | 0 | 184510.9364 | 0 | 666828.6985 | 1734951.488 | 1184140.0403 | 5295737.4023 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 26025332.4921 | 56061168.8468 | 1333.5214 | 0.45961 | 56624.8893 | 121975.6743 | 1154.375 | 2486.6391
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1131 | 2.4854 | 0.16553 | 4 | 41485.2084 | 86849.0848 | 845.7321 | 1770.5361 | 135.0397 | 0 | 77.2294 | 807937.4538 | 36198.1693 | 698419.1122 | 414382.8575 | 0 | 218583.2551 | 0 | 848453.1307 | 2207501.0045 | 1506664.7952 | 6738139.7784 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 27467734.8682 | 57503571.2229 | 1778.2794 | 0.66211 | 41485.2084 | 86849.0848 | 845.7321 | 1770.5361
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0969 | 3.3841 | 0.23425 | 4 | 31243.16 | 63298.1975 | 636.9341 | 1290.4194 | 136.9611 | 0 | 74.6688 | 1012091.4644 | 45935.1403 | 892888.3771 | 548715.1527 | 0 | 259428.8043 | 0 | 1076032.9861 | 2799617.1052 | 1910796.2007 | 8545505.2309 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 29275100.3208 | 59310936.6754 | 2371.3737 | 0.93701 | 31243.16 | 63298.1975 | 636.9341 | 1290.4194
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0682 | 4.5795 | 0.3256 | 4 | 24220.0847 | 47282.3149 | 493.7592 | 963.9139 | 138.368 | 0 | 63.2928 | 1259872.2771 | 57708.2327 | 1136296.644 | 728158.1441 | 0 | 309512.8994 | 0 | 1361703.7969 | 3542873.9558 | 2418084.2736 | 10814210.2235 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 31543805.3134 | 61579641.668 | 3162.2777 | 1.3024 | 24220.0847 | 47282.3149 | 493.7592 | 963.9139
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3199 | 6.1623 | 0.44692 | 4 | 19232.24 | 36033.7152 | 392.0752 | 734.596 | 139.4389 | 0 | 89.8605 | 1560177.4058 | 71931.5046 | 1439863.7843 | 965667.2018 | 0 | 370037.9626 | 0 | 1718994.365 | 4472470.7236 | 3052553.1689 | 13651696.1165 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 34381291.2064 | 64417127.561 | 4216.965 | 1.7877 | 19232.24 | 36033.7152 | 392.0752 | 734.596
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2506 | 8.2542 | 0.60754 | 4 | 15610.5067 | 27970.1047 | 318.2413 | 570.2084 | 140.253 | 0 | 86.3965 | 1924298.437 | 89122.7735 | 1818128.45 | 1280467.784 | 0 | 443381.3793 | 0 | 2166605.5413 | 5637063.1865 | 3847411.4549 | 17206479.0066 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 37936074.0964 | 67971910.451 | 5623.4133 | 2.4302 | 15610.5067 | 27970.1047 | 318.2413 | 570.2084
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.3226 | 10.9945 | 0.81812 | 4 | 12944.0166 | 22122.3487 | 263.8813 | 450.994 | 140.8695 | 0 | 93.2393 | 2362721.8484 | 109747.9151 | 2285820.2439 | 1693481.273 | 0 | 531621.7039 | 0 | 2723523.2639 | 7086048.8611 | 4836373.9515 | 21629339.0608 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 42358934.1506 | 72394770.5053 | 7498.9421 | 3.2725 | 12944.0166 | 22122.3487 | 263.8813 | 450.994
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.0548 | 14.5376 | 1.0898 | 4 | 10964.9665 | 17855.3275 | 223.5357 | 364.005 | 141.3278 | 0 | 86.5463 | 2884507.6684 | 134173.2575 | 2857327.1214 | 2226357.7254 | 0 | 636954.6997 | 0 | 3408334.9842 | 8867788.4834 | 6052447.8547 | 27067891.7948 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 47797486.8846 | 77833323.2393 | 10000 | 4.3591 | 10964.9665 | 17855.3275 | 223.5357 | 364.005
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.2345 | 18.8096 | 1.4226 | 4 | 9497.0725 | 14775.5329 | 193.6107 | 301.2192 | 141.6137 | 0 | 101.1816 | 3465971.7669 | 161226.227 | 3510659.1598 | 2869097.8159 | 0 | 748141.1466 | 0 | 4194487.4853 | 10913196.029 | 7448480.5336 | 33311260.164 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 54040855.2539 | 84076691.6085 | 13335.2143 | 5.6903 | 9497.0725 | 14775.5329 | 193.6107 | 301.2192
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.966 | 22.3229 | 1.7519 | 4 | 8394.3221 | 12680.4745 | 171.1296 | 258.5086 | 141.6952 | 0 | 127.0181 | 3914529.2432 | 181931.0448 | 4025887.8433 | 3399002.2655 | 0 | 778204.0144 | 0 | 4796826.2204 | 12480357.8611 | 8518100.6859 | 38094839.1787 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 58824434.2685 | 88860270.6232 | 17782.7941 | 7.0076 | 8394.3221 | 12680.4745 | 171.1296 | 258.5086
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6586 | 25.7938 | 2.0966 | 4 | 7556.4197 | 11137.8496 | 154.0478 | 227.0601 | 141.6628 | 0 | 144.4397 | 4336345.3585 | 201223.3378 | 4519418.3644 | 3924437.9986 | 0 | 786477.9005 | 0 | 5369482.1543 | 13970291.1333 | 9535010.7593 | 42642687.0067 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 63372282.0965 | 93408118.4511 | 23713.7371 | 8.3865 | 7556.4197 | 11137.8496 | 154.0478 | 227.0601
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.723 | 29.0415 | 2.4374 | 4 | 6921.5049 | 10002.2341 | 141.1042 | 203.9091 | 141.5424 | 0 | 167.0354 | 4714498.008 | 218334.3288 | 4969589.5703 | 4418410.0979 | 0 | 773900.9168 | 0 | 5886945.8395 | 15316625.4956 | 10453911.626 | 46752215.8828 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 67481810.9726 | 97517647.3273 | 31622.7766 | 9.7496 | 6921.5049 | 10002.2341 | 141.1042 | 203.9091
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7056 | 31.9357 | 2.7568 | 4 | 6441.4002 | 9165.2156 | 131.3167 | 186.8453 | 141.3681 | 0 | 176.6031 | 5039477.5098 | 232873.1442 | 5362607.0762 | 4860916.3459 | 0 | 744479.2302 | 0 | 6333737.7895 | 16479086.5 | 11247315.1476 | 50300492.7434 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 71030087.8333 | 101065924.1879 | 42169.6503 | 11.0271 | 6441.4002 | 9165.2156 | 131.3167 | 186.8453
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.3755 | 34.4184 | 3.0429 | 4 | 6078.8828 | 8546.5825 | 123.9262 | 174.2336 | 141.1717 | 0 | 190.303 | 5309993.0871 | 244840.66 | 5694341.8732 | 5242526.1994 | 0 | 704207.3745 | 0 | 6706404.5857 | 17448689.0593 | 11909088.8177 | 53260091.6569 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 73989686.7468 | 104025523.1014 | 56234.1325 | 12.1716 | 6078.8828 | 8546.5825 | 123.9262 | 174.2336
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.5787 | 36.4572 | 3.2881 | 4 | 5805.4207 | 8089.1039 | 118.3514 | 164.9073 | 140.9795 | 0 | 177.9679 | 5526788.0344 | 254331.3711 | 5963403.3315 | 5557313.381 | 0 | 657759.1143 | 0 | 7004242.1406 | 18223601.2823 | 12437982.3327 | 55625420.9879 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 76355016.0778 | 106390852.4324 | 74989.4209 | 13.1524 | 5805.4207 | 8089.1039 | 118.3514 | 164.9073
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4714 | 38.1066 | 3.4924 | 4 | 5599.3353 | 7749.4018 | 114.15 | 157.982 | 140.804 | 0 | 186.1842 | 5698641.4468 | 261774.3408 | 6179028.0305 | 5811659.4725 | 0 | 611010.7832 | 0 | 7239224.4888 | 18834977.1508 | 12855258.9255 | 57491574.639 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 78221169.7288 | 108257006.0834 | 100000 | 13.9697 | 5599.3353 | 7749.4018 | 114.15 | 157.982
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1387 | 39.4017 | 3.6578 | 4 | 5444.0291 | 7496.8709 | 110.9839 | 152.8339 | 140.6539 | 0 | 226.7013 | 5831508.2191 | 267482.4547 | 6347116.1134 | 6011912.8956 | 0 | 566535.7626 | 0 | 7419576.6237 | 19304216.4106 | 13175524.3622 | 58923872.842 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 79653467.9319 | 109689304.2865 | 133352.1432 | 14.6313 | 5444.0291 | 7496.8709 | 110.9839 | 152.8339
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7271 | 40.9532 | 3.8247 | 4 | 5325.2226 | 7288.517 | 108.5619 | 148.5863 | 140.4887 | 0 | 198.4093 | 5989160.6861 | 274260.9389 | 6547030.2849 | 6251788.9893 | 0 | 548468.8284 | 0 | 7648176.7937 | 19898987.1606 | 13581467.6204 | 60739341.3022 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 81468936.3921 | 111504772.7467 | 177827.941 | 15.2987 | 5325.2226 | 7288.517 | 108.5619 | 148.5863
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.748 | 41.7882 | 3.9332 | 4 | 5235.6745 | 7144.8081 | 106.7363 | 145.6566 | 140.3981 | 0 | 207.5389 | 6073133.5407 | 277857.3039 | 6654030.5695 | 6381076.7105 | 0 | 515961.5124 | 0 | 7761803.2585 | 20194619.9137 | 13783243.0491 | 61641725.8583 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 82371320.9481 | 112407157.3028 | 237137.3706 | 15.7327 | 5235.6745 | 7144.8081 | 106.7363 | 145.6566
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.0519 | 42.4227 | 4.0171 | 4 | 5168.2571 | 7037.4831 | 105.3619 | 143.4686 | 140.3274 | 0 | 217.6789 | 6136506.6761 | 280562.3243 | 6735069.09 | 6479431.7933 | 0 | 488525.6268 | 0 | 7846837.2491 | 20415860.9145 | 13934244.5781 | 62317038.2522 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 83046633.342 | 113082469.6967 | 316227.766 | 16.0686 | 5168.2571 | 7037.4831 | 105.3619 | 143.4686
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7964 | 42.9019 | 4.0815 | 4 | 5117.5313 | 6957.2654 | 104.3278 | 141.8333 | 140.2729 | 0 | 225.1998 | 6184114.6572 | 282589.1506 | 6796112.7366 | 6553767.8737 | 0 | 465952.4982 | 0 | 7910189.3973 | 20580690.2089 | 14046743.9585 | 62820160.481 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 83549755.5708 | 113585591.9254 | 421696.5034 | 16.3262 | 5117.5313 | 6957.2654 | 104.3278 | 141.8333
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.107 | 43.2611 | 4.1305 | 4 | 5079.3854 | 6897.302 | 103.5501 | 140.6108 | 140.2314 | 0 | 212.1089 | 6219666.4737 | 284099.7056 | 6841791.0933 | 6609532.4033 | 0 | 447703.4321 | 0 | 7957089.3121 | 20702714.1667 | 14130027.817 | 63192624.4038 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 83922219.4937 | 113958055.8483 | 562341.3252 | 16.5221 | 5079.3854 | 6897.302 | 103.5501 | 140.6108
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1035 | 43.5337 | 4.1679 | 4 | 5050.7138 | 6852.3392 | 102.9656 | 139.6942 | 140.1996 | 0 | 173.9404 | 6246575.5395 | 285241.3249 | 6876418.1721 | 6651884.9199 | 0 | 433354.4981 | 0 | 7992455.0373 | 20794728.529 | 14192829.51 | 63473487.5309 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84203082.6208 | 114238918.9754 | 749894.2093 | 16.6715 | 5050.7138 | 6852.3392 | 102.9656 | 139.6942
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8346 | 43.7335 | 4.1958 | 4 | 5029.1727 | 6818.8047 | 102.5265 | 139.0106 | 140.1761 | 0 | 199.1177 | 6266249.2116 | 286075.0148 | 6901764.2875 | 6682929.511 | 0 | 421922.8288 | 0 | 8017986.9329 | 20861157.2842 | 14238168.5004 | 63676253.5712 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84405848.6611 | 114441685.0157 | 1000000 | 16.7832 | 5029.1727 | 6818.8047 | 102.5265 | 139.0106
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.3922 | 43.8858 | 4.217 | 4 | 5012.9949 | 6793.6147 | 102.1967 | 138.497 | 140.158 | 0 | 195.5311 | 6281219.9645 | 286708.8814 | 6921068.0317 | 6706597.8277 | 0 | 413167.9411 | 0 | 8037417.4321 | 20911711.4573 | 14272672.7623 | 63830564.2982 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84560159.3881 | 114595995.7427 | 1333521.4322 | 16.8682 | 5012.9949 | 6793.6147 | 102.1967 | 138.497
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7944 | 43.9955 | 4.2328 | 4 | 5000.8488 | 6774.8625 | 101.9491 | 138.1147 | 140.145 | 0 | 193.7334 | 6291993.2277 | 287164.7172 | 6934968.6823 | 6723654.775 | 0 | 406251.8579 | 0 | 8051172.9714 | 20947500.5489 | 14297099.5527 | 63939806.333 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84669401.4228 | 114705237.7774 | 1778279.41 | 16.931 | 5000.8488 | 6774.8625 | 101.9491 | 138.1147
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.1102 | 44.0816 | 4.2448 | 4 | 4991.7321 | 6760.7003 | 101.7632 | 137.826 | 140.1347 | 0 | 217.476 | 6300445.4268 | 287522.1881 | 6945879.4646 | 6737050.5793 | 0 | 401129.4724 | 0 | 8062090.5812 | 20975905.9301 | 14316486.8091 | 64026510.4516 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84756105.5415 | 114791941.8961 | 2371373.7057 | 16.9793 | 4991.7321 | 6760.7003 | 101.7632 | 137.826
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.342 | 44.1448 | 4.2538 | 4 | 4984.8907 | 6750.1237 | 101.6237 | 137.6104 | 140.1272 | 0 | 221.4309 | 6306638.0328 | 287783.9923 | 6953876.4277 | 6746873.2945 | 0 | 397173.1115 | 0 | 8070014.4949 | 20996522.3283 | 14330557.9244 | 64089439.6064 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84819034.6963 | 114854871.0509 | 3162277.6602 | 17.0152 | 4984.8907 | 6750.1237 | 101.6237 | 137.6104
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.5124 | 44.1912 | 4.2605 | 4 | 4979.7575 | 6742.2198 | 101.5191 | 137.4493 | 140.1216 | 0 | 211.3576 | 6311188.5971 | 287976.3208 | 6959754.561 | 6754095.806 | 0 | 394135.9513 | 0 | 8075788.9821 | 21011546.3592 | 14340812.1343 | 64135298.7117 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84864893.8015 | 114900730.1561 | 4216965.0343 | 17.042 | 4979.7575 | 6742.2198 | 101.5191 | 137.4493
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.6561 | 44.2304 | 4.2658 | 4 | 4975.9065 | 6736.1752 | 101.4406 | 137.326 | 140.1169 | 0 | 220.8659 | 6315024.9223 | 288138.4447 | 6964710.8089 | 6760186.9679 | 0 | 392020.4094 | 0 | 8080831.8058 | 21024666.7521 | 14349767.072 | 64175347.1831 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84904942.2729 | 114940778.6276 | 5623413.2519 | 17.0632 | 4975.9065 | 6736.1752 | 101.4406 | 137.326
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.7487 | 44.2556 | 4.2695 | 4 | 4973.0178 | 6731.7563 | 101.3817 | 137.236 | 140.1139 | 0 | 217.6147 | 6317495.2569 | 288242.8108 | 6967903.0808 | 6764111.1057 | 0 | 390251.732 | 0 | 8083921.5546 | 21032705.6448 | 14355253.7814 | 64199884.9669 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84929480.0568 | 114965316.4114 | 7498942.0933 | 17.0781 | 4973.0178 | 6731.7563 | 101.3817 | 137.236
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.8265 | 44.2768 | 4.2725 | 4 | 4970.851 | 6728.3808 | 101.3375 | 137.1671 | 140.1113 | 0 | 234.3847 | 6319569.9834 | 288330.4624 | 6970584.2625 | 6767407.3446 | 0 | 389014.0129 | 0 | 8086613.3656 | 21039709.1848 | 14360033.8414 | 64221262.4576 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84950857.5474 | 114986693.9021 | 10000000 | 17.0898 | 4970.851 | 6728.3808 | 101.3375 | 137.1671
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8198 | [19 empty] | 100 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6694 | [19 empty] | 133.3521 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4202 | [19 empty] | 177.8279 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7356 | [19 empty] | 237.1374 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.33053 | 0.0087813 | 4 | 648527.544 | 1524231.9898 | 13221.1112 | 31073.5308 | 110.0735 | 0 | 266.3591 | 173511.8182 | 6504.5049 | 141489.8635 | 86259.4171 | 0 | 87288.332 | 0 | 193071.0349 | 502331.2285 | 342851.3853 | 1533307.5844 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 22779612.0003 | 53538841.4113 | 316.2278 | 0.035125 | 648527.544 | 1524231.9898 | 13221.1112 | 31073.5308
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.48966 | 0.019133 | 4 | 304010.5932 | 705933.0095 | 6197.6671 | 14391.3992 | 117.3081 | 0 | 359.4664 | 237696.1956 | 9384.6446 | 192758.9565 | 110956.1795 | 0 | 101300.1709 | 0 | 254317.4974 | 661681.9604 | 451611.5342 | 2019707.139 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23266011.5549 | 54025240.9659 | 421.6965 | 0.07653 | 304010.5932 | 705933.0095 | 6197.6671 | 14391.3992
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 0.69996 | 0.034182 | 4 | 174466.571 | 399430.8413 | 3556.737 | 8142.938 | 123.1244 | 0 | 481.4314 | 314390.398 | 12937.9174 | 255499.6619 | 142901.1184 | 0 | 116437.956 | 0 | 328445.1502 | 854546.9074 | 583245.8235 | 2608404.9327 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23854709.3485 | 54613938.7596 | 562.3413 | 0.13673 | 174466.571 | 399430.8413 | 3556.737 | 8142.938
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 0.98733 | 0.05564 | 4 | 110539.9319 | 248746.1156 | 2253.506 | 5071.026 | 127.9311 | 0 | 66.2597 | 409442.313 | 17439.9225 | 335321.1391 | 186285.7557 | 0 | 134893.8259 | 0 | 422519.3529 | 1099308.6856 | 750300.7665 | 3355511.7612 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 24601816.1771 | 55361045.5881 | 749.8942 | 0.22256 | 110539.9319 | 248746.1156 | 2253.506 | 5071.026
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2958 | 1.3832 | 0.085711 | 4 | 74555.9371 | 164273.8931 | 1519.9236 | 3348.9455 | 131.8638 | 0 | 74.8856 | 528101.6794 | 23133.8476 | 437967.9548 | 245507.2351 | 0 | 158369.7435 | 0 | 543301.3795 | 1413558.7431 | 964782.8879 | 4314723.4709 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 25561027.8868 | 56320257.2978 | 1000 | 0.34284 | 74555.9371 | 164273.8931 | 1519.9236 | 3348.9455
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9937 | 1.9029 | 0.1262 | 4 | 52961.3292 | 113892.8611 | 1079.6883 | 2321.86 | 134.8619 | 0 | 76.5143 | 669530.1017 | 29963.9974 | 564121.9448 | 323253.9229 | 0 | 185486.3335 | 0 | 691218.9571 | 1798409.938 | 1227451.7363 | 5489436.9318 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 26735741.3477 | 57494970.7587 | 1333.5214 | 0.50482 | 52961.3292 | 113892.8611 | 1079.6883 | 2321.86
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 2.6074 | 0.18152 | 4 | 38877.5322 | 81241.5888 | 792.5711 | 1656.2197 | 137.2985 | 0 | 70.9807 | 844188.2931 | 38424.0553 | 724631.5249 | 427523.3692 | 0 | 219316.0497 | 0 | 879092.4839 | 2287218.3165 | 1561073.4987 | 6981467.5912 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 28227772.0071 | 58987001.4181 | 1778.2794 | 0.72607 | 38877.5322 | 81241.5888 | 792.5711 | 1656.2197
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 3.5474 | 0.25593 | 4 | 29401.7424 | 59447.7532 | 599.3943 | 1211.9229 | 139.189 | 0 | 76.2815 | 1056770.3715 | 48725.0458 | 925827.9954 | 566803.5985 | 0 | 260329.0636 | 0 | 1114797.8692 | 2900475.3791 | 1979634.045 | 8853363.368 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 30099667.7839 | 60858897.1949 | 2371.3737 | 1.0237 | 29401.7424 | 59447.7532 | 599.3943 | 1211.9229
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.348 | 4.7998 | 0.35545 | 4 | 22826.4619 | 44460.2047 | 465.3483 | 906.3814 | 140.6192 | 0 | 79.4256 | 1315653.4717 | 61250.5105 | 1178027.7925 | 753602.8703 | 0 | 310398.4877 | 0 | 1411383.9217 | 3672131.4497 | 2506305.1692 | 11208753.6733 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 32455058.0892 | 63214287.5002 | 3162.2777 | 1.4218 | 22826.4619 | 44460.2047 | 465.3483 | 906.3814
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6754 | 6.4554 | 0.4874 | 4 | 18154.7221 | 33931.8573 | 370.1086 | 691.7468 | 141.7076 | 0 | 82.6281 | 1628847.3957 | 76346.7279 | 1492093.2234 | 999981.2048 | 0 | 370742.0323 | 0 | 1781524.1278 | 4635160.3397 | 3163592.1749 | 14148287.2266 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 35394591.6425 | 66153821.0535 | 4216.965 | 1.9496 | 18154.7221 | 33931.8573 | 370.1086 | 691.7468
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.7259 | 8.6476 | 0.66196 | 4 | 14759.2834 | 26376.0629 | 300.888 | 537.7117 | 142.5379 | 0 | 79.8435 | 2009124.0269 | 94599.6913 | 1884228.7299 | 1325580.6781 | 0 | 444385.1935 | 0 | 2245588.1447 | 5842559.719 | 3987667.0608 | 17833733.2441 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 39080037.66 | 69839267.071 | 5623.4133 | 2.6478 | 14759.2834 | 26376.0629 | 300.888 | 537.7117
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.9365 | 11.5131 | 0.89033 | 4 | 12257.5802 | 20894.645 | 249.8874 | 425.9656 | 143.1655 | 0 | 73.7044 | 2465966.0872 | 116440.1948 | 2368052.2047 | 1751248.2173 | 0 | 532666.2217 | 0 | 2821405.441 | 7340718.2077 | 5010191.0135 | 22406687.588 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 43652992.0038 | 74412221.4149 | 7498.9421 | 3.5613 | 12257.5802 | 20894.645 | 249.8874 | 425.9656
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8396 | 15.2165 | 1.185 | 4 | 10396.7492 | 16886.1732 | 211.9518 | 344.2475 | 143.6307 | 0 | 92.883 | 3009795.188 | 142326.6909 | 2959053.1756 | 2301714.7557 | 0 | 638116.1117 | 0 | 3529892.3095 | 9184055.7088 | 6268306.7347 | 28033260.6748 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 49279565.0907 | 80038794.5017 | 10000 | 4.7399 | 10396.7492 | 16886.1732 | 211.9518 | 344.2475
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.8548 | 19.8758 | 1.5536 | 4 | 9017.28 | 13966.815 | 183.8294 | 284.7324 | 143.9237 | 0 | 98.2959 | 3641200.8137 | 172186.8594 | 3663320.4174 | 2994966.6227 | 0 | 761570.4393 | 0 | 4380965.6095 | 11398373.8562 | 7779624.37 | 34792208.9881 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 56038513.4039 | 86797742.815 | 13335.2143 | 6.2146 | 9017.28 | 13966.815 | 183.8294 | 284.7324
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.8554 | 23.881 | 1.9218 | 4 | 7997.1815 | 11998.4967 | 163.0334 | 244.6056 | 143.9916 | 0 | 131.761 | 4148475.295 | 195955.7029 | 4242647.1425 | 3592476.7263 | 0 | 809457.7278 | 0 | 5065714.9119 | 13179951.0797 | 8995587.4328 | 40230266.019 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 61476570.4349 | 92235799.8459 | 17782.7941 | 7.6873 | 7997.1815 | 11998.4967 | 163.0334 | 244.6056
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.5823 | 27.4571 | 2.2875 | 4 | 7223.4269 | 10585.0874 | 147.2593 | 215.7913 | 143.9326 | 0 | 140.7606 | 4578933.2912 | 215911.6986 | 4743905.3794 | 4127987.1766 | 0 | 813229.6435 | 0 | 5647187.2038 | 14692822.707 | 10028153.4048 | 44848130.505 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 66094434.9208 | 96853664.3319 | 23713.7371 | 9.15 | 7223.4269 | 10585.0874 | 147.2593 | 215.7913
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.5903 | 30.7738 | 2.6454 | 4 | 6637.2305 | 9544.1407 | 135.3089 | 194.5702 | 143.7883 | 0 | 169.2541 | 4961794.6796 | 233454.7207 | 5197550.3231 | 4626878.5337 | 0 | 795946.6982 | 0 | 6168093.7326 | 16048114.6421 | 10953167.999 | 48985001.329 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 70231305.7449 | 100990535.1559 | 31622.7766 | 10.5814 | 6637.2305 | 9544.1407 | 135.3089 | 194.5702
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4512 | 33.7064 | 2.9777 | 4 | 6193.9446 | 8776.3785 | 126.2719 | 178.9183 | 143.595 | 0 | 166.8684 | 5288555.9657 | 248244.8333 | 5590883.3891 | 5070172.5916 | 0 | 762146.0843 | 0 | 6614401.117 | 17209314.9061 | 11745711.0395 | 52529429.9266 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 73775734.3424 | 104534963.7535 | 42169.6503 | 11.9109 | 6193.9446 | 8776.3785 | 126.2719 | 178.9183
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.9501 | 36.2018 | 3.273 | 4 | 5859.1591 | 8208.646 | 119.4469 | 167.3444 | 143.385 | 0 | 210.8003 | 5558580.4056 | 260321.6704 | 5920469.0497 | 5449226.6512 | 0 | 717968.0295 | 0 | 6983560.6645 | 18169792.3237 | 12401256.6128 | 55461175.4074 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 76707479.8233 | 107466709.2343 | 56234.1325 | 13.0919 | 5859.1591 | 8208.646 | 119.4469 | 167.3444
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.042 | 38.2597 | 3.5255 | 4 | 5606.5399 | 7787.7128 | 114.2969 | 158.7631 | 143.1814 | 0 | 186.9193 | 5776026.9785 | 269940.3463 | 6189053.9321 | 5763247.0129 | 0 | 669227.2977 | 0 | 7280323.2713 | 18941907.7523 | 12928241.2582 | 57817967.8493 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 79064272.2652 | 109823501.6762 | 74989.4209 | 14.1022 | 5606.5399 | 7787.7128 | 114.2969 | 158.7631
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.7929 | 39.9113 | 3.7348 | 4 | 5416.0373 | 7474.979 | 110.4132 | 152.3876 | 142.9987 | 0 | 210.5189 | 5947267.9049 | 277441.9932 | 6402671.1338 | 6016302.0085 | 0 | 620390.0205 | 0 | 7512988.4937 | 19547254.9349 | 13341403.149 | 59665719.6385 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 80912024.0543 | 111671253.4654 | 100000 | 14.9393 | 5416.0373 | 7474.979 | 110.4132 | 152.3876
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.1802 | 41.7362 | 3.9379 | 4 | 5271.42 | 7224.18 | 107.465 | 147.2747 | 142.7959 | 0 | 203.2891 | 6133817.0981 | 285584.4596 | 6636722.4908 | 6297000.3404 | 0 | 595955.3826 | 0 | 7780141.1109 | 20242331.2441 | 13815807.0124 | 61787359.139 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 83033663.5549 | 113792892.9659 | 133352.1432 | 15.7517 | 5271.42 | 7224.18 | 107.465 | 147.2747
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9781 | 42.8192 | 4.0789 | 4 | 5161.4068 | 7046.662 | 105.2223 | 143.6557 | 142.6798 | 0 | 201.7414 | 6243337.0773 | 290356.8432 | 6774656.5277 | 6463720.3413 | 0 | 557418.1492 | 0 | 7928500.6861 | 20628332.426 | 14079260.7506 | 62965582.8014 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 84211887.2172 | 114971116.6283 | 177827.941 | 16.3157 | 5161.4068 | 7046.662 | 105.2223 | 143.6557
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8887 | 43.6453 | 4.189 | 4 | 5078.5196 | 6914.2476 | 103.5325 | 140.9563 | 142.5882 | 0 | 202.2718 | 6326174.1425 | 293951.293 | 6879445.0975 | 6591159.1901 | 0 | 523900.1456 | 0 | 8039705.6488 | 20917664.9278 | 14276736.1283 | 63848736.5737 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 85095040.9895 | 115854270.4006 | 237137.3706 | 16.7559 | 5078.5196 | 6914.2476 | 103.5325 | 140.9563
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.113 | 44.2744 | 4.2741 | 4 | 5016.1118 | 6815.2638 | 102.2602 | 138.9384 | 142.5165 | 0 | 203.1492 | 6388845.7043 | 296661.7907 | 6958992.1529 | 6688351.8381 | 0 | 495834.8507 | 0 | 8123187.6713 | 21134868.0258 | 14424981.7057 | 64511723.7395 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 85758028.1554 | 116517257.5664 | 316227.766 | 17.0965 | 5016.1118 | 6815.2638 | 102.2602 | 138.9384
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.7844 | 44.7459 | 4.3391 | 4 | 4969.152 | 6741.3478 | 101.3029 | 137.4315 | 142.4619 | 0 | 220.2996 | 6435581.6448 | 298677.9513 | 7018465.1939 | 6761272.7442 | 0 | 472692.4288 | 0 | 8184809.0856 | 21295194.3055 | 14534407.686 | 65001101.0402 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 86247405.456 | 117006634.8671 | 421696.5034 | 17.3566 | 4969.152 | 6741.3478 | 101.3029 | 137.4315
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.0561 | 45.1038 | 4.3889 | 4 | 4933.8361 | 6685.9544 | 100.5829 | 136.3022 | 142.4197 | 0 | 195.5945 | 6470938.3879 | 300200.2774 | 7063545.0463 | 6816691.4053 | 0 | 454233.8313 | 0 | 8231187.4898 | 21415861.3997 | 14616765.4572 | 65369423.2949 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 86615727.7108 | 117374957.1218 | 562341.3252 | 17.5555 | 4933.8361 | 6685.9544 | 100.5829 | 136.3022
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.9964 | 45.3681 | 4.4263 | 4 | 4907.2905 | 6644.6057 | 100.0418 | 135.4593 | 142.3883 | 0 | 214.4707 | 6496969.1409 | 301319.4027 | 7096783.0363 | 6857633.0676 | 0 | 439442.032 | 0 | 8264937.205 | 21503671.2357 | 14676697.4746 | 65637452.5948 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 86883757.0107 | 117642986.4217 | 749894.2093 | 17.705 | 4907.2905 | 6644.6057 | 100.0418 | 135.4593
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.7144 | 45.5697 | 4.4547 | 4 | 4887.3464 | 6613.5512 | 99.6352 | 134.8262 | 142.3642 | 0 | 230.5471 | 6516781.7436 | 302170.2789 | 7122108.4727 | 6888873.8223 | 0 | 428021.6494 | 0 | 8290602.8271 | 21570447.9196 | 14722273.9335 | 65841280.6472 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87087585.0631 | 117846814.4741 | 1000000 | 17.819 | 4887.3464 | 6613.5512 | 99.6352 | 134.8262
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.246 | 45.7188 | 4.4761 | 4 | 4872.3676 | 6590.3385 | 99.3298 | 134.353 | 142.3463 | 0 | 234.6765 | 6531414.2614 | 302798.1544 | 7140828.1022 | 6911991.512 | 0 | 419097.2266 | 0 | 8309390.41 | 21619329.3566 | 14755636.5187 | 65990485.5418 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87236789.9577 | 117996019.3687 | 1333521.4322 | 17.9044 | 4872.3676 | 6590.3385 | 99.3298 | 134.353
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.6307 | 45.8266 | 4.4919 | 4 | 4861.1215 | 6573.0449 | 99.1005 | 134.0004 | 142.3332 | 0 | 224.1263 | 6541983.73 | 303251.3895 | 7154358.3119 | 6928714.317 | 0 | 412079.0649 | 0 | 8322750.8572 | 21654090.4994 | 14779361.7129 | 66096589.8826 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87342894.2985 | 118102123.7095 | 1778279.41 | 17.9676 | 4861.1215 | 6573.0449 | 99.1005 | 134.0004
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9324 | 45.9111 | 4.5041 | 4 | 4852.6801 | 6559.9873 | 98.9284 | 133.7342 | 142.323 | 0 | 214.7702 | 6550263.5453 | 303606.2912 | 7164962.0304 | 6941827.8339 | 0 | 406873.6659 | 0 | 8333338.013 | 21681636.1071 | 14798162.1562 | 66180669.6429 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87426974.0588 | 118186203.4698 | 2371373.7057 | 18.0162 | 4852.6801 | 6559.9873 | 98.9284 | 133.7342
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.1519 | 45.9725 | 4.5131 | 4 | 4846.3454 | 6550.2478 | 98.7993 | 133.5357 | 142.3155 | 0 | 196.6285 | 6556279.993 | 303864.0781 | 7172669.9269 | 6951364.6038 | 0 | 402836.6864 | 0 | 8340935.9624 | 21701404.4129 | 14811654.4311 | 66241010.0946 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87487314.5105 | 118246543.9215 | 3162277.6602 | 18.0522 | 4846.3454 | 6550.2478 | 98.7993 | 133.5357
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3151 | 46.0182 | 4.5198 | 4 | 4841.5923 | 6542.9563 | 98.7024 | 133.387 | 142.3099 | 0 | 209.9981 | 6560749.3366 | 304055.5247 | 7178397.2567 | 6958453.2869 | 0 | 399761.3286 | 0 | 8346552.5261 | 21716017.5595 | 14821628.2039 | 66285615.0229 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87531919.4388 | 118291148.8498 | 4216965.0343 | 18.0792 | 4841.5923 | 6542.9563 | 98.7024 | 133.387
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.4466 | 46.055 | 4.525 | 4 | 4838.0265 | 6537.424 | 98.6297 | 133.2742 | 142.3054 | 0 | 213.9266 | 6564349.7051 | 304209.7283 | 7183011.7254 | 6964165.926 | 0 | 397543.0821 | 0 | 8351179.2651 | 21728055.3853 | 14829844.2673 | 66322359.0845 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87568663.5004 | 118327892.9114 | 5623413.2519 | 18.1001 | 4838.0265 | 6537.424 | 98.6297 | 133.2742
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.5392 | 46.0809 | 4.5288 | 4 | 4835.3517 | 6533.3189 | 98.5752 | 133.1905 | 142.3023 | 0 | 211.2276 | 6566883.8272 | 304318.2413 | 7186260.2278 | 6968188.4037 | 0 | 395799.8349 | 0 | 8354365.7086 | 21736345.8578 | 14835502.6852 | 66347664.7865 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87593969.2023 | 118353198.6134 | 7498942.0933 | 18.1153 | 4835.3517 | 6533.3189 | 98.5752 | 133.1905
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6124 | 46.1014 | 4.5318 | 4 | 4833.3453 | 6530.2144 | 98.5343 | 133.1273 | 142.2998 | 0 | 207.4656 | 6568885.2937 | 304403.9404 | 7188826.119 | 6971366.039 | 0 | 394529.8528 | 0 | 8356924.3855 | 21743003.0102 | 14840046.3285 | 66367984.969 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87614289.3848 | 118373518.7959 | 10000000 | 18.127 | 4833.3453 | 6530.2144 | 98.5343 | 133.1273
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8249 | [19 empty] | 100 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4373 | [19 empty] | 133.3521 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0821 | [19 empty] | 177.8279 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.354 | [19 empty] | 237.1374 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.34799 | 0.010402 | 4 | 561347.0184 | 1318187.7361 | 11443.8182 | 26873.04 | 111.9046 | 0 | 269.5697 | 181817.7562 | 6904.2052 | 147242.1932 | 88576.0812 | 0 | 88107.4129 | 0 | 199932.5829 | 520183.569 | 355035.9745 | 1587799.7751 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23356673.6078 | 54847500.2025 | 316.2278 | 0.041608 | 561347.0184 | 1318187.7361 | 11443.8182 | 26873.04
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.51174 | 0.021648 | 4 | 275438.5288 | 639114.5899 | 5615.187 | 13029.2154 | 119.1217 | 0 | 370.5837 | 247547.0325 | 9897.5399 | 199426.0641 | 113614.2951 | 0 | 101541.5951 | 0 | 262090.3454 | 681905.3166 | 465414.3903 | 2081436.5789 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23850310.4116 | 55341137.0063 | 421.6965 | 0.08659 | 275438.5288 | 639114.5899 | 5615.187 | 13029.2154
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0906 | 0.73392 | 0.038081 | 4 | 160618.2171 | 367353.8572 | 3274.4196 | 7489.0053 | 125.0935 | 0 | 488.5421 | 328219.492 | 13692.1956 | 265011.7091 | 146838.4691 | 0 | 117060.0829 | 0 | 339620.56 | 883623.0313 | 603090.8755 | 2697156.4155 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 24466030.2482 | 55956856.8429 | 562.3413 | 0.15232 | 160618.2171 | 367353.8572 | 3274.4196 | 7489.0053
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0849 | 1.0404 | 0.061652 | 4 | 102413.0868 | 230109.8494 | 2087.8293 | 4691.1005 | 130.042 | 0 | 66.63 | 429112.1935 | 18551.0209 | 349167.3193 | 192630.9772 | 0 | 136322.616 | 0 | 439055.8095 | 1142333.1536 | 779665.8499 | 3486838.9399 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 25255712.7727 | 56746539.3673 | 749.8942 | 0.24661 | 102413.0868 | 230109.8494 | 2087.8293 | 4691.1005
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3884 | 1.4483 | 0.094072 | 4 | 69712.7268 | 153401.1939 | 1421.1882 | 3127.2908 | 133.956 | 0 | 72.8877 | 550831.6607 | 24491.9446 | 453730.5538 | 253095.5593 | 0 | 158827.7383 | 0 | 561981.2081 | 1462159.8253 | 997954.1252 | 4463072.6153 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 26231946.448 | 57722773.0426 | 1000 | 0.37629 | 69712.7268 | 153401.1939 | 1421.1882 | 3127.2908
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1354 | 1.9979 | 0.13813 | 4 | 49701.0353 | 106697.3379 | 1013.2228 | 2175.1696 | 137.0267 | 0 | 63.579 | 699616.5839 | 31788.2703 | 585702.73 | 333693.5872 | 0 | 186720.4015 | 0 | 716633.4134 | 1864533.1399 | 1272582.1803 | 5691270.3064 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 27460144.1392 | 58950970.7338 | 1333.5214 | 0.55251 | 49701.0353 | 106697.3379 | 1013.2228 | 2175.1696
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4421 | 2.7318 | 0.19817 | 4 | 36582.7066 | 76310.3517 | 745.788 | 1555.6897 | 139.5122 | 0 | 82.4115 | 880998.7072 | 40736.9923 | 751040.4029 | 441335.6924 | 0 | 219911.1924 | 0 | 910268.965 | 2368333.1251 | 1616436.0223 | 7229061.0996 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 28997934.9323 | 60488761.527 | 1778.2794 | 0.79267 | 36582.7066 | 76310.3517 | 745.788 | 1555.6897
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5379 | 3.72 | 0.27918 | 4 | 27715.385 | 55914.6089 | 565.0156 | 1139.8949 | 141.4176 | 0 | 80.8169 | 1103801.2447 | 51731.7229 | 960229.9383 | 587340.2272 | 0 | 261341.5857 | 0 | 1156133.4403 | 3008022.0562 | 2053036.862 | 9181637.0774 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 30950510.9101 | 62441337.5048 | 2371.3737 | 1.1167 | 27715.385 | 55914.6089 | 565.0156 | 1139.8949
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6259 | 5.0263 | 0.38675 | 4 | 21576.5787 | 41932.8323 | 439.8677 | 854.8575 | 142.8671 | 0 | 73.7532 | 1372699.3202 | 64954.9057 | 1220457.679 | 779245.4507 | 0 | 311053.1425 | 0 | 1461880.0942 | 3803512.1324 | 2595975.1847 | 11609777.9094 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 33378651.7421 | 64869478.3368 | 3162.2777 | 1.547 | 21576.5787 | 41932.8323 | 439.8677 | 854.8575
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.058 | 6.7647 | 0.53006 | 4 | 17184.0088 | 32036.3938 | 350.3193 | 653.1052 | 143.9777 | 0 | 72.9022 | 1700446.9168 | 81026.2439 | 1546680.0804 | 1034961.9757 | 0 | 371914.2594 | 0 | 1846661.4957 | 4804634.4094 | 3279261.7098 | 14665587.091 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 36434460.9238 | 67925287.5184 | 4216.965 | 2.1203 | 17184.0088 | 32036.3938 | 350.3193 | 653.1052
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2058 | 9.0537 | 0.71901 | 4 | 13992.3932 | 24941.7344 | 285.2539 | 508.471 | 144.8203 | 0 | 88.4654 | 2096201.1806 | 100350.0322 | 1951714.0705 | 1371107.2534 | 0 | 445239.1146 | 0 | 2326198.544 | 6052291.4426 | 4130813.2717 | 18473914.9096 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 40242788.7424 | 71733615.337 | 5623.4133 | 2.876 | 13992.3932 | 24941.7344 | 285.2539 | 508.471
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5601 | 12.0482 | 0.96584 | 4 | 11639.0199 | 19790.1412 | 237.2772 | 403.4488 | 145.459 | 0 | 89.214 | 2571822.8449 | 123451.4499 | 2451998.3561 | 1808666.3633 | 0 | 533602.1827 | 0 | 2920921.0668 | 7599637.4525 | 5186908.7183 | 23197008.4345 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 44965882.2673 | 76456708.8619 | 7498.9421 | 3.8634 | 11639.0199 | 19790.1412 | 237.2772 | 403.4488
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6205 | 15.9079 | 1.2834 | 4 | 9887.3313 | 16021.6131 | 201.5666 | 326.6223 | 145.9302 | 0 | 107.3893 | 3136447.2014 | 150739.828 | 3061570.338 | 2371885.011 | 0 | 638789.1048 | 0 | 3650178.2785 | 9497015.1261 | 6481907.9677 | 28988532.8557 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 50757406.6884 | 82248233.283 | 10000 | 5.1336 | 9887.3313 | 16021.6131 | 201.5666 | 326.6223
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.817 | 20.7595 | 1.6806 | 4 | 8586.2943 | 13270.8841 | 175.0432 | 270.5449 | 146.2217 | 0 | 80.4284 | 3791971.4433 | 182238.5173 | 3787430.7609 | 3083336.5028 | 0 | 762097.6824 | 0 | 4526759.2136 | 11777698.9077 | 8038521.512 | 35950054.54 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 57718928.3727 | 89209754.9674 | 13335.2143 | 6.7222 | 8586.2943 | 13270.8841 | 175.0432 | 270.5449
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.7083 | 25.4747 | 2.0996 | 4 | 7634.8129 | 11384.4102 | 155.646 | 232.0866 | 146.2781 | 0 | 111.8941 | 4385331.093 | 210454.4507 | 4461094.738 | 3777271.9508 | 0 | 839821.2047 | 0 | 5332849.6405 | 13874980.8467 | 9469959.5302 | 42351763.4547 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 64120637.2875 | 95611463.8821 | 17782.7941 | 8.3985 | 7634.8129 | 11384.4102 | 155.646 | 232.0866
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.4593 | 29.1519 | 2.486 | 4 | 6918.3982 | 10085.1604 | 141.0409 | 205.5996 | 146.1921 | 0 | 119.1952 | 4823817.7961 | 231046.948 | 4969498.4404 | 4320641.9665 | 0 | 839048.0759 | 0 | 5921780.7585 | 15407258.8094 | 10515770.7249 | 47028863.5197 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 68797737.3524 | 100288563.9471 | 23713.7371 | 9.9442 | 6918.3982 | 10085.1604 | 141.0409 | 205.5996
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.3944 | 32.5303 | 2.8604 | 4 | 6375.7594 | 9128.0762 | 129.9785 | 186.0882 | 146.0244 | 0 | 159.4095 | 5210510.5649 | 248977.8321 | 5425733.6599 | 4822083.2591 | 0 | 816954.8996 | 0 | 6444461.4841 | 16767166.8408 | 11443935.8997 | 51179824.4402 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 72948698.273 | 104439524.8676 | 31622.7766 | 11.4416 | 6375.7594 | 9128.0762 | 129.9785 | 186.0882
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2233 | 35.5292 | 3.2077 | 4 | 5965.1067 | 8419.4572 | 121.6068 | 171.642 | 145.8103 | 0 | 191.3366 | 5542469.1941 | 264202.5898 | 5823105.9939 | 5272539.049 | 0 | 780160.6397 | 0 | 6896166.2119 | 17942409.8852 | 12246063.4263 | 54767116.9899 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 76535990.8227 | 108026817.4173 | 42169.6503 | 12.8306 | 5965.1067 | 8419.4572 | 121.6068 | 171.642
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.5714 | 38.0444 | 3.513 | 4 | 5654.9321 | 7895.9776 | 115.2834 | 160.9702 | 145.586 | 0 | 179.4568 | 5813201.0746 | 276477.7442 | 6151478.7735 | 5653737.0646 | 0 | 732369.8646 | 0 | 7264633.1634 | 18901085.3099 | 12900379.1025 | 57693362.0971 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 79462235.9298 | 110953062.5245 | 56234.1325 | 14.0518 | 5654.9321 | 7895.9776 | 115.2834 | 160.9702
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.4897 | 40.1049 | 3.7725 | 4 | 5420.8857 | 7507.7378 | 110.5121 | 153.0554 | 145.3729 | 0 | 205.6685 | 6030031.2297 | 286204.6869 | 6417452.5915 | 5968360.2684 | 0 | 680569.7567 | 0 | 7559221.228 | 19667543.0257 | 13423502.2427 | 60032885.0297 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 81801758.8625 | 113292585.4571 | 74989.4209 | 15.0901 | 5420.8857 | 7507.7378 | 110.5121 | 153.0554
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.0728 | 41.7513 | 3.9866 | 4 | 5244.3839 | 7219.1601 | 106.9139 | 147.1723 | 145.1842 | 0 | 207.4442 | 6200193.387 | 293767.6032 | 6628131.6014 | 6221382.093 | 0 | 629332.4117 | 0 | 7789394.7675 | 20266407.3605 | 13832239.4566 | 61860848.6808 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 83629722.5136 | 115120549.1082 | 100000 | 15.9465 | 5244.3839 | 7219.1601 | 106.9139 | 147.1723
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4628 | 43.6333 | 4.1988 | 4 | 5109.3188 | 6984.3135 | 104.1604 | 142.3847 | 144.9826 | 0 | 219.5466 | 6392331.6186 | 302299.0766 | 6866955.9802 | 6510542.3058 | 0 | 605198.2595 | 0 | 8064157.6239 | 20981283.9512 | 14320157.419 | 64042926.2349 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 85811800.0676 | 117302626.6622 | 133352.1432 | 16.7952 | 5109.3188 | 6984.3135 | 104.1604 | 142.3847
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1434 | 44.7091 | 4.342 | 4 | 5007.3584 | 6820.5237 | 102.0818 | 139.0456 | 144.8645 | 0 | 229.2796 | 6500681.3269 | 307073.4818 | 7002623.4759 | 6674511.1287 | 0 | 565468.7399 | 0 | 8209639.6797 | 21359798.418 | 14578501.3203 | 65198297.5711 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 86967171.4039 | 118457997.9985 | 177827.941 | 17.3679 | 5007.3584 | 6820.5237 | 102.0818 | 139.0456
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.9692 | 45.5314 | 4.4537 | 4 | 4930.5262 | 6698.2219 | 100.5154 | 136.5523 | 144.7713 | 0 | 196.4257 | 6582811.0706 | 310676.9291 | 7105903.1636 | 6800075.6277 | 0 | 531228.9857 | 0 | 8318971.3529 | 21644257.0045 | 14772650.1506 | 66066574.2847 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 87835448.1174 | 119326274.712 | 237137.3706 | 17.8146 | 4930.5262 | 6698.2219 | 100.5154 | 136.5523
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1204 | 46.1551 | 4.5398 | 4 | 4872.6694 | 6606.8126 | 99.336 | 134.6888 | 144.6988 | 0 | 208.1522 | 6644720.1328 | 313384.0708 | 7184011.9714 | 6895463.886 | 0 | 502597.9418 | 0 | 8400669.4211 | 21856818.6195 | 14917727.8205 | 66715393.8641 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 88484267.6968 | 119975094.2915 | 316227.766 | 18.1593 | 4872.6694 | 6606.8126 | 99.336 | 134.6888
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7406 | 46.6236 | 4.6056 | 4 | 4829.1293 | 6538.4956 | 98.4483 | 133.2961 | 144.6434 | 0 | 210.624 | 6691006.7753 | 315402.84 | 7242557.0075 | 6967201.5359 | 0 | 479127.2524 | 0 | 8461165.2103 | 22014216.2537 | 15025154.94 | 67195831.8151 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 88964705.6479 | 120455532.2425 | 421696.5034 | 18.4225 | 4829.1293 | 6538.4956 | 98.4483 | 133.2961
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.9682 | 46.9778 | 4.6558 | 4 | 4796.382 | 6487.3205 | 97.7807 | 132.2528 | 144.601 | 0 | 218.5312 | 6725878.141 | 316920.7409 | 7286747.1292 | 7021486.4654 | 0 | 460390.5489 | 0 | 8506454.9799 | 22132050.944 | 15105579.5374 | 67555508.4869 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 89324382.3196 | 120815208.9143 | 562341.3252 | 18.6233 | 4796.382 | 6487.3205 | 97.7807 | 132.2528
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.8741 | 47.2388 | 4.6935 | 4 | 4771.7652 | 6449.123 | 97.2789 | 131.4741 | 144.5694 | 0 | 214.0217 | 6751504.2644 | 318034.522 | 7319267.9927 | 7061512.1118 | 0 | 445391.064 | 0 | 8539326.8824 | 22217576.8913 | 15163952.7538 | 67816566.4824 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 89585440.3152 | 121076266.9098 | 749894.2093 | 18.7741 | 4771.7652 | 6449.123 | 97.2789 | 131.4741
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.5586 | 47.4358 | 4.7221 | 4 | 4753.2688 | 6420.4794 | 96.9018 | 130.8902 | 144.5453 | 0 | 219.8052 | 6770808.8018 | 318872.6139 | 7343792.3933 | 7091738.2645 | 0 | 433739.6174 | 0 | 8563991.1594 | 22281748.2807 | 15207751.0457 | 68012442.1767 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 89781316.0095 | 121272142.6041 | 1000000 | 18.8883 | 4753.2688 | 6420.4794 | 96.9018 | 130.8902
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0682 | 47.5823 | 4.7435 | 4 | 4739.3765 | 6399.0457 | 96.6186 | 130.4532 | 144.5274 | 0 | 217.2584 | 6785143.5256 | 319494.4127 | 7362017.8131 | 7114224.6554 | 0 | 424682.6512 | 0 | 8582169.5926 | 22329044.835 | 15240031.9159 | 68156809.4016 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 89925683.2343 | 121416509.829 | 1333521.4322 | 18.9742 | 4739.3765 | 6399.0457 | 96.6186 | 130.4532
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4406 | 47.6893 | 4.7595 | 4 | 4728.9459 | 6383.049 | 96.406 | 130.1271 | 144.5142 | 0 | 224.4082 | 6795603.6068 | 319947.8429 | 7375325.0275 | 7130655.8944 | 0 | 417616.5679 | 0 | 8595268.0864 | 22363124.4289 | 15263291.939 | 68260833.3938 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90029707.2266 | 121520533.8212 | 1778279.41 | 19.038 | 4728.9459 | 6383.049 | 96.406 | 130.1271
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7307 | 47.7726 | 4.7717 | 4 | 4721.1164 | 6370.9842 | 96.2463 | 129.8811 | 144.5039 | 0 | 221.6223 | 6803738.873 | 320300.3431 | 7385678.9801 | 7143447.8158 | 0 | 412351.2193 | 0 | 8605551.7202 | 22389880.3345 | 15281553.3943 | 68342502.6802 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90111376.513 | 121602203.1076 | 2371373.7057 | 19.0869 | 4721.1164 | 6370.9842 | 96.2463 | 129.8811
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.9398 | 47.8326 | 4.7807 | 4 | 4715.2407 | 6361.9971 | 96.1266 | 129.6979 | 144.4965 | 0 | 218.5582 | 6809598.29 | 320554.1292 | 7393139.0931 | 7152668.682 | 0 | 408250.0269 | 0 | 8612841.9863 | 22408848.1115 | 15294499.2919 | 68400399.6108 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90169273.4436 | 121660100.0382 | 3162277.6602 | 19.1229 | 4715.2407 | 6361.9971 | 96.1266 | 129.6979
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1056 | 47.8802 | 4.7877 | 4 | 4710.832 | 6355.198 | 96.0367 | 129.5593 | 144.4906 | 0 | 207.4404 | 6814240.0188 | 320755.1324 | 7399050.1386 | 7159977.1139 | 0 | 405249.7271 | 0 | 8618716.131 | 22424131.4312 | 15304930.4716 | 68447050.1646 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90215923.9973 | 121706750.592 | 4216965.0343 | 19.1507 | 4710.832 | 6355.198 | 96.0367 | 129.5593
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.2176 | 47.9123 | 4.7927 | 4 | 4707.5245 | 6350.1837 | 95.9693 | 129.4571 | 144.4866 | 0 | 205.6972 | 6817375.454 | 320890.8648 | 7403044.0056 | 7164916.5445 | 0 | 402837.1635 | 0 | 8622534.9727 | 22434067.2738 | 15311711.8883 | 68477378.1672 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90246252 | 121737078.5946 | 5623413.2519 | 19.1706 | 4707.5245 | 6350.1837 | 95.9693 | 129.4571
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3102 | 47.9389 | 4.7966 | 4 | 4705.0434 | 6346.3655 | 95.9187 | 129.3792 | 144.4833 | 0 | 210.1846 | 6819966.1069 | 321003.0095 | 7406344.1751 | 7168998.6179 | 0 | 401119.6362 | 0 | 8625798.3028 | 22442557.7895 | 15317506.8398 | 68503294.4778 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90272168.3106 | 121762994.9052 | 7498942.0933 | 19.1863 | 4705.0434 | 6346.3655 | 95.9187 | 129.3792
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3808 | 47.9591 | 4.7995 | 4 | 4703.1824 | 6343.495 | 95.8807 | 129.3207 | 144.4808 | 0 | 227.2769 | 6821939.3541 | 321088.4193 | 7408858.0963 | 7172108.5843 | 0 | 399839.2297 | 0 | 8628295.1366 | 22449054.0388 | 15321940.6634 | 68523123.5226 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90291997.3554 | 121782823.95 | 10000000 | 19.1981 | 4703.1824 | 6343.495 | 95.8807 | 129.3207
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0559 | [19 empty] | 100 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7688 | [19 empty] | 133.3521 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7837 | [19 empty] | 177.8279 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.753 | [19 empty] | 237.1374 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.36596 | 0.012122 | 4 | 493723.6122 | 1158419.8816 | 10065.2236 | 23615.9562 | 113.734 | 0 | 279.0778 | 190304.1546 | 7319.2178 | 153091.4622 | 90871.569 | 0 | 88879.5354 | 0 | 206881.7162 | 538263.7883 | 367376.0958 | 1642987.5393 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 23940290.8798 | 56170918.7853 | 316.2278 | 0.048489 | 493723.6122 | 1158419.8816 | 10065.2236 | 23615.9562
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4099 | 0.54034 | 0.024493 | 4 | 249665.5111 | 578639.4267 | 5089.7691 | 11796.3474 | 121.1317 | 0 | 375.768 | 259875.9775 | 10537.3289 | 208000.0819 | 117193.3981 | 0 | 102826.891 | 0 | 272389.1342 | 708700.6525 | 483702.7577 | 2163226.2219 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 24460529.5624 | 56691157.4679 | 421.6965 | 0.097973 | 249665.5111 | 578639.4267 | 5089.7691 | 11796.3474
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1489 | 0.76905 | 0.042219 | 4 | 148545.3739 | 339398.7117 | 3028.2984 | 6919.1018 | 127.0611 | 0 | 490.1224 | 342475.4424 | 14485.3805 | 274739.4659 | 150992.4935 | 0 | 117623.2926 | 0 | 351123.2692 | 913550.7211 | 623517.1387 | 2788507.2037 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25085810.5442 | 57316438.4497 | 562.3413 | 0.16888 | 148545.3739 | 339398.7117 | 3028.2984 | 6919.1018
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 1.0892 | 0.067744 | 4 | 95585.858 | 214528.5117 | 1948.647 | 4373.4539 | 132.0752 | 0 | 59.4924 | 447378.9391 | 19618.5112 | 361697.5511 | 198187.3959 | 0 | 136790.125 | 0 | 453832.2837 | 1180778.5084 | 805905.5946 | 3604188.9091 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25901492.2495 | 58132120.155 | 749.8942 | 0.27098 | 95585.858 | 214528.5117 | 1948.647 | 4373.4539
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.481 | 1.5146 | 0.10271 | 4 | 65491.5736 | 143939.0725 | 1335.1343 | 2934.3927 | 136.0459 | 0 | 72.807 | 573760.2872 | 25884.6662 | 469619.0678 | 260066.7563 | 0 | 159182.9766 | 0 | 580520.3641 | 1510394.9063 | 1030875.559 | 4610304.5835 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 26907607.924 | 59138235.8294 | 1000 | 0.41086 | 65491.5736 | 143939.0725 | 1335.1343 | 2934.3927
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2495 | 2.0874 | 0.15034 | 4 | 46855.343 | 100453.0149 | 955.2095 | 2047.8706 | 139.1518 | 0 | 82.2961 | 728396.0897 | 33600.9328 | 605761.7068 | 343498.3047 | 0 | 186833.217 | 0 | 740255.1979 | 1925992.1777 | 1314529.2365 | 5878866.8631 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 28176170.2035 | 60406798.109 | 1333.5214 | 0.60134 | 46855.343 | 100453.0149 | 955.2095 | 2047.8706
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6273 | 2.8679 | 0.21615 | 4 | 34467.1472 | 71745.2947 | 702.6594 | 1462.6249 | 141.725 | 0 | 78.8408 | 920759.4814 | 43273.6596 | 779650.8004 | 457590.7231 | 0 | 221174.0975 | 0 | 944755.0172 | 2458058.7589 | 1677675.611 | 7502938.1492 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 29800241.4897 | 62030869.3952 | 1778.2794 | 0.8646 | 34467.1472 | 71745.2947 | 702.6594 | 1462.6249
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7548 | 3.8946 | 0.30331 | 4 | 26215.0516 | 52781.1077 | 534.4293 | 1076.0143 | 143.6401 | 0 | 80.4403 | 1151191.3294 | 54832.8677 | 994653.0073 | 607007.9896 | 0 | 261962.3494 | 0 | 1197162.542 | 3114771.3624 | 2125895.457 | 9507476.9047 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 31804780.2452 | 64035408.1507 | 2371.3737 | 1.2132 | 26215.0516 | 52781.1077 | 534.4293 | 1076.0143
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9205 | 5.2648 | 0.41983 | 4 | 20440.5228 | 39633.1296 | 416.7077 | 807.975 | 145.1166 | 0 | 90.604 | 1432222.2379 | 68893.9588 | 1264682.9315 | 805965.5147 | 0 | 311992.7052 | 0 | 1514665.3658 | 3940848.5812 | 2689710.133 | 12028981.428 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 34326284.7685 | 66556912.674 | 3162.2777 | 1.6793 | 20440.5228 | 39633.1296 | 416.7077 | 807.975
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4453 | 7.0817 | 0.57427 | 4 | 16315.7086 | 30346.8367 | 332.6178 | 618.6613 | 146.2455 | 0 | 89.5095 | 1773100.9788 | 85863.2942 | 1602038.045 | 1067571.2993 | 0 | 372926.5852 | 0 | 1911585.079 | 4973552.2556 | 3394551.6107 | 15181189.1479 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 37478492.4883 | 69709120.3938 | 4216.965 | 2.2971 | 16315.7086 | 30346.8367 | 332.6178 | 618.6613
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7005 | 9.4732 | 0.77839 | 4 | 13302.2022 | 23653.8906 | 271.1834 | 482.2166 | 147.1009 | 0 | 82.9408 | 2185262.6074 | 106339.9071 | 2020739.6281 | 1414719.3904 | 0 | 446127.8508 | 0 | 2407543.8597 | 6263935.2679 | 4275264.5313 | 19119933.0428 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 41417236.3833 | 73647864.2887 | 5623.4133 | 3.1136 | 13302.2022 | 23653.8906 | 271.1834 | 482.2166
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2058 | 12.6076 | 1.0455 | 4 | 11074.8741 | 18781.557 | 225.7763 | 382.8874 | 147.7504 | 0 | 92.9549 | 2681744.7432 | 130889.6725 | 2538840.1899 | 1868939.1658 | 0 | 534734.2115 | 0 | 3024507.7133 | 7869148.6583 | 5370855.6541 | 24019660.0087 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 46316963.3491 | 78547591.2546 | 7498.9421 | 4.1822 | 11074.8741 | 18781.557 | 225.7763 | 382.8874
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.4442 | 16.6426 | 1.3889 | 4 | 9417.4269 | 15218.7514 | 191.987 | 310.2548 | 148.2275 | 0 | 104.4884 | 3270540.7795 | 159866.0586 | 3169328.8405 | 2453725.8061 | 0 | 640105.4901 | 0 | 3780491.1202 | 9836062.4093 | 6713314.7052 | 30023435.2094 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 52320738.5499 | 84551366.4553 | 10000 | 5.5557 | 9417.4269 | 15218.7514 | 191.987 | 310.2548
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.8085 | 21.6909 | 1.8162 | 4 | 8189.4763 | 12626.0188 | 166.9536 | 257.3985 | 148.5158 | 0 | 105.3796 | 3950656.1781 | 193098.6154 | 3916797.819 | 3186357.4507 | 0 | 762977.7527 | 0 | 4683856.2482 | 12186433.1668 | 8317491.0425 | 37197668.2733 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 59494971.6138 | 91725599.5193 | 13335.2143 | 7.2648 | 8189.4763 | 12626.0188 | 166.9536 | 257.3985
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.5707 | 27.1461 | 2.2915 | 4 | 7297.4408 | 10813.791 | 148.7682 | 220.4538 | 148.5539 | 0 | 105.5348 | 4632809.5831 | 226034.7082 | 4686660.3905 | 3980933.5161 | 0 | 870362.8041 | 0 | 5614752.3908 | 14608433.9767 | 9970556.3624 | 44590543.7319 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 66887847.0724 | 99118474.9779 | 17782.7941 | 9.1659 | 7297.4408 | 10813.791 | 148.7682 | 220.4538
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.3144 | 30.917 | 2.699 | 4 | 6633.8905 | 9619.3341 | 135.2408 | 196.1031 | 148.4405 | 0 | 144.3888 | 5078479.116 | 247249.2334 | 5201007.6945 | 4533028.4659 | 0 | 864565.2665 | 0 | 6210488.6128 | 16158417.4241 | 11028451.9142 | 49321687.7274 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 71618991.0679 | 103849618.9733 | 23713.7371 | 10.7959 | 6633.8905 | 9619.3341 | 135.2408 | 196.1031
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.1936 | 34.3635 | 3.0907 | 4 | 6131.2785 | 8738.3212 | 124.9944 | 178.1425 | 148.2489 | 0 | 151.9304 | 5469883.9175 | 265632.1101 | 5660610.6647 | 5040295.3602 | 0 | 837955.0402 | 0 | 6737007.0662 | 17528310.436 | 11963432.0434 | 53503126.6384 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 75800429.9788 | 108031057.8843 | 31622.7766 | 12.3629 | 6131.2785 | 8738.3212 | 124.9944 | 178.1425
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.8102 | 37.3678 | 3.4486 | 4 | 5751.1367 | 8087.6089 | 117.2447 | 164.8768 | 148.0185 | 0 | 178.4294 | 5799787.7016 | 280914.7859 | 6054104.2244 | 5484927.1495 | 0 | 795662.0304 | 0 | 7182004.3978 | 18686102.2114 | 12753648.7203 | 57037151.2214 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 79334454.5618 | 111565082.4673 | 42169.6503 | 13.7946 | 5751.1367 | 8087.6089 | 117.2447 | 164.8768
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0197 | 39.8971 | 3.7624 | 4 | 5463.916 | 7605.5649 | 111.3893 | 155.0497 | 147.7809 | 0 | 183.6861 | 6070019.0833 | 293275.571 | 6380767.0985 | 5861309.6691 | 0 | 744545.571 | 0 | 7546467.6273 | 19634360.7728 | 13400854.6732 | 59931600.0662 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 82228903.4067 | 114459531.3122 | 56234.1325 | 15.0494 | 5463.916 | 7605.5649 | 111.3893 | 155.0497
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7749 | 41.953 | 4.027 | 4 | 5247.082 | 7247.9696 | 106.9689 | 147.7597 | 147.5593 | 0 | 193.2842 | 6284821.5233 | 302985.6528 | 6643438.116 | 6168759.9843 | 0 | 689910.3697 | 0 | 7835067.102 | 20385237.4062 | 13913343.4045 | 62223563.5588 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 84520866.8993 | 116751494.8048 | 74989.4209 | 16.1082 | 5247.082 | 7247.9696 | 106.9689 | 147.7597
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.107 | 44.1667 | 4.2822 | 4 | 5082.6386 | 6964.295 | 103.6165 | 141.9766 | 147.3108 | 0 | 214.6074 | 6511959.7057 | 313175.6097 | 6923569.0666 | 6500924.794 | 0 | 660023.5259 | 0 | 8154764.5538 | 21217024.5967 | 14481055.2535 | 64762497.1058 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 87059800.4463 | 119290428.3518 | 100000 | 17.1289 | 5082.6386 | 6964.295 | 103.6165 | 141.9766
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7091 | 45.5529 | 4.4661 | 4 | 4957.086 | 6761.2568 | 101.0569 | 137.8374 | 147.1617 | 0 | 204.6168 | 6652407.1834 | 319463.4126 | 7097565.1824 | 6709133.2742 | 0 | 614127.2834 | 0 | 8343151.571 | 21707168.9721 | 14815588.8612 | 66258605.7403 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 88555909.0808 | 120786536.9862 | 133352.1432 | 17.8645 | 4957.086 | 6761.2568 | 101.0569 | 137.8374
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2823 | 46.6229 | 4.6114 | 4 | 4862.3895 | 6609.7256 | 99.1264 | 134.7482 | 147.0416 | 0 | 230.4026 | 6759696.2718 | 324239.8346 | 7231208.4757 | 6870248.6515 | 0 | 573332.019 | 0 | 8485902.8485 | 22078578.5138 | 15069083.5051 | 67392290.1201 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 89689593.4605 | 121920221.366 | 177827.941 | 18.4456 | 4862.3895 | 6609.7256 | 99.1264 | 134.7482
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.0233 | 47.4397 | 4.7244 | 4 | 4791.0229 | 6496.549 | 97.6715 | 132.4409 | 146.9471 | 0 | 201.8131 | 6840914.0106 | 327837.4929 | 7332838.0626 | 6993205.2005 | 0 | 538374.0302 | 0 | 8592935.8308 | 22357056.3782 | 15259150.3697 | 68242311.3755 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 90539614.716 | 122770242.6215 | 237137.3706 | 18.8978 | 4791.0229 | 6496.549 | 97.6715 | 132.4409
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0908 | 48.0534 | 4.8111 | 4 | 4737.2747 | 6412.0663 | 96.5758 | 130.7186 | 146.8744 | 0 | 208.7663 | 6901552.5379 | 330512.9464 | 7408984.0555 | 7085554.8698 | 0 | 509050.7618 | 0 | 8671905.5169 | 22562519.3024 | 15399383.0373 | 68869463.0281 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 91166766.3685 | 123397394.274 | 316227.766 | 19.2446 | 4737.2747 | 6412.0663 | 96.5758 | 130.7186
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.665 | 48.5193 | 4.8776 | 4 | 4696.8215 | 6348.7806 | 95.7511 | 129.4285 | 146.8182 | 0 | 228.4222 | 6947387.5488 | 332529.8233 | 7466683.0772 | 7155746.3885 | 0 | 485311.4748 | 0 | 8731186.7419 | 22716756.8898 | 15504653.36 | 69340255.3043 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 91637558.6448 | 123868186.5502 | 421696.5034 | 19.5105 | 4696.8215 | 6348.7806 | 95.7511 | 129.4285
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.8292 | 48.8632 | 4.9277 | 4 | 4666.393 | 6301.553 | 95.1307 | 128.4657 | 146.7762 | 0 | 205.5283 | 6981102.6268 | 334010.3177 | 7509204.8153 | 7207593.3481 | 0 | 466064.6793 | 0 | 8774210.557 | 22828696.0313 | 15581054.1242 | 69681936.4997 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 91979239.8402 | 124209867.7457 | 562341.3252 | 19.711 | 4666.393 | 6301.553 | 95.1307 | 128.4657
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7159 | 49.1247 | 4.9659 | 4 | 4643.5174 | 6266.1047 | 94.6644 | 127.743 | 146.744 | 0 | 233.8073 | 7006673.0468 | 335131.4427 | 7541499.3804 | 7247037.3675 | 0 | 451035.6488 | 0 | 8806736.9856 | 22913323.1265 | 15638813.8555 | 69940250.8539 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92237554.1944 | 124468182.0999 | 749894.2093 | 19.8637 | 4643.5174 | 6266.1047 | 94.6644 | 127.743
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3808 | 49.3206 | 4.9948 | 4 | 4626.3283 | 6239.5526 | 94.314 | 127.2017 | 146.7197 | 0 | 219.5821 | 7025790.5814 | 335968.6536 | 7565669.8454 | 7276596.7899 | 0 | 439313.2509 | 0 | 8830902.2573 | 22976196.2063 | 15681726.0244 | 70132163.6092 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92429466.9497 | 124660094.8552 | 1000000 | 19.979 | 4626.3283 | 6239.5526 | 94.314 | 127.2017
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.8755 | 49.4662 | 5.0164 | 4 | 4613.4174 | 6219.683 | 94.0508 | 126.7967 | 146.7016 | 0 | 212.471 | 7039980.8033 | 336589.5263 | 7583625.0403 | 7298576.3598 | 0 | 430207.9809 | 0 | 8848702.0871 | 23022507.7123 | 15713334.5789 | 70273524.0889 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92570827.4294 | 124801455.3348 | 1333521.4322 | 20.0656 | 4613.4174 | 6219.683 | 94.0508 | 126.7967
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.2387 | 49.573 | 5.0325 | 4 | 4603.7231 | 6204.8417 | 93.8531 | 126.4941 | 146.6882 | 0 | 222.1336 | 7050380.6835 | 337044.2461 | 7596792.1878 | 7314706.266 | 0 | 423129.7216 | 0 | 8861600.7109 | 23056067.2856 | 15736239.6772 | 70375960.7786 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92673264.119 | 124903892.0245 | 1778279.41 | 20.1301 | 4603.7231 | 6204.8417 | 93.8531 | 126.4941
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5017 | 49.6503 | 5.0445 | 4 | 4596.4462 | 6193.7773 | 93.7048 | 126.2685 | 146.6785 | 0 | 205.3428 | 7057901.7107 | 337372.9185 | 7606318.8056 | 7326382.6587 | 0 | 417617.8568 | 0 | 8870781.6407 | 23079954.1815 | 15752542.9745 | 70448872.7471 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92746176.0875 | 124976803.993 | 2371373.7057 | 20.1778 | 4596.4462 | 6193.7773 | 93.7048 | 126.2685
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.7038 | 49.7097 | 5.0535 | 4 | 4590.9851 | 6185.4503 | 93.5934 | 126.0988 | 146.671 | 0 | 233.8559 | 7063674.8223 | 337625.1235 | 7613633.609 | 7335351.4858 | 0 | 413490.4466 | 0 | 8877872.44 | 23098402.9869 | 15765134.6633 | 70505185.5775 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92802488.918 | 125033116.8234 | 3162277.6602 | 20.2141 | 4590.9851 | 6185.4503 | 93.5934 | 126.0988
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.865 | 49.757 | 5.0605 | 4 | 4586.8875 | 6179.1443 | 93.5099 | 125.9702 | 146.6651 | 0 | 220.0826 | 7068275.8619 | 337826.0844 | 7619464.541 | 7342502.903 | 0 | 410481.6421 | 0 | 8883634.9026 | 23113395.7326 | 15775367.5203 | 70550949.1879 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92848252.5284 | 125078880.4339 | 4216965.0343 | 20.2421 | 4586.8875 | 6179.1443 | 93.5099 | 125.9702
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.9887 | 49.7934 | 5.0658 | 4 | 4583.8133 | 6174.3973 | 93.4472 | 125.8734 | 146.6605 | 0 | 199.3955 | 7071807.3114 | 337980.2989 | 7623940.7763 | 7347994.0827 | 0 | 408243.5787 | 0 | 8888086.7588 | 23124978.549 | 15783273.0305 | 70586304.3863 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92883607.7268 | 125114235.6323 | 5623413.2519 | 20.2634 | 4583.8133 | 6174.3973 | 93.4472 | 125.8734
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.0741 | 49.8185 | 5.0697 | 4 | 4581.5071 | 6170.8861 | 93.4002 | 125.8019 | 146.6573 | 0 | 201.6834 | 7074242.4117 | 338086.6087 | 7627027.9786 | 7351782.0359 | 0 | 406465.7397 | 0 | 8891065.8621 | 23132729.5647 | 15788563.258 | 70609963.4594 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92907266.7998 | 125137894.7053 | 7498942.0933 | 20.2788 | 4581.5071 | 6170.8861 | 93.4002 | 125.8019
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.1324 | 49.8356 | 5.0725 | 4 | 4579.7773 | 6168.29 | 93.365 | 125.7489 | 146.6552 | 0 | 212.949 | 7075905.6987 | 338159.206 | 7629137.044 | 7354370.2224 | 0 | 405058.1806 | 0 | 8893025.8372 | 23137829.0179 | 15792043.7396 | 70625528.9463 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92922832.2868 | 125153460.1923 | 10000000 | 20.2898 | 4579.7773 | 6168.29 | 93.365 | 125.7489
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1378 | [19 empty] | 100 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3051 | [19 empty] | 133.3521 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6486 | [19 empty] | 177.8279 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.2596 | 0.0053428 | 4 | 1129163.0023 | 2672283.4771 | 23019.5151 | 54478.1132 | 107.2871 | 0 | 57.1811 | 144296.3991 | 5298.3788 | 116861.9381 | 74167.609 | 0 | 79164.6067 | 0 | 163717.6834 | 425959.8291 | 290726.336 | 1300192.7803 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24131785.7193 | 57110419.0628 | 237.1374 | 0.021371 | 1129163.0023 | 2672283.4771 | 23019.5151 | 54478.1132
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.3845 | 0.013954 | 4 | 439484.0649 | 1030314.3561 | 8959.4771 | 21004.3518 | 115.5617 | 0 | 290.4895 | 199013.0749 | 7752.4242 | 159056.6648 | 93213.8687 | 0 | 89605.4304 | 0 | 213970.1706 | 556706.4926 | 379963.6204 | 1699281.7467 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24530874.6857 | 57509508.0293 | 316.2278 | 0.055817 | 439484.0649 | 1030314.3561 | 8959.4771 | 21004.3518
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.56379 | 0.027293 | 4 | 229532.7529 | 531608.5925 | 4679.3356 | 10837.5602 | 122.9432 | 0 | 386.149 | 270218.3673 | 11095.3156 | 214922.3842 | 119909.2394 | 0 | 102965.3681 | 0 | 280453.1631 | 729681.6016 | 498022.6866 | 2227268.126 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25058861.065 | 58037494.4085 | 421.6965 | 0.10917 | 229532.7529 | 531608.5925 | 4679.3356 | 10837.5602
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2267 | 0.81173 | 0.046889 | 4 | 137199.1745 | 313031.8467 | 2796.9907 | 6381.5776 | 129.1498 | 0 | 491.1139 | 359344.9672 | 15426.6617 | 286455.2983 | 156328.3846 | 0 | 119100.5784 | 0 | 365295.7972 | 950424.7318 | 648684.4087 | 2901060.8279 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25732653.7669 | 58711287.1104 | 562.3413 | 0.18756 | 137199.1745 | 313031.8467 | 2796.9907 | 6381.5776
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 1.1445 | 0.074433 | 4 | 89241.6549 | 200008.1548 | 1819.3118 | 4077.4368 | 134.1638 | 0 | 66.3804 | 467746.165 | 20820.8649 | 375775.8244 | 204814.3658 | 0 | 137855.4445 | 0 | 470734.9392 | 1224755.7508 | 835920.9661 | 3738424.3207 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 26570017.2598 | 59548650.6033 | 749.8942 | 0.29773 | 89241.6549 | 200008.1548 | 1819.3118 | 4077.4368
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5905 | 1.5893 | 0.11221 | 4 | 61514.0227 | 134988.3548 | 1254.0466 | 2751.9202 | 138.1725 | 0 | 81.617 | 599204.9955 | 27448.283 | 487357.3355 | 268719.9134 | 0 | 160154.9786 | 0 | 601725.3473 | 1565565.923 | 1068530.9116 | 4778707.6879 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 27610300.627 | 60588933.9705 | 1000 | 0.44885 | 61514.0227 | 134988.3548 | 1254.0466 | 2751.9202
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3958 | 2.1914 | 0.16389 | 4 | 44134.3884 | 94440.9496 | 899.7392 | 1925.3065 | 141.3153 | 0 | 69.8966 | 761097.3631 | 35675.1525 | 628854.3014 | 356074.9755 | 0 | 188060.0797 | 0 | 768207.1302 | 1998717.3718 | 1364165.6758 | 6100852.05 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 28932444.989 | 61911078.3326 | 1333.5214 | 0.65555 | 44134.3884 | 94440.9496 | 899.7392 | 1925.3065
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7905 | 3 | 0.23452 | 4 | 32614.294 | 67769.6336 | 664.8865 | 1381.5756 | 143.9126 | 0 | 86.0163 | 959530.0362 | 45825.0038 | 807082.0657 | 472521.7752 | 0 | 221561.1329 | 0 | 977542.8054 | 2543365.8581 | 1735899.4591 | 7763328.1364 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 30594921.0755 | 63573554.419 | 1778.2794 | 0.93808 | 32614.294 | 67769.6336 | 664.8865 | 1381.5756
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9789 | 4.0754 | 0.32844 | 4 | 24867.0086 | 49969.6739 | 506.9476 | 1018.6994 | 145.8632 | 0 | 82.5673 | 1199713.3695 | 58062.8098 | 1029928.9982 | 625860.6443 | 0 | 262617.8715 | 0 | 1238711.6404 | 3222873.5936 | 2199677.451 | 9837446.3782 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 32669039.3173 | 65647672.6608 | 2371.3737 | 1.3138 | 24867.0086 | 49969.6739 | 506.9476 | 1018.6994
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.228 | 5.5134 | 0.4545 | 4 | 19411.418 | 37551.4769 | 395.728 | 765.5376 | 147.3668 | 0 | 83.6902 | 1493612.0471 | 73029.9495 | 1310310.0045 | 832369.8933 | 0 | 313071.2286 | 0 | 1568733.318 | 4081522.3019 | 2785722.8379 | 12458371.5808 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 35289964.5198 | 68268597.8633 | 3162.2777 | 1.818 | 19411.418 | 37551.4769 | 395.728 | 765.5376
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8326 | 7.4126 | 0.62148 | 4 | 15510.8746 | 28777.04 | 316.2102 | 586.6589 | 148.5104 | 0 | 98.9535 | 1848998.7922 | 91061.9873 | 1659159.1218 | 1104778.7663 | 0 | 373793.1942 | 0 | 1980338.8262 | 5152435.4023 | 3516643.034 | 15727209.1244 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 38558802.0635 | 71537435.407 | 4216.965 | 2.4859 | 15510.8746 | 28777.04 | 316.2102 | 586.6589
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2138 | 9.9157 | 0.84177 | 4 | 12663.6831 | 22458.1206 | 258.1663 | 457.8392 | 149.3802 | 0 | 84.473 | 2278828.3066 | 112786.8113 | 2092763.0196 | 1463713.9594 | 0 | 447255.6735 | 0 | 2494185.6304 | 6489359.3825 | 4429121.1216 | 19808013.9048 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 42639606.8439 | 75618240.1874 | 5623.4133 | 3.3671 | 12663.6831 | 22458.1206 | 258.1663 | 457.8392
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.8636 | 13.1898 | 1.1297 | 4 | 10557.1584 | 17855.0306 | 215.222 | 363.9989 | 150.0394 | 0 | 96.4861 | 2795716.6036 | 138796.3434 | 2628223.6416 | 1932898.2162 | 0 | 535852.4879 | 0 | 3132280.0442 | 8149550.1559 | 5562235.4379 | 24875552.9308 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 47707145.8698 | 80685779.2134 | 7498.9421 | 4.5189 | 10557.1584 | 17855.0306 | 215.222 | 363.9989
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.2601 | 17.3912 | 1.4984 | 4 | 8990.9676 | 14493.3751 | 183.293 | 295.4671 | 150.5212 | 0 | 101.7721 | 3406501.2558 | 169340.2075 | 3277975.779 | 2532172.2363 | 0 | 640860.3393 | 0 | 3910471.429 | 10174244.5102 | 6944130.938 | 31055696.6949 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 53887289.634 | 86865922.9775 | 10000 | 5.9935 | 8990.9676 | 14493.3751 | 183.293 | 295.4671
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.822 | 22.6469 | 1.9566 | 4 | 7829.4236 | 12043.2934 | 159.6134 | 245.5188 | 150.8061 | 0 | 118.2825 | 4112073.0774 | 204363.6029 | 4048300.8889 | 3283465.8684 | 0 | 763801.4227 | 0 | 4840681.8955 | 12594461.3318 | 8595978.6492 | 38443126.7369 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 61274719.676 | 94253353.0195 | 13335.2143 | 7.8262 | 7829.4236 | 12043.2934 | 159.6134 | 245.5188
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.4017 | 28.8555 | 2.4919 | 4 | 6987.8037 | 10296.3944 | 142.4558 | 209.9059 | 150.8193 | 0 | 98.5244 | 4883564.344 | 242170.5546 | 4914119.7128 | 4176635.7955 | 0 | 900089.0735 | 0 | 5895465.9974 | 15338793.1989 | 10469041.5389 | 46819880.2156 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 69651473.1547 | 102630106.4982 | 17782.7941 | 9.9676 | 6987.8037 | 10296.3944 | 142.4558 | 209.9059
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.1797 | 32.7335 | 2.9214 | 4 | 6371.5816 | 9193.7198 | 129.8933 | 187.4264 | 150.6775 | 0 | 150.0216 | 5338056.5426 | 264104.2368 | 5436186.7567 | 4739489.4901 | 0 | 890070.1914 | 0 | 6500483.8149 | 16912925.4537 | 11543419.148 | 51624735.6341 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 74456328.5732 | 107434961.9167 | 23713.7371 | 11.6857 | 6371.5816 | 9193.7198 | 129.8933 | 187.4264
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9897 | 36.2441 | 3.3306 | 4 | 5904.8215 | 8380.2124 | 120.3778 | 170.842 | 150.462 | 0 | 165.2946 | 5733897.2893 | 282950.9977 | 5898588.7847 | 5253299.8559 | 0 | 858834.0314 | 0 | 7030752.674 | 18292576.2521 | 12485059.1669 | 55835959.0519 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 78667551.991 | 111646185.3345 | 31622.7766 | 13.3226 | 5904.8215 | 8380.2124 | 120.3778 | 170.842
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4755 | 39.2818 | 3.7017 | 4 | 5551.8073 | 7779.0414 | 113.1811 | 158.5863 | 150.2132 | 0 | 185.1687 | 6065505.2763 | 298525.5597 | 6291835.7612 | 5701748.2848 | 0 | 812260.7683 | 0 | 7476251.5036 | 19451672.8223 | 13276166.3931 | 59373966.3692 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 82205559.3083 | 115184192.6518 | 42169.6503 | 14.807 | 5551.8073 | 7779.0414 | 113.1811 | 158.5863
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.448 | 41.8005 | 4.0234 | 4 | 5285.0991 | 7334.2667 | 107.7439 | 149.5189 | 149.9651 | 0 | 213.2745 | 6333249.7817 | 310934.6101 | 6613590.8619 | 6076146.67 | 0 | 756477.8832 | 0 | 7835255.9247 | 20385728.684 | 13913678.7117 | 62225063.1272 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 85056656.0663 | 118035289.4098 | 56234.1325 | 16.0937 | 5285.0991 | 7334.2667 | 107.7439 | 149.5189
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0575 | 43.8598 | 4.2942 | 4 | 5083.8563 | 7003.8231 | 103.6413 | 142.7824 | 149.7345 | 0 | 208.169 | 6547181.7955 | 320702.193 | 6874023.687 | 6381215.867 | 0 | 699234.1327 | 0 | 8120719.4933 | 21128446.333 | 14420598.7684 | 64492122.2699 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 87323715.209 | 120302348.5525 | 74989.4209 | 17.1767 | 5083.8563 | 7003.8231 | 103.6413 | 142.7824
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4387 | 46.1492 | 4.5603 | 4 | 4930.1122 | 6738.0214 | 100.507 | 137.3637 | 149.4838 | 0 | 212.189 | 6781250.329 | 331344.0341 | 7160794.0567 | 6721025.1178 | 0 | 669979.673 | 0 | 8449113.3521 | 21982859.7908 | 15003753.5098 | 67100119.8633 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 89931712.8024 | 122910346.1459 | 100000 | 18.2413 | 4930.1122 | 6738.0214 | 100.507 | 137.3637
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9157 | 47.5306 | 4.7474 | 4 | 4813.4296 | 6550.1158 | 98.1283 | 133.533 | 149.3315 | 0 | 214.9449 | 6920552.0299 | 337645.1651 | 7332506.8424 | 6926510.3103 | 0 | 622580.5818 | 0 | 8634520.0225 | 22465249.9151 | 15332994.6817 | 68572559.5489 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 91404152.488 | 124382785.8315 | 133352.1432 | 18.9894 | 4813.4296 | 6550.1158 | 98.1283 | 133.533
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3823 | 48.5941 | 4.8946 | 4 | 4725.4075 | 6409.8338 | 96.3338 | 130.6731 | 149.2096 | 0 | 226.6787 | 7026717.2567 | 342419.639 | 7464076.8548 | 7085085.1509 | 0 | 580684.235 | 0 | 8774603.4232 | 22829718.1886 | 15581751.7675 | 69685056.5157 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 92516649.4548 | 125495282.7983 | 177827.941 | 19.5786 | 4725.4075 | 6409.8338 | 96.3338 | 130.6731
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0176 | 49.3991 | 5.0087 | 4 | 4659.0604 | 6305.1347 | 94.9812 | 128.5387 | 149.1145 | 0 | 218.8953 | 7106450.3574 | 345989.0011 | 7563300.3278 | 7205324.3548 | 0 | 544706.847 | 0 | 8878650.6464 | 23100427.7202 | 15766516.5854 | 70511365.8402 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 93342958.7792 | 126321592.1227 | 237137.3706 | 20.0347 | 4659.0604 | 6305.1347 | 94.9812 | 128.5387
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.025 | 50.0101 | 5.0965 | 4 | 4609.0875 | 6226.7919 | 93.9625 | 126.9416 | 149.0408 | 0 | 214.3053 | 7166623.9952 | 348673.2203 | 7638420.3675 | 7296727.6621 | 0 | 514926.2753 | 0 | 8956494.8929 | 23302962.4816 | 15904750.7217 | 71129579.6166 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 93961172.5556 | 126939805.8991 | 316227.766 | 20.3861 | 4609.0875 | 6226.7919 | 93.9625 | 126.9416
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.5675 | 50.4782 | 5.1641 | 4 | 4571.4713 | 6167.994 | 93.1956 | 125.7429 | 148.9834 | 0 | 198.6181 | 7212529.4196 | 350715.7512 | 7695860.9015 | 7366826.0766 | 0 | 491057.8743 | 0 | 9015626.1091 | 23456809.7766 | 16009754.6618 | 71599180.5708 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 94430773.5099 | 127409406.8534 | 421696.5034 | 20.6565 | 4571.4713 | 6167.994 | 93.1956 | 125.7429
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.6929 | 50.8188 | 5.2147 | 4 | 4543.1718 | 6124.2088 | 92.6187 | 124.8503 | 148.9411 | 0 | 190.6718 | 7245828.8051 | 352194.9212 | 7737594.1057 | 7417856.3542 | 0 | 471553.1917 | 0 | 9057760.6774 | 23566435.2804 | 16084576.3207 | 71933799.6563 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 94765392.5954 | 127744025.9389 | 562341.3252 | 20.8589 | 4543.1718 | 6124.2088 | 92.6187 | 124.8503
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5406 | 51.075 | 5.253 | 4 | 4521.8956 | 6091.3974 | 92.185 | 124.1814 | 148.909 | 0 | 214.1553 | 7270813.6958 | 353303.0413 | 7768949.2555 | 7456261.9049 | 0 | 456231.9673 | 0 | 9089168.3473 | 23648151.5948 | 16140349.3844 | 72183229.1913 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95014822.1304 | 127993455.4739 | 749894.2093 | 21.0122 | 4521.8956 | 6091.3974 | 92.185 | 124.1814
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.1667 | 51.264 | 5.2818 | 4 | 4505.9075 | 6066.8776 | 91.859 | 123.6815 | 148.8852 | 0 | 196.4769 | 7289209.8402 | 354117.9704 | 7792059.3988 | 7484604.6273 | 0 | 444180.9244 | 0 | 9112027.3768 | 23707626.1007 | 16180941.9567 | 72364768.1954 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95196361.1345 | 128174994.478 | 1000000 | 21.127 | 4505.9075 | 6066.8776 | 91.859 | 123.6815
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.642 | 51.4073 | 5.3035 | 4 | 4493.8982 | 6048.4649 | 91.6142 | 123.3061 | 148.867 | 0 | 201.3993 | 7303144.8486 | 354734.745 | 7809578.3423 | 7506110.438 | 0 | 434953.2116 | 0 | 9129323.4184 | 23752626.8528 | 16211655.8947 | 72502127.7515 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95333720.6905 | 128312354.034 | 1333521.4322 | 21.214 | 4493.8982 | 6048.4649 | 91.6142 | 123.3061
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.995 | 51.5137 | 5.3198 | 4 | 4484.8808 | 6034.6845 | 91.4304 | 123.0252 | 148.8535 | 0 | 209.7055 | 7313478.1843 | 355191.798 | 7822576.8028 | 7522078.4302 | 0 | 427838.7496 | 0 | 9142053.9463 | 23785749.0753 | 16234262.4921 | 72603229.4787 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95434822.4178 | 128413455.7613 | 1778279.41 | 21.2792 | 4484.8808 | 6034.6845 | 91.4304 | 123.0252
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.2534 | 51.5916 | 5.3319 | 4 | 4478.1118 | 6024.3933 | 91.2924 | 122.8154 | 148.8436 | 0 | 200.6744 | 7321031.6916 | 355525.7215 | 7832082.6576 | 7533762.166 | 0 | 422336.546 | 0 | 9151248.1253 | 23809670.4428 | 16250589.317 | 72676246.6679 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95507839.607 | 128486472.9505 | 2371373.7057 | 21.3277 | 4478.1118 | 6024.3933 | 91.2924 | 122.8154
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.4554 | 51.6524 | 5.3412 | 4 | 4473.0317 | 6016.6254 | 91.1888 | 122.657 | 148.8358 | 0 | 218.119 | 7326933.8959 | 355786.5634 | 7839512.5145 | 7542897.718 | 0 | 418261.8056 | 0 | 9158523.074 | 23828598.3671 | 16263508.0142 | 72734021.9526 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95565614.8917 | 128544248.2352 | 3162277.6602 | 21.3648 | 4473.0317 | 6016.6254 | 91.1888 | 122.657
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6017 | 51.6965 | 5.3481 | 4 | 4469.22 | 6010.8336 | 91.1111 | 122.539 | 148.8301 | 0 | 203.5053 | 7331204.6237 | 355975.2417 | 7844890.0616 | 7549511.8749 | 0 | 415112.615 | 0 | 9163710.8226 | 23842095.8248 | 16272720.3065 | 72775221.3707 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95606814.3097 | 128585447.6532 | 4216965.0343 | 21.3923 | 4469.22 | 6010.8336 | 91.1111 | 122.539
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.713 | 51.7299 | 5.3533 | 4 | 4466.3602 | 6006.4813 | 91.0528 | 122.4502 | 148.8259 | 0 | 230.6037 | 7334449.4272 | 356118.5684 | 7848976.484 | 7554539.0825 | 0 | 412752.8853 | 0 | 9167666.2145 | 23852386.9431 | 16279744.2062 | 72806633.8111 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95638226.7501 | 128616860.0936 | 5623413.2519 | 21.413 | 4466.3602 | 6006.4813 | 91.0528 | 122.4502
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.801 | 51.7564 | 5.3572 | 4 | 4464.2149 | 6003.1894 | 91.0091 | 122.3831 | 148.8225 | 0 | 224.2951 | 7337015.2474 | 356231.8937 | 7852208.1244 | 7558515.3092 | 0 | 411030.415 | 0 | 9170850.386 | 23860671.5044 | 16285398.5895 | 72831921.4697 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95663514.4088 | 128642147.7523 | 7498942.0933 | 21.429 | 4464.2149 | 6003.1894 | 91.0091 | 122.3831
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.8593 | 51.774 | 5.3601 | 4 | 4462.6058 | 6000.7684 | 90.9763 | 122.3338 | 148.8202 | 0 | 220.2531 | 7338715.8736 | 356306.9836 | 7854350.4814 | 7561151.7441 | 0 | 409638.9007 | 0 | 9172863.9535 | 23865910.394 | 16288974.2393 | 72847912.5702 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95679505.5093 | 128658138.8528 | 10000000 | 21.4403 | 4462.6058 | 6000.7684 | 90.9763 | 122.3338
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0081 | [19 empty] | 100 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.934 | [19 empty] | 133.3521 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6002 | [19 empty] | 177.8279 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.26947 | 0.0064518 | 4 | 957197.9575 | 2264384.5499 | 19513.7751 | 46162.5419 | 108.7416 | 0 | 60.0247 | 149422.1809 | 5542.6957 | 120274.1131 | 75400.5171 | 0 | 79053.7566 | 0 | 167580.3728 | 436009.7545 | 297585.6166 | 1330869.0074 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 24702611.6359 | 58437454.5446 | 237.1374 | 0.025807 | 957197.9575 | 2264384.5499 | 19513.7751 | 46162.5419
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9042 | 0.40368 | 0.015909 | 4 | 394889.209 | 925019.9695 | 8050.3507 | 18857.7833 | 117.3879 | 0 | 292.8345 | 207977.7994 | 8206.1212 | 165157.821 | 95652.9043 | 0 | 90285.7683 | 0 | 221239.3615 | 575619.4363 | 392872.0931 | 1757011.3051 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25128753.9336 | 58863596.8423 | 316.2278 | 0.063635 | 394889.209 | 925019.9695 | 8050.3507 | 18857.7833
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.59415 | 0.030487 | 4 | 210614.2814 | 487250.0948 | 4293.657 | 9933.2522 | 124.9491 | 0 | 390.259 | 283148.3197 | 11789.7018 | 223822.5316 | 123569.5322 | 0 | 104133.7981 | 0 | 291120.9145 | 757436.9025 | 516966.2497 | 2311987.9502 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25683730.5787 | 59418573.4875 | 421.6965 | 0.12195 | 210614.2814 | 487250.0948 | 4293.657 | 9933.2522
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 0.84932 | 0.051532 | 4 | 127925.4402 | 291586.1036 | 2607.9331 | 5944.3771 | 131.1139 | 0 | 494.8351 | 374436.6326 | 16300.5259 | 296621.5676 | 160774.8676 | 0 | 119534.7862 | 0 | 377390.6682 | 981893.1052 | 670162.2202 | 2997114.3737 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 26368857.0022 | 60103699.9109 | 562.3413 | 0.20613 | 127925.4402 | 291586.1036 | 2607.9331 | 5944.3771
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3212 | 1.1966 | 0.081157 | 4 | 83888.3928 | 187807.326 | 1710.1784 | 3828.7064 | 136.201 | 0 | 65.0996 | 486996.9575 | 21988.3914 | 388881.6678 | 210357.4677 | 0 | 138252.5274 | 0 | 486126.0346 | 1264800.2239 | 863252.1418 | 3860655.4122 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 27232398.0407 | 60967240.9494 | 749.8942 | 0.32463 | 83888.3928 | 187807.326 | 1710.1784 | 3828.7064
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7025 | 1.6672 | 0.12229 | 4 | 57907.9384 | 126875.0819 | 1180.5317 | 2586.5202 | 140.3024 | 0 | 85.0439 | 625619.7775 | 29105.6679 | 505673.205 | 277802.5022 | 0 | 161138.3082 | 0 | 623742.3897 | 1622849.7509 | 1107628.3012 | 4953559.9026 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 28325302.5311 | 62060145.4399 | 1000 | 0.48914 | 57907.9384 | 126875.0819 | 1180.5317 | 2586.5202
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5273 | 2.293 | 0.17774 | 4 | 41751.8222 | 89200.5495 | 851.1674 | 1818.4739 | 143.4556 | 0 | 76.6553 | 793076.6477 | 37761.033 | 651136.0859 | 367583.1147 | 0 | 188618.2132 | 0 | 794888.2868 | 2068136.2683 | 1411545.4991 | 6312745.1486 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 29684487.7771 | 63419330.6859 | 1333.5214 | 0.71097 | 41751.8222 | 89200.5495 | 851.1674 | 1818.4739
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9757 | 3.1422 | 0.25392 | 4 | 30925.1106 | 64139.5114 | 630.4502 | 1307.5707 | 146.1147 | 0 | 81.8658 | 1000427.5561 | 48539.2031 | 836349.1746 | 487346.5595 | 0 | 222520.1649 | 0 | 1012121.2367 | 2633331.8432 | 1797303.0926 | 8037938.8307 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 31409681.4592 | 65144524.3679 | 1778.2794 | 1.0157 | 30925.1106 | 64139.5114 | 630.4502 | 1307.5707
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2152 | 4.2679 | 0.35544 | 4 | 23607.6329 | 47335.1513 | 481.2735 | 964.9911 | 148.0893 | 0 | 85.7891 | 1251133.2136 | 61565.5735 | 1067085.3501 | 647558.3265 | 0 | 263525.2283 | 0 | 1283438.3999 | 3339243.4471 | 2279102.2672 | 10192651.8062 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 33564394.4347 | 67299237.3434 | 2371.3737 | 1.4218 | 23607.6329 | 47335.1513 | 481.2735 | 964.9911
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5273 | 5.7688 | 0.4911 | 4 | 18464.9671 | 35638.1136 | 376.4333 | 726.5311 | 149.6119 | 0 | 85.1793 | 1556721.7829 | 77407.2592 | 1356621.4339 | 860700.3208 | 0 | 313770.3907 | 0 | 1624436.2631 | 4226449.939 | 2884638.9282 | 12900746.3178 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 36272488.9463 | 70007331.8551 | 3162.2777 | 1.9644 | 18464.9671 | 35638.1136 | 376.4333 | 726.5311
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.2152 | 7.7488 | 0.67026 | 4 | 14785.2913 | 27368.0817 | 301.4182 | 557.9354 | 150.7716 | 0 | 91.1643 | 1925589.7219 | 96426.0957 | 1716567.8487 | 1139570.4411 | 0 | 374264.3299 | 0 | 2048443.1905 | 5329628.9883 | 3637581.2975 | 16268071.9136 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 39639814.5421 | 73374657.4509 | 4216.965 | 2.681 | 14785.2913 | 27368.0817 | 301.4182 | 557.9354
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.7326 | 10.3696 | 0.9075 | 4 | 12084.8213 | 21378.128 | 246.3654 | 435.8221 | 151.657 | 0 | 105.8546 | 2373952.7479 | 119474.9944 | 2165874.8718 | 1510104.011 | 0 | 448178.7528 | 0 | 2580858.2974 | 6714863.883 | 4583032.5768 | 20496340.1351 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 43868082.7636 | 77602925.6724 | 5623.4133 | 3.63 | 12084.8213 | 21378.128 | 246.3654 | 435.8221
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5279 | 13.7918 | 1.2181 | 4 | 10082.5427 | 17006.3484 | 205.5463 | 346.6974 | 152.3255 | 0 | 109.6534 | 2912988.4625 | 147131.5949 | 2719663.8412 | 1998331.1108 | 0 | 536802.2746 | 0 | 3242817.7408 | 8437146.5682 | 5758525.8988 | 25753407.492 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 49125150.1205 | 82859993.0292 | 7498.9421 | 4.8723 | 10082.5427 | 17006.3484 | 205.5463 | 346.6974
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.1032 | 18.1879 | 1.6169 | 4 | 8591.4137 | 13807.2972 | 175.1476 | 281.4804 | 152.812 | 0 | 103.1543 | 3551525.6227 | 179772.2868 | 3392217.3407 | 2629167.3889 | 0 | 642031.0961 | 0 | 4053938.3567 | 10547516.0271 | 7198896.4183 | 32195064.5374 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 55566807.1659 | 89301650.0747 | 10000 | 6.4677 | 8591.4137 | 13807.2972 | 175.1476 | 281.4804
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8379 | 23.6623 | 2.11 | 4 | 7490.5431 | 11487.5554 | 152.7049 | 234.1894 | 153.0919 | 0 | 95.2877 | 4285239.064 | 216930.0382 | 4186151.7253 | 3412775.7125 | 0 | 764673.7629 | 0 | 5017650.4181 | 13054897.1264 | 8910235.54 | 39848553.3874 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 63220296.0159 | 96955138.9247 | 13335.2143 | 8.44 | 7490.5431 | 11487.5554 | 152.7049 | 234.1894
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.7831 | 30.1724 | 2.6863 | 4 | 6695.6643 | 9835.2105 | 136.5002 | 200.5041 | 153.086 | 0 | 121.5184 | 5091823.7419 | 257143.227 | 5084617.7652 | 4345191.1954 | 0 | 904171.5236 | 0 | 6116349.5067 | 15913486.7806 | 10861281.7172 | 48574065.4577 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 71945808.0862 | 105680650.9949 | 17782.7941 | 10.7451 | 6695.6643 | 9835.2105 | 136.5002 | 200.5041
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.8398 | 34.5807 | 3.1603 | 4 | 6124.0913 | 8792.7412 | 124.8479 | 179.2519 | 152.9059 | 0 | 105.2711 | 5605172.4025 | 282239.8918 | 5671452.1838 | 4977735.9921 | 0 | 912375.2927 | 0 | 6805100.5475 | 17705475.7066 | 12084350.9809 | 54043902.9978 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 77415645.6263 | 111150488.5351 | 23713.7371 | 12.6412 | 6124.0913 | 8792.7412 | 124.8479 | 179.2519
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4964 | 38.1158 | 3.5827 | 4 | 5692.0376 | 8046.05 | 116.0399 | 164.0296 | 152.6699 | 0 | 181.9676 | 5999850.1509 | 301162.934 | 6131812.8933 | 5482521.4722 | 0 | 875371.1756 | 0 | 7328380.2641 | 19066942.1897 | 13013579.831 | 58199620.9108 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 81571363.5393 | 115306206.4481 | 31622.7766 | 14.3308 | 5692.0376 | 8046.05 | 116.0399 | 164.0296
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8332 | 41.1635 | 3.9625 | 4 | 5365.0598 | 7493.4264 | 109.374 | 152.7636 | 152.4056 | 0 | 200.0307 | 6329075.2164 | 316671.0629 | 6522316.8125 | 5917072.0507 | 0 | 824453.1683 | 0 | 7764739.4412 | 20202259.2589 | 13788457.0591 | 61665044.07 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 85036786.6985 | 118771629.6073 | 42169.6503 | 15.8501 | 5365.0598 | 7493.4264 | 109.374 | 152.7636
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6749 | 43.6847 | 4.2896 | 4 | 5117.8104 | 7083.8901 | 104.3335 | 144.4147 | 152.1456 | 0 | 202.022 | 6594106.7228 | 328946.9726 | 6841343.6316 | 6276079.4025 | 0 | 765651.4137 | 0 | 8114389.9758 | 21111978.2269 | 14409358.9476 | 64441855.2936 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 87813597.9221 | 121548440.8308 | 56234.1325 | 17.1584 | 5117.8104 | 7083.8901 | 104.3335 | 144.4147
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1861 | 46.3919 | 4.6077 | 4 | 4930.5739 | 6760.924 | 100.5164 | 137.8306 | 151.8379 | 0 | 200.4879 | 6872738.8448 | 341737.6529 | 7180032.0386 | 6667082.0357 | 0 | 732798.2515 | 0 | 8499811.6411 | 22114766.3391 | 15093782.4394 | 67502749.243 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 90874491.8715 | 124609334.7803 | 74989.4209 | 18.4308 | 4930.5739 | 6760.924 | 100.5164 | 137.8306
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.724 | 48.1523 | 4.8448 | 4 | 4786.6827 | 6527.4451 | 97.583 | 133.0708 | 151.6493 | 0 | 208.0025 | 7051696.7669 | 349974.5519 | 7398107.9334 | 6924849.4734 | 0 | 679431.887 | 0 | 8737583.6389 | 22733400.3036 | 15516012.8319 | 69391057.3871 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 92762800.0156 | 126497642.9243 | 100000 | 19.3794 | 4786.6827 | 6527.4451 | 97.583 | 133.0708
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.0741 | 49.5253 | 5.0345 | 4 | 4678.0153 | 6353.2037 | 95.3677 | 129.5187 | 151.4944 | 0 | 195.0345 | 7189491.1494 | 356269.6007 | 7567158.6629 | 7126434.5273 | 0 | 630534.6442 | 0 | 8919256.548 | 23206075.9468 | 15838623.6709 | 70833844.7503 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 94205587.3788 | 127940430.2875 | 133352.1432 | 20.1379 | 4678.0153 | 6353.2037 | 95.3677 | 129.5187
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4434 | 50.5825 | 5.1836 | 4 | 4596.026 | 6223.0175 | 93.6962 | 126.8646 | 151.3705 | 0 | 215.4837 | 7294563.193 | 361040.8542 | 7696750.1408 | 7282014.5408 | 0 | 587663.8836 | 0 | 9056592.7189 | 23563396.4919 | 16082502.2851 | 71924524.1083 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 95296266.7368 | 129031109.6455 | 177827.941 | 20.7345 | 4596.026 | 6223.0175 | 93.6962 | 126.8646
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.023 | 51.3883 | 5.2994 | 4 | 4534.2144 | 6125.6744 | 92.4361 | 124.8802 | 151.2733 | 0 | 224.8129 | 7374043.6544 | 364632.6958 | 7795183.8572 | 7400799.629 | 0 | 551274.7407 | 0 | 9159514.4851 | 23831177.8154 | 16265268.5407 | 72741895.4183 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 96113638.0468 | 129848480.9555 | 237137.3706 | 21.1974 | 4534.2144 | 6125.6744 | 92.4361 | 124.8802
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.9741 | 51.9956 | 5.3881 | 4 | 4487.6496 | 6052.8947 | 91.4868 | 123.3964 | 151.1986 | 0 | 211.3497 | 7433609.3007 | 367314.6127 | 7869186.0895 | 7490449.8319 | 0 | 521076.6081 | 0 | 9235838.2127 | 24029756.4986 | 16400802.5724 | 73348033.7266 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 96719776.3551 | 130454619.2639 | 316227.766 | 21.5524 | 4487.6496 | 6052.8947 | 91.4868 | 123.3964
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.424 | 52.4456 | 5.4553 | 4 | 4452.5954 | 5998.5627 | 90.7722 | 122.2888 | 151.1423 | 0 | 217.8043 | 7477568.7015 | 369288.2515 | 7923929.8567 | 7556962.338 | 0 | 496318.7715 | 0 | 9291386.4885 | 24174281.7177 | 16499444.0042 | 73789180.1297 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 97160922.7582 | 130895765.667 | 421696.5034 | 21.8212 | 4452.5954 | 5998.5627 | 90.7722 | 122.2888
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5151 | 52.7837 | 5.5063 | 4 | 4426.2234 | 5957.8721 | 90.2346 | 121.4593 | 151.0995 | 0 | 204.4082 | 7510481.1441 | 370762.7706 | 7964989.4478 | 7606956.6406 | 0 | 476603.2157 | 0 | 9332619.3553 | 24281561.1791 | 16572664.4409 | 74116638.1941 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 97488380.8226 | 131223223.7313 | 562341.3252 | 22.0252 | 4426.2234 | 5957.8721 | 90.2346 | 121.4593
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.3387 | 53.0385 | 5.545 | 4 | 4406.3947 | 5927.3628 | 89.8303 | 120.8373 | 151.067 | 0 | 219.9641 | 7535229.7078 | 371869.75 | 7995905.637 | 7644661.3148 | 0 | 461160.6913 | 0 | 9363442.5694 | 24361756.8594 | 16627399.6406 | 74361426.1703 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 97733168.7988 | 131468011.7076 | 749894.2093 | 22.1798 | 4406.3947 | 5927.3628 | 89.8303 | 120.8373
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.9519 | 53.2279 | 5.574 | 4 | 4391.4934 | 5904.53 | 89.5265 | 120.3718 | 151.0427 | 0 | 214.7592 | 7553599.963 | 372690.4182 | 8018877.307 | 7672711.1605 | 0 | 449090.8296 | 0 | 9386118.1746 | 24420754.1326 | 16667666.4918 | 74541508.4774 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 97913251.1059 | 131648094.0146 | 1000000 | 22.2961 | 4391.4934 | 5904.53 | 89.5265 | 120.3718
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.3929 | 53.3641 | 5.5955 | 4 | 4380.2999 | 5887.5305 | 89.2983 | 120.0253 | 151.0252 | 0 | 218.2326 | 7566782.5854 | 373278.7645 | 8035374.7655 | 7692873.8695 | 0 | 439547.4456 | 0 | 9402064.3979 | 24462242.9348 | 16695983.4518 | 74668148.2151 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98039890.8437 | 131774733.7524 | 1333521.4322 | 22.382 | 4380.2999 | 5887.5305 | 89.2983 | 120.0253
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7413 | 53.4716 | 5.6121 | 4 | 4371.8946 | 5874.6796 | 89.127 | 119.7633 | 151.0113 | 0 | 227.2065 | 7577181.3021 | 373742.5867 | 8048394.9687 | 7708797.0245 | 0 | 432462.8718 | 0 | 9414825.714 | 24495445.2616 | 16718644.7221 | 74769494.4515 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98141237.08 | 131876079.9888 | 1778279.41 | 22.4482 | 4371.8946 | 5874.6796 | 89.127 | 119.7633
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.9971 | 53.5504 | 5.6244 | 4 | 4365.585 | 5865.0779 | 88.9984 | 119.5675 | 151.001 | 0 | 239.2844 | 7584806.1005 | 374082.4931 | 8057946.1979 | 7720483.8179 | 0 | 426994.5651 | 0 | 9424082.1381 | 24519528.5783 | 16735082.0806 | 74843005.9716 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98214748.6001 | 131949591.5088 | 2371373.7057 | 22.4975 | 4365.585 | 5865.0779 | 88.9984 | 119.5675
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.1823 | 53.6076 | 5.6335 | 4 | 4360.8495 | 5857.909 | 88.9018 | 119.4214 | 150.9936 | 0 | 227.4049 | 7590350.478 | 374331.1513 | 8064869.6731 | 7729092.264 | 0 | 422760.8384 | 0 | 9430747.7178 | 24536871.0495 | 16746918.6735 | 74895941.8456 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98267684.4741 | 132002527.3828 | 3162277.6602 | 22.5341 | 4360.8495 | 5857.909 | 88.9018 | 119.4214
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3138 | 53.6483 | 5.6402 | 4 | 4357.2962 | 5852.577 | 88.8294 | 119.3127 | 150.9883 | 0 | 231.5264 | 7594287.3177 | 374507.838 | 8069784.2603 | 7735220.5183 | 0 | 419463.9845 | 0 | 9435372.9283 | 24548904.8984 | 16755132.0227 | 74932673.7683 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98304416.3969 | 132039259.3056 | 4216965.0343 | 22.5609 | 4357.2962 | 5852.577 | 88.8294 | 119.3127
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4186 | 53.6806 | 5.6454 | 4 | 4354.6304 | 5848.5413 | 88.775 | 119.2304 | 150.9841 | 0 | 230.028 | 7597424.3796 | 374648.6172 | 8073700.8576 | 7740105.2822 | 0 | 417053.5605 | 0 | 9439143.7519 | 24558715.8077 | 16761828.1699 | 74962620.4265 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98334363.0551 | 132069205.9638 | 5623413.2519 | 22.5816 | 4354.6304 | 5848.5413 | 88.775 | 119.2304
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.5159 | 53.7107 | 5.6497 | 4 | 4352.6306 | 5845.4029 | 88.7343 | 119.1664 | 150.9802 | 0 | 247.4918 | 7600334.4453 | 374779.2263 | 8077333.9794 | 7744636.7846 | 0 | 415472.0362 | 0 | 9442897.024 | 24568481.0518 | 16768493.1497 | 74992427.6971 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98364170.3257 | 132099013.2344 | 7498942.0933 | 22.5988 | 4352.6306 | 5845.4029 | 88.7343 | 119.1664
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.565 | 53.7258 | 5.6524 | 4 | 4351.1306 | 5843.193 | 88.7037 | 119.1214 | 150.9782 | 0 | 243.1013 | 7601801.7066 | 374845.0333 | 8079166.5674 | 7746923.5426 | 0 | 413979.7115 | 0 | 9444519.4589 | 24572702.2948 | 16771374.2348 | 75005312.55 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98377055.1785 | 132111898.0872 | 10000000 | 22.6095 | 4351.1306 | 5843.193 | 88.7037 | 119.1214
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5278 | [19 empty] | 100 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7925 | [19 empty] | 133.3521 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.757 | [19 empty] | 177.8279 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4908 | 0.28395 | 0.0077117 | 4 | 820051.9447 | 1938453.8917 | 16717.8681 | 39518.0045 | 110.545 | 0 | 50.1701 | 156645.0507 | 5884.2633 | 125255.4304 | 77291.0496 | 0 | 79939.4983 | 0 | 173555.964 | 451557.0171 | 308196.9428 | 1378325.2163 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25296077.6251 | 59795334.2263 | 237.1374 | 0.030847 | 820051.9447 | 1938453.8917 | 16717.8681 | 39518.0045
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.42343 | 0.017977 | 4 | 357872.6136 | 837650.3822 | 7295.7173 | 17076.636 | 119.2125 | 0 | 297.3848 | 217151.9494 | 8678.0532 | 171372.1363 | 98108.6445 | 0 | 90918.7623 | 0 | 228629.5228 | 594847.12 | 405995.3823 | 1815701.5707 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25733453.9796 | 60232710.5808 | 316.2278 | 0.071907 | 357872.6136 | 837650.3822 | 7295.7173 | 17076.636
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.61912 | 0.033603 | 4 | 195642.2891 | 452309.7247 | 3988.4327 | 9220.9455 | 126.7584 | 0 | 377.8381 | 294049.8604 | 12399.8544 | 231030.6419 | 126442.1759 | 0 | 104169.1701 | 0 | 299555.764 | 779382.6507 | 531944.6738 | 2378974.7912 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 26296727.2001 | 60795983.8013 | 421.6965 | 0.13441 | 195642.2891 | 452309.7247 | 3988.4327 | 9220.9455
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3434 | 0.88786 | 0.056387 | 4 | 119762.05 | 272720.0018 | 2441.5114 | 5559.7661 | 133.0763 | 0 | 501.3604 | 389819.3589 | 17207.7296 | 306935.0676 | 165168.8885 | 0 | 119901.5832 | 0 | 389622.7248 | 1013718.4074 | 691883.6429 | 3094257.403 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 27012009.8119 | 61511266.4131 | 562.3413 | 0.22555 | 119762.05 | 272720.0018 | 2441.5114 | 5559.7661
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4092 | 1.2553 | 0.088562 | 4 | 78809.1524 | 176196.7836 | 1606.6312 | 3592.0098 | 138.2853 | 0 | 60.0744 | 508374.6441 | 23300.5688 | 403508.6553 | 217171.8866 | 0 | 139155.3917 | 0 | 503689.3471 | 1310496.3603 | 894440.6939 | 4000137.5478 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 27917889.9566 | 62417146.5578 | 749.8942 | 0.35425 | 78809.1524 | 176196.7836 | 1606.6312 | 3592.0098
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8124 | 1.7472 | 0.13289 | 4 | 54649.335 | 119551.2755 | 1114.1006 | 2437.2145 | 142.4246 | 0 | 49.0669 | 652620.4538 | 30840.7705 | 524232.3197 | 287197.0872 | 0 | 161942.4398 | 0 | 646164.8976 | 1681188.517 | 1147445.7078 | 5131632.1934 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 29049384.6023 | 63548641.2035 | 1000 | 0.53156 | 54649.335 | 119551.2755 | 1114.1006 | 2437.2145
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.671 | 2.4012 | 0.1924 | 4 | 39569.7941 | 84396.5936 | 806.6838 | 1720.5387 | 145.6075 | 0 | 80.8846 | 826667.85 | 39981.3947 | 674656.4222 | 379337.5751 | 0 | 189499.7902 | 0 | 822955.7826 | 2141162.1348 | 1461387.1535 | 6535648.103 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 30453400.5119 | 64952657.1131 | 1333.5214 | 0.76961 | 39569.7941 | 84396.5936 | 806.6838 | 1720.5387
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1601 | 3.2904 | 0.27465 | 4 | 29351.2903 | 60754.4017 | 598.3658 | 1238.5607 | 148.3133 | 0 | 85.4487 | 1043096.7162 | 51453.5466 | 866489.4441 | 504241.4645 | 0 | 223354.544 | 0 | 1048567.929 | 2728158.6605 | 1862024.3439 | 8327386.6489 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 32245139.0578 | 66744395.6589 | 1778.2794 | 1.0986 | 29351.2903 | 60754.4017 | 598.3658 | 1238.5607
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4588 | 4.4679 | 0.38379 | 4 | 22456.7304 | 44929.3155 | 457.8108 | 915.9449 | 150.316 | 0 | 96.3434 | 1304164.6021 | 65255.0289 | 1105296.055 | 669372.3861 | 0 | 264468.6378 | 0 | 1329337.1168 | 3458662.4935 | 2360608.2202 | 10557164.5404 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 34474916.9492 | 68974173.5504 | 2371.3737 | 1.5352 | 22456.7304 | 44929.3155 | 457.8108 | 915.9449
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8368 | 6.0332 | 0.52922 | 4 | 17604.6146 | 33901.9171 | 358.8939 | 691.1364 | 151.8568 | 0 | 84.9986 | 1621377.4242 | 81972.0891 | 1404129.6813 | 887923.8571 | 0 | 314516.2232 | 0 | 1680868.5172 | 4373275.0882 | 2984850.1095 | 13348912.9899 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 37266665.3987 | 71765921.9999 | 3162.2777 | 2.1169 | 17604.6146 | 33901.9171 | 358.8939 | 691.1364
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.6368 | 8.1194 | 0.72446 | 4 | 14083.447 | 25988.5371 | 287.1101 | 529.8115 | 153.0358 | 0 | 92.7475 | 2010098.4253 | 102529.346 | 1779109.2613 | 1187130.7657 | 0 | 375665.2125 | 0 | 2127267.8742 | 5534714.646 | 3777556.4729 | 16894072.0038 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 40811824.4127 | 75311081.0139 | 4216.965 | 2.8979 | 14083.447 | 25988.5371 | 287.1101 | 529.8115
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.2468 | 10.8512 | 0.97972 | 4 | 11530.6053 | 20333.9341 | 235.067 | 414.5348 | 153.9302 | 0 | 104.7329 | 2476178.0433 | 126977.4702 | 2242368.878 | 1572677.3556 | 0 | 448976.9728 | 0 | 2678199.7008 | 6968126.2471 | 4755889.3443 | 21269394.0122 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 45187146.421 | 79686403.0222 | 5623.4133 | 3.9189 | 11530.6053 | 20333.9341 | 235.067 | 414.5348
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.1884 | 14.422 | 1.3131 | 4 | 9637.3116 | 16205.6589 | 196.4696 | 330.3743 | 154.6082 | 0 | 98.618 | 3036473.8854 | 156232.321 | 2814177.2061 | 2076378.0818 | 0 | 537530.2633 | 0 | 3362108.7855 | 8747517.3964 | 5970360.3666 | 26700778.306 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 50618530.7148 | 85117787.316 | 7498.9421 | 5.2523 | 9637.3116 | 16205.6589 | 196.4696 | 330.3743
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.9385 | 18.9986 | 1.7395 | 4 | 8227.3025 | 13185.6115 | 167.7247 | 268.8065 | 155.0991 | 0 | 99.1376 | 3698238.5633 | 190588.6653 | 3507272.8694 | 2721371.9116 | 0 | 642617.7983 | 0 | 4196435.0251 | 10918263.128 | 7451938.9328 | 33326726.8937 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 57244479.3026 | 91743735.9038 | 10000 | 6.9579 | 8227.3025 | 13185.6115 | 167.7247 | 268.8065
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.8831 | 24.6934 | 2.266 | 4 | 7184.2715 | 10990.5354 | 146.4611 | 224.0569 | 155.3737 | 0 | 111.3238 | 4458440.4441 | 229692.6059 | 4324960.4007 | 3523278.9977 | 0 | 765452.5014 | 0 | 5187711.7305 | 13497361.7767 | 9212226.7556 | 41199125.2127 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 65116877.6215 | 99616134.2227 | 13335.2143 | 9.0638 | 7184.2715 | 10990.5354 | 146.4611 | 224.0569
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9816 | 31.4329 | 2.8794 | 4 | 6430.96 | 9426.2986 | 131.1038 | 192.1678 | 155.3489 | 0 | 106.2163 | 5291003.394 | 271886.4131 | 5246036.95 | 4479057.2238 | 0 | 904355.6822 | 0 | 6315012.4686 | 16430367.0562 | 11214063.1261 | 50151782.3141 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 74069534.723 | 108568791.3241 | 17782.7941 | 11.5176 | 6430.96 | 9426.2986 | 131.1038 | 192.1678
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.746 | 36.5504 | 3.4116 | 4 | 5896.2081 | 8424.2698 | 120.2022 | 171.7401 | 155.1183 | 0 | 140.9503 | 5884313.1338 | 301376.8111 | 5919698.8119 | 5212556.5637 | 0 | 938549.915 | 0 | 7120033.1419 | 18524865.7156 | 12643601.4988 | 56544995.5919 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 80462748.0007 | 114962004.6019 | 23713.7371 | 13.6465 | 5896.2081 | 8424.2698 | 120.2022 | 171.7401
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2614 | 40.1309 | 3.8519 | 4 | 5493.8533 | 7732.9344 | 111.9996 | 157.6463 | 154.8594 | 0 | 168.0649 | 6282023.6377 | 320777.5467 | 6380311.1312 | 5728820.4315 | 0 | 895858.3504 | 0 | 7647038.528 | 19896025.6266 | 13579446.3126 | 60730301.5648 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 84648053.9736 | 119147310.5748 | 31622.7766 | 15.4078 | 5493.8533 | 7732.9344 | 111.9996 | 157.6463
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4667 | 43.215 | 4.2463 | 4 | 5189.5385 | 7220.6862 | 105.7958 | 147.2035 | 154.5767 | 0 | 178.4841 | 6613935.6827 | 336691.1513 | 6770912.1159 | 6174529.8315 | 0 | 840723.2494 | 0 | 8087348.8921 | 21041622.8738 | 14361339.9735 | 64227103.7702 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 88144856.179 | 122644112.7802 | 42169.6503 | 16.9851 | 5189.5385 | 7220.6862 | 105.7958 | 147.2035
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1692 | 45.7586 | 4.5846 | 4 | 4959.4587 | 6840.7223 | 101.1053 | 139.4574 | 154.3033 | 0 | 185.2584 | 6880767.7568 | 349288.7925 | 7089193.3895 | 6544096.2346 | 0 | 778569.801 | 0 | 8440347.23 | 21960052.1393 | 14988186.819 | 67030502.1628 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 90948254.5717 | 125447511.1729 | 56234.1325 | 18.3383 | 4959.4587 | 6840.7223 | 101.1053 | 139.4574
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5419 | 48.4988 | 4.914 | 4 | 4784.3105 | 6539.4726 | 97.5346 | 133.316 | 153.997 | 0 | 207.132 | 7162333.917 | 362456.2039 | 7428332.6435 | 6943581.1322 | 0 | 743379.7921 | 0 | 8829632.6386 | 22972892.919 | 15679471.463 | 70122080.7093 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 94039833.1182 | 128539089.7194 | 74989.4209 | 19.6559 | 4784.3105 | 6539.4726 | 97.5346 | 133.316
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9593 | 50.2624 | 5.1561 | 4 | 4650.5001 | 6323.2294 | 94.8067 | 128.9076 | 153.8032 | 0 | 221.0726 | 7340796.9592 | 370762.9491 | 7644645.1852 | 7200911.6544 | 0 | 688198.1883 | 0 | 9065672.8251 | 23587021.0657 | 16098626.5422 | 71996635.3692 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 95914387.778 | 130413644.3792 | 100000 | 20.6245 | 4650.5001 | 6323.2294 | 94.8067 | 128.9076
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1935 | 51.6309 | 5.349 | 4 | 4549.4239 | 6161.8547 | 92.7462 | 125.6177 | 153.6454 | 0 | 195.0418 | 7477567.3686 | 377079.5055 | 7811534.9462 | 7401125.1099 | 0 | 637836.9486 | 0 | 9245006.1127 | 24053609.4938 | 16417082.7318 | 73420842.2171 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 97338594.6259 | 131837851.2271 | 133352.1432 | 21.3958 | 4549.4239 | 6161.8547 | 92.7462 | 125.6177
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4675 | 52.683 | 5.5002 | 4 | 4473.1473 | 6041.2293 | 91.1912 | 123.1586 | 153.5196 | 0 | 211.3196 | 7581715.5467 | 381859.4194 | 7939285.0198 | 7555373.927 | 0 | 593922.0196 | 0 | 9380340.8137 | 24405722.6247 | 16657407.1788 | 74495626.5497 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 98413378.9585 | 132912635.5597 | 177827.941 | 22.0009 | 4473.1473 | 6041.2293 | 91.1912 | 123.1586
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.9398 | 53.474 | 5.6167 | 4 | 4415.6358 | 5951.201 | 90.0187 | 121.3233 | 153.4226 | 0 | 220.9558 | 7659453.8347 | 385410.0387 | 8035021.226 | 7671531.0114 | 0 | 556412.8399 | 0 | 9480053.2907 | 24665154.0362 | 16834474.4479 | 75287510.7254 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 99205263.1342 | 133704519.7354 | 237137.3706 | 22.4668 | 4415.6358 | 5951.201 | 90.0187 | 121.3233
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.8159 | 54.0723 | 5.7061 | 4 | 4372.3116 | 5883.8217 | 89.1355 | 119.9497 | 153.348 | 0 | 236.6383 | 7717943.4877 | 388072.0942 | 8107263.581 | 7759498.7316 | 0 | 525532.7744 | 0 | 9554341.1609 | 24858435.8358 | 16966393.2477 | 75877480.9132 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 99795233.3221 | 134294489.9233 | 316227.766 | 22.8244 | 4372.3116 | 5883.8217 | 89.1355 | 119.9497
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.2191 | 54.5186 | 5.7739 | 4 | 4339.6969 | 5833.4503 | 88.4706 | 118.9228 | 153.2916 | 0 | 216.4151 | 7761400.4357 | 390044.262 | 8161062.9706 | 7825188.7466 | 0 | 500426.2717 | 0 | 9608867.8478 | 25000303.0901 | 17063220.5639 | 76310514.1884 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 100228266.5972 | 134727523.1984 | 421696.5034 | 23.0957 | 4339.6969 | 5833.4503 | 88.4706 | 118.9228
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.264 | 54.8503 | 5.8251 | 4 | 4315.1599 | 5795.7845 | 87.9704 | 118.1549 | 153.2492 | 0 | 236.6668 | 7793599.4949 | 391502.3319 | 8200994.5165 | 7874045.4476 | 0 | 480334.4211 | 0 | 9648785.7227 | 25104161.2123 | 17134105.8663 | 76627529.0132 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 100545281.422 | 135044538.0232 | 562341.3252 | 23.3005 | 4315.1599 | 5795.7845 | 87.9704 | 118.1549
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.036 | 55.095 | 5.8635 | 4 | 4296.7108 | 5767.6367 | 87.5943 | 117.5811 | 153.2176 | 0 | 242.7271 | 7817299.1645 | 392573.7514 | 8230423.8684 | 7910107.138 | 0 | 464409.5516 | 0 | 9677777.2548 | 25179591.232 | 17185588.4047 | 76857770.3654 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 100775522.7742 | 135274779.3754 | 749894.2093 | 23.4541 | 4296.7108 | 5767.6367 | 87.5943 | 117.5811
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6233 | 55.2809 | 5.8927 | 4 | 4282.846 | 5746.4927 | 87.3116 | 117.15 | 153.1935 | 0 | 231.6646 | 7835280.839 | 393385.6958 | 8252774.1255 | 7937525.0317 | 0 | 452150.4984 | 0 | 9699735.3142 | 25236721.5984 | 17224581.0537 | 77032154.1567 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 100949906.5655 | 135449163.1667 | 1000000 | 23.5708 | 4282.846 | 5746.4927 | 87.3116 | 117.15
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.0519 | 55.4165 | 5.9144 | 4 | 4272.431 | 5730.712 | 87.0993 | 116.8283 | 153.1759 | 0 | 210.8317 | 7848375.3317 | 393976.3923 | 8269062.0569 | 7957523.0613 | 0 | 442555.0857 | 0 | 9715481.8519 | 25277690.8594 | 17252543.4161 | 77157208.0554 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101074960.4642 | 135574217.0654 | 1333521.4322 | 23.6575 | 4272.431 | 5730.712 | 87.0993 | 116.8283
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3855 | 55.522 | 5.931 | 4 | 4264.6103 | 5718.8106 | 86.9398 | 116.5857 | 153.1621 | 0 | 236.0027 | 7858551.3547 | 394435.1484 | 8281726.2188 | 7973081.4354 | 0 | 435368.8224 | 0 | 9727833.5621 | 25309827.4755 | 17274477.317 | 77255301.3343 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101173053.7431 | 135672310.3443 | 1778279.41 | 23.7239 | 4264.6103 | 5718.8106 | 86.9398 | 116.5857
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6218 | 55.5967 | 5.9431 | 4 | 4258.7394 | 5709.9667 | 86.8202 | 116.4054 | 153.1523 | 0 | 247.4058 | 7865751.6217 | 394759.5494 | 8290691.1407 | 7984100.6101 | 0 | 429717.1335 | 0 | 9736357.8216 | 25332005.8502 | 17289614.5134 | 77322998.2407 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101240750.6495 | 135740007.2507 | 2371373.7057 | 23.7725 | 4258.7394 | 5709.9667 | 86.8202 | 116.4054
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.805 | 55.6546 | 5.9524 | 4 | 4254.3332 | 5703.3009 | 86.7303 | 116.2695 | 153.1447 | 0 | 234.6663 | 7871328.5265 | 395010.7305 | 8297636.7061 | 7992640.5359 | 0 | 425506.6618 | 0 | 9743028.0327 | 25349360.3712 | 17301459.3306 | 77375970.8953 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101293723.3042 | 135792979.9054 | 3162277.6602 | 23.8095 | 4254.3332 | 5703.3009 | 86.7303 | 116.2695
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.9339 | 55.6953 | 5.9591 | 4 | 4251.027 | 5698.351 | 86.6629 | 116.1686 | 153.1394 | 0 | 214.4681 | 7875249.6706 | 395187.2655 | 8302521.5506 | 7998648.4166 | 0 | 422211.8492 | 0 | 9747589.3135 | 25361227.8881 | 17309559.1548 | 77412195.1089 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101329947.5177 | 135829204.1189 | 4216965.0343 | 23.8366 | 4251.027 | 5698.351 | 86.6629 | 116.1686
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.0387 | 55.7284 | 5.9644 | 4 | 4248.5465 | 5694.5925 | 86.6124 | 116.092 | 153.135 | 0 | 236.2691 | 7878437.4594 | 395330.7748 | 8306493.1572 | 8003533.8691 | 0 | 419830.3448 | 0 | 9751413.9861 | 25371178.9018 | 17316350.926 | 77442569.4193 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101360321.8281 | 135859578.4293 | 5623413.2519 | 23.8576 | 4248.5465 | 5694.5925 | 86.6124 | 116.092
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1165 | 55.7529 | 5.9683 | 4 | 4246.6857 | 5691.7788 | 86.5744 | 116.0346 | 153.1318 | 0 | 231.09 | 7880802.2177 | 395437.2128 | 8309439.7781 | 8007159.0535 | 0 | 418024.8457 | 0 | 9754236.6121 | 25378522.7956 | 17321363.2845 | 77464985.8 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101382738.2088 | 135881994.81 | 7498942.0933 | 23.8734 | 4246.6857 | 5691.7788 | 86.5744 | 116.0346
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1749 | 55.7714 | 5.9713 | 4 | 4245.2899 | 5689.6688 | 86.546 | 115.9916 | 153.1294 | 0 | 246.29 | 7882575.2943 | 395517.0092 | 8311649.3454 | 8009877.7562 | 0 | 416665.8641 | 0 | 9756351.255 | 25384024.6628 | 17325118.4219 | 77481779.609 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101399532.0178 | 135898788.619 | 10000000 | 23.8852 | 4245.2899 | 5689.6688 | 86.546 | 115.9916
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2531 | [19 empty] | 100 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1748 | [19 empty] | 133.3521 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4905 | [19 empty] | 177.8279 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5297 | 0.30039 | 0.0091081 | 4 | 710959.5349 | 1679106.101 | 14493.8718 | 34230.849 | 112.4529 | 0 | 57.8182 | 164739.5611 | 6271.9891 | 130843.3422 | 79490.2005 | 0 | 81102.97 | 0 | 180354.7445 | 469246.0495 | 320270.0708 | 1432318.9278 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 25901941.2078 | 61173815.6286 | 237.1374 | 0.036432 | 710959.5349 | 1679106.101 | 14493.8718 | 34230.849
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.44377 | 0.020165 | 4 | 326626.6989 | 763927.8276 | 6658.7271 | 15573.7021 | 121.0356 | 0 | 308.4772 | 226548.9327 | 9169.822 | 177699.6182 | 100602.4163 | 0 | 91504.0106 | 0 | 236154.6719 | 614426.0144 | 419358.38 | 1875463.8663 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 26345086.1463 | 61616960.5671 | 316.2278 | 0.080658 | 326626.6989 | 763927.8276 | 6658.7271 | 15573.7021
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.65162 | 0.037222 | 4 | 180930.9225 | 417834.2553 | 3688.5216 | 8518.1165 | 128.7603 | 0 | 406.0694 | 307790.9902 | 13166.7075 | 240347.7084 | 130523.1094 | 0 | 105224.9002 | 0 | 310850.8321 | 808770.1009 | 552002.2124 | 2468676.5612 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 26938298.8412 | 62210173.262 | 421.6965 | 0.14889 | 180930.9225 | 417834.2553 | 3688.5216 | 8518.1165
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4212 | 0.9345 | 0.06187 | 4 | 111857.8914 | 254381.7696 | 2280.3744 | 5185.9165 | 135.158 | 0 | 533.1336 | 407928.2711 | 18276.4366 | 319319.455 | 170690.8178 | 0 | 121162.0481 | 0 | 404577.0411 | 1052626.4707 | 718439.1956 | 3213019.7359 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 27682642.0159 | 62954516.4367 | 562.3413 | 0.24748 | 111857.8914 | 254381.7696 | 2280.3744 | 5185.9165
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4916 | 1.314 | 0.096274 | 4 | 74287.5681 | 165879.8214 | 1514.4526 | 3381.6845 | 140.3461 | 0 | 81.8645 | 529774.5299 | 24650.0767 | 417950.3307 | 224004.6753 | 0 | 139731.5046 | 0 | 521083.3357 | 1355751.9505 | 925328.5642 | 4138274.9675 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 28607897.2475 | 63879771.6684 | 749.8942 | 0.3851 | 74287.5681 | 165879.8214 | 1514.4526 | 3381.6845
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.907 | 1.8239 | 0.14367 | 4 | 51802.102 | 113179.8415 | 1056.0559 | 2307.3242 | 144.5096 | 0 | 70.143 | 678708.6223 | 32573.3801 | 541811.1247 | 295879.1409 | 0 | 162037.6353 | 0 | 667293.8623 | 1736161.7488 | 1184966.0681 | 5299431.5824 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 29769053.8624 | 65040928.2832 | 1000 | 0.57467 | 51802.102 | 113179.8415 | 1056.0559 | 2307.3242
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8025 | 2.5088 | 0.20761 | 4 | 37600.7885 | 80073.9969 | 766.5429 | 1632.4167 | 147.7397 | 0 | 90.4734 | 860214.2255 | 42269.7216 | 697750.2142 | 391201.8477 | 0 | 189835.5542 | 0 | 850695.9097 | 2213336.2552 | 1510647.4737 | 6755951.2019 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 31225573.4819 | 66497447.9027 | 1333.5214 | 0.83045 | 37600.7885 | 80073.9969 | 766.5429 | 1632.4167
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3453 | 3.4423 | 0.29621 | 4 | 27926.0127 | 57694.9872 | 569.3095 | 1176.1904 | 150.5098 | 0 | 84.7187 | 1086520.4099 | 54483.5567 | 897057.3396 | 520547.9341 | 0 | 224053.6031 | 0 | 1085238.5089 | 2823567.9872 | 1927143.1698 | 8618612.5094 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 33088234.7895 | 68360109.2103 | 1778.2794 | 1.1849 | 27926.0127 | 57694.9872 | 569.3095 | 1176.1904
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7022 | 4.6761 | 0.41397 | 4 | 21383.9258 | 42684.7842 | 435.9403 | 870.1871 | 152.5397 | 0 | 82.6807 | 1359372.8621 | 69210.3942 | 1144608.1564 | 693623.4369 | 0 | 265283.0122 | 0 | 1377518.1661 | 3584019.7004 | 2446167.0898 | 10939802.8181 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 35409425.0981 | 70681299.519 | 2371.3737 | 1.6559 | 21383.9258 | 42684.7842 | 435.9403 | 870.1871
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.158 | 6.319 | 0.57145 | 4 | 16768.1565 | 32199.1329 | 341.8416 | 656.4229 | 154.1019 | 0 | 86.2575 | 1691842.9696 | 87146.0949 | 1454767.5819 | 925223.9956 | 0 | 315550.102 | 0 | 1745066.9902 | 4540306.3461 | 3098852.3751 | 13858756.4555 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 38328378.7355 | 73600253.1564 | 3162.2777 | 2.2858 | 16768.1565 | 32199.1329 | 341.8416 | 656.4229
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0311 | 8.4835 | 0.77901 | 4 | 13462.7325 | 24782.128 | 274.456 | 505.2172 | 155.2927 | 0 | 87.7858 | 2092563.6923 | 108628.6768 | 1839918.8946 | 1226903.9214 | 0 | 376020.8905 | 0 | 2201174.0695 | 5727003.4059 | 3908797.5027 | 17481011.0538 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 41950633.3338 | 77222507.7546 | 4216.965 | 3.1161 | 13462.7325 | 24782.128 | 274.456 | 505.2172
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.7802 | 11.3392 | 1.0525 | 4 | 11038.2289 | 19416.1184 | 225.0292 | 395.8238 | 156.202 | 0 | 83.1643 | 2577617.0074 | 134491.5471 | 2319303.9201 | 1622780.5124 | 0 | 449708.92 | 0 | 2770521.7437 | 7208329.265 | 4919832.8397 | 22002585.7555 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 46472208.0355 | 81744082.4563 | 5623.4133 | 4.2101 | 11038.2289 | 19416.1184 | 225.0292 | 395.8238
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8728 | 15.0642 | 1.4097 | 4 | 9236.4992 | 15491.6289 | 188.2985 | 315.8178 | 156.8888 | 0 | 82.4779 | 3160116.4144 | 165461.9954 | 2909700.5695 | 2142075.0723 | 0 | 538225.9788 | 0 | 3477076.2119 | 9046639.057 | 6174517.0462 | 27613812.3456 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 52083434.6256 | 87355309.0464 | 7498.9421 | 5.6389 | 9236.4992 | 15491.6289 | 188.2985 | 315.8178
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8011 | 19.8334 | 1.8663 | 4 | 7893.6765 | 12618.4891 | 160.9233 | 257.245 | 157.3833 | 0 | 101.4167 | 3847774.316 | 201836.1074 | 3624643.3275 | 2808015.1854 | 0 | 643262.1284 | 0 | 4338957.1152 | 11289076.3712 | 7705026.5906 | 34458591.1415 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 58928213.4215 | 94200087.8424 | 10000 | 7.4652 | 7893.6765 | 12618.4891 | 160.9233 | 257.245
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.928 | 25.7536 | 2.4289 | 4 | 6901.0551 | 10531.4724 | 140.6873 | 214.6983 | 157.651 | 0 | 110.8322 | 4636059.7191 | 243145.6712 | 4466193.0546 | 3635976.5681 | 0 | 765847.6062 | 0 | 5361416.8214 | 13949306.7915 | 9520688.5148 | 42578634.7468 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 67048257.0268 | 102320131.4477 | 13335.2143 | 9.7157 | 6901.0551 | 10531.4724 | 140.6873 | 214.6983
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.1795 | 32.7259 | 3.0806 | 4 | 6186.146 | 9048.6078 | 126.113 | 184.4681 | 157.6063 | 0 | 117.0212 | 5494789.3538 | 287382.7414 | 5409961.4084 | 4614475.4217 | 0 | 904134.2329 | 0 | 6517189.8317 | 16956391.0827 | 11573085.3329 | 51757409.4056 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 76227031.6856 | 111498906.1064 | 17782.7941 | 12.3222 | 6186.146 | 9048.6078 | 126.113 | 184.4681
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.3692 | 38.4697 | 3.667 | 4 | 5684.4948 | 8089.1726 | 115.8861 | 164.9087 | 157.325 | 0 | 116.487 | 6156710.7119 | 320689.8085 | 6158271.5602 | 5424894.9418 | 0 | 959732.1119 | 0 | 7417916.6624 | 19299897.5316 | 13172576.6386 | 58910689.9669 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 83380312.2469 | 118652186.6678 | 23713.7371 | 14.668 | 5684.4948 | 8089.1726 | 115.8861 | 164.9087
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8218 | 42.1063 | 4.1229 | 4 | 5309.8871 | 7448.6726 | 108.2492 | 151.8513 | 157.0435 | 0 | 172.0696 | 6557357.3825 | 340413.6889 | 6621022.293 | 5940718.3182 | 0 | 912929.5384 | 0 | 7945252.0762 | 20671916.1069 | 14109007.5084 | 63098616.9124 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 87568239.1924 | 122840113.6133 | 31622.7766 | 16.4915 | 5309.8871 | 7448.6726 | 108.2492 | 151.8513
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9151 | 45.22 | 4.5289 | 4 | 5026.3015 | 6973.3611 | 102.468 | 142.1614 | 156.7436 | 0 | 176.8176 | 6890208.9538 | 356531.312 | 7011307.0178 | 6385639.4216 | 0 | 854109.5434 | 0 | 8384140.5369 | 21813813.8534 | 14888376.184 | 66584126.823 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 91053749.103 | 126325623.5239 | 42169.6503 | 18.1155 | 5026.3015 | 6973.3611 | 102.468 | 142.1614
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.464 | 47.7673 | 4.8746 | 4 | 4811.8394 | 6620.7863 | 98.0959 | 134.9737 | 156.4589 | 0 | 211.6331 | 7155786.5291 | 369185.9055 | 7326912.0129 | 6751697.1982 | 0 | 788628.7978 | 0 | 8732962.073 | 22721375.937 | 15507805.9546 | 69354354.4081 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 93823976.6881 | 129095851.1089 | 56234.1325 | 19.4986 | 4811.8394 | 6620.7863 | 98.0959 | 134.9737
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.866 | 50.5861 | 5.2168 | 4 | 4647.4529 | 6337.766 | 94.7446 | 129.2039 | 156.1494 | 0 | 204.6005 | 7444285.1757 | 382849.819 | 7672400.9459 | 7157684.8103 | 0 | 753546.6391 | 0 | 9130199.2821 | 23754905.6706 | 16213211.2347 | 72509083.5774 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 96978705.8574 | 132250580.2783 | 74989.4209 | 20.8671 | 4647.4529 | 6337.766 | 94.7446 | 129.2039
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.2056 | 52.3651 | 5.4645 | 4 | 4522.5495 | 6136.2337 | 92.1983 | 125.0954 | 155.9492 | 0 | 201.8346 | 7623509.5688 | 391283.7094 | 7888550.5158 | 7415616.5442 | 0 | 697207.7042 | 0 | 9366305.5365 | 24369205.7126 | 16632483.6359 | 74384162.9274 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 98853785.2074 | 134125659.6283 | 100000 | 21.858 | 4522.5495 | 6136.2337 | 92.1983 | 125.0954
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3271 | 53.7305 | 5.6608 | 4 | 4428.1656 | 5985.8797 | 90.2741 | 122.0303 | 155.7885 | 0 | 214.9954 | 7759731.8181 | 397676.4653 | 8053477.4134 | 7616583.3513 | 0 | 645471.2306 | 0 | 9544446.7087 | 24832692.5008 | 16948822.8926 | 75798902.3808 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 100268524.6608 | 135540399.0817 | 133352.1432 | 22.6434 | 4428.1656 | 5985.8797 | 90.2741 | 122.0303
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4749 | 54.7676 | 5.8138 | 4 | 4356.9442 | 5873.6797 | 88.8222 | 119.7429 | 155.6622 | 0 | 204.9608 | 7862267.323 | 402459.8181 | 8178227.564 | 7769749.6426 | 0 | 600137.7921 | 0 | 9677008.4345 | 25177590.9193 | 17184223.1502 | 76851664.6438 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 101321286.9238 | 136593161.3446 | 177827.941 | 23.2551 | 4356.9442 | 5873.6797 | 88.8222 | 119.7429
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.887 | 55.5589 | 5.9323 | 4 | 4303.2449 | 5789.6841 | 87.7275 | 118.0305 | 155.5634 | 0 | 226.5401 | 7939971.0986 | 406067.9753 | 8273121.5186 | 7886932.0135 | 0 | 562095.9429 | 0 | 9776593.534 | 25436690.9205 | 17361064.225 | 77642537.2283 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 102112159.5083 | 137384033.9292 | 237137.3706 | 23.7291 | 4303.2449 | 5789.6841 | 87.7275 | 118.0305
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6935 | 56.1495 | 6.0226 | 4 | 4262.7872 | 5726.9401 | 86.9027 | 116.7514 | 155.4882 | 0 | 225.3716 | 7997676.2262 | 408737.8443 | 8343795.3799 | 7974587.7492 | 0 | 530539.5157 | 0 | 9849581.319 | 25626590.165 | 17490674.3614 | 78222182.5605 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 102691804.8406 | 137963679.2614 | 316227.766 | 24.0903 | 4262.7872 | 5726.9401 | 86.9027 | 116.7514
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.0313 | 56.5859 | 6.0907 | 4 | 4232.3304 | 5680.0978 | 86.2818 | 115.7965 | 155.4321 | 0 | 241.0169 | 8040151.1626 | 410698.0717 | 8395923.1468 | 8039445.9713 | 0 | 504794.9566 | 0 | 9902495.1905 | 25764261.2046 | 17584637.6748 | 78642407.3789 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103112029.659 | 138383904.0798 | 421696.5034 | 24.3629 | 4232.3304 | 5680.0978 | 86.2818 | 115.7965
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.0371 | 56.9133 | 6.1424 | 4 | 4209.416 | 5645.0062 | 85.8146 | 115.0811 | 155.3895 | 0 | 223.6481 | 8071933.7276 | 412161.8598 | 8434991.0041 | 8088172.235 | 0 | 484369.36 | 0 | 9941734.9928 | 25866355.1209 | 17654318.8705 | 78954037.1707 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103423659.4507 | 138695533.8716 | 562341.3252 | 24.5696 | 4209.416 | 5645.0062 | 85.8146 | 115.0811
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.783 | 57.1558 | 6.1812 | 4 | 4192.186 | 5618.7615 | 85.4634 | 114.5461 | 155.3577 | 0 | 232.3149 | 8095420.5452 | 413241.8928 | 8463896.4799 | 8124289.1468 | 0 | 468244.976 | 0 | 9970386.2859 | 25940899.9083 | 17705197.2196 | 79181576.4545 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103651198.7345 | 138923073.1553 | 749894.2093 | 24.7249 | 4192.186 | 5618.7615 | 85.4634 | 114.5461
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3406 | 57.337 | 6.2104 | 4 | 4179.2371 | 5599.0998 | 85.1994 | 114.1452 | 155.3339 | 0 | 233.2933 | 8112935.8841 | 414046.3982 | 8485472.1438 | 8151283.8299 | 0 | 455713.7343 | 0 | 9991586.2763 | 25996057.9346 | 17742843.706 | 79349939.9073 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103819562.1873 | 139091436.6081 | 1000000 | 24.8417 | 4179.2371 | 5599.0998 | 85.1994 | 114.1452
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.7498 | 57.4697 | 6.2322 | 4 | 4169.5098 | 5584.4105 | 85.0011 | 113.8458 | 155.3163 | 0 | 193.6928 | 8125760.8758 | 414634.9399 | 8501280.989 | 8171083.3222 | 0 | 445951.0283 | 0 | 10006897.3505 | 26035894.2092 | 17770032.7819 | 79471535.497 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103941157.777 | 139213032.1978 | 1333521.4322 | 24.9289 | 4169.5098 | 5584.4105 | 85.0011 | 113.8458
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0593 | 57.5701 | 6.2487 | 4 | 4162.2052 | 5573.3817 | 84.8522 | 113.6209 | 155.303 | 0 | 198.623 | 8135448.032 | 415079.2084 | 8513227.7632 | 8186056.7921 | 0 | 438519.8605 | 0 | 10018449.346 | 26065950.1316 | 17790546.5666 | 79563277.7004 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104032899.9805 | 139304774.4013 | 1778279.41 | 24.9947 | 4162.2052 | 5573.3817 | 84.8522 | 113.6209
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.3003 | 57.6482 | 6.2612 | 4 | 4156.7217 | 5565.0625 | 84.7404 | 113.4513 | 155.2926 | 0 | 228.7059 | 8142982.4926 | 415424.605 | 8522522.9053 | 8197713.0769 | 0 | 432979.6341 | 0 | 10027532.8584 | 26089583.5677 | 17806676.8723 | 79635416.0123 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104105038.2923 | 139376912.7131 | 2371373.7057 | 25.045 | 4156.7217 | 5565.0625 | 84.7404 | 113.4513
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.464 | 57.7013 | 6.2703 | 4 | 4152.6063 | 5558.9186 | 84.6565 | 113.3261 | 155.2855 | 0 | 219.6771 | 8148097.0638 | 415658.9394 | 8528835.0253 | 8205632.5581 | 0 | 428554.1763 | 0 | 10033443.3276 | 26104961.3961 | 17817172.5562 | 79682355.0428 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104151977.3228 | 139423851.7437 | 3162277.6602 | 25.0811 | 4152.6063 | 5558.9186 | 84.6565 | 113.3261
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5929 | 57.7431 | 6.2772 | 4 | 4149.5181 | 5554.2773 | 84.5935 | 113.2315 | 155.2799 | 0 | 198.5568 | 8152121.5506 | 415843.2986 | 8533802.589 | 8211866.7058 | 0 | 425287.977 | 0 | 10038179.6272 | 26117284.2761 | 17825583.175 | 79719969.1992 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104189591.4792 | 139461465.9001 | 4216965.0343 | 25.1088 | 4149.5181 | 5554.2773 | 84.5935 | 113.2315
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6829 | 57.7722 | 6.2822 | 4 | 4147.2012 | 5550.8337 | 84.5463 | 113.1613 | 155.276 | 0 | 223.3194 | 8154929.9238 | 415971.9048 | 8537269.8329 | 8216219.2534 | 0 | 422735.2162 | 0 | 10041379.1912 | 26125608.8853 | 17831264.8918 | 79745379.0994 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104215001.3795 | 139486875.8003 | 5623413.2519 | 25.129 | 4147.2012 | 5550.8337 | 84.5463 | 113.1613
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.7561 | 57.7959 | 6.2862 | 4 | 4145.4632 | 5548.22 | 84.5109 | 113.108 | 155.2729 | 0 | 214.7824 | 8157212.3904 | 416076.4292 | 8540087.8786 | 8219757.1804 | 0 | 420886.4163 | 0 | 10044067.915 | 26132604.3931 | 17836039.4696 | 79766732.0726 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104236354.3526 | 139508228.7734 | 7498942.0933 | 25.1447 | 4145.4632 | 5548.22 | 84.5109 | 113.108
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8144 | 57.8148 | 6.2892 | 4 | 4144.1594 | 5546.2407 | 84.4843 | 113.0676 | 155.2703 | 0 | 225.3514 | 8159032.3693 | 416159.7738 | 8542334.9893 | 8222578.562 | 0 | 419540.7665 | 0 | 10046262.1198 | 26138313.2639 | 17839935.8913 | 79784157.7359 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104253780.0159 | 139525654.4367 | 10000000 | 25.1568 | 4144.1594 | 5546.2407 | 84.4843 | 113.0676
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1597 | [19 empty] | 100 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5819 | [19 empty] | 133.3521 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0019 | [19 empty] | 177.8279 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.31125 | 0.010416 | 4 | 635857.3995 | 1501178.0777 | 12962.8131 | 30603.5456 | 113.9079 | 0 | 58.0567 | 170281.7485 | 6549.2105 | 134472.163 | 80806.3641 | 0 | 80887.7987 | 0 | 184468.9411 | 479950.3448 | 327575.9723 | 1464992.543 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 26492344.7851 | 62545041.1528 | 237.1374 | 0.041664 | 635857.3995 | 1501178.0777 | 12962.8131 | 30603.5456
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.47121 | 0.022752 | 4 | 296513.1486 | 692661.8827 | 6044.8216 | 14120.8494 | 123.155 | 0 | 313.4618 | 238824.4492 | 9811.3014 | 186163.4103 | 104052.7589 | 0 | 93227.6378 | 0 | 246511.0275 | 641371.1272 | 437748.9732 | 1957710.6857 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 26985062.9277 | 63037759.2954 | 316.2278 | 0.091008 | 296513.1486 | 692661.8827 | 6044.8216 | 14120.8494
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6627 | 0.68504 | 0.041036 | 4 | 168064.5425 | 387703.8564 | 3426.223 | 7903.8675 | 130.7592 | 0 | 407.2224 | 321828.3597 | 13964.874 | 249818.6044 | 134583.1232 | 0 | 106215.5714 | 0 | 322300.1078 | 838558.7676 | 572333.5895 | 2559602.9976 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 27586955.2397 | 63639651.6074 | 421.6965 | 0.16415 | 168064.5425 | 387703.8564 | 3426.223 | 7903.8675
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4795 | 0.97542 | 0.067229 | 4 | 105389.4695 | 239455.3432 | 2148.5069 | 4881.6211 | 137.117 | 0 | 540.9248 | 424054.1382 | 19264.7534 | 330027.9012 | 175161.6292 | 0 | 121390.8369 | 0 | 417260.711 | 1085626.7781 | 740962.5834 | 3313749.3314 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 28341101.5735 | 64393797.9412 | 562.3413 | 0.26892 | 105389.4695 | 239455.3432 | 2148.5069 | 4881.6211
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5842 | 1.3783 | 0.10463 | 4 | 70048.222 | 156190.1692 | 1428.0278 | 3184.1479 | 142.4432 | 0 | 79.1167 | 552923.8139 | 26129.4384 | 433640.077 | 231627.8893 | 0 | 140677.4159 | 0 | 540149.4674 | 1405358.1144 | 959185.7903 | 4289692.0066 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 29317044.2487 | 65369740.6164 | 749.8942 | 0.41853 | 70048.222 | 156190.1692 | 1428.0278 | 3184.1479
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0385 | 1.9157 | 0.15566 | 4 | 49026.27 | 106928.1745 | 999.4668 | 2179.8755 | 146.6752 | 0 | 74.098 | 708829.8735 | 34559.6191 | 562717.9883 | 305824.715 | 0 | 163485.4484 | 0 | 692412.8813 | 1801516.2836 | 1229571.881 | 5498918.6902 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 30526270.9323 | 66578967.3 | 1000 | 0.62265 | 49026.27 | 106928.1745 | 999.4668 | 2179.8755
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9559 | 2.6277 | 0.22411 | 4 | 35727.4662 | 75945.2474 | 728.3527 | 1548.2466 | 149.8945 | 0 | 62.6912 | 896722.1967 | 44790.3328 | 723062.0488 | 404657.1253 | 0 | 190854.7179 | 0 | 881433.7044 | 2293309.6919 | 1565230.9875 | 7000060.8053 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 32027413.0474 | 68080109.4151 | 1333.5214 | 0.89644 | 35727.4662 | 75945.2474 | 728.3527 | 1548.2466
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5279 | 3.6006 | 0.31935 | 4 | 26582.0365 | 54805.9166 | 541.9108 | 1117.2927 | 152.7016 | 0 | 97.2423 | 1131991.3365 | 57766.3581 | 928516.2817 | 539720.7863 | 0 | 224585.3235 | 0 | 1124206.2336 | 2924954.0134 | 1996341.2159 | 8928081.549 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 33955433.7911 | 70008130.1588 | 1778.2794 | 1.2774 | 26582.0365 | 54805.9166 | 541.9108 | 1117.2927
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9385 | 4.8894 | 0.44575 | 4 | 20392.7778 | 40613.1214 | 415.7344 | 827.9534 | 154.7573 | 0 | 86.4837 | 1416024.5433 | 73402.933 | 1184385.3429 | 719420.2942 | 0 | 265748.1446 | 0 | 1427002.6906 | 3712768.2825 | 2534040.6426 | 11332792.8738 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 36360145.1159 | 72412841.4836 | 2371.3737 | 1.783 | 20392.7778 | 40613.1214 | 415.7344 | 827.9534
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.4675 | 6.6002 | 0.61348 | 4 | 16038.5366 | 30730.504 | 326.9673 | 626.4829 | 156.3408 | 0 | 84.3268 | 1760157.9298 | 92239.3249 | 1504170.5537 | 954106.9104 | 0 | 315907.2193 | 0 | 1804366.9559 | 4694592.6926 | 3204155.9769 | 14329697.5634 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 39357049.8055 | 75409746.1732 | 3162.2777 | 2.4539 | 16038.5366 | 30730.504 | 326.9673 | 626.4829
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.4527 | 8.8678 | 0.83667 | 4 | 12885.1591 | 23657.8088 | 262.6814 | 482.2964 | 157.5507 | 0 | 87.1114 | 2178757.1702 | 115134.6997 | 1903493.7207 | 1268166.406 | 0 | 376802.6387 | 0 | 2278518.3078 | 5928237.2485 | 4046143.7352 | 18095253.9267 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 43122606.1688 | 79175302.5365 | 4216.965 | 3.3467 | 12885.1591 | 23657.8088 | 262.6814 | 482.2964
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3332 | 11.8566 | 1.131 | 4 | 10571.7479 | 18541.0682 | 215.5194 | 377.9848 | 158.4724 | 0 | 89.1085 | 2685270.2769 | 142728.5084 | 2399908.7392 | 1682265.2148 | 0 | 450723.1375 | 0 | 2870749.3919 | 7469101.0461 | 5097814.9386 | 22798561.2532 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 47825913.4953 | 83878609.863 | 5623.4133 | 4.5239 | 10571.7479 | 18541.0682 | 215.5194 | 377.9848
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.5768 | 15.7415 | 1.5134 | 4 | 8858.5898 | 14814.2739 | 180.5943 | 302.009 | 159.1672 | 0 | 102.6427 | 3290667.7406 | 175527.7838 | 3009303.3376 | 2218726.0321 | 0 | 539137.6312 | 0 | 3601011.3849 | 9369092.9545 | 6394598.457 | 28598065.3217 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 53625417.5638 | 89678113.9315 | 7498.9421 | 6.0535 | 8858.5898 | 14814.2739 | 180.5943 | 302.009
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6831 | 20.7029 | 2.0001 | 4 | 7582.8374 | 12089.1669 | 154.5864 | 246.454 | 159.6642 | 0 | 111.6055 | 4003002.1054 | 213837.5683 | 3745611.5147 | 2900167.2567 | 0 | 643966.9833 | 0 | 4487568.3171 | 11675732.2342 | 7968927.1621 | 35638813.1418 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 60666165.3839 | 96718861.7516 | 10000 | 8.0005 | 7582.8374 | 12089.1669 | 154.5864 | 246.454
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9849 | 26.8427 | 2.5982 | 4 | 6639.1943 | 10108.2658 | 135.349 | 206.0707 | 159.9238 | 0 | 97.3764 | 4817456.7062 | 257226.8569 | 4609874.946 | 3746240.6831 | 0 | 766031.3415 | 0 | 5536763.9082 | 14405523.9426 | 9832066.0947 | 43971184.4792 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 68998536.7212 | 105051233.0889 | 13335.2143 | 10.3926 | 6639.1943 | 10108.2658 | 135.349 | 206.0707
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4099 | 34.0606 | 3.2897 | 4 | 5959.3898 | 8699.1693 | 121.4902 | 177.3443 | 159.8576 | 0 | 132.9804 | 5703833.6527 | 303660.9707 | 5577603.7935 | 4749336.1281 | 0 | 904104.0044 | 0 | 6723030.0343 | 17491945.0661 | 11938611.9312 | 53392125.581 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 78419477.8231 | 114472174.1908 | 17782.7941 | 13.159 | 5959.3898 | 8699.1693 | 121.4902 | 177.3443
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1271 | 40.5057 | 3.9398 | 4 | 5486.1393 | 7773.8563 | 111.8424 | 158.4806 | 159.5164 | 0 | 121.1394 | 6443503.214 | 341503.6453 | 6408393.2998 | 5657145.2756 | 0 | 983177.6692 | 0 | 7735152.0105 | 20125278.8335 | 13735916.337 | 61430070.285 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 86457422.527 | 122510118.8948 | 23713.7371 | 15.7592 | 5486.1393 | 7773.8563 | 111.8424 | 158.4806
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4749 | 44.1946 | 4.4135 | 4 | 5136.552 | 7178.7409 | 104.7156 | 146.3483 | 159.212 | 0 | 169.9471 | 6847853.9241 | 361736.4945 | 6872456.6917 | 6183601.8847 | 0 | 931540.9545 | 0 | 8266904.0803 | 21508788.6417 | 14680190.2094 | 65653072.8809 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 90680425.1229 | 126733121.4906 | 31622.7766 | 17.6539 | 5136.552 | 7178.7409 | 104.7156 | 146.3483
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3124 | 47.2935 | 4.8295 | 4 | 4872.0328 | 6738.3089 | 99.323 | 137.3695 | 158.8997 | 0 | 170.2819 | 7177520.8867 | 377926.8819 | 7256770.6179 | 6627996.6044 | 0 | 866808.1629 | 0 | 8699739.03 | 22634936.3942 | 15448809.1904 | 69090507.7684 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 94117860.0104 | 130170556.3782 | 42169.6503 | 19.318 | 4872.0328 | 6738.3089 | 99.323 | 137.3695
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7003 | 50.5308 | 5.2301 | 4 | 4671.829 | 6395.1442 | 95.2416 | 130.3737 | 158.5322 | 0 | 192.6959 | 7512505.8119 | 394049.5953 | 7653392.0063 | 7089444.944 | 0 | 826200.575 | 0 | 9155481.2437 | 23820684.1486 | 16258106.3975 | 72709864.7222 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 97737216.9643 | 133789913.332 | 56234.1325 | 20.9205 | 4671.829 | 6395.1442 | 95.2416 | 130.3737
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1971 | 52.7621 | 5.5396 | 4 | 4517.714 | 6144.7615 | 92.0997 | 125.2693 | 158.2903 | 0 | 218.2432 | 7739473.839 | 404929.1128 | 7923877.2542 | 7407990.1137 | 0 | 763836.5199 | 0 | 9453641.6675 | 24596436.4102 | 16787573.2562 | 75077758.1736 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 100105110.4157 | 136157806.7834 | 74989.4209 | 22.1584 | 4517.714 | 6144.7615 | 92.0997 | 125.2693
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3445 | 54.5144 | 5.7895 | 4 | 4401.1335 | 5957.9354 | 89.7231 | 121.4606 | 158.0889 | 0 | 206.3229 | 7915019.6528 | 413256.76 | 8134818.105 | 7658905.7137 | 0 | 704797.3033 | 0 | 9682451.0386 | 25191751.4586 | 17193888.0092 | 76894888.0411 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 101922240.2832 | 137974936.6509 | 100000 | 23.1582 | 4401.1335 | 5957.9354 | 89.7231 | 121.4606
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3734 | 55.875 | 5.9879 | 4 | 4313.0447 | 5818.2825 | 87.9273 | 118.6136 | 157.9253 | 0 | 223.6319 | 8049717.5169 | 419591.0974 | 8297759.8656 | 7853836.8298 | 0 | 651975.34 | 0 | 9856423.4534 | 25644391.9952 | 17502824.4763 | 78276520.5746 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 103303872.8167 | 139356569.1844 | 133352.1432 | 23.9515 | 4313.0447 | 5818.2825 | 87.9273 | 118.6136
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.448 | 56.9063 | 6.1419 | 4 | 4246.5432 | 5714.0289 | 86.5715 | 116.4882 | 157.7971 | 0 | 221.0298 | 8150886.796 | 424315.0033 | 8420790.9812 | 8001497.4897 | 0 | 605934.2482 | 0 | 9985335.5622 | 25979794.8588 | 17731743.8225 | 79300298.7619 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 104327651.0039 | 140380347.3717 | 177827.941 | 24.5677 | 4246.5432 | 5714.0289 | 86.5715 | 116.4882
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.7861 | 57.687 | 6.2607 | 4 | 4196.3861 | 5636.0382 | 85.549 | 114.8983 | 157.6977 | 0 | 219.1916 | 8226954.0097 | 427847.8497 | 8513662.8716 | 8113429.1827 | 0 | 567218.8699 | 0 | 10081153.9856 | 26229094.7415 | 17901896.1151 | 80061257.6257 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 105088609.8678 | 141141306.2355 | 237137.3706 | 25.0426 | 4196.3861 | 5636.0382 | 85.549 | 114.8983
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.5501 | 58.274 | 6.3514 | 4 | 4158.5873 | 5577.6756 | 84.7784 | 113.7085 | 157.6216 | 0 | 236.7111 | 8283851.2088 | 430479.4465 | 8583340.154 | 8197671.0061 | 0 | 535391.3235 | 0 | 10151985.9242 | 26413384.916 | 18027677.946 | 80623781.9251 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 105651134.1671 | 141703830.5348 | 316227.766 | 25.4055 | 4158.5873 | 5577.6756 | 84.7784 | 113.7085
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.8607 | 58.709 | 6.4199 | 4 | 4130.1234 | 5534.0618 | 84.1982 | 112.8193 | 157.5644 | 0 | 217.4622 | 8325850.6088 | 432415.8299 | 8634891.3632 | 8260144.5971 | 0 | 509528.4942 | 0 | 10203504.0484 | 26547424.5074 | 18119162.7213 | 81032922.1703 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106060274.4123 | 142112970.7801 | 421696.5034 | 25.6797 | 4130.1234 | 5534.0618 | 84.1982 | 112.8193
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.8398 | 59.0333 | 6.4717 | 4 | 4108.7041 | 5501.413 | 83.7615 | 112.1537 | 157.5214 | 0 | 218.5942 | 8357073.9633 | 433851.95 | 8673281.4085 | 8306749.6641 | 0 | 488955.3479 | 0 | 10241365.8102 | 26645933.045 | 18186396.8224 | 81333608.0114 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106360960.2534 | 142413656.6211 | 562341.3252 | 25.8867 | 4108.7041 | 5501.413 | 83.7615 | 112.1537
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5781 | 59.2774 | 6.5109 | 4 | 4092.5957 | 5476.9233 | 83.4331 | 111.6545 | 157.4888 | 0 | 208.442 | 8380533.1649 | 434929.019 | 8702162.255 | 8341856.3567 | 0 | 472896.8761 | 0 | 10269627.292 | 26719463.6235 | 18236582.9531 | 81558051.5403 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106585403.7824 | 142638100.1501 | 749894.2093 | 26.0435 | 4092.5957 | 5476.9233 | 83.4331 | 111.6545
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.1117 | 59.4537 | 6.5399 | 4 | 4080.4883 | 5458.6717 | 83.1863 | 111.2824 | 157.465 | 0 | 209.107 | 8397441.7367 | 435704.2267 | 8722999.2603 | 8367209.9046 | 0 | 460179.5329 | 0 | 10289578.5179 | 26771372.6207 | 18272011.9103 | 81716497.7101 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106743849.9522 | 142796546.3199 | 1000000 | 26.1596 | 4080.4883 | 5458.6717 | 83.1863 | 111.2824
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.5138 | 59.5864 | 6.5618 | 4 | 4071.3923 | 5444.9762 | 83.0008 | 111.0032 | 157.4471 | 0 | 206.6331 | 8410158.2226 | 436286.6682 | 8738681.1572 | 8386304.4073 | 0 | 450426.234 | 0 | 10304524.1088 | 26810257.9827 | 18298551.9689 | 81835190.7498 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106862542.9919 | 142915239.3596 | 1333521.4322 | 26.2472 | 4071.3923 | 5444.9762 | 83.0008 | 111.0032
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.8233 | 59.6885 | 6.5785 | 4 | 4064.5614 | 5434.6645 | 82.8616 | 110.793 | 157.4333 | 0 | 212.2939 | 8419931.8946 | 436734.0113 | 8750740.0983 | 8400995.3001 | 0 | 443076.7197 | 0 | 10316076.4293 | 26840314.7508 | 18319066.3308 | 81926935.5348 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106954287.7769 | 143006984.1446 | 1778279.41 | 26.3139 | 4064.5614 | 5434.6645 | 82.8616 | 110.793
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.0324 | 59.7575 | 6.5904 | 4 | 4059.4332 | 5427.0528 | 82.757 | 110.6378 | 157.4239 | 0 | 201.7552 | 8426526.7323 | 437035.6144 | 8758881.1037 | 8410917.3973 | 0 | 437176.1936 | 0 | 10323509.4461 | 26859653.9358 | 18332265.7219 | 81985966.145 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107013318.387 | 143066014.7547 | 2371373.7057 | 26.3616 | 4059.4332 | 5427.0528 | 82.757 | 110.6378
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1982 | 59.8121 | 6.5996 | 4 | 4055.5843 | 5421.2975 | 82.6786 | 110.5205 | 157.4165 | 0 | 195.779 | 8431751.1272 | 437274.4802 | 8765331.7608 | 8418781.3892 | 0 | 432823.4216 | 0 | 10329525.2498 | 26875305.8229 | 18342948.4564 | 82033741.708 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107061093.95 | 143113790.3177 | 3162277.6602 | 26.3984 | 4055.5843 | 5421.2975 | 82.6786 | 110.5205
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.3297 | 59.8555 | 6.6067 | 4 | 4052.696 | 5416.9436 | 82.6197 | 110.4317 | 157.4106 | 0 | 195.494 | 8435893.6591 | 437463.8472 | 8770447.4412 | 8425019.183 | 0 | 429628.5508 | 0 | 10334396.5457 | 26887979.9356 | 18351598.7988 | 82072427.9613 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107099780.2033 | 143152476.571 | 4216965.0343 | 26.4268 | 4052.696 | 5416.9436 | 82.6197 | 110.4317
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.4151 | 59.8836 | 6.6117 | 4 | 4050.5291 | 5413.748 | 82.5755 | 110.3666 | 157.4068 | 0 | 195.5947 | 8438580.7423 | 437586.6084 | 8773766.8789 | 8429067.6122 | 0 | 427039.6616 | 0 | 10337356.1863 | 26895680.3135 | 18356854.4649 | 82095932.4682 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107123284.7102 | 143175981.0779 | 5623413.2519 | 26.4467 | 4050.5291 | 5413.748 | 82.5755 | 110.3666
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.4929 | 59.9092 | 6.6158 | 4 | 4048.9034 | 5411.2795 | 82.5424 | 110.3163 | 157.4033 | 0 | 217.9004 | 8441029.611 | 437698.5206 | 8776791.7282 | 8432756.9473 | 0 | 425274.2308 | 0 | 10340284.9048 | 26903300.2381 | 18362055.22 | 82119191.4007 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107146543.6427 | 143199240.0104 | 7498942.0933 | 26.4631 | 4048.9034 | 5411.2795 | 82.5424 | 110.3163
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.5466 | 59.9269 | 6.6187 | 4 | 4047.684 | 5409.4525 | 82.5175 | 110.279 | 157.4009 | 0 | 202.6838 | 8442719.6495 | 437775.7289 | 8778879.6655 | 8435303.8785 | 0 | 423883.3194 | 0 | 10342239.2743 | 26908385.1067 | 18365525.7474 | 82134712.3702 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107162064.6122 | 143214760.9799 | 10000000 | 26.4749 | 4047.684 | 5409.4525 | 82.5175 | 110.279
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0039 | [19 empty] | 100 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9806 | [19 empty] | 133.3521 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2285 | [19 empty] | 177.8279 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5834 | 0.3271 | 0.011941 | 4 | 567482.2676 | 1338782.4092 | 11568.8936 | 27292.8902 | 115.7054 | 0 | 48.6434 | 178068.6221 | 6935.5409 | 139746.973 | 82828.7765 | 0 | 81649.7905 | 0 | 190799.5842 | 496421.3797 | 338817.7921 | 1515268.459 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 27106210.754 | 63947933.1958 | 237.1374 | 0.047766 | 567482.2676 | 1338782.4092 | 11568.8936 | 27292.8902
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.49292 | 0.025213 | 4 | 273776.467 | 639083.4358 | 5581.3036 | 13028.5803 | 124.9736 | 0 | 325.3839 | 248712.3534 | 10347.7569 | 192754.7504 | 106602.5024 | 0 | 93708.799 | 0 | 254329.2032 | 661712.4166 | 451632.3212 | 2019800.103 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 27610742.3979 | 64452464.8397 | 316.2278 | 0.10085 | 273776.467 | 639083.4358 | 5581.3036 | 13028.5803
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7016 | 0.71244 | 0.044666 | 4 | 157961.7973 | 364170.3969 | 3220.2649 | 7424.1061 | 132.5654 | 0 | 421.7479 | 333582.8341 | 14660.9425 | 257464.9142 | 137631.6728 | 0 | 106086.6436 | 0 | 331276.5328 | 861913.5841 | 588273.7317 | 2630890.8558 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 28221833.1507 | 65063555.5925 | 421.6965 | 0.17866 | 157961.7973 | 364170.3969 | 3220.2649 | 7424.1061
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5573 | 1.0249 | 0.073313 | 4 | 98987.086 | 224619.0362 | 2017.9856 | 4579.1629 | 139.1936 | 0 | 556.2783 | 443059.5922 | 20431.7847 | 342874.5735 | 180870.8464 | 0 | 122501.6047 | 0 | 432797.9766 | 1126051.556 | 768553.325 | 3437141.2592 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 29028083.5541 | 65869805.9959 | 562.3413 | 0.29325 | 98987.086 | 224619.0362 | 2017.9856 | 4579.1629
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6574 | 1.4372 | 0.11293 | 4 | 66449.4991 | 148009.6117 | 1354.6629 | 3017.3761 | 144.465 | 0 | 73.6069 | 574387.3516 | 27555.1391 | 447795.692 | 238305.5496 | 0 | 140682.382 | 0 | 557203.1846 | 1449728.3881 | 989469.4138 | 4425127.1008 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 30016069.3958 | 66857791.8376 | 749.8942 | 0.45171 | 66449.4991 | 148009.6117 | 1354.6629 | 3017.3761
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1506 | 2.0039 | 0.16798 | 4 | 46556.0148 | 101388.0017 | 949.1073 | 2066.9316 | 148.7939 | 0 | 76.7221 | 738134.151 | 36569.8148 | 582541.8694 | 315832.3432 | 0 | 164077.7667 | 0 | 716490.8186 | 1864162.1376 | 1272328.9636 | 5690137.865 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 31281080.16 | 68122802.6018 | 1000 | 0.6719 | 46556.0148 | 101388.0017 | 949.1073 | 2066.9316
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0996 | 2.7457 | 0.24096 | 4 | 34058.8222 | 72282.5148 | 694.3352 | 1473.5768 | 152.0326 | 0 | 65.2928 | 932814.6648 | 47345.2567 | 747891.2641 | 416981.195 | 0 | 191389.0711 | 0 | 911204.3662 | 2370766.8471 | 1618097.0875 | 7236489.7527 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 32827432.0476 | 69669154.4894 | 1333.5214 | 0.96385 | 34058.8222 | 72282.5148 | 694.3352 | 1473.5768
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7326 | 3.7717 | 0.34412 | 4 | 25318.9141 | 52083.9417 | 516.1603 | 1061.8016 | 154.908 | 0 | 93.1498 | 1180453.7602 | 61319.8886 | 962227.2164 | 560133.0541 | 0 | 225683.6558 | 0 | 1166028.8543 | 3033767.8935 | 2070608.925 | 9260223.248 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 34851165.543 | 71692887.9847 | 1778.2794 | 1.3765 | 25318.9141 | 52083.9417 | 516.1603 | 1061.8016
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1969 | 5.1132 | 0.47869 | 4 | 19491.0036 | 38731.8292 | 397.3505 | 789.6007 | 156.9821 | 0 | 72.5533 | 1474273.1765 | 77753.2076 | 1225806.0211 | 742722.379 | 0 | 266611.1021 | 0 | 1476994.6957 | 3842837.2249 | 2622815.3684 | 11729813.1753 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 37320755.4703 | 74162477.9121 | 2371.3737 | 1.9148 | 19491.0036 | 38731.8292 | 397.3505 | 789.6007
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.799 | 6.9027 | 0.65909 | 4 | 15338.7917 | 29313.1788 | 312.702 | 597.5888 | 158.5827 | 0 | 65.5896 | 1833501.6996 | 97869.6172 | 1556716.2739 | 989055.3656 | 0 | 316737.0648 | 0 | 1869613.2082 | 4864350.0574 | 3320018.8666 | 14847862.1533 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 40438804.4482 | 77280526.89 | 3162.2777 | 2.6364 | 15338.7917 | 29313.1788 | 312.702 | 597.5888
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8937 | 9.2706 | 0.89746 | 4 | 12347.0988 | 22609.8822 | 251.7123 | 460.933 | 159.8087 | 0 | 87.8495 | 2268349.8646 | 122052.7727 | 1969450.9021 | 1310642.7932 | 0 | 377808.3008 | 0 | 2358838.807 | 6137214.7114 | 4188775.1477 | 18733133.2994 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 44324075.5943 | 81165798.0361 | 4216.965 | 3.5898 | 12347.0988 | 22609.8822 | 251.7123 | 460.933
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.8863 | 12.3834 | 1.2118 | 4 | 10145.2726 | 17745.8479 | 206.8251 | 361.7731 | 160.7396 | 0 | 92.7051 | 2793980.3405 | 151241.6285 | 2481173.9651 | 1737222.0453 | 0 | 451356.838 | 0 | 2969840.1788 | 7726914.9473 | 5273778.2237 | 23585508.1672 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 49176450.4622 | 86018172.904 | 5623.4133 | 4.8472 | 10145.2726 | 17745.8479 | 206.8251 | 361.7731
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.2884 | 16.4365 | 1.621 | 4 | 8509.9813 | 14191.988 | 173.4875 | 289.3229 | 161.4426 | 0 | 93.0568 | 3423755.969 | 186053.3095 | 3110474.2531 | 2292622.6309 | 0 | 539803.3797 | 0 | 3725556.7215 | 9693134.3726 | 6615763.3833 | 29587164.0197 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 55178106.3146 | 92019828.7564 | 7498.9421 | 6.4839 | 8509.9813 | 14191.988 | 173.4875 | 289.3229
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.5721 | 21.6065 | 2.1417 | 4 | 7291.8501 | 11592.4378 | 148.6542 | 236.3275 | 161.9415 | 0 | 99.3807 | 4164354.9036 | 226727.0008 | 3869919.5062 | 3000488.5101 | 0 | 644522.968 | 0 | 4643345.0266 | 12081031.2782 | 8245552.0877 | 36875941.2811 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 62466883.5761 | 99308606.0179 | 10000 | 8.5667 | 7291.8501 | 11592.4378 | 148.6542 | 236.3275
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0495 | 27.9812 | 2.7789 | 4 | 6392.7388 | 9707.1901 | 130.3246 | 197.8942 | 162.1919 | 0 | 113.649 | 5007947.968 | 272570.6876 | 4758322.4506 | 3874922.7045 | 0 | 766153.8615 | 0 | 5725167.8922 | 14895712.462 | 10166629.8316 | 45467427.8581 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 71058370.1531 | 107900092.5948 | 13335.2143 | 11.1155 | 6392.7388 | 9707.1901 | 130.3246 | 197.8942
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.6279 | 35.4439 | 3.5117 | 4 | 5746.6311 | 8369.449 | 117.1528 | 170.6225 | 162.1029 | 0 | 121.9267 | 5921657.7553 | 321263.0549 | 5749374.3457 | 4903640.4875 | 0 | 903637.0832 | 0 | 6941833.3634 | 18061226.4458 | 12327158.1703 | 55129790.7062 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 80720733.0012 | 117562455.4429 | 17782.7941 | 14.0466 | 5746.6311 | 8369.449 | 117.1528 | 170.6225
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.6876 | 42.5361 | 4.2226 | 4 | 5300.005 | 7481.2095 | 108.0478 | 152.5146 | 161.7008 | 0 | 124.9128 | 6730806.02 | 363170.8072 | 6654417.2674 | 5889023.5983 | 0 | 1003128.5171 | 0 | 8049813.0219 | 20943962.2393 | 14294684.5837 | 63929006.0548 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 89519948.3498 | 126361670.7915 | 23713.7371 | 16.8905 | 5300.005 | 7481.2095 | 108.0478 | 152.5146
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9038 | 46.2507 | 4.7095 | 4 | 4974.0558 | 6929.7661 | 101.4029 | 141.2727 | 161.3763 | 0 | 168.471 | 7134567.2148 | 383522.2227 | 7116927.4048 | 6409173.008 | 0 | 946407.5157 | 0 | 8576332.9727 | 22313859.1473 | 15229667.372 | 68110456.858 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 93701399.153 | 130543121.5948 | 31622.7766 | 18.838 | 4974.0558 | 6929.7661 | 101.4029 | 141.2727
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.6823 | 49.3902 | 5.1369 | 4 | 4727.2738 | 6520.2799 | 96.3719 | 132.9247 | 161.0459 | 0 | 184.0283 | 7465942.8045 | 399896.7382 | 7502512.8191 | 6851399.3326 | 0 | 878948.8597 | 0 | 9008493.2161 | 23438251.4521 | 15997088.224 | 71542533.4462 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 97133475.7412 | 133975198.183 | 42169.6503 | 20.5475 | 4727.2738 | 6520.2799 | 96.3719 | 132.9247
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0903 | 52.7087 | 5.5518 | 4 | 4539.2752 | 6198.271 | 92.5393 | 126.3601 | 160.6727 | 0 | 210.0687 | 7807520.1722 | 416509.1913 | 7905170.9933 | 7317069.6365 | 0 | 837775.6151 | 0 | 9470777.7873 | 24641021.0788 | 16818003.2087 | 75213847.6832 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 100804789.9781 | 137646512.4199 | 56234.1325 | 22.2072 | 4539.2752 | 6198.271 | 92.5393 | 126.3601
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.446 | 54.9358 | 5.8662 | 4 | 4395.1793 | 5965.2628 | 89.6017 | 121.61 | 160.4252 | 0 | 225.5429 | 8032645.6993 | 427376.8739 | 8172677.8596 | 7629751.8024 | 0 | 772997.5088 | 0 | 9763825.4001 | 25403470.8552 | 17338390.8478 | 77541136.847 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 103132079.142 | 139973801.5838 | 74989.4209 | 23.4648 | 4395.1793 | 5965.2628 | 89.6017 | 121.61
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.4586 | 56.6761 | 6.1189 | 4 | 4286.1663 | 5791.3976 | 87.3793 | 118.0655 | 160.22 | 0 | 227.1938 | 8205937.8338 | 435647.0607 | 8380347.2011 | 7874622.9145 | 0 | 712054.8645 | 0 | 9987357.8511 | 25985056.4397 | 17735334.9596 | 79316359.1248 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 104907301.4198 | 141749023.8616 | 100000 | 24.4758 | 4286.1663 | 5791.3976 | 87.3793 | 118.0655
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3614 | 58.0211 | 6.3187 | 4 | 4203.7669 | 5661.4022 | 85.6995 | 115.4153 | 160.0545 | 0 | 225.7125 | 8338327.4207 | 441907.1277 | 8540062.4568 | 8064213.5231 | 0 | 657669.2219 | 0 | 10156450.1026 | 26424999.7926 | 18035605.3379 | 80659234.9833 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 106250177.2782 | 143091899.72 | 133352.1432 | 25.275 | 4203.7669 | 5661.4022 | 85.6995 | 115.4153
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.3971 | 59.0643 | 6.4762 | 4 | 4141.5397 | 5563.7451 | 84.4309 | 113.4245 | 159.9225 | 0 | 215.696 | 8440471.2021 | 446744.8455 | 8663415.2102 | 8214362.5649 | 0 | 611329.2272 | 0 | 10286765.9895 | 26764054.9987 | 18267017.483 | 81694161.5211 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 107285103.8161 | 144126826.2578 | 177827.941 | 25.9046 | 4141.5397 | 5563.7451 | 84.4309 | 113.4245
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6427 | 59.8342 | 6.5962 | 4 | 4094.6046 | 5490.9245 | 83.4741 | 111.9399 | 159.823 | 0 | 230.8836 | 8515565.1898 | 450305.659 | 8754170.5177 | 8326979.0996 | 0 | 571620.2392 | 0 | 10381269.875 | 27009934.7236 | 18434835.4475 | 82444680.7515 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 108035623.0464 | 144877345.4882 | 237137.3706 | 26.3849 | 4094.6046 | 5490.9245 | 83.4741 | 111.9399
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3212 | 60.4078 | 6.6875 | 4 | 4059.2365 | 5436.5013 | 82.753 | 110.8304 | 159.7476 | 0 | 228.6252 | 8571245.3114 | 452936.0277 | 8821647.062 | 8411065.9068 | 0 | 538878.6846 | 0 | 10450351.4671 | 27189670.8555 | 18557509.0508 | 82993304.3659 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 108584246.6609 | 145425969.1027 | 316227.766 | 26.7499 | 4059.2365 | 5436.5013 | 82.753 | 110.8304
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5781 | 60.8363 | 6.7567 | 4 | 4032.604 | 5395.7675 | 82.2101 | 110 | 159.6905 | 0 | 221.4318 | 8612692.5799 | 454888.4737 | 8871978.4802 | 8473986.5904 | 0 | 512493.8893 | 0 | 10501155.6052 | 27321852.8017 | 18647725.9451 | 83396774.3654 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 108987716.6604 | 145829439.1022 | 421696.5034 | 27.0266 | 4032.604 | 5395.7675 | 82.2101 | 110
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.5138 | 61.1547 | 6.8088 | 4 | 4012.5631 | 5365.2868 | 81.8015 | 109.3786 | 159.6477 | 0 | 221.2945 | 8643410.482 | 456332.3766 | 8909338.3333 | 8520802.3706 | 0 | 491502.3885 | 0 | 10538340.5209 | 27418600.3245 | 18713758.1174 | 83692084.9138 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109283027.2088 | 146124749.6505 | 562341.3252 | 27.2352 | 4012.5631 | 5365.2868 | 81.8015 | 109.3786
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2176 | 61.3939 | 6.8482 | 4 | 3997.4916 | 5342.4295 | 81.4943 | 108.9127 | 159.6153 | 0 | 206.917 | 8666439.3652 | 457413.117 | 8937378.811 | 8556002.2592 | 0 | 475113.8894 | 0 | 10566015.5024 | 27490604.9494 | 18762902.7534 | 83911870.6471 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109502812.9421 | 146344535.3839 | 749894.2093 | 27.3929 | 3997.4916 | 5342.4295 | 81.4943 | 108.9127
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.7272 | 61.5668 | 6.8774 | 4 | 3986.1635 | 5325.3882 | 81.2633 | 108.5652 | 159.5918 | 0 | 206.2111 | 8683067.9165 | 458192.4919 | 8957644.1683 | 8581476.1811 | 0 | 462172.6357 | 0 | 10585595.8235 | 27541548.9284 | 18797673.0659 | 84067371.2114 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109658313.5064 | 146500035.9482 | 1000000 | 27.5097 | 3986.1635 | 5325.3882 | 81.2633 | 108.5652
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0996 | 61.6932 | 6.8992 | 4 | 3977.6529 | 5312.6594 | 81.0898 | 108.3057 | 159.5745 | 0 | 216.2848 | 8695200.6685 | 458760.6164 | 8972440.0834 | 8600093.1855 | 0 | 452097.4096 | 0 | 10599650.8657 | 27578117.2652 | 18822631.7071 | 84178991.8014 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109769934.0964 | 146611656.5381 | 1333521.4322 | 27.5967 | 3977.6529 | 5312.6594 | 81.0898 | 108.3057
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.389 | 61.7913 | 6.9158 | 4 | 3971.2615 | 5303.0616 | 80.9595 | 108.1101 | 159.5611 | 0 | 256.1897 | 8704615.4178 | 459201.2141 | 8983926.3112 | 8614555.5794 | 0 | 444538.0505 | 0 | 10610666.2635 | 27606777.0706 | 18842192.6132 | 84266472.5203 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109857414.8153 | 146699137.2571 | 1778279.41 | 27.6631 | 3971.2615 | 5303.0616 | 80.9595 | 108.1101
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5741 | 61.854 | 6.9274 | 4 | 3966.4637 | 5296.029 | 80.8617 | 107.9667 | 159.5524 | 0 | 229.1537 | 8710628.0494 | 459482.3989 | 8991265.1213 | 8623801.6324 | 0 | 438354.2529 | 0 | 10617177.2674 | 27623717.3673 | 18853754.7138 | 84318180.8033 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109909123.0983 | 146750845.54 | 2371373.7057 | 27.7096 | 3966.4637 | 5296.029 | 80.8617 | 107.9667
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.725 | 61.9051 | 6.9365 | 4 | 3962.8631 | 5290.6922 | 80.7883 | 107.8579 | 159.5454 | 0 | 240.7478 | 8715532.0773 | 459711.76 | 8997251.0348 | 8631344.4839 | 0 | 433837.1096 | 0 | 10622693.8216 | 27638070.3097 | 18863550.8919 | 84361991.4888 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109952933.7838 | 146794656.2256 | 3162277.6602 | 27.7458 | 3962.8631 | 5290.6922 | 80.7883 | 107.8579
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8519 | 61.9481 | 6.9436 | 4 | 3960.1612 | 5286.6196 | 80.7332 | 107.7749 | 159.5395 | 0 | 220.1773 | 8719652.8693 | 459904.4886 | 9002281.2642 | 8637684.1998 | 0 | 430609.5725 | 0 | 10627551.6338 | 27650709.3405 | 18872177.2902 | 84400570.6589 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109991512.9538 | 146833235.3956 | 4216965.0343 | 27.7745 | 3960.1612 | 5286.6196 | 80.7332 | 107.7749
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.9251 | 61.9729 | 6.9484 | 4 | 3958.1341 | 5283.6782 | 80.6919 | 107.7149 | 159.5361 | 0 | 215.1176 | 8722026.2092 | 460015.3914 | 9005179.7184 | 8641339.0969 | 0 | 427873.2478 | 0 | 10630009.1288 | 27657103.2385 | 18876541.2569 | 84420087.2879 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 110011029.5828 | 146852752.0246 | 5623413.2519 | 27.7937 | 3958.1341 | 5283.6782 | 80.6919 | 107.7149
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.0003 | 61.9984 | 6.9526 | 4 | 3956.6133 | 5281.3681 | 80.6609 | 107.6678 | 159.5326 | 0 | 250.7127 | 8724466.9234 | 460129.5167 | 9008159.6552 | 8645095.9965 | 0 | 426090.6505 | 0 | 10632937.6695 | 27664722.7006 | 18881741.6963 | 84443344.8086 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 110034287.1036 | 146876009.5454 | 7498942.0933 | 27.8102 | 3956.6133 | 5281.3681 | 80.6609 | 107.6678
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.0493 | 62.015 | 6.9555 | 4 | 3955.4726 | 5279.6732 | 80.6377 | 107.6333 | 159.5303 | 0 | 235.0054 | 8726059.1798 | 460203.9359 | 9010104.1472 | 8647548.1603 | 0 | 424648.9986 | 0 | 10634740.1245 | 27669412.3188 | 18884942.4572 | 84457659.3223 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 110048601.6173 | 146890324.0591 | 10000000 | 27.8219 | 3955.4726 | 5279.6732 | 80.6377 | 107.6333
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5344 | [19 empty] | 100 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5921 | [19 empty] | 133.3521 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7033 | [19 empty] | 177.8279 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.34825 | 0.013748 | 4 | 504512.6331 | 1188962.2329 | 10285.1724 | 24238.6033 | 117.8245 | 0 | 237.1721 | 188185.9104 | 7439.729 | 146707.0446 | 85604.3976 | 0 | 83336.9515 | 0 | 199396.8729 | 518789.7613 | 354084.6722 | 1583545.3394 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 27743937.7782 | 65382890.4212 | 237.1374 | 0.054992 | 504512.6331 | 1188962.2329 | 10285.1724 | 24238.6033
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.51532 | 0.027816 | 4 | 253848.2309 | 592137.6677 | 5175.0395 | 12071.5273 | 126.7908 | 0 | 318.0943 | 258873.1848 | 10909.2363 | 199479.5617 | 109261.2741 | 0 | 94141.8731 | 0 | 262339.4007 | 682553.3074 | 465856.6573 | 2083414.4953 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 28243806.9341 | 65882759.5771 | 316.2278 | 0.11126 | 253848.2309 | 592137.6677 | 5175.0395 | 12071.5273
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.76 | 0.7479 | 0.0489 | 4 | 147678.0658 | 340105.147 | 3010.6171 | 6933.5034 | 134.5605 | 0 | 417.2252 | 348324.6173 | 15530.2799 | 267305.0784 | 141889.5074 | 0 | 106956.8103 | 0 | 343202.4544 | 892942.3858 | 609451.5264 | 2725602.6598 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 28885995.0985 | 66524947.7416 | 421.6965 | 0.1956 | 147678.0658 | 340105.147 | 3010.6171 | 6933.5034
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6157 | 1.069 | 0.079355 | 4 | 93586.9068 | 212164.6434 | 1907.8957 | 4325.2632 | 141.1492 | 0 | 546.8398 | 460376.795 | 21543.1481 | 354168.5233 | 186181.5049 | 0 | 122605.422 | 0 | 446501.4034 | 1161705.0616 | 792887.5752 | 3545969.4334 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 29706361.8721 | 67345314.5152 | 562.3413 | 0.31742 | 93586.9068 | 212164.6434 | 1907.8957 | 4325.2632
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7622 | 1.5094 | 0.1223 | 4 | 62857.8131 | 139795.6471 | 1281.4415 | 2849.9234 | 146.6029 | 0 | 69.9374 | 599726.8352 | 29223.1056 | 465042.3894 | 246137.7153 | 0 | 141969.2919 | 0 | 578018.7416 | 1503886.1977 | 1026433.2317 | 4590437.5085 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 30750829.9472 | 68389782.5903 | 749.8942 | 0.48921 | 62857.8131 | 139795.6471 | 1281.4415 | 2849.9234
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.258 | 2.092 | 0.18057 | 4 | 44354.8563 | 96465.735 | 904.2337 | 1966.5845 | 150.8995 | 0 | 59.435 | 767255.4588 | 38613.4122 | 602128.6703 | 324960.4717 | 0 | 164366.3079 | 0 | 739956.4851 | 1925214.9884 | 1313998.7888 | 5876494.5831 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 32036887.0218 | 69675839.6649 | 1000 | 0.72229 | 44354.8563 | 96465.735 | 904.2337 | 1966.5845
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2608 | 2.8777 | 0.25994 | 4 | 32385.6524 | 68585.1119 | 660.2253 | 1398.2003 | 154.1865 | 0 | 55.4928 | 973263.7148 | 50300.5154 | 775334.1426 | 434317.1327 | 0 | 192512.501 | 0 | 946033.9225 | 2461386.2082 | 1679946.6635 | 7513094.8007 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 33673487.2394 | 71312439.8825 | 1333.5214 | 1.0398 | 32385.6524 | 68585.1119 | 660.2253 | 1398.2003
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.928 | 3.9417 | 0.36924 | 4 | 24197.3285 | 49681.0696 | 493.2953 | 1012.8158 | 157.1042 | 0 | 89.1831 | 1228223.6076 | 64904.3421 | 995349.1483 | 577843.7726 | 0 | 226275.6801 | 0 | 1206112.6548 | 3138057.7201 | 2141788.8746 | 9578555.8002 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 35738948.2389 | 73377900.882 | 1778.2794 | 1.477 | 24197.3285 | 49681.0696 | 493.2953 | 1012.8158
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4527 | 5.3456 | 0.51379 | 4 | 18640.0056 | 36954.3508 | 380.0017 | 753.3644 | 159.2028 | 0 | 80.7786 | 1534967.5373 | 82449.1956 | 1268283.8376 | 769157.9218 | 0 | 267276.0255 | 0 | 1529632.462 | 3979789.8953 | 2716288.38 | 12147845.2551 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 38308237.6939 | 75947190.3369 | 2371.3737 | 2.0552 | 18640.0056 | 36954.3508 | 380.0017 | 753.3644
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1326 | 7.2116 | 0.70617 | 4 | 14700.1436 | 28025.1394 | 299.6823 | 571.3304 | 160.822 | 0 | 88.8588 | 1907732.8848 | 103697.4858 | 1609848.8696 | 1021547.6141 | 0 | 317349.333 | 0 | 1934468.713 | 5033090.7772 | 3435187.8751 | 15362923.5525 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 41523315.9913 | 79162268.6343 | 3162.2777 | 2.8247 | 14700.1436 | 28025.1394 | 299.6823 | 571.3304
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3152 | 9.6821 | 0.96157 | 4 | 11843.404 | 21629.1674 | 241.4438 | 440.9398 | 162.0605 | 0 | 88.9642 | 2360478.9287 | 129456.7344 | 2035982.3676 | 1357225.4328 | 0 | 378164.0064 | 0 | 2441909.9132 | 6353348.6896 | 4336291.0289 | 19392857.1016 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 45553249.5404 | 83192202.1834 | 4216.965 | 3.8463 | 11843.404 | 21629.1674 | 241.4438 | 440.9398
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4394 | 12.9306 | 1.2976 | 4 | 9743.804 | 16995.588 | 198.6406 | 346.478 | 163.0036 | 0 | 99.2651 | 2907167.646 | 160426.4714 | 2564605.0055 | 1798134.4618 | 0 | 451777.9333 | 0 | 3074023.492 | 7997978.5573 | 5458784.7074 | 24412898.2747 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 50573290.7134 | 88212243.3565 | 5623.4133 | 5.1903 | 9743.804 | 16995.588 | 198.6406 | 346.478
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.0117 | 17.1459 | 1.7319 | 4 | 8188.5086 | 13621.7049 | 166.9338 | 277.6969 | 163.7152 | 0 | 88.8496 | 3558573.2583 | 196977.9512 | 3212741.0283 | 2360303.8201 | 0 | 540222.1067 | 0 | 3848839.0842 | 10013889.7917 | 6834685.5477 | 30566232.5883 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 56726625.027 | 94365577.6701 | 7498.9421 | 6.9276 | 8188.5086 | 13621.7049 | 166.9338 | 277.6969
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4736 | 22.5111 | 2.2842 | 4 | 7026.3573 | 11145.8348 | 143.2418 | 227.2229 | 164.2152 | 0 | 110.6715 | 4323961.857 | 239725.8346 | 3993306.9762 | 3079718.2619 | 0 | 644560.8364 | 0 | 4789696.7688 | 12461808.4904 | 8505440.3593 | 38038219.3845 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 64198611.8232 | 101837564.4663 | 10000 | 9.1368 | 7026.3573 | 11145.8348 | 143.2418 | 227.2229
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1432 | 29.118 | 2.9595 | 4 | 6167.4253 | 9346.8842 | 125.7313 | 190.5489 | 164.4555 | 0 | 102.5008 | 5195418.9466 | 287922.3739 | 4905413.4898 | 3971826.2456 | 0 | 765914.4083 | 0 | 5899333.231 | 15348854.9475 | 10475908.8891 | 46850592.5317 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 73010984.9705 | 110649937.6135 | 13335.2143 | 11.8382 | 6167.4253 | 9346.8842 | 125.7313 | 190.5489
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8802 | 36.8229 | 3.733 | 4 | 5551.1354 | 8071.8123 | 113.1674 | 164.5548 | 164.3425 | 0 | 97.5047 | 6135804.807 | 338860.8679 | 5919331.2676 | 5019223.2141 | 0 | 902882.2981 | 0 | 7143279.9573 | 18585349.1607 | 12684882.6929 | 56729614.2656 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 82890006.7044 | 120528959.3474 | 17782.7941 | 14.9321 | 5551.1354 | 8071.8123 | 113.1674 | 164.5548
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.4092 | 44.6431 | 4.5137 | 4 | 5127 | 7211.7284 | 104.5208 | 147.0208 | 163.8692 | 0 | 116.9254 | 7023804.7508 | 385531.8012 | 6907377.2983 | 6098001.168 | 0 | 1025432.8801 | 0 | 8361657.6803 | 21755318.0724 | 14848451.6115 | 66405575.2626 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 92565967.7014 | 130204920.3444 | 23713.7371 | 18.0546 | 5127 | 7211.7284 | 104.5208 | 147.0208
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.501 | 48.4048 | 5.0185 | 4 | 4821.6563 | 6696.6644 | 98.296 | 136.5206 | 163.5228 | 0 | 138.0955 | 7431261.2605 | 406461.622 | 7370665.4448 | 6631737.0413 | 0 | 963831.1017 | 0 | 8893543.0234 | 23139174.6305 | 15792962.1478 | 70629636.2721 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 96790028.7108 | 134428981.3539 | 31622.7766 | 20.074 | 4821.6563 | 6696.6644 | 98.296 | 136.5206
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1501 | 51.5799 | 5.4605 | 4 | 4590.6145 | 6313.8408 | 93.5859 | 128.7162 | 163.1754 | 0 | 188.5756 | 7765814.7175 | 423342.53 | 7756517.6705 | 7088901.3608 | 0 | 892576.4318 | 0 | 9331589.5572 | 24278881.8555 | 16570835.7475 | 74108459.8709 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 100268852.3097 | 137907804.9527 | 42169.6503 | 21.8421 | 4590.6145 | 6313.8408 | 93.5859 | 128.7162
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.4728 | 54.9627 | 5.8918 | 4 | 4413.6256 | 6010.7195 | 89.9777 | 122.5366 | 162.8015 | 0 | 192.4078 | 8113770.4894 | 440636.9564 | 8162770.8108 | 7570699.2661 | 0 | 849290.7415 | 0 | 9803495.623 | 25506684.6376 | 17408836.3751 | 77856184.8997 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 104016577.3385 | 141655529.9815 | 56234.1325 | 23.5672 | 4413.6256 | 6010.7195 | 89.9777 | 122.5366
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6749 | 57.1861 | 6.2122 | 4 | 4278.8188 | 5793.5403 | 87.2295 | 118.1092 | 162.5485 | 0 | 205.8051 | 8337704.4868 | 451588.844 | 8427310.6037 | 7883465.341 | 0 | 781876.8508 | 0 | 10093958.9892 | 26262410.7342 | 17924634.9647 | 80162950.8142 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 106323343.2529 | 143962295.896 | 74989.4209 | 24.8488 | 4278.8188 | 5793.5403 | 87.2295 | 118.1092
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.5929 | 58.9335 | 6.4701 | 4 | 4176.8213 | 5631.17 | 85.1502 | 114.799 | 162.3388 | 0 | 201.8969 | 8511180.0394 | 459977.7011 | 8633912.6568 | 8130090.7668 | 0 | 719539.0932 | 0 | 10317333.1003 | 26843584.351 | 18321297.9001 | 81936915.6087 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 108097308.0475 | 145736260.6905 | 100000 | 25.8803 | 4176.8213 | 5631.17 | 85.1502 | 114.799
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3714 | 60.2664 | 6.6723 | 4 | 4099.7352 | 5510.0012 | 83.5786 | 112.3288 | 162.1723 | 0 | 190.6487 | 8642047.7147 | 466248.2983 | 8790774.6108 | 8318732.9038 | 0 | 663591.3704 | 0 | 10483744.0102 | 27276551.403 | 18616806.8096 | 83258497.1209 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 109418889.5596 | 147057842.2026 | 133352.1432 | 26.6893 | 4099.7352 | 5510.0012 | 83.5786 | 112.3288
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.2749 | 61.2851 | 6.8297 | 4 | 4041.5343 | 5419.3032 | 82.3921 | 110.4798 | 162.0412 | 0 | 216.6549 | 8741209.0835 | 470965.203 | 8910226.5633 | 8463197.9617 | 0 | 615710.7105 | 0 | 10608510.7136 | 27601168.772 | 18838364.8342 | 84249353.8418 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 110409746.2806 | 148048698.9236 | 177827.941 | 27.3188 | 4041.5343 | 5419.3032 | 82.3921 | 110.4798
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.5038 | 62.0629 | 6.9513 | 4 | 3997.6235 | 5351.2866 | 81.497 | 109.0932 | 161.9389 | 0 | 237.7343 | 8816473.7763 | 474528.2768 | 9001204.8553 | 8573656.26 | 0 | 576049.9228 | 0 | 10702346.1056 | 27845309.2137 | 19004995.7022 | 84994564.1128 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 111154956.5515 | 148793909.1945 | 237137.3706 | 27.8053 | 3997.6235 | 5351.2866 | 81.497 | 109.0932
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.1387 | 62.6312 | 7.0428 | 4 | 3964.5228 | 5300.598 | 80.8222 | 108.0599 | 161.8628 | 0 | 230.574 | 8871206.8903 | 477109.5342 | 9067541.6201 | 8654434.3419 | 0 | 542977.6507 | 0 | 10769175.3145 | 28019185.1068 | 19123669.5721 | 85525300.0306 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 111685692.4693 | 149324645.1124 | 316227.766 | 28.1713 | 3964.5228 | 5300.598 | 80.8222 | 108.0599
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.3614 | 63.0551 | 7.1121 | 4 | 3939.5928 | 5262.6544 | 80.3139 | 107.2863 | 161.8053 | 0 | 217.7379 | 8911888.504 | 479021.8216 | 9116955.1071 | 8714747.3069 | 0 | 516357.5882 | 0 | 10818198.4278 | 28146733.1916 | 19210723.7608 | 85914625.7079 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112075018.1467 | 149713970.7897 | 421696.5034 | 28.4484 | 3939.5928 | 5262.6544 | 80.3139 | 107.2863
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.2628 | 63.3671 | 7.164 | 4 | 3920.8301 | 5234.297 | 79.9314 | 106.7082 | 161.7626 | 0 | 230.5587 | 8941745.8563 | 480421.7853 | 9153280.5329 | 8759163.3813 | 0 | 495092.3253 | 0 | 10853584.5136 | 28238800.528 | 19273561.6097 | 86195650.5323 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112356042.9711 | 149994995.6141 | 562341.3252 | 28.6562 | 3920.8301 | 5234.297 | 79.9314 | 106.7082
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.9445 | 63.6027 | 7.2034 | 4 | 3906.7183 | 5213.0092 | 79.6437 | 106.2742 | 161.7302 | 0 | 218.6474 | 8964249.2493 | 481475.0074 | 9180691.7825 | 8792723.4136 | 0 | 478560.6734 | 0 | 10880103.0492 | 28307796.318 | 19320652.6541 | 86406252.1475 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112566644.5862 | 150205597.2293 | 749894.2093 | 28.8136 | 3906.7183 | 5213.0092 | 79.6437 | 106.2742
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.4413 | 63.7741 | 7.2327 | 4 | 3896.1104 | 5197.118 | 79.4275 | 105.9503 | 161.7064 | 0 | 255.1842 | 8980604.1478 | 482239.3392 | 9200632.3278 | 8817160.9895 | 0 | 465567.5203 | 0 | 10899019.6866 | 28357013.5282 | 19354244.4113 | 86556481.9507 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112716874.3895 | 150355827.0325 | 1000000 | 28.9306 | 3896.1104 | 5197.118 | 79.4275 | 105.9503
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8117 | 63.9019 | 7.2546 | 4 | 3888.1404 | 5185.2106 | 79.265 | 105.7075 | 161.6887 | 0 | 247.6859 | 8992777.7621 | 482807.6698 | 9215484.8915 | 8835376.1657 | 0 | 455560.1315 | 0 | 10912982.5821 | 28393342.118 | 19379039.4204 | 86667370.741 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112827763.1798 | 150466715.8228 | 1333521.4322 | 29.0184 | 3888.1404 | 5185.2106 | 79.265 | 105.7075
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.0823 | 63.9952 | 7.2709 | 4 | 3882.1547 | 5176.3154 | 79.143 | 105.5262 | 161.6757 | 0 | 242.4918 | 9001657.3157 | 483221.8673 | 9226324.2278 | 8848676.7221 | 0 | 447818.0848 | 0 | 10923002.3049 | 28419411.3814 | 19396832.2283 | 86746944.1322 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112907336.5709 | 150546289.214 | 1778279.41 | 29.0837 | 3882.1547 | 5176.3154 | 79.143 | 105.5262
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.2844 | 64.0648 | 7.2832 | 4 | 3877.6609 | 5169.6482 | 79.0514 | 105.3903 | 161.666 | 0 | 243.3174 | 9008281.2193 | 483530.6693 | 9234413.0712 | 8858606.1268 | 0 | 441920.2162 | 0 | 10930433.0081 | 28438744.547 | 19410027.5111 | 86805956.3691 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112966348.8079 | 150605301.4509 | 2371373.7057 | 29.1326 | 3877.6609 | 5169.6482 | 79.0514 | 105.3903
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.4501 | 64.1219 | 7.2927 | 4 | 3874.2879 | 5164.5785 | 78.9826 | 105.2869 | 161.658 | 0 | 231.2525 | 9013712.6421 | 483783.8355 | 9241046.8042 | 8866751.3723 | 0 | 437649.256 | 0 | 10936748.1249 | 28455175.1855 | 19421241.7595 | 86856108.9798 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 113016501.4186 | 150655454.0616 | 3162277.6602 | 29.1709 | 3874.2879 | 5164.5785 | 78.9826 | 105.2869
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.5498 | 64.1562 | 7.2992 | 4 | 3871.7567 | 5160.8963 | 78.931 | 105.2119 | 161.6532 | 0 | 210.5921 | 9016973.8682 | 483935.69 | 9245032.0003 | 8871646.3177 | 0 | 434077.1699 | 0 | 10940149.368 | 28464024.5223 | 19427281.6137 | 86883120.55 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 113043512.9888 | 150682465.6318 | 4216965.0343 | 29.197 | 3871.7567 | 5160.8963 | 78.931 | 105.2119
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.6398 | 64.1872 | 7.3045 | 4 | 3869.8576 | 5158.0605 | 78.8923 | 105.154 | 161.6488 | 0 | 239.7708 | 9019919.7295 | 484072.9121 | 9248631.3893 | 8876067.5714 | 0 | 431595.849 | 0 | 10943512.106 | 28472773.6768 | 19433253.0914 | 86909826.3254 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 113070218.7642 | 150709171.4072 | 5623413.2519 | 29.2182 | 3869.8576 | 5158.0605 | 78.8923 | 105.154
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7083 | 64.2108 | 7.3086 | 4 | 3868.4329 | 5155.9289 | 78.8632 | 105.1106 | 161.6455 | 0 | 232.9983 | 9022162.0286 | 484177.3463 | 9251371.4147 | 8879433.6485 | 0 | 429741.0277 | 0 | 10946085.3317 | 28479468.6822 | 19437822.5702 | 86930262.0499 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 113090654.4886 | 150729607.1317 | 7498942.0933 | 29.2342 | 3868.4329 | 5155.9289 | 78.8632 | 105.1106
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7519 | 64.2258 | 7.3113 | 4 | 3867.3642 | 5154.3684 | 78.8415 | 105.0788 | 161.6434 | 0 | 241.3472 | 9023585.0375 | 484243.5783 | 9253110.8478 | 8881570.9221 | 0 | 428235.532 | 0 | 10947590.9079 | 28483385.8827 | 19440496.14 | 86942218.8484 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 113102611.2872 | 150741563.9302 | 10000000 | 29.2454 | 3867.3642 | 5154.3684 | 78.8415 | 105.0788
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8426 | [19 empty] | 100 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0425 | [19 empty] | 133.3521 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.23658 | 0.0056806 | 4 | 1230183.7154 | 2922113.826 | 25078.959 | 59571.2428 | 108.9762 | 0 | 46.8115 | 136758.1497 | 5075.2813 | 108360.5873 | 69038.1311 | 0 | 73627.807 | 0 | 153215.383 | 398634.9978 | 272076.5771 | 1216786.9143 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 27952489.5877 | 66396876.5592 | 177.8279 | 0.022722 | 1230183.7154 | 2922113.826 | 25078.959 | 59571.2428
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.36022 | 0.015287 | 4 | 463695.9569 | 1092403.8456 | 9453.0693 | 22270.13 | 119.2809 | 0 | 251.1814 | 194194.3224 | 7756.0434 | 150575.0607 | 87023.1606 | 0 | 83009.0384 | 0 | 203797.4739 | 530239.2226 | 361899.1647 | 1618493.4868 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 28354196.1601 | 66798583.1317 | 237.1374 | 0.061148 | 463695.9569 | 1092403.8456 | 9453.0693 | 22270.13
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.53855 | 0.030585 | 4 | 236105.2945 | 550348.6348 | 4813.3258 | 11219.6013 | 128.6066 | 0 | 330.5833 | 269384.4407 | 11501.4282 | 206380.1578 | 112146.4647 | 0 | 94528.5546 | 0 | 270637.0079 | 704141.9793 | 480591.3695 | 2149311.4027 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 28885014.076 | 67329401.0476 | 316.2278 | 0.12234 | 236105.2945 | 550348.6348 | 4813.3258 | 11219.6013
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8183 | 0.7841 | 0.053305 | 4 | 138617.9215 | 318922.4967 | 2825.9138 | 6501.6665 | 136.5528 | 0 | 431.2809 | 363244.4195 | 16424.9894 | 277244.0346 | 145908.9885 | 0 | 107755.8023 | 0 | 355125.5114 | 923963.7344 | 630624.2343 | 2820291.7145 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 29555994.3878 | 68000381.3594 | 421.6965 | 0.21322 | 138617.9215 | 318922.4967 | 2825.9138 | 6501.6665
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7022 | 1.1251 | 0.08635 | 4 | 88072.4678 | 199375.8154 | 1795.4764 | 4064.5457 | 143.2733 | 0 | 69.5765 | 481568.8643 | 22890.9302 | 368438.3694 | 192777.2647 | 0 | 123989.6398 | 0 | 463969.3767 | 1207153.1449 | 823906.8259 | 3684694.4158 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 30420397.0892 | 68864784.0607 | 562.3413 | 0.3454 | 88072.4678 | 199375.8154 | 1795.4764 | 4064.5457
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8548 | 1.5797 | 0.13198 | 4 | 59643.7577 | 132466.3915 | 1215.9187 | 2700.5066 | 148.6925 | 0 | 69.3071 | 624647.1156 | 30923.9459 | 481636.2369 | 254185.3049 | 0 | 142649.3589 | 0 | 598276.3652 | 1556592.379 | 1062406.2834 | 4751316.9898 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 31487019.6632 | 69931406.6347 | 749.8942 | 0.52792 | 59643.7577 | 132466.3915 | 1215.9187 | 2700.5066
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 2.1943 | 0.19504 | 4 | 42091.0827 | 91367.4176 | 858.0837 | 1862.6484 | 153.0492 | 0 | 80.8824 | 800924.2915 | 41035.65 | 624623.2538 | 338380.7062 | 0 | 165458.441 | 0 | 768464.7136 | 1999387.551 | 1364623.0869 | 6102897.6941 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 32838600.3674 | 71282987.339 | 1000 | 0.78018 | 42091.0827 | 91367.4176 | 858.0837 | 1862.6484
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4164 | 3.0076 | 0.27881 | 4 | 30940.5272 | 65412.2741 | 630.7645 | 1333.5177 | 156.3293 | 0 | 71.6054 | 1012423.518 | 53200.3259 | 802094.9814 | 447889.7929 | 0 | 193231.7549 | 0 | 978447.7455 | 2545720.3266 | 1737506.4322 | 7770514.8776 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 34506217.5509 | 72950604.5225 | 1333.5214 | 1.1152 | 30940.5272 | 65412.2741 | 630.7645 | 1333.5177
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1152 | 4.1153 | 0.39573 | 4 | 23148.8224 | 47435.9916 | 471.9201 | 967.0469 | 159.2913 | 0 | 89.5976 | 1277279.4706 | 68723.389 | 1028763.3135 | 597308.2671 | 0 | 226496.2287 | 0 | 1247442.5609 | 3245589.6577 | 2215181.6316 | 9906784.5191 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 36642487.1925 | 75086874.164 | 1778.2794 | 1.5829 | 23148.8224 | 47435.9916 | 471.9201 | 967.0469
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7085 | 5.5833 | 0.55022 | 4 | 17858.1412 | 35325.7762 | 364.0624 | 720.1637 | 161.4205 | 0 | 88.4503 | 1596709.403 | 87352.4546 | 1311293.6005 | 794746.7752 | 0 | 267733.462 | 0 | 1582555.9212 | 4117485.88 | 2810268.719 | 12568146.2156 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 39303848.8889 | 77748235.8605 | 2371.3737 | 2.2009 | 17858.1412 | 35325.7762 | 364.0624 | 720.1637
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.481 | 7.5377 | 0.75646 | 4 | 14094.0972 | 26799.4449 | 287.3272 | 546.3429 | 163.0621 | 0 | 95.2045 | 1985902.8814 | 110023.3625 | 1665328.174 | 1057640.2994 | 0 | 318179.6559 | 0 | 2003459.0056 | 5212589.3665 | 3557699.3507 | 15910822.096 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 42646524.7693 | 81090911.7409 | 3162.2777 | 3.0258 | 14094.0972 | 26799.4449 | 287.3272 | 546.3429
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7562 | 10.099 | 1.0265 | 4 | 11388.4137 | 20751.7239 | 232.1682 | 423.052 | 164.312 | 0 | 98.4499 | 2452352.1238 | 136951.2949 | 2102860.1472 | 1394249.2271 | 0 | 378496.5161 | 0 | 2521314.6306 | 6559943.476 | 4477296.2158 | 20023463.6316 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 46759166.305 | 85203553.2765 | 4216.965 | 4.1059 | 11388.4137 | 20751.7239 | 232.1682 | 423.052
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0117 | 13.4815 | 1.3842 | 4 | 9379.7038 | 16323.2111 | 191.2179 | 332.7707 | 165.266 | 0 | 88.6202 | 3019626.4586 | 169722.9385 | 2647884.4006 | 1846106.1042 | 0 | 452018.5856 | 0 | 3172789.8101 | 8254948.2573 | 5634171.8078 | 25197268.3627 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 51932971.0361 | 90377358.0076 | 5623.4133 | 5.5367 | 9379.7038 | 16323.2111 | 191.2179 | 332.7707
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.7279 | 17.8822 | 1.8499 | 4 | 7884.2205 | 13079.7328 | 160.7305 | 266.648 | 165.984 | 0 | 105.1597 | 3699289.9115 | 208849.1038 | 3317615.3314 | 2437800.8323 | 0 | 540285.1866 | 0 | 3979497.7426 | 10353836.819 | 7066706.379 | 31603881.3061 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 58339583.9795 | 96783970.951 | 7498.9421 | 7.3995 | 7884.2205 | 13079.7328 | 160.7305 | 266.648
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.3775 | 23.4743 | 2.4403 | 4 | 6770.8739 | 10709.3673 | 138.0334 | 218.3249 | 166.485 | 0 | 81.0573 | 4495953.309 | 254417.3116 | 4122969.0451 | 3188755.7517 | 0 | 644675.3477 | 0 | 4955640.5984 | 12893560.2954 | 8800119.8378 | 39356091.4968 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 66091794.1701 | 104536181.1417 | 10000 | 9.7612 | 6770.8739 | 10709.3673 | 138.0334 | 218.3249
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2421 | 30.3361 | 3.1585 | 4 | 5951.0175 | 8993.9567 | 121.3195 | 183.354 | 166.714 | 0 | 112.5042 | 5398818.3902 | 305399.5323 | 5060951.696 | 4111568.2463 | 0 | 765909.0068 | 0 | 6100632.28 | 15872593.7807 | 10833371.4045 | 48449244.3369 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 75184947.0103 | 113629333.9818 | 13335.2143 | 12.634 | 5951.0175 | 8993.9567 | 121.3195 | 183.354
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.13 | 38.2929 | 3.9757 | 4 | 5364.4741 | 7781.9321 | 109.3621 | 158.6452 | 166.5753 | 0 | 114.7617 | 6367135.3541 | 358800.2791 | 6098210.9276 | 5185391.1752 | 0 | 902228.7555 | 0 | 7375588.9317 | 19189769.459 | 13097411.9661 | 58574536.8484 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 85310239.5217 | 123754626.4933 | 17782.7941 | 15.9028 | 5364.4741 | 7781.9321 | 109.3621 | 158.6452
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8233 | 46.7332 | 4.8199 | 4 | 4962.3999 | 6956.4536 | 101.1652 | 141.8167 | 166.0343 | 0 | 113.39 | 7319793.2764 | 409426.0175 | 7154424.6622 | 6331378.7816 | 0 | 1042425.8359 | 0 | 8680404.9437 | 22584633.0677 | 15414476.1365 | 68936962.7215 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 95672665.3949 | 134117052.3664 | 23713.7371 | 19.2795 | 4962.3999 | 6956.4536 | 101.1652 | 141.8167
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.7707 | 50.4925 | 5.3332 | 4 | 4677.442 | 6479.5576 | 95.356 | 132.0945 | 165.6705 | 0 | 153.4896 | 7722548.4823 | 430089.2007 | 7613182.1374 | 6843202.0797 | 0 | 975676.6718 | 0 | 9198032.4431 | 23931393.641 | 16333667.9009 | 73047792.5569 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 99783495.2303 | 138227882.2018 | 31622.7766 | 21.3329 | 4677.442 | 6479.5576 | 95.356 | 132.0945
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.1723 | 53.6108 | 5.7762 | 4 | 4461.6184 | 6125.5283 | 90.9561 | 124.8772 | 165.3151 | 0 | 195.2795 | 8047256.2817 | 446363.6665 | 7989045.4096 | 7268936.5729 | 0 | 899049.1136 | 0 | 9613753.9073 | 25013015.6146 | 17071897.1231 | 76349317.6893 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 103085020.3626 | 141529407.3342 | 42169.6503 | 23.1048 | 4461.6184 | 6125.5283 | 90.9561 | 124.8772
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8233 | 57.1752 | 6.2269 | 4 | 4294.9258 | 5838.3943 | 87.5579 | 119.0236 | 164.9245 | 0 | 208.0631 | 8411149.0562 | 464503.038 | 8413511.6275 | 7757956.1322 | 0 | 860154.105 | 0 | 10103836.844 | 26288110.886 | 17942175.8464 | 80241397.5352 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 106977100.2086 | 145421487.1801 | 56234.1325 | 24.9078 | 4294.9258 | 5838.3943 | 87.5579 | 119.0236
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8861 | 59.3966 | 6.5527 | 4 | 4168.4749 | 5635.2173 | 84.98 | 114.8815 | 164.6662 | 0 | 212.5358 | 8633887.8026 | 475505.6806 | 8675508.4466 | 8068576.7866 | 0 | 790466.1506 | 0 | 10391138.4981 | 27035610.8566 | 18452359.9359 | 82523054.1576 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 109258756.8309 | 147703143.8025 | 74989.4209 | 26.2107 | 4168.4749 | 5635.2173 | 84.98 | 114.8815
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.6197 | 61.1162 | 6.8124 | 4 | 4072.809 | 5483.633 | 83.0297 | 111.7913 | 164.4557 | 0 | 204.0004 | 8803908.001 | 483807.1642 | 8877096.0594 | 8310047.2788 | 0 | 725595.1723 | 0 | 10608176.9335 | 27600300.3447 | 18837772.1147 | 84246703.0687 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 110982405.7421 | 149426792.7136 | 100000 | 27.2496 | 4072.809 | 5483.633 | 83.0297 | 111.7913
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.3197 | 62.4508 | 7.0176 | 4 | 4000.513 | 5370.0922 | 81.5559 | 109.4766 | 164.2857 | 0 | 207.1811 | 8934447.0451 | 490119.7634 | 9032865.2616 | 8498136.8863 | 0 | 668767.1038 | 0 | 10773491.0634 | 28030413.8002 | 19131333.386 | 85559574.3098 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 112295276.9832 | 150739663.9547 | 133352.1432 | 28.0702 | 4000.513 | 5370.0922 | 81.5559 | 109.4766
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1165 | 63.4542 | 7.1758 | 4 | 3945.9191 | 5285.3033 | 80.4429 | 107.7481 | 164.1541 | 0 | 217.2711 | 9031777.9509 | 494791.1038 | 9149582.2513 | 8639936.3524 | 0 | 619671.9218 | 0 | 10894946.2362 | 28346415.2459 | 19347010.8659 | 86524131.9283 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 113259834.6016 | 151704221.5732 | 177827.941 | 28.703 | 3945.9191 | 5285.3033 | 80.4429 | 107.7481
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.236 | 64.2114 | 7.2972 | 4 | 3904.7294 | 5221.8235 | 79.6032 | 106.4539 | 164.0527 | 0 | 226.4454 | 9104776.0374 | 498274.2166 | 9237449.7485 | 8747180.1141 | 0 | 578767.7548 | 0 | 10984914.6699 | 28580494.6551 | 19506774.8726 | 87238632.069 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 113974334.7424 | 152418721.7139 | 237137.3706 | 29.1888 | 3904.7294 | 5221.8235 | 79.6032 | 106.4539
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8218 | 64.7771 | 7.3897 | 4 | 3873.6794 | 5174.2848 | 78.9702 | 105.4848 | 163.9758 | 0 | 218.9151 | 9159188.5594 | 500875.8106 | 9302949.5167 | 8828380.6917 | 0 | 545247.4832 | 0 | 11051290.404 | 28753190.6999 | 19624643.4716 | 87765766.6371 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 114501469.3105 | 152945856.282 | 316227.766 | 29.5588 | 3873.6794 | 5174.2848 | 78.9702 | 105.4848
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.9808 | 65.191 | 7.4594 | 4 | 3850.2949 | 5138.7485 | 78.4935 | 104.7603 | 163.9191 | 0 | 240.0846 | 9199081.7928 | 502804.3118 | 9350774.2602 | 8889426.4835 | 0 | 517939.8305 | 0 | 11099410.4048 | 28878389.0711 | 19710093.9326 | 88147920.0873 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 114883622.7607 | 153328009.7322 | 421696.5034 | 29.8376 | 3850.2949 | 5138.7485 | 78.4935 | 104.7603
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8387 | 65.4968 | 7.5118 | 4 | 3832.6964 | 5112.1701 | 78.1347 | 104.2185 | 163.8769 | 0 | 249.3741 | 9228491.1441 | 504222.9995 | 9386080.5578 | 8934613.8863 | 0 | 496223.8883 | 0 | 11134356.6657 | 28969312.0735 | 19772150.75 | 88425451.9652 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115161154.6386 | 153605541.6101 | 562341.3252 | 30.047 | 3832.6964 | 5112.1701 | 78.1347 | 104.2185
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.4696 | 65.7215 | 7.5509 | 4 | 3819.4606 | 5092.3036 | 77.8649 | 103.8135 | 163.8456 | 0 | 243.3329 | 9250050.5696 | 505261.347 | 9411990.3097 | 8967841.1949 | 0 | 479106.3934 | 0 | 11159557.4277 | 29034879.2869 | 19816901.7204 | 88625588.2498 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115361290.9231 | 153805677.8947 | 749894.2093 | 30.2036 | 3819.4606 | 5092.3036 | 77.8649 | 103.8135
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.9519 | 65.893 | 7.5806 | 4 | 3809.5114 | 5077.3599 | 77.662 | 103.5088 | 163.8216 | 0 | 211.0885 | 9266498.0846 | 506052.6121 | 9431771.5403 | 8993245.6379 | 0 | 466004.2994 | 0 | 11178793.148 | 29084926.6852 | 19851060.0981 | 88778352.1055 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115514054.7789 | 153958441.7504 | 1000000 | 30.3225 | 3809.5114 | 5077.3599 | 77.662 | 103.5088
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3003 | 66.0169 | 7.6026 | 4 | 3802.0363 | 5066.2173 | 77.5097 | 103.2817 | 163.8043 | 0 | 214.8452 | 9278357.1421 | 506622.5768 | 9446043.1976 | 9011595.5974 | 0 | 455758.8153 | 0 | 11192367.1583 | 29120243.4758 | 19875164.5334 | 88886152.4967 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115621855.1701 | 154066242.1416 | 1333521.4322 | 30.4105 | 3802.0363 | 5066.2173 | 77.5097 | 103.2817
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.5561 | 66.1077 | 7.619 | 4 | 3796.4223 | 5057.8865 | 77.3952 | 103.1119 | 163.7915 | 0 | 223.5212 | 9287052.5956 | 507040.2019 | 9456512.3465 | 9025067.7035 | 0 | 447861.2478 | 0 | 11202178.2971 | 29145770.0464 | 19892586.9424 | 88964069.3811 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115699772.0545 | 154144159.026 | 1778279.41 | 30.476 | 3796.4223 | 5057.8865 | 77.3952 | 103.1119
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.7413 | 66.1735 | 7.6311 | 4 | 3792.2074 | 5051.6701 | 77.3093 | 102.9851 | 163.7822 | 0 | 219.2331 | 9293342.975 | 507342.1438 | 9464088.5152 | 9034823.3273 | 0 | 441765.8924 | 0 | 11209131.5129 | 29163860.8876 | 19904934.3132 | 89019289.5675 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115754992.2409 | 154199379.2124 | 2371373.7057 | 30.5244 | 3792.2074 | 5051.6701 | 77.3093 | 102.9851
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8922 | 66.2271 | 7.6406 | 4 | 3789.0439 | 5046.9494 | 77.2448 | 102.8889 | 163.7747 | 0 | 232.9243 | 9298467.5181 | 507588.0962 | 9470261.3517 | 9042774.2857 | 0 | 437319.0143 | 0 | 11215000.0038 | 29179129.497 | 19915355.4529 | 89065895.2197 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115801597.8931 | 154245984.8646 | 3162277.6602 | 30.5622 | 3789.0439 | 5046.9494 | 77.2448 | 102.8889
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9971 | 66.2643 | 7.6474 | 4 | 3786.6698 | 5043.4493 | 77.1964 | 102.8175 | 163.7694 | 0 | 230.2185 | 9302023.3908 | 507758.6762 | 9474545.8072 | 9048295.5274 | 0 | 433839.5851 | 0 | 11218920.5648 | 29189329.9927 | 19922317.5008 | 89097031.0451 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115832733.7184 | 154277120.69 | 4216965.0343 | 30.5896 | 3786.6698 | 5043.4493 | 77.1964 | 102.8175
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.0749 | 66.2919 | 7.6525 | 4 | 3784.8886 | 5040.8283 | 77.1601 | 102.7641 | 163.7655 | 0 | 248.4208 | 9304661.1793 | 507885.1858 | 9477724.5182 | 9052392.9033 | 0 | 431203.653 | 0 | 11221808.3014 | 29196843.2909 | 19927445.4812 | 89119964.5131 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115855667.1865 | 154300054.158 | 5623413.2519 | 30.6101 | 3784.8886 | 5040.8283 | 77.1601 | 102.7641
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.1286 | 66.311 | 7.6562 | 4 | 3783.5524 | 5038.8848 | 77.1328 | 102.7245 | 163.7628 | 0 | 236.5366 | 9306481.4958 | 507972.4539 | 9479918.5742 | 9055222.0031 | 0 | 429152.8292 | 0 | 11223711.4689 | 29201794.9423 | 19930825.085 | 89135078.8524 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115870781.5258 | 154315168.4973 | 7498942.0933 | 30.6249 | 3783.5524 | 5038.8848 | 77.1328 | 102.7245
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.1823 | 66.33 | 7.6594 | 4 | 3782.55 | 5037.3627 | 77.1124 | 102.6935 | 163.7601 | 0 | 227.8834 | 9308303.0865 | 508059.8453 | 9482113.54 | 9058051.2402 | 0 | 427800.4566 | 0 | 11225887.9858 | 29207457.7927 | 19934690.0968 | 89152364.0439 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115888066.7173 | 154332453.6888 | 10000000 | 30.6376 | 3782.55 | 5037.3627 | 77.1124 | 102.6935
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0264 | [19 empty] | 100 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4806 | [19 empty] | 133.3521 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2934 | 0.2458 | 0.0066596 | 4 | 1072268.1362 | 2546012.3055 | 21859.6363 | 51903.9046 | 110.4068 | 0 | 49.7899 | 141646.3886 | 5309.4089 | 111610.782 | 70192.4287 | 0 | 73699.8661 | 0 | 156958.961 | 408375.0197 | 278724.3422 | 1246517.1972 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 28563390.1961 | 67821415.6233 | 177.8279 | 0.026638 | 1072268.1362 | 2546012.3055 | 21859.6363 | 51903.9046
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.37924 | 0.017186 | 4 | 421775.3828 | 992855.3672 | 8598.4617 | 20240.6996 | 121.175 | 0 | 249.8314 | 203303.5158 | 8228.7885 | 156692.8792 | 89411.9713 | 0 | 83950.5761 | 0 | 211219.2151 | 549549.0706 | 375078.5328 | 1677434.5493 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 28994307.5482 | 68252332.9754 | 237.1374 | 0.068743 | 421775.3828 | 992855.3672 | 8598.4617 | 20240.6996
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.5623 | 0.033473 | 4 | 220567.6999 | 513771.2967 | 4496.5709 | 10473.9228 | 130.4211 | 0 | 340.9958 | 280065.0033 | 12113.2493 | 213364.5928 | 114964.8939 | 0 | 94863.2862 | 0 | 278994.6999 | 725886.9795 | 495432.779 | 2215685.4837 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 29532558.4826 | 68790583.9098 | 316.2278 | 0.13389 | 220567.6999 | 513771.2967 | 4496.5709 | 10473.9228
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8766 | 0.82173 | 0.057995 | 4 | 130335.2922 | 299564.3114 | 2657.0612 | 6107.0237 | 138.5424 | 0 | 444.2233 | 378697.1293 | 17372.0234 | 287453.6484 | 150275.6115 | 0 | 108495.0619 | 0 | 367494.4551 | 956145.1886 | 652588.7381 | 2918521.8563 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 30235394.8552 | 69493420.2824 | 421.6965 | 0.23198 | 130335.2922 | 299564.3114 | 2657.0612 | 6107.0237
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7754 | 1.1775 | 0.093337 | 4 | 83376.8791 | 188528.7057 | 1699.7505 | 3843.4127 | 145.3137 | 0 | 66.2033 | 501494.8949 | 24201.2237 | 381592.7235 | 198689.0627 | 0 | 124648.0017 | 0 | 479944.1036 | 1248716.1074 | 852274.4019 | 3811560.5194 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 31128433.5183 | 70386458.9455 | 562.3413 | 0.37335 | 83376.8791 | 188528.7057 | 1699.7505 | 3843.4127
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9474 | 1.6515 | 0.142 | 4 | 56740.5664 | 125855.869 | 1156.7332 | 2565.7421 | 150.7794 | 0 | 68.6542 | 649877.267 | 32680.1575 | 498396.7802 | 261809.253 | 0 | 143224.4322 | 0 | 618535.2771 | 1609301.912 | 1098381.6228 | 4912206.7018 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 32229079.7007 | 71487105.1279 | 749.8942 | 0.56801 | 56740.5664 | 125855.869 | 1156.7332 | 2565.7421
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5092 | 2.2949 | 0.20958 | 4 | 40121.2229 | 86951.5425 | 817.9254 | 1772.6248 | 155.1808 | 0 | 63.1822 | 833713.2489 | 43443.5543 | 646514.3253 | 349705.9579 | 0 | 166137.0346 | 0 | 795410.5072 | 2069494.9786 | 1412472.8468 | 6316892.4536 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 33633765.4524 | 72891790.8796 | 1000 | 0.8383 | 40121.2229 | 86951.5425 | 817.9254 | 1772.6248
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5601 | 3.1384 | 0.29865 | 4 | 29591.6904 | 62454.5357 | 603.2666 | 1273.2202 | 158.4561 | 0 | 75.6238 | 1052291.0706 | 56278.5547 | 828694.767 | 463015.568 | 0 | 193444.9437 | 0 | 1011552.7126 | 2631852.6603 | 1796293.5198 | 8033423.7968 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 35350296.7957 | 74608322.2229 | 1333.5214 | 1.1946 | 29591.6904 | 62454.5357 | 603.2666 | 1273.2202
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3199 | 4.3005 | 0.42387 | 4 | 22159.022 | 45313.3769 | 451.7416 | 923.7745 | 161.489 | 0 | 89.1425 | 1328992.4759 | 72825.896 | 1064091.6707 | 617517.4238 | 0 | 227109.781 | 0 | 1291109.5265 | 3359202.1449 | 2292724.4886 | 10253573.4074 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 37570446.4063 | 76828471.8335 | 1778.2794 | 1.6955 | 22159.022 | 45313.3769 | 451.7416 | 923.7745
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9863 | 5.834 | 0.58849 | 4 | 17128.0571 | 33805.5215 | 349.1786 | 689.1713 | 163.6451 | 0 | 86.0866 | 1660949.3419 | 92544.7777 | 1356247.6384 | 819530.2907 | 0 | 268585.1112 | 0 | 1637164.2923 | 4259565.66 | 2907241.0883 | 13001828.2005 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 40318701.1993 | 79576726.6265 | 2371.3737 | 2.354 | 17128.0571 | 33805.5215 | 349.1786 | 689.1713
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8099 | 7.8548 | 0.80653 | 4 | 13556.0311 | 25724.8125 | 276.358 | 524.4351 | 165.2939 | 0 | 97.4197 | 2061613.3263 | 116327.8735 | 1718737.5474 | 1085606.3815 | 0 | 318086.5235 | 0 | 2067144.9444 | 5378287.1155 | 3670791.4691 | 16416595.1812 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 43733468.1801 | 82991493.6073 | 3162.2777 | 3.2261 | 13556.0311 | 25724.8125 | 276.358 | 524.4351
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2043 | 10.5464 | 1.0979 | 4 | 10942.2676 | 19881.3889 | 223.0729 | 405.309 | 166.5615 | 0 | 74.7142 | 2551968.2256 | 145465.6469 | 2173678.3693 | 1445621.51 | 0 | 379001.2924 | 0 | 2611336.6672 | 6794162.3493 | 4637155.4095 | 20738389.4702 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 48055262.469 | 87313287.8963 | 4216.965 | 4.3917 | 10942.2676 | 19881.3889 | 223.0729 | 405.309
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.599 | 14.08 | 1.4807 | 4 | 9020.8725 | 15649.2059 | 183.9027 | 319.0302 | 167.5264 | 0 | 77.2972 | 3143235.8052 | 180454.6324 | 2737144.6276 | 1917042.9457 | 0 | 452683.154 | 0 | 3287918.8543 | 8554490.4141 | 5838615.4848 | 26111585.9182 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 53428458.9171 | 92686484.3443 | 5623.4133 | 5.9228 | 9020.8725 | 15649.2059 | 183.9027 | 319.0302
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.481 | 18.6614 | 1.9767 | 4 | 7593.7963 | 12558.9792 | 154.8098 | 256.0318 | 168.2511 | 0 | 88.7914 | 3848627.4301 | 221959.6405 | 3427310.3533 | 2526970.2822 | 0 | 540851.6285 | 0 | 4120630.5405 | 10721035.4089 | 7317326.9618 | 32724712.246 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 60041585.2449 | 99299610.6721 | 7498.9421 | 7.9067 | 7593.7963 | 12558.9792 | 154.8098 | 256.0318
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.3178 | 24.4761 | 2.6042 | 4 | 6530.9889 | 10299.6599 | 133.143 | 209.9725 | 168.7516 | 0 | 96.1543 | 4674191.6134 | 270151.3762 | 4256449.1644 | 3300005.9981 | 0 | 645060.5216 | 0 | 5126884.8828 | 13339102.7963 | 9104211.7496 | 40716058.1024 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 68032931.1012 | 107290956.5285 | 10000 | 10.4169 | 6530.9889 | 10299.6599 | 133.143 | 209.9725
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.348 | 31.5802 | 3.3646 | 4 | 5748.9444 | 8665.9591 | 117.2 | 176.6673 | 168.9673 | 0 | 99.9214 | 5606111.0547 | 323827.9562 | 5218227.3758 | 4247100.6485 | 0 | 765528.1106 | 0 | 6302710.1069 | 16398358.8345 | 11192216.8571 | 50054080.9443 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 77370953.9431 | 116628979.3704 | 13335.2143 | 13.4583 | 5748.9444 | 8665.9591 | 117.2 | 176.6673
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.3869 | 39.7943 | 4.2272 | 4 | 5189.7088 | 7511.4449 | 105.7992 | 153.131 | 168.8017 | 0 | 111.1235 | 6603262.544 | 379882.2168 | 6279075.619 | 5349125.6974 | 0 | 901243.6608 | 0 | 7609909.9979 | 19799424.8073 | 13513514.2685 | 60435438.8117 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 87752311.8106 | 127010337.2378 | 17782.7941 | 16.9089 | 5189.7088 | 7511.4449 | 105.7992 | 153.131
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5601 | 48.6243 | 5.1254 | 4 | 4807.0692 | 6721.9502 | 97.9986 | 137.036 | 168.2104 | 0 | 113.1529 | 7597634.7511 | 433687.9201 | 7373838.6424 | 6546779.5504 | 0 | 1047626.0434 | 0 | 8969831.0938 | 23337660.5408 | 15928432.8601 | 71235491.402 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 98552364.4009 | 137810389.8281 | 23713.7371 | 20.5015 | 4807.0692 | 6721.9502 | 97.9986 | 137.036
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1413 | 52.7185 | 5.6746 | 4 | 4540.448 | 6269.9964 | 92.5632 | 127.8224 | 167.8002 | 0 | 136.6959 | 8034474.1576 | 456408.0734 | 7868703.6241 | 7106265.3598 | 0 | 989409.8344 | 0 | 9537551.8092 | 24814753.3867 | 16936579.0786 | 75744145.3238 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 103061018.3227 | 142319043.7499 | 31622.7766 | 22.6984 | 4540.448 | 6269.9964 | 92.5632 | 127.8224
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6741 | 56.724 | 6.1924 | 4 | 4337.7449 | 5922.6678 | 88.4308 | 120.7416 | 167.3471 | 0 | 158.6423 | 8448810.5702 | 477433.9252 | 8346117.1816 | 7654201.6126 | 0 | 943987.2914 | 0 | 10089514.7266 | 26250847.6745 | 17916742.9388 | 80127655.9208 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 107444528.9197 | 146702554.3469 | 42169.6503 | 24.7697 | 4337.7449 | 5922.6678 | 88.4308 | 120.7416
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.0741 | 59.5192 | 6.597 | 4 | 4181.5514 | 5669.2735 | 85.2466 | 115.5758 | 167.0366 | 0 | 189.386 | 8732051.765 | 491677.1125 | 8675440.8843 | 8037461.8792 | 0 | 869679.7184 | 0 | 10454461.4302 | 27200364.1364 | 18564807.4347 | 83025944.3605 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 110342817.3594 | 149600842.7866 | 56234.1325 | 26.388 | 4181.5514 | 5669.2735 | 85.2466 | 115.5758
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.023 | 61.7377 | 6.9271 | 4 | 4063.1849 | 5480.0212 | 82.8335 | 111.7176 | 166.7726 | 0 | 209.8892 | 8952894.021 | 502611.2294 | 8934850.1029 | 8341480.8409 | 0 | 797967.3225 | 0 | 10736623.3715 | 27934491.6285 | 19065864.5328 | 85266783.0496 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 112583656.0484 | 151841681.4757 | 74989.4209 | 27.7082 | 4063.1849 | 5480.0212 | 82.8335 | 111.7176
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.6855 | 63.4603 | 7.1901 | 4 | 3973.5964 | 5338.6068 | 81.0071 | 108.8347 | 166.5573 | 0 | 208.7773 | 9121990.1637 | 510874.1564 | 9135134.0192 | 8577949.5207 | 0 | 732060.7748 | 0 | 10950423.3676 | 28490755.3618 | 19445525.9609 | 86964713.3251 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 114281586.324 | 153539611.7512 | 100000 | 28.7602 | 3973.5964 | 5338.6068 | 81.0071 | 108.8347
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.2882 | 64.7821 | 7.3963 | 4 | 3905.8611 | 5232.8078 | 79.6263 | 106.6779 | 166.3861 | 0 | 182.2941 | 9250357.5865 | 517081.8017 | 9288165.7208 | 8759737.8716 | 0 | 674067.9466 | 0 | 11110870.2616 | 28908205.2678 | 19730444.0995 | 88238930.5561 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 115555803.5549 | 154813828.9822 | 133352.1432 | 29.5852 | 3905.8611 | 5232.8078 | 79.6263 | 106.6779
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0339 | 65.784 | 7.5558 | 4 | 3854.706 | 5153.6466 | 78.5834 | 105.0641 | 166.2529 | 0 | 197.5755 | 9346856.6461 | 521709.7506 | 9403788.9615 | 8897728.4245 | 0 | 624567.2559 | 0 | 11229913.9051 | 29217932.4089 | 19941839.2375 | 89184336.5901 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 116501209.589 | 155759235.0162 | 177827.941 | 30.2231 | 3854.706 | 5153.6466 | 78.5834 | 105.0641
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0756 | 66.5258 | 7.6769 | 4 | 3816.1092 | 5094.5512 | 77.7965 | 103.8593 | 166.1523 | 0 | 209.1657 | 9417863.8307 | 525092.8607 | 9489201.753 | 9000020.9601 | 0 | 582912.0949 | 0 | 11315885.6848 | 29441613.3445 | 20094506.0723 | 89867096.6011 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 117183969.6 | 156441995.0272 | 237137.3706 | 30.7077 | 3816.1092 | 5094.5512 | 77.7965 | 103.8593
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.607 | 67.0804 | 7.769 | 4 | 3787.0121 | 5050.3071 | 77.2034 | 102.9573 | 166.0759 | 0 | 246.1845 | 9470711.88 | 527598.2971 | 9552958.1722 | 9076575.3774 | 0 | 548949.5665 | 0 | 11378949.3844 | 29605692.1547 | 20206493.2317 | 90367928.064 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 117684801.0629 | 156942826.4901 | 316227.766 | 31.0759 | 3787.0121 | 5050.3071 | 77.2034 | 102.9573
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7519 | 67.494 | 7.8386 | 4 | 3765.0942 | 5017.1723 | 76.7565 | 102.2818 | 166.0184 | 0 | 239.3316 | 9509986.2568 | 529453.1853 | 9600444.3185 | 9133703.9634 | 0 | 521719.343 | 0 | 11425169.7561 | 29725948.0808 | 20288570.3723 | 90734995.276 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118051868.2749 | 157309893.7021 | 421696.5034 | 31.3543 | 3765.0942 | 5017.1723 | 76.7565 | 102.2818
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.7218 | 67.8427 | 7.8943 | 4 | 3748.5871 | 4991.8274 | 76.42 | 101.7652 | 165.9694 | 0 | 216.8369 | 9543028.6403 | 531012.311 | 9640431.9253 | 9181660.5564 | 0 | 501826.7873 | 0 | 11465204.4859 | 29830110.2356 | 20359663.1833 | 91052938.1251 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118369811.124 | 157627836.5512 | 562341.3252 | 31.5772 | 3748.5871 | 4991.8274 | 76.42 | 101.7652
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3675 | 68.0739 | 7.9339 | 4 | 3736.1662 | 4973.2024 | 76.1668 | 101.3855 | 165.9365 | 0 | 214.7992 | 9564898.352 | 532042.4809 | 9666927.5968 | 9213382.16 | 0 | 485116.2282 | 0 | 11490323.059 | 29895463.6101 | 20404268.2042 | 91252421.6911 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118569294.69 | 157827320.1172 | 749894.2093 | 31.7356 | 3736.1662 | 4973.2024 | 76.1668 | 101.3855
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.8324 | 68.2401 | 7.9631 | 4 | 3726.8286 | 4959.3204 | 75.9764 | 101.1025 | 165.9127 | 0 | 225.1446 | 9580603.6978 | 532780.9891 | 9685973.6917 | 9236201.4451 | 0 | 471927.6611 | 0 | 11507920.1191 | 29941247.5508 | 20435516.6845 | 91392171.8391 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118709044.838 | 157967070.2652 | 1000000 | 31.8526 | 3726.8286 | 4959.3204 | 75.9764 | 101.1025
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1614 | 68.3577 | 7.9846 | 4 | 3719.8123 | 4948.996 | 75.8334 | 100.892 | 165.8959 | 0 | 225.1372 | 9591693.5539 | 533301.743 | 9699432.6883 | 9252335.2552 | 0 | 461528.2894 | 0 | 11519933.6967 | 29972504.4154 | 20456850.1369 | 91487579.7788 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118804452.7776 | 158062478.2049 | 1333521.4322 | 31.9383 | 3719.8123 | 4948.996 | 75.8334 | 100.892
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.4197 | 68.45 | 8.001 | 4 | 3714.5426 | 4941.1989 | 75.726 | 100.733 | 165.8826 | 0 | 216.0968 | 9600394.6931 | 533710.0621 | 9709996.9942 | 9265003.788 | 0 | 453764.1396 | 0 | 11529519.174 | 29997443.8612 | 20473871.8211 | 91563704.5334 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118880577.5322 | 158138602.9595 | 1778279.41 | 32.0041 | 3714.5426 | 4941.1989 | 75.726 | 100.733
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.6024 | 68.5152 | 8.0131 | 4 | 3710.5861 | 4935.4004 | 75.6453 | 100.6148 | 165.8732 | 0 | 235.8125 | 9606536.8436 | 533998.0383 | 9717457.8533 | 9273953.3785 | 0 | 447704.0809 | 0 | 11536063.5759 | 30014471.0524 | 20485493.229 | 91615678.0518 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118932551.0507 | 158190576.4779 | 2371373.7057 | 32.0522 | 3710.5861 | 4935.4004 | 75.6453 | 100.6148
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.7487 | 68.5674 | 8.0224 | 4 | 3707.6163 | 4931.0093 | 75.5848 | 100.5253 | 165.8657 | 0 | 220.277 | 9611455.969 | 534228.6281 | 9723434.0659 | 9281123.5072 | 0 | 443250.0492 | 0 | 11541461.9656 | 30028516.5551 | 20495079.5731 | 91658550.3132 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118975423.3121 | 158233448.7393 | 3162277.6602 | 32.0895 | 3707.6163 | 4931.0093 | 75.5848 | 100.5253
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.8607 | 68.6074 | 8.0294 | 4 | 3705.3877 | 4927.7056 | 75.5393 | 100.4579 | 165.8599 | 0 | 190.8173 | 9615221.2685 | 534405.0802 | 9728009.3293 | 9286613.7016 | 0 | 439918.187 | 0 | 11545625.351 | 30039348.83 | 20502472.8234 | 91691614.5712 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 119008487.5701 | 158266512.9973 | 4216965.0343 | 32.1177 | 3705.3877 | 4927.7056 | 75.5393 | 100.4579
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.9339 | 68.6335 | 8.0344 | 4 | 3703.7155 | 4925.2761 | 75.5053 | 100.4084 | 165.8561 | 0 | 207.5701 | 9617677.1481 | 534520.0685 | 9730994.6853 | 9290196.5795 | 0 | 437247.9717 | 0 | 11548148.2167 | 30045912.809 | 20506952.8739 | 91711650.3528 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 119028523.3517 | 158286548.7789 | 5623413.2519 | 32.1376 | 3703.7155 | 4925.2761 | 75.5053 | 100.4084
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.9922 | 68.6543 | 8.0382 | 4 | 3702.461 | 4923.4386 | 75.4797 | 100.371 | 165.8531 | 0 | 226.9564 | 9619635.5788 | 534611.7735 | 9733375.3397 | 9293053.9296 | 0 | 435287.5313 | 0 | 11550226.0197 | 30051318.826 | 20510642.5916 | 91728151.5903 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 119045024.5892 | 158303050.0164 | 7498942.0933 | 32.1529 | 3702.461 | 4923.4386 | 75.4797 | 100.371
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0387 | 68.6708 | 8.0412 | 4 | 3701.52 | 4922.0485 | 75.4605 | 100.3426 | 165.8507 | 0 | 244.5649 | 9621195.8298 | 534684.8414 | 9735271.9387 | 9295330.4248 | 0 | 433852.1965 | 0 | 11551930.7401 | 30055754.159 | 20513669.7975 | 91741689.9278 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 119058562.9266 | 158316588.3539 | 10000000 | 32.1648 | 3701.52 | 4922.0485 | 75.4605 | 100.3426
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9514 | [19 empty] | 100 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5236 | [19 empty] | 133.3521 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.25931 | 0.0078247 | 4 | 932823.7219 | 2213381.5321 | 19016.8733 | 45122.7764 | 112.2349 | 0 | 52.6845 | 148609.5814 | 5642.8668 | 116337.9367 | 72002.4514 | 0 | 74654.1692 | 0 | 162726.3321 | 423380.5364 | 288965.9157 | 1292319.7897 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 29196223.2049 | 69276091.215 | 177.8279 | 0.031299 | 932823.7219 | 2213381.5321 | 19016.8733 | 45122.7764
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.39882 | 0.019197 | 4 | 386005.8411 | 907950.6711 | 7869.2512 | 18509.8025 | 123.0648 | 0 | 268.0428 | 212618.4289 | 8720.4895 | 162919.8776 | 91807.3667 | 0 | 84844.1193 | 0 | 218755.01 | 569155.6631 | 388460.4351 | 1737281.3901 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 29641184.8053 | 69721052.8154 | 237.1374 | 0.076789 | 386005.8411 | 907950.6711 | 7869.2512 | 18509.8025
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.59411 | 0.036934 | 4 | 204487.2657 | 475781.9689 | 4168.7495 | 9699.459 | 132.5207 | 0 | 340.2796 | 293916.6998 | 12903.7909 | 222654.1206 | 118797.6135 | 0 | 96301.0014 | 0 | 290383.5583 | 755518.4528 | 515656.8684 | 2306132.1058 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 30210035.521 | 70289903.5311 | 316.2278 | 0.14774 | 204487.2657 | 475781.9689 | 4168.7495 | 9699.459
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.935 | 0.86069 | 0.062972 | 4 | 122767.5345 | 281884.2935 | 2502.7822 | 5746.5926 | 140.5292 | 0 | 450.1433 | 394656.6011 | 18372.5628 | 297906.3485 | 154940.3193 | 0 | 109171.9984 | 0 | 380268.6538 | 989381.0333 | 675272.885 | 3019970.4022 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 30923873.8174 | 71003741.8275 | 421.6965 | 0.25189 | 122767.5345 | 281884.2935 | 2502.7822 | 5746.5926
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8459 | 1.2303 | 0.10057 | 4 | 79153.1879 | 178785.63 | 1613.6448 | 3644.7869 | 147.3364 | 0 | 74.0788 | 521506.0616 | 25548.4911 | 394695.6306 | 204475.7653 | 0 | 125102.2631 | 0 | 495818.0025 | 1290016.7362 | 880462.9297 | 3937625.8799 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 31841529.2951 | 71921397.3053 | 562.3413 | 0.40228 | 79153.1879 | 178785.63 | 1613.6448 | 3644.7869
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.04 | 1.7274 | 0.15294 | 4 | 53930.1471 | 119447.9095 | 1099.439 | 2435.1072 | 152.8637 | 0 | 65.089 | 676766.3057 | 34622.4071 | 515886.3241 | 271511.5483 | 0 | 143749.6056 | 0 | 640589.1144 | 1666681.4728 | 1137544.3521 | 5087351.1301 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 32991254.5453 | 73071122.5555 | 749.8942 | 0.61174 | 53930.1471 | 119447.9095 | 1099.439 | 2435.1072
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 2.3955 | 0.22449 | 4 | 38343.9799 | 82978.693 | 781.6939 | 1691.6329 | 157.2969 | 0 | 68.2591 | 866428.9097 | 45912.045 | 668174.3738 | 360415.3213 | 0 | 166479.219 | 0 | 821889.8488 | 2138388.7938 | 1459494.2913 | 6527182.8027 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 34431086.2179 | 74510954.228 | 1000 | 0.89795 | 38343.9799 | 82978.693 | 781.6939 | 1691.6329
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7259 | 3.2808 | 0.31982 | 4 | 28311.0342 | 59641.2917 | 577.1587 | 1215.8684 | 160.6142 | 0 | 68.4086 | 1094802.1933 | 59588.2502 | 857439.8013 | 478081.4023 | 0 | 194260.5283 | 0 | 1046827.1484 | 2723629.5064 | 1858933.1031 | 8313561.9334 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 36217465.3486 | 76297333.3587 | 1333.5214 | 1.2793 | 28311.0342 | 59641.2917 | 577.1587 | 1215.8684
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5368 | 4.4934 | 0.4532 | 4 | 21242.9632 | 43352.0979 | 433.0665 | 883.7912 | 163.6931 | 0 | 87.82 | 1382201.9721 | 77126.6415 | 1100561.3909 | 636460.8506 | 0 | 227893.1837 | 0 | 1335455.1751 | 3474580.4262 | 2371472.5363 | 10605752.1764 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 38509655.5917 | 78589523.6018 | 1778.2794 | 1.8128 | 21242.9632 | 43352.0979 | 433.0665 | 883.7912
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2421 | 6.0845 | 0.62826 | 4 | 16450.786 | 32399.543 | 335.3715 | 660.5085 | 165.8567 | 0 | 94.4706 | 1725769.8563 | 98027.4357 | 1400573.2646 | 845531.3854 | 0 | 268646.0757 | 0 | 1692033.7269 | 4402324.6736 | 3004677.0485 | 13437583.4668 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 41341486.882 | 81421354.8921 | 2371.3737 | 2.513 | 16450.786 | 32399.543 | 335.3715 | 660.5085
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1795 | 8.2126 | 0.86337 | 4 | 13009.5175 | 24615.1298 | 265.2166 | 501.8127 | 167.5332 | 0 | 94.4641 | 2147273.1489 | 123744.187 | 1778280.6319 | 1128194.278 | 0 | 319099.2013 | 0 | 2143670.6644 | 5577391.3414 | 3806684.1944 | 17024337.6473 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 44928241.0625 | 85008109.0727 | 3162.2777 | 3.4535 | 13009.5175 | 24615.1298 | 265.2166 | 501.8127
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6648 | 11.0098 | 1.1728 | 4 | 10524.6785 | 19067.983 | 214.5598 | 388.7266 | 168.8095 | 0 | 87.8474 | 2654772.1093 | 154548.2507 | 2246258.0783 | 1497296.4263 | 0 | 379504.9263 | 0 | 2703628.1185 | 7034285.7739 | 4801044.5808 | 21471338.264 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 49375241.6792 | 89455109.6894 | 4216.965 | 4.6914 | 10524.6785 | 19067.983 | 214.5598 | 388.7266
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.2032 | 14.6937 | 1.5818 | 4 | 8684.3045 | 15018.8612 | 177.0413 | 306.1798 | 169.7849 | 0 | 91.5388 | 3270579.6579 | 192011.5349 | 2827569.0775 | 1987932.2572 | 0 | 453267.8523 | 0 | 3405230.5481 | 8859711.3774 | 6046935.064 | 27043237.3694 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 54947140.7846 | 95027008.7947 | 5623.4133 | 6.3272 | 8684.3045 | 15018.8612 | 177.0413 | 306.1798
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2432 | 19.4649 | 2.1104 | 4 | 7319.7354 | 12067.6149 | 149.2227 | 246.0147 | 170.5151 | 0 | 95.1608 | 4003504.1305 | 236196.7133 | 3539051.3316 | 2620889.8916 | 0 | 541223.685 | 0 | 4266937.6433 | 11101696.4786 | 7577135.9637 | 33886635.8376 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 61790539.2529 | 101870407.263 | 7498.9421 | 8.4416 | 7319.7354 | 12067.6149 | 149.2227 | 246.0147
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.2527 | 25.5106 | 2.7779 | 4 | 6303.965 | 9910.9772 | 128.5149 | 202.0487 | 171.0139 | 0 | 103.097 | 4859719.9974 | 287344.7898 | 4392567.527 | 3422079.2185 | 0 | 645042.1026 | 0 | 5306633.9178 | 13806772.9139 | 9423406.2145 | 42143566.6817 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 70047470.0969 | 110127338.107 | 10000 | 11.1117 | 6303.965 | 9910.9772 | 128.5149 | 202.0487
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.4884 | 32.8775 | 3.5852 | 4 | 5556.3814 | 8351.2202 | 113.2744 | 170.2509 | 171.2155 | 0 | 101.7872 | 5824971.9962 | 344356.416 | 5380066.095 | 4402675.6237 | 0 | 765432.1371 | 0 | 6519825.8845 | 16963249.5514 | 11577766.3787 | 51778344.0826 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 79682247.4978 | 119762115.5079 | 13335.2143 | 14.3407 | 5556.3814 | 8351.2202 | 113.2744 | 170.2509
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.671 | 41.3564 | 4.4943 | 4 | 5024.1158 | 7253.598 | 102.4234 | 147.8744 | 171.021 | 0 | 121.1259 | 6850719.0312 | 403023.3668 | 6465066.0325 | 5532694.4559 | 0 | 900439.9215 | 0 | 7859257.6951 | 20448176.3672 | 13956300.5386 | 62415677.4089 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 90319580.8241 | 130399448.8342 | 17782.7941 | 17.9772 | 5024.1158 | 7253.598 | 102.4234 | 147.8744
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9025 | 50.3974 | 5.4343 | 4 | 4660.2452 | 6504.073 | 95.0054 | 132.5943 | 170.3923 | 0 | 130.7855 | 7866664.0432 | 458958.8778 | 7576129.0967 | 6750341.2661 | 0 | 1045456.6089 | 0 | 9242044.4581 | 24045903.876 | 16411823.4893 | 73397321.716 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 101301225.1312 | 141381093.1413 | 23713.7371 | 21.7373 | 4660.2452 | 6504.073 | 95.0054 | 132.5943
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3191 | 54.8994 | 6.0245 | 4 | 4410.4219 | 6073.6236 | 89.9124 | 123.819 | 169.927 | 0 | 149.0134 | 8345390.0596 | 484186.4543 | 8115462.465 | 7361121.6199 | 0 | 999655.7941 | 0 | 9869268.3932 | 25677811.8938 | 17525634.2438 | 78378530.9238 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 106282434.339 | 146362302.3491 | 31622.7766 | 24.098 | 4410.4219 | 6073.6236 | 89.9124 | 123.819
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.8861 | 59.0123 | 6.5595 | 4 | 4220.0365 | 5747.5899 | 86.0312 | 117.1724 | 169.4647 | 0 | 153.3002 | 8767234.7538 | 505574.0149 | 8601474.9341 | 7912377.71 | 0 | 953543.953 | 0 | 10428680.0927 | 27133286.3847 | 18519025.4909 | 82821197.3341 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 110725100.7493 | 150804968.7594 | 42169.6503 | 26.2379 | 4220.0365 | 5747.5899 | 86.0312 | 117.1724
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1593 | 61.8194 | 6.9704 | 4 | 4073.8511 | 5511.3563 | 83.051 | 112.3565 | 169.146 | 0 | 203.1182 | 9048863.6112 | 519646.8202 | 8929552.9845 | 8288991.2175 | 0 | 876603.6265 | 0 | 10788826.7214 | 28070314.0364 | 19158566.1171 | 85681365.1348 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 113585268.55 | 153665136.5601 | 56234.1325 | 27.8815 | 4073.8511 | 5511.3563 | 83.051 | 112.3565
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1787 | 64.1152 | 7.3112 | 4 | 3962.9377 | 5333.4312 | 80.7898 | 108.7292 | 168.8679 | 0 | 195.1221 | 9275918.9377 | 530916.1943 | 9195766.6449 | 8601265.9262 | 0 | 805686.6617 | 0 | 11079726.2022 | 28827174.8139 | 19675139.1497 | 87991594.5306 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 115895497.9458 | 155975365.9559 | 74989.4209 | 29.2448 | 3962.9377 | 5333.4312 | 80.7898 | 108.7292
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7265 | 65.8314 | 7.5782 | 4 | 3878.9076 | 5201.109 | 79.0768 | 106.0316 | 168.6492 | 0 | 229.6922 | 9444123.5421 | 539265.6115 | 9393536.417 | 8838788.3504 | 0 | 738116.5879 | 0 | 11291993.8985 | 29379451.8174 | 20052079.5527 | 89677355.7776 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 117581259.1928 | 157661127.2029 | 100000 | 30.313 | 3878.9076 | 5201.109 | 79.0768 | 106.0316
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2102 | 67.1369 | 7.7865 | 4 | 3815.381 | 5102.2195 | 77.7817 | 104.0156 | 168.477 | 0 | 205.9358 | 9570771.0244 | 545486.9697 | 9543376.3713 | 9020043.8585 | 0 | 678572.2651 | 0 | 11449717.6907 | 29789816.7713 | 20332162.0659 | 90929947.017 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 118833850.4322 | 158913718.4423 | 133352.1432 | 31.146 | 3815.381 | 5102.2195 | 77.7817 | 104.0156
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8561 | 68.1232 | 7.9471 | 4 | 3767.4017 | 5028.233 | 76.8036 | 102.5073 | 168.3437 | 0 | 208.2426 | 9665705.6272 | 550112.9526 | 9656232.8871 | 9157306.2108 | 0 | 627865.5886 | 0 | 11566317.0738 | 30093184.4483 | 20539216.7391 | 91855941.5275 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 119759844.9427 | 159839712.9528 | 177827.941 | 31.7884 | 3767.4017 | 5028.233 | 76.8036 | 102.5073
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8387 | 68.8592 | 8.0695 | 4 | 3731.199 | 4972.9066 | 76.0655 | 101.3794 | 168.2422 | 0 | 248.3655 | 9736133.6511 | 553522.8727 | 9740266.5246 | 9259935.1386 | 0 | 585588.2588 | 0 | 11651424.1138 | 30314615.5085 | 20690347.9876 | 92531834.0557 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 120435737.4709 | 160515605.481 | 237137.3706 | 32.278 | 3731.199 | 4972.9066 | 76.0655 | 101.3794
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3003 | 69.4 | 8.1617 | 4 | 3703.9051 | 4931.5906 | 75.5091 | 100.5371 | 168.1665 | 0 | 215.4064 | 9787660.6222 | 556005.4214 | 9801919.9821 | 9335463.7221 | 0 | 550827.4424 | 0 | 11712432.1042 | 30473345.785 | 20798684.6629 | 93016339.7423 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 120920243.1575 | 161000111.1677 | 316227.766 | 32.6467 | 3703.9051 | 4931.5906 | 75.5091 | 100.5371
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.4038 | 69.8074 | 8.2317 | 4 | 3683.3441 | 4900.5904 | 75.09 | 99.9052 | 168.1089 | 0 | 249.3456 | 9826348.5729 | 557862.6202 | 9848307.0268 | 9392419.7959 | 0 | 523175.2988 | 0 | 11757764.1927 | 30591290.5803 | 20879184.4092 | 93376352.4966 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121280255.9119 | 161360123.922 | 421696.5034 | 32.9267 | 3683.3441 | 4900.5904 | 75.09 | 99.9052
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.2151 | 70.1064 | 8.284 | 4 | 3667.8665 | 4877.4184 | 74.7744 | 99.4328 | 168.0663 | 0 | 218.769 | 9854669.8129 | 559218.3052 | 9882318.374 | 9434252.2932 | 0 | 501160.8565 | 0 | 11790331.6603 | 30676024.4506 | 20937017.0168 | 93634992.7695 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121538896.1847 | 161618764.1949 | 562341.3252 | 33.1361 | 3667.8665 | 4877.4184 | 74.7744 | 99.4328
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.805 | 70.3235 | 8.3229 | 4 | 3656.2233 | 4860.1201 | 74.5371 | 99.0801 | 168.0352 | 0 | 232.8721 | 9875198.5782 | 560198.8458 | 9907001.1476 | 9464649.6794 | 0 | 483749.6869 | 0 | 11813411.1957 | 30736072.6675 | 20978001.1587 | 93818282.9598 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121722186.375 | 161802054.3851 | 749894.2093 | 33.2918 | 3656.2233 | 4860.1201 | 74.5371 | 99.0801
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.246 | 70.4856 | 8.3522 | 4 | 3647.47 | 4847.1499 | 74.3586 | 98.8157 | 168.0118 | 0 | 234.1812 | 9890510.0622 | 560929.0711 | 9925426.5989 | 9487361.9331 | 0 | 470290.3909 | 0 | 11830462.0419 | 30780435.4717 | 21008279.6841 | 93953695.2539 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121857598.6691 | 161937466.6792 | 1000000 | 33.4088 | 3647.47 | 4847.1499 | 74.3586 | 98.8157
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.6501 | 70.6339 | 8.3764 | 4 | 3640.8914 | 4837.1037 | 74.2245 | 98.6109 | 167.9905 | 0 | 226.7958 | 9904489.5646 | 561593.4564 | 9942275.3167 | 9508003.2432 | 0 | 461041.0573 | 0 | 11847187.0289 | 30823950.457 | 21037979.5558 | 94086519.6799 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121990423.0951 | 162070291.1053 | 1333521.4322 | 33.5056 | 3640.8914 | 4837.1037 | 74.2245 | 98.6109
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8935 | 70.723 | 8.3927 | 4 | 3635.9489 | 4829.8329 | 74.1237 | 98.4627 | 167.9775 | 0 | 213.063 | 9912862.4904 | 561989.1038 | 9952390.6056 | 9520298.3433 | 0 | 453105.0388 | 0 | 11856251.7769 | 30847535.0719 | 21054076.54 | 94158508.9708 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122062412.386 | 162142280.3961 | 1778279.41 | 33.571 | 3635.9489 | 4829.8329 | 74.1237 | 98.4627
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0787 | 70.7907 | 8.4051 | 4 | 3632.238 | 4824.3672 | 74.0481 | 98.3513 | 167.9676 | 0 | 208.8134 | 9919228.562 | 562289.7415 | 9960084.023 | 9529652.6063 | 0 | 447116.2473 | 0 | 11863164.7603 | 30865521.2365 | 21066352.4669 | 94213409.6438 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122117313.059 | 162197181.0692 | 2371373.7057 | 33.6204 | 3632.238 | 4824.3672 | 74.0481 | 98.3513
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2102 | 70.8388 | 8.4142 | 4 | 3629.4524 | 4820.2994 | 73.9913 | 98.2683 | 167.9606 | 0 | 208.871 | 9923744.1726 | 562502.8283 | 9965543.1838 | 9536292.0369 | 0 | 442472.4672 | 0 | 11867916.3286 | 30877883.8427 | 21074790.1997 | 94251145.0597 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122155048.4749 | 162234916.4851 | 3162277.6602 | 33.6566 | 3629.4524 | 4820.2994 | 73.9913 | 98.2683
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2956 | 70.8699 | 8.4205 | 4 | 3627.362 | 4817.3055 | 73.9487 | 98.2073 | 167.956 | 0 | 206.8448 | 9926672.3494 | 562640.8499 | 9969084.9284 | 9540600.5432 | 0 | 438769.931 | 0 | 11870729.7548 | 30885203.8004 | 21079786.2213 | 94273488.3784 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122177391.7936 | 162257259.8038 | 4216965.0343 | 33.6822 | 3627.362 | 4817.3055 | 73.9487 | 98.2073
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.3734 | 70.8984 | 8.4258 | 4 | 3625.7935 | 4815.0006 | 73.9167 | 98.1603 | 167.9519 | 0 | 222.0244 | 9929341.8654 | 562766.7781 | 9972312.9883 | 9544527.5309 | 0 | 436180.8936 | 0 | 11873600.722 | 30892673.4681 | 21084884.423 | 94296288.6693 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122200192.0846 | 162280060.0947 | 5623413.2519 | 33.703 | 3625.7935 | 4815.0006 | 73.9167 | 98.1603
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4271 | 70.918 | 8.4295 | 4 | 3624.6168 | 4813.2918 | 73.8927 | 98.1255 | 167.949 | 0 | 215.6565 | 9931183.874 | 562853.6164 | 9974541.0039 | 9547238.3273 | 0 | 434163.0873 | 0 | 11875492.1644 | 30897594.6135 | 21088243.2058 | 94311309.8925 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122215213.3077 | 162295081.3178 | 7498942.0933 | 33.7181 | 3624.6168 | 4813.2918 | 73.8927 | 98.1255
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.466 | 70.9322 | 8.4323 | 4 | 3623.7341 | 4812.0162 | 73.8747 | 98.0995 | 167.9469 | 0 | 220.1869 | 9932517.2413 | 562916.4547 | 9976154.0313 | 9549201.0487 | 0 | 432624.8106 | 0 | 11876831.2988 | 30901078.7664 | 21090621.2117 | 94321944.8635 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 122225848.2787 | 162305716.2888 | 10000000 | 33.7293 | 3623.7341 | 4812.0162 | 73.8747 | 98.0995
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.052 | [19 empty] | 100 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0531 | [19 empty] | 133.3521 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.2691 | 0.0089189 | 4 | 835863.5797 | 1982577.8543 | 17040.2097 | 40417.5312 | 113.6649 | 0 | 56.5073 | 153750.1154 | 5896.8198 | 119716.2774 | 73219.4657 | 0 | 74661.2837 | 0 | 166625.1451 | 433524.4481 | 295889.3438 | 1323282.8988 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 29820076.8213 | 70729991.5415 | 177.8279 | 0.035676 | 835863.5797 | 1982577.8543 | 17040.2097 | 40417.5312
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.41902 | 0.02133 | 4 | 355075.2075 | 834562.7026 | 7238.6884 | 17013.6895 | 124.9505 | 0 | 259.2367 | 222162.7705 | 9233.1022 | 169268.0002 | 94242.6805 | 0 | 85689.6287 | 0 | 226432.511 | 589130.946 | 402093.976 | 1798253.6151 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 30295047.5375 | 71204962.2577 | 237.1374 | 0.08532 | 355075.2075 | 834562.7026 | 7238.6884 | 17013.6895
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.6195 | 0.04016 | 4 | 192186.7805 | 446857.6232 | 3917.9875 | 9109.7971 | 134.3313 | 0 | 331.2374 | 305199.9128 | 13575.57 | 229950.1262 | 121806.3672 | 0 | 96528.7191 | 0 | 299153.6712 | 778336.4876 | 531230.646 | 2375781.5 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 30872575.4225 | 71782490.1427 | 316.2278 | 0.16064 | 192186.7805 | 446857.6232 | 3917.9875 | 9109.7971
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9933 | 0.90082 | 0.068198 | 4 | 115913.2918 | 265881.0948 | 2363.0492 | 5420.3457 | 142.5135 | 0 | 449.4149 | 410993.8587 | 19417.2022 | 308557.8284 | 159672.9751 | 0 | 109782.4292 | 0 | 393285.4745 | 1023248.1307 | 698387.8749 | 3123345.7737 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 31620139.6962 | 72530054.4164 | 421.6965 | 0.27279 | 115913.2918 | 265881.0948 | 2363.0492 | 5420.3457
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 1.2861 | 0.10829 | 4 | 75185.2764 | 169629.6707 | 1532.7536 | 3458.1303 | 149.372 | 0 | 70.6236 | 542522.4424 | 26994.1777 | 408385.5945 | 210803.1944 | 0 | 125608.5461 | 0 | 512582.4425 | 1333634.3702 | 910232.8611 | 4070763.6289 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 32567557.5513 | 73477472.2716 | 562.3413 | 0.43316 | 75185.2764 | 169629.6707 | 1532.7536 | 3458.1303
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.13 | 1.8035 | 0.16409 | 4 | 51426.4664 | 113753.2476 | 1048.3981 | 2319.0138 | 154.9361 | 0 | 79.0949 | 703512.112 | 36596.8311 | 533237.7336 | 280362.104 | 0 | 144052.1952 | 0 | 662126.7805 | 1722718.0621 | 1175790.4757 | 5258396.2941 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 33755190.2166 | 74665104.9368 | 749.8942 | 0.65638 | 51426.4664 | 113753.2476 | 1048.3981 | 2319.0138
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7574 | 2.5061 | 0.24075 | 4 | 36610.4238 | 79091.422 | 746.353 | 1612.3856 | 159.441 | 0 | 72.4162 | 901995.0046 | 48647.0499 | 691749.8948 | 372779.0692 | 0 | 167297.6639 | 0 | 851162.7862 | 2214550.9721 | 1511476.5429 | 6759658.9837 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 35256452.9061 | 76166367.6264 | 1000 | 0.96302 | 36610.4238 | 79091.422 | 746.353 | 1612.3856
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.889 | 3.4289 | 0.34248 | 4 | 27085.2703 | 56948.4915 | 552.1699 | 1160.972 | 162.7935 | 0 | 74.9737 | 1139227.5685 | 63182.0429 | 886962.2102 | 494888.6639 | 0 | 194840.0063 | 0 | 1083849.1918 | 2819953.269 | 1924676.0504 | 8607579.003 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 37104372.9254 | 78014287.6456 | 1333.5214 | 1.3699 | 27085.2703 | 56948.4915 | 552.1699 | 1160.972
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7459 | 4.6906 | 0.48413 | 4 | 20380.1165 | 41505.7144 | 415.4762 | 846.1501 | 165.8881 | 0 | 85.8982 | 1436949.6614 | 81740.3006 | 1137369.294 | 657314.3963 | 0 | 228308.9946 | 0 | 1381256.2323 | 3593745.3818 | 2452805.0671 | 10969489.3281 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 39466283.2505 | 80376197.9707 | 1778.2794 | 1.9365 | 20380.1165 | 41505.7144 | 415.4762 | 846.1501
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5199 | 6.3555 | 0.67169 | 4 | 15787.4485 | 31013.858 | 321.8485 | 632.2594 | 168.075 | 0 | 85.0476 | 1795938.8304 | 104184.7681 | 1447998.1243 | 877120.5738 | 0 | 269225.1853 | 0 | 1752842.3179 | 4560536.1539 | 3112659.6347 | 13920505.5884 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 42417299.5108 | 83327214.2311 | 2371.3737 | 2.6868 | 15787.4485 | 31013.858 | 321.8485 | 632.2594
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5279 | 8.5663 | 0.92178 | 4 | 12507.6811 | 23603.0529 | 254.986 | 481.1802 | 169.7636 | 0 | 98.9734 | 2232952.5254 | 131565.6132 | 1836320.2961 | 1168991.8136 | 0 | 319231.821 | 0 | 2218734.207 | 5772691.2818 | 3939980.4167 | 17620467.9749 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 46117261.8973 | 87027176.6175 | 3162.2777 | 3.6871 | 12507.6811 | 23603.0529 | 254.986 | 481.1802
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.14 | 11.496 | 1.2531 | 4 | 10125.0012 | 18286.8715 | 206.4118 | 372.8026 | 171.0564 | 0 | 73.5399 | 2763241.1246 | 164586.3128 | 2321475.9101 | 1555290.5782 | 0 | 380146.5996 | 0 | 2802048.8049 | 7290356.211 | 4975817.9159 | 22252963.457 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 50749757.3795 | 91659672.0997 | 4216.965 | 5.0123 | 10125.0012 | 18286.8715 | 206.4118 | 372.8026
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.8022 | 15.325 | 1.6885 | 4 | 8366.3156 | 14423.2777 | 170.5587 | 294.038 | 172.0396 | 0 | 83.335 | 3402568.3396 | 204612.0174 | 2919415.0882 | 2063747.9585 | 0 | 453458.7958 | 0 | 3527082.8578 | 9176746.0919 | 6263317.771 | 28010948.9204 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 56507742.8428 | 97417657.563 | 5623.4133 | 6.7542 | 8366.3156 | 14423.2777 | 170.5587 | 294.038
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.0131 | 20.3011 | 2.2513 | 4 | 7061.4867 | 11604.3745 | 143.958 | 236.5709 | 172.7759 | 0 | 88.9707 | 4164228.7241 | 251553.9473 | 3654140.334 | 2719199.5592 | 0 | 541488.1504 | 0 | 4418938.1788 | 11497170.6925 | 7847055.2409 | 35093774.8272 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 63590568.7497 | 104500483.4699 | 7498.9421 | 9.0053 | 7061.4867 | 11604.3745 | 143.958 | 236.5709
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.2079 | 26.5799 | 2.9601 | 4 | 6089.9847 | 9545.0871 | 124.1526 | 194.5895 | 173.2724 | 0 | 98.0454 | 5051572.8005 | 305902.7734 | 4531740.3357 | 3546430.9407 | 0 | 644980.0663 | 0 | 5491444.4975 | 14287612.1324 | 9751588.8614 | 43611272.4081 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 72108066.3305 | 113017981.0508 | 10000 | 11.8404 | 6089.9847 | 9545.0871 | 124.1526 | 194.5895
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.6138 | 34.2075 | 3.8134 | 4 | 5376.3113 | 8058.2929 | 109.6034 | 164.2792 | 173.4583 | 0 | 87.6585 | 6047848.2141 | 365992.7246 | 5544485.6877 | 4554026.0308 | 0 | 764692.5147 | 0 | 6738047.617 | 17531017.7359 | 11965279.8312 | 53511390.356 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 82008184.2784 | 122918098.9986 | 13335.2143 | 15.2536 | 5376.3113 | 8058.2929 | 109.6034 | 164.2792
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9576 | 42.955 | 4.7722 | 4 | 4868.1443 | 7011.2847 | 99.2437 | 142.9345 | 173.2336 | 0 | 101.5063 | 7104525.7534 | 427815.5794 | 6653418.7235 | 5717288.7326 | 0 | 899281.1096 | 0 | 8112908.6605 | 21108124.1481 | 14406728.4597 | 64430091.1668 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 92926885.0892 | 133836799.8095 | 17782.7941 | 19.0888 | 4868.1443 | 7011.2847 | 99.2437 | 142.9345
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2662 | 52.2332 | 5.7574 | 4 | 4521.8563 | 6298.2753 | 92.1842 | 128.3989 | 172.5654 | 0 | 135.5694 | 8144810.4301 | 486098.9628 | 7783668.9899 | 6963313.7763 | 0 | 1043413.2391 | 0 | 9524309.1053 | 24780298.5875 | 16913062.9702 | 75638976.0612 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 104135769.9836 | 145045684.7038 | 23713.7371 | 23.0294 | 4521.8563 | 6298.2753 | 92.1842 | 128.3989
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8017 | 57.2656 | 6.4003 | 4 | 4287.0908 | 5885.0546 | 87.3981 | 119.9748 | 172.0279 | 0 | 144.0652 | 8678938.123 | 514764.9757 | 8380943.7957 | 7646101.0039 | 0 | 1014820.7722 | 0 | 10231871.7815 | 26621231.53 | 18169537.5309 | 81258209.513 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 109755003.4354 | 150664918.1556 | 31622.7766 | 25.6013 | 4287.0908 | 5885.0546 | 87.3981 | 119.9748
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1519 | 61.3909 | 6.9485 | 4 | 4107.8763 | 5579.7777 | 83.7446 | 113.7513 | 171.5686 | 0 | 146.5052 | 9100159.8245 | 536339.5531 | 8863876.74 | 8198063.2509 | 0 | 963875.2 | 0 | 10788302.6817 | 28068950.5927 | 19157635.5388 | 85677203.3818 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 114173997.3042 | 155083912.0244 | 42169.6503 | 27.7939 | 4107.8763 | 5579.7777 | 83.7446 | 113.7513
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3519 | 64.2332 | 7.3692 | 4 | 3970.9233 | 5358.7959 | 80.9526 | 109.2463 | 171.2395 | 0 | 202.7227 | 9383543.9688 | 550536.5586 | 9193211.5856 | 8578444.9969 | 0 | 885061.4601 | 0 | 11150411.4423 | 29011083.3089 | 19800660.4765 | 88552953.7976 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 117049747.7201 | 157959662.4403 | 56234.1325 | 29.4767 | 3970.9233 | 5358.7959 | 80.9526 | 109.2463
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3714 | 66.5817 | 7.7186 | 4 | 3867.0378 | 5192.0825 | 78.8348 | 105.8476 | 170.9507 | 0 | 191.8566 | 9613807.8585 | 561901.4721 | 9463333.6994 | 8894201.1174 | 0 | 813898.2651 | 0 | 11445385.5409 | 29778545.406 | 20324469.1275 | 90895542.487 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 119392336.4094 | 160302251.1297 | 74989.4209 | 30.8744 | 3867.0378 | 5192.0825 | 78.8348 | 105.8476
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.805 | 68.2794 | 7.9879 | 4 | 3788.203 | 5068.5799 | 77.2276 | 103.3299 | 170.7297 | 0 | 227.9005 | 9779637.3953 | 570215.8326 | 9657293.3372 | 9126844.0294 | 0 | 744683.9562 | 0 | 11652683.0748 | 30317891.0666 | 20692583.6233 | 92541832.3155 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 121038626.2379 | 161948540.9581 | 100000 | 31.9515 | 3788.203 | 5068.5799 | 77.2276 | 103.3299
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1982 | 69.5692 | 8.1974 | 4 | 3728.5964 | 4976.2389 | 76.0125 | 101.4474 | 170.556 | 0 | 202.4471 | 9904372.4665 | 576401.8435 | 9804089.6204 | 9304064.9455 | 0 | 684031.6178 | 0 | 11806454.5926 | 30717973.013 | 20965647.7726 | 93763035.8719 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 122259829.7943 | 163169744.5145 | 133352.1432 | 32.7898 | 3728.5964 | 4976.2389 | 76.0125 | 101.4474
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7728 | 70.5421 | 8.3588 | 4 | 3683.5734 | 4907.1344 | 75.0946 | 100.0386 | 170.4213 | 0 | 229.4233 | 9997742.2974 | 580991.2166 | 9914511.255 | 9438038.1308 | 0 | 632552.0613 | 0 | 11919895.6349 | 31013123.3351 | 21167093.9322 | 94663947.8633 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 123160741.7857 | 164070656.5059 | 177827.941 | 33.4351 | 3683.5734 | 4907.1344 | 75.0946 | 100.0386
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.705 | 71.2691 | 8.4817 | 4 | 3649.593 | 4855.4193 | 74.4019 | 98.9843 | 170.3188 | 0 | 232.3299 | 10067109.7533 | 584377.917 | 9996848.3373 | 9538310.4664 | 0 | 589805.3458 | 0 | 12002816.2097 | 31228865.6615 | 21314342.503 | 95322476.194 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 123819270.1165 | 164729184.8367 | 237137.3706 | 33.9269 | 3649.593 | 4855.4193 | 74.4019 | 98.9843
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1445 | 71.809 | 8.5747 | 4 | 3623.9692 | 4816.7189 | 73.8795 | 98.1953 | 170.2416 | 0 | 201.0407 | 10118397.6782 | 586869.0341 | 10057894.7861 | 9612862.6225 | 0 | 554959.005 | 0 | 12063083.4191 | 31385668.5779 | 21421363.7154 | 95801098.8383 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 124297892.7607 | 165207807.4809 | 316227.766 | 34.2988 | 3623.9692 | 4816.7189 | 73.8795 | 98.1953
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.1897 | 72.1999 | 8.644 | 4 | 3604.6631 | 4787.853 | 73.4859 | 97.6069 | 170.185 | 0 | 220.2085 | 10155422.675 | 588660.2263 | 10102057.4407 | 9666907.8179 | 0 | 526662.9911 | 0 | 12105487.3489 | 31495994.9049 | 21496663.7006 | 96137857.1053 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 124634651.0277 | 165544565.748 | 421696.5034 | 34.576 | 3604.6631 | 4787.853 | 73.4859 | 97.6069
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.9861 | 72.4973 | 8.6967 | 4 | 3590.1282 | 4766.148 | 73.1896 | 97.1644 | 170.1417 | 0 | 210.8963 | 10183521.4186 | 590015.7768 | 10135623.4405 | 9708047.3589 | 0 | 504599.0271 | 0 | 12137504.7385 | 31579297.5851 | 21553519.4915 | 96392128.8369 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 124888922.7594 | 165798837.4796 | 562341.3252 | 34.7868 | 3590.1282 | 4766.148 | 73.1896 | 97.1644
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5586 | 72.7107 | 8.7356 | 4 | 3579.1932 | 4749.9705 | 72.9667 | 96.8346 | 170.1104 | 0 | 215.2807 | 10203653.2961 | 590984.6939 | 10159701.7173 | 9737592.7495 | 0 | 487064.0065 | 0 | 12159808.6206 | 31637327.7112 | 21593126.245 | 96569259.04 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125066052.9624 | 165975967.6827 | 749894.2093 | 34.9425 | 3579.1932 | 4749.9705 | 72.9667 | 96.8346
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.9802 | 72.8678 | 8.7647 | 4 | 3570.9716 | 4737.8659 | 72.7991 | 96.5878 | 170.0873 | 0 | 219.859 | 10218442.3348 | 591695.2787 | 10177405.1443 | 9759334.0198 | 0 | 473422.8513 | 0 | 12175916.8553 | 31679238.0334 | 21621730.9011 | 96697185.4186 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125193979.3411 | 166103894.0613 | 1000000 | 35.0588 | 3570.9716 | 4737.8659 | 72.7991 | 96.5878
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3085 | 72.9899 | 8.7869 | 4 | 3564.7933 | 4728.7335 | 72.6731 | 96.4016 | 170.0693 | 0 | 268.8023 | 10229941.7522 | 592247.2478 | 10191178.3914 | 9776258.7813 | 0 | 463149.7605 | 0 | 12188582.6139 | 31712191.7394 | 21644222.4825 | 96797772.7689 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125294566.6913 | 166204481.4116 | 1333521.4322 | 35.1478 | 3564.7933 | 4728.7335 | 72.6731 | 96.4016
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.5324 | 73.0732 | 8.803 | 4 | 3560.1526 | 4721.9754 | 72.5785 | 96.2639 | 170.0569 | 0 | 249.4988 | 10237772.8414 | 592622.619 | 10200564.0124 | 9787798.0243 | 0 | 454985.2318 | 0 | 12196759.6643 | 31733466.747 | 21658743.1123 | 96862712.2524 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125359506.1749 | 166269420.8951 | 1778279.41 | 35.2118 | 3560.1526 | 4721.9754 | 72.5785 | 96.2639
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6982 | 73.1349 | 8.8149 | 4 | 3556.6681 | 4716.9146 | 72.5075 | 96.1607 | 170.0477 | 0 | 234.3093 | 10243564.2505 | 592900.0268 | 10207507.5281 | 9796337.6428 | 0 | 448753.5751 | 0 | 12202734.5791 | 31749012.2498 | 21669353.2374 | 96910163.0896 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125406957.012 | 166316871.7323 | 2371373.7057 | 35.2597 | 3556.6681 | 4716.9146 | 72.5075 | 96.1607
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8251 | 73.182 | 8.824 | 4 | 3554.0525 | 4713.1077 | 72.4542 | 96.0831 | 170.0407 | 0 | 220.3349 | 10247994.2709 | 593112.148 | 10212819.923 | 9802872.6822 | 0 | 444074.2477 | 0 | 12207340.576 | 31760996.1088 | 21677532.4675 | 96946742.4241 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125443536.3465 | 166353451.0667 | 3162277.6602 | 35.2959 | 3554.0525 | 4713.1077 | 72.4542 | 96.0831
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.9345 | 73.2227 | 8.8312 | 4 | 3552.0895 | 4710.1927 | 72.4141 | 96.0236 | 170.0347 | 0 | 146.6434 | 10251816.4568 | 593295.2269 | 10217403.1228 | 9808511.2546 | 0 | 440753.6031 | 0 | 12211594.0691 | 31772062.8253 | 21685085.7289 | 96980522.2875 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125477316.2099 | 166387230.9302 | 4216965.0343 | 35.3249 | 3552.0895 | 4710.1927 | 72.4141 | 96.0236
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0077 | 73.2499 | 8.8364 | 4 | 3550.6167 | 4708.0435 | 72.3841 | 95.9798 | 170.0307 | 0 | 145.5366 | 10254368.8689 | 593417.3773 | 10220464.8558 | 9812278.8825 | 0 | 438115.9891 | 0 | 12214271.9297 | 31779030.0695 | 21689841.0162 | 97001788.9891 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125498582.9115 | 166408497.6317 | 5623413.2519 | 35.3456 | 3550.6167 | 4708.0435 | 72.3841 | 95.9798
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0466 | 73.2643 | 8.8398 | 4 | 3549.5117 | 4706.4978 | 72.3616 | 95.9483 | 170.0285 | 0 | 153.8348 | 10255722.8344 | 593482.0177 | 10222090.4689 | 9814280.0775 | 0 | 435890.8961 | 0 | 12215371.8549 | 31781891.8492 | 21691794.2396 | 97010524.2384 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125507318.1608 | 166417232.8811 | 7498942.0933 | 35.359 | 3549.5117 | 4706.4978 | 72.3616 | 95.9483
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1003 | 73.2843 | 8.8431 | 4 | 3548.6828 | 4705.2368 | 72.3447 | 95.9226 | 170.0255 | 0 | 152.1315 | 10257597.9828 | 593571.8404 | 10224339.1462 | 9817047.1904 | 0 | 434584.9363 | 0 | 12217585.0275 | 31787650.0702 | 21695724.3438 | 97028100.5376 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125524894.4601 | 166434809.1803 | 10000000 | 35.3722 | 3548.6828 | 4705.2368 | 72.3447 | 95.9226
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.8395 | [19 empty] | 100 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.0715 | [19 empty] | 133.3521 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3834 | 0.28584 | 0.010327 | 4 | 737757.7314 | 1748415.6491 | 15040.1892 | 35643.8179 | 115.7179 | 0 | 40.9279 | 162204.8842 | 6311.7461 | 125453.2779 | 75411.3835 | 0 | 76072.9992 | 0 | 173727.1735 | 452002.469 | 308500.9728 | 1379684.9062 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 30475229.4267 | 72223394.9843 | 177.8279 | 0.041308 | 737757.7314 | 1748415.6491 | 15040.1892 | 35643.8179
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.43987 | 0.023596 | 4 | 327976.2437 | 770291.5607 | 6686.2393 | 15703.4354 | 126.8323 | 0 | 181.7215 | 231971.9015 | 9769.886 | 175747.7398 | 96770.8236 | 0 | 86487.0398 | 0 | 234291.4824 | 609578.3774 | 416049.7682 | 1860667.0187 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 30956211.5393 | 72704377.0968 | 237.1374 | 0.094386 | 327976.2437 | 770291.5607 | 6686.2393 | 15703.4354
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.65309 | 0.043989 | 4 | 179385.8401 | 416648.842 | 3657.023 | 8493.9502 | 136.4208 | 0 | 244.5285 | 319626.8764 | 14429.2776 | 239539.9132 | 125625.2909 | 0 | 97842.8151 | 0 | 310855.0276 | 808781.0166 | 552009.6626 | 2468709.8801 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 31564254.4006 | 73312419.9582 | 316.2278 | 0.17596 | 179385.8401 | 416648.842 | 3657.023 | 8493.9502
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0517 | 0.94209 | 0.07368 | 4 | 109678.075 | 251332.353 | 2235.9359 | 5123.75 | 144.4951 | 0 | 381.0823 | 427713.897 | 20509.3476 | 319391.609 | 164479.4736 | 0 | 110324.6195 | 0 | 406543.3892 | 1057742.5051 | 721930.9942 | 3228635.8351 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 32324180.3556 | 74072345.9132 | 421.6965 | 0.29472 | 109678.075 | 251332.353 | 2235.9359 | 5123.75
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 1.3429 | 0.11626 | 4 | 71601.9996 | 161371.7286 | 1459.7036 | 3289.781 | 151.4051 | 0 | 60.0192 | 563752.4751 | 28481.1287 | 422202.9774 | 216730.4739 | 0 | 126024.3879 | 0 | 529304.6628 | 1377142.1573 | 939927.8198 | 4203566.0829 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 33299110.6035 | 75047276.161 | 562.3413 | 0.46506 | 71601.9996 | 161371.7286 | 1459.7036 | 3289.781
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2421 | 1.8903 | 0.17635 | 4 | 48974.9867 | 108160.0259 | 998.4213 | 2204.9884 | 157.0844 | 0 | 79.1849 | 733256.8964 | 38794.2691 | 552928.6738 | 289668.3749 | 0 | 145174.0533 | 0 | 686330.6843 | 1785691.6548 | 1218771.2467 | 5450615.8533 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 34546160.3738 | 76294325.9314 | 749.8942 | 0.70538 | 48974.9867 | 108160.0259 | 998.4213 | 2204.9884
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8816 | 2.6167 | 0.25754 | 4 | 35029.3003 | 75554.9161 | 714.1197 | 1540.2892 | 161.5658 | 0 | 74.6761 | 937657.0349 | 51484.1383 | 715069.9858 | 385061.2716 | 0 | 167725.9282 | 0 | 880229.3599 | 2290176.2346 | 1563092.3386 | 6990496.2919 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 36086040.8124 | 77834206.3699 | 1000 | 1.0302 | 35029.3003 | 75554.9161 | 714.1197 | 1540.2892
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0548 | 3.5795 | 0.36579 | 4 | 25962.3935 | 54495.4424 | 529.2785 | 1110.9633 | 165.0402 | 0 | 69.1576 | 1183939.9115 | 66876.1745 | 916718.4645 | 508050.469 | 0 | 195139.9822 | 0 | 1119582.7506 | 2912924.6592 | 1988130.9345 | 8891363.3459 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 37986907.8664 | 79735073.424 | 1333.5214 | 1.4632 | 25962.3935 | 54495.4424 | 529.2785 | 1110.9633
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9654 | 4.9006 | 0.51759 | 4 | 19542.2981 | 39706.9127 | 398.3962 | 809.4791 | 168.0879 | 0 | 69.3146 | 1495408.5875 | 86865.7663 | 1176101.2971 | 681807.5251 | 0 | 228937.3841 | 0 | 1430957.0184 | 3723056.6323 | 2541062.6527 | 11364196.8636 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 40459741.3842 | 82207906.9417 | 1778.2794 | 2.0704 | 19542.2981 | 39706.9127 | 398.3962 | 809.4791
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8022 | 6.6342 | 0.71744 | 4 | 15162.6623 | 29710.1925 | 309.1114 | 605.6825 | 170.2921 | 0 | 76.3607 | 1868534.8791 | 110856.4071 | 1496170.0327 | 909805.0327 | 0 | 269697.3663 | 0 | 1815474.85 | 4723493.1545 | 3223881.136 | 14417912.8583 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 43513457.3788 | 85261622.9363 | 2371.3737 | 2.8698 | 15162.6623 | 29710.1925 | 309.1114 | 605.6825
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8984 | 8.941 | 0.98449 | 4 | 12025.1747 | 22626.6712 | 245.1495 | 461.2753 | 171.9965 | 0 | 92.7759 | 2323897.2937 | 140238.3734 | 1897119.4156 | 1214236.3181 | 0 | 319729.7251 | 0 | 2299136.2391 | 5981880.8764 | 4082756.6135 | 18258994.855 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 47354539.3755 | 89102704.933 | 3162.2777 | 3.938 | 12025.1747 | 22626.6712 | 245.1495 | 461.2753
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6199 | 11.9978 | 1.3371 | 4 | 9750.0101 | 17555.472 | 198.7671 | 357.892 | 173.3006 | 0 | 85.4917 | 2875029.9294 | 175366.9362 | 2398250.0416 | 1613845.4556 | 0 | 380617.6105 | 0 | 2902812.8895 | 7552523.6898 | 5154752.6071 | 23053199.1596 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 52148743.6801 | 93896909.2377 | 4216.965 | 5.3486 | 9750.0101 | 17555.472 | 198.7671 | 357.892
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4166 | 15.9918 | 1.7996 | 4 | 8070.4231 | 13870.0092 | 164.5265 | 282.7589 | 174.2921 | 0 | 76.0483 | 3538354.2298 | 217723.3997 | 3015885.877 | 2137069.8876 | 0 | 453835.7 | 0 | 3651518.9467 | 9500503.2698 | 6484288.6974 | 28999180.008 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 58094724.5285 | 99842890.086 | 5623.4133 | 7.1985 | 8070.4231 | 13870.0092 | 164.5265 | 282.7589
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.7831 | 21.158 | 2.3986 | 4 | 6818.4182 | 11169.6904 | 139.0027 | 227.7092 | 175.0329 | 0 | 101.3889 | 4329495.4969 | 268140.8089 | 3770700.8454 | 2817991.2852 | 0 | 541347.7842 | 0 | 4573793.726 | 11900073.061 | 8122044.3862 | 36323587.3937 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 65419131.9142 | 107167297.4717 | 7498.9421 | 9.5945 | 6818.4182 | 11169.6904 | 139.0027 | 227.7092
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.1869 | 27.678 | 3.1511 | 4 | 5887.4084 | 9199.5598 | 120.0228 | 187.5455 | 175.527 | 0 | 103.2087 | 5249887.7961 | 326139.2572 | 4672953.7181 | 3671540.5935 | 0 | 644823.7828 | 0 | 5680484.6076 | 14779455.7214 | 10087282.2173 | 45112567.6941 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 74208112.2146 | 115956277.7722 | 10000 | 12.6045 | 5887.4084 | 9199.5598 | 120.0228 | 187.5455
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.771 | 35.5675 | 4.0529 | 4 | 5205.1767 | 7780.3897 | 106.1146 | 158.6138 | 175.6957 | 0 | 106.1388 | 6278554.9397 | 389760.6699 | 5710477.4771 | 4708078.7944 | 0 | 763903.5756 | 0 | 6961802.4281 | 18113181.8559 | 12362618.8053 | 55288378.5461 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 84383923.0666 | 126132088.6241 | 13335.2143 | 16.2115 | 5205.1767 | 7780.3897 | 106.1146 | 158.6138
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.2527 | 44.5794 | 5.0613 | 4 | 4720.3841 | 6782.5206 | 96.2314 | 138.2709 | 175.4396 | 0 | 113.4438 | 7364841.0082 | 454679.0743 | 6842556.0585 | 5900903.9441 | 0 | 897683.3723 | 0 | 8369658.7484 | 21776135.2102 | 14862659.7358 | 66469117.1517 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 95564661.6722 | 137312827.2297 | 17782.7941 | 20.2451 | 4720.3841 | 6782.5206 | 96.2314 | 138.2709
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.6085 | 54.1066 | 6.0904 | 4 | 4391.5242 | 6105.2014 | 89.5272 | 124.4628 | 174.7308 | 0 | 125.8823 | 8427826.6911 | 514792.4013 | 7993649.5362 | 7170948.5707 | 0 | 1040754.1833 | 0 | 9807708.8392 | 25517646.5619 | 17416318.1137 | 77889644.8974 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 106985189.4179 | 148733354.9754 | 23713.7371 | 24.3617 | 4391.5242 | 6105.2014 | 89.5272 | 124.4628
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8091 | 59.5367 | 6.7725 | 4 | 4171.2545 | 5712.347 | 85.0367 | 116.4539 | 174.1374 | 0 | 143.6898 | 8997646.3201 | 545007.9984 | 8633322.9093 | 7891614.568 | 0 | 1022105.6006 | 0 | 10564981.9846 | 27487915.9481 | 18761067.4548 | 83903662.784 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 112999207.3045 | 154747372.862 | 31622.7766 | 27.09 | 4171.2545 | 5712.347 | 85.0367 | 116.4539
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6929 | 63.9636 | 7.3578 | 4 | 4001.7591 | 5420.2581 | 81.5813 | 110.4993 | 173.6487 | 0 | 147.6162 | 9449981.5469 | 568800.7856 | 9146434.2381 | 8488462.4803 | 0 | 978504.9391 | 0 | 11166551.7561 | 29053077.0946 | 19829322.0981 | 88681134.9388 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 117776679.4593 | 159524845.0168 | 42169.6503 | 29.4312 | 4001.7591 | 5420.2581 | 81.5813 | 110.4993
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.7567 | 66.7983 | 7.7878 | 4 | 3873.0104 | 5213.183 | 78.9566 | 106.2778 | 173.3116 | 0 | 198.6294 | 9733196.761 | 583422.6177 | 9471571.5987 | 8874810.9969 | 0 | 896704.1432 | 0 | 11528285.3858 | 29994233.7974 | 20471680.8866 | 91553906.1872 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 120649450.7077 | 162397616.2652 | 56234.1325 | 31.1513 | 3873.0104 | 5213.183 | 78.9566 | 106.2778
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.264 | 68.9861 | 8.1318 | 4 | 3775.4111 | 5058.8938 | 76.9669 | 103.1324 | 173.0369 | 0 | 219.4563 | 9948143.3493 | 594316.6715 | 9720853.5489 | 9174391.7518 | 0 | 817550.8471 | 0 | 11799549.9058 | 30700008.4343 | 20953386.5785 | 93708201.0872 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 122803745.6077 | 164551911.1652 | 74989.4209 | 32.5273 | 3775.4111 | 5058.8938 | 76.9669 | 103.1324
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8339 | 70.7679 | 8.4117 | 4 | 3701.4282 | 4942.2048 | 75.4586 | 100.7535 | 172.8011 | 0 | 227.6918 | 10121710.3385 | 603110.193 | 9922725.548 | 9418237.8965 | 0 | 750448.466 | 0 | 12018330.6524 | 31269231.059 | 21341892.7162 | 95445686.8696 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 124541231.3901 | 166289396.9477 | 100000 | 33.6468 | 3701.4282 | 4942.2048 | 75.4586 | 100.7535
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.1466 | 72.0471 | 8.6232 | 4 | 3645.4714 | 4855.8168 | 74.3179 | 98.9924 | 172.6255 | 0 | 222.574 | 10245176.2028 | 609309.7016 | 10067084.1585 | 9593667.675 | 0 | 688814.8535 | 0 | 12169580.5106 | 31662752.1645 | 21610478.9567 | 96646864.2232 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 125742408.7437 | 167490574.3013 | 133352.1432 | 34.4928 | 3645.4714 | 4855.8168 | 74.3179 | 98.9924
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.6144 | 72.9941 | 8.7844 | 4 | 3603.2046 | 4791.3444 | 73.4562 | 97.678 | 172.4918 | 0 | 223.451 | 10335905.8916 | 613822.6688 | 10173682.7718 | 9723862.5589 | 0 | 636024.9627 | 0 | 12278486.553 | 31946103.347 | 21803871.9611 | 97511760.715 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 126607305.2356 | 168355470.7931 | 177827.941 | 35.1374 | 3603.2046 | 4791.3444 | 73.4562 | 97.678
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.4929 | 73.7117 | 8.9079 | 4 | 3571.3009 | 4742.9622 | 72.8058 | 96.6917 | 172.3885 | 0 | 195.7054 | 10404265.6841 | 617198.5994 | 10254293.1998 | 9822688.5268 | 0 | 592733.3203 | 0 | 12359559.9389 | 32157039.6666 | 21947840.3336 | 98155619.2696 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 127251163.7901 | 168999329.3477 | 237137.3706 | 35.6316 | 3571.3009 | 4742.9622 | 72.8058 | 96.6917
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8935 | 74.2449 | 9.0013 | 4 | 3547.239 | 4706.7384 | 72.3153 | 95.9532 | 172.3106 | 0 | 213.5912 | 10454851.81 | 619683.5241 | 10314106.8268 | 9896225.347 | 0 | 557532.0147 | 0 | 12418535.8138 | 32310482.7955 | 22052568.422 | 98623986.5539 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 127719531.0744 | 169467696.6319 | 316227.766 | 36.0053 | 3547.239 | 4706.7384 | 72.3153 | 95.9532
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.907 | 74.6297 | 9.0708 | 4 | 3529.107 | 4679.7262 | 71.9456 | 95.4025 | 172.2538 | 0 | 164.403 | 10491247.8158 | 621464.0083 | 10357230.9968 | 9949355.1555 | 0 | 528946.6878 | 0 | 12459815.4191 | 32417883.8608 | 22125871.8559 | 98951815.8001 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128047360.3206 | 169795525.8781 | 421696.5034 | 36.2832 | 3529.107 | 4679.7262 | 71.9456 | 95.4025
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6787 | 74.9222 | 9.1236 | 4 | 3515.4545 | 4659.4136 | 71.6673 | 94.9884 | 172.2103 | 0 | 192.3907 | 10518848.741 | 622810.3529 | 10389982.1417 | 9989766.8312 | 0 | 506666.0294 | 0 | 12490948.8975 | 32498886.7854 | 22181158.0164 | 99199067.7956 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128294612.3161 | 170042777.8736 | 562341.3252 | 36.4945 | 3515.4545 | 4659.4136 | 71.6673 | 94.9884
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2318 | 75.1314 | 9.1626 | 4 | 3505.1824 | 4644.2773 | 71.4579 | 94.6799 | 172.179 | 0 | 219.5592 | 10538564.5152 | 623769.7025 | 10413404.8214 | 10018702.1239 | 0 | 488956.554 | 0 | 12512525.1096 | 32555023.6635 | 22219472.5892 | 99370419.0793 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128465963.5998 | 170214129.1573 | 749894.2093 | 36.6503 | 3505.1824 | 4644.2773 | 71.4579 | 94.6799
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.6339 | 75.2834 | 9.1915 | 4 | 3497.4585 | 4632.9708 | 71.3004 | 94.4494 | 172.1561 | 0 | 234.4536 | 10552865.0497 | 624464.3083 | 10430408.8325 | 10039725.9392 | 0 | 475113.7245 | 0 | 12527805.3631 | 32594779.7486 | 22246606.9342 | 99491769.9001 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128587314.4206 | 170335479.9782 | 1000000 | 36.7659 | 3497.4585 | 4632.9708 | 71.3004 | 94.4494
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.946 | 75.4013 | 9.2136 | 4 | 3491.6539 | 4624.4447 | 71.1821 | 94.2756 | 172.1383 | 0 | 249.7474 | 10563948.0306 | 625002.0858 | 10443594.0736 | 10056037.8222 | 0 | 464669.7826 | 0 | 12539768.1999 | 32625904.5961 | 22267850.2821 | 99586774.8729 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128682319.3934 | 170430484.9509 | 1333521.4322 | 36.8543 | 3491.6539 | 4624.4447 | 71.1821 | 94.2756
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.1649 | 75.484 | 9.2297 | 4 | 3487.2937 | 4618.1086 | 71.0932 | 94.1464 | 172.1258 | 0 | 253.4706 | 10571709.6916 | 625378.215 | 10452833.4073 | 10067473.9752 | 0 | 456480.1417 | 0 | 12547811.418 | 32646831.3996 | 22282133.2556 | 99650651.504 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128746196.0245 | 170494361.5821 | 1778279.41 | 36.9187 | 3487.2937 | 4618.1086 | 71.0932 | 94.1464
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.3307 | 75.5465 | 9.2418 | 4 | 3484.0197 | 4613.3486 | 71.0265 | 94.0494 | 172.1163 | 0 | 247.3568 | 10577582.2683 | 625662.629 | 10459826.1514 | 10076132.1799 | 0 | 450287.0274 | 0 | 12553901.1999 | 32662675.7628 | 22292947.359 | 99699014.5778 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128794559.0983 | 170542724.6558 | 2371373.7057 | 36.9672 | 3484.0197 | 4613.3486 | 71.0265 | 94.0494
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4498 | 75.5914 | 9.2508 | 4 | 3481.562 | 4609.7987 | 70.9763 | 93.977 | 172.1095 | 0 | 228.2112 | 10581798.2649 | 625866.6594 | 10464848.0083 | 10082351.8567 | 0 | 445520.2866 | 0 | 12558150.1796 | 32673730.7364 | 22300492.6056 | 99732758.5975 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128828303.118 | 170576468.6755 | 3162277.6602 | 37.003 | 3481.562 | 4609.7987 | 70.9763 | 93.977
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5593 | 75.6327 | 9.2581 | 4 | 3479.7175 | 4607.0557 | 70.9387 | 93.9211 | 172.1033 | 0 | 246.2232 | 10585674.2337 | 626054.381 | 10469463.868 | 10088068.887 | 0 | 442225.8705 | 0 | 12562480.0237 | 32684996.1026 | 22308181.4495 | 99767144.816 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128862689.3365 | 170610854.894 | 4216965.0343 | 37.0325 | 3479.7175 | 4607.0557 | 70.9387 | 93.9211
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.613 | 75.653 | 9.2627 | 4 | 3478.3336 | 4605.1113 | 70.9105 | 93.8814 | 172.1002 | 0 | 235.5197 | 10587571.0435 | 626145.9688 | 10471725.2309 | 10090871.2049 | 0 | 439310.6254 | 0 | 12564093.3887 | 32689193.7474 | 22311046.4283 | 99779957.6379 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128875502.1584 | 170623667.7159 | 5623413.2519 | 37.0509 | 3478.3336 | 4605.1113 | 70.9105 | 93.8814
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6667 | 75.6732 | 9.2666 | 4 | 3477.2953 | 4603.5994 | 70.8894 | 93.8506 | 172.0971 | 0 | 226.8553 | 10589470.6601 | 626237.8587 | 10473988.5843 | 10093675.4649 | 0 | 437320.2166 | 0 | 12566070.186 | 32694336.9685 | 22314556.7824 | 99795656.7214 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128891201.2419 | 170639366.7994 | 7498942.0933 | 37.0665 | 3477.2953 | 4603.5994 | 70.8894 | 93.8506
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.7056 | 75.6879 | 9.2695 | 4 | 3476.5164 | 4602.4711 | 70.8735 | 93.8276 | 172.0949 | 0 | 231.463 | 10590845.6939 | 626304.3483 | 10475627.1582 | 10095705.8562 | 0 | 435801.9648 | 0 | 12567471.1584 | 32697982.0113 | 22317044.5991 | 99806782.7902 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128902327.3108 | 170650492.8683 | 10000000 | 37.078 | 3476.5164 | 4602.4711 | 70.8735 | 93.8276
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1508 | [19 empty] | 100 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6447 | [19 empty] | 133.3521 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.30155 | 0.011778 | 4 | 660815.6182 | 1564952.6886 | 13471.6202 | 31903.6773 | 117.6145 | 0 | 51.8696 | 170129.2017 | 6709.2866 | 130766.5042 | 77446.3545 | 0 | 77099.0836 | 0 | 180238.6679 | 468944.042 | 320063.9445 | 1431397.085 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 31131552.2944 | 73726172.8165 | 177.8279 | 0.047111 | 660815.6182 | 1564952.6886 | 13471.6202 | 31903.6773
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.46153 | 0.026019 | 4 | 303868.4252 | 713133.6853 | 6194.7689 | 14538.1948 | 128.7104 | 0 | 277.0155 | 242117.8153 | 10336.2513 | 182396.1826 | 99496.3625 | 0 | 87237.1433 | 0 | 242417.6645 | 630721.0363 | 430480.0673 | 1925202.5233 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 31625357.7328 | 74219978.2548 | 237.1374 | 0.10408 | 303868.4252 | 713133.6853 | 6194.7689 | 14538.1948
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.68004 | 0.047551 | 4 | 169508.5935 | 393450.3269 | 3455.662 | 8021.0171 | 138.2278 | 0 | 357.846 | 331461.7816 | 15161.1959 | 247118.6565 | 128723.2265 | 0 | 97959.6116 | 0 | 319965.5441 | 832484.7117 | 568187.9216 | 2541062.6494 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 32241217.8589 | 74835838.3809 | 316.2278 | 0.1902 | 169508.5935 | 393450.3269 | 3455.662 | 8021.0171
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.11 | 0.9841 | 0.079336 | 4 | 104094.3497 | 238317.208 | 2122.1041 | 4858.4186 | 146.4743 | 0 | 469.3232 | 444572.6396 | 21628.6472 | 330313.799 | 168940.6155 | 0 | 110790.8148 | 0 | 419736.1413 | 1092067.3399 | 745358.3992 | 3333408.3966 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 33033563.606 | 75628184.1281 | 421.6965 | 0.31734 | 104094.3497 | 238317.208 | 2122.1041 | 4858.4186
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0654 | 1.4033 | 0.12506 | 4 | 68069.3277 | 153218.4561 | 1387.6853 | 3123.5655 | 153.4358 | 0 | 61.6254 | 586628.7334 | 30150.9122 | 436709.0928 | 224757.1382 | 0 | 126399.1816 | 0 | 547811.5727 | 1425293.3404 | 972791.9917 | 4350541.9629 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 34050697.1724 | 76645317.6944 | 562.3413 | 0.50024 | 68069.3277 | 153218.4561 | 1387.6853 | 3123.5655
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3347 | 1.9722 | 0.1887 | 4 | 46811.2062 | 103244.3074 | 954.3098 | 2104.7749 | 159.1604 | 0 | 80.2033 | 761745.4235 | 41005.738 | 571202.9221 | 299049.8286 | 0 | 145395.3997 | 0 | 709175.7316 | 1845129.7818 | 1259338.9897 | 5632043.8149 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 35332199.0244 | 77926819.5464 | 749.8942 | 0.75478 | 46811.2062 | 103244.3074 | 954.3098 | 2104.7749
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0131 | 2.7318 | 0.27498 | 4 | 33570.1805 | 72295.6952 | 684.3735 | 1473.8455 | 163.7016 | 0 | 81.0226 | 974242.0149 | 54444.1452 | 739103.4365 | 396343.9394 | 0 | 168273.6168 | 0 | 909638.7896 | 2366693.5379 | 1615316.9703 | 7224056.4507 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 36924211.6601 | 79518832.1822 | 1000 | 1.0999 | 33570.1805 | 72295.6952 | 684.3735 | 1473.8455
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2252 | 3.7458 | 0.39231 | 4 | 24803.734 | 51947.1152 | 505.6577 | 1059.0122 | 167.3309 | 0 | 83.0085 | 1233964.5023 | 71229.8786 | 949103.0373 | 527962.6456 | 0 | 195534.5872 | 0 | 1161339.9139 | 3021568.2324 | 2062282.4056 | 9222985.2029 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 38923140.4123 | 81517760.9344 | 1333.5214 | 1.5692 | 24803.734 | 51947.1152 | 505.6577 | 1059.0122
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1675 | 5.107 | 0.55197 | 4 | 18774.7172 | 38066.7026 | 382.748 | 776.0412 | 170.2715 | 0 | 87.1113 | 1553753.7266 | 92279.7381 | 1213639.2199 | 705958.4369 | 0 | 228825.0378 | 0 | 1479837.9022 | 3850234.6649 | 2627864.2732 | 11752392.9996 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 41452548.2091 | 84047168.7312 | 1778.2794 | 2.2079 | 18774.7172 | 38066.7026 | 382.748 | 776.0412
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0922 | 6.9268 | 0.76595 | 4 | 14569.9558 | 28472.4652 | 297.0283 | 580.4497 | 172.5093 | 0 | 74.0008 | 1944408.6011 | 118090.2756 | 1546211.6568 | 944485.827 | 0 | 270235.9845 | 0 | 1881138.6146 | 4894336.8005 | 3340485.4349 | 14939393.1951 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 44639548.4046 | 87234168.9266 | 2371.3737 | 3.0638 | 14569.9558 | 28472.4652 | 297.0283 | 580.4497
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.2662 | 9.3319 | 1.0492 | 4 | 11580.6398 | 21729.7682 | 236.087 | 442.9907 | 174.2254 | 0 | 105.2547 | 2416394.2534 | 149165.981 | 1960171.0958 | 1257155.8731 | 0 | 320048.2952 | 0 | 2380144.8444 | 6192648.6504 | 4226609.9501 | 18902338.9435 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 48602494.153 | 91197114.675 | 3162.2777 | 4.1969 | 11580.6398 | 21729.7682 | 236.087 | 442.9907
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0996 | 12.5084 | 1.425 | 4 | 9397.2766 | 16869.8519 | 191.5762 | 343.9147 | 175.5413 | 0 | 78.7974 | 2989834.6909 | 187088.9217 | 2475372.7958 | 1672364.9346 | 0 | 380715.3773 | 0 | 3005096.9209 | 7818645.758 | 5336386.387 | 23865505.7861 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 53565660.9956 | 96160281.5176 | 4216.965 | 5.7001 | 9397.2766 | 16869.8519 | 191.5762 | 343.9147
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0326 | 16.6574 | 1.9158 | 4 | 7789.6249 | 13347.832 | 158.802 | 272.1136 | 176.5413 | 0 | 102.1646 | 3677709.4461 | 232314.6525 | 3110578.9806 | 2210074.1518 | 0 | 453597.4165 | 0 | 3776867.1125 | 9826633.4848 | 6706879.2705 | 29994654.5152 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 59694809.7247 | 102289430.2468 | 5623.4133 | 7.6634 | 7789.6249 | 13347.832 | 158.802 | 272.1136
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.5795 | 22.0314 | 2.5504 | 4 | 6590.7062 | 10765.9491 | 134.3605 | 219.4784 | 177.2874 | 0 | 98.9442 | 4497548.8233 | 285781.0673 | 3888322.4428 | 2906486.3585 | 0 | 541089.9083 | 0 | 4726499.154 | 12297381.2605 | 8393215.3962 | 37536324.4109 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 67236479.6204 | 109831100.1425 | 7498.9421 | 10.2017 | 6590.7062 | 10765.9491 | 134.3605 | 219.4784
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1615 | 28.8136 | 3.3475 | 4 | 5698.5586 | 8879.5891 | 116.1728 | 181.0224 | 177.777 | 0 | 117.2651 | 5451104.4551 | 347180.1395 | 4818055.1799 | 3786462.2985 | 0 | 644290.1947 | 0 | 5868365.9844 | 15268284.5239 | 10420917.9195 | 46604660.6954 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 76304815.9048 | 118899436.4269 | 10000 | 13.3902 | 5698.5586 | 8879.5891 | 116.1728 | 181.0224
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.9495 | 36.9956 | 4.3001 | 4 | 5045.0197 | 7521.3737 | 102.8495 | 153.3334 | 177.9272 | 0 | 123.4658 | 6514428.178 | 414420.952 | 5884010.7722 | 4852063.3757 | 0 | 763303.8052 | 0 | 7187008.5624 | 18699122.0213 | 12762535.0081 | 57076892.6749 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 86777047.8843 | 129371668.4064 | 13335.2143 | 17.2005 | 5045.0197 | 7521.3737 | 102.8495 | 153.3334
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5562 | 46.2514 | 5.3573 | 4 | 4581.5716 | 6569.2704 | 93.4015 | 133.9235 | 177.6386 | 0 | 123.626 | 7628365.5173 | 482608.7859 | 7036094.9162 | 6066702.0891 | 0 | 895770.1666 | 0 | 8622721.1753 | 22434551.7347 | 15312042.5429 | 68478856.928 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 98179012.1374 | 140773632.6595 | 17782.7941 | 21.4291 | 4581.5716 | 6569.2704 | 93.4015 | 133.9235
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9728 | 55.9664 | 6.4312 | 4 | 4267.3894 | 5923.1591 | 86.9965 | 120.7516 | 176.8894 | 0 | 106.861 | 8713651.6302 | 545695.8398 | 8199446.7913 | 7358239.1528 | 0 | 1037580.0985 | 0 | 10083299.2699 | 26234676.3312 | 17905705.6647 | 80078294.7784 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 109778449.9879 | 152373070.5099 | 23713.7371 | 25.725 | 4267.3894 | 5923.1591 | 86.9965 | 120.7516
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.5085 | 62.9322 | 7.2495 | 4 | 4058.6991 | 5527.5747 | 82.7421 | 112.6871 | 176.126 | 0 | 150.4741 | 9442429.6901 | 585107.5287 | 9011335.5772 | 8297429.6995 | 0 | 1074176.3477 | 0 | 11080086.7489 | 28828112.8822 | 19675779.4006 | 87994457.8749 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 117694613.0844 | 160289233.6065 | 31622.7766 | 28.9981 | 4058.6991 | 5527.5747 | 82.7421 | 112.6871
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.8829 | 66.4097 | 7.7744 | 4 | 3899.6943 | 5269.4088 | 79.5005 | 107.424 | 175.7344 | 0 | 108.0781 | 9795224.5232 | 603790.7705 | 9410270.7179 | 8768439.3915 | 0 | 987297.1938 | 0 | 11530358.8127 | 29999628.4289 | 20475362.8335 | 91570372.6719 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 121270527.8813 | 163865148.4034 | 42169.6503 | 31.0974 | 3899.6943 | 5269.4088 | 79.5005 | 107.424
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.7714 | 69.2322 | 8.2102 | 4 | 3778.9953 | 5076.0016 | 77.0399 | 103.4812 | 175.3918 | 0 | 112.8812 | 10075675.1276 | 618301.2702 | 9731348.1768 | 9152619.214 | 0 | 902211.8871 | 0 | 11887260.7135 | 30928213.9642 | 21109141.5418 | 94404771.8952 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 124104927.1046 | 166699547.6267 | 56234.1325 | 32.8407 | 3778.9953 | 5076.0016 | 77.0399 | 103.4812
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.1297 | 71.4067 | 8.5578 | 4 | 3687.4791 | 4931.8023 | 75.1742 | 100.5415 | 175.1137 | 0 | 141.2075 | 10288171.0105 | 629072.2582 | 9977169.2498 | 9450140.9448 | 0 | 820640.5788 | 0 | 12154425.6764 | 31623322.3945 | 21583567.3285 | 96526509.4416 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 126226664.651 | 168821285.1731 | 74989.4209 | 34.2312 | 3687.4791 | 4931.8023 | 75.1742 | 100.5415
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.3956 | 73.1156 | 8.8338 | 4 | 3618.1921 | 4823.6301 | 73.7617 | 98.3362 | 174.8849 | 0 | 140.4502 | 10452642.4775 | 637205.7999 | 10169510.8928 | 9680930.7124 | 0 | 749097.1317 | 0 | 12358860.9356 | 32155221.0034 | 21946599.0586 | 98150068.0119 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 127850223.2214 | 170444843.7434 | 100000 | 35.3354 | 3618.1921 | 4823.6301 | 73.7617 | 98.3362
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.6157 | 74.3902 | 9.0455 | 4 | 3565.7596 | 4742.9893 | 72.6928 | 96.6923 | 174.7079 | 0 | 175.1324 | 10573782.0105 | 643060.6898 | 10312533.2038 | 9850325.2585 | 0 | 686270.7219 | 0 | 12505729.035 | 32537341.6712 | 22207404.2661 | 99316446.8567 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 129016602.0662 | 171611222.5882 | 133352.1432 | 36.1821 | 3565.7596 | 4742.9893 | 72.6928 | 96.6923
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.0371 | 75.3436 | 9.2074 | 4 | 3526.1323 | 4682.6583 | 71.885 | 95.4623 | 174.5724 | 0 | 177.2537 | 10663683.9622 | 647353.5303 | 10419258.182 | 9977157.1468 | 0 | 633000.1633 | 0 | 12612776.664 | 32815857.6434 | 22397497.1401 | 100166584.432 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 129866739.6415 | 172461360.1636 | 177827.941 | 36.8298 | 3526.1323 | 4682.6583 | 71.885 | 95.4623
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8398 | 76.0507 | 9.3302 | 4 | 3496.2114 | 4637.525 | 71.275 | 94.5422 | 174.4701 | 0 | 206.0409 | 10729960.0434 | 650488.9386 | 10498263.7992 | 10071284.2205 | 0 | 588797.7577 | 0 | 12690129.9562 | 33017115.0424 | 22534859.4503 | 100780899.2084 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 130481054.4179 | 173075674.9399 | 237137.3706 | 37.3207 | 3496.2114 | 4637.525 | 71.275 | 94.5422
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.1723 | 76.5718 | 9.4226 | 4 | 3473.6406 | 4603.7651 | 70.8149 | 93.854 | 174.3938 | 0 | 251.3382 | 10778587.8378 | 652773.0151 | 10556414.5125 | 10140694.1033 | 0 | 552763.8414 | 0 | 12745680.9909 | 33161647.4398 | 22633505.7814 | 101222067.5222 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 130922222.7316 | 173516843.2537 | 316227.766 | 37.6902 | 3473.6406 | 4603.7651 | 70.8149 | 93.854
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1586 | 76.9567 | 9.492 | 4 | 3456.6292 | 4578.4907 | 70.4681 | 93.3387 | 174.3368 | 0 | 236.3087 | 10814382.736 | 654445.2579 | 10599320.3016 | 10191977.884 | 0 | 523910.9343 | 0 | 12785774.4744 | 33265962.4593 | 22704702.9257 | 101540476.9732 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131240632.1826 | 173835252.7047 | 421696.5034 | 37.9678 | 3456.6292 | 4578.4907 | 70.4681 | 93.3387
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.8702 | 77.2339 | 9.5434 | 4 | 3443.8184 | 4559.6348 | 70.2069 | 92.9543 | 174.2955 | 0 | 240.1422 | 10840099.8672 | 655641.6013 | 10630202.217 | 10228927.0682 | 0 | 500836.2999 | 0 | 12813725.7509 | 33338685.9473 | 22754338.2006 | 101762456.9525 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131462612.1619 | 174057232.684 | 562341.3252 | 38.1735 | 3443.8184 | 4559.6348 | 70.2069 | 92.9543
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4085 | 77.4433 | 9.5823 | 4 | 3434.1781 | 4545.4655 | 70.0104 | 92.6655 | 174.2641 | 0 | 251.2608 | 10859495.4862 | 656541.3006 | 10653522.1594 | 10256849.3135 | 0 | 482980.8528 | 0 | 12834661.7539 | 33393157.1324 | 22791515.9036 | 101928723.9024 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131628879.1118 | 174223499.6339 | 749894.2093 | 38.3291 | 3434.1781 | 4545.4655 | 70.0104 | 92.6655
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.7936 | 77.593 | 9.6109 | 4 | 3426.9285 | 4534.9038 | 69.8626 | 92.4501 | 174.2416 | 0 | 231.7813 | 10873338.1837 | 657181.7611 | 10670183.4073 | 10276809.6001 | 0 | 468934.9998 | 0 | 12849114.7013 | 33430760.7368 | 22817181.1363 | 102043504.5264 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131743659.7358 | 174338280.2579 | 1000000 | 38.4437 | 3426.9285 | 4534.9038 | 69.8626 | 92.4501
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.0734 | 77.7017 | 9.6322 | 4 | 3421.4797 | 4527.0122 | 69.7515 | 92.2893 | 174.2252 | 0 | 244.3746 | 10883380.6703 | 657645.5314 | 10682279.9619 | 10291307.0365 | 0 | 458042.2926 | 0 | 12859335.6421 | 33457353.5283 | 22835331.263 | 102124675.926 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131824831.1355 | 174419451.6575 | 1333521.4322 | 38.5286 | 3421.4797 | 4527.0122 | 69.7515 | 92.2893
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.2929 | 77.7869 | 9.6484 | 4 | 3417.3865 | 4521.0536 | 69.668 | 92.1678 | 174.2123 | 0 | 228.9075 | 10891249.4613 | 658008.634 | 10691761.9051 | 10302674.3209 | 0 | 449889.7636 | 0 | 12867497.7931 | 33478589.771 | 22849825.4349 | 102189497.0839 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131889652.2933 | 174484272.8154 | 1778279.41 | 38.5937 | 3417.3865 | 4521.0536 | 69.668 | 92.1678
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.4561 | 77.8502 | 9.6606 | 4 | 3414.3127 | 4516.5886 | 69.6054 | 92.0768 | 174.2027 | 0 | 237.6142 | 10897093.6845 | 658278.0464 | 10698807.1661 | 10311122.3362 | 0 | 443678.2407 | 0 | 12873501.9948 | 33494211.4722 | 22860487.567 | 102237180.5079 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131937335.7173 | 174531956.2394 | 2371373.7057 | 38.6424 | 3414.3127 | 4516.5886 | 69.6054 | 92.0768
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.5681 | 77.8937 | 9.6694 | 4 | 3412.0052 | 4513.2785 | 69.5583 | 92.0093 | 174.1961 | 0 | 236.0285 | 10901102.4922 | 658462.5725 | 10703642.4104 | 10316921.2186 | 0 | 438817.3497 | 0 | 12877388.9569 | 33504324.5502 | 22867389.9506 | 102268049.5011 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131968204.7106 | 174562825.2326 | 3162277.6602 | 38.6776 | 3412.0052 | 4513.2785 | 69.5583 | 92.0093
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.6413 | 77.9221 | 9.6756 | 4 | 3410.2734 | 4510.8371 | 69.523 | 91.9595 | 174.1918 | 0 | 232.5439 | 10903716.1975 | 658582.6502 | 10706796.9619 | 10320704.8317 | 0 | 434978.6043 | 0 | 12879663.9058 | 33510243.5005 | 22871429.7558 | 102286116.4077 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131986271.6172 | 174580892.1392 | 4216965.0343 | 38.7025 | 3410.2734 | 4510.8371 | 69.523 | 91.9595
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.7191 | 77.9523 | 9.6811 | 4 | 3408.9739 | 4508.918 | 69.4965 | 91.9204 | 174.1872 | 0 | 245.7601 | 10906500.2936 | 658710.9405 | 10710154.2589 | 10324732.0749 | 0 | 432439.5571 | 0 | 12882689.4787 | 33518115.4207 | 22876802.5031 | 102310144.5275 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 132010299.737 | 174604920.259 | 5623413.2519 | 38.7244 | 3408.9739 | 4508.918 | 69.4965 | 91.9204
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.7534 | 77.9655 | 9.6844 | 4 | 3407.9989 | 4507.5707 | 69.4767 | 91.8929 | 174.1851 | 0 | 228.2075 | 10907721.8739 | 658766.8964 | 10711630.0503 | 10326502.4078 | 0 | 430154.9302 | 0 | 12883562.7019 | 33520387.3682 | 22878353.1539 | 102317079.3825 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 132017234.592 | 174611855.114 | 7498942.0933 | 38.7375 | 3407.9989 | 4507.5707 | 69.4767 | 91.8929
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.7922 | 77.9806 | 9.6873 | 4 | 3407.2676 | 4506.5097 | 69.4618 | 91.8713 | 174.1829 | 0 | 229.8307 | 10909112.4193 | 658830.8795 | 10713307.7182 | 10328515.0601 | 0 | 428641.2119 | 0 | 12884978.8427 | 33524071.8761 | 22880867.9062 | 102328325.9139 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 132028481.1233 | 174623101.6454 | 10000000 | 38.7491 | 3407.2676 | 4506.5097 | 69.4618 | 91.8713
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7482 | [19 empty] | 100 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9633 | [19 empty] | 133.3521 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.31238 | 0.01308 | 4 | 607335.8214 | 1437805.757 | 12381.3622 | 29311.6151 | 119.0439 | 0 | 38.7883 | 175708.6163 | 6999.2906 | 134372.1943 | 78766.9863 | 0 | 76997.8169 | 0 | 184409.5127 | 479795.7245 | 327470.4408 | 1464520.5823 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 31775146.5715 | 75224426.1853 | 177.8279 | 0.052319 | 607335.8214 | 1437805.757 | 12381.3622 | 29311.6151
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.47596 | 0.028093 | 4 | 287222.9156 | 673881.0083 | 5855.4276 | 13737.9758 | 130.1704 | 0 | 216.8117 | 249128.6229 | 10747.0091 | 186760.4588 | 101125.9809 | 0 | 86668.2812 | 0 | 247427.8376 | 643756.4791 | 439377.0249 | 1964991.6946 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 32275617.6839 | 75724897.2976 | 237.1374 | 0.11237 | 287222.9156 | 673881.0083 | 5855.4276 | 13737.9758
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.716 | 0.05187 | 4 | 158810.3633 | 368222.6649 | 3237.5641 | 7506.7171 | 140.3078 | 0 | 326.5996 | 346800.6393 | 16108.158 | 257157.6322 | 133037.4017 | 0 | 99155.4476 | 0 | 332381.1188 | 864787.4903 | 590235.2317 | 2639663.1197 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 32950289.109 | 76399568.7228 | 316.2278 | 0.20748 | 158810.3633 | 368222.6649 | 3237.5641 | 7506.7171
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1878 | 1.0364 | 0.086043 | 4 | 98140.5132 | 224383.0527 | 2000.7271 | 4574.352 | 148.6273 | 0 | 476.2385 | 465163.8848 | 23005.8308 | 343804.8911 | 175097.2263 | 0 | 112208.0224 | 0 | 436519.1436 | 1135733.2693 | 775161.2933 | 3466693.5616 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 33777319.5509 | 77226599.1647 | 421.6965 | 0.34417 | 98140.5132 | 224383.0527 | 2000.7271 | 4574.352
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 1.4727 | 0.13464 | 4 | 64660.8268 | 145336.4618 | 1318.1984 | 2962.8804 | 155.5748 | 0 | 57.8571 | 611988.358 | 31989.3356 | 453265.1968 | 232480.0566 | 0 | 127567.3031 | 0 | 568343.1975 | 1478712.4168 | 1009251.609 | 4513597.4734 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 34824223.4627 | 78273503.0765 | 562.3413 | 0.53857 | 64660.8268 | 145336.4618 | 1318.1984 | 2962.8804
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4468 | 2.0647 | 0.20226 | 4 | 44676.5118 | 98380.2533 | 910.7911 | 2005.6145 | 161.3015 | 0 | 80.1359 | 793266.3029 | 43470.9842 | 591706.7666 | 309201.19 | 0 | 146323.339 | 0 | 734747.7472 | 1911662.9208 | 1304749.2242 | 5835128.475 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 36145754.4643 | 79595034.078 | 749.8942 | 0.80905 | 44676.5118 | 98380.2533 | 910.7911 | 2005.6145
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.14 | 2.8491 | 0.29332 | 4 | 32196.4642 | 69229.1814 | 656.3685 | 1411.3305 | 165.8236 | 0 | 65.4279 | 1011795.3265 | 57609.1329 | 763311.6549 | 408749.1583 | 0 | 168552.3088 | 0 | 939906.8568 | 2445444.8399 | 1669066.3521 | 7464435.6303 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 37775061.6196 | 81224341.2334 | 1000 | 1.1733 | 32196.4642 | 69229.1814 | 656.3685 | 1411.3305
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4032 | 3.9154 | 0.41966 | 4 | 23750.7934 | 49634.6939 | 484.192 | 1011.8704 | 169.5692 | 0 | 71.9216 | 1284842.8429 | 75821.6023 | 981764.8338 | 547436.738 | 0 | 196085.2029 | 0 | 1203520.9758 | 3131314.7029 | 2137186.6268 | 9557973.5256 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 39868599.5148 | 83317879.1286 | 1333.5214 | 1.6786 | 23750.7934 | 49634.6939 | 484.192 | 1011.8704
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4064 | 5.3383 | 0.58979 | 4 | 18014.0861 | 36431.2869 | 367.2415 | 742.7011 | 172.4793 | 0 | 71.8649 | 1618012.2008 | 98368.1839 | 1255384.2623 | 733490.4795 | 0 | 229727.225 | 0 | 1534643.1171 | 3992826.592 | 2725186.1935 | 12187638.2541 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 42498264.2433 | 85947543.8571 | 1778.2794 | 2.3592 | 18014.0861 | 36431.2869 | 367.2415 | 742.7011
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.3869 | 7.231 | 0.81677 | 4 | 14014.0484 | 27313.1189 | 285.6953 | 556.8149 | 174.7251 | 0 | 85.4916 | 2022713.6083 | 125821.5819 | 1597740.7116 | 979216.0449 | 0 | 270725.2987 | 0 | 1948524.7257 | 5069661.6389 | 3460148.2397 | 15474551.8496 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 45785177.8389 | 89234457.4527 | 2371.3737 | 3.2671 | 14014.0484 | 27313.1189 | 285.6953 | 556.8149
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6365 | 9.7231 | 1.1172 | 4 | 11158.721 | 20881.6922 | 227.4856 | 425.7015 | 176.4515 | 0 | 72.8908 | 2511642.5122 | 159141.4963 | 2022225.619 | 1300550.3428 | 0 | 319976.43 | 0 | 2462279.1961 | 6406345.3853 | 4372462.3627 | 19554623.3444 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 49865249.3337 | 93314528.9475 | 3162.2777 | 4.4687 | 11158.721 | 20881.6922 | 227.4856 | 425.7015
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5795 | 13.0379 | 1.5156 | 4 | 9070.2832 | 16237.1212 | 184.91 | 331.0157 | 177.7787 | 0 | 56.2434 | 3106581.7888 | 199293.425 | 2554820.6102 | 1726516.9727 | 0 | 380612.8246 | 0 | 3107451.9923 | 8084952.658 | 5518146.3183 | 24678376.59 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 54989002.5793 | 98438282.1931 | 4216.965 | 6.0625 | 9070.2832 | 16237.1212 | 184.91 | 331.0157
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.671 | 17.5243 | 2.0407 | 4 | 7532.9694 | 12855.8833 | 153.5698 | 262.0846 | 178.7889 | 0 | 65.0815 | 3829401.4882 | 244874.9059 | 3236875.8902 | 2299078.4114 | 0 | 456314.8428 | 0 | 3925952.76 | 10214523.7579 | 6971622.3523 | 31178644.4087 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 61489270.398 | 104938550.0117 | 5623.4133 | 8.1627 | 7532.9694 | 12855.8833 | 153.5698 | 262.0846
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3689 | 23.2571 | 2.7127 | 4 | 6392.1935 | 10396.4636 | 130.3135 | 211.946 | 179.5378 | 0 | 68.2904 | 4681016.3531 | 298617.5108 | 4059311.9017 | 3023538.8479 | 0 | 545259.4733 | 0 | 4917020.1938 | 12793077.9248 | 8731538.5551 | 39049380.7605 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 69360006.7498 | 112809286.3636 | 7498.9421 | 10.8507 | 6392.1935 | 10396.4636 | 130.3135 | 211.946
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.158 | 30.4462 | 3.5551 | 4 | 5539.6288 | 8595.0281 | 112.9328 | 175.2213 | 180.0219 | 0 | 56.5764 | 5669499.1672 | 361010.4581 | 5035131.1851 | 3932380.6534 | 0 | 649911.6885 | 0 | 6102693.9294 | 15877957.7697 | 10837032.4372 | 48465617.2886 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 78776243.2779 | 122225522.8917 | 10000 | 14.2205 | 5539.6288 | 8595.0281 | 112.9328 | 175.2213
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.1164 | 39.0453 | 4.5577 | 4 | 4914.0053 | 7297.2988 | 100.1786 | 148.7653 | 180.1484 | 0 | 69.9063 | 6766367.1362 | 429679.9814 | 6143837.879 | 5029121.951 | 0 | 769071.8958 | 0 | 7463850.7489 | 19419408.6024 | 13254145.4001 | 59275483.5949 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 89586109.5842 | 133035389.198 | 13335.2143 | 18.2308 | 4914.0053 | 7297.2988 | 100.1786 | 148.7653
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.8669 | 48.6648 | 5.67 | 4 | 4467.3823 | 6383.1474 | 91.0736 | 130.1291 | 179.8179 | 0 | 78.6727 | 7913631.2372 | 501063.3958 | 7327675.4878 | 6283461.9184 | 0 | 900597.9776 | 0 | 8941307.7066 | 23263448.5382 | 15877781.6434 | 71008967.9052 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 101319593.8944 | 144768873.5082 | 17782.7941 | 22.6799 | 4467.3823 | 6383.1474 | 91.0736 | 130.1291
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3541 | 58.592 | 6.7996 | 4 | 4161.4165 | 5758.9091 | 84.8361 | 117.4032 | 179.021 | 0 | 89.4553 | 9027658.3763 | 569418.5944 | 8501693.8995 | 7619107.0601 | 0 | 1039163.3351 | 0 | 10435246.0935 | 27150369.772 | 18530685.2537 | 82873342.3846 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 113183968.3739 | 156633247.9877 | 23713.7371 | 27.1984 | 4161.4165 | 5758.9091 | 84.8361 | 117.4032
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.7085 | 66.3694 | 7.7313 | 4 | 3953.4873 | 5358.471 | 80.5972 | 109.2397 | 178.1233 | 0 | 103.2804 | 9877934.3986 | 624126.3546 | 9391193.1849 | 8676173.4803 | 0 | 1118622.6296 | 0 | 11578339.5187 | 30124464.3837 | 20560565.9377 | 91951419.8882 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 122262045.8775 | 165711325.4912 | 31622.7766 | 30.9251 | 3953.4873 | 5358.471 | 80.5972 | 109.2397
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.536 | 69.1377 | 8.2162 | 4 | 3802.7129 | 5124.7812 | 77.5234 | 104.4756 | 177.7874 | 0 | 129.7479 | 10163971.2518 | 640766.7848 | 9704279.7234 | 9051497.8855 | 0 | 1003373.3644 | 0 | 11919916.7138 | 31013178.1783 | 21167131.3638 | 94664115.2657 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 124974741.255 | 168424020.8688 | 42169.6503 | 32.8646 | 3802.7129 | 5124.7812 | 77.5234 | 104.4756
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1077 | 71.8421 | 8.6507 | 4 | 3688.9613 | 4944.625 | 75.2045 | 100.8029 | 177.4484 | 0 | 139.608 | 10433260.8983 | 655139.5267 | 10008909.3129 | 9417153.9894 | 0 | 912465.999 | 0 | 12256502.5933 | 31888905.5933 | 21764833.3189 | 97337171.2319 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 127647797.2211 | 171097076.8349 | 56234.1325 | 34.6026 | 3688.9613 | 4944.625 | 75.2045 | 100.8029
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.4077 | 73.997 | 9.0024 | 4 | 3602.8187 | 4809.4248 | 73.4483 | 98.0466 | 177.162 | 0 | 185.1499 | 10644531.3121 | 666194.208 | 10250222.6077 | 9710213.8855 | 0 | 829877.78 | 0 | 12519405.5194 | 32572925.0783 | 22231690.6726 | 99425061.0637 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 129735687.053 | 173184966.6667 | 74989.4209 | 36.0095 | 3602.8187 | 4809.4248 | 73.4483 | 98.0466
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.1466 | 75.5075 | 9.2665 | 4 | 3537.6231 | 4709.8326 | 72.1192 | 96.0163 | 176.9532 | 0 | 186.0734 | 10790608.0435 | 673663.285 | 10418712.2202 | 9916485.4524 | 0 | 750467.6076 | 0 | 12694475.2774 | 33028420.6768 | 22542575.7781 | 100815408.3409 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 131126034.3302 | 174575313.944 | 100000 | 37.0661 | 3537.6231 | 4709.8326 | 72.1192 | 96.0163
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2406 | 76.7629 | 9.4799 | 4 | 3488.4028 | 4634.2277 | 71.1158 | 94.475 | 176.7767 | 0 | 223.0521 | 10910085.3599 | 679539.527 | 10558444.356 | 10088114.0126 | 0 | 686009.6972 | 0 | 12839655.2515 | 33406149.189 | 22800383.2492 | 101968380.6424 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 132279006.6316 | 175728286.2454 | 133352.1432 | 37.9196 | 3488.4028 | 4634.2277 | 71.1158 | 94.475
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.5575 | 77.6985 | 9.6427 | 4 | 3451.2066 | 4577.685 | 70.3575 | 93.3223 | 176.6423 | 0 | 231.0541 | 10998467.1984 | 683835.2103 | 10662342.5075 | 10216394.4288 | 0 | 631434.3896 | 0 | 12945064.7564 | 33680403.0984 | 22987567.1777 | 102805508.767 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 133116134.7563 | 176565414.3701 | 177827.941 | 38.5709 | 3451.2066 | 4577.685 | 70.3575 | 93.3223
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.287 | 78.3946 | 9.7662 | 4 | 3423.1209 | 4535.3521 | 69.7849 | 92.4593 | 176.5408 | 0 | 178.6747 | 11063865.3369 | 686986.9221 | 10739508.5338 | 10312035.5497 | 0 | 586373.2454 | 0 | 13021620.1393 | 33879584.5009 | 23123512.5777 | 103413486.8058 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 133724112.795 | 177173392.4088 | 237137.3706 | 39.065 | 3423.1209 | 4535.3521 | 69.7849 | 92.4593
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5607 | 78.906 | 9.859 | 4 | 3401.9347 | 4503.6991 | 69.353 | 91.814 | 176.4654 | 0 | 190.0229 | 11111710.1003 | 689277.3715 | 10796124.2667 | 10382409.0083 | 0 | 549656.4982 | 0 | 13076379.1255 | 34022056.1505 | 23220752.406 | 103848364.9271 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134158990.9163 | 177608270.5301 | 316227.766 | 39.4361 | 3401.9347 | 4503.6991 | 69.353 | 91.814
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4887 | 79.2777 | 9.9282 | 4 | 3385.9668 | 4480.0565 | 69.0275 | 91.332 | 176.4101 | 0 | 218.8898 | 11146388.259 | 690928.7048 | 10837250.7269 | 10433640.0564 | 0 | 520078.6944 | 0 | 13115031.7122 | 34122622.2523 | 23289390.8369 | 104155331.243 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134465957.2322 | 177915236.846 | 421696.5034 | 39.7127 | 3385.9668 | 4480.0565 | 69.0275 | 91.332
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.164 | 79.5479 | 9.9796 | 4 | 3373.9414 | 4462.3917 | 68.7824 | 90.9719 | 176.3696 | 0 | 242.0369 | 11171529.2512 | 692121.1049 | 10867115.8593 | 10470902.1771 | 0 | 496568.1561 | 0 | 13142312.2539 | 34193600.6258 | 23337835.0353 | 104371984.4635 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134682610.4528 | 178131890.0666 | 562341.3252 | 39.9185 | 3373.9414 | 4462.3917 | 68.7824 | 90.9719
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.6607 | 79.7464 | 10.018 | 4 | 3364.8917 | 4449.1697 | 68.5979 | 90.7023 | 176.3397 | 0 | 171.5321 | 11189971.4926 | 692993.2264 | 10889049.9864 | 10498300.8234 | 0 | 478165.4625 | 0 | 13161907.5866 | 34244583.6618 | 23372632.005 | 104527604.2447 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134838230.2339 | 178287509.8477 | 749894.2093 | 40.0721 | 3364.8917 | 4449.1697 | 68.5979 | 90.7023
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.0091 | 79.8855 | 10.0461 | 4 | 3358.0859 | 4439.3379 | 68.4591 | 90.5019 | 176.3186 | 0 | 195.9013 | 11202876.0533 | 693601.8575 | 10904413.6623 | 10517509.4594 | 0 | 463615.3241 | 0 | 13174986.3791 | 34278611.997 | 23395857.043 | 104631471.7757 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134942097.765 | 178391377.3788 | 1000000 | 40.1842 | 3358.0859 | 4439.3379 | 68.4591 | 90.5019
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.2797 | 79.9935 | 10.0675 | 4 | 3352.9704 | 4431.9231 | 68.3548 | 90.3507 | 176.3022 | 0 | 172.1759 | 11212887.1297 | 694073.4842 | 10916338.6199 | 10532427.2054 | 0 | 452622.671 | 0 | 13185256.153 | 34305331.8421 | 23414093.8863 | 104713030.9916 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135023656.9809 | 178472936.5946 | 1333521.4322 | 40.2699 | 3352.9704 | 4431.9231 | 68.3548 | 90.3507
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4696 | 80.0692 | 10.0831 | 4 | 3349.1273 | 4426.4088 | 68.2765 | 90.2383 | 176.2907 | 0 | 171.0773 | 11219900.645 | 694403.3074 | 10924698.4176 | 10542890.6201 | 0 | 444042.9479 | 0 | 13192115.0158 | 34323177.1963 | 23426273.7072 | 104767501.8573 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135078127.8466 | 178527407.4604 | 1778279.41 | 40.3323 | 3349.1273 | 4426.4088 | 68.2765 | 90.2383
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.6204 | 80.1293 | 10.0951 | 4 | 3346.2412 | 4422.2392 | 68.2177 | 90.1533 | 176.2815 | 0 | 145.4638 | 11225468.4526 | 694665.0815 | 10931336.135 | 10551200.8066 | 0 | 437662.3692 | 0 | 13197729.8095 | 34337785.7377 | 23436244.3369 | 104812092.7291 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135122718.7183 | 178571998.3321 | 2371373.7057 | 40.3804 | 3346.2412 | 4422.2392 | 68.2177 | 90.1533
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.7324 | 80.174 | 10.1041 | 4 | 3344.0746 | 4419.1149 | 68.1735 | 90.0896 | 176.2747 | 0 | 147.3677 | 11229603.6861 | 694859.3616 | 10936267.4176 | 10557376.2555 | 0 | 432817.0276 | 0 | 13201860.2619 | 34348532.3275 | 23443579.1053 | 104844895.443 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135155521.4322 | 178604801.046 | 3162277.6602 | 40.4164 | 3344.0746 | 4419.1149 | 68.1735 | 90.0896
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8056 | 80.2031 | 10.1105 | 4 | 3342.4484 | 4416.8123 | 68.1403 | 90.0427 | 176.2702 | 0 | 229.4328 | 11232299.9671 | 694985.7914 | 10939484.7299 | 10561406.7609 | 0 | 428987.2146 | 0 | 13204294.1409 | 34354864.7815 | 23447901.1352 | 104864224.5214 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135174850.5107 | 178624130.1245 | 4216965.0343 | 40.4419 | 3342.4484 | 4416.8123 | 68.1403 | 90.0427
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8593 | 80.2245 | 10.1152 | 4 | 3341.2282 | 4415.0895 | 68.1155 | 90.0076 | 176.267 | 0 | 220.3612 | 11234278.6417 | 695078.5204 | 10941846.2366 | 10564365.6101 | 0 | 426082.0979 | 0 | 13206043.9316 | 34359417.3781 | 23451008.3759 | 104878120.7924 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135188746.7817 | 178638026.3955 | 5623413.2519 | 40.4608 | 3341.2282 | 4415.0895 | 68.1155 | 90.0076
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8982 | 80.24 | 10.1187 | 4 | 3340.3127 | 4413.8025 | 68.0968 | 89.9813 | 176.2646 | 0 | 174.3095 | 11235710.8049 | 695145.594 | 10943555.8618 | 10566507.9894 | 0 | 423873.1773 | 0 | 13207269.4367 | 34362605.8908 | 23453184.6014 | 104887853.3564 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135198479.3457 | 178647758.9595 | 7498942.0933 | 40.4748 | 3340.3127 | 4413.8025 | 68.0968 | 89.9813
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.9371 | 80.2555 | 10.1217 | 4 | 3339.6259 | 4412.8003 | 68.0828 | 89.9609 | 176.2622 | 0 | 200.256 | 11237145.3723 | 695212.974 | 10945266.9738 | 10568651.5991 | 0 | 422364.915 | 0 | 13208770.3154 | 34366510.8692 | 23455849.8294 | 104899772.8482 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 135210398.8375 | 178659678.4513 | 10000000 | 40.4867 | 3339.6259 | 4412.8003 | 68.0828 | 89.9609

## Water (R600a)
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 12.1253 | [19 empty] | 100 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4857 | [19 empty] | 133.3521 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.5287 | [19 empty] | 177.8279 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4634 | [19 empty] | 237.1374 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5286 | [19 empty] | 316.2278 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6139 | [19 empty] | 421.6965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8753 | [19 empty] | 562.3413 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.598 | [19 empty] | 749.8942 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.323 | [19 empty] | 1000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2102 | [19 empty] | 1333.5214 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6099 | [19 empty] | 1778.2794 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.971 | [19 empty] | 2371.3737 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8802 | [19 empty] | 3162.2777 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.2166 | [19 empty] | 4216.965 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.1548 | [19 empty] | 5623.4133 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.9835 | [19 empty] | 7498.9421 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.0685 | [19 empty] | 10000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8648 | [19 empty] | 13335.2143 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.2706 | [19 empty] | 17782.7941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7908 | [19 empty] | 23713.7371 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6421 | [19 empty] | 31622.7766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.0792 | [19 empty] | 42169.6503 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.0745 | [19 empty] | 56234.1325 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2616 | [19 empty] | 74989.4209 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7605 | [19 empty] | 100000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9376 | [19 empty] | 133352.1432 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.5248 | [19 empty] | 177827.941 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.466 | [19 empty] | 237137.3706 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1926 | [19 empty] | 316227.766 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6011 | [19 empty] | 421696.5034 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.0691 | [19 empty] | 562341.3252 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.7035 | [19 empty] | 749894.2093 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8227 | [19 empty] | 1000000 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.0983 | [19 empty] | 1333521.4322 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.2891 | [19 empty] | 1778279.41 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8123 | [19 empty] | 2371373.7057 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.7157 | [19 empty] | 3162277.6602 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8473 | [19 empty] | 4216965.0343 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.157 | [19 empty] | 5623413.2519 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.1719 | [19 empty] | 7498942.0933 | 0
1 | 1000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5186 | [19 empty] | 10000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.098 | [19 empty] | 100 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.7285 | [19 empty] | 133.3521 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9823 | [19 empty] | 177.8279 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9883 | [19 empty] | 237.1374 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.038 | [19 empty] | 316.2278 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0713 | [19 empty] | 421.6965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2003 | [19 empty] | 562.3413 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7784 | [19 empty] | 749.8942 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7497 | [19 empty] | 1000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.441 | [19 empty] | 1333.5214 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4968 | [19 empty] | 1778.2794 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5701 | [19 empty] | 2371.3737 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3135 | [19 empty] | 3162.2777 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.3223 | [19 empty] | 4216.965 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.053 | [19 empty] | 5623.4133 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.9165 | [19 empty] | 7498.9421 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.2677 | [19 empty] | 10000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.4486 | [19 empty] | 13335.2143 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8374 | [19 empty] | 17782.7941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.6763 | [19 empty] | 23713.7371 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8307 | [19 empty] | 31622.7766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.4458 | [19 empty] | 42169.6503 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.1296 | [19 empty] | 56234.1325 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.0876 | [19 empty] | 74989.4209 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9187 | [19 empty] | 100000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8822 | [19 empty] | 133352.1432 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.992 | [19 empty] | 177827.941 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.152 | [19 empty] | 237137.3706 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3972 | [19 empty] | 316227.766 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6815 | [19 empty] | 421696.5034 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3614 | [19 empty] | 562341.3252 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5548 | [19 empty] | 749894.2093 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2209 | [19 empty] | 1000000 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6797 | [19 empty] | 1333521.4322 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.265 | [19 empty] | 1778279.41 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.7853 | [19 empty] | 2371373.7057 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.228 | [19 empty] | 3162277.6602 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2486 | [19 empty] | 4216965.0343 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9619 | [19 empty] | 5623413.2519 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8125 | [19 empty] | 7498942.0933 | 0
1 | 1100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.0836 | [19 empty] | 10000000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.6261 | [19 empty] | 100 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.4811 | [19 empty] | 133.3521 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4165 | [19 empty] | 177.8279 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6386 | [19 empty] | 237.1374 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.4048 | [19 empty] | 316.2278 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4248 | [19 empty] | 421.6965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5906 | [19 empty] | 562.3413 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0782 | [19 empty] | 749.8942 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.882 | [19 empty] | 1000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5094 | [19 empty] | 1333.5214 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0238 | [19 empty] | 1778.2794 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9331 | [19 empty] | 2371.3737 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.3218 | [19 empty] | 3162.2777 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.6646 | [19 empty] | 4216.965 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.8569 | [19 empty] | 5623.4133 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.04 | [19 empty] | 7498.9421 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.4622 | [19 empty] | 10000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.9865 | [19 empty] | 13335.2143 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.6552 | [19 empty] | 17782.7941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.0379 | [19 empty] | 23713.7371 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.0907 | [19 empty] | 31622.7766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2322 | [19 empty] | 42169.6503 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6144 | [19 empty] | 56234.1325 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8378 | [19 empty] | 74989.4209 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8895 | [19 empty] | 100000 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6822 | [19 empty] | 133352.1432 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.0741 | [19 empty] | 177827.941 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.2937 | [19 empty] | 237137.3706 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2622 | [19 empty] | 316227.766 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.3471 | [19 empty] | 421696.5034 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.2304 | [19 empty] | 562341.3252 | 0
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8 | 0.16663 | 4.3161e-05 | 4 | 30844960.2166 | 73942133.2789 | 628816.2349 | 1507410.401 | 43.9594 | 0 | 29.6586 | 43798.3338 | 1956.9651 | 86636.3421 | 97115.8304 | 0 | 7848.2325 | 0 | 92568.7245 | 240844.8326 | 164381.5471 | 735150.8081 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5325201.7641 | 12765676.3314 | 749894.2093 | 0.00017264 | 30844960.2166 | 73942133.2789 | 628816.2349 | 1507410.401
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4009 | 0.18459 | 0.00010938 | 4 | 12247494.9602 | 29253528.3329 | 249681.7507 | 596372.7434 | 44.0184 | 0 | 76.5569 | 47082.0594 | 2107.8283 | 94026.9179 | 104896.3379 | 0 | 0 | 0 | 96764.126 | 251760.4068 | 171831.6508 | 768469.3272 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5358520.2832 | 12798994.8505 | 1000000 | 0.00043752 | 12247494.9602 | 29253528.3329 | 249681.7507 | 596372.7434
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0405 | 0.23343 | 0.00017506 | 4 | 7871062.5041 | 18496838.7391 | 160462.2555 | 377083.0765 | 44.1238 | 0 | 70.6533 | 55517.7024 | 2495.8106 | 113438.3574 | 126067.7498 | 0 | 0 | 0 | 116032.6519 | 301893.1586 | 206048.284 | 921493.7146 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5511544.6706 | 12952019.2379 | 1333521.4322 | 0.00070023 | 7871062.5041 | 18496838.7391 | 160462.2555 | 377083.0765
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0091 | 0.29266 | 0.00026874 | 4 | 5294727.4073 | 12216467.6334 | 107940.1798 | 249049.2167 | 44.2366 | 0 | 74.2368 | 65110.4681 | 2938.3338 | 135917.177 | 151664.5563 | 0 | 0 | 0 | 138695.9087 | 360858.3041 | 246293.2074 | 1101477.9555 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5691528.9115 | 13132003.4788 | 1778279.41 | 0.0010749 | 5294727.4073 | 12216467.6334 | 107940.1798 | 249049.2167
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0749 | 0.35452 | 0.0003602 | 4 | 4077286.9457 | 9241465.2024 | 83121.0093 | 188399.7682 | 44.3022 | 0 | 83.0223 | 74461.0063 | 3370.0315 | 158439.7713 | 178434.0353 | 0 | 0 | 0 | 161734.8893 | 420801.0056 | 287205.3329 | 1284446.0723 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5874497.0283 | 13314971.5956 | 2371373.7057 | 0.0014408 | 4077286.9457 | 9241465.2024 | 83121.0093 | 188399.7682
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1749 | 0.4174 | 0.0004535 | 4 | 3338680.0074 | 7440347.7659 | 68063.5078 | 151681.553 | 44.3495 | 0 | 79.0677 | 83459.4143 | 3785.9205 | 180543.0037 | 205648.7313 | 0 | 0 | 0 | 184640.4572 | 480396.5947 | 327880.547 | 1466354.6686 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6056405.6246 | 13496880.1919 | 3162277.6602 | 0.001814 | 3338680.0074 | 7440347.7659 | 68063.5078 | 151681.553
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1303 | 0.47597 | 0.0005406 | 4 | 2877699.1263 | 6318528.4701 | 58665.7891 | 128811.7493 | 44.3826 | 0 | 82.9612 | 91467.3316 | 4156.3291 | 200531.812 | 230991.1277 | 0 | 0 | 0 | 205587.1741 | 534895.6554 | 365077.2758 | 1632706.7057 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6222757.6618 | 13663232.229 | 4216965.0343 | 0.0021624 | 2877699.1263 | 6318528.4701 | 58665.7891 | 128811.7493
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8943 | 0.5288 | 0.00061932 | 4 | 2571662.147 | 5575162.731 | 52426.8113 | 113657.2332 | 44.4063 | 0 | 95.0135 | 98433.8099 | 4478.7556 | 218144.9326 | 253853.2098 | 0 | 0 | 0 | 224215.1761 | 583361.8953 | 398156.4804 | 1780644.2597 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6370695.2157 | 13811169.783 | 5623413.2519 | 0.0024773 | 2571662.147 | 5575162.731 | 52426.8113 | 113657.2332
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4024 | 0.57397 | 0.00068671 | 4 | 2364828.6192 | 5073585.3246 | 48210.2301 | 103431.8994 | 44.4233 | 0 | 85.4589 | 104221.233 | 4746.7278 | 232924.9602 | 273398.677 | 0 | 0 | 0 | 239963.7232 | 624336.3844 | 426122.4112 | 1905714.1168 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6495765.0728 | 13936239.6401 | 7498942.0933 | 0.0027468 | 2364828.6192 | 5073585.3246 | 48210.2301 | 103431.8994
1 | 1200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6593 | 0.61162 | 0.00074293 | 4 | 2220626.3529 | 4724372.8782 | 45270.4718 | 96312.7313 | 44.4356 | 0 | 80.4569 | 108938.7539 | 4965.2292 | 245066.684 | 289689.5209 | 0 | 0 | 0 | 252977.4733 | 658195.4928 | 449231.9484 | 2009065.1027 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6599116.0587 | 14039590.626 | 10000000 | 0.0029717 | 2220626.3529 | 4724372.8782 | 45270.4718 | 96312.7313
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.3124 | [19 empty] | 100 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.3764 | [19 empty] | 133.3521 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.7441 | [19 empty] | 177.8279 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4934 | [19 empty] | 237.1374 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8612 | [19 empty] | 316.2278 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.9535 | [19 empty] | 421.6965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4854 | [19 empty] | 562.3413 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0637 | [19 empty] | 749.8942 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6843 | [19 empty] | 1000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9716 | [19 empty] | 1333.5214 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.9748 | [19 empty] | 1778.2794 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.0384 | [19 empty] | 2371.3737 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.6843 | [19 empty] | 3162.2777 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 35.2225 | [19 empty] | 4216.965 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.6902 | [19 empty] | 5623.4133 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.5716 | [19 empty] | 7498.9421 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.7304 | [19 empty] | 10000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.9056 | [19 empty] | 13335.2143 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.4842 | [19 empty] | 17782.7941 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6901 | [19 empty] | 23713.7371 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8443 | [19 empty] | 31622.7766 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7642 | [19 empty] | 42169.6503 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5457 | [19 empty] | 56234.1325 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.2222 | [19 empty] | 74989.4209 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6759 | [19 empty] | 100000 | 0
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.047212 | 3.5529e-05 | 4 | 36471054.0355 | 91549861.5471 | 743511.7673 | 1866367.758 | 44.3825 | 0 | 30.442 | 18825.1909 | 824.5956 | 31576.4528 | 44601.2228 | 0 | 6382.3985 | 0 | 39861.8456 | 103712.3455 | 70785.8069 | 316569.8586 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5183066.4153 | 13010564.8235 | 133352.1432 | 0.00014211 | 36471054.0355 | 91549861.5471 | 743511.7673 | 1866367.758
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.1065 | 0.00014047 | 4 | 9641425.4977 | 23572387.6759 | 196553.4998 | 480555.0068 | 45.7378 | 0 | 63.5712 | 34355.4792 | 1542.5131 | 60451.1997 | 69196.0694 | 0 | 12291.7778 | 0 | 69356.4453 | 180451.2437 | 123161.6817 | 550806.4099 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5417302.9666 | 13244801.3748 | 177827.941 | 0.00056188 | 9641425.4977 | 23572387.6759 | 196553.4998 | 480555.0068
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3944 | 0.14324 | 0.00025954 | 4 | 5340847.9729 | 12880759.1591 | 108880.41 | 262591.698 | 46.0542 | 0 | 65.0134 | 42520.2584 | 1922.5015 | 76602.1535 | 84405.9355 | 0 | 13472.7773 | 0 | 85380.2143 | 222141.8036 | 151616.3455 | 678061.9897 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5544558.5464 | 13372056.9546 | 237137.3706 | 0.0010381 | 5340847.9729 | 12880759.1591 | 108880.41 | 262591.698
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7313 | 0.18929 | 0.00041633 | 4 | 3420801.2982 | 8121064.5293 | 69737.6614 | 165558.885 | 46.2856 | 0 | 89.1597 | 51859.0972 | 2358.3124 | 95716.666 | 103460.6738 | 0 | 14672.7572 | 0 | 104546.3275 | 272008.0989 | 185651.1167 | 830273.0496 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5696769.6063 | 13524268.0145 | 316227.766 | 0.0016653 | 3420801.2982 | 8121064.5293 | 69737.6614 | 165558.885
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2272 | 0.24072 | 0.00061339 | 4 | 2388101.6422 | 5578374.961 | 48684.6821 | 113722.7189 | 46.4363 | 0 | 71.7343 | 61457.5763 | 2807.0603 | 115993.6127 | 124751.5592 | 0 | 15542.7944 | 0 | 125015.5151 | 325264.7261 | 221999.8591 | 992832.7031 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5859329.2598 | 13686827.668 | 421696.5034 | 0.0024536 | 2388101.6422 | 5578374.961 | 48684.6821 | 113722.7189
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5144 | 0.31972 | 0.00087708 | 4 | 1739230.5359 | 3970353.0344 | 35456.567 | 80941.0169 | 46.5953 | 0 | 91.1405 | 75077.418 | 3445.3636 | 145538.0967 | 157405.2613 | 0 | 17366.5419 | 0 | 155544.7458 | 404695.522 | 276213.0095 | 1235285.959 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6101782.5157 | 13929280.9238 | 562341.3252 | 0.0035083 | 1739230.5359 | 3970353.0344 | 35456.567 | 80941.0169
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6681 | 0.394 | 0.0011851 | 4 | 1333178.3721 | 2984402.636 | 27178.6444 | 60841.0844 | 46.6827 | 0 | 73.0164 | 86928.8602 | 4001.4636 | 171996.3293 | 188119.1803 | 0 | 18186.1284 | 0 | 183000.4651 | 476129.6716 | 324968.2843 | 1453330.3827 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6319826.9393 | 14147325.3475 | 749894.2093 | 0.0047404 | 1333178.3721 | 2984402.636 | 27178.6444 | 60841.0844
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1165 | 0.47844 | 0.00154 | 4 | 1065104.1703 | 2335793.1714 | 21713.5892 | 47618.3032 | 46.7498 | 0 | 75.7667 | 99586.9874 | 4596.0153 | 200890.1713 | 223035.061 | 0 | 19018.5909 | 0 | 213379.4621 | 555169.5903 | 378914.6529 | 1694590.5312 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6561087.0879 | 14388585.4961 | 1000000 | 0.00616 | 1065104.1703 | 2335793.1714 | 21713.5892 | 47618.3032
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6056 | 0.5643 | 0.0019263 | 4 | 882524.5916 | 1898400.2341 | 17991.4575 | 38701.4565 | 46.7979 | 0 | 77.6141 | 111765.6464 | 5168.496 | 229234.9988 | 258532.5957 | 0 | 19563.8463 | 0 | 243463.5774 | 633442.2873 | 432337.377 | 1933508.8249 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6800005.3816 | 14627503.7897 | 1333521.4322 | 0.0077052 | 882524.5916 | 1898400.2341 | 17991.4575 | 38701.4565
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.387 | 0.62575 | 0.002418 | 4 | 719690.8199 | 1528978.409 | 14671.8708 | 31170.293 | 46.8245 | 0 | 99.4047 | 120133.3124 | 5562.0349 | 248990.6654 | 283939.2326 | 0 | 17591.3478 | 0 | 263724.4713 | 686156.9771 | 468316.236 | 2094414.2776 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6960910.8343 | 14788409.2424 | 1778279.41 | 0.0096721 | 719690.8199 | 1528978.409 | 14671.8708 | 31170.293
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.4707 | 0.73214 | 0.0028535 | 4 | 635107.4369 | 1320876.8978 | 12947.5241 | 26927.8622 | 46.8603 | 0 | 76.6238 | 134048.6082 | 6216.7697 | 282305.3564 | 327921.0376 | 0 | 18814.3697 | 0 | 300029.3952 | 780614.9419 | 532785.7379 | 2382736.2165 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7249232.7732 | 15076731.1814 | 2371373.7057 | 0.011414 | 635107.4369 | 1320876.8978 | 12947.5241 | 26927.8622
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.3419 | 0.7967 | 0.0032186 | 4 | 576193.9309 | 1184175.8764 | 11746.4926 | 24141.027 | 46.8775 | 0 | 69.594 | 142190.5961 | 6599.9965 | 302045.9501 | 354611.5084 | 0 | 18425.472 | 0 | 321310.674 | 835984.4639 | 570576.5743 | 2551745.2353 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7418241.7919 | 15245740.2001 | 3162277.6602 | 0.012875 | 576193.9309 | 1184175.8764 | 11746.4926 | 24141.027
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8929 | 0.85021 | 0.0035379 | 4 | 533968.9145 | 1087089.697 | 10885.6786 | 22161.7939 | 46.8899 | 0 | 96.5532 | 148787.555 | 6910.5619 | 318166.0929 | 376733.7202 | 0 | 17905.0104 | 0 | 338716.1467 | 881269.9335 | 601484.8379 | 2689973.8585 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7556470.4152 | 15383968.8234 | 4216965.0343 | 0.014152 | 533968.9145 | 1087089.697 | 10885.6786 | 22161.7939
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1381 | 0.89318 | 0.0038069 | 4 | 503445.406 | 1017483.8373 | 10263.4156 | 20742.7843 | 46.8988 | 0 | 95.3593 | 153993.2868 | 7155.6653 | 330962.6225 | 394495.8833 | 0 | 17321.4317 | 0 | 352532.267 | 917216.6444 | 626019.2067 | 2799697.0078 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7666193.5645 | 15493691.9726 | 5623413.2519 | 0.015227 | 503445.406 | 1017483.8373 | 10263.4156 | 20742.7843
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.1197 | 0.92705 | 0.0040272 | 4 | 481215.119 | 967124.7274 | 9810.2211 | 19716.1457 | 46.9053 | 0 | 76.2855 | 158043.9035 | 7346.4001 | 340964.5254 | 408499.1805 | 0 | 16738.5825 | 0 | 363321.1109 | 945287.0031 | 645177.8033 | 2885378.5093 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7751875.066 | 15579373.4742 | 7498942.0933 | 0.016109 | 481215.119 | 967124.7274 | 9810.2211 | 19716.1457
1 | 1300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.8897 | 0.95362 | 0.0042042 | 4 | 464922.1581 | 930374.0903 | 9478.067 | 18966.9343 | 46.9101 | 0 | 84.1369 | 161189.5934 | 7494.5338 | 348758.3501 | 419482.4812 | 0 | 16207.4058 | 0 | 371721.6221 | 967143.4102 | 660095.2503 | 2952092.647 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7818589.2036 | 15646087.6118 | 10000000 | 0.016817 | 464922.1581 | 930374.0903 | 9478.067 | 18966.9343
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 11.8058 | [19 empty] | 100 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.8642 | [19 empty] | 133.3521 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.3909 | [19 empty] | 177.8279 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7667 | [19 empty] | 237.1374 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8561 | [19 empty] | 316.2278 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2738 | [19 empty] | 421.6965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7756 | [19 empty] | 562.3413 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7986 | [19 empty] | 749.8942 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2891 | [19 empty] | 1000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8601 | [19 empty] | 1333.5214 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2482 | [19 empty] | 1778.2794 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2678 | [19 empty] | 2371.3737 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.4538 | [19 empty] | 3162.2777 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.8996 | [19 empty] | 4216.965 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.4936 | [19 empty] | 5623.4133 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.0715 | [19 empty] | 7498.9421 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.4791 | [19 empty] | 10000 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5619 | [19 empty] | 13335.2143 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.7062 | [19 empty] | 17782.7941 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9457 | [19 empty] | 23713.7371 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.4131 | [19 empty] | 31622.7766 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1358 | [19 empty] | 42169.6503 | 0
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.053227 | 7.4965e-05 | 4 | 18359790.8149 | 45781540.5355 | 374289.1692 | 933318.6279 | 46.4147 | 0 | 32.061 | 21897.4035 | 975.2582 | 34685.1177 | 46346.8592 | 0 | 11226.9559 | 0 | 44901.3218 | 116824.0288 | 79734.8001 | 356591.7451 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5505393.9933 | 13728120.3696 | 56234.1325 | 0.00029986 | 18359790.8149 | 45781540.5355 | 374289.1692 | 933318.6279
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.053227 | 0.00013687 | 4 | 10046056.3227 | 25064898.4495 | 204802.4464 | 510981.8577 | 46.4147 | 0 | 31.3009 | 21897.4575 | 975.2608 | 34685.1709 | 46346.8886 | 0 | 9535.5928 | 0 | 44241.7446 | 115107.9441 | 78563.5371 | 351353.5964 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5500155.8446 | 13722882.2209 | 74989.4209 | 0.00054749 | 10046056.3227 | 25064898.4495 | 204802.4464 | 510981.8577
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4929 | 0.12712 | 0.00037608 | 4 | 3845002.8096 | 9311129.8539 | 78385.583 | 189819.9763 | 48.046 | 0 | 59.2215 | 41690.887 | 1906.4318 | 69490.1321 | 75700.5774 | 0 | 16315.49 | 0 | 79990.3721 | 208118.54 | 142045.18 | 635257.6105 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5784059.8587 | 14006786.235 | 100000 | 0.0015043 | 3845002.8096 | 9311129.8539 | 78385.583 | 189819.9763
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6307 | 0.17163 | 0.00060598 | 4 | 2448594.5119 | 5840927.1012 | 49917.9111 | 119075.1994 | 48.3989 | 0 | 76.1908 | 51743.7178 | 2382.5026 | 88321.2096 | 93344.9213 | 0 | 18104.5525 | 0 | 99019.7925 | 257629.1883 | 175837.2148 | 786383.0993 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5935185.3475 | 14157911.7238 | 133352.1432 | 0.0024239 | 2448594.5119 | 5840927.1012 | 49917.9111 | 119075.1994
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0332 | 0.22651 | 0.00090876 | 4 | 1681581.4471 | 3943656.1556 | 34281.3123 | 80396.7649 | 48.6513 | 0 | 89.316 | 63055.1344 | 2919.4238 | 110242.3048 | 115092.8595 | 0 | 19872.2093 | 0 | 121360.9534 | 315756.3063 | 215510.1672 | 963809.3587 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6112611.6069 | 14335337.9832 | 177827.941 | 0.003635 | 1681581.4471 | 3943656.1556 | 34281.3123 | 80396.7649
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6534 | 0.28973 | 0.0012906 | 4 | 1221873.1255 | 2814627.8901 | 24909.5364 | 57379.9966 | 48.8161 | 0 | 78.5187 | 75034.0802 | 3488.7977 | 134217.6747 | 140166.9516 | 0 | 21365.1794 | 0 | 145966.3467 | 379774.4922 | 259203.8945 | 1159217.4171 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6308019.6653 | 14530746.0416 | 237137.3706 | 0.0051626 | 1221873.1255 | 2814627.8901 | 24909.5364 | 57379.9966
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0675 | 0.38458 | 0.0018154 | 4 | 907751.9444 | 2040084.9109 | 18505.7512 | 41589.8903 | 48.9963 | 0 | 94.4431 | 91655.3227 | 4280.8119 | 168316.6427 | 177694.3301 | 0 | 23972.5744 | 0 | 181708.6759 | 472768.701 | 322674.3529 | 1443071.4114 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6591873.6596 | 14814600.0359 | 316227.766 | 0.0072618 | 907751.9444 | 2040084.9109 | 18505.7512 | 41589.8903
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6427 | 0.48554 | 0.002443 | 4 | 704170.0262 | 1545613.7965 | 14355.4584 | 31509.4278 | 49.1015 | 0 | 82.264 | 107952.562 | 5057.9376 | 202801.5197 | 217665.6902 | 0 | 25876.7491 | 0 | 218148.2389 | 567576.9693 | 387382.9441 | 1732462.6112 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6881264.8594 | 15103991.2357 | 421696.5034 | 0.0097722 | 704170.0262 | 1545613.7965 | 14355.4584 | 31509.4278
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5534 | 0.59966 | 0.003192 | 4 | 563750.0856 | 1207768.9876 | 11492.808 | 24622.0044 | 49.179 | 0 | 86.3478 | 125158.5117 | 5879.0845 | 240095.0781 | 262845.0027 | 0 | 27597.2132 | 0 | 258014.2072 | 671300.0412 | 458176.072 | 2049065.2108 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7197867.459 | 15420593.8353 | 562341.3252 | 0.012768 | 563750.0856 | 1207768.9876 | 11492.808 | 24622.0044
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6667 | 0.72175 | 0.0040432 | 4 | 465398.408 | 973822.1072 | 9487.776 | 19852.6808 | 49.2355 | 0 | 78.73 | 142482.5865 | 6706.3677 | 278446.4851 | 311173.7956 | 0 | 28992.5847 | 0 | 299442.7096 | 779088.5063 | 531743.9142 | 2378076.9497 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7526879.1979 | 15749605.5742 | 749894.2093 | 0.016173 | 465398.408 | 973822.1072 | 9487.776 | 19852.6808
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7996 | 0.84462 | 0.0049575 | 4 | 395849.6878 | 810507.721 | 8069.9313 | 16523.2962 | 49.2763 | 0 | 83.1727 | 159032.271 | 7496.9968 | 315749.8809 | 359810.1219 | 0 | 29958.1545 | 0 | 340098.4958 | 884866.5222 | 603939.5836 | 2700952.0267 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7849754.2749 | 16072480.6512 | 1000000 | 0.01983 | 395849.6878 | 810507.721 | 8069.9313 | 16523.2962
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7567 | 0.9606 | 0.0058816 | 4 | 346336.549 | 695848.6949 | 7060.539 | 14185.8169 | 49.3056 | 0 | 103.3526 | 173991.9583 | 8211.8584 | 349975.0055 | 405719.2157 | 0 | 30448.2723 | 0 | 377655.061 | 982581.001 | 670631.7232 | 2999214.0955 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8148016.3437 | 16370742.72 | 1333521.4322 | 0.023526 | 346336.549 | 695848.6949 | 7060.539 | 14185.8169
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4 | 1.0643 | 0.006763 | 4 | 310879.0944 | 614840.2726 | 6337.6908 | 12534.3506 | 49.3267 | 0 | 96.0943 | 186905.9826 | 8829.0695 | 379874.7169 | 446758.7617 | 0 | 30521.321 | 0 | 410627.0422 | 1068367.3325 | 729182.6572 | 3261066.8836 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8409869.1318 | 16632595.5081 | 1778279.41 | 0.027052 | 310879.0944 | 614840.2726 | 6337.6908 | 12534.3506
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.6756 | 1.1536 | 0.0075631 | 4 | 285335.861 | 557141.2877 | 5816.9575 | 11358.0787 | 49.3419 | 0 | 89.3262 | 197721.5423 | 9346.0392 | 405152.0708 | 482091.276 | 0 | 30314.5277 | 0 | 438603.9279 | 1141157.4503 | 778863.4082 | 3483250.2424 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8632052.4906 | 16854778.8669 | 2371373.7057 | 0.030252 | 285335.861 | 557141.2877 | 5816.9575 | 11358.0787
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.5561 | 1.2273 | 0.0082578 | 4 | 266822.5588 | 515761.0977 | 5439.5388 | 10514.4876 | 49.353 | 0 | 86.4584 | 206470.1784 | 9764.2376 | 425748.0339 | 511291.4148 | 0 | 29920.7833 | 0 | 461445.9128 | 1200587.6095 | 819425.7131 | 3664653.8834 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8813456.1316 | 17036182.5079 | 3162277.6602 | 0.033031 | 266822.5588 | 515761.0977 | 5439.5388 | 10514.4876
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.0519 | 1.286 | 0.0088387 | 4 | 253324.9091 | 485902.473 | 5164.3709 | 9905.7791 | 49.3609 | 0 | 67.786 | 213316.5996 | 10091.5185 | 441955.1604 | 534519.235 | 0 | 29413.5809 | 0 | 479425.4768 | 1247366.7469 | 851353.4356 | 3807441.7536 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8956244.0018 | 17178970.3781 | 4216965.0343 | 0.035355 | 253324.9091 | 485902.473 | 5164.3709 | 9905.7791
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.5379 | 1.2659 | 0.009341 | 4 | 237963.7734 | 458035.3673 | 4851.2134 | 9337.6705 | 49.3583 | 0 | 79.5009 | 210974.9033 | 9979.5771 | 436403.1228 | 526537.7764 | 0 | 24415.49 | 0 | 471241.2391 | 1226073.0393 | 836820.0426 | 3742445.1907 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8891247.4389 | 17113973.8152 | 5623413.2519 | 0.037364 | 237963.7734 | 458035.3673 | 4851.2134 | 9337.6705
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4607 | 1.3805 | 0.0099697 | 4 | 230203.1812 | 436395.6779 | 4693.0032 | 8896.5162 | 49.3724 | 0 | 90.7102 | 224148.1803 | 10609.3156 | 467750.1819 | 571926.3246 | 0 | 27184.759 | 0 | 507631.3169 | 1320752.5571 | 901440.759 | 4031443.3943 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9180245.6425 | 17402972.0188 | 7498942.0933 | 0.039879 | 230203.1812 | 436395.6779 | 4693.0032 | 8896.5162
1 | 1400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.177 | 1.4086 | 0.010275 | 4 | 224985.6563 | 425047.8053 | 4586.6369 | 8665.1744 | 49.3755 | 0 | 104.2117 | 227325.356 | 10761.2003 | 475351.2949 | 583049.0717 | 0 | 26718.1603 | 0 | 516049.9824 | 1342656.1979 | 916390.4439 | 4098301.7074 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9247103.9556 | 17469830.3319 | 10000000 | 0.041101 | 224985.6563 | 425047.8053 | 4586.6369 | 8665.1744
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.5134 | [19 empty] | 100 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.0607 | [19 empty] | 133.3521 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.3267 | [19 empty] | 177.8279 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.0708 | [19 empty] | 237.1374 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4162 | [19 empty] | 316.2278 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5037 | [19 empty] | 421.6965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4807 | [19 empty] | 562.3413 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5989 | [19 empty] | 749.8942 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7727 | [19 empty] | 1000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.705 | [19 empty] | 1333.5214 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0325 | [19 empty] | 1778.2794 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.1428 | [19 empty] | 2371.3737 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.3211 | [19 empty] | 3162.2777 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.0679 | [19 empty] | 4216.965 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.442 | [19 empty] | 5623.4133 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.7075 | [19 empty] | 7498.9421 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.1756 | [19 empty] | 10000 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8653 | [19 empty] | 13335.2143 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.5013 | [19 empty] | 17782.7941 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6699 | [19 empty] | 23713.7371 | 0
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.059356 | 0.00011951 | 4 | 12190771.852 | 30235858.1274 | 248525.3734 | 616398.865 | 48.4168 | 0 | 32.8059 | 25061.3327 | 1133.7661 | 37770.7267 | 48025.0331 | 0 | 14130.9238 | 0 | 49187.4951 | 127975.7725 | 87346.0944 | 390631.1442 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5827599.1748 | 14453757.6464 | 31622.7766 | 0.00047803 | 12190771.852 | 30235858.1274 | 248525.3734 | 616398.865
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.059356 | 0.00022544 | 4 | 6455995.703 | 16021979.0446 | 131614.2048 | 326629.7142 | 48.4169 | 0 | 32.6406 | 25061.4328 | 1133.7712 | 37770.8208 | 48025.0835 | 0 | 12231.3194 | 0 | 48446.7468 | 126048.4974 | 86030.6895 | 384748.3616 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5821716.3921 | 14447874.8638 | 42169.6503 | 0.00090175 | 6455995.703 | 16021979.0446 | 131614.2048 | 326629.7142
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1102 | 0.12537 | 0.00051861 | 4 | 2929071.4785 | 7087386.2488 | 59713.084 | 144485.9551 | 50.0763 | 0 | 65.546 | 43731.0579 | 2026.1226 | 68584.4789 | 73230.0569 | 0 | 18805.8702 | 0 | 80487.2587 | 209411.337 | 142927.5405 | 639203.7227 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6076171.7533 | 14702330.2249 | 56234.1325 | 0.0020744 | 2929071.4785 | 7087386.2488 | 59713.084 | 144485.9551
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.136 | 0.17045 | 0.00083265 | 4 | 1870696.313 | 4460657.1496 | 38136.6746 | 90936.5295 | 50.5307 | 0 | 80.3788 | 54621.3429 | 2549.6902 | 87650.5961 | 90386.5583 | 0 | 21018.272 | 0 | 99928.3192 | 259992.9885 | 177450.557 | 793598.3241 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6230566.3547 | 14856724.8264 | 74989.4209 | 0.0033306 | 1870696.313 | 4460657.1496 | 38136.6746 | 90936.5295
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4413 | 0.22786 | 0.0012519 | 4 | 1281557.0288 | 3004212.135 | 26126.2735 | 61244.9279 | 50.8651 | 0 | 81.3327 | 67244.9491 | 3158.0673 | 110532.1318 | 112224.2813 | 0 | 23379.4825 | 0 | 123450.1757 | 321192.0341 | 219220.1631 | 980401.2851 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6417369.3157 | 15043527.7873 | 100000 | 0.0050075 | 1281557.0288 | 3004212.135 | 26126.2735 | 61244.9279
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0271 | 0.29757 | 0.0017958 | 4 | 923472.2266 | 2124348.4308 | 18826.2304 | 43307.7162 | 51.0979 | 0 | 82.8555 | 81268.7347 | 3834.9362 | 136812.1469 | 138736.5572 | 0 | 25669.4055 | 0 | 150665.4944 | 392000.7106 | 267548.5398 | 1196536.5252 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6633504.5558 | 15259663.0274 | 133352.1432 | 0.0071832 | 923472.2266 | 2124348.4308 | 18826.2304 | 43307.7162
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4024 | 0.40243 | 0.002534 | 4 | 685356.7623 | 1536395.6623 | 13971.9246 | 31321.5037 | 51.32 | 0 | 94.3489 | 100604.332 | 4770.0025 | 174143.2819 | 178551.4156 | 0 | 29405.0348 | 0 | 190114.886 | 494639.9355 | 337601.9198 | 1509830.808 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6946798.8386 | 15572957.3102 | 177827.941 | 0.010136 | 685356.7623 | 1536395.6623 | 13971.9246 | 31321.5037
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7607 | 0.50645 | 0.0034445 | 4 | 525630.6509 | 1151709.8166 | 10715.6918 | 23479.1624 | 51.4483 | 0 | 77.7896 | 118271.8061 | 5625.1857 | 209285.087 | 218060.8651 | 0 | 31597.425 | 0 | 227307.7439 | 591408.1223 | 403648.1957 | 1805204.4307 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7242172.4613 | 15868330.9329 | 237137.3706 | 0.013778 | 525630.6509 | 1151709.8166 | 10715.6918 | 23479.1624
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7567 | 0.6386 | 0.0045814 | 4 | 415047.9088 | 885769.0883 | 8461.313 | 18057.601 | 51.5516 | 0 | 99.0989 | 139168.4682 | 6637.3697 | 251909.5286 | 268246.6065 | 0 | 34321.3184 | 0 | 273110.4836 | 710577.4558 | 484983.7145 | 2168954.9453 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7605922.9758 | 16232081.4475 | 316227.766 | 0.018325 | 415047.9088 | 885769.0883 | 8461.313 | 18057.601
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1527 | 0.7884 | 0.00594 | 4 | 336907.9014 | 699959.9608 | 6868.3233 | 14269.6306 | 51.628 | 0 | 96.9405 | 161309.6568 | 7710.3948 | 298146.5079 | 325136.0124 | 0 | 36819.8011 | 0 | 323357.7255 | 841310.4719 | 574211.6843 | 2568002.2547 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8004970.2853 | 16631128.7569 | 421696.5034 | 0.02376 | 336907.9014 | 699959.9608 | 6868.3233 | 14269.6306
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7802 | 0.94844 | 0.0074863 | 4 | 281141.2874 | 569204.4258 | 5731.4454 | 11604.0021 | 51.6837 | 0 | 80.9401 | 183583.9684 | 8790.222 | 345634.3234 | 385908.0968 | 0 | 38843.76 | 0 | 375476.5445 | 976912.9481 | 666763.1606 | 2981913.0238 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8418881.0544 | 17045039.526 | 562341.3252 | 0.029945 | 281141.2874 | 569204.4258 | 5731.4454 | 11604.0021
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4607 | 1.1108 | 0.0091537 | 4 | 241114.2476 | 476706.2313 | 4915.4401 | 9718.3013 | 51.7244 | 0 | 92.737 | 205044.6792 | 9830.7907 | 392205.5729 | 447573.6984 | 0 | 40311.181 | 0 | 427036.7097 | 1111061.9214 | 758322.5914 | 3391387.1447 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8828355.1753 | 17454513.6469 | 749894.2093 | 0.036615 | 241114.2476 | 476706.2313 | 4915.4401 | 9718.3013
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.9445 | 1.2646 | 0.010844 | 4 | 212277.7537 | 411153.5791 | 4327.5691 | 8381.9218 | 51.7537 | 0 | 69.983 | 224498.8287 | 10774.1376 | 435048.0128 | 505947.0325 | 0 | 41098.7732 | 0 | 474773.0461 | 1235262.0766 | 843091.7494 | 3770493.657 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9207461.6876 | 17833620.1592 | 1000000 | 0.043375 | 212277.7537 | 411153.5791 | 4327.5691 | 8381.9218
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.0897 | 1.4034 | 0.012463 | 4 | 191433.1951 | 364464.7751 | 3902.6246 | 7430.1074 | 51.775 | 0 | 86.1095 | 241457.8516 | 11596.5037 | 472841.0053 | 558650.9679 | 0 | 41327.5891 | 0 | 517090.8278 | 1345364.2641 | 918238.7547 | 4106567.7641 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9543535.7947 | 18169694.2663 | 1333521.4322 | 0.049853 | 191433.1951 | 364464.7751 | 3902.6246 | 7430.1074
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.7808 | 1.5222 | 0.013934 | 4 | 176307.8371 | 331076.5311 | 3594.2737 | 6749.4429 | 51.7903 | 0 | 108.8386 | 255572.0718 | 12280.906 | 504589.6624 | 603749.5227 | 0 | 41093.1449 | 0 | 552741.27 | 1438119.4017 | 981546.042 | 4389692.0214 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9826660.0519 | 18452818.5236 | 1778279.41 | 0.055736 | 176307.8371 | 331076.5311 | 3594.2737 | 6749.4429
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0271 | 1.6213 | 0.015216 | 4 | 165284.734 | 307009.6122 | 3369.5529 | 6258.8062 | 51.8015 | 0 | 92.9546 | 267102.1608 | 12839.9818 | 530714.2274 | 641396.009 | 0 | 40616.2651 | 0 | 582140.7712 | 1514610.8732 | 1033753.0431 | 4623173.3315 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10060141.3621 | 18686299.8337 | 2371373.7057 | 0.060866 | 165284.734 | 307009.6122 | 3369.5529 | 6258.8062
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.8371 | 1.7012 | 0.016294 | 4 | 157214.735 | 289570.1782 | 3205.035 | 5903.2798 | 51.8097 | 0 | 94.8712 | 276239.3852 | 13283.0124 | 551532.8043 | 671730.4287 | 0 | 40001.195 | 0 | 605586.862 | 1575612.7919 | 1075388.1061 | 4809374.5855 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10246342.6161 | 18872501.0877 | 3162277.6602 | 0.065174 | 157214.735 | 289570.1782 | 3205.035 | 5903.2798
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.2675 | 1.7644 | 0.017174 | 4 | 151280.8813 | 276852.1225 | 3084.0654 | 5644.005 | 51.8156 | 0 | 83.3066 | 283369.9466 | 13628.733 | 567848.2731 | 695704.6052 | 0 | 39357.0774 | 0 | 623964.3677 | 1623427.2922 | 1108022.485 | 4955322.7802 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10392290.8107 | 19018449.2824 | 4216965.0343 | 0.068695 | 151280.8813 | 276852.1225 | 3084.0654 | 5644.005
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.3781 | 1.8134 | 0.017877 | 4 | 146900.6038 | 267529.6407 | 2994.7675 | 5453.9536 | 51.8199 | 0 | 92.9927 | 288853.4058 | 13894.5851 | 580435.2013 | 714318.1843 | 0 | 38743.3815 | 0 | 638135.4556 | 1660297.5559 | 1133187.1976 | 5067864.9672 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10504832.9978 | 19130991.4694 | 5623413.2519 | 0.07151 | 146900.6038 | 267529.6407 | 2994.7675 | 5453.9536
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.2398 | 1.8515 | 0.018432 | 4 | 143656.3202 | 260653.2987 | 2928.6284 | 5313.7701 | 51.8232 | 0 | 112.3251 | 293077.5639 | 14099.3768 | 590154.9289 | 728761.0184 | 0 | 38212.9181 | 0 | 649079.2644 | 1688771.1015 | 1152620.9775 | 5154777.1495 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10591745.18 | 19217903.6517 | 7498942.0933 | 0.07373 | 143656.3202 | 260653.2987 | 2928.6284 | 5313.7701
1 | 1500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.8808 | 1.8798 | 0.018861 | 4 | 141246.7781 | 255587.7945 | 2879.5066 | 5210.5029 | 51.8255 | 0 | 92.1862 | 296203.0372 | 14250.8993 | 597359.5744 | 739505.1024 | 0 | 37730.7348 | 0 | 657169.2457 | 1709819.5735 | 1166986.9922 | 5219025.1594 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10655993.19 | 19282151.6616 | 10000000 | 0.075442 | 141246.7781 | 255587.7945 | 2879.5066 | 5210.5029
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 15.9394 | [19 empty] | 100 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.8855 | [19 empty] | 133.3521 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.8237 | [19 empty] | 177.8279 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6437 | [19 empty] | 237.1374 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.682 | [19 empty] | 316.2278 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2335 | [19 empty] | 421.6965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3059 | [19 empty] | 562.3413 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4544 | [19 empty] | 749.8942 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4957 | [19 empty] | 1000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1462 | [19 empty] | 1333.5214 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.3786 | [19 empty] | 1778.2794 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.6557 | [19 empty] | 2371.3737 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.072 | [19 empty] | 3162.2777 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.59 | [19 empty] | 4216.965 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.1817 | [19 empty] | 5623.4133 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.5297 | [19 empty] | 7498.9421 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2667 | [19 empty] | 10000 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8164 | [19 empty] | 13335.2143 | 0
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065487 | 6.9613e-05 | 4 | 22114747.9365 | 54571852.1014 | 450839.0491 | 1112521.019 | 50.3894 | 0 | 32.0916 | 28293.7859 | 1299.2547 | 40782.1209 | 49615.2863 | 0 | 17852.7563 | 0 | 53758.8496 | 139869.4992 | 95463.8073 | 426935.3602 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6157929.264 | 15195723.9582 | 17782.7941 | 0.00027845 | 22114747.9365 | 54571852.1014 | 450839.0491 | 1112521.019
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065487 | 0.00025158 | 4 | 6112111.6172 | 15093095.5077 | 124603.6626 | 307693.1668 | 50.3895 | 0 | 30.9408 | 28293.9724 | 1299.2644 | 40782.2931 | 49615.376 | 0 | 15542.38 | 0 | 52857.9815 | 137525.6252 | 93864.065 | 419780.9576 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6150774.8614 | 15188569.5555 | 23713.7371 | 0.0010063 | 6112111.6172 | 15093095.5077 | 124603.6626 | 307693.1668
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065488 | 0.00038805 | 4 | 3958432.6793 | 9781058.5322 | 80698.0043 | 199400.108 | 50.3896 | 0 | 32.0899 | 28294.1122 | 1299.2716 | 40782.4223 | 49615.4432 | 0 | 13426.1142 | 0 | 52032.7718 | 135378.5988 | 92398.6755 | 413227.4097 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6144221.3135 | 15182016.0077 | 31622.7766 | 0.0015522 | 3958432.6793 | 9781058.5322 | 80698.0043 | 199400.108
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.15322 | 0.00087997 | 4 | 1839874.8538 | 4407504.4102 | 37508.3375 | 89852.939 | 52.4395 | 0 | 57.2606 | 53236.8236 | 2511.377 | 80342.4871 | 81815.1379 | 0 | 22687.4248 | 0 | 93831.3677 | 244129.9713 | 166623.7218 | 745178.3112 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6476172.215 | 15513966.9092 | 42169.6503 | 0.0035199 | 1839874.8538 | 4407504.4102 | 37508.3375 | 89852.939
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5038 | 0.2071 | 0.0013627 | 4 | 1221011.6202 | 2879033.5093 | 24891.9734 | 58692.9923 | 52.907 | 0 | 85.8418 | 66210.8556 | 3145.7763 | 102198.9513 | 101546.8578 | 0 | 25445.7928 | 0 | 116433.8112 | 302936.8929 | 206760.6541 | 924679.592 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6655673.4958 | 15693468.19 | 56234.1325 | 0.005451 | 1221011.6202 | 2879033.5093 | 24891.9734 | 58692.9923
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9017 | 0.2755 | 0.0020035 | 4 | 857499.5664 | 1985239.2667 | 17481.2885 | 40471.7877 | 53.2505 | 0 | 84.9527 | 81212.5965 | 3880.618 | 128367.2534 | 126568.0055 | 0 | 28386.6584 | 0 | 143681.9014 | 373830.8341 | 255147.2258 | 1141075.093 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6872068.9968 | 15909863.691 | 74989.4209 | 0.0080141 | 857499.5664 | 1985239.2667 | 17481.2885 | 40471.7877
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5607 | 0.35652 | 0.0028274 | 4 | 629223.9508 | 1428361.4005 | 12827.5813 | 29119.0792 | 53.4804 | 0 | 78.7922 | 97502.2454 | 4679.2611 | 157733.2038 | 156219.1365 | 0 | 31092.9376 | 0 | 174418.4459 | 453801.0181 | 309728.5195 | 1385174.7678 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7116168.6717 | 16153963.3658 | 100000 | 0.011309 | 629223.9508 | 1428361.4005 | 12827.5813 | 29119.0792
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9749 | 0.47519 | 0.0039583 | 4 | 471234.6832 | 1042054.5488 | 9606.7564 | 21243.6915 | 53.7161 | 0 | 96.2934 | 119515.4145 | 5760.8645 | 198452.3891 | 199545.1256 | 0 | 35307.5061 | 0 | 217846.7069 | 566792.4449 | 386847.4901 | 1730067.9417 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7461061.8455 | 16498856.5397 | 133352.1432 | 0.015833 | 471234.6832 | 1042054.5488 | 9606.7564 | 21243.6915
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7398 | 0.61078 | 0.005369 | 4 | 364948.2572 | 785784.2578 | 7439.9639 | 16019.2749 | 53.8633 | 0 | 79.4619 | 142622.5254 | 6896.5793 | 242553.1259 | 249084.9629 | 0 | 38982.8306 | 0 | 265254.6094 | 690138.0825 | 471033.4223 | 2106566.1384 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7837560.0422 | 16875354.7364 | 177827.941 | 0.021476 | 364948.2572 | 785784.2578 | 7439.9639 | 16019.2749
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0138 | 0.77136 | 0.0071256 | 4 | 290052.0707 | 607142.5338 | 5913.1038 | 12377.4218 | 53.9726 | 0 | 90.0306 | 168032.8692 | 8146.1194 | 292319.8294 | 307749.6169 | 0 | 42588.4563 | 0 | 319346.3876 | 830873.7935 | 567088.4368 | 2536145.5092 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8267139.413 | 17304934.1071 | 237137.3706 | 0.028502 | 290052.0707 | 607142.5338 | 5913.1038 | 12377.4218
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.7534 | 0.95481 | 0.0092399 | 4 | 236519.7807 | 481051.9867 | 4821.7756 | 9806.8954 | 54.0537 | 0 | 78.675 | 195154.1003 | 9480.145 | 346701.8733 | 374765.9358 | 0 | 45941.4817 | 0 | 379096.9791 | 986332.576 | 673192.2502 | 3010665.3414 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8741659.2452 | 17779453.9394 | 316227.766 | 0.03696 | 236519.7807 | 481051.9867 | 4821.7756 | 9806.8954
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.8265 | 1.1547 | 0.011675 | 4 | 197929.3265 | 391459.1624 | 4035.057 | 7980.4245 | 54.1136 | 0 | 85.2343 | 222949.2836 | 10847.4668 | 403612.2778 | 447767.9741 | 0 | 48813.4124 | 0 | 442256.2617 | 1150660.0738 | 785349.1441 | 3512255.8944 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9243249.7982 | 18281044.4923 | 421696.5034 | 0.0467 | 197929.3265 | 391459.1624 | 4035.057 | 7980.4245
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.9628 | 1.3577 | 0.014323 | 4 | 169985.068 | 327730.0545 | 3465.3755 | 6681.2204 | 54.1571 | 0 | 82.5707 | 249722.5776 | 12164.5107 | 459424.3341 | 521909.8859 | 0 | 50854.322 | 0 | 504689.4959 | 1313098.5422 | 896216.7365 | 4008080.4049 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9739074.3087 | 18776869.0029 | 562341.3252 | 0.057294 | 169985.068 | 327730.0545 | 3465.3755 | 6681.2204
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.9823 | 1.555 | 0.017051 | 4 | 149702.4595 | 282215.6171 | 3051.8871 | 5753.3471 | 54.189 | 0 | 104.6286 | 274605.9611 | 13388.4861 | 512082.3526 | 593961.9669 | 0 | 52133.6477 | 0 | 564007.2416 | 1467431.1489 | 1001551.9119 | 4479162.7169 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10210156.6207 | 19247951.3149 | 749894.2093 | 0.068203 | 149702.4595 | 282215.6171 | 3051.8871 | 5753.3471
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.6265 | 1.7338 | 0.01969 | 4 | 134953.0324 | 249704.157 | 2751.2001 | 5090.557 | 54.2121 | 0 | 83.3629 | 296358.9908 | 14458.3564 | 558683.2548 | 659294.6411 | 0 | 52574.2505 | 0 | 616734.1025 | 1604615.6252 | 1095183.1358 | 4897902.3571 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10628896.2609 | 19666690.9551 | 1000000 | 0.07876 | 134953.0324 | 249704.157 | 2751.2001 | 5090.557
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.7936 | 1.8893 | 0.022115 | 4 | 124201.8213 | 226369.6148 | 2532.0221 | 4614.8508 | 54.2288 | 0 | 87.0094 | 314722.9557 | 15361.4243 | 598407.5716 | 716075.7513 | 0 | 52399.4799 | 0 | 661817.2012 | 1721912.6002 | 1175240.7314 | 5255937.7156 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10986931.6194 | 20024726.3135 | 1333521.4322 | 0.08846 | 124201.8213 | 226369.6148 | 2532.0221 | 4614.8508
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.4318 | 2.0189 | 0.024242 | 4 | 116340.7794 | 209546.3481 | 2371.7641 | 4271.8857 | 54.2408 | 0 | 83.9668 | 329677.5609 | 16096.7375 | 631002.7078 | 763377.7631 | 0 | 51799.0651 | 0 | 698861.9954 | 1818295.5558 | 1241024.079 | 5550135.4646 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11281129.3684 | 20318924.0626 | 1778279.41 | 0.096966 | 116340.7794 | 209546.3481 | 2371.7641 | 4271.8857
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5823 | 2.1245 | 0.026043 | 4 | 110572.4483 | 197332.2217 | 2254.1689 | 4022.8843 | 54.2496 | 0 | 125.0713 | 341655.4579 | 16685.6167 | 657262.701 | 801934.4483 | 0 | 51012.3933 | 0 | 728734.7407 | 1896018.3112 | 1294071.4567 | 5787375.1258 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11518369.0296 | 20556163.7238 | 2371373.7057 | 0.10417 | 110572.4483 | 197332.2217 | 2254.1689 | 4022.8843
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.2903 | 2.2083 | 0.027522 | 4 | 106324.2247 | 188419.5834 | 2167.5631 | 3841.1881 | 54.256 | 0 | 103.7568 | 351042.3252 | 17147.0628 | 677934.5299 | 832559.2612 | 0 | 50165.0289 | 0 | 752250.8011 | 1957202.2767 | 1335830.7703 | 5974132.0562 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11705125.96 | 20742920.6542 | 3162277.6602 | 0.11009 | 106324.2247 | 188419.5834 | 2167.5631 | 3841.1881
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.623 | 2.2737 | 0.02871 | 4 | 103184.776 | 181883.5982 | 2103.5612 | 3707.9432 | 54.2606 | 0 | 97.0985 | 358291.6122 | 17503.3971 | 693953.3394 | 856452.4583 | 0 | 49347.6435 | 0 | 770463.8957 | 2004589.0127 | 1368173.1914 | 6118774.5503 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11849768.4541 | 20887563.1482 | 4216965.0343 | 0.11484 | 103184.776 | 181883.5982 | 2103.5612 | 3707.9432
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.6534 | 2.3243 | 0.029648 | 4 | 100857.7127 | 177066.5621 | 2056.1209 | 3609.7414 | 54.264 | 0 | 92.9883 | 363853.3028 | 17776.7591 | 706274.6996 | 874925.1162 | 0 | 48619.8967 | 0 | 784465.412 | 2041018.0861 | 1393036.7825 | 6229970.0551 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11960963.9589 | 20998758.6531 | 5623413.2519 | 0.11859 | 100857.7127 | 177066.5621 | 2056.1209 | 3609.7414
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.4427 | 2.3631 | 0.030379 | 4 | 99128.4453 | 173503.3291 | 2020.8674 | 3537.1 | 54.2664 | 0 | 99.3425 | 368089.5413 | 17984.9621 | 715677.8925 | 889077.3177 | 0 | 48000.208 | 0 | 795143.6695 | 2068800.7216 | 1411999.0021 | 6314773.3148 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12045767.2186 | 21083561.9128 | 7498942.0933 | 0.12152 | 99128.4453 | 173503.3291 | 2020.8674 | 3537.1
1 | 1600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.0345 | 2.3921 | 0.030941 | 4 | 97840.7591 | 170865.9919 | 1994.6162 | 3483.3344 | 54.2682 | 0 | 94.0242 | 371251.4944 | 18140.3591 | 722706.6884 | 899686.5176 | 0 | 47470.1237 | 0 | 803109.5215 | 2089526.2344 | 1426144.5905 | 6378035.5296 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12109029.4334 | 21146824.1275 | 10000000 | 0.12376 | 97840.7591 | 170865.9919 | 1994.6162 | 3483.3344
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.3169 | [19 empty] | 100 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.8176 | [19 empty] | 133.3521 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0735 | [19 empty] | 177.8279 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1978 | [19 empty] | 237.1374 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4125 | [19 empty] | 316.2278 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6081 | [19 empty] | 421.6965 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1184 | [19 empty] | 562.3413 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1359 | [19 empty] | 749.8942 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0295 | [19 empty] | 1000 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6065 | [19 empty] | 1333.5214 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.084 | [19 empty] | 1778.2794 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.4825 | [19 empty] | 2371.3737 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.58 | [19 empty] | 3162.2777 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.4434 | [19 empty] | 4216.965 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.2227 | [19 empty] | 5623.4133 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.0314 | [19 empty] | 7498.9421 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.6678 | [19 empty] | 10000 | 0
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071762 | 0.00014335 | 4 | 11316723.2507 | 27811205.0856 | 230706.7105 | 566969.0331 | 52.333 | 0 | 35.1328 | 31603.6988 | 1471.9313 | 43797.7254 | 51164.8187 | 0 | 19809.8548 | 0 | 57660.7313 | 150021.395 | 102392.6848 | 457922.8401 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6488802.7081 | 15946437.752 | 13335.2143 | 0.00057338 | 11316723.2507 | 27811205.0856 | 230706.7105 | 566969.0331
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071762 | 0.00037804 | 4 | 4285733.1314 | 10540120.4826 | 87370.4668 | 214874.6126 | 52.3331 | 0 | 31.7082 | 31603.9552 | 1471.9449 | 43797.9487 | 51164.932 | 0 | 17197.89 | 0 | 56642.3016 | 147371.6497 | 100584.1791 | 449834.8011 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6480714.669 | 15938349.7129 | 17782.7941 | 0.0015122 | 4285733.1314 | 10540120.4826 | 87370.4668 | 214874.6126
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071762 | 0.00055405 | 4 | 2920952.7204 | 7188468.4192 | 59547.5721 | 146546.6518 | 52.3332 | 0 | 31.7784 | 31604.1475 | 1471.955 | 43798.1162 | 51165.0169 | 0 | 14833.4029 | 0 | 55720.3291 | 144972.8664 | 98946.9602 | 442512.7943 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6473392.6622 | 15931027.7061 | 23713.7371 | 0.0022162 | 2920952.7204 | 7188468.4192 | 59547.5721 | 146546.6518
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4929 | 0.17346 | 0.0012485 | 4 | 1372436.6234 | 3266260.0491 | 27978.9769 | 66587.129 | 54.6871 | 0 | 59.3621 | 61016.5304 | 2924.2623 | 88538.2414 | 87153.6317 | 0 | 26080.8964 | 0 | 103628.2893 | 269619.5516 | 184020.8841 | 822982.2871 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6853862.155 | 16311497.1989 | 31622.7766 | 0.0049939 | 1372436.6234 | 3266260.0491 | 27978.9769 | 66587.129
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6307 | 0.23491 | 0.001908 | 4 | 924420.3597 | 2163638.3492 | 18845.5594 | 44108.6943 | 55.2008 | 0 | 71.9257 | 75986.9527 | 3667.6734 | 112789.0346 | 108822.0632 | 0 | 29426.9703 | 0 | 128970.1507 | 335553.8768 | 229022.4159 | 1024239.1376 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7055119.0055 | 16512754.0494 | 42169.6503 | 0.0076319 | 924420.3597 | 2163638.3492 | 18845.5594 | 44108.6943
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0481 | 0.31139 | 0.0027838 | 4 | 654935.1682 | 1504280.0133 | 13351.7393 | 30666.7828 | 55.5724 | 0 | 74.5909 | 92999.9302 | 4514.0992 | 141267.9802 | 135792.3472 | 0 | 32871.187 | 0 | 158903.7621 | 413434.9934 | 282177.8782 | 1261962.1775 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7292842.0454 | 16750477.0893 | 56234.1325 | 0.011135 | 654935.1682 | 1504280.0133 | 13351.7393 | 30666.7828
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7628 | 0.40367 | 0.0039113 | 4 | 483605.9926 | 1088114.3898 | 9858.9623 | 22182.6836 | 55.8235 | 0 | 99.5722 | 111821.0083 | 5451.0082 | 173824.7219 | 168356.9117 | 0 | 36216.7147 | 0 | 193311.4423 | 502956.7193 | 343278.2956 | 1535216.8221 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7566096.69 | 17023731.7339 | 74989.4209 | 0.015645 | 483605.9926 | 1088114.3898 | 9858.9623 | 22182.6836
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2675 | 0.53953 | 0.0054708 | 4 | 363472.7564 | 795662.6954 | 7409.8838 | 16220.6603 | 56.0884 | 0 | 71.6345 | 137390.7036 | 6726.7004 | 219177.3364 | 216158.1663 | 0 | 41424.0779 | 0 | 242142.024 | 630003.8762 | 429990.5908 | 1923013.4756 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7953893.3435 | 17411528.3874 | 100000 | 0.021883 | 363472.7564 | 795662.6954 | 7409.8838 | 16220.6603
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1297 | 0.69439 | 0.007418 | 4 | 282270.3751 | 601011.8859 | 5754.4634 | 12252.4402 | 56.2504 | 0 | 74.1371 | 164140.4048 | 8061.1045 | 268162.3407 | 270689.6828 | 0 | 45936.7422 | 0 | 295226.2073 | 768118.0321 | 524256.3402 | 2344590.8546 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8375470.7226 | 17833105.7665 | 133352.1432 | 0.029672 | 282270.3751 | 601011.8859 | 5754.4634 | 12252.4402
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5667 | 0.88038 | 0.0098627 | 4 | 224657.6975 | 464390.225 | 4579.951 | 9467.2229 | 56.3718 | 0 | 81.6208 | 193953.3019 | 9548.7493 | 324191.7667 | 336177.5313 | 0 | 50500.4619 | 0 | 356605.0063 | 927813.0767 | 633251.4895 | 2832041.3836 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8862921.2515 | 18320556.2954 | 177827.941 | 0.039451 | 224657.6975 | 464390.225 | 4579.951 | 9467.2229
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5452 | 1.0957 | 0.012838 | 4 | 183202.9942 | 367374.4089 | 3734.8408 | 7489.4242 | 56.4622 | 0 | 69.4646 | 226159.6377 | 11155.9727 | 386175.3082 | 411988.5068 | 0 | 54849.2807 | 0 | 425228.1954 | 1106356.5381 | 755111.0706 | 3377024.5102 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9407904.3782 | 18865539.4221 | 237137.3706 | 0.051352 | 183202.9942 | 367374.4089 | 3734.8408 | 7489.4242
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9271 | 1.3329 | 0.01631 | 4 | 153122.5899 | 298092.3922 | 3121.6111 | 6077.0166 | 56.5291 | 0 | 90.519 | 259484.4212 | 12818.9108 | 451691.2594 | 495494.5369 | 0 | 58621.2878 | 0 | 498463.0623 | 1296898.6392 | 885159.9699 | 3958632.0875 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9989511.9554 | 19447146.9993 | 316227.766 | 0.065239 | 153122.5899 | 298092.3922 | 3121.6111 | 6077.0166
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5 | 1.5805 | 0.020159 | 4 | 131202.1763 | 248489.0009 | 2674.7338 | 5065.7844 | 56.5783 | 0 | 95.4249 | 292404.205 | 14461.3703 | 517622.6304 | 582646.6278 | 0 | 61535.5721 | 0 | 572781.4582 | 1490259.8606 | 1017132.9766 | 4548844.7011 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 10579724.569 | 20037359.6129 | 421696.5034 | 0.080637 | 131202.1763 | 248489.0009 | 2674.7338 | 5065.7844
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0038 | 1.8244 | 0.024191 | 4 | 115199.7077 | 212940.0381 | 2348.5019 | 4341.0707 | 56.6144 | 0 | 121.1956 | 323344.3775 | 16004.7198 | 580570.548 | 668490.9781 | 0 | 63431.7259 | 0 | 644218.5162 | 1676124.4318 | 1143989.3656 | 5116174.6629 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11147054.5309 | 20604689.5748 | 562341.3252 | 0.096763 | 115199.7077 | 212940.0381 | 2348.5019 | 4341.0707
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.1649 | 2.0497 | 0.028163 | 4 | 103507.0679 | 187461.9297 | 2110.1316 | 3821.665 | 56.6406 | 0 | 107.9689 | 350846.3865 | 17376.2337 | 637250.3534 | 747809.9877 | 0 | 64243.0931 | 0 | 708835.1612 | 1844243.6874 | 1258734.2121 | 5629339.115 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11660218.9829 | 21117854.0268 | 749894.2093 | 0.11265 | 103507.0679 | 187461.9297 | 2110.1316 | 3821.665
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8527 | 2.2494 | 0.031877 | 4 | 94953.4982 | 169127.3731 | 1935.7555 | 3447.8903 | 56.6596 | 0 | 111.0016 | 374472.5658 | 18554.1748 | 686449.5247 | 818110.0257 | 0 | 64244.571 | 0 | 765114.0362 | 1990669.7757 | 1358673.0261 | 6076287.7001 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12107167.568 | 21564802.6119 | 1000000 | 0.12751 | 94953.4982 | 169127.3731 | 1935.7555 | 3447.8903
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.9466 | 2.417 | 0.035171 | 4 | 88683.9833 | 155910.0196 | 1807.943 | 3178.4366 | 56.6732 | 0 | 101.275 | 393812.5141 | 19518.1945 | 727053.1116 | 877088.699 | 0 | 63579.9724 | 0 | 811610.4717 | 2111643.9631 | 1441240.3948 | 6445547.3211 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12476427.189 | 21934062.2329 | 1333521.4322 | 0.14068 | 88683.9833 | 155910.0196 | 1807.943 | 3178.4366
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4876 | 2.5546 | 0.03799 | 4 | 84076.27 | 146314.6774 | 1714.0085 | 2982.8226 | 56.6829 | 0 | 98.1124 | 409396.242 | 20294.8219 | 759978.3644 | 925525.882 | 0 | 62604.0778 | 0 | 849341.7614 | 2209813.0392 | 1508242.8064 | 6745196.9951 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12776076.863 | 22233711.9069 | 1778279.41 | 0.15196 | 84076.27 | 146314.6774 | 1714.0085 | 2982.8226
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.5144 | 2.6644 | 0.040322 | 4 | 80679.5482 | 139317.5892 | 1644.7617 | 2840.1775 | 56.6898 | 0 | 103.4161 | 421645.2695 | 20905.1533 | 785984.6184 | 964159.4926 | 0 | 61494.2551 | 0 | 879133.6277 | 2287325.3641 | 1561146.5608 | 6981794.3415 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13012674.2094 | 22470309.2533 | 2371373.7057 | 0.16129 | 80679.5482 | 139317.5892 | 1644.7617 | 2840.1775
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.1144 | 2.751 | 0.04221 | 4 | 78167.9254 | 134182.7013 | 1593.5589 | 2735.4959 | 56.6948 | 0 | 118.8865 | 431206.6328 | 21381.4956 | 806360.5324 | 994654.8447 | 0 | 60424.8271 | 0 | 902471.0497 | 2348044.5492 | 1602588.6523 | 7167132.5839 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13198012.4518 | 22655647.4957 | 3162277.6602 | 0.16884 | 78167.9254 | 134182.7013 | 1593.5589 | 2735.4959
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.3324 | 2.817 | 0.043699 | 4 | 76305.6003 | 130412.0669 | 1555.5929 | 2658.6264 | 56.6983 | 0 | 105.594 | 438423.6216 | 21740.999 | 821783.9146 | 1017867.7157 | 0 | 59400.2525 | 0 | 920094.4363 | 2393896.986 | 1633883.8826 | 7307091.8083 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13337971.6762 | 22795606.7201 | 4216965.0343 | 0.1748 | 76305.6003 | 130412.0669 | 1555.5929 | 2658.6264
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.2876 | 2.8687 | 0.044872 | 4 | 74921.41 | 127614.2437 | 1527.3743 | 2601.589 | 56.7009 | 0 | 108.0383 | 444046.9891 | 22021.0916 | 833827.2661 | 1036070.1528 | 0 | 58567.9228 | 0 | 933868.0348 | 2429733.0638 | 1658342.7421 | 7416477.2632 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13447357.1311 | 22904992.175 | 5623413.2519 | 0.17949 | 74921.41 | 127614.2437 | 1527.3743 | 2601.589
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.0038 | 2.9074 | 0.045774 | 4 | 73890.5644 | 125545.0965 | 1506.3591 | 2559.4066 | 56.7028 | 0 | 122.589 | 448243.1998 | 22230.0836 | 842828.6908 | 1049718.4666 | 0 | 57846.6647 | 0 | 944138.1711 | 2456453.8519 | 1676580.229 | 7498039.3575 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13528919.2255 | 22986554.2694 | 7498942.0933 | 0.18309 | 73890.5644 | 125545.0965 | 1506.3591 | 2559.4066
1 | 1700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.5593 | 2.9375 | 0.046471 | 4 | 73121.6407 | 124001.0483 | 1490.6835 | 2527.9291 | 56.7042 | 0 | 84.9938 | 451485.7634 | 22391.5697 | 849792.8993 | 1060303.2028 | 0 | 57291.3355 | 0 | 952093.2606 | 2477151.3629 | 1690706.7055 | 7561216.0998 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13592095.9677 | 23049731.0116 | 10000000 | 0.18588 | 73121.6407 | 124001.0483 | 1490.6835 | 2527.9291
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 13.5459 | [19 empty] | 100 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.3875 | [19 empty] | 133.3521 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8357 | [19 empty] | 177.8279 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5171 | [19 empty] | 237.1374 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1842 | [19 empty] | 316.2278 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5043 | [19 empty] | 421.6965 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5238 | [19 empty] | 562.3413 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.438 | [19 empty] | 749.8942 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.728 | [19 empty] | 1000 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.581 | [19 empty] | 1333.5214 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.0365 | [19 empty] | 1778.2794 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.1037 | [19 empty] | 2371.3737 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.8696 | [19 empty] | 3162.2777 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.9925 | [19 empty] | 4216.965 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.5382 | [19 empty] | 5623.4133 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.8038 | [19 empty] | 7498.9421 | 0
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077988 | 0.00018613 | 4 | 9168846.9173 | 22447108.3263 | 186919.3462 | 457614.6652 | 54.248 | 0 | 33.2297 | 34959.9993 | 1650.7029 | 46726.5726 | 52632.6533 | 0 | 22102.4385 | 0 | 61648.223 | 160396.0304 | 109473.5865 | 489590.2065 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6826216.1294 | 16711895.6502 | 10000 | 0.0007445 | 9168846.9173 | 22447108.3263 | 186919.3462 | 457614.6652
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077989 | 0.00048909 | 4 | 3484559.0771 | 8537667.581 | 71037.45 | 174051.9017 | 54.2482 | 0 | 32.1676 | 34960.3565 | 1650.7221 | 46726.8842 | 52632.8076 | 0 | 19138.3874 | 0 | 60492.5715 | 157389.2624 | 107421.4056 | 480412.3973 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6817038.3202 | 16702717.841 | 13335.2143 | 0.0019564 | 3484559.0771 | 8537667.581 | 71037.45 | 174051.9017
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077989 | 0.0007163 | 4 | 2376397.5187 | 5826670.276 | 48446.0777 | 118784.5547 | 54.2484 | 0 | 31.8617 | 34960.6245 | 1650.7364 | 46727.118 | 52632.9234 | 0 | 16486.0301 | 0 | 59458.3986 | 154698.5566 | 105584.9436 | 472199.3313 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6808825.2541 | 16694504.775 | 17782.7941 | 0.0028652 | 2376397.5187 | 5826670.276 | 48446.0777 | 118784.5547
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4392 | 0.1861 | 0.001583 | 4 | 1138834.4858 | 2700103.6346 | 23216.6814 | 55045.2648 | 56.8322 | 0 | 66.2391 | 66989.1824 | 3256.6893 | 93468.8479 | 89599.3028 | 0 | 28959.3396 | 0 | 110086.6112 | 286422.7804 | 195489.433 | 874272.1866 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7210898.1094 | 17096577.6303 | 23713.7371 | 0.0063318 | 1138834.4858 | 2700103.6346 | 23216.6814 | 55045.2648
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5723 | 0.25317 | 0.0024165 | 4 | 768546.8032 | 1791253.2296 | 15667.8661 | 36517.1199 | 57.4191 | 0 | 83.8348 | 83740.5035 | 4101.1417 | 119499.5054 | 112438.2895 | 0 | 32886.927 | 0 | 137539.8831 | 357850.5626 | 244240.3621 | 1092297.1749 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7428923.0978 | 17314602.6186 | 31622.7766 | 0.0096662 | 768546.8032 | 1791253.2296 | 15667.8661 | 36517.1199
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9944 | 0.33743 | 0.0035254 | 4 | 545201.3629 | 1246225.12 | 11114.6672 | 25405.9847 | 57.845 | 0 | 85.7295 | 102910.4729 | 5068.9889 | 150321.2885 | 141108.7526 | 0 | 37003.3257 | 0 | 170201.0032 | 442828.0973 | 302239.2756 | 1351681.2047 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7688307.1276 | 17573986.6484 | 42169.6503 | 0.014102 | 545201.3629 | 1246225.12 | 11114.6672 | 25405.9847
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6922 | 0.43777 | 0.0049563 | 4 | 402610.9851 | 901254.1331 | 8207.7695 | 18373.2845 | 58.1301 | 0 | 84.0279 | 123832.9755 | 6125.7905 | 185076.1861 | 175273.7518 | 0 | 40871.8012 | 0 | 207160.3969 | 538988.8584 | 367870.971 | 1645200.7313 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7981826.6542 | 17867506.175 | 56234.1325 | 0.019825 | 402610.9851 | 901254.1331 | 8207.7695 | 18373.2845
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1749 | 0.58559 | 0.006934 | 4 | 302800.3686 | 659220.5652 | 6172.9951 | 13439.1029 | 58.4264 | 0 | 76.8671 | 152267.7203 | 7565.0633 | 233513.7937 | 225459.7989 | 0 | 46897.1691 | 0 | 259624.3826 | 675489.3874 | 461035.3868 | 2061852.7021 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8398478.6249 | 18284158.1458 | 74989.4209 | 0.027736 | 302800.3686 | 659220.5652 | 6172.9951 | 13439.1029
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0714 | 0.75756 | 0.0094275 | 4 | 234965.6418 | 497116.8511 | 4790.0924 | 10134.3994 | 58.6122 | 0 | 67.3402 | 182618.6473 | 9100.9752 | 286879.2805 | 283901.9955 | 0 | 52379.1811 | 0 | 317803.2311 | 826858.8168 | 564348.1327 | 2523890.2603 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8860516.1831 | 18746195.704 | 100000 | 0.03771 | 234965.6418 | 497116.8511 | 4790.0924 | 10134.3994
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5472 | 0.96398 | 0.012578 | 4 | 186707.2401 | 383200.2486 | 3806.2796 | 7812.0554 | 58.7503 | 0 | 77.3861 | 216383.8488 | 10809.8899 | 347828.1738 | 354041.3219 | 0 | 57851.691 | 0 | 384896.8209 | 1001422.5747 | 683491.4844 | 3056725.8054 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9393351.7282 | 19279031.2491 | 133352.1432 | 0.050311 | 186707.2401 | 383200.2486 | 3806.2796 | 7812.0554
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6398 | 1.2071 | 0.01646 | 4 | 151861.9489 | 302008.6556 | 3095.9112 | 6156.8549 | 58.854 | 0 | 88.402 | 253435.7532 | 12685.0322 | 416344.7268 | 436631.0686 | 0 | 63236.4948 | 0 | 461109.8995 | 1199713.3717 | 818829.0278 | 3661985.3745 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9998611.2974 | 19884290.8183 | 177827.941 | 0.06584 | 151861.9489 | 302008.6556 | 3095.9112 | 6156.8549
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2561 | 1.4813 | 0.021071 | 4 | 126467.8653 | 243757.5391 | 2578.2185 | 4969.3271 | 58.9315 | 0 | 101.2031 | 292615.1635 | 14667.4314 | 490401.6574 | 529797.0594 | 0 | 68152.2805 | 0 | 544297.1009 | 1416149.406 | 966551.0685 | 4322631.1676 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 10659257.0905 | 20544936.6114 | 237137.3706 | 0.084284 | 126467.8653 | 243757.5391 | 2578.2185 | 4969.3271
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.1601 | 1.7727 | 0.026282 | 4 | 107871.4364 | 201905.2886 | 2199.1051 | 4116.1124 | 58.9885 | 0 | 100.9083 | 331913.4462 | 16655.2413 | 566133.6232 | 628780.1001 | 0 | 72072.8027 | 0 | 630066.5333 | 1639303.8752 | 1118858.5792 | 5003784.2012 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11340410.1241 | 21226089.645 | 316227.766 | 0.10513 | 107871.4364 | 201905.2886 | 2199.1051 | 4116.1124
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.1124 | 2.0669 | 0.031866 | 4 | 94225.4757 | 171781.1779 | 1920.9138 | 3501.9917 | 59.0306 | 0 | 90.5204 | 369674.5185 | 18564.7248 | 640104.8526 | 728727.4786 | 0 | 74833.7306 | 0 | 714443.069 | 1858834.3131 | 1268692.6139 | 5673875.301 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 12010501.2239 | 21896180.7447 | 421696.5034 | 0.12747 | 94225.4757 | 171781.1779 | 1920.9138 | 3501.9917
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.8117 | 2.3461 | 0.037501 | 4 | 84210.9501 | 150113.3733 | 1716.7541 | 3060.2642 | 59.0614 | 0 | 97.6122 | 404045.6834 | 20302.1795 | 708368.748 | 823571.9531 | 0 | 76292.9508 | 0 | 792706.7908 | 2062460.4633 | 1407671.6455 | 6295420.4146 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 12632046.3375 | 22517725.8583 | 562341.3252 | 0.15 | 84210.9501 | 150113.3733 | 1716.7541 | 3060.2642
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.0233 | 2.5963 | 0.042864 | 4 | 76860.8178 | 134518.0115 | 1566.9117 | 2742.3316 | 59.0835 | 0 | 132.5252 | 433822.7453 | 21806.8601 | 768176.0512 | 908574.1531 | 0 | 76555.4719 | 0 | 861484.7598 | 2241406.6301 | 1529806.0814 | 6841632.7527 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13178258.6756 | 23063938.1965 | 749894.2093 | 0.17146 | 76860.8178 | 134518.0115 | 1566.9117 | 2742.3316
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.6339 | 2.8108 | 0.047714 | 4 | 71461.4568 | 123257.9296 | 1456.8385 | 2512.7796 | 59.0991 | 0 | 89.0476 | 458671.0422 | 23062.0565 | 818531.7561 | 981445.1748 | 0 | 75939.4441 | 0 | 919483.2948 | 2392306.921 | 1632798.6306 | 7302238.3202 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13638864.2431 | 23524543.7639 | 1000000 | 0.19086 | 71461.4568 | 123257.9296 | 1456.8385 | 2512.7796
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6345 | 2.9891 | 0.051922 | 4 | 67488.0278 | 115086.5025 | 1375.8347 | 2346.194 | 59.1102 | 0 | 116.0947 | 478887.4947 | 24082.9638 | 859789.6741 | 1041998.4386 | 0 | 74823.6564 | 0 | 967037.0688 | 2516032.0865 | 1717243.5983 | 7679894.9812 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14016520.9041 | 23902200.425 | 1333521.4322 | 0.20769 | 67488.0278 | 115086.5025 | 1375.8347 | 2346.194
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0318 | 3.1314 | 0.055434 | 4 | 64556.8503 | 109139.7947 | 1316.0787 | 2224.9623 | 59.1179 | 0 | 104.2432 | 494775.8397 | 24885.0916 | 892391.7238 | 1090369.7066 | 0 | 73409.2166 | 0 | 1004574.3156 | 2613696.3026 | 1783901.4326 | 7978003.6291 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14314629.552 | 24200309.0728 | 1778279.41 | 0.22174 | 64556.8503 | 109139.7947 | 1316.0787 | 2224.9623
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.9271 | 3.244 | 0.058296 | 4 | 62388.7818 | 104782.8436 | 1271.8797 | 2136.14 | 59.1232 | 0 | 106.2982 | 507180.6463 | 25511.2111 | 917952.0769 | 1128607.4566 | 0 | 71978.6964 | 0 | 1033979.734 | 2690203.1696 | 1836118.9414 | 8211531.9323 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14548157.8552 | 24433837.376 | 2371373.7057 | 0.23319 | 62388.7818 | 104782.8436 | 1271.8797 | 2136.14
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4157 | 3.3323 | 0.060588 | 4 | 60781.029 | 101571.801 | 1239.1035 | 2070.6785 | 59.127 | 0 | 105.5169 | 516830.0986 | 25998.167 | 937898.6731 | 1158635.3562 | 0 | 70687.0107 | 0 | 1056919.2292 | 2749887.0303 | 1876854.4027 | 8393709.9678 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14730335.8907 | 24616015.4115 | 3162277.6602 | 0.24235 | 60781.029 | 101571.801 | 1239.1035 | 2070.6785
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.5413 | 3.3991 | 0.062376 | 4 | 59586.0524 | 99207.1972 | 1214.7423 | 2022.4729 | 59.1297 | 0 | 101.6266 | 524073.3554 | 26363.6411 | 952907.7003 | 1181337.4288 | 0 | 69500.0887 | 0 | 1074131.0636 | 2794668.6929 | 1907418.8076 | 8530400.7784 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14867026.7012 | 24752706.2221 | 4216965.0343 | 0.24951 | 59586.0524 | 99207.1972 | 1214.7423 | 2022.4729
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.4102 | 3.4507 | 0.06377 | 4 | 58696.1583 | 97451.5508 | 1196.6006 | 1986.6817 | 59.1316 | 0 | 113.4593 | 529634.7694 | 26644.2219 | 964452.7421 | 1198862.0337 | 0 | 68528.0871 | 0 | 1087367.5231 | 2829107.2455 | 1930923.8274 | 8635520.4502 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14972146.373 | 24857825.8939 | 5623413.2519 | 0.25508 | 58696.1583 | 97451.5508 | 1196.6006 | 1986.6817
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.083 | 3.4906 | 0.064849 | 4 | 58032.4114 | 96142.8342 | 1183.0692 | 1960.0017 | 59.1329 | 0 | 124.5244 | 533922.1839 | 26860.508 | 973365.4833 | 1212427.5828 | 0 | 67766.4772 | 0 | 1097593.4717 | 2855713.066 | 1949082.8466 | 8716731.6195 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 15053357.5424 | 24939037.0633 | 7498942.0933 | 0.2594 | 58032.4114 | 96142.8342 | 1183.0692 | 1960.0017
1 | 1800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.5823 | 3.5202 | 0.065668 | 4 | 57536.7218 | 95171.6441 | 1172.9639 | 1940.2027 | 59.1339 | 0 | 118.6368 | 537094.7076 | 27020.5403 | 979967.5138 | 1222496.5797 | 0 | 67131.0813 | 0 | 1105147.0649 | 2875365.9659 | 1962496.3546 | 8776719.8081 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 15113345.731 | 24999025.2518 | 10000000 | 0.26267 | 57536.7218 | 95171.6441 | 1172.9639 | 1940.2027
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.2789 | [19 empty] | 100 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7819 | [19 empty] | 133.3521 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4835 | [19 empty] | 177.8279 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5448 | [19 empty] | 237.1374 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2403 | [19 empty] | 316.2278 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6657 | [19 empty] | 421.6965 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4235 | [19 empty] | 562.3413 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.758 | [19 empty] | 749.8942 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7288 | [19 empty] | 1000 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.016 | [19 empty] | 1333.5214 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.3667 | [19 empty] | 1778.2794 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.2344 | [19 empty] | 2371.3737 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.1427 | [19 empty] | 3162.2777 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.7614 | [19 empty] | 4216.965 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.2711 | [19 empty] | 5623.4133 | 0
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.084231 | 0.00017754 | 4 | 10096849.7047 | 24631153.4999 | 205837.9382 | 502139.3802 | 56.1349 | 0 | 37.537 | 38364.0865 | 1835.5375 | 49606.9902 | 54043.7971 | 0 | 24788.7553 | 0 | 65769.275 | 171118.1623 | 116791.6619 | 522318.2658 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7170550.3345 | 17492478.4595 | 7498.9421 | 0.00071018 | 10096849.7047 | 24631153.4999 | 205837.9382 | 502139.3802
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.084232 | 0.00056899 | 4 | 3145966.9251 | 7681167.7172 | 64134.791 | 156590.9935 | 56.1351 | 0 | 37.1369 | 38364.5765 | 1835.5644 | 49607.4002 | 54043.9959 | 0 | 21410.2397 | 0 | 64452.0929 | 167691.1248 | 114452.6384 | 511857.6326 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7160089.7013 | 17482017.8263 | 10000 | 0.002276 | 3145966.9251 | 7681167.7172 | 64134.791 | 156590.9935
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.084233 | 0.00086256 | 4 | 2072568.7824 | 5064236.3946 | 42252.118 | 103241.3088 | 56.1353 | 0 | 35.4722 | 38364.9441 | 1835.5845 | 49607.708 | 54044.145 | 0 | 18419.6914 | 0 | 63286.1085 | 164657.4725 | 112382.1084 | 502597.7624 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7150829.8311 | 17472757.9561 | 13335.2143 | 0.0034502 | 2072568.7824 | 5064236.3946 | 42252.118 | 103241.3088
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3077 | 0.1937 | 0.0018477 | 4 | 1022451.9445 | 2419071.3925 | 20844.0659 | 49316.0424 | 58.8901 | 0 | 73.2138 | 71623.1589 | 3527.4205 | 96329.7392 | 90246.5472 | 0 | 31550.4749 | 0 | 114378.1629 | 297588.5176 | 203110.2781 | 908354.2992 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7556586.3679 | 17878514.493 | 17782.7941 | 0.0073907 | 1022451.9445 | 2419071.3925 | 20844.0659 | 49316.0424
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3944 | 0.2636 | 0.002841 | 4 | 684916.0093 | 1593223.4257 | 13962.9393 | 32480.0145 | 59.5639 | 0 | 79.1212 | 89662.6945 | 4450.6262 | 123179.443 | 113289.4194 | 0 | 35902.2177 | 0 | 142928.9164 | 371871.7216 | 253810.0912 | 1135095.13 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7783327.1987 | 18105255.3237 | 23713.7371 | 0.011364 | 684916.0093 | 1593223.4257 | 13962.9393 | 32480.0145
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7702 | 0.3522 | 0.0041675 | 4 | 483213.1383 | 1102398.1696 | 9850.9534 | 22473.8778 | 60.0588 | 0 | 100.2757 | 110488.1298 | 5518.0959 | 155239.8468 | 142469.894 | 0 | 40563.7999 | 0 | 177169.1089 | 460957.679 | 314613.0876 | 1407019.642 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8055251.7107 | 18377179.8357 | 31622.7766 | 0.01667 | 483213.1383 | 1102398.1696 | 9850.9534 | 22473.8778
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4487 | 0.46022 | 0.0058929 | 4 | 355088.0439 | 792986.8263 | 7238.9501 | 16166.109 | 60.4011 | 0 | 94.3032 | 133716.5253 | 6708.9298 | 192224.6662 | 178049.2094 | 0 | 45187.7635 | 0 | 216795.9667 | 564058.6345 | 384981.6083 | 1721723.3037 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8369955.3724 | 18691883.4974 | 42169.6503 | 0.023571 | 355088.0439 | 792986.8263 | 7238.9501 | 16166.109
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8434 | 0.61532 | 0.0082588 | 4 | 266507.3277 | 578960.4411 | 5433.1124 | 11802.8917 | 60.7321 | 0 | 107.7647 | 164424.1538 | 8285.9882 | 242430.8221 | 229004.238 | 0 | 51913.7881 | 0 | 271463.0061 | 706291.0572 | 482058.1594 | 2155871.2129 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8804103.2816 | 19126031.4066 | 56234.1325 | 0.033035 | 266507.3277 | 578960.4411 | 5433.1124 | 11802.8917
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6692 | 0.79796 | 0.01127 | 4 | 206100.2222 | 435072.077 | 4201.6318 | 8869.5328 | 60.9469 | 0 | 78.9964 | 197604.0513 | 9989.5201 | 298403.2182 | 289047.6612 | 0 | 58180.8576 | 0 | 332757.8703 | 865767.7204 | 590904.2589 | 2642655.1581 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9290887.2268 | 19612815.3518 | 74989.4209 | 0.045079 | 206100.2222 | 435072.077 | 4201.6318 | 8869.5328
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1233 | 1.0213 | 0.015111 | 4 | 163158.1268 | 333921.1792 | 3326.1991 | 6807.4349 | 61.1083 | 0 | 136.5411 | 235158.6671 | 11917.558 | 363476.6961 | 362455.5903 | 0 | 64688.0495 | 0 | 404701.6588 | 1052950.7004 | 718660.489 | 3214009.4091 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9862241.4778 | 20184169.6028 | 100000 | 0.060446 | 163158.1268 | 333921.1792 | 3326.1991 | 6807.4349
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2332 | 1.2871 | 0.0199 | 4 | 132124.3779 | 261797.973 | 2693.5342 | 5337.1058 | 61.2296 | 0 | 102.9842 | 276734.1927 | 14051.5699 | 437324.5426 | 449817.7123 | 0 | 71171.0782 | 0 | 487148.6473 | 1267460.8524 | 865068.0755 | 3868776.6709 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 10517008.7396 | 20838936.8646 | 133352.1432 | 0.079599 | 132124.3779 | 261797.973 | 2693.5342 | 5337.1058
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9419 | 1.5917 | 0.025676 | 4 | 109454.4045 | 209954.2195 | 2231.3761 | 4280.2007 | 61.3202 | 0 | 108.4156 | 321295.6475 | 16338.07 | 518283.0986 | 549914.7468 | 0 | 77219.6173 | 0 | 578389.9603 | 1504852.0325 | 1027092.4338 | 4593385.6067 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 11241617.6754 | 21563545.8004 | 177827.941 | 0.10271 | 109454.4045 | 209954.2195 | 2231.3761 | 4280.2007
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.0823 | 1.9243 | 0.032352 | 4 | 92793.9389 | 172557.2331 | 1891.73 | 3517.8126 | 61.3876 | 0 | 98.6891 | 367106.9795 | 18687.6861 | 603207.3353 | 659198.6191 | 0 | 82349.5121 | 0 | 674914.5515 | 1755989.2191 | 1198498.724 | 5359952.6268 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 12008184.6955 | 22330112.8205 | 237137.3706 | 0.12941 | 92793.9389 | 172557.2331 | 1891.73 | 3517.8126
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.407 | 2.2689 | 0.039681 | 4 | 80519.7434 | 145550.3017 | 1641.5039 | 2967.2398 | 61.4376 | 0 | 124.9575 | 412127.0744 | 20995.6145 | 688142.1692 | 772415.0025 | 0 | 86205.0617 | 0 | 772155.1197 | 2008989.2307 | 1371176.4305 | 6132205.7032 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 12780437.7719 | 23102365.8969 | 316227.766 | 0.15872 | 80519.7434 | 145550.3017 | 1641.5039 | 2967.2398
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.6009 | 2.6051 | 0.047273 | 4 | 71475.0685 | 126061.4848 | 1457.1159 | 2569.9339 | 61.4742 | 0 | 103.1785 | 454113.5511 | 23146.9701 | 768540.0171 | 882858.6761 | 0 | 88539.8561 | 0 | 864707.6375 | 2249791.8968 | 1535529.1982 | 6867227.8029 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 13515459.8716 | 23837387.9966 | 421696.5034 | 0.18909 | 71475.0685 | 126061.4848 | 1457.1159 | 2569.9339
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.383 | 2.9146 | 0.054687 | 4 | 64814.0308 | 112000.438 | 1321.3217 | 2283.2804 | 61.5006 | 0 | 122.8878 | 491359.7702 | 25054.519 | 840741.3666 | 984546.1305 | 0 | 89388.1167 | 0 | 948125.0622 | 2466826.9246 | 1683660.0643 | 7529701.9541 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 14177934.0228 | 24499862.1478 | 562341.3252 | 0.21875 | 64814.0308 | 112000.438 | 1321.3217 | 2283.2804
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.548 | 3.1841 | 0.061528 | 4 | 59909.2264 | 101849.4251 | 1221.3306 | 2076.3383 | 61.5192 | 0 | 145.0136 | 522841.1082 | 26666.0839 | 902374.2609 | 1073106.5517 | 0 | 88961.5049 | 0 | 1019440.3087 | 2652374.5674 | 1810300.1431 | 8096064.5288 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 14744296.5975 | 25066224.7225 | 749894.2093 | 0.24611 | 59909.2264 | 101849.4251 | 1221.3306 | 2076.3383
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0512 | 3.4108 | 0.067561 | 4 | 56294.6414 | 94489.273 | 1147.6424 | 1926.2916 | 61.5319 | 0 | 122.1803 | 548697.3405 | 27989.137 | 953393.058 | 1147581.0449 | 0 | 87738.6247 | 0 | 1078505.69 | 2806050.5735 | 1915187.175 | 8565142.6438 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15213374.7125 | 25535302.8375 | 1000000 | 0.27025 | 56294.6414 | 94489.273 | 1147.6424 | 1926.2916
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.9017 | 3.5951 | 0.072679 | 4 | 53626.3053 | 89131.3222 | 1093.2448 | 1817.0626 | 61.5406 | 0 | 122.1514 | 569348.0143 | 29045.4312 | 994391.5063 | 1208165.5019 | 0 | 86081.7429 | 0 | 1125942.5567 | 2929471.5699 | 1999424.5411 | 8941870.8644 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15590102.9331 | 25912031.0581 | 1333521.4322 | 0.29072 | 53626.3053 | 89131.3222 | 1093.2448 | 1817.0626
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.1667 | 3.7416 | 0.07689 | 4 | 51652.1289 | 85212.6628 | 1052.9985 | 1737.1754 | 61.5464 | 0 | 125.8968 | 585522.4364 | 29872.5011 | 1026656.0889 | 1256292.9699 | 0 | 84290.0847 | 0 | 1163227.2916 | 3026478.8019 | 2065633.9702 | 9237974.1446 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15886206.2133 | 26208134.3383 | 1778279.41 | 0.30756 | 51652.1289 | 85212.6628 | 1052.9985 | 1737.1754
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.9307 | 3.8556 | 0.080272 | 4 | 50188.1243 | 82335.0472 | 1023.1528 | 1678.5113 | 61.5503 | 0 | 136.8026 | 597981.9294 | 30509.4446 | 1051600.7485 | 1293767.4093 | 0 | 82549.5182 | 0 | 1191999.5295 | 3101338.2631 | 2116727.0907 | 9466473.9333 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16114706.002 | 26436634.127 | 2371373.7057 | 0.32109 | 50188.1243 | 82335.0472 | 1023.1528 | 1678.5113
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.3191 | 3.9453 | 0.082961 | 4 | 49100.085 | 80204.8276 | 1000.9716 | 1635.0839 | 61.553 | 0 | 140.9388 | 607706.4214 | 31006.4672 | 1071124.1287 | 1323256.6678 | 0 | 81067.1535 | 0 | 1214522.7271 | 3159939.003 | 2156723.2998 | 9645345.8685 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16293577.9372 | 26615506.0622 | 3162277.6602 | 0.33184 | 49100.085 | 80204.8276 | 1000.9716 | 1635.0839
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.3667 | 4.0129 | 0.085047 | 4 | 48289.9281 | 78631.9068 | 984.4555 | 1603.0178 | 61.5549 | 0 | 116.7077 | 614997.1465 | 31379.037 | 1085792.4582 | 1345503.5269 | 0 | 79752.2401 | 0 | 1231395.5194 | 3203838.5475 | 2186685.641 | 9779344.1166 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16427576.1853 | 26749504.3103 | 4216965.0343 | 0.34019 | 48289.9281 | 78631.9068 | 984.4555 | 1603.0178
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1561 | 4.0639 | 0.086651 | 4 | 47685.7348 | 77466.0595 | 972.1382 | 1579.2504 | 61.5561 | 0 | 124.2396 | 620464.7862 | 31658.4079 | 1096810.3221 | 1362264.7697 | 0 | 78644.4095 | 0 | 1244038.6512 | 3236733.383 | 2209137.0421 | 9879751.7715 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16527983.8402 | 26849911.9653 | 5623413.2519 | 0.3466 | 47685.7348 | 77466.0595 | 972.1382 | 1579.2504
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.7823 | 4.1043 | 0.0879 | 4 | 47234.5708 | 76591.5101 | 962.9406 | 1561.4215 | 61.557 | 0 | 123.9327 | 624786.4986 | 31879.2052 | 1105529.5675 | 1375559.9292 | 0 | 77831.8352 | 0 | 1254078.9439 | 3262856.165 | 2226966.3776 | 9959488.5222 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16607720.5909 | 26929648.7159 | 7498942.0933 | 0.3516 | 47234.5708 | 76591.5101 | 962.9406 | 1561.4215
1 | 1900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.2427 | 4.134 | 0.088843 | 4 | 46897.3411 | 75942.7218 | 956.0657 | 1548.1951 | 61.5577 | 0 | 129.6869 | 627955.3727 | 32041.0911 | 1111928.8183 | 1385334.7583 | 0 | 77150.9053 | 0 | 1261420.2688 | 3281956.7866 | 2240002.9443 | 10017790.9454 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16666023.0141 | 26987951.1391 | 10000000 | 0.35537 | 46897.3411 | 75942.7218 | 956.0657 | 1548.1951
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.5654 | [19 empty] | 100 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.0705 | [19 empty] | 133.3521 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1291 | [19 empty] | 177.8279 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.9085 | [19 empty] | 237.1374 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7517 | [19 empty] | 316.2278 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6458 | [19 empty] | 421.6965 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9 | [19 empty] | 562.3413 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6355 | [19 empty] | 749.8942 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5743 | [19 empty] | 1000 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.1554 | [19 empty] | 1333.5214 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6811 | [19 empty] | 1778.2794 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.1616 | [19 empty] | 2371.3737 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.4948 | [19 empty] | 3162.2777 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.5515 | [19 empty] | 4216.965 | 0
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.090585 | 9.1608e-05 | 4 | 20528545.9524 | 49910346.7514 | 418502.1762 | 1017489.9273 | 57.994 | 0 | 36.8195 | 41822.2741 | 2026.5166 | 52487.4414 | 55425.6954 | 0 | 27939.8867 | 0 | 70083.7075 | 182343.4308 | 124453.1383 | 556582.0906 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7522280.396 | 18288661.2524 | 5623.4133 | 0.00036643 | 20528545.9524 | 49910346.7514 | 418502.1762 | 1017489.9273
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.090586 | 0.00059786 | 4 | 3140480.1472 | 7642510.9246 | 64022.9356 | 155802.9225 | 57.9944 | 0 | 37.3295 | 41822.9504 | 2026.5542 | 52488.0015 | 55425.9614 | 0 | 24070.5333 | 0 | 68575.2603 | 178418.7606 | 121774.4703 | 544602.492 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7510300.7974 | 18276681.6538 | 7498.9421 | 0.0023914 | 3140480.1472 | 7642510.9246 | 64022.9356 | 155802.9225
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.090587 | 0.00097753 | 4 | 1918042.3985 | 4671498.7692 | 39101.8886 | 95234.8211 | 57.9946 | 0 | 34.0444 | 41823.4581 | 2026.5825 | 52488.4219 | 55426.1611 | 0 | 20679.3563 | 0 | 67253.1522 | 174978.9064 | 119426.6991 | 534102.7375 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7499801.0429 | 18266181.8993 | 10000 | 0.0039101 | 1918042.3985 | 4671498.7692 | 39101.8886 | 95234.8211
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1102 | 0.19514 | 0.0020222 | 4 | 975165.4142 | 2306211.9867 | 19880.066 | 47015.2507 | 60.8365 | 0 | 73.7871 | 74585.5094 | 3717.7374 | 96725.4078 | 88973.4242 | 0 | 33707.3112 | 0 | 116106.6621 | 302085.7181 | 206179.7098 | 922081.48 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7887779.7854 | 18654160.6417 | 13335.2143 | 0.0080887 | 975165.4142 | 2306211.9867 | 19880.066 | 47015.2507
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 0.27448 | 0.0031565 | 4 | 645245.5721 | 1497963.0463 | 13154.2037 | 30538.0028 | 61.6882 | 0 | 53.5921 | 95705.0347 | 4813.7827 | 126978.5341 | 114295.6315 | 0 | 39560.8745 | 0 | 148728.0044 | 386959.7591 | 264107.9868 | 1181149.6078 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8146847.9132 | 18913228.7696 | 17782.7941 | 0.012626 | 645245.5721 | 1497963.0463 | 13154.2037 | 30538.0028
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4413 | 0.35808 | 0.004662 | 4 | 450504.6543 | 1027849.4978 | 9184.1467 | 20954.1023 | 62.2091 | 0 | 87.4244 | 115974.9467 | 5867.5159 | 157003.3919 | 140952.6568 | 0 | 43629.7305 | 0 | 180737.0143 | 470240.6371 | 320948.8973 | 1435354.7906 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8401053.096 | 19167433.9524 | 23713.7371 | 0.018648 | 450504.6543 | 1027849.4978 | 9184.1467 | 20954.1023
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.066 | 0.47155 | 0.0066498 | 4 | 328269.3399 | 733034.9524 | 6692.2145 | 14943.909 | 62.6261 | 0 | 93.406 | 141242.0636 | 7181.8425 | 195604.2567 | 177140.2283 | 0 | 48999.4348 | 0 | 222365.4521 | 578549.2929 | 394871.7804 | 1765954.3513 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8731652.6567 | 19498033.5131 | 31622.7766 | 0.026599 | 328269.3399 | 733034.9524 | 6692.2145 | 14943.909
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4218 | 0.63682 | 0.0093665 | 4 | 245384.2853 | 532746.8449 | 5002.4906 | 10860.765 | 63.0092 | 0 | 97.7769 | 174983.969 | 8939.3056 | 248664.8728 | 229746.3277 | 0 | 56985.5249 | 0 | 280534.8 | 729894.0039 | 498167.6555 | 2227916.4593 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9193614.7647 | 19959995.6211 | 42169.6503 | 0.037466 | 245384.2853 | 532746.8449 | 5002.4906 | 10860.765
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0165 | 0.81886 | 0.012819 | 4 | 188685.1907 | 398655.0214 | 3846.6028 | 8127.1218 | 63.2507 | 0 | 89.7372 | 209102.0102 | 10715.7512 | 304003.9761 | 287687.442 | 0 | 63231.7904 | 0 | 341148.9782 | 887599.6621 | 605805.0077 | 2709294.6179 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9674992.9233 | 20441373.7796 | 56234.1325 | 0.051276 | 188685.1907 | 398655.0214 | 3846.6028 | 8127.1218
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.3487 | 1.0527 | 0.01728 | 4 | 148577.1735 | 304337.2992 | 3028.9466 | 6204.3275 | 63.4412 | 0 | 89.9964 | 249680.7032 | 12828.2589 | 371594.5731 | 362094.4736 | 0 | 70613.4981 | 0 | 416056.4877 | 1082493.6361 | 738824.1497 | 3304185.7805 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10269884.0859 | 21036264.9422 | 74989.4209 | 0.069122 | 148577.1735 | 304337.2992 | 3028.9466 | 6204.3275
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3855 | 1.336 | 0.02291 | 4 | 119629.3963 | 237112.9421 | 2438.8071 | 4833.868 | 63.5853 | 0 | 72.7115 | 295338.8209 | 15204.4697 | 449592.5421 | 452244.6956 | 0 | 78224.7179 | 0 | 503336.046 | 1309577.1433 | 893813.3095 | 3997331.7451 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10963030.0505 | 21729410.9068 | 100000 | 0.091642 | 119629.3963 | 237112.9421 | 2438.8071 | 4833.868
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.077 | 1.6653 | 0.029804 | 4 | 98472.737 | 188781.905 | 2007.4999 | 3848.5745 | 63.693 | 0 | 109.745 | 344871.3079 | 17781.1465 | 536203.3757 | 557023.3425 | 0 | 85459.9381 | 0 | 601122.2532 | 1563996.7956 | 1067459.9499 | 4773918.1094 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 11739616.4148 | 22505997.2711 | 133352.1432 | 0.11922 | 98472.737 | 188781.905 | 2007.4999 | 3848.5745
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.3512 | 2.0356 | 0.037955 | 4 | 82890.8619 | 153806.8155 | 1689.8423 | 3135.56 | 63.774 | 0 | 89.0715 | 397164.7626 | 20499.949 | 629589.0638 | 674830.7018 | 0 | 92006.4831 | 0 | 707495.4745 | 1840758.0973 | 1256355.2252 | 5618699.7571 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 12584398.0625 | 23350778.9189 | 177827.941 | 0.15182 | 82890.8619 | 153806.8155 | 1689.8423 | 3135.56
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.966 | 2.4299 | 0.047137 | 4 | 71372.5525 | 128473.8142 | 1455.026 | 2619.1125 | 63.8343 | 0 | 100.6713 | 449797.6629 | 23234.7525 | 725350.3572 | 800257.8313 | 0 | 97254.5874 | 0 | 817399.1246 | 2126704.8507 | 1451519.76 | 6491518.9266 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 13457217.232 | 24223598.0884 | 237137.3706 | 0.18855 | 71372.5525 | 128473.8142 | 1455.026 | 2619.1125
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.6035 | 2.8258 | 0.056922 | 4 | 62852.1 | 110138.1344 | 1281.3251 | 2245.3148 | 63.8787 | 0 | 63.6343 | 500139.4954 | 25848.9054 | 818423.7649 | 926203.8134 | 0 | 100795.2571 | 0 | 924850.3821 | 2406270.9814 | 1642329.3887 | 7344861.9884 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 14310560.2938 | 25076941.1501 | 316227.766 | 0.22769 | 62852.1 | 110138.1344 | 1281.3251 | 2245.3148
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9212 | 3.1993 | 0.066735 | 4 | 56554.9648 | 96887.6044 | 1152.9495 | 1975.1849 | 63.9107 | 0 | 103.6785 | 545727.4644 | 28214.7646 | 903846.656 | 1045005.9307 | 0 | 102454.9991 | 0 | 1023847.4278 | 2663840.9871 | 1818126.2101 | 8131064.4398 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15096762.7452 | 25863143.6016 | 421696.5034 | 0.26694 | 56554.9648 | 96887.6044 | 1152.9495 | 1975.1849
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6929 | 3.5343 | 0.076042 | 4 | 51905.8546 | 87301.8994 | 1058.1711 | 1779.7673 | 63.9331 | 0 | 119.5334 | 585287.9411 | 30266.614 | 978794.6795 | 1151596.658 | 0 | 102531.0595 | 0 | 1110906.0113 | 2890349.5633 | 1972722.9677 | 8822455.4943 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15788153.7997 | 26554534.6561 | 562341.3252 | 0.30417 | 51905.8546 | 87301.8994 | 1058.1711 | 1779.7673
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.7567 | 3.8196 | 0.084409 | 4 | 48474.093 | 80361.6309 | 988.21 | 1638.2805 | 63.9481 | 0 | 107.4206 | 618086.0886 | 31966.7921 | 1041482.9724 | 1242353.4463 | 0 | 101348.3537 | 0 | 1183742.6847 | 3079855.6467 | 2102064.7636 | 9400900.7481 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 16366599.0535 | 27132979.9099 | 749894.2093 | 0.33764 | 48474.093 | 80361.6309 | 988.21 | 1638.2805
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.113 | 4.055 | 0.091629 | 4 | 45938.6394 | 75313.4336 | 936.5213 | 1535.3662 | 63.958 | 0 | 112.4672 | 644604.7424 | 33340.7764 | 1092524.2259 | 1317282.545 | 0 | 99466.3261 | 0 | 1243015.2602 | 3234070.7295 | 2207319.7264 | 9871624.3321 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 16837322.6374 | 27603703.4938 | 1000000 | 0.36652 | 45938.6394 | 75313.4336 | 936.5213 | 1535.3662
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8197 | 4.2448 | 0.09766 | 4 | 44062.2418 | 71623.2482 | 898.2684 | 1460.1368 | 63.9645 | 0 | 119.9133 | 665640.4471 | 34430.2111 | 1133234.1519 | 1377690.6569 | 0 | 97320.8936 | 0 | 1290243.3806 | 3356948.611 | 2291186.4054 | 10246694.7575 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17212393.0629 | 27978773.9193 | 1333521.4322 | 0.39064 | 44062.2418 | 71623.2482 | 898.2684 | 1460.1368
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.9392 | 4.3933 | 0.10255 | 4 | 42670.7632 | 68918.3693 | 869.9012 | 1404.9942 | 63.9685 | 0 | 113.6969 | 681902.9503 | 35272.1415 | 1164839.6677 | 1424975.2212 | 0 | 95127.1086 | 0 | 1326825.6648 | 3452128.2105 | 2356148.4378 | 10537219.4023 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17502917.7077 | 28269298.564 | 1778279.41 | 0.41019 | 42670.7632 | 68918.3693 | 869.9012 | 1404.9942
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5936 | 4.5092 | 0.10644 | 4 | 41636.7807 | 66923.3238 | 848.8221 | 1364.3225 | 63.9711 | 0 | 103.6603 | 694473.8668 | 35922.7653 | 1189349.7023 | 1461872.8945 | 0 | 93138.8239 | 0 | 1355155.6406 | 3525836.9961 | 2406456.1986 | 10762206.888 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17727905.1934 | 28494286.0497 | 2371373.7057 | 0.42578 | 41636.7807 | 66923.3238 | 848.8221 | 1364.3225
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.8692 | 4.5985 | 0.1095 | 4 | 40867.0248 | 65447.0936 | 833.1296 | 1334.2275 | 63.9728 | 0 | 108.0013 | 704095.5609 | 36420.6332 | 1208155.8367 | 1490317.5684 | 0 | 91420.4233 | 0 | 1376859.9088 | 3582307.0498 | 2444998.1705 | 10934575.1515 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17900273.4569 | 28666654.3132 | 3162277.6602 | 0.43801 | 40867.0248 | 65447.0936 | 833.1296 | 1334.2275
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.8413 | 4.6665 | 0.11187 | 4 | 40293.0705 | 64352.3855 | 821.4287 | 1311.9104 | 63.9739 | 0 | 131.1377 | 711385.6435 | 36797.7852 | 1222431.3771 | 1511986.4388 | 0 | 89976.2525 | 0 | 1393305.2239 | 3625094.3863 | 2474201.4069 | 11065178.5142 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18030876.8196 | 28797257.676 | 4216965.0343 | 0.44749 | 40293.0705 | 64352.3855 | 821.4287 | 1311.9104
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.5749 | 4.7178 | 0.11369 | 4 | 39864.56 | 63539.2136 | 812.693 | 1295.3328 | 63.9746 | 0 | 111.6002 | 716864.7871 | 37081.2089 | 1233175.8189 | 1528338.8793 | 0 | 88787.171 | 0 | 1405656.6675 | 3657230.3089 | 2496134.8344 | 11163269.676 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18128967.9814 | 28895348.8378 | 5623413.2519 | 0.45476 | 39864.56 | 63539.2136 | 812.693 | 1295.3328
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.1324 | 4.7568 | 0.11508 | 4 | 39544.308 | 62932.8805 | 806.1642 | 1282.9719 | 63.975 | 0 | 117.9302 | 721015.2837 | 37295.8817 | 1241323.4417 | 1540763.8499 | 0 | 87847.0732 | 0 | 1415015.7568 | 3681580.7396 | 2512754.5037 | 11237596.5303 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18203294.8357 | 28969675.692 | 7498942.0933 | 0.46033 | 39544.308 | 62932.8805 | 806.1642 | 1282.9719
1 | 2000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.554 | 4.7863 | 0.11614 | 4 | 39304.7714 | 62480.2892 | 801.2809 | 1273.7452 | 63.9754 | 0 | 116.6678 | 724146.0686 | 37457.7996 | 1247474.2338 | 1550157.7764 | 0 | 87111.4331 | 0 | 1422075.4515 | 3699948.617 | 2525290.9574 | 11293662.3373 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18259360.6427 | 29025741.4991 | 10000000 | 0.46456 | 39304.7714 | 62480.2892 | 801.2809 | 1273.7452
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7688 | [19 empty] | 100 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0458 | [19 empty] | 133.3521 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7311 | [19 empty] | 177.8279 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.2908 | [19 empty] | 237.1374 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9802 | [19 empty] | 316.2278 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0806 | [19 empty] | 421.6965 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6359 | [19 empty] | 562.3413 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5439 | [19 empty] | 749.8942 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8467 | [19 empty] | 1000 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.4161 | [19 empty] | 1333.5214 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.1225 | [19 empty] | 1778.2794 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5529 | [19 empty] | 2371.3737 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.4909 | [19 empty] | 3162.2777 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.2598 | [19 empty] | 4216.965 | 0
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.096866 | 0.00055242 | 4 | 3560460.6214 | 8637719.2361 | 72584.8056 | 176091.59 | 59.8263 | 0 | 36.9364 | 45306.6606 | 2222.7514 | 55284.6235 | 56742.5053 | 0 | 27189.0725 | 0 | 72830.7892 | 189490.7737 | 129331.3467 | 578398.5228 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7867423.1558 | 19086460.8707 | 5623.4133 | 0.0022097 | 3560460.6214 | 8637719.2361 | 72584.8056 | 176091.59
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.12229 | 0.0011884 | 4 | 1674141.2327 | 4034223.6121 | 34129.6335 | 82243.105 | 60.9247 | 0 | 289.6589 | 54194.8226 | 2686.0191 | 66549.3749 | 64697.4537 | 0 | 27960.4204 | 0 | 84274.3554 | 219264.5856 | 149652.5851 | 669279.6168 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7958304.2497 | 19177341.9647 | 7498.9421 | 0.0047537 | 1674141.2327 | 4034223.6121 | 34129.6335 | 82243.105
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8519 | 0.19032 | 0.0020859 | 4 | 983150.7514 | 2327806.9942 | 20042.8579 | 47455.4942 | 62.6255 | 0 | 78.4327 | 75552.5999 | 3805.3142 | 94652.9259 | 85852.9116 | 0 | 35178.0696 | 0 | 115066.3102 | 299378.9359 | 204332.2754 | 913819.3427 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8202843.9756 | 19421881.6906 | 10000 | 0.0083434 | 983150.7514 | 2327806.9942 | 20042.8579 | 47455.4942
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 0.26226 | 0.0033172 | 4 | 635989.6191 | 1481504.763 | 12965.5086 | 30202.4785 | 63.5734 | 0 | 76.1665 | 95657.962 | 4863.1232 | 122228.4644 | 108142.6274 | 0 | 40354.2553 | 0 | 144786.1086 | 376703.7549 | 257108.0532 | 1149844.3491 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8438868.982 | 19657906.697 | 13335.2143 | 0.013269 | 635989.6191 | 1481504.763 | 12965.5086 | 30202.4785
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0445 | 0.35572 | 0.0049807 | 4 | 438090.718 | 1001219.6264 | 8931.0718 | 20411.2163 | 64.283 | 0 | 68.664 | 119357.2753 | 6112.3836 | 155883.1482 | 137047.8079 | 0 | 46177.7711 | 0 | 181185.5706 | 471407.6883 | 321745.4338 | 1438917.0787 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8727941.7117 | 19946979.4266 | 17782.7941 | 0.019923 | 438090.718 | 1001219.6264 | 8931.0718 | 20411.2163
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5861 | 0.47209 | 0.0071843 | 4 | 315563.7138 | 705967.197 | 6433.1931 | 14392.0962 | 64.7933 | 0 | 79.4064 | 146293.678 | 7533.6483 | 195401.2119 | 173029.3499 | 0 | 52231.7738 | 0 | 224050.9681 | 582934.6599 | 397864.8835 | 1779340.1734 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9068364.8063 | 20287402.5213 | 23713.7371 | 0.028737 | 315563.7138 | 705967.197 | 6433.1931 | 14392.0962
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1551 | 0.59008 | 0.010003 | 4 | 234732.4243 | 515135.8435 | 4785.338 | 10501.7409 | 65.0856 | 0 | 51.8806 | 171477.5027 | 8861.3165 | 233520.9363 | 209564.0843 | 0 | 55468.1929 | 0 | 264767.8928 | 688871.7456 | 470169.1213 | 2102700.7923 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9391725.4253 | 20610763.1402 | 31622.7766 | 0.04001 | 234732.4243 | 515135.8435 | 4785.338 | 10501.7409
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1929 | 0.82154 | 0.014003 | 4 | 178841.0587 | 379138.2254 | 3645.9169 | 7729.2455 | 65.5178 | 0 | 88.653 | 217057.9237 | 11269.5464 | 304185.4075 | 280879.2994 | 0 | 67457.3366 | 0 | 343531.3103 | 893798.0015 | 610035.5018 | 2728214.3273 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10017238.9602 | 21236276.6752 | 42169.6503 | 0.056012 | 178841.0587 | 379138.2254 | 3645.9169 | 7729.2455
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.246 | 1.0533 | 0.018952 | 4 | 139888.5046 | 287877.768 | 2851.8164 | 5868.7777 | 65.7394 | 0 | 48.3741 | 258760.4897 | 13470.418 | 371007.9674 | 352375.7884 | 0 | 74977.7192 | 0 | 417531.0293 | 1086330.0907 | 741442.6088 | 3315896.1115 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10604920.7444 | 21823958.4594 | 56234.1325 | 0.07581 | 139888.5046 | 287877.768 | 2851.8164 | 5868.7777
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.2381 | 1.3563 | 0.025356 | 4 | 111865.8511 | 222481.0784 | 2280.5367 | 4535.5777 | 65.9186 | 0 | 91.3946 | 309305.966 | 16136.9263 | 454128.106 | 445869.4306 | 0 | 84383.3222 | 0 | 510831.2629 | 1329078.1602 | 907123.1542 | 4056856.3284 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 11345880.9613 | 22564918.6763 | 74989.4209 | 0.10142 | 111865.8511 | 222481.0784 | 2280.5367 | 4535.5777
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8324 | 1.705 | 0.033265 | 4 | 91417.7814 | 175732.7852 | 1863.6751 | 3582.5505 | 66.0484 | 0 | 81.8273 | 363410.785 | 18989.9129 | 545274.4385 | 553429.8913 | 0 | 92907.4123 | 0 | 613864.8516 | 1597150.4229 | 1090087.9818 | 4875115.6964 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 12164140.3293 | 23383178.0442 | 100000 | 0.13306 | 91417.7814 | 175732.7852 | 1863.6751 | 3582.5505
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1092 | 2.1052 | 0.042802 | 4 | 76346.5029 | 141875.0313 | 1556.4267 | 2892.3144 | 66.1462 | 0 | 94.5547 | 421583.4372 | 22055.8119 | 645411.4949 | 676903.1689 | 0 | 100907.0173 | 0 | 728075.7628 | 1894303.7859 | 1292901.2579 | 5782141.7367 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 13071166.3697 | 24290204.0846 | 133352.1432 | 0.17121 | 76346.5029 | 141875.0313 | 1556.4267 | 2892.3144
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8749 | 2.5426 | 0.053816 | 4 | 65180.4713 | 117297.9413 | 1328.7921 | 2391.2772 | 66.2193 | 0 | 91.9215 | 481484.4632 | 25210.5187 | 750577.3575 | 811833.0461 | 0 | 107665.9022 | 0 | 848940.8022 | 2208769.8257 | 1507530.7917 | 6742012.7075 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 14031037.3405 | 25250075.0554 | 177827.941 | 0.21526 | 65180.4713 | 117297.9413 | 1328.7921 | 2391.2772
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.8628 | 2.997 | 0.065913 | 4 | 56892.8378 | 99445.315 | 1159.8375 | 2027.3273 | 66.2736 | 0 | 104.363 | 540527.0358 | 28317.7193 | 856038.0227 | 951975.6732 | 0 | 112726.2427 | 0 | 970938.0305 | 2526181.5887 | 1724170.8421 | 7710875.155 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 14999899.7879 | 26218937.5029 | 237137.3706 | 0.26365 | 56892.8378 | 99445.315 | 1159.8375 | 2027.3273
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.6971 | 3.4397 | 0.07843 | 4 | 50745.7843 | 86506.8758 | 1034.5215 | 1763.5597 | 66.313 | 0 | 101.3308 | 595537.3946 | 31210.5901 | 955750.5651 | 1088524.8135 | 0 | 115651.7179 | 0 | 1086803.2817 | 2827639.2049 | 1929921.8595 | 8631039.4272 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 15920064.0602 | 27139101.7751 | 316227.766 | 0.31372 | 50745.7843 | 86506.8758 | 1034.5215 | 1763.5597
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.0561 | 3.8462 | 0.090631 | 4 | 46193.8656 | 77140.8411 | 941.7244 | 1572.6204 | 66.3405 | 0 | 109.9183 | 644217.7298 | 33768.7262 | 1045074.3008 | 1213934.0739 | 0 | 116479.6139 | 0 | 1190855.0334 | 3098360.5189 | 2114694.7191 | 9457384.7159 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 16746409.3488 | 27965447.0638 | 421696.5034 | 0.36252 | 46193.8656 | 77140.8411 | 941.7244 | 1572.6204
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.736 | 4.2011 | 0.10189 | 4 | 42827.0688 | 70355.3422 | 873.0877 | 1434.2888 | 66.3588 | 0 | 111.9386 | 685457.8361 | 35934.371 | 1121504.3272 | 1323419.4416 | 0 | 115616.1046 | 0 | 1279953.5114 | 3330176.4821 | 2272913.8773 | 10164975.9513 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 17454000.5843 | 28673038.2992 | 562341.3252 | 0.40755 | 42827.0688 | 70355.3422 | 873.0877 | 1434.2888
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.6749 | 4.4996 | 0.11181 | 4 | 40336.9081 | 65422.6721 | 822.3224 | 1333.7297 | 66.3705 | 0 | 109.8731 | 719335.1208 | 37712.2229 | 1184793.7381 | 1415533.0524 | 0 | 113681.8207 | 0 | 1353711.8224 | 3522080.4775 | 2403892.2974 | 10750740.5522 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 18039765.1851 | 29258802.9001 | 749894.2093 | 0.44723 | 40336.9081 | 65422.6721 | 822.3224 | 1333.7297
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.866 | 4.7412 | 0.1202 | 4 | 38493.2566 | 61827.5087 | 784.7371 | 1260.4374 | 66.3776 | 0 | 111.3381 | 746261.1953 | 39124.4742 | 1235416.0692 | 1490125.4853 | 0 | 111125.7253 | 0 | 1412600.6502 | 3675297.1276 | 2508465.8094 | 11218416.5365 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 18507441.1695 | 29726478.8844 | 1000000 | 0.4808 | 38493.2566 | 61827.5087 | 784.7371 | 1260.4374
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4166 | 4.9342 | 0.12711 | 4 | 37126.0269 | 59190.8855 | 756.8643 | 1206.6863 | 66.3818 | 0 | 128.9813 | 767465.0695 | 40236.061 | 1275477.3598 | 1549718.0886 | 0 | 108474.0001 | 0 | 1459134.5258 | 3796368.7265 | 2591099.6634 | 11587973.4947 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 18876998.1277 | 30096035.8426 | 1333521.4322 | 0.50846 | 37126.0269 | 59190.8855 | 756.8643 | 1206.6863
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.4091 | 5.0848 | 0.13267 | 4 | 36110.2319 | 57251.2195 | 736.1559 | 1167.1435 | 66.3842 | 0 | 122.3046 | 783841.9832 | 41094.257 | 1306537.0283 | 1596255.8192 | 0 | 105940.8597 | 0 | 1495131.2795 | 3890024.8957 | 2655021.9233 | 11873848.046 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19162872.679 | 30381910.3939 | 1778279.41 | 0.53068 | 36110.2319 | 57251.2195 | 736.1559 | 1167.1435
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.9561 | 5.2017 | 0.13706 | 4 | 35354.1941 | 55817.3177 | 720.7431 | 1137.9115 | 66.3856 | 0 | 114.8895 | 796445.6403 | 41754.5117 | 1330510.418 | 1632373.4853 | 0 | 103709.9105 | 0 | 1522869.6466 | 3962194.4371 | 2704279.1182 | 12094137.1677 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19383161.8006 | 30602199.5156 | 2371373.7057 | 0.54826 | 35354.1941 | 55817.3177 | 720.7431 | 1137.9115
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.1398 | 5.2911 | 0.14049 | 4 | 34790.6033 | 54755.0227 | 709.2535 | 1116.2552 | 66.3863 | 0 | 118.4292 | 806026.178 | 42256.2701 | 1348774.1439 | 1660003.4514 | 0 | 101805.6545 | 0 | 1543957.6222 | 4017061.0236 | 2741726.691 | 12261611.0346 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19550635.6676 | 30769673.3825 | 3162277.6602 | 0.56195 | 34790.6033 | 54755.0227 | 709.2535 | 1116.2552
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.0413 | 5.3592 | 0.14313 | 4 | 34369.9197 | 53965.7462 | 700.6773 | 1100.1647 | 66.3867 | 0 | 129.3315 | 813285.4794 | 42636.3842 | 1362636.1463 | 1681039.8456 | 0 | 100237.1862 | 0 | 1559935.6663 | 4058632.6168 | 2770100.1575 | 12388503.4824 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19677528.1153 | 30896565.8303 | 4216965.0343 | 0.57252 | 34369.9197 | 53965.7462 | 700.6773 | 1100.1647
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.7166 | 5.4102 | 0.14515 | 4 | 34055.5729 | 53379.3244 | 694.2689 | 1088.2097 | 66.3869 | 0 | 116.2451 | 818703.1913 | 42920.0255 | 1372994.6443 | 1696796.1639 | 0 | 98948.5943 | 0 | 1571841.4215 | 4089608.9497 | 2791242.1412 | 12483055.1317 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19772079.7646 | 30991117.4796 | 5623413.2519 | 0.58058 | 34055.5729 | 53379.3244 | 694.2689 | 1088.2097
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.2398 | 5.4497 | 0.1467 | 4 | 33820.4872 | 52940.0212 | 689.4764 | 1079.2539 | 66.387 | 0 | 113.5114 | 822889.084 | 43139.1503 | 1381005.6076 | 1709003.078 | 0 | 97973.3786 | 0 | 1581064.0164 | 4113604.2499 | 2807619.4267 | 12556297.9915 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19845322.6245 | 31064360.3394 | 7498942.0933 | 0.58678 | 33820.4872 | 52940.0212 | 689.4764 | 1079.2539
1 | 2100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.6297 | 5.4791 | 0.14787 | 4 | 33644.5621 | 52612.6764 | 685.8899 | 1072.5806 | 66.387 | 0 | 105.932 | 826001.383 | 43302.0597 | 1386966.2589 | 1718097.868 | 0 | 97196.4197 | 0 | 1587909.9558 | 4131415.9799 | 2819776.2984 | 12610666.2232 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19899690.8562 | 31118728.5711 | 10000000 | 0.59147 | 33644.5621 | 52612.6764 | 685.8899 | 1072.5806
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.8232 | [19 empty] | 100 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.4811 | [19 empty] | 133.3521 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0677 | [19 empty] | 177.8279 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.9378 | [19 empty] | 237.1374 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3468 | [19 empty] | 316.2278 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9881 | [19 empty] | 421.6965 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1392 | [19 empty] | 562.3413 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.989 | [19 empty] | 749.8942 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5053 | [19 empty] | 1000 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4213 | [19 empty] | 1333.5214 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.7564 | [19 empty] | 1778.2794 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.5504 | [19 empty] | 2371.3737 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.8096 | [19 empty] | 3162.2777 | 0
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10322 | 0.00039971 | 4 | 5148758.5649 | 12453919.2459 | 104964.4076 | 253889.989 | 61.6313 | 0 | 35.0945 | 48831.1823 | 2424.497 | 58073.3155 | 58032.817 | 0 | 30849.7803 | 0 | 77302.5209 | 201125.3025 | 137272.1517 | 613911.5671 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8232122.6185 | 19912021.3192 | 4216.965 | 0.0015989 | 5148758.5649 | 12453919.2459 | 104964.4076 | 253889.989
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10323 | 0.0010362 | 4 | 1982827.8743 | 4800802.645 | 40422.6282 | 97870.8555 | 61.6318 | 0 | 214.7903 | 48832.1361 | 2424.552 | 58074.0694 | 58033.1629 | 0 | 26415.3604 | 0 | 75573.9195 | 196627.8362 | 134202.5385 | 600183.5749 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8218394.6262 | 19898293.3269 | 5623.4133 | 0.0041448 | 1982827.8743 | 4800802.645 | 40422.6282 | 97870.8555
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.13365 | 0.0018393 | 4 | 1131777.8135 | 2719286.637 | 23072.8216 | 55436.3362 | 62.938 | 0 | 287.3558 | 59568.4144 | 2992.1247 | 71318.5052 | 67281.1812 | 0 | 27656.5013 | 0 | 89238.5234 | 232180.3327 | 158467.8479 | 708703.4308 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8326914.4821 | 20006813.1828 | 7498.9421 | 0.0073574 | 1131777.8135 | 2719286.637 | 23072.8216 | 55436.3362
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4586 | 0.25288 | 0.0033376 | 4 | 655198.1203 | 1530081.2904 | 13357.0999 | 31192.7767 | 65.4008 | 0 | 68.619 | 95942.3026 | 4928.1377 | 118526.153 | 103244.2451 | 0 | 41823.9603 | 0 | 142141.2715 | 369822.4312 | 252411.4084 | 1128839.9098 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8747050.9612 | 20426949.6619 | 10000 | 0.01335 | 655198.1203 | 1530081.2904 | 13357.0999 | 31192.7767
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5964 | 0.3454 | 0.0051063 | 4 | 442400.3616 | 1014242.8378 | 9018.9298 | 20676.7121 | 66.2569 | 0 | 82.7054 | 120460.0194 | 6238.042 | 151986.9308 | 131037.4701 | 0 | 48047.2245 | 0 | 178530.1779 | 464498.9012 | 317030.0446 | 1417828.8105 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9036039.8619 | 20715938.5626 | 13335.2143 | 0.020425 | 442400.3616 | 1014242.8378 | 9018.9298 | 20676.7121
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0332 | 0.46193 | 0.0074687 | 4 | 313974.7386 | 704935.6061 | 6400.7997 | 14371.0658 | 66.8838 | 0 | 89.878 | 148646.6846 | 7746.7387 | 191673.2146 | 166032.0554 | 0 | 54707.9149 | 0 | 221834.5772 | 577168.0654 | 393929.0643 | 1761738.3152 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9379949.3666 | 21059848.0673 | 17782.7941 | 0.029875 | 313974.7386 | 704935.6061 | 6400.7997 | 14371.0658
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7628 | 0.60198 | 0.010532 | 4 | 231935.9115 | 509178.9004 | 4728.3273 | 10380.3006 | 67.3076 | 0 | 98.9336 | 179653.8989 | 9405.4211 | 236810.9929 | 208119.2295 | 0 | 61128.6792 | 0 | 271096.1065 | 705336.4596 | 481406.6269 | 2152957.4147 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9771168.466 | 21451067.1667 | 23713.7371 | 0.042129 | 231935.9115 | 509178.9004 | 4728.3273 | 10380.3006
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2649 | 0.80642 | 0.014778 | 4 | 174577.2251 | 372161.1166 | 3558.9929 | 7587.0077 | 67.7402 | 0 | 94.0988 | 221392.7844 | 11642.4225 | 299102.0353 | 269335.9576 | 0 | 70809.3781 | 0 | 340190.2054 | 885105.1318 | 604102.4396 | 2701680.3547 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10319891.406 | 21999790.1067 | 31622.7766 | 0.059114 | 174577.2251 | 372161.1166 | 3558.9929 | 7587.0077
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2345 | 1.0483 | 0.020188 | 4 | 135434.2548 | 280073.1144 | 2761.0105 | 5709.6693 | 68.0166 | 0 | 78.3508 | 266676.8497 | 14066.703 | 368856.4964 | 341847.2921 | 0 | 79952.181 | 0 | 417845.8136 | 1087149.0951 | 742001.5961 | 3318396.0271 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10936607.0784 | 22616505.7791 | 42169.6503 | 0.080752 | 135434.2548 | 280073.1144 | 2761.0105 | 5709.6693
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.8808 | 1.3453 | 0.027132 | 4 | 107456.3604 | 215078.666 | 2190.6433 | 4384.6695 | 68.2246 | 0 | 96.0831 | 318139.2212 | 16820.5473 | 450246.5151 | 430878.6028 | 0 | 89484.0713 | 0 | 509171.8935 | 1324760.8213 | 904176.4817 | 4043678.1541 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 11661889.2054 | 23341787.9061 | 56234.1325 | 0.10853 | 107456.3604 | 215078.666 | 2190.6433 | 4384.6695
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3003 | 1.7054 | 0.035894 | 4 | 87110.686 | 168461.2414 | 1775.8692 | 3434.3103 | 68.3825 | 0 | 73.2156 | 376115.4346 | 19920.9319 | 544240.7603 | 538799.6049 | 0 | 99320.9396 | 0 | 615575.0918 | 1601600.1171 | 1093124.9895 | 4888697.8698 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 12506908.9212 | 24186807.6219 | 74989.4209 | 0.14357 | 87110.686 | 168461.2414 | 1775.8692 | 3434.3103
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.741 | 2.0673 | 0.046206 | 4 | 72056.9059 | 135252.0924 | 1468.9775 | 2757.2968 | 68.4875 | 0 | 109.0548 | 430761.7512 | 22841.1594 | 634759.0685 | 647248.7152 | 0 | 104578.8408 | 0 | 717673.9187 | 1867240.3213 | 1274429.8872 | 5699533.6624 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 13317744.7137 | 24997643.4144 | 100000 | 0.18482 | 72056.9059 | 135252.0924 | 1468.9775 | 2757.2968
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.7 | 2.7161 | 0.060524 | 4 | 60960.2708 | 109204.9575 | 1242.7576 | 2226.2908 | 68.6083 | 0 | 54.7515 | 522072.9781 | 27716.1567 | 789568.0921 | 841644.8909 | 0 | 124296.2425 | 0 | 899066.3605 | 2339186.2463 | 1596542.6785 | 7140093.6457 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 14758304.6971 | 26438203.3978 | 133352.1432 | 0.2421 | 60960.2708 | 109204.9575 | 1242.7576 | 2226.2908
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4692 | 3.1049 | 0.073733 | 4 | 52767.6624 | 92369.7811 | 1075.7402 | 1883.0829 | 68.6575 | 0 | 80.2923 | 573646.8867 | 30467.1215 | 878730.8122 | 958145.5305 | 0 | 124061.6949 | 0 | 1000370.2979 | 2602758.3109 | 1776436.0285 | 7944616.6832 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 15562827.7345 | 27242726.4353 | 177827.941 | 0.29493 | 52767.6624 | 92369.7811 | 1075.7402 | 1883.0829
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.7297 | 3.6153 | 0.0891 | 4 | 46617.6368 | 79389.4288 | 950.3636 | 1618.4609 | 68.7065 | 0 | 94.762 | 638527.1189 | 33925.2427 | 992470.5868 | 1111077.0938 | 0 | 128624.9695 | 0 | 1132803.7545 | 2947322.9993 | 2011608.5085 | 8996360.274 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 16614571.3253 | 28294470.026 | 237137.3706 | 0.3564 | 46617.6368 | 79389.4288 | 950.3636 | 1618.4609
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6734 | 4.0999 | 0.10457 | 4 | 42048.3222 | 69970.6622 | 857.2119 | 1426.4466 | 68.741 | 0 | 112.4369 | 697626.2151 | 37072.54 | 1097487.7999 | 1256253.6356 | 0 | 130727.2153 | 0 | 1255475.2883 | 3266489.1667 | 2229445.9759 | 9970577.8367 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 17588788.888 | 29268687.5887 | 316227.766 | 0.4183 | 42048.3222 | 69970.6622 | 857.2119 | 1426.4466
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.9944 | 4.5334 | 0.11926 | 4 | 38660.113 | 63144.8391 | 788.1387 | 1287.293 | 68.7638 | 0 | 100.6131 | 748749.3679 | 39792.792 | 1189357.2951 | 1386175.2746 | 0 | 130551.421 | 0 | 1362904.1988 | 3545997.1551 | 2420215.9213 | 10823743.4258 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 18441954.4772 | 30121853.1779 | 421696.5034 | 0.47703 | 38660.113 | 63144.8391 | 788.1387 | 1287.293
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.5567 | 4.9048 | 0.1325 | 4 | 36150.2775 | 58187.6759 | 736.9723 | 1186.2345 | 68.7779 | 0 | 120.992 | 791382.7708 | 42059.4926 | 1266672.9626 | 1497519.4684 | 0 | 128751.5907 | 0 | 1453290.6512 | 3781164.1635 | 2580722.2367 | 11541563.3366 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19159774.3879 | 30839673.0886 | 562341.3252 | 0.53 | 36150.2775 | 58187.6759 | 736.9723 | 1186.2345
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.3204 | 5.2108 | 0.14393 | 4 | 34290.7294 | 54577.7755 | 699.0629 | 1112.6418 | 68.7861 | 0 | 108.5735 | 825782.7456 | 43887.1186 | 1329514.0708 | 1589316.744 | 0 | 125952.4859 | 0 | 1526636.7343 | 3971995.6265 | 2710968.6314 | 12124054.1573 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19742265.2087 | 31422163.9094 | 749894.2093 | 0.57573 | 34290.7294 | 54577.7755 | 699.0629 | 1112.6418
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.3554 | 5.4574 | 0.15349 | 4 | 32911.454 | 51935.9185 | 670.9445 | 1058.7839 | 68.7906 | 0 | 130.6684 | 853046.537 | 45334.6983 | 1379605.7872 | 1663300.1799 | 0 | 122790.6754 | 0 | 1584990.3723 | 4123819.8225 | 2814591.7649 | 12587479.8373 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20205690.8887 | 31885589.5894 | 1000000 | 0.61394 | 32911.454 | 51935.9185 | 670.9445 | 1058.7839
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.7675 | 5.6532 | 0.16127 | 4 | 31886.8102 | 49992.4592 | 650.0558 | 1019.1639 | 68.7927 | 0 | 103.8819 | 874423.9107 | 46469.1387 | 1419058.8911 | 1722066.2473 | 0 | 119709.9323 | 0 | 1630873.9668 | 4243199.5234 | 2896070.8638 | 12951872.4741 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20570083.5254 | 32249982.2262 | 1333521.4322 | 0.6451 | 31886.8102 | 49992.4592 | 650.0558 | 1019.1639
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.624 | 5.8038 | 0.16745 | 4 | 31124.3533 | 48561.7987 | 634.512 | 989.998 | 68.7936 | 0 | 118.9181 | 890707.3136 | 47332.8862 | 1449214.6364 | 1767273.5719 | 0 | 116808.0511 | 0 | 1665821.2191 | 4334125.1052 | 2958129.4416 | 13229412.2251 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 20847623.2765 | 32527521.9772 | 1778279.41 | 0.66982 | 31124.3533 | 48561.7987 | 634.512 | 989.998
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0707 | 5.921 | 0.17233 | 4 | 30556.1192 | 47500.5051 | 622.9278 | 968.362 | 68.7938 | 0 | 109.6464 | 903297.5563 | 48000.5047 | 1472592.3914 | 1802490.6395 | 0 | 114355.6532 | 0 | 1692887.3306 | 4404545.5752 | 3006192.8595 | 13444362.5104 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21062573.5617 | 32742472.2625 | 2371373.7057 | 0.68931 | 30556.1192 | 47500.5051 | 622.9278 | 968.362
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1714 | 6.0102 | 0.1761 | 4 | 30132.0683 | 46713.4042 | 614.283 | 952.3159 | 68.7936 | 0 | 113.3435 | 912818.5627 | 48505.2373 | 1490306.7418 | 1829274.6742 | 0 | 112286.3043 | 0 | 1713344.6929 | 4457771.4357 | 3042520.6029 | 13606828.2518 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21225039.3032 | 32904938.0039 | 3162277.6602 | 0.7044 | 30132.0683 | 46713.4042 | 614.283 | 952.3159
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.9996 | 6.0773 | 0.17899 | 4 | 29815.2684 | 46128.8595 | 607.8246 | 940.3992 | 68.7934 | 0 | 128.0258 | 919951.2299 | 48883.2805 | 1503597.5457 | 1849425.7455 | 0 | 110573.9474 | 0 | 1728648.3822 | 4497588.4959 | 3069696.5646 | 13728365.1919 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21346576.2433 | 33026474.944 | 4216965.0343 | 0.71596 | 29815.2684 | 46128.8595 | 607.8246 | 940.3992
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.6381 | 6.1289 | 0.18121 | 4 | 29578.3864 | 45691.7682 | 602.9954 | 931.4885 | 68.7931 | 0 | 129.4663 | 925430.3165 | 49173.6356 | 1513818.8006 | 1864955.0389 | 0 | 109250.466 | 0 | 1740425.0205 | 4528228.893 | 3090609.2653 | 13821891.4363 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21440102.4877 | 33120001.1884 | 5623413.2519 | 0.72486 | 29578.3864 | 45691.7682 | 602.9954 | 931.4885
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1056 | 6.1668 | 0.18289 | 4 | 29401.14 | 45367.3021 | 599.382 | 924.8738 | 68.7928 | 0 | 117.7978 | 929432.2204 | 49385.6845 | 1521290.7872 | 1876324.9698 | 0 | 108159.3795 | 0 | 1748991.2861 | 4550516.559 | 3105821.0553 | 13889921.9416 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21508132.9929 | 33188031.6937 | 7498942.0933 | 0.73154 | 29401.14 | 45367.3021 | 599.382 | 924.8738
1 | 2200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.4734 | 6.1965 | 0.18417 | 4 | 29268.445 | 45122.971 | 596.6768 | 919.8928 | 68.7926 | 0 | 126.0869 | 932574.8994 | 49552.1905 | 1527162.304 | 1885269.9293 | 0 | 107368.231 | 0 | 1755751.7462 | 4568105.8893 | 3117826.1346 | 13943611.3243 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21561822.3756 | 33241721.0764 | 10000000 | 0.73669 | 29268.445 | 45122.971 | 596.6768 | 919.8928
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7168 | [19 empty] | 100 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7485 | [19 empty] | 133.3521 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.63 | [19 empty] | 177.8279 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3965 | [19 empty] | 237.1374 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2904 | [19 empty] | 316.2278 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5854 | [19 empty] | 421.6965 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2124 | [19 empty] | 562.3413 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2594 | [19 empty] | 749.8942 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2337 | [19 empty] | 1000 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8016 | [19 empty] | 1333.5214 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.6489 | [19 empty] | 1778.2794 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.214 | [19 empty] | 2371.3737 | 0
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10962 | 9.8888e-05 | 4 | 21753492.2831 | 52467559.9086 | 443474.364 | 1069622.1764 | 63.4098 | 0 | 33.5522 | 52386.5642 | 2631.3976 | 60835.0264 | 59290.685 | 0 | 35154.4069 | 0 | 82016.2512 | 213389.4619 | 145642.6925 | 651346.4857 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8604604.0463 | 20753567.8601 | 3162.2777 | 0.00039555 | 21753492.2831 | 52467559.9086 | 443474.364 | 1069622.1764
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10962 | 0.00092395 | 4 | 2323921.0713 | 5611144.1775 | 47376.2744 | 114390.7637 | 63.4104 | 0 | 32.9926 | 52387.8716 | 2631.4741 | 60836.0462 | 59291.146 | 0 | 30042.1833 | 0 | 80023.6013 | 208204.9955 | 142104.1876 | 635521.5057 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8588779.0664 | 20737742.8801 | 4216.965 | 0.0036958 | 2323921.0713 | 5611144.1775 | 47376.2744 | 114390.7637
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.10962 | 0.0015427 | 4 | 1389623.4601 | 3358410.3743 | 28329.3538 | 68465.7381 | 63.4109 | 0 | 213.4875 | 52388.8534 | 2631.5316 | 60836.8121 | 59291.4923 | 0 | 25613.7536 | 0 | 78297.3528 | 203713.651 | 139038.7527 | 621812.1995 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8575069.7602 | 20724033.5739 | 5623.4133 | 0.0061708 | 1389623.4601 | 3358410.3743 | 28329.3538 | 68465.7381
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0862 | 0.23749 | 0.0032085 | 4 | 704429.2258 | 1651055.3509 | 14360.7426 | 33658.9965 | 67.054 | 0 | 61.0022 | 94143.6319 | 4879.7258 | 112552.4416 | 96909.8286 | 0 | 42586.8274 | 0 | 136918.2576 | 356233.2205 | 243136.4929 | 1087360.4264 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9040617.9871 | 21189581.8008 | 7498.9421 | 0.012834 | 704429.2258 | 1651055.3509 | 14360.7426 | 33658.9965
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1165 | 0.32687 | 0.0050355 | 4 | 462934.6729 | 1066099.8271 | 9437.5495 | 21733.887 | 68.0995 | 0 | 76.2806 | 119103.4218 | 6232.0545 | 145188.0894 | 123061.626 | 0 | 49123.5601 | 0 | 172656.4132 | 449216.5705 | 306599.5398 | 1371181.2754 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9324438.836 | 21473402.6497 | 10000 | 0.020142 | 462934.6729 | 1066099.8271 | 9437.5495 | 21733.887
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4413 | 0.44199 | 0.0074974 | 4 | 322408.6692 | 727514.8598 | 6572.7368 | 14831.3745 | 68.8776 | 0 | 81.6165 | 148319.8759 | 7817.6217 | 184697.9747 | 156700.6305 | 0 | 56387.6912 | 0 | 216030.2797 | 562066.4738 | 383621.9177 | 1715642.4652 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9668900.0258 | 21817863.8395 | 13335.2143 | 0.02999 | 322408.6692 | 727514.8598 | 6572.7368 | 14831.3745
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.064 | 0.58297 | 0.010736 | 4 | 234437.7369 | 517353.0319 | 4779.3304 | 10546.9413 | 69.425 | 0 | 89.2438 | 181002.0903 | 9591.3951 | 230378.3834 | 197886.0376 | 0 | 63675.9174 | 0 | 266188.1913 | 692567.0711 | 472691.2569 | 2113980.3433 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10067237.9039 | 22216201.7176 | 17782.7941 | 0.042942 | 234437.7369 | 517353.0319 | 4779.3304 | 10546.9413
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4218 | 0.78884 | 0.015173 | 4 | 175059.46 | 375235.3212 | 3568.8239 | 7649.6796 | 69.9266 | 0 | 95.1797 | 224748.1212 | 11968.0678 | 293307.3283 | 257896.6092 | 0 | 74571.5281 | 0 | 336371.7453 | 875170.282 | 597321.7004 | 2671355.3824 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10624612.943 | 22773576.7567 | 23713.7371 | 0.060691 | 175059.46 | 375235.3212 | 3568.8239 | 7649.6796
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.036 | 1.0169 | 0.020835 | 4 | 134470.0782 | 280242.6149 | 2741.3544 | 5713.1248 | 70.2456 | 0 | 91.9344 | 269244.2076 | 14384.0232 | 359274.5365 | 324386.2155 | 0 | 83234.4901 | 0 | 409704.1545 | 1065966.168 | 727543.8131 | 3253737.6086 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11206995.1692 | 23355958.9829 | 31622.7766 | 0.083342 | 134470.0782 | 280242.6149 | 2741.3544 | 5713.1248
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4265 | 1.3127 | 0.028208 | 4 | 105755.2661 | 213427.9569 | 2155.9641 | 4351.0176 | 70.4987 | 0 | 121.9536 | 322655.193 | 17282.3337 | 440595.9177 | 410621.4611 | 0 | 93647.4458 | 0 | 501072.917 | 1303688.9458 | 889794.4937 | 3979358.7078 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11932616.2684 | 24081580.0821 | 42169.6503 | 0.11283 | 105755.2661 | 213427.9569 | 2155.9641 | 4351.0176
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5829 | 1.6754 | 0.03761 | 4 | 84990.5201 | 165745.9606 | 1732.6467 | 3378.9556 | 70.6909 | 0 | 102.0935 | 383396.5706 | 20576.025 | 535468.2789 | 516350.209 | 0 | 104571.1882 | 0 | 608541.286 | 1583299.5971 | 1080634.5086 | 4832837.6634 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 12786095.224 | 24935059.0377 | 56234.1325 | 0.15044 | 84990.5201 | 165745.9606 | 1732.6467 | 3378.9556
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.523 | 2.1066 | 0.049322 | 4 | 69753.5152 | 131332.7829 | 1422.0198 | 2677.3964 | 70.8359 | 0 | 107.3083 | 450659.7049 | 24220.2369 | 643053.3155 | 642023.7069 | 0 | 115382.6042 | 0 | 731382.4317 | 1902907.0601 | 1298773.1693 | 5808402.2296 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 13761659.7902 | 25910623.6039 | 74989.4209 | 0.19729 | 69753.5152 | 131332.7829 | 1422.0198 | 2677.3964
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2138 | 2.6034 | 0.063485 | 4 | 58462.1845 | 106303.9768 | 1191.8307 | 2167.1504 | 70.9455 | 0 | 95.3077 | 523230.0301 | 28148.3182 | 761684.6118 | 786812.1155 | 0 | 125532.8958 | 0 | 867909.1088 | 2258121.4685 | 1541214.302 | 6892652.8506 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 14845910.4112 | 26994874.2249 | 100000 | 0.25394 | 58462.1845 | 106303.9768 | 1191.8307 | 2167.1504
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.5083 | 3.1531 | 0.079956 | 4 | 50048.3956 | 88034.6777 | 1020.3042 | 1794.706 | 71.0282 | 0 | 101.7212 | 598852.6736 | 32237.6252 | 887763.14 | 946983.846 | 0 | 134360.5385 | 0 | 1014077.1511 | 2638420.7313 | 1800776.3632 | 8053472.0689 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 16006729.6295 | 28155693.4432 | 133352.1432 | 0.31983 | 50048.3956 | 88034.6777 | 1020.3042 | 1794.706
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.0707 | 3.7262 | 0.098138 | 4 | 43768.1094 | 74716.6851 | 892.2721 | 1523.2007 | 71.0894 | 0 | 104.664 | 673632.0741 | 36277.3485 | 1014618.5683 | 1113988.8856 | 0 | 140914.8988 | 0 | 1161978.3923 | 3023229.4223 | 2063416.2019 | 9228055.7918 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 17181313.3524 | 29330277.1661 | 177827.941 | 0.39255 | 43768.1094 | 74716.6851 | 892.2721 | 1523.2007
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.5091 | 4.2885 | 0.11707 | 4 | 39085.713 | 65029.5125 | 796.8151 | 1325.7146 | 71.133 | 0 | 126.7461 | 743726.165 | 40060.2733 | 1135309.0887 | 1277826.3478 | 0 | 144684.461 | 0 | 1303226.4709 | 3390727.9488 | 2314241.4976 | 10349802.2531 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 18303059.8137 | 30452023.6274 | 237137.3706 | 0.46828 | 39085.713 | 65029.5125 | 796.8151 | 1325.7146
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.4756 | 4.8092 | 0.13565 | 4 | 35603.0455 | 57993.6215 | 725.8162 | 1182.2784 | 71.1622 | 0 | 111.6984 | 806228.7292 | 43430.1827 | 1244287.9346 | 1429602.414 | 0 | 145732.5054 | 0 | 1431019.8887 | 3723220.208 | 2541174.2965 | 11364696.1592 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 19317953.7198 | 31466917.5335 | 316227.766 | 0.54259 | 35603.0455 | 57993.6215 | 725.8162 | 1182.2784
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.7077 | 5.2655 | 0.15286 | 4 | 33017.829 | 52886.6171 | 673.1131 | 1078.1652 | 71.1801 | 0 | 110.4871 | 859326.6665 | 46290.2802 | 1337835.174 | 1562623.6955 | 0 | 144461.2788 | 0 | 1540709.467 | 4008609.9902 | 2735958.687 | 12235815.2393 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 20189072.7999 | 32338036.6136 | 421696.5034 | 0.61146 | 33017.829 | 52886.6171 | 673.1131 | 1078.1652
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.1265 | 5.6503 | 0.1681 | 4 | 31100.2403 | 49168.6151 | 634.0205 | 1002.3687 | 71.1901 | 0 | 119.6776 | 903036.1404 | 48642.5598 | 1415493.0969 | 1674888.1122 | 0 | 141704.7314 | 0 | 1631668.2099 | 4245265.9809 | 2897481.2635 | 12958180.095 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 20911437.6556 | 33060401.4693 | 562341.3252 | 0.67239 | 31100.2403 | 49168.6151 | 634.0205 | 1002.3687
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.7346 | 5.9642 | 0.18105 | 4 | 29677.2762 | 46453.1826 | 605.0114 | 947.011 | 71.195 | 0 | 123.0916 | 938006.6309 | 50523.0381 | 1478043.2687 | 1766485.2246 | 0 | 138157.9195 | 0 | 1704774.2719 | 4435472.9582 | 3027301.4338 | 13538764.7456 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21492022.3062 | 33640986.1199 | 749894.2093 | 0.72419 | 29677.2762 | 46453.1826 | 605.0114 | 947.011
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.6091 | 6.2139 | 0.19172 | 4 | 28620.1376 | 44462.0356 | 583.4602 | 906.4187 | 71.1968 | 0 | 124.535 | 965428.5997 | 51996.6062 | 1527350.7506 | 1839410.1361 | 0 | 134393.4618 | 0 | 1762246.0262 | 4585002.6739 | 3129358.5373 | 13995186.7919 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21948444.3525 | 34097408.1662 | 1000000 | 0.76689 | 28620.1376 | 44462.0356 | 583.4602 | 906.4187
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.8546 | 6.4088 | 0.20031 | 4 | 27833.6309 | 42996.6434 | 567.4262 | 876.5447 | 71.197 | 0 | 123.4099 | 986588.5092 | 53133.0375 | 1565553.7553 | 1896340.5999 | 0 | 130780.0558 | 0 | 1806634.4235 | 4700492.1783 | 3208182.4972 | 14347705.0568 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22300962.6174 | 34449926.4311 | 1333521.4322 | 0.80122 | 27833.6309 | 42996.6434 | 567.4262 | 876.5447
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.6038 | 6.5605 | 0.20711 | 4 | 27247.6114 | 41912.2908 | 555.4794 | 854.4387 | 71.1964 | 0 | 152.2303 | 1002917.3786 | 54009.6164 | 1595127.0652 | 1940664.8438 | 0 | 127606.544 | 0 | 1840926.9248 | 4789714.2322 | 3269078.3823 | 14620044.9873 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22573302.5479 | 34722266.3616 | 1778279.41 | 0.82845 | 27247.6114 | 41912.2908 | 555.4794 | 854.4387
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9487 | 6.677 | 0.21243 | 4 | 26810.3932 | 41108.0584 | 546.5661 | 838.0434 | 71.1956 | 0 | 130.0682 | 1015382.1041 | 54678.5203 | 1617756.2392 | 1974729.4512 | 0 | 124914.179 | 0 | 1867109.5926 | 4857836.1632 | 3315572.9999 | 14827979.2497 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22781236.8103 | 34930200.624 | 2371373.7057 | 0.84972 | 26810.3932 | 41108.0584 | 546.5661 | 838.0434
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.9887 | 6.7671 | 0.21656 | 4 | 26483.8264 | 40508.746 | 539.9086 | 825.8256 | 71.1946 | 0 | 115.7111 | 1024968.5351 | 55192.8215 | 1635191.9551 | 2001063.1417 | 0 | 122749.8486 | 0 | 1887274.8577 | 4910302.0465 | 3351382.0433 | 14988125.2494 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 22941382.81 | 35090346.6238 | 3162277.6602 | 0.86624 | 26483.8264 | 40508.746 | 539.9086 | 825.8256
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.7586 | 6.8337 | 0.2197 | 4 | 26239.6841 | 40064.406 | 534.9315 | 816.7671 | 71.1938 | 0 | 127.6562 | 1032036.2767 | 55571.917 | 1648064.5169 | 2020553.3057 | 0 | 120931.5338 | 0 | 1902091.4445 | 4948851.766 | 3377693.0191 | 15105793.7797 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23059051.3403 | 35208015.154 | 4216965.0343 | 0.87879 | 26239.6841 | 40064.406 | 534.9315 | 816.7671
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.3434 | 6.8843 | 0.22209 | 4 | 26057.0311 | 39732.683 | 531.2078 | 810.0045 | 71.1931 | 0 | 139.316 | 1037387.2826 | 55858.885 | 1657820.4284 | 2035351.8398 | 0 | 119503.3841 | 0 | 1913309.5098 | 4978038.8707 | 3397613.8177 | 15194884.0181 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23148141.5788 | 35297105.3925 | 5623413.2519 | 0.88836 | 26057.0311 | 39732.683 | 531.2078 | 810.0045
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.7844 | 6.9225 | 0.22391 | 4 | 25920.3039 | 39484.9332 | 528.4205 | 804.9538 | 71.1925 | 0 | 141.0325 | 1041413.678 | 56074.7894 | 1665167.0401 | 2046511.2216 | 0 | 118388.1847 | 0 | 1921746.4164 | 4999989.971 | 3412595.8947 | 15261887.1958 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23215144.7564 | 35364108.5701 | 7498942.0933 | 0.89564 | 25920.3039 | 39484.9332 | 528.4205 | 804.9538
1 | 2300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1204 | 6.9516 | 0.22529 | 4 | 25817.9107 | 39299.3294 | 526.333 | 801.17 | 71.192 | 0 | 128.2053 | 1044476.0344 | 56238.9844 | 1670757.9431 | 2055012.5929 | 0 | 117540.8734 | 0 | 1928170.307 | 5016703.6167 | 3424003.3013 | 15312903.6532 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23266161.2138 | 35415125.0275 | 10000000 | 0.90116 | 25817.9107 | 39299.3294 | 526.333 | 801.17
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.3562 | [19 empty] | 100 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.6448 | [19 empty] | 133.3521 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2268 | [19 empty] | 177.8279 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3931 | [19 empty] | 237.1374 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2575 | [19 empty] | 316.2278 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.76 | [19 empty] | 421.6965 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6645 | [19 empty] | 562.3413 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.668 | [19 empty] | 749.8942 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8818 | [19 empty] | 1000 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.6434 | [19 empty] | 1333.5214 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.1569 | [19 empty] | 1778.2794 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9311 | [19 empty] | 2371.3737 | 0
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.11607 | 0.00066675 | 4 | 3362213.4854 | 8096482.4467 | 68543.2696 | 165057.746 | 65.163 | 0 | 33.555 | 55974.3114 | 2843.4503 | 63582.9969 | 60525.7238 | 0 | 34303.0608 | 0 | 84719.5218 | 220422.8174 | 150443.1021 | 672814.9845 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 8966979.1453 | 21593212.1992 | 3162.2777 | 0.002667 | 3362213.4854 | 8096482.4467 | 68543.2696 | 165057.746
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.15265 | 0.0016149 | 4 | 1408389.6189 | 3362988.6877 | 28711.9274 | 68559.0732 | 66.7541 | 0 | 299.258 | 69151.9864 | 3559.0826 | 79052.4816 | 71062.584 | 0 | 36658.3081 | 0 | 101198.9327 | 263298.864 | 179706.885 | 803689.1244 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9097853.2852 | 21724086.3391 | 4216.965 | 0.0064598 | 1408389.6189 | 3362988.6877 | 28711.9274 | 68559.0732
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7204 | 0.21859 | 0.0029418 | 4 | 792646.072 | 1865659.5303 | 16159.1623 | 38033.993 | 68.5054 | 0 | 78.7589 | 90762.3026 | 4740.5768 | 105192.2726 | 89955.5275 | 0 | 42858.9795 | 0 | 130068.767 | 338412.2509 | 230973.3149 | 1032963.9918 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9327128.1526 | 21953361.2065 | 5623.4133 | 0.011767 | 792646.072 | 1865659.5303 | 16159.1623 | 38033.993
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.30502 | 0.0047826 | 4 | 502208.0867 | 1162219.8626 | 10238.1911 | 23693.4239 | 69.8028 | 0 | 74.3651 | 116243.433 | 6139.442 | 137164.9747 | 114618.0634 | 0 | 49833.8004 | 0 | 165359.8883 | 430232.5093 | 293642.528 | 1313234.6391 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9607398.7998 | 22233631.8537 | 7498.9421 | 0.01913 | 502208.0867 | 1162219.8626 | 10238.1911 | 23693.4239
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8398 | 0.41476 | 0.0072787 | 4 | 341442.308 | 775113.6483 | 6960.7633 | 15801.7401 | 70.7507 | 0 | 78.6378 | 145560.3807 | 7752.2747 | 175248.2272 | 145860.7542 | 0 | 57289.2927 | 0 | 207367.2626 | 539527.0803 | 368238.3185 | 1646843.591 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9941007.7517 | 22567240.8056 | 10000 | 0.029115 | 341442.308 | 775113.6483 | 6960.7633 | 15801.7401
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3427 | 0.5543 | 0.010608 | 4 | 243728.4939 | 541306.2798 | 4968.735 | 11035.2607 | 71.4499 | 0 | 103.8072 | 179536.8669 | 9622.5563 | 220876.1914 | 185547.1608 | 0 | 65403.4802 | 0 | 257784.6397 | 670702.7535 | 457768.4108 | 2047242.0595 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10341406.2203 | 22967639.2742 | 13335.2143 | 0.04243 | 243728.4939 | 541306.2798 | 4968.735 | 11035.2607
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1332 | 0.71992 | 0.014894 | 4 | 181119.9442 | 393050.18 | 3692.375 | 8012.8596 | 71.9099 | 0 | 103.5218 | 216476.8878 | 11653.6637 | 272147.3937 | 232707.205 | 0 | 73043.3404 | 0 | 314351.1114 | 817877.1095 | 558217.9329 | 2496474.6444 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10790638.8052 | 23416871.8591 | 17782.7941 | 0.059577 | 181119.9442 | 393050.18 | 3692.375 | 8012.8596
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.823 | 0.97153 | 0.020944 | 4 | 136645.5234 | 287356.985 | 2785.7038 | 5858.1608 | 72.4238 | 0 | 97.0021 | 268314.1422 | 14511.5052 | 345739.0035 | 304024.9746 | 0 | 85621.936 | 0 | 397102.509 | 1033179.2714 | 705166.0825 | 3153659.4243 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 11447823.5851 | 24074056.639 | 23713.7371 | 0.083778 | 136645.5234 | 287356.985 | 2785.7038 | 5858.1608
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9339 | 1.2613 | 0.02858 | 4 | 106403.8319 | 216849.0554 | 2169.186 | 4420.7613 | 72.7335 | 0 | 80.5254 | 322987.5902 | 17520.1189 | 425911.4094 | 386287.0158 | 0 | 96804.7438 | 0 | 487309.2425 | 1267878.6881 | 865353.2569 | 3870052.0657 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 12164216.2265 | 24790449.2804 | 31622.7766 | 0.11432 | 106403.8319 | 216849.0554 | 2169.186 | 4420.7613
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7628 | 1.618 | 0.038392 | 4 | 84708.4062 | 166928.5421 | 1726.8954 | 3403.0641 | 72.9676 | 0 | 130.4005 | 385308.6765 | 20946.8817 | 519721.0466 | 487548.6206 | 0 | 108527.4372 | 0 | 593600.5384 | 1544426.8368 | 1054103.0509 | 4714183.0888 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 13008347.2495 | 25634580.3034 | 42169.6503 | 0.15357 | 84708.4062 | 166928.5421 | 1726.8954 | 3403.0641
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4038 | 2.0505 | 0.050778 | 4 | 68879.7788 | 131043.3748 | 1404.2075 | 2671.4964 | 73.1455 | 0 | 123.8581 | 455519.0949 | 24803.473 | 628053.9775 | 610159.6158 | 0 | 120581.1714 | 0 | 717255.7597 | 1866152.3573 | 1273687.3295 | 5696212.7791 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 13990376.9399 | 26616609.9937 | 56234.1325 | 0.20311 | 68879.7788 | 131043.3748 | 1404.2075 | 2671.4964
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.8897 | 2.5617 | 0.066059 | 4 | 57176.7242 | 104960.3204 | 1165.6249 | 2139.7581 | 73.2809 | 0 | 111.3479 | 533018.552 | 29056.0153 | 750394.8913 | 755075.929 | 0 | 132496.7738 | 0 | 858016.4429 | 2232382.7812 | 1523647.119 | 6814088.5045 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 15108252.6652 | 27734485.7191 | 74989.4209 | 0.26424 | 57176.7242 | 104960.3204 | 1165.6249 | 2139.7581
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0964 | 3.1403 | 0.084251 | 4 | 48454.3723 | 85920.3577 | 987.8079 | 1751.6027 | 73.383 | 0 | 142.8795 | 615341.1878 | 33568.3866 | 883082.8178 | 919052.1814 | 0 | 143257.9325 | 0 | 1011777.9774 | 2632438.753 | 1796693.5402 | 8035212.7768 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 16329376.9376 | 28955609.9915 | 100000 | 0.33701 | 48454.3723 | 85920.3577 | 987.8079 | 1751.6027
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.8003 | 3.7653 | 0.10498 | 4 | 41929.5183 | 71998.0205 | 854.7899 | 1467.777 | 73.4594 | 0 | 119.2499 | 699349.3705 | 38168.183 | 1021027.7135 | 1096178.4161 | 0 | 152035.1399 | 0 | 1172635.941 | 3050958.1777 | 2082341.6472 | 9312694.5887 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 17606858.7495 | 30233091.8034 | 133352.1432 | 0.41992 | 41929.5183 | 71998.0205 | 854.7899 | 1467.777
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.6339 | 4.4024 | 0.12735 | 4 | 37048.2168 | 61835.4352 | 755.278 | 1260.599 | 73.515 | 0 | 103.2273 | 780812.1806 | 42623.7668 | 1156985.9329 | 1276728.4549 | 0 | 158015.7669 | 0 | 1331914.7799 | 3465369.0439 | 2365185.5787 | 10577635.5046 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 18871799.6653 | 31498032.7192 | 177827.941 | 0.50938 | 37048.2168 | 61835.4352 | 755.278 | 1260.599
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.1696 | 5.0115 | 0.15005 | 4 | 33404.7757 | 54440.9754 | 681.0015 | 1109.8529 | 73.5529 | 0 | 134.6915 | 855456.0867 | 46701.8786 | 1283311.7274 | 1449363.6214 | 0 | 160744.8649 | 0 | 1480275.4898 | 3851373.1783 | 2628641.332 | 11755868.1791 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 20050032.3398 | 32676265.3937 | 237137.3706 | 0.60021 | 33404.7757 | 54440.9754 | 681.0015 | 1109.8529
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1035 | 5.5639 | 0.17183 | 4 | 30692.7018 | 49063.4376 | 625.7122 | 1000.2245 | 73.5765 | 0 | 108.7071 | 920833.6097 | 50269.7475 | 1395260.3205 | 1606023.4658 | 0 | 160620.8337 | 0 | 1611873.1111 | 4193763.1945 | 2862329.5535 | 12800973.8365 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 21095137.9972 | 33721371.0511 | 316227.766 | 0.6873 | 30692.7018 | 49063.4376 | 625.7122 | 1000.2245
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2165 | 6.0393 | 0.19159 | 4 | 28677.5204 | 45153.3165 | 584.63 | 920.5114 | 73.5895 | 0 | 156.9154 | 975527.1479 | 53251.3395 | 1489824.6943 | 1740914.0842 | 0 | 158224.0685 | 0 | 1722919.1204 | 4482682.1321 | 3059522.665 | 13682865.252 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 21977029.4127 | 34603262.4666 | 421696.5034 | 0.76635 | 28677.5204 | 45153.3165 | 584.63 | 920.5114
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4554 | 6.4328 | 0.20874 | 4 | 27180.858 | 42302.7999 | 554.1186 | 862.3998 | 73.5953 | 0 | 153.84 | 1019808.9083 | 55662.9624 | 1566986.6784 | 1852654.9993 | 0 | 154423.2331 | 0 | 1813319.3448 | 4717884.9722 | 3220053.4364 | 14400794.5349 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 22694958.6957 | 35321191.7496 | 562341.3252 | 0.83496 | 27180.858 | 42302.7999 | 554.1186 | 862.3998
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.9003 | 6.7522 | 0.22316 | 4 | 26068.6672 | 40213.5235 | 531.445 | 819.8071 | 73.597 | 0 | 122.0316 | 1055128.3318 | 57584.8375 | 1628913.9756 | 1943393.7733 | 0 | 150137.8923 | 0 | 1885711.9361 | 4906235.645 | 3348606.6408 | 14975713.0323 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23269877.1931 | 35896110.247 | 749894.2093 | 0.89264 | 26068.6672 | 40213.5235 | 531.445 | 819.8071
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.6233 | 7.0043 | 0.23492 | 4 | 25241.244 | 38678.1042 | 514.5769 | 788.5055 | 73.5964 | 0 | 179.9043 | 1082641.0316 | 59080.8377 | 1677388.1272 | 2015066.335 | 0 | 145819.7194 | 0 | 1942198.4598 | 5053201.9928 | 3448914.193 | 15424310.6964 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23718474.8572 | 36344707.9111 | 1000000 | 0.93967 | 25241.244 | 38678.1042 | 514.5769 | 788.5055
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.7575 | 7.2016 | 0.24433 | 4 | 24624.8578 | 37543.9713 | 502.011 | 765.3846 | 73.5947 | 0 | 158.5796 | 1103963.6823 | 60239.5744 | 1715097.6056 | 2071209.396 | 0 | 141885.2271 | 0 | 1986034.2393 | 5167253.699 | 3526756.826 | 15772440.2498 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24066604.4105 | 36692837.4644 | 1333521.4322 | 0.97733 | 24624.8578 | 37543.9713 | 502.011 | 765.3846
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.3971 | 7.3531 | 0.25172 | 4 | 24165.0907 | 36704.8992 | 492.6381 | 748.279 | 73.5928 | 0 | 148.4518 | 1120202.9958 | 61121.655 | 1743900.0807 | 2114317.1602 | 0 | 138423.7698 | 0 | 2019406.608 | 5254081.7567 | 3586018.7596 | 16037472.7858 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24331636.9466 | 36957870.0005 | 1778279.41 | 1.0069 | 24165.0907 | 36704.8992 | 492.6381 | 748.279
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.6493 | 7.4687 | 0.25746 | 4 | 23821.7577 | 36082.1246 | 485.6388 | 735.5829 | 73.5909 | 0 | 144.5257 | 1132525.4293 | 61790.736 | 1765803.408 | 2147229.08 | 0 | 135511.4614 | 0 | 2044715.4447 | 5319930.1583 | 3630961.6467 | 16238467.3644 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24532631.5251 | 37158864.579 | 2371373.7057 | 1.0298 | 23821.7577 | 36082.1246 | 485.6388 | 735.5829
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.6085 | 7.5572 | 0.26189 | 4 | 23565.1302 | 35618.1346 | 480.4071 | 726.1239 | 73.5893 | 0 | 182.7595 | 1141916.7012 | 62300.5174 | 1782524.3528 | 2172429.0758 | 0 | 133163.1485 | 0 | 2064010.1803 | 5370131.1025 | 3665224.8226 | 16391699.9011 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24685864.0618 | 37312097.1157 | 3162277.6602 | 1.0476 | 23565.1302 | 35618.1346 | 480.4071 | 726.1239
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.3271 | 7.6235 | 0.26526 | 4 | 23373.166 | 35272.9573 | 476.4936 | 719.0869 | 73.5879 | 0 | 156.1789 | 1148927.0291 | 62680.9729 | 1795021.7804 | 2191306.1488 | 0 | 131254.417 | 0 | 2078384.2358 | 5407529.4463 | 3690749.9607 | 16505853.9909 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24800018.1517 | 37426251.2056 | 4216965.0343 | 1.061 | 23373.166 | 35272.9573 | 476.4936 | 719.0869
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.8756 | 7.674 | 0.26784 | 4 | 23229.4862 | 35014.8143 | 473.5645 | 713.8244 | 73.5868 | 0 | 161.0982 | 1154261.7813 | 62970.446 | 1804541.1282 | 2205709.1075 | 0 | 129776.294 | 0 | 2089330.9152 | 5436010.4607 | 3710188.8383 | 16592788.9713 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24886953.132 | 37513186.1859 | 5623413.2519 | 1.0714 | 23229.4862 | 35014.8143 | 473.5645 | 713.8244
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.2823 | 7.7115 | 0.26978 | 4 | 23121.8966 | 34822.473 | 471.3711 | 709.9032 | 73.586 | 0 | 153.926 | 1158209.8682 | 63184.6494 | 1811591.1199 | 2216389.3466 | 0 | 128600.2887 | 0 | 2097410.3564 | 5457031.5093 | 3724536.1359 | 16656953.2744 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 24951117.4352 | 37577350.4891 | 7498942.0933 | 1.0791 | 23121.8966 | 34822.473 | 471.3711 | 709.9032
1 | 2400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.5964 | 7.7405 | 0.27126 | 4 | 23041.3033 | 34677.9522 | 469.7281 | 706.957 | 73.5853 | 0 | 177.7152 | 1161254.1604 | 63349.8019 | 1817030.1395 | 2224636.8896 | 0 | 127726.6179 | 0 | 2103659.0676 | 5473289.374 | 3735632.4626 | 16706578.5133 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 25000742.6741 | 37626975.728 | 10000000 | 1.085 | 23041.3033 | 34677.9522 | 469.7281 | 706.957
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.465 | [19 empty] | 100 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0513 | [19 empty] | 133.3521 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1197 | [19 empty] | 177.8279 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5651 | [19 empty] | 237.1374 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4556 | [19 empty] | 316.2278 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2433 | [19 empty] | 421.6965 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0474 | [19 empty] | 562.3413 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6625 | [19 empty] | 749.8942 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7779 | [19 empty] | 1000 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7442 | [19 empty] | 1333.5214 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8006 | [19 empty] | 1778.2794 | 0
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.12252 | 0.00018679 | 4 | 12519230.6077 | 30068352.7099 | 255221.4495 | 612984.0404 | 66.8898 | 0 | 34.7827 | 59580.2935 | 3060.0325 | 66294.3184 | 61727.0834 | 0 | 39453.9395 | 0 | 89745.1102 | 233498.3675 | 159367.4337 | 712726.5787 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9353657.4304 | 22465363.8517 | 2371.3737 | 0.00074714 | 12519230.6077 | 30068352.7099 | 255221.4495 | 612984.0404
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.13307 | 0.0012719 | 4 | 1843317.7335 | 4420420.6319 | 37578.5253 | 90116.2536 | 67.4299 | 0 | 242.6844 | 63547.9714 | 3278.0116 | 70789.2254 | 64701.6234 | 0 | 35779.7622 | 0 | 92857.6717 | 241596.6139 | 164894.6533 | 737445.5329 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9378376.3847 | 22490082.806 | 3162.2777 | 0.0050878 | 1843317.7335 | 4420420.6319 | 37578.5253 | 90116.2536
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.18966 | 0.0025425 | 4 | 942037.8638 | 2231285.7548 | 19204.7161 | 45487.7781 | 69.4991 | 0 | 341.7275 | 83437.3453 | 4376.5089 | 93814.136 | 80572.7819 | 0 | 41175.9616 | 0 | 118316.9262 | 307836.3717 | 210104.6491 | 939634.6807 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9580565.5325 | 22692271.9538 | 4216.965 | 0.01017 | 942037.8638 | 2231285.7548 | 19204.7161 | 45487.7781
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.164 | 0.27496 | 0.0043189 | 4 | 571165.8735 | 1330136.0685 | 11643.9889 | 27116.6229 | 71.25 | 0 | 64.3077 | 110294.1196 | 5868.7161 | 126080.1245 | 104356.4077 | 0 | 49342.7367 | 0 | 154417.4208 | 401762.4535 | 274211.1299 | 1226333.1087 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9867263.9605 | 22978970.3817 | 5623.4133 | 0.017276 | 571165.8735 | 1330136.0685 | 11643.9889 | 27116.6229
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2286 | 0.37988 | 0.0067815 | 4 | 375802.9334 | 859166.4196 | 7661.2511 | 17515.2696 | 72.4532 | 0 | 94.712 | 140001.7046 | 7524.5903 | 163114.1239 | 133505.3341 | 0 | 57295.4507 | 0 | 195562.0694 | 508812.3893 | 347274.9107 | 1553090.5731 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10194021.4248 | 23305727.8461 | 7498.9421 | 0.027126 | 375802.9334 | 859166.4196 | 7661.2511 | 17515.2696
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4802 | 0.50346 | 0.010118 | 4 | 260741.6425 | 584698.4433 | 5315.5711 | 11919.8686 | 73.2873 | 0 | 101.2238 | 171888.4821 | 9304.274 | 204186.686 | 167727.788 | 0 | 64287.7712 | 0 | 240784.0505 | 626470.7078 | 427579.1308 | 1912228.8904 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10553159.7421 | 23664866.1634 | 10000 | 0.040474 | 260741.6425 | 584698.4433 | 5315.5711 | 11919.8686
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2661 | 0.67958 | 0.014521 | 4 | 190121.4682 | 415865.7931 | 3875.8833 | 8477.9867 | 73.968 | 0 | 74.458 | 213351.0332 | 11617.4052 | 259416.591 | 216379.7997 | 0 | 74672.1348 | 0 | 302420.4159 | 786835.8873 | 537031.6609 | 2401724.928 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11042655.7797 | 24154362.201 | 13335.2143 | 0.058082 | 190121.4682 | 415865.7931 | 3875.8833 | 8477.9867
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6218 | 0.91349 | 0.020517 | 4 | 142080.4907 | 301849.291 | 2896.503 | 6153.6061 | 74.5368 | 0 | 82.8839 | 263804.6544 | 14436.2729 | 328515.7449 | 281036.1195 | 0 | 86991.2742 | 0 | 380165.7857 | 989113.3917 | 675090.2141 | 3019153.4574 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11660084.3092 | 24771790.7304 | 17782.7941 | 0.082067 | 142080.4907 | 301849.291 | 2896.503 | 6153.6061
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4381 | 1.1927 | 0.028247 | 4 | 109374.6693 | 225420.7395 | 2229.7506 | 4595.5067 | 74.9179 | 0 | 95.0369 | 319019.9423 | 17517.5099 | 406510.5154 | 358259.2169 | 0 | 98786.1721 | 0 | 468036.4091 | 1217734.7289 | 831128.9744 | 3716993.4689 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 12357924.3206 | 25469630.7419 | 23713.7371 | 0.11299 | 109374.6693 | 225420.7395 | 2229.7506 | 4595.5067
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8823 | 1.5338 | 0.038174 | 4 | 86248.6368 | 172116.3901 | 1758.2951 | 3508.8254 | 75.2026 | 0 | 101.7671 | 381329.5814 | 20990.1872 | 497005.6109 | 452073.0772 | 0 | 110843.817 | 0 | 570274.4868 | 1483737.2351 | 1012681.1507 | 4528935.1464 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 13169865.9981 | 26281572.4194 | 31622.7766 | 0.1527 | 86248.6368 | 172116.3901 | 1758.2951 | 3508.8254
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1749 | 1.9588 | 0.050881 | 4 | 69476.002 | 133899.2463 | 1416.3623 | 2729.7172 | 75.4231 | 0 | 90.347 | 453364.9353 | 25000.4004 | 604323.3285 | 568748.1771 | 0 | 124050.7617 | 0 | 692440.1652 | 1801587.2709 | 1229620.3313 | 5499135.3706 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 14140066.2223 | 27251772.6436 | 42169.6503 | 0.20352 | 69476.002 | 133899.2463 | 1416.3623 | 2729.7172
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3339 | 2.4698 | 0.066804 | 4 | 57109.5524 | 106177.4414 | 1164.2555 | 2164.5708 | 75.5908 | 0 | 119.6591 | 534005.2606 | 29484.7634 | 727341.1208 | 708979.5316 | 0 | 137448.4951 | 0 | 833531.0769 | 2168676.8814 | 1480166.5334 | 6619633.6633 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 15260564.5151 | 28372270.9364 | 56234.1325 | 0.26722 | 57109.5524 | 106177.4414 | 1164.2555 | 2164.5708
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.3003 | 3.0608 | 0.086162 | 4 | 47900.4344 | 85944.1902 | 976.5151 | 1752.0886 | 75.7173 | 0 | 80.7409 | 621298.7238 | 34333.5088 | 863449.9069 | 871169.9188 | 0 | 150018.0425 | 0 | 990705.3393 | 2577612.0712 | 1759273.2033 | 7867860.7146 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 16508791.5663 | 29620497.9876 | 74989.4209 | 0.34465 | 47900.4344 | 85944.1902 | 976.5151 | 1752.0886
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.9823 | 3.7229 | 0.1089 | 4 | 41002.6477 | 71103.9179 | 835.8944 | 1449.5495 | 75.8133 | 0 | 96.8158 | 713320.1793 | 39438.8682 | 1009802.564 | 1052824.1579 | 0 | 161208.7892 | 0 | 1160871.8778 | 3020350.4986 | 2061451.2773 | 9219268.2123 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 17860199.0641 | 30971905.4854 | 100000 | 0.43559 | 41002.6477 | 71103.9179 | 835.8944 | 1449.5495
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0392 | 4.4221 | 0.13428 | 4 | 35826.721 | 60237.8379 | 730.3762 | 1228.0298 | 75.8841 | 0 | 104.4326 | 805376.5257 | 44540.1239 | 1158815.4057 | 1244674.5648 | 0 | 169731.9659 | 0 | 1335024.0485 | 3473458.7232 | 2370706.951 | 10602328.3087 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 19243259.1605 | 32354965.5818 | 133352.1432 | 0.53712 | 35826.721 | 60237.8379 | 730.3762 | 1228.0298
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0696 | 5.1185 | 0.16106 | 4 | 31948.5384 | 52300.8518 | 651.3142 | 1066.2236 | 75.934 | 0 | 124.7201 | 892847.176 | 49381.4226 | 1302595.6506 | 1435784.7281 | 0 | 174899.9474 | 0 | 1503648.4806 | 3912184.9058 | 2670146.5856 | 11941488.8966 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 20582419.7484 | 33694126.1697 | 177827.941 | 0.64424 | 31948.5384 | 52300.8518 | 651.3142 | 1066.2236
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.664 | 5.7712 | 0.18765 | 4 | 29051.6251 | 46519.5703 | 592.2567 | 948.3644 | 75.9659 | 0 | 125.9627 | 971641.3446 | 53737.0989 | 1433825.8092 | 1614992.0303 | 0 | 176557.5351 | 0 | 1657793.989 | 4313239.8991 | 2943874.8594 | 13165662.5654 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 21806593.4172 | 34918299.8385 | 237137.3706 | 0.75062 | 29051.6251 | 46519.5703 | 592.2567 | 948.3644
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5003 | 6.3481 | 0.21255 | 4 | 26893.7394 | 42315.6471 | 548.2653 | 862.6617 | 75.9837 | 0 | 117.934 | 1039065.5963 | 57459.6644 | 1547360.1331 | 1773524.2575 | 0 | 175087.198 | 0 | 1791073.7712 | 4660006.553 | 3180550.226 | 14224127.3994 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 22865058.2512 | 35976764.6725 | 316227.766 | 0.8502 | 26893.7394 | 42315.6471 | 548.2653 | 862.6617
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4749 | 6.839 | 0.23478 | 4 | 25288.8158 | 39250.3846 | 515.5467 | 800.1722 | 75.9917 | 0 | 141.0257 | 1094977.3579 | 60543.0223 | 1642360.0775 | 1908574.3309 | 0 | 171581.4736 | 0 | 1902434.1423 | 4949743.3953 | 3378301.5743 | 15108515.3741 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 23749446.2259 | 36861152.6472 | 421696.5034 | 0.93913 | 25288.8158 | 39250.3846 | 515.5467 | 800.1722
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.5575 | 7.2412 | 0.25381 | 4 | 24095.4423 | 37010.3122 | 491.2182 | 754.5053 | 75.9936 | 0 | 148.494 | 1139867.0598 | 63015.9692 | 1719186.3158 | 2019346.7846 | 0 | 166900.4636 | 0 | 1992243.4713 | 5183408.847 | 3537783.0465 | 15821751.9578 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 24462682.8096 | 37574389.2309 | 562341.3252 | 1.0152 | 24095.4423 | 37010.3122 | 491.2182 | 754.5053
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.8413 | 7.5642 | 0.26961 | 4 | 23207.5122 | 35365.3991 | 473.1165 | 720.9715 | 75.9922 | 0 | 146.3002 | 1175353.7559 | 64969.1676 | 1780268.0421 | 2108394.5336 | 0 | 161919.3523 | 0 | 2063452.8921 | 5368681.1527 | 3664235.2021 | 16387274.0983 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25028204.9501 | 38139911.3714 | 749894.2093 | 1.0785 | 23207.5122 | 35365.3991 | 473.1165 | 720.9715
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.4165 | 7.8172 | 0.28238 | 4 | 22546.1349 | 34154.408 | 459.6335 | 696.2838 | 75.9893 | 0 | 135.9797 | 1202813.2315 | 66479.4325 | 1827743.8744 | 2178197.2117 | 0 | 157076.6853 | 0 | 2118601.0698 | 5512165.3988 | 3762166.1484 | 16825243.0523 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25466173.9041 | 38577880.3254 | 1000000 | 1.1295 | 22546.1349 | 34154.408 | 459.6335 | 696.2838
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.4233 | 8.0141 | 0.29253 | 4 | 22052.9197 | 33258.5152 | 449.5786 | 678.0198 | 75.986 | 0 | 163.3023 | 1223991.1436 | 67643.5234 | 1864485.1393 | 2232568.3799 | 0 | 152759.0667 | 0 | 2161164.4286 | 5622906.5275 | 3837749.2442 | 17163267.4531 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 25804198.3049 | 38915904.7262 | 1333521.4322 | 1.1701 | 22052.9197 | 33258.5152 | 449.5786 | 678.0198
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9682 | 8.1655 | 0.30047 | 4 | 21684.6975 | 32594.0433 | 442.0719 | 664.4737 | 75.9828 | 0 | 133.2987 | 1240167.1779 | 68532.2586 | 1892622.6782 | 2274413.3958 | 0 | 149066.167 | 0 | 2193672.6542 | 5707486.2622 | 3895476.6511 | 17421437.245 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26062368.0968 | 39174074.5181 | 1778279.41 | 1.2019 | 21684.6975 | 32594.0433 | 442.0719 | 664.4737
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.1325 | 8.2796 | 0.30658 | 4 | 21409.5259 | 32101.2683 | 436.4621 | 654.4278 | 75.9801 | 0 | 119.2966 | 1252285.4151 | 69197.8109 | 1913743.888 | 2305940.8932 | 0 | 145940.5082 | 0 | 2217972.321 | 5770709.0106 | 3938627.4759 | 17614417.3229 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26255348.1747 | 39367054.596 | 2371373.7057 | 1.2263 | 21409.5259 | 32101.2683 | 436.4621 | 654.4278
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.0339 | 8.3678 | 0.31132 | 4 | 21203.7274 | 31732.9357 | 432.2667 | 646.9188 | 75.9778 | 0 | 125.628 | 1261625.7312 | 69710.6521 | 1930047.9796 | 2330346.2268 | 0 | 143490.2007 | 0 | 2236736.1083 | 5819528.5361 | 3971947.8052 | 17763433.2401 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26404364.0919 | 39516070.5132 | 3162277.6602 | 1.2453 | 21203.7274 | 31732.9357 | 432.2667 | 646.9188
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.7159 | 8.4345 | 0.31493 | 4 | 21049.7153 | 31458.1888 | 429.1269 | 641.3177 | 75.9759 | 0 | 160.6353 | 1268667.5901 | 70097.2102 | 1942354.1514 | 2348806.4724 | 0 | 141543.7362 | 0 | 2250872.9725 | 5856309.7569 | 3997051.7442 | 17875703.6338 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26516634.4856 | 39628340.9069 | 4216965.0343 | 1.2597 | 21049.7153 | 31458.1888 | 429.1269 | 641.3177
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.2176 | 8.4836 | 0.31764 | 4 | 20934.4016 | 31253.9225 | 426.7761 | 637.1535 | 75.9745 | 0 | 129.1635 | 1273835.5613 | 70380.8563 | 1951393.3325 | 2362387.4961 | 0 | 139964.5747 | 0 | 2261205.1102 | 5883191.8597 | 4015399.3318 | 17957758.1225 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26598688.9743 | 39710395.3956 | 5623413.2519 | 1.2706 | 20934.4016 | 31253.9225 | 426.7761 | 637.1535
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6197 | 8.523 | 0.31975 | 4 | 20848.0297 | 31099.4793 | 425.0153 | 634.005 | 75.9733 | 0 | 128.7748 | 1277968.9521 | 70607.6909 | 1958627.6747 | 2373269.9174 | 0 | 138844.9956 | 0 | 2269534.5 | 5904863.2234 | 4030190.4828 | 18023907.437 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26664838.2888 | 39776544.71 | 7498942.0933 | 1.279 | 20848.0297 | 31099.4793 | 425.0153 | 634.005
1 | 2500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.9 | 8.5504 | 0.3213 | 4 | 20783.3172 | 30985.5264 | 423.696 | 631.6819 | 75.9724 | 0 | 147.206 | 1280845.5935 | 70765.5419 | 1963664.9223 | 2380854.2017 | 0 | 137888.6698 | 0 | 2275267.3824 | 5919779.0075 | 4040370.8119 | 18069436.1311 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26710366.9828 | 39822073.4041 | 10000000 | 1.2852 | 20783.3172 | 30985.5264 | 423.696 | 631.6819
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.9031 | [19 empty] | 100 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.759 | [19 empty] | 133.3521 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.977 | [19 empty] | 177.8279 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5667 | [19 empty] | 237.1374 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2847 | [19 empty] | 316.2278 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6936 | [19 empty] | 421.6965 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.1279 | [19 empty] | 562.3413 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5592 | [19 empty] | 749.8942 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2483 | [19 empty] | 1000 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.106 | [19 empty] | 1333.5214 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.2546 | [19 empty] | 1778.2794 | 0
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.12889 | 0.00082094 | 4 | 2962191.8038 | 7105445.377 | 60388.2866 | 144854.1148 | 68.5924 | 0 | 34.2485 | 63192.8801 | 3280.9377 | 68932.9162 | 62882.5965 | 0 | 38540.4288 | 0 | 92363.6061 | 240311.1568 | 164017.3024 | 733521.8247 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9727079.4583 | 23332463.3742 | 2371.3737 | 0.0032837 | 2962191.8038 | 7105445.377 | 60388.2866 | 144854.1148
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.14205 | 0.0019598 | 4 | 1245253.1972 | 2980840.9861 | 25386.1708 | 60768.4754 | 69.2665 | 0 | 236.962 | 68184.2414 | 3558.8467 | 74464.158 | 66508.033 | 0 | 35266.3492 | 0 | 96712.8351 | 251626.9583 | 171740.5695 | 768061.9912 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9761619.6248 | 23367003.5407 | 3162.2777 | 0.0078391 | 1245253.1972 | 2980840.9861 | 25386.1708 | 60768.4754
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7398 | 0.24642 | 0.0037522 | 4 | 675297.3359 | 1581787.5844 | 13766.8496 | 32246.8794 | 72.4954 | 0 | 93.1187 | 103891.0408 | 5562.0524 | 115369.9517 | 95026.5822 | 0 | 48826.854 | 0 | 143783.8277 | 374096.0254 | 255328.2243 | 1141884.5585 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10135442.1921 | 23740826.108 | 4216.965 | 0.015009 | 675297.3359 | 1581787.5844 | 13766.8496 | 32246.8794
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.34188 | 0.0061224 | 4 | 426285.8892 | 981845.3247 | 8690.4144 | 20016.245 | 73.9607 | 0 | 83.9791 | 132582.2339 | 7181.2023 | 149729.4193 | 120828.3888 | 0 | 56537.2603 | 0 | 182074.8168 | 473721.3246 | 323324.538 | 1445979.184 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10439536.8177 | 24044920.7336 | 5623.4133 | 0.02449 | 426285.8892 | 981845.3247 | 8690.4144 | 20016.245
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8398 | 0.46581 | 0.0093542 | 4 | 288921.2384 | 652539.715 | 5890.0502 | 13302.9047 | 75.0638 | 0 | 87.9053 | 166388.4891 | 9093.6099 | 191586.1233 | 154349.5013 | 0 | 65200.7377 | 0 | 228781.1999 | 595241.7526 | 406264.7271 | 1816906.1407 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10810463.7743 | 24415847.6902 | 7498.9421 | 0.037417 | 288921.2384 | 652539.715 | 5890.0502 | 13302.9047
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3427 | 0.62268 | 0.013602 | 4 | 206782.002 | 456847.7282 | 4215.5308 | 9313.4589 | 75.8793 | 0 | 108.0421 | 205277.8701 | 11291.777 | 241504.1055 | 195963.4802 | 0 | 74633.7014 | 0 | 284181.6644 | 739382.397 | 504643.6787 | 2256878.6744 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11250436.308 | 24855820.2239 | 10000 | 0.054407 | 206782.002 | 456847.7282 | 4215.5308 | 9313.4589
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1138 | 0.80669 | 0.019058 | 4 | 153965.4845 | 332443.5426 | 3138.7947 | 6777.3113 | 76.4146 | 0 | 95.107 | 247090.1133 | 13651.5284 | 296958.0927 | 244734.8737 | 0 | 83263.799 | 0 | 345422.3788 | 898718.1737 | 613393.6204 | 2743232.5799 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11736790.2135 | 25342174.1294 | 13335.2143 | 0.07623 | 153965.4845 | 332443.5426 | 3138.7947 | 6777.3113
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8398 | 1.093 | 0.026769 | 4 | 116417.9852 | 243481.2574 | 2373.3381 | 4963.6948 | 77.0181 | 0 | 71.1782 | 307127.9977 | 17047.7562 | 378467.706 | 319996.0799 | 0 | 98345.5594 | 0 | 437184.1887 | 1137463.5802 | 776342.266 | 3471975.1342 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 12465532.7678 | 26070916.6837 | 17782.7941 | 0.10708 | 116417.9852 | 243481.2574 | 2373.3381 | 4963.6948
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9715 | 1.4215 | 0.036593 | 4 | 90573.5078 | 183523.8223 | 1846.4635 | 3741.3814 | 77.3809 | 0 | 180.0108 | 370292.1584 | 20616.139 | 466866.195 | 407375.627 | 0 | 111529.7896 | 0 | 536905.1646 | 1396917.1038 | 953424.6271 | 4263926.8045 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13257484.4382 | 26862868.3541 | 23713.7371 | 0.14637 | 90573.5078 | 183523.8223 | 1846.4635 | 3741.3814
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.064 | 1.746 | 0.048666 | 4 | 71881.3217 | 141773.6288 | 1465.398 | 2890.2472 | 77.6102 | 0 | 151.7536 | 428458.2443 | 23899.1699 | 550227.3972 | 493672.6387 | 0 | 117756.9957 | 0 | 629465.6338 | 1637740.4581 | 1117791.5148 | 4999012.0525 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13992569.6861 | 27597953.602 | 31622.7766 | 0.19466 | 71881.3217 | 141773.6288 | 1465.398 | 2890.2472
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.7548 | 2.3433 | 0.065768 | 4 | 58283.7782 | 110001.0464 | 1188.1937 | 2242.5201 | 77.8716 | 0 | 91.7992 | 527690.4432 | 29493.4594 | 696098.4858 | 652495.7477 | 0 | 140968.5598 | 0 | 798231.2114 | 2076833.8723 | 1417481.7925 | 6339293.572 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 15332851.2057 | 28938235.1215 | 42169.6503 | 0.26307 | 58283.7782 | 110001.0464 | 1188.1937 | 2242.5201
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.3501 | 2.9306 | 0.085754 | 4 | 48328.0124 | 87992.1404 | 985.2319 | 1793.8388 | 78.028 | 0 | 98.6112 | 618055.467 | 34580.5107 | 832369.2209 | 808508.7703 | 0 | 154999.4617 | 0 | 954920.238 | 2484506.5781 | 1695726.7911 | 7583667.0378 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 16577224.6714 | 30182608.5873 | 56234.1325 | 0.34301 | 48328.0124 | 87992.1404 | 985.2319 | 1793.8388
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8151 | 3.6087 | 0.10979 | 4 | 40900.6215 | 71881.6395 | 833.8145 | 1465.4044 | 78.1478 | 0 | 102.2838 | 715877.9576 | 40078.7767 | 983101.8085 | 988080.1065 | 0 | 168343.5021 | 0 | 1129238.0391 | 2938045.7391 | 2005276.5877 | 8968042.5173 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 17961600.1509 | 31566984.0668 | 74989.4209 | 0.43915 | 40900.6215 | 71881.6395 | 833.8145 | 1465.4044
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.9233 | 4.3545 | 0.13755 | 4 | 35319.9577 | 60047.1474 | 720.0451 | 1224.1423 | 78.238 | 0 | 135.3777 | 817344.6685 | 45774.5914 | 1142443.472 | 1185526.2317 | 0 | 179695.5839 | 0 | 1314605.9735 | 3420335.0804 | 2334448.9732 | 10440174.5747 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 19433732.2083 | 33039116.1242 | 100000 | 0.55022 | 35319.9577 | 60047.1474 | 720.0451 | 1224.1423
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.2682 | 5.125 | 0.16793 | 4 | 31125.9196 | 51380.0065 | 634.544 | 1047.4509 | 78.3031 | 0 | 113.1267 | 916895.6042 | 51355.6196 | 1301422.5509 | 1389541.9208 | 0 | 187682.526 | 0 | 1500290.3064 | 3903447.6254 | 2664183.2122 | 11914819.3655 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 20908376.9991 | 34513760.915 | 133352.1432 | 0.67174 | 31125.9196 | 51380.0065 | 634.544 | 1047.4509
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4151 | 5.8743 | 0.19926 | 4 | 27982.1102 | 45051.6484 | 570.4532 | 918.4388 | 78.3465 | 0 | 118.1709 | 1009501.8768 | 56540.3486 | 1451479.8066 | 1588023.7759 | 0 | 191732.6338 | 0 | 1675938.5923 | 4360448.4349 | 2976095.655 | 13309761.1239 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 22303318.7576 | 35908702.6735 | 177827.941 | 0.79706 | 27982.1102 | 45051.6484 | 570.4532 | 918.4388
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.9781 | 6.5614 | 0.2297 | 4 | 25633.5413 | 40441.3201 | 522.5744 | 824.451 | 78.3719 | 0 | 117.0845 | 1091353.8053 | 61116.6665 | 1585766.2962 | 1770229.5325 | 0 | 191999.4784 | 0 | 1833181.6538 | 4769562.6259 | 3255324.4969 | 14558534.5555 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 23552092.1892 | 37157476.1051 | 237137.3706 | 0.9188 | 25633.5413 | 40441.3201 | 522.5744 | 824.451
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.7197 | 7.1616 | 0.25771 | 4 | 23883.5606 | 37081.8189 | 486.8987 | 755.963 | 78.3838 | 0 | 119.8105 | 1160724.8655 | 64989.942 | 1700761.1305 | 1929560.4866 | 0 | 189316.4184 | 0 | 1967687.6088 | 5119519.5298 | 3494177.2747 | 15626737.2564 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 24620294.89 | 38225678.8059 | 316227.766 | 1.0308 | 23883.5606 | 37081.8189 | 486.8987 | 755.963
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.5233 | 7.6627 | 0.28227 | 4 | 22581.1386 | 34630.9539 | 460.3471 | 705.9988 | 78.3869 | 0 | 158.9966 | 1217286.6521 | 68144.0748 | 1795317.1467 | 2062791.2923 | 0 | 184629.1827 | 0 | 2077985.6559 | 5406492.4233 | 3690042.1712 | 16502688.599 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 25496246.2326 | 39101630.1485 | 421696.5034 | 1.1291 | 22581.1386 | 34630.9539 | 460.3471 | 705.9988
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.446 | 8.0712 | 0.30307 | 4 | 21611.8107 | 32834.6638 | 440.586 | 669.379 | 78.3849 | 0 | 135.6813 | 1262541.5693 | 70664.9177 | 1871483.2369 | 2171539.6263 | 0 | 179106.6428 | 0 | 2166581.0373 | 5636999.4322 | 3847367.9412 | 17206284.4038 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 26199842.0374 | 39805225.9533 | 562341.3252 | 1.2123 | 21611.8107 | 32834.6638 | 440.586 | 669.379
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5567 | 8.3946 | 0.32013 | 4 | 20889.8677 | 31514.8352 | 425.8682 | 642.4725 | 78.3807 | 0 | 130.1881 | 1297858.0331 | 72630.3386 | 1931238.6695 | 2257738.7898 | 0 | 173400.2522 | 0 | 2235817.7725 | 5817139.2147 | 3970317.0443 | 17756140.1147 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 26749697.7483 | 40355081.6642 | 749894.2093 | 1.2805 | 20889.8677 | 31514.8352 | 425.8682 | 642.4725
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9922 | 8.6474 | 0.33382 | 4 | 20351.6184 | 30540.7599 | 414.8953 | 622.6147 | 78.3757 | 0 | 137.8213 | 1325168.6294 | 74149.075 | 1977638.5384 | 2325202.2528 | 0 | 168076.1904 | 0 | 2289391.5275 | 5956527.1358 | 4065452.1646 | 18181605.5139 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27175163.1475 | 40780547.0634 | 1000000 | 1.3353 | 20351.6184 | 30540.7599 | 414.8953 | 622.6147
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.8876 | 8.8439 | 0.34466 | 4 | 19949.8894 | 29818.7281 | 406.7055 | 607.8951 | 78.3709 | 0 | 139.8354 | 1346220.5549 | 75319.0631 | 2013518.6611 | 2377686.3392 | 0 | 163443.416 | 0 | 2330713.3334 | 6064037.9983 | 4138830.5374 | 18509769.9033 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27503327.537 | 41108711.4529 | 1333521.4322 | 1.3786 | 19949.8894 | 29818.7281 | 406.7055 | 607.8951
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.3419 | 8.9946 | 0.3531 | 4 | 19649.7585 | 29282.6118 | 400.5869 | 596.9657 | 78.3666 | 0 | 136.7552 | 1362257.0376 | 76209.889 | 2040917.1215 | 2417948.5383 | 0 | 159531.056 | 0 | 2362176.8205 | 6145899.5378 | 4194702.7202 | 18759642.7208 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27753200.3544 | 41358584.2703 | 1778279.41 | 1.4124 | 19649.7585 | 29282.6118 | 400.5869 | 596.9657
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.448 | 9.1091 | 0.35961 | 4 | 19425.3442 | 28883.8339 | 396.0119 | 588.836 | 78.3631 | 0 | 140.8156 | 1374386.7406 | 76883.446 | 2061679.0742 | 2448564.6109 | 0 | 156311.8981 | 0 | 2385952.0502 | 6207757.8086 | 4236922.261 | 18948457.8897 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 27942015.5233 | 41547399.4392 | 2371373.7057 | 1.4384 | 19425.3442 | 28883.8339 | 396.0119 | 588.836
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.2936 | 9.1965 | 0.36461 | 4 | 19257.4312 | 28586.1617 | 392.5888 | 582.7676 | 78.3602 | 0 | 116.105 | 1383620.196 | 77396.0308 | 2077505.7495 | 2471964.4135 | 0 | 153758.6864 | 0 | 2404055.5797 | 6254859.4789 | 4269070.1188 | 19092230.2537 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28085787.8873 | 41691171.8032 | 3162277.6602 | 1.4584 | 19257.4312 | 28586.1617 | 392.5888 | 582.7676
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9218 | 9.2615 | 0.36839 | 4 | 19131.7273 | 28364.6675 | 390.0261 | 578.2521 | 78.3579 | 0 | 137.4658 | 1390459.3298 | 77775.6158 | 2089240.7695 | 2489348.9482 | 0 | 151693.3542 | 0 | 2417422.0268 | 6289636.2323 | 4292805.9677 | 19198382.2443 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28191939.8779 | 41797323.7938 | 4216965.0343 | 1.4736 | 19131.7273 | 28364.6675 | 390.0261 | 578.2521
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.3971 | 9.3106 | 0.37127 | 4 | 19037.5834 | 28199.0623 | 388.1069 | 574.876 | 78.3562 | 0 | 129.6254 | 1395620.9725 | 78062.0506 | 2098104.4067 | 2502499.063 | 0 | 150090.7841 | 0 | 2427507.138 | 6315875.6229 | 4310714.8909 | 19278474.9286 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28272032.5622 | 41877416.4781 | 5623413.2519 | 1.4851 | 19037.5834 | 28199.0623 | 388.1069 | 574.876
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7667 | 9.3488 | 0.37347 | 4 | 18967.0534 | 28074.4806 | 386.669 | 572.3363 | 78.3547 | 0 | 138.2449 | 1399627.9657 | 78284.3828 | 2104989.3921 | 2512725.0971 | 0 | 148906.5714 | 0 | 2435368.0295 | 6336328.0501 | 4324674.0927 | 19340903.5814 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28334461.2151 | 41939845.131 | 7498942.0933 | 1.4939 | 18967.0534 | 28074.4806 | 386.669 | 572.3363
1 | 2600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.0445 | 9.3775 | 0.37513 | 4 | 18914.202 | 27981.2631 | 385.5916 | 570.4359 | 78.3537 | 0 | 123.9097 | 1402635.8372 | 78451.2618 | 2110160.0199 | 2520411.44 | 0 | 147997.4438 | 0 | 2441265.841 | 6351672.9459 | 4335147.2994 | 19387742.089 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28381299.7226 | 41986683.6385 | 10000000 | 1.5005 | 18914.202 | 27981.2631 | 385.5916 | 570.4359
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.6256 | [19 empty] | 100 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.3259 | [19 empty] | 133.3521 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6462 | [19 empty] | 177.8279 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.467 | [19 empty] | 237.1374 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2243 | [19 empty] | 316.2278 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1344 | [19 empty] | 421.6965 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5381 | [19 empty] | 562.3413 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3492 | [19 empty] | 749.8942 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5538 | [19 empty] | 1000 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.9011 | [19 empty] | 1333.5214 | 0
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.13527 | 0.00013879 | 4 | 18242406.638 | 43653765.1906 | 371896.134 | 889941.0495 | 70.269 | 0 | 32.484 | 66818.8911 | 3506.0975 | 71541.6404 | 64014.3454 | 0 | 44448.8999 | 0 | 97628.651 | 254009.7235 | 173366.8557 | 775335.1045 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10127379.6108 | 24234645.1485 | 1778.2794 | 0.00055516 | 18242406.638 | 43653765.1906 | 371896.134 | 889941.0495
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.14289 | 0.0014845 | 4 | 1707166.6906 | 4082853.7185 | 34802.9021 | 83234.4955 | 70.6769 | 0 | 249.8374 | 69757.2999 | 3671.7266 | 74722.682 | 66069.0874 | 0 | 39366.6363 | 0 | 98899.0986 | 257315.1675 | 175622.8891 | 785424.5875 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10137469.0938 | 24244734.6315 | 2371.3737 | 0.0059382 | 1707166.6906 | 4082853.7185 | 34802.9021 | 83234.4955
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3321 | 0.21478 | 0.0030733 | 4 | 845597.6433 | 1993181.635 | 17238.6517 | 40633.7036 | 73.3822 | 0 | 374.653 | 95540.1292 | 5133.8666 | 103282.0215 | 85290.0749 | 0 | 47471.1741 | 0 | 131319.7339 | 341667.0101 | 233194.755 | 1042898.7652 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10394943.2716 | 24502208.8093 | 3162.2777 | 0.012293 | 845597.6433 | 1993181.635 | 17238.6517 | 40633.7036
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1102 | 0.30024 | 0.0053091 | 4 | 502687.2102 | 1166984.9126 | 10247.9587 | 23790.5659 | 75.1862 | 0 | 79.2392 | 122979.2146 | 6700.3135 | 134813.5343 | 107880.5782 | 0 | 54844.3133 | 0 | 166615.002 | 433498.0578 | 295871.332 | 1323202.3458 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10675246.8521 | 24782512.3898 | 4216.965 | 0.021236 | 502687.2102 | 1166984.9126 | 10247.9587 | 23790.5659
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1554 | 0.4149 | 0.0083178 | 4 | 331371.6746 | 755378.0353 | 6755.4598 | 15399.403 | 76.5963 | 0 | 99.281 | 156136.9491 | 8595.9446 | 174430.4135 | 137210.2953 | 0 | 63827.445 | 0 | 210678.4085 | 548142.0029 | 374118.1802 | 1673139.639 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11025184.1454 | 25132449.6831 | 5623.4133 | 0.033271 | 331371.6746 | 755378.0353 | 6755.4598 | 15399.403
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5339 | 0.56703 | 0.012433 | 4 | 230499.4543 | 514163.7216 | 4699.0432 | 10481.9229 | 77.6674 | 0 | 91.3691 | 196116.6442 | 10886.5847 | 223753.9011 | 176486.0643 | 0 | 74397.679 | 0 | 265839.9406 | 691660.9941 | 472072.8407 | 2111214.6486 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11463259.1549 | 25570524.6926 | 7498.9421 | 0.049732 | 230499.4543 | 514163.7216 | 4699.0432 | 10481.9229
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1392 | 0.74402 | 0.017806 | 4 | 167639.9969 | 365704.1339 | 3417.5681 | 7455.3734 | 78.3848 | 0 | 97.2457 | 238587.5141 | 13318.5726 | 277910.7059 | 222036.097 | 0 | 83803.2593 | 0 | 325905.8981 | 847940.2943 | 578736.6743 | 2588239.0156 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11940283.522 | 26047549.0597 | 10000 | 0.071226 | 167639.9969 | 365704.1339 | 3417.5681 | 7455.3734
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5 | 1.0054 | 0.025159 | 4 | 125344.8537 | 265528.5196 | 2555.3244 | 5413.158 | 79.0586 | 0 | 104.51 | 296101.9918 | 16613.0965 | 353398.4147 | 288615.6774 | 0 | 98439.221 | 0 | 410735.6766 | 1068649.9769 | 729375.5678 | 3261929.6228 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12613974.1291 | 26721239.6668 | 13335.2143 | 0.10063 | 125344.8537 | 265528.5196 | 2555.3244 | 5413.158
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2406 | 1.3088 | 0.034661 | 4 | 96307.6728 | 198058.7532 | 1963.3622 | 4037.6956 | 79.5024 | 0 | 105.6788 | 357409.7371 | 20122.3109 | 436253.2268 | 366375.0145 | 0 | 111474.4932 | 0 | 503737.5652 | 1310621.8138 | 894526.3185 | 4000520.4799 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 13352564.9863 | 27459830.524 | 17782.7941 | 0.13864 | 96307.6728 | 198058.7532 | 1963.3622 | 4037.6956
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7165 | 1.6937 | 0.047039 | 4 | 75723.484 | 150700.2495 | 1543.7256 | 3072.2284 | 79.8449 | 0 | 119.8517 | 429294.0749 | 24232.6357 | 536040.8037 | 465004.4412 | 0 | 126092.9207 | 0 | 616459.3018 | 1603900.65 | 1094695.1505 | 4895719.9787 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 14247764.485 | 28355030.0227 | 23713.7371 | 0.18816 | 75723.484 | 150700.2495 | 1543.7256 | 3072.2284
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.0239 | 2.1709 | 0.062947 | 4 | 60803.9234 | 116832.0469 | 1239.5702 | 2381.7793 | 80.1066 | 0 | 108.6204 | 511897.8473 | 28950.344 | 653665.811 | 587304.9166 | 0 | 141728.7556 | 0 | 750183.5931 | 1951823.8253 | 1332159.8667 | 5957714.9596 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 15309759.4659 | 29417025.0037 | 31622.7766 | 0.25179 | 60803.9234 | 116832.0469 | 1239.5702 | 2381.7793
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2024 | 2.7449 | 0.082976 | 4 | 49816.5693 | 92320.5365 | 1015.5781 | 1882.079 | 80.3047 | 0 | 128.9809 | 604342.509 | 34223.3285 | 788484.0663 | 734436.4136 | 0 | 157441.6202 | 0 | 904381.8957 | 2353016.1783 | 1605981.8914 | 7182307.903 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 16534352.4094 | 30641617.9471 | 42169.6503 | 0.3319 | 49816.5693 | 92320.5365 | 1015.5781 | 1882.079
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.046 | 3.2819 | 0.106 | 4 | 41550.4795 | 74822.7823 | 847.0627 | 1525.3636 | 80.4294 | 0 | 252.5421 | 685709.047 | 38858.7529 | 909551.0567 | 872067.6329 | 0 | 162345.5381 | 0 | 1040727.4907 | 2707759.4483 | 1848101.4624 | 8265120.429 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 17617164.9353 | 31724430.473 | 56234.1325 | 0.42399 | 41550.4795 | 74822.7823 | 847.0627 | 1525.3636
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4692 | 4.2159 | 0.1377 | 4 | 35396.7243 | 61009.3365 | 721.6101 | 1243.7578 | 80.5736 | 0 | 88.4482 | 818436.4889 | 46409.5618 | 1111203.6479 | 1111436.0991 | 0 | 187754.0279 | 0 | 1277343.532 | 3323385.851 | 2268279.132 | 10144248.3405 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 19496292.8469 | 33603558.3846 | 74989.4209 | 0.55079 | 35396.7243 | 61009.3365 | 721.6101 | 1243.7578
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9406 | 5.0445 | 0.17105 | 4 | 30810.8722 | 51429.0759 | 628.1213 | 1048.4513 | 80.6576 | 0 | 112.4178 | 928995.641 | 52689.4984 | 1282636.4301 | 1323760.7768 | 0 | 198881.8557 | 0 | 1476916.0388 | 3842632.5757 | 2622675.6912 | 11729188.5076 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 21081233.014 | 35188498.5517 | 100000 | 0.68421 | 30810.8722 | 51429.0759 | 628.1213 | 1048.4513
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.4922 | 5.8816 | 0.20679 | 4 | 27364.1512 | 44419.1565 | 557.8552 | 905.5446 | 80.716 | 0 | 111.5854 | 1035335.9677 | 58721.0815 | 1450191.3736 | 1538322.9346 | 0 | 205925.6247 | 0 | 1672513.823 | 4351537.8877 | 2970014.0235 | 13282562.7163 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 22634607.2227 | 36741872.7604 | 133352.1432 | 0.82716 | 27364.1512 | 44419.1565 | 557.8552 | 905.5446
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.7077 | 6.6806 | 0.2429 | 4 | 24781.8822 | 39301.5282 | 505.2122 | 801.2148 | 80.7524 | 0 | 111.8013 | 1132668.6366 | 64233.3438 | 1605702.147 | 1743226.9809 | 0 | 208701.7096 | 0 | 1854267.799 | 4824424.4504 | 3292768.8194 | 14725993.8867 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 24078038.3931 | 38185303.9308 | 177827.941 | 0.9716 | 24781.8822 | 39301.5282 | 505.2122 | 801.2148
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.1922 | 7.3973 | 0.27722 | 4 | 22853.6106 | 35575.4686 | 465.9018 | 725.254 | 80.7707 | 0 | 129.0634 | 1217015.1431 | 69002.7025 | 1742070.5844 | 1927224.8313 | 0 | 207428.082 | 0 | 2013469.1239 | 5238633.641 | 3575475.1032 | 15990319.2114 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 25342363.7178 | 39449629.2555 | 237137.3706 | 1.1089 | 22853.6106 | 35575.4686 | 465.9018 | 725.254
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.7681 | 8.0122 | 0.30823 | 4 | 21416.7354 | 32858.8649 | 436.6091 | 669.8724 | 80.7766 | 0 | 139.6484 | 1287395.2657 | 72976.3402 | 1856983.8307 | 2085281.6378 | 0 | 203254.6604 | 0 | 2147297.7766 | 5586828.3433 | 3813125.1421 | 17053142.9968 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 26405187.5031 | 40512453.0408 | 316227.766 | 1.2329 | 21416.7354 | 32858.8649 | 436.6091 | 669.8724
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.4091 | 8.5229 | 0.3351 | 4 | 20346.8229 | 30871.4969 | 414.7975 | 629.3572 | 80.7749 | 0 | 135.4917 | 1344567.6878 | 76199.8445 | 1951083.0259 | 2216701.5988 | 0 | 197484.4055 | 0 | 2256554.2594 | 5871091.3 | 4007140.4511 | 17920822.573 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 27272867.0793 | 41380132.617 | 421696.5034 | 1.3404 | 20346.8229 | 30871.4969 | 414.7975 | 629.3572
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.148 | 8.9334 | 0.35755 | 4 | 19549.9471 | 29413.875 | 398.5521 | 599.6416 | 80.7693 | 0 | 148.7439 | 1389746.5193 | 78744.0939 | 2025919.0326 | 2322473.6134 | 0 | 191034.1123 | 0 | 2343087.7749 | 6096233.7569 | 4160804.8042 | 18608043.7076 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 27960088.214 | 42067353.7517 | 562341.3252 | 1.4302 | 19549.9471 | 29413.875 | 398.5521 | 599.6416
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.1176 | 9.2588 | 0.37585 | 4 | 18955.9522 | 28339.4816 | 386.4427 | 577.7387 | 80.7624 | 0 | 132.1902 | 1425092.2601 | 80732.618 | 2084761.7128 | 2406411.1108 | 0 | 184759.6095 | 0 | 2410885.3514 | 6272629.1437 | 4281198.2802 | 19146470.0865 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28498514.5929 | 42605780.1306 | 749894.2093 | 1.5034 | 18955.9522 | 28339.4816 | 386.4427 | 577.7387
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.4151 | 9.5102 | 0.3904 | 4 | 18512.7421 | 27546.4859 | 377.4073 | 561.5724 | 80.7555 | 0 | 125.8801 | 1452120.8126 | 82252.0033 | 2129933.3935 | 2471302.8642 | 0 | 178954.4976 | 0 | 2462679.7928 | 6407387.6557 | 4373173.7337 | 19557804.7533 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28909849.2597 | 43017114.7974 | 1000000 | 1.5616 | 18512.7421 | 27546.4859 | 377.4073 | 561.5724
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.2056 | 9.7059 | 0.40188 | 4 | 18181.7137 | 26957.4029 | 370.6588 | 549.5631 | 80.7493 | 0 | 123.5776 | 1472998.342 | 83424.8678 | 2164929.4874 | 2521846.9036 | 0 | 174026.1474 | 0 | 2502718.0418 | 6511558.9666 | 4444272.7939 | 19875775.5504 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29227820.0567 | 43335085.5944 | 1333521.4322 | 1.6075 | 18181.7137 | 26957.4029 | 370.6588 | 549.5631
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.5692 | 9.8547 | 0.41078 | 4 | 17934.2571 | 26519.9583 | 365.6141 | 540.6452 | 80.7441 | 0 | 134.946 | 1488790.7464 | 84311.6155 | 2191462.2521 | 2560323.9529 | 0 | 169878.9042 | 0 | 2532959.3137 | 6590240.553 | 4497974.5933 | 20115941.9312 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29467986.4375 | 43575251.9752 | 1778279.41 | 1.6431 | 17934.2571 | 26519.9583 | 365.6141 | 540.6452
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6144 | 9.9687 | 0.41764 | 4 | 17749.1398 | 26193.7385 | 361.8402 | 533.9948 | 80.7398 | 0 | 154.0203 | 1500832.2011 | 84987.4856 | 2211728.251 | 2589803.6408 | 0 | 166544.3675 | 0 | 2556019.4189 | 6650238.2164 | 4538924.2314 | 20299077.8127 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29651122.3191 | 43758387.8568 | 2371373.7057 | 1.6706 | 17749.1398 | 26193.7385 | 361.8402 | 533.9948
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4038 | 10.0548 | 0.42288 | 4 | 17610.5776 | 25950.5529 | 359.0154 | 529.0371 | 80.7364 | 0 | 164.0068 | 1509891.2 | 85495.8038 | 2226994.8416 | 2612062.6432 | 0 | 163873.4599 | 0 | 2573344 | 6695313.2225 | 4569688.8493 | 20436664.0205 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29788708.5268 | 43895974.0645 | 3162277.6602 | 1.6915 | 17610.5776 | 25950.5529 | 359.0154 | 529.0371
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.9936 | 10.1191 | 0.42685 | 4 | 17506.8156 | 25769.2956 | 356.9001 | 525.3419 | 80.7337 | 0 | 136.1671 | 1516639.299 | 85874.3679 | 2238378.2632 | 2628688.7345 | 0 | 161744.5439 | 0 | 2586216.8312 | 6728805.6888 | 4592548.1458 | 20538895.8741 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29890940.3805 | 43998205.9182 | 4216965.0343 | 1.7074 | 17506.8156 | 25769.2956 | 356.9001 | 525.3419
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.4392 | 10.1676 | 0.42986 | 4 | 17429.0871 | 25633.7343 | 355.3155 | 522.5783 | 80.7317 | 0 | 134.9683 | 1521727.1263 | 86159.7434 | 2246967.318 | 2641249.78 | 0 | 160096.9822 | 0 | 2595918.3704 | 6754047.1038 | 4609775.9301 | 20615942.3542 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 29967986.8606 | 44075252.3983 | 5623413.2519 | 1.7194 | 17429.0871 | 25633.7343 | 355.3155 | 522.5783
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.783 | 10.205 | 0.43215 | 4 | 17370.8452 | 25531.8676 | 354.1282 | 520.5017 | 80.73 | 0 | 141.9962 | 1525645.3249 | 86379.4862 | 2253585.5795 | 2650938.1755 | 0 | 158868.1526 | 0 | 2603412.5203 | 6773545.3445 | 4623083.88 | 20675458.4636 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 30027502.9699 | 44134768.5076 | 7498942.0933 | 1.7286 | 17370.8452 | 25531.8676 | 354.1282 | 520.5017
1 | 2700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.0387 | 10.2329 | 0.43388 | 4 | 17327.1959 | 25455.7634 | 353.2383 | 518.9502 | 80.7288 | 0 | 149.2148 | 1528557.0264 | 86542.766 | 2258505.8646 | 2658146.3021 | 0 | 157914.9557 | 0 | 2608970.0968 | 6788005.0184 | 4632952.9046 | 20719594.9346 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 30071639.4409 | 44178904.9786 | 10000000 | 1.7355 | 17327.1959 | 25455.7634 | 353.2383 | 518.9502
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.1665 | [19 empty] | 100 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.6457 | [19 empty] | 133.3521 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.5869 | [19 empty] | 177.8279 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2299 | [19 empty] | 237.1374 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2518 | [19 empty] | 316.2278 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.173 | [19 empty] | 421.6965 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0927 | [19 empty] | 562.3413 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5974 | [19 empty] | 749.8942 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4459 | [19 empty] | 1000 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8566 | [19 empty] | 1333.5214 | 0
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.14167 | 0.00083988 | 4 | 3129055.729 | 7480065.3265 | 63790.0334 | 152491.2492 | 71.9225 | 0 | 36.0259 | 70462.53 | 3735.6745 | 74131.9819 | 65127.9984 | 0 | 43468.7939 | 0 | 100201.5217 | 260703.8052 | 177935.704 | 795768.0096 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10512159.4795 | 25129510.7662 | 1778.2794 | 0.0033595 | 3129055.729 | 7480065.3265 | 63790.0334 | 152491.2492
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.18074 | 0.0023235 | 4 | 1145480.1895 | 2718220.4707 | 23352.163 | 55414.601 | 73.7584 | 0 | 305.5656 | 85216.7396 | 4580.1468 | 89935.518 | 75352.4866 | 0 | 45155.9995 | 0 | 117093.9472 | 304654.4314 | 207932.9095 | 929922.1784 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10646313.6484 | 25263664.9351 | 2371.3737 | 0.0092942 | 1145480.1895 | 2718220.4707 | 23352.163 | 55414.601
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6304 | 0.25963 | 0.0043591 | 4 | 625965.1183 | 1464295.4276 | 12761.1456 | 29851.6429 | 76.1062 | 0 | 68.4247 | 112354.9029 | 6143.3942 | 119926.9443 | 95476.1572 | 0 | 52926.3374 | 0 | 150862.817 | 392514.1037 | 267898.9411 | 1198103.5978 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10914495.0677 | 25531846.3544 | 3162.2777 | 0.017436 | 625965.1183 | 1464295.4276 | 12761.1456 | 29851.6429
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5855 | 0.37004 | 0.0072016 | 4 | 391024.8683 | 898460.1959 | 7971.5708 | 18316.3264 | 77.96 | 0 | 67.6474 | 146409.2259 | 8114.453 | 158991.4706 | 123216.1378 | 0 | 62937.6136 | 0 | 194870.8713 | 507014.0337 | 346047.4961 | 1547601.302 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11263992.772 | 25881344.0587 | 4216.965 | 0.028806 | 391024.8683 | 898460.1959 | 7971.5708 | 18316.3264
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7427 | 0.50412 | 0.011029 | 4 | 264227.7376 | 595564.2689 | 5386.6398 | 12141.3832 | 79.2481 | 0 | 88.9872 | 183730.2446 | 10277.8822 | 203407.6875 | 156382.9544 | 0 | 72680.8393 | 0 | 244327.0471 | 635688.8583 | 433870.7079 | 1940366.2214 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11656757.6914 | 26274108.9781 | 5623.4133 | 0.044116 | 264227.7376 | 595564.2689 | 5386.6398 | 12141.3832
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2307 | 0.6772 | 0.016198 | 4 | 187302.9946 | 412910.5605 | 3818.4249 | 8417.7403 | 80.215 | 0 | 106.0331 | 227706.6915 | 12830.5962 | 257382.5513 | 199531.4553 | 0 | 83616.9341 | 0 | 304616.6091 | 792549.9313 | 540931.6134 | 2419166.3821 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12135557.852 | 26752909.1388 | 7498.9421 | 0.064791 | 187302.9946 | 412910.5605 | 3818.4249 | 8417.7403
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0166 | 0.88446 | 0.022905 | 4 | 138349.9674 | 297889.9112 | 2820.4512 | 6072.8888 | 80.8647 | 0 | 99.64 | 275916.4359 | 15625.1894 | 318506.1674 | 251359.9387 | 0 | 94114.3207 | 0 | 372653.6003 | 969568.2262 | 661750.237 | 2959494.1155 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12675885.5855 | 27293236.8722 | 10000 | 0.091622 | 138349.9674 | 297889.9112 | 2820.4512 | 6072.8888
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6398 | 1.1921 | 0.032295 | 4 | 104076.6557 | 217230.2143 | 2121.7434 | 4428.5317 | 81.547 | 0 | 105.8629 | 341922.5132 | 19459.8944 | 404206.2184 | 327707.7935 | 0 | 110476.9842 | 0 | 469471.6275 | 1221468.8728 | 833677.6043 | 3728391.5083 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 13444782.9783 | 28062134.265 | 13335.2143 | 0.12918 | 104076.6557 | 217230.2143 | 2121.7434 | 4428.5317
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7292 | 1.5531 | 0.044251 | 4 | 80769.0095 | 163350.17 | 1646.5855 | 3330.1142 | 81.9751 | 0 | 86.0736 | 412867.1687 | 23571.6806 | 499297.7555 | 417436.3302 | 0 | 125620.544 | 0 | 576729.4568 | 1500531.7431 | 1024143.7475 | 4580198.4264 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 14296589.8963 | 28913941.183 | 17782.7941 | 0.17701 | 80769.0095 | 163350.17 | 1646.5855 | 3330.1142
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5756 | 2.0026 | 0.059706 | 4 | 64097.0533 | 125302.3384 | 1306.7051 | 2554.4577 | 82.3008 | 0 | 113.2807 | 494537.2521 | 28298.4267 | 611726.8614 | 528924.3078 | 0 | 141850.0894 | 0 | 704081.4056 | 1831875.3904 | 1250292.5952 | 5591586.3287 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 15307977.7987 | 29925329.0854 | 23713.7371 | 0.23882 | 64097.0533 | 125302.3384 | 1306.7051 | 2554.4577
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2944 | 2.5542 | 0.07943 | 4 | 51918.9166 | 97925.9175 | 1058.4373 | 1996.3523 | 82.5489 | 0 | 97.6424 | 587569.8583 | 33675.4808 | 743015.1347 | 665693.8975 | 0 | 158853.9923 | 0 | 853635.2618 | 2220983.8466 | 1515867.112 | 6779294.584 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 16495686.054 | 31113037.3407 | 31622.7766 | 0.31772 | 51918.9166 | 97925.9175 | 1058.4373 | 1996.3523
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.948 | 3.2152 | 0.1041 | 4 | 42894.7022 | 77998.7535 | 874.4665 | 1590.1101 | 82.7378 | 0 | 125.2717 | 691479.5116 | 39672.6304 | 893095.0921 | 829572.5665 | 0 | 175926.8509 | 0 | 1025601.1941 | 2668403.9273 | 1821240.5106 | 8144992.2837 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 17861383.7536 | 32478735.0403 | 42169.6503 | 0.4164 | 42894.7022 | 77998.7535 | 874.4665 | 1590.1101
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.525 | 3.9843 | 0.13413 | 4 | 36141.0431 | 63385.6549 | 736.784 | 1292.2023 | 82.8816 | 0 | 121.1564 | 804688.3629 | 46196.9341 | 1060152.3761 | 1020229.6425 | 0 | 192176.2367 | 0 | 1218142.9854 | 3169358.1726 | 2163152.0766 | 9674096.7871 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 19390488.257 | 34007839.5438 | 56234.1325 | 0.53652 | 36141.0431 | 63385.6549 | 736.784 | 1292.2023
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.441 | 4.5593 | 0.16476 | 4 | 31038.8123 | 53218.5121 | 632.7682 | 1084.9314 | 82.9586 | 0 | 497.635 | 885108.2031 | 50825.8765 | 1180803.7914 | 1162743.5047 | 0 | 187940.8788 | 0 | 1352294.6792 | 3518393.3616 | 2401375.765 | 10739486.0603 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 20455877.5302 | 35073228.8169 | 74989.4209 | 0.65904 | 31038.8123 | 53218.5121 | 632.7682 | 1084.9314
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.965 | 5.7904 | 0.20989 | 4 | 27157.6384 | 44568.5286 | 553.6452 | 908.5897 | 83.0715 | 0 | 148.7497 | 1047965.3533 | 60187.0889 | 1429512.7488 | 1468333.6182 | 0 | 218344.8632 | 0 | 1647494.0323 | 4286441.5244 | 2925584.418 | 13083863.6471 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 22800255.1171 | 37417606.4038 | 100000 | 0.83955 | 27157.6384 | 44568.5286 | 553.6452 | 908.5897
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.6797 | 6.6922 | 0.25132 | 4 | 24297.5082 | 38838.3572 | 495.3376 | 791.7724 | 83.1226 | 0 | 155.9924 | 1160745.9212 | 66658.0043 | 1604934.6398 | 1692408.9769 | 0 | 224282.5926 | 0 | 1852121.7525 | 4818840.8777 | 3288957.9163 | 14708950.6812 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 24425342.1511 | 39042693.4379 | 133352.1432 | 1.0053 | 24297.5082 | 38838.3572 | 495.3376 | 791.7724
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.883 | 7.5328 | 0.29226 | 4 | 22155.6829 | 34659.5394 | 451.6736 | 706.5816 | 83.151 | 0 | 138.3541 | 1261802.2267 | 72446.2138 | 1764233.9427 | 1901428.8279 | 0 | 225430.9518 | 0 | 2037883.4435 | 5302154.6926 | 3618829.5261 | 16184209.825 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 25900601.2949 | 40517952.5816 | 177827.941 | 1.169 | 22155.6829 | 34659.5394 | 451.6736 | 706.5816
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.2607 | 8.2753 | 0.33048 | 4 | 20556.5906 | 31614.3534 | 419.0739 | 644.5014 | 83.1622 | 0 | 111.3725 | 1348226.535 | 77387.6894 | 1902022.022 | 2086257.0527 | 0 | 222565.2812 | 0 | 2198218.8463 | 5719314.5215 | 3903549.6811 | 17457541.6292 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 27173933.0991 | 41791284.3858 | 237137.3706 | 1.3219 | 20556.5906 | 31614.3534 | 419.0739 | 644.5014
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6781 | 8.9044 | 0.36447 | 4 | 19364.6801 | 29391.0927 | 394.7752 | 599.1772 | 83.162 | 0 | 127.9686 | 1419569.1598 | 81460.0689 | 2016839.4087 | 2243023.3494 | 0 | 217008.9712 | 0 | 2331381.3736 | 6065776.102 | 4140016.8289 | 18515075.2625 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 28231466.7324 | 42848818.0192 | 316227.766 | 1.4579 | 19364.6801 | 29391.0927 | 394.7752 | 599.1772
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.565 | 9.4703 | 0.39562 | 4 | 18433.6227 | 27670.6171 | 375.7943 | 564.103 | 83.1548 | 0 | 127.2751 | 1482401.3354 | 85041.0932 | 2118766.5636 | 2384226.6852 | 0 | 210752.3748 | 0 | 2449663.3403 | 6373521.5165 | 4350059.3978 | 19454432.3068 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 29170823.7767 | 43788175.0635 | 421696.5034 | 1.5825 | 18433.6227 | 27670.6171 | 375.7943 | 564.103
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.7024 | 9.8328 | 0.41758 | 4 | 17814.6735 | 26565.8314 | 363.1762 | 541.5804 | 83.1467 | 0 | 146.7997 | 1522011.4827 | 87295.7159 | 2183414.4873 | 2474760.5049 | 0 | 202783.1261 | 0 | 2523403.4736 | 6565378.217 | 4481005.5381 | 20040052.5454 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 29756444.0154 | 44373795.3021 | 562341.3252 | 1.6703 | 17814.6735 | 26565.8314 | 363.1762 | 541.5804
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.5212 | 10.1579 | 0.43705 | 4 | 17320.8567 | 25682.2982 | 353.1091 | 523.5684 | 83.1373 | 0 | 135.7549 | 1557132.7673 | 89292.8829 | 2240989.8242 | 2556016.712 | 0 | 195894.9795 | 0 | 2589337.5947 | 6736925.2752 | 4598089.9303 | 20563679.9661 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30280071.4361 | 44897422.7228 | 749894.2093 | 1.7482 | 17320.8567 | 25682.2982 | 353.1091 | 523.5684
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.713 | 10.4102 | 0.45249 | 4 | 16952.1218 | 25028.1939 | 345.5919 | 510.2336 | 83.1286 | 0 | 140.6675 | 1584143.1109 | 90827.5222 | 2285432.2322 | 2619138.7706 | 0 | 189757.8123 | 0 | 2640026.7848 | 6868808.1502 | 4688102.7024 | 20966237.0856 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30682628.5556 | 45299979.8423 | 1000000 | 1.81 | 16952.1218 | 25028.1939 | 345.5919 | 510.2336
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4038 | 10.6046 | 0.46458 | 4 | 16676.5429 | 24542.4228 | 339.9739 | 500.3305 | 83.1211 | 0 | 161.0936 | 1604805.43 | 92000.7018 | 2319526.2142 | 2667797.5594 | 0 | 184543.6342 | 0 | 2678782.6805 | 6969643.0407 | 4756924.5871 | 21274023.8478 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 30990415.3178 | 45607766.6045 | 1333521.4322 | 1.8583 | 16676.5429 | 24542.4228 | 339.9739 | 500.3305
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.6755 | 10.7507 | 0.47387 | 4 | 16470.4286 | 24182.042 | 335.772 | 492.9836 | 83.115 | 0 | 136.6411 | 1620247.2075 | 92877.011 | 2345060.8979 | 2704373.3267 | 0 | 180134.4971 | 0 | 2707650.2466 | 7044750.5263 | 4808186.9894 | 21503280.7025 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31219672.1724 | 45837023.4592 | 1778279.41 | 1.8955 | 16470.4286 | 24182.042 | 335.772 | 492.9836
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6501 | 10.8625 | 0.48103 | 4 | 16316.1741 | 23913.0128 | 332.6273 | 487.4991 | 83.1101 | 0 | 139.3205 | 1632024.6727 | 93545.1077 | 2364567.8929 | 2732391.3659 | 0 | 176622.5789 | 0 | 2729669.1311 | 7102039.1469 | 4847287.6501 | 21678147.5462 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31394539.0161 | 46011890.3029 | 2371373.7057 | 1.9241 | 16316.1741 | 23913.0128 | 332.6273 | 487.4991
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3929 | 10.9477 | 0.48651 | 4 | 16200.6748 | 23711.9715 | 330.2727 | 483.4006 | 83.1062 | 0 | 144.7527 | 1640967.3097 | 94052.2387 | 2379397.915 | 2753735.9327 | 0 | 173864.5246 | 0 | 2746386.9891 | 7145535.5841 | 4876974.8622 | 21810915.3561 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31527306.8261 | 46144658.1128 | 3162277.6602 | 1.946 | 16200.6748 | 23711.9715 | 330.2727 | 483.4006
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9607 | 11.0128 | 0.4907 | 4 | 16114.1617 | 23561.4114 | 328.509 | 480.3312 | 83.1031 | 0 | 130.2386 | 1647785.6237 | 94438.8098 | 2390715.7265 | 2770051.012 | 0 | 171743.018 | 0 | 2759146.3341 | 7178732.7826 | 4899632.6324 | 21912245.9392 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31628637.4091 | 46245988.6958 | 4216965.0343 | 1.9628 | 16114.1617 | 23561.4114 | 328.509 | 480.3312
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.3823 | 11.0611 | 0.49384 | 4 | 16049.3415 | 23449.1265 | 327.1875 | 478.0422 | 83.1007 | 0 | 126.3751 | 1652836.4616 | 94725.1209 | 2399105.6473 | 2782159.6913 | 0 | 170068.3231 | 0 | 2768569.1453 | 7203249.0044 | 4916365.4575 | 21987078.8514 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31703470.3213 | 46320821.6081 | 5623413.2519 | 1.9754 | 16049.3415 | 23449.1265 | 327.1875 | 478.0422
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.6964 | 11.0971 | 0.49621 | 4 | 16000.7646 | 23365.248 | 326.1972 | 476.3322 | 83.099 | 0 | 150.2491 | 1656594.295 | 94938.1085 | 2405351.0634 | 2791181.2131 | 0 | 168766.6341 | 0 | 2775564.2125 | 7221448.7345 | 4928787.1472 | 22042631.4084 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31759022.8784 | 46376374.1651 | 7498942.0933 | 1.9848 | 16000.7646 | 23365.248 | 326.1972 | 476.3322
1 | 2800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.9204 | 11.1227 | 0.49796 | 4 | 15964.3546 | 23303.0244 | 325.455 | 475.0637 | 83.0977 | 0 | 135.3089 | 1659270.2258 | 95089.7607 | 2409800.1146 | 2797611.9877 | 0 | 167712.1571 | 0 | 2780498.8559 | 7234287.6644 | 4937549.9807 | 22081820.7471 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31798212.217 | 46415563.5038 | 10000000 | 1.9918 | 15964.3546 | 23303.0244 | 325.455 | 475.0637
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.5294 | [19 empty] | 100 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2947 | [19 empty] | 133.3521 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2451 | [19 empty] | 177.8279 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.627 | [19 empty] | 237.1374 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4069 | [19 empty] | 316.2278 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0926 | [19 empty] | 421.6965 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5237 | [19 empty] | 562.3413 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2651 | [19 empty] | 749.8942 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.706 | [19 empty] | 1000 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.525 | [19 empty] | 1333.5214 | 0
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.14802 | 0.0015535 | 4 | 1754473.6039 | 4190189.7504 | 35767.3175 | 85422.6857 | 73.552 | 0 | 246.8815 | 74093.5419 | 3968.042 | 76668.3939 | 66175.0523 | 0 | 42480.9651 | 0 | 102720.5382 | 267257.7694 | 182408.9192 | 815773.2221 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 10902371.7465 | 26038012.9095 | 1778.2794 | 0.006214 | 1754473.6039 | 4190189.7504 | 35767.3175 | 85422.6857
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.21922 | 0.0033577 | 4 | 830547.6275 | 1957467.4362 | 16931.8368 | 39905.6214 | 76.5885 | 0 | 353.3343 | 100487.7928 | 5499.0936 | 104705.3847 | 83860.2418 | 0 | 50421.7616 | 0 | 134539.9671 | 350045.3965 | 238913.1758 | 1068472.814 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11155071.3384 | 26290712.5013 | 2371.3737 | 0.013431 | 830547.6275 | 1957467.4362 | 16931.8368 | 39905.6214
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9787 | 0.31382 | 0.0059293 | 4 | 483378.2599 | 1121554.5349 | 9854.3196 | 22864.4062 | 78.8622 | 0 | 71.6109 | 131839.7122 | 7331.4686 | 139258.7359 | 106909.0212 | 0 | 59472.7526 | 0 | 173476.5594 | 451350.4225 | 308055.9377 | 1377694.6103 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11464293.1347 | 26599934.2976 | 3162.2777 | 0.023717 | 483378.2599 | 1121554.5349 | 9854.3196 | 22864.4062
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0434 | 0.44355 | 0.0095167 | 4 | 311558.0939 | 709164.1953 | 6351.5332 | 14457.2713 | 80.6156 | 0 | 97.1981 | 170504.4462 | 9601.2226 | 183407.9611 | 138415.5093 | 0 | 70661.9129 | 0 | 223310.5104 | 581008.1407 | 396549.9945 | 1773459.6978 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11860058.2222 | 26995699.3852 | 4216.965 | 0.038067 | 311558.0939 | 709164.1953 | 6351.5332 | 14457.2713
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3487 | 0.60336 | 0.014369 | 4 | 214238.9794 | 477569.9745 | 4367.5514 | 9735.9099 | 81.848 | 0 | 95.0601 | 213624.2215 | 12136.8482 | 234366.3864 | 177142.2318 | 0 | 81867.4163 | 0 | 280463.4706 | 729708.4196 | 498040.9904 | 2227349.9849 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12313948.5093 | 27449589.6723 | 5623.4133 | 0.057478 | 214238.9794 | 477569.9745 | 4367.5514 | 9735.9099
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.954 | 0.79981 | 0.020766 | 4 | 154550.5582 | 336770.595 | 3150.7222 | 6865.5241 | 82.7273 | 0 | 103.7568 | 261980.9939 | 14978.571 | 293444.6964 | 224482.5007 | 0 | 93238.1855 | 0 | 346368.7295 | 901180.3842 | 615074.1296 | 2750748.1908 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12837346.7152 | 27972987.8782 | 7498.9421 | 0.083062 | 154550.5582 | 336770.595 | 3150.7222 | 6865.5241
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3829 | 1.099 | 0.029653 | 4 | 114678.2949 | 242285.1821 | 2337.8722 | 4939.3112 | 83.5411 | 0 | 107.063 | 329373.7157 | 18944.0792 | 378125.6636 | 296903.5572 | 0 | 111711.226 | 0 | 442672.7143 | 1151743.5978 | 786088.6715 | 3515563.2252 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 13602161.7496 | 28737802.9126 | 10000 | 0.11861 | 114678.2949 | 242285.1821 | 2337.8722 | 4939.3112
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8922 | 1.4081 | 0.040941 | 4 | 87555.8824 | 179978.4868 | 1784.9451 | 3669.1049 | 84.0298 | 0 | 95.3621 | 393340.5936 | 22704.4145 | 460886.8847 | 371920.5562 | 0 | 123989.9597 | 0 | 535408.5394 | 1393023.1921 | 950766.9524 | 4252041.0925 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 14338639.6169 | 29474280.7799 | 13335.2143 | 0.16377 | 87555.8824 | 179978.4868 | 1784.9451 | 3669.1049
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.3 | 1.8272 | 0.055724 | 4 | 68620.9482 | 136525.5898 | 1398.9308 | 2783.2588 | 84.4373 | 0 | 121.6765 | 473466.6949 | 27404.3874 | 567503.6986 | 472615.337 | 0 | 140726.9374 | 0 | 655869.6516 | 1706438.296 | 1164679.2008 | 5208704.2038 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 15295302.7282 | 30430943.8911 | 17782.7941 | 0.2229 | 68620.9482 | 136525.5898 | 1398.9308 | 2783.2588
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5339 | 2.348 | 0.074786 | 4 | 54926.343 | 105523.1794 | 1119.7478 | 2151.2327 | 84.7483 | 0 | 120.059 | 565703.7951 | 32807.3329 | 693423.5686 | 597732.9848 | 0 | 158656.7015 | 0 | 798846.5093 | 2078434.7513 | 1418574.4254 | 6344180.0689 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 16430778.5933 | 31566419.7563 | 23713.7371 | 0.29914 | 54926.343 | 105523.1794 | 1119.7478 | 2151.2327
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6862 | 2.9819 | 0.098962 | 4 | 44850.3173 | 83086.2676 | 914.3344 | 1693.8259 | 84.9851 | 0 | 103.8463 | 670073.8213 | 38911.9183 | 839390.7572 | 750003.1922 | 0 | 177145.5538 | 0 | 965454.8447 | 2511915.4639 | 1714433.9188 | 7667329.4702 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 17753927.9946 | 32889569.1576 | 31622.7766 | 0.39585 | 44850.3173 | 83086.2676 | 914.3344 | 1693.8259
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.825 | 3.7379 | 0.12904 | 4 | 37333.7406 | 66657.1331 | 761.0988 | 1358.8958 | 85.1658 | 0 | 102.9262 | 786286.8326 | 45700.0882 | 1005567.4251 | 931967.0289 | 0 | 195584.7064 | 0 | 1156391.3717 | 3008693.1406 | 2053494.8909 | 9183685.4845 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 19270284.0089 | 34405925.1718 | 42169.6503 | 0.51616 | 37333.7406 | 66657.1331 | 761.0988 | 1358.8958
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8702 | 4.6058 | 0.16525 | 4 | 31688.8628 | 54587.4362 | 646.0203 | 1112.8387 | 85.3029 | 0 | 105.7493 | 911408.876 | 52997.3258 | 1188239.7169 | 1140859.0688 | 0 | 212602.051 | 0 | 1367381.745 | 3557646.812 | 2428167.0515 | 10859302.6471 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 20945901.1715 | 36081542.3345 | 56234.1325 | 0.66099 | 31688.8628 | 54587.4362 | 646.0203 | 1112.8387
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.6265 | 5.5614 | 0.20712 | 4 | 27432.0825 | 45700.9698 | 559.2401 | 931.6761 | 85.4053 | 0 | 105.5202 | 1041346.9405 | 60563.472 | 1381555.8451 | 1370840.2482 | 0 | 226949.1169 | 0 | 1591689.6928 | 4141250.0803 | 2826488.274 | 12640683.6697 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 22727282.194 | 37862923.357 | 74989.4209 | 0.82849 | 27432.0825 | 45700.9698 | 559.2401 | 931.6761
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.636 | 6.5476 | 0.25294 | 4 | 24222.2864 | 39182.1025 | 493.8041 | 798.7802 | 85.4767 | 0 | 138.3058 | 1168688.8004 | 67966.1842 | 1574227.0895 | 1608282.0082 | 0 | 236695.0248 | 0 | 1815785.0518 | 4724300.236 | 3224431.9857 | 14420376.3806 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 24506974.905 | 39642616.0679 | 100000 | 1.0118 | 24222.2864 | 39182.1025 | 493.8041 | 798.7802
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.7749 | 7.5485 | 0.30166 | 4 | 21766.0387 | 34309.7276 | 443.7301 | 699.4502 | 85.522 | 0 | 111.631 | 1292170.941 | 75131.4655 | 1763900.0955 | 1849424.8171 | 0 | 242401.017 | 0 | 2036981.051 | 5299806.8525 | 3617227.077 | 16177043.3165 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 26263641.8409 | 41399283.0039 | 133352.1432 | 1.2066 | 21766.0387 | 34309.7276 | 443.7301 | 699.4502
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.9413 | 8.4278 | 0.34751 | 4 | 19973.8379 | 30862.397 | 407.1937 | 629.1717 | 85.5421 | 0 | 138.7736 | 1396601.9302 | 81179.6068 | 1926419.8714 | 2061551.2776 | 0 | 241895.6553 | 0 | 2225982.8531 | 5791550.772 | 3952852.4063 | 17678034.3728 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 27764632.8972 | 42900274.0602 | 177827.941 | 1.39 | 19973.8379 | 30862.397 | 407.1937 | 629.1717
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.1971 | 9.1934 | 0.38961 | 4 | 18635.4079 | 28347.3597 | 379.908 | 577.8993 | 85.546 | 0 | 136.6603 | 1484803.5155 | 86278.2888 | 2065169.7052 | 2246511.9817 | 0 | 237448.5864 | 0 | 2386882.7102 | 6210179.1951 | 4238574.9071 | 18955848.89 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 29042447.4144 | 44178088.5773 | 237137.3706 | 1.5585 | 18635.4079 | 28347.3597 | 379.908 | 577.8993
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.4519 | 9.8345 | 0.42655 | 4 | 17637.1961 | 26508.2025 | 359.5581 | 540.4056 | 85.54 | 0 | 104.0618 | 1556917.6267 | 90439.7812 | 2179623.2254 | 2401688.1407 | 0 | 230552.5636 | 0 | 2519096.3216 | 6554171.8912 | 4473356.9905 | 20005846.5409 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 30092445.0653 | 45228086.2282 | 316227.766 | 1.7062 | 17637.1961 | 26508.2025 | 359.5581 | 540.4056
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.7413 | 10.3565 | 0.45779 | 4 | 16892.8752 | 25158.4782 | 344.3841 | 512.8896 | 85.5292 | 0 | 149.7109 | 1614521.0981 | 93758.8434 | 2271702.9118 | 2528206.9911 | 0 | 222598.3671 | 0 | 2625007.4025 | 6829730.7982 | 4661431.6067 | 20846958.0189 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 30933556.5432 | 46069197.7062 | 421696.5034 | 1.8312 | 16892.8752 | 25158.4782 | 344.3841 | 512.8896
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.1667 | 10.7723 | 0.48347 | 4 | 16337.6054 | 24164.2354 | 333.0642 | 492.6206 | 85.5169 | 0 | 118.1066 | 1659743.3214 | 96361.1568 | 2344402.0458 | 2629139.8161 | 0 | 214607.4602 | 0 | 2708258.9821 | 7046334.3312 | 4809267.9687 | 21508115.0823 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 31594713.6067 | 46730354.7696 | 562341.3252 | 1.9339 | 16337.6054 | 24164.2354 | 333.0642 | 492.6206
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.8339 | 11.0954 | 0.50402 | 4 | 15923.0467 | 23430.4836 | 324.6128 | 477.6621 | 85.5052 | 0 | 127.0681 | 1694491.9573 | 98358.6693 | 2400511.1146 | 2707663.5329 | 0 | 207091.0098 | 0 | 2772165.3507 | 7212605.5932 | 4922751.5216 | 22015638.7494 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32102237.2738 | 47237878.4367 | 749894.2093 | 2.0161 | 15923.0467 | 23430.4836 | 324.6128 | 477.6621
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.9191 | 11.3475 | 0.52031 | 4 | 15613.2818 | 22885.6553 | 318.2979 | 466.555 | 85.4948 | 0 | 144.3129 | 1721381.8558 | 99903.13 | 2444078.9115 | 2769008.5851 | 0 | 200609.4783 | 0 | 2821642.9647 | 7341336.1955 | 5010612.8028 | 22408573.9237 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32495172.4481 | 47630813.611 | 1000000 | 2.0813 | 15613.2818 | 22885.6553 | 318.2979 | 466.555
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.5003 | 11.5385 | 0.53294 | 4 | 15381.6426 | 22481.7097 | 313.5756 | 458.3201 | 85.4862 | 0 | 119.8964 | 1741614.1015 | 101064.4335 | 2476945.5752 | 2815500.7519 | 0 | 195039.1222 | 0 | 2858763.9539 | 7437917.395 | 5076531.456 | 22703376.7893 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 32789975.3137 | 47925616.4767 | 1333521.4322 | 2.1318 | 15381.6426 | 22481.7097 | 313.5756 | 458.3201
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.7112 | 11.6846 | 0.5427 | 4 | 15208.3127 | 22180.6785 | 310.042 | 452.1831 | 85.4792 | 0 | 133.9816 | 1757017.4495 | 101948.116 | 2502017.4291 | 2851090.392 | 0 | 190507.7158 | 0 | 2887006.63 | 7511399.0447 | 5126684.1918 | 22927670.969 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33014269.4934 | 48149910.6563 | 1778279.41 | 2.1708 | 15208.3127 | 22180.6785 | 310.042 | 452.1831
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.6392 | 11.7965 | 0.55021 | 4 | 15078.5465 | 21955.7678 | 307.3966 | 447.598 | 85.4735 | 0 | 127.3901 | 1768768.1817 | 102621.9851 | 2521172.8778 | 2878353.6895 | 0 | 186922.7069 | 0 | 2908557.382 | 7567469.6808 | 5164953.5531 | 23098820.0571 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33185418.5814 | 48321059.7444 | 2371373.7057 | 2.2008 | 15078.5465 | 21955.7678 | 307.3966 | 447.598
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.3307 | 11.8798 | 0.55589 | 4 | 14981.3558 | 21788.2673 | 305.4152 | 444.1833 | 85.4692 | 0 | 156.0994 | 1777494.9179 | 103122.287 | 2535415.0148 | 2898664.436 | 0 | 184039.6797 | 0 | 2924507.1708 | 7608967.7595 | 5193276.8445 | 23225488.1102 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33312086.6346 | 48447727.7975 | 3162277.6602 | 2.2236 | 14981.3558 | 21788.2673 | 305.4152 | 444.1833
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8714 | 11.9449 | 0.56027 | 4 | 14908.5406 | 21662.2466 | 303.9308 | 441.6142 | 85.4657 | 0 | 129.49 | 1784300.6969 | 103512.3718 | 2546531.735 | 2914541.9046 | 0 | 181892.9657 | 0 | 2937004.0729 | 7641482.1354 | 5215468.5741 | 23324734.4566 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33411332.981 | 48546974.144 | 4216965.0343 | 2.2411 | 14908.5406 | 21662.2466 | 303.9308 | 441.6142
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.2586 | 11.9915 | 0.56351 | 4 | 14853.9747 | 21568.8281 | 302.8184 | 439.7097 | 85.4632 | 0 | 148.3864 | 1789166.2902 | 103791.2028 | 2554484.5113 | 2925913.3431 | 0 | 180130.2759 | 0 | 2945859.3931 | 7664521.862 | 5231193.661 | 23395060.5395 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33481659.0639 | 48617300.2268 | 5623413.2519 | 2.2541 | 14853.9747 | 21568.8281 | 302.8184 | 439.7097
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5487 | 12.0264 | 0.56596 | 4 | 14813.0774 | 21498.9558 | 301.9846 | 438.2853 | 85.4613 | 0 | 146.1229 | 1792805.0828 | 103999.7035 | 2560434.9193 | 2934428.6636 | 0 | 178773.1082 | 0 | 2952472.1761 | 7681726.967 | 5242936.4987 | 23447577.1191 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33534175.6435 | 48669816.8064 | 7498942.0933 | 2.2638 | 14813.0774 | 21498.9558 | 301.9846 | 438.2853
1 | 2900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7728 | 12.0534 | 0.56782 | 4 | 14782.4205 | 21446.3739 | 301.3596 | 437.2133 | 85.4598 | 0 | 144.9758 | 1795613.7557 | 104160.6233 | 2565029.5062 | 2941007.8331 | 0 | 177770.77 | 0 | 2957597.1704 | 7695061.1509 | 5252037.3532 | 23488278.1627 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33574876.6871 | 48710517.8501 | 10000000 | 2.2713 | 14782.4205 | 21446.3739 | 301.3596 | 437.2133
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.42 | [19 empty] | 100 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0605 | [19 empty] | 133.3521 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5546 | [19 empty] | 177.8279 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1767 | [19 empty] | 237.1374 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8162 | [19 empty] | 316.2278 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7829 | [19 empty] | 421.6965 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4464 | [19 empty] | 562.3413 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8025 | [19 empty] | 749.8942 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.314 | [19 empty] | 1000 | 0
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.15434 | 0.00062709 | 4 | 4513854.7862 | 10757803.9629 | 92021.0353 | 219312.3848 | 75.1565 | 0 | 32.4831 | 77717.2853 | 4203.298 | 79168.3797 | 67177.2912 | 0 | 49319.1936 | 0 | 108258.3247 | 281665.9539 | 192242.8012 | 859752.5277 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11322418.1974 | 26984553.3638 | 1333.5214 | 0.0025084 | 4513854.7862 | 10757803.9629 | 92021.0353 | 219312.3848
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.17756 | 0.0023585 | 4 | 1207331.1784 | 2867510.4529 | 24613.0791 | 58458.0792 | 76.3758 | 0 | 284.5668 | 86714.4267 | 4728.9204 | 88474.8164 | 72678.6355 | 0 | 46797.315 | 0 | 116763.7045 | 303795.2075 | 207346.4715 | 927299.4974 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11389965.1671 | 27052100.3335 | 1778.2794 | 0.009434 | 1207331.1784 | 2867510.4529 | 24613.0791 | 58458.0792
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.26808 | 0.0046485 | 4 | 629273.9629 | 1471600.437 | 12828.6009 | 30000.5654 | 79.5061 | 0 | 410.506 | 119028.3353 | 6632.6917 | 122705.7732 | 94189.0139 | 0 | 57150.6137 | 0 | 155885.5068 | 405582.1123 | 276818.1255 | 1237992.1724 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11700657.8421 | 27362793.0085 | 2371.3737 | 0.018594 | 629273.9629 | 1471600.437 | 12828.6009 | 30000.5654
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.38202 | 0.0079068 | 4 | 381314.8402 | 876526.4356 | 7773.6188 | 17869.177 | 81.6676 | 0 | 71.5327 | 155372.3588 | 8789.6465 | 162617.9037 | 121221.1875 | 0 | 67694.122 | 0 | 201121.1352 | 523275.9383 | 357146.5801 | 1597238.8722 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12059904.5419 | 27722039.7083 | 3162.2777 | 0.031627 | 381314.8402 | 876526.4356 | 7773.6188 | 17869.177
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5723 | 0.53243 | 0.012382 | 4 | 252410.3532 | 568640.0453 | 5145.7265 | 11592.4965 | 83.2837 | 0 | 92.2603 | 198583.3641 | 11361.3712 | 211814.1721 | 156596.6319 | 0 | 79854.4451 | 0 | 256701.8939 | 667885.6711 | 455845.6942 | 2038643.2436 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12501308.9133 | 28163444.0797 | 4216.965 | 0.049528 | 252410.3532 | 568640.0453 | 5145.7265 | 11592.4965
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9601 | 0.71119 | 0.018387 | 4 | 176622.7095 | 389568.7937 | 3600.6928 | 7941.8868 | 84.3986 | 0 | 110.152 | 245353.4606 | 14149.084 | 266777.395 | 198766.5035 | 0 | 91126.2129 | 0 | 318307.3359 | 828170.3941 | 565243.3112 | 2527893.6973 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12990559.367 | 28652694.5334 | 5623.4133 | 0.07355 | 176622.7095 | 389568.7937 | 3600.6928 | 7941.8868
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7265 | 0.93786 | 0.026216 | 4 | 129455.31 | 278810.9262 | 2639.1216 | 5683.9379 | 85.2113 | 0 | 83.7362 | 299545.6014 | 17372.3142 | 332659.3417 | 251740.2256 | 0 | 103646.8584 | 0 | 391936.0931 | 1019737.3171 | 695991.6724 | 3112629.424 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 13575295.0937 | 29237430.2601 | 7498.9421 | 0.10486 | 129455.31 | 278810.9262 | 2639.1216 | 5683.9379
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2527 | 1.2656 | 0.037124 | 4 | 96862.5996 | 202333.3555 | 1974.6751 | 4124.8391 | 85.9961 | 0 | 107.819 | 371674.1509 | 21671.5866 | 422526.4803 | 328330.3084 | 0 | 121816.0128 | 0 | 493747.2302 | 1284629.0114 | 876785.6968 | 3921180.4773 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 14383846.147 | 30045981.3134 | 10000 | 0.1485 | 96862.5996 | 202333.3555 | 1974.6751 | 4124.8391
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.254 | 1.6538 | 0.051139 | 4 | 74735.3956 | 151301.4407 | 1523.5821 | 3084.4845 | 86.5064 | 0 | 93.9825 | 450009.9808 | 26331.7129 | 523165.4439 | 419360.3383 | 0 | 138963.2995 | 0 | 607554.0024 | 1580730.8878 | 1078881.3117 | 4824996.9773 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 15287662.647 | 30949797.8134 | 13335.2143 | 0.20456 | 74735.3956 | 151301.4407 | 1523.5821 | 3084.4845
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0077 | 2.1396 | 0.069349 | 4 | 58995.3078 | 115456.469 | 1202.6991 | 2353.7363 | 86.8948 | 0 | 96.8209 | 540591.6686 | 31712.8503 | 642671.4977 | 533234.3986 | 0 | 157488.6212 | 0 | 743222.6242 | 1933712.8122 | 1319798.7282 | 5902433.201 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 16365098.8707 | 32027234.0371 | 17782.7941 | 0.2774 | 58995.3078 | 115456.469 | 1202.6991 | 2353.7363
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6144 | 2.736 | 0.092654 | 4 | 47562.6184 | 89822.441 | 969.6283 | 1831.152 | 87.1898 | 0 | 105.5593 | 643683.5087 | 37826.7526 | 782174.5403 | 672789.199 | 0 | 176790.4223 | 0 | 902173.1249 | 2347269.4098 | 1602059.6038 | 7164766.5614 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 17627432.2311 | 33289567.3974 | 23713.7371 | 0.37062 | 47562.6184 | 89822.441 | 969.6283 | 1831.152
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.2124 | 3.4607 | 0.12206 | 4 | 39115.3928 | 71194.6103 | 797.4202 | 1451.3984 | 87.416 | 0 | 96.5196 | 760319.7525 | 44732.23 | 943783.8611 | 842272.981 | 0 | 196768.4907 | 0 | 1087272.1529 | 2828859.1117 | 1930754.471 | 8634763.0509 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 19097428.7206 | 34759563.887 | 31622.7766 | 0.48823 | 39115.3928 | 71194.6103 | 797.4202 | 1451.3984
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8166 | 4.3159 | 0.15827 | 4 | 32797.864 | 57537.34 | 668.6288 | 1172.9765 | 87.5887 | 0 | 119.2691 | 888985.9747 | 52337.3749 | 1126016.1605 | 1042241.2881 | 0 | 216299.8542 | 0 | 1297093.4545 | 3374771.0982 | 2303350.6191 | 10301095.8243 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 20763761.494 | 36425896.6604 | 42169.6503 | 0.63308 | 32797.864 | 57537.34 | 668.6288 | 1172.9765
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.2996 | 5.2852 | 0.20135 | 4 | 28038.5825 | 47484.8935 | 571.6044 | 968.0438 | 87.7192 | 0 | 130.1941 | 1025991.9911 | 60422.0609 | 1324003.7788 | 1268837.0951 | 0 | 233798.4436 | 0 | 1526090.8141 | 3970575.2541 | 2709999.1981 | 12119718.6359 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 22582384.3056 | 38244519.472 | 56234.1325 | 0.8054 | 28038.5825 | 47484.8935 | 571.6044 | 968.0438
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3971 | 6.3339 | 0.25041 | 4 | 24443.4681 | 40080.1452 | 498.3132 | 817.088 | 87.8147 | 0 | 138.51 | 1166098.0152 | 68675.6456 | 1530188.5687 | 1514023.7283 | 0 | 247798.2445 | 0 | 1765445.8389 | 4593327.93 | 3135040.6957 | 14020598.6667 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 24483264.3364 | 40145399.5028 | 74989.4209 | 1.0016 | 24443.4681 | 40080.1452 | 498.3132 | 817.088
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.6092 | 7.3965 | 0.30312 | 4 | 21731.6034 | 34649.2206 | 443.0281 | 706.3712 | 87.8781 | 0 | 139.4555 | 1301185.772 | 76619.087 | 1732244.1104 | 1762598.1686 | 0 | 256446.3587 | 0 | 2000346.4637 | 5204491.1711 | 3552172.1659 | 15886103.2975 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 26348768.9672 | 42010904.1336 | 100000 | 1.2125 | 21731.6034 | 34649.2206 | 443.0281 | 706.3712
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.128 | 8.2386 | 0.35299 | 4 | 19659.142 | 30751.4916 | 400.7782 | 626.9107 | 87.9087 | 0 | 315.2982 | 1404129.685 | 82661.4614 | 1888262.3933 | 1959793.3124 | 0 | 249319.0372 | 0 | 2177824.6968 | 5666253.1279 | 3867334.1896 | 17295577.9036 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 27758243.5733 | 43420378.7397 | 133352.1432 | 1.412 | 19659.142 | 30751.4916 | 400.7782 | 626.9107
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.9003 | 9.3689 | 0.40901 | 4 | 18139.5375 | 27712.7267 | 369.799 | 564.9614 | 87.9256 | 0 | 106.4573 | 1537382.4303 | 90466.5165 | 2092774.5952 | 2224881.8218 | 0 | 258174.957 | 0 | 2419435.3251 | 6294874.4216 | 4296381.1395 | 19214371.2071 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 29677036.8768 | 45339172.0432 | 177827.941 | 1.636 | 18139.5375 | 27712.7267 | 369.799 | 564.9614
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.0144 | 10.1539 | 0.45495 | 4 | 17009.6757 | 25616.1012 | 346.7652 | 522.2189 | 87.9221 | 0 | 134.6328 | 1626997.9959 | 95703.7763 | 2231929.5068 | 2409396.7833 | 0 | 252111.7002 | 0 | 2580294.5074 | 6713397.0169 | 4582031.4106 | 20491862.6973 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 30954528.367 | 46616663.5334 | 237137.3706 | 1.8198 | 17009.6757 | 25616.1012 | 346.7652 | 522.2189
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0936 | 10.804 | 0.49474 | 4 | 16166.5711 | 24080.9215 | 329.5774 | 490.9222 | 87.9104 | 0 | 127.5225 | 1699558.8575 | 99936.5826 | 2345556.6524 | 2562491.8868 | 0 | 243851.4864 | 0 | 2711044.2316 | 7053580.979 | 4814213.9548 | 21530234.631 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 31992900.3007 | 47655035.4671 | 316227.766 | 1.979 | 16166.5711 | 24080.9215 | 329.5774 | 490.9222
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.2056 | 11.3288 | 0.52805 | 4 | 15537.4665 | 22952.5724 | 316.7523 | 467.9192 | 87.8954 | 0 | 117.9019 | 1757114.2647 | 103288.7366 | 2436297.7587 | 2686297.979 | 0 | 234835.6213 | 0 | 2814955.4005 | 7323936.5254 | 4998737.1704 | 22355463.4567 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 32818129.1264 | 48480264.2928 | 421696.5034 | 2.1122 | 15537.4665 | 22952.5724 | 316.7523 | 467.9192
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.8207 | 11.789 | 0.55738 | 4 | 15042.0176 | 22066.9304 | 306.6519 | 449.8642 | 87.8783 | 0 | 138.3828 | 1806872.2933 | 106182.7583 | 2515184.5339 | 2795034.3607 | 0 | 226458.1744 | 0 | 2905395.527 | 7559243.1828 | 5159338.7992 | 23073709.6296 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33536375.2993 | 49198510.4657 | 562341.3252 | 2.2295 | 15042.0176 | 22066.9304 | 306.6519 | 449.8642
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.025 | 12.069 | 0.57692 | 4 | 14716.9149 | 21503.9289 | 300.0242 | 438.3867 | 87.8661 | 0 | 128.8547 | 1836833.1407 | 107923.435 | 2562884.3526 | 2861280.5001 | 0 | 218123.135 | 0 | 2958947.3797 | 7698574.1183 | 5254435.0256 | 23499001.0869 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33961666.7566 | 49623801.923 | 749894.2093 | 2.3077 | 14716.9149 | 21503.9289 | 300.0242 | 438.3867
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.9935 | 12.3186 | 0.59396 | 4 | 14454.5689 | 21046.8648 | 294.6759 | 429.0688 | 87.8542 | 0 | 124.4708 | 1863354.4274 | 109463.083 | 2605232.4971 | 2920404.982 | 0 | 211228.9947 | 0 | 3006776.7538 | 7823016.3387 | 5339369.3981 | 23878846.4749 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34341512.1446 | 50003647.311 | 1000000 | 2.3758 | 14454.5689 | 21046.8648 | 294.6759 | 429.0688
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.5035 | 12.5099 | 0.6072 | 4 | 14258.2916 | 20706.8193 | 290.6746 | 422.1365 | 87.8444 | 0 | 122.5731 | 1883549.9686 | 110634.7197 | 2637559.1689 | 2965734.8 | 0 | 205487.4498 | 0 | 3043156.7817 | 7917669.7088 | 5403972.2681 | 24167764.8656 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34630430.5353 | 50292565.7017 | 1333521.4322 | 2.4288 | 14258.2916 | 20706.8193 | 290.6746 | 422.1365
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.6413 | 12.6538 | 0.61734 | 4 | 14111.3635 | 20453.9097 | 287.6792 | 416.9806 | 87.8366 | 0 | 138.1496 | 1898683.2249 | 111512.219 | 2661827.8375 | 2999877.1542 | 0 | 200753.31 | 0 | 3070334.9608 | 7988381.7558 | 5452234.6931 | 24383605.1554 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 34846270.8251 | 50508405.9915 | 1778279.41 | 2.4694 | 14111.3635 | 20453.9097 | 287.6792 | 416.9806
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5233 | 12.7653 | 0.62518 | 4 | 14001.3291 | 20264.4065 | 285.436 | 413.1173 | 87.8304 | 0 | 138.0247 | 1910365.2073 | 112189.3298 | 2680588.3141 | 3026335.9011 | 0 | 197087.7123 | 0 | 3091360.9212 | 8043086.9916 | 5489572.1407 | 24550586.518 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35013252.1877 | 50675387.3541 | 2371373.7057 | 2.5007 | 14001.3291 | 20264.4065 | 285.436 | 413.1173
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1734 | 12.8475 | 0.63107 | 4 | 13918.8967 | 20123.472 | 283.7555 | 410.2442 | 87.8256 | 0 | 151.4216 | 1918948.6388 | 112686.6919 | 2694387.5129 | 3045834.0464 | 0 | 194116.2587 | 0 | 3106729.528 | 8083072.954 | 5516863.3817 | 24672639.0124 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35135304.6821 | 50797439.8485 | 3162277.6602 | 2.5243 | 13918.8967 | 20123.472 | 283.7555 | 410.2442
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6681 | 12.91 | 0.63556 | 4 | 13857.127 | 20017.913 | 282.4963 | 408.0922 | 87.8219 | 0 | 160.3667 | 1925464.758 | 113064.1794 | 2704871.5509 | 3060668.5541 | 0 | 191833.5677 | 0 | 3118402.0179 | 8113442.3785 | 5537591.1379 | 24765338.1444 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35228003.8141 | 50890138.9805 | 4216965.0343 | 2.5422 | 13857.127 | 20017.913 | 282.4963 | 408.0922
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.036 | 12.9564 | 0.63893 | 4 | 13810.8317 | 19939.102 | 281.5525 | 406.4856 | 87.8192 | 0 | 162.7677 | 1930301.0901 | 113344.3064 | 2712657.5983 | 3071697.0568 | 0 | 190050.4273 | 0 | 3127039.6868 | 8135915.821 | 5552929.7242 | 24833935.711 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35296601.3807 | 50958736.5471 | 5623413.2519 | 2.5557 | 13810.8317 | 19939.102 | 281.5525 | 406.4856
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.3138 | 12.9914 | 0.64148 | 4 | 13776.1294 | 19880.053 | 280.845 | 405.2818 | 87.8171 | 0 | 138.3074 | 1933949.1302 | 113555.5788 | 2718533.2447 | 3080026.0905 | 0 | 188693.0032 | 0 | 3133555.2485 | 8152867.9761 | 5564499.9184 | 24885680.1904 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35348345.8601 | 51010481.0265 | 7498942.0933 | 2.5659 | 13776.1294 | 19880.053 | 280.845 | 405.2818
1 | 3000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 13.0188 | 0.64343 | 4 | 13750.1143 | 19835.5231 | 280.3147 | 404.374 | 87.8154 | 0 | 142.2788 | 1936794.0282 | 113720.322 | 2723116.8921 | 3086527.5225 | 0 | 187703.8975 | 0 | 3138666.4383 | 8166166.2436 | 5573576.2592 | 24926271.6035 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 35388937.2732 | 51051072.4396 | 10000000 | 2.5737 | 13750.1143 | 19835.5231 | 280.3147 | 404.374
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.7931 | [19 empty] | 100 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8014 | [19 empty] | 133.3521 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5106 | [19 empty] | 177.8279 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3598 | [19 empty] | 237.1374 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6294 | [19 empty] | 316.2278 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0088 | [19 empty] | 421.6965 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0119 | [19 empty] | 562.3413 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0508 | [19 empty] | 749.8942 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4715 | [19 empty] | 1000 | 0
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.16029 | 0.0013724 | 4 | 2135096.7127 | 5085499.2738 | 43526.8344 | 103674.7813 | 76.7392 | 0 | 31.6362 | 81122.7901 | 4427.3099 | 81496.0698 | 67675.7207 | 0 | 48255.7662 | 0 | 110361.2861 | 287137.4282 | 195977.1948 | 876453.5658 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11721046.4717 | 27917879.7687 | 1333.5214 | 0.0054897 | 2135096.7127 | 5085499.2738 | 43526.8344 | 103674.7813
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.22036 | 0.0033685 | 4 | 885276.7219 | 2087351.782 | 18047.5634 | 42553.4894 | 79.5275 | 0 | 328.78 | 103993.667 | 5784.1952 | 104894.0965 | 81691.7567 | 0 | 53520.4842 | 0 | 136454.8379 | 355027.4974 | 242313.562 | 1083680.0969 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11928273.0027 | 28125106.2998 | 1778.2794 | 0.013474 | 885276.7219 | 2087351.782 | 18047.5634 | 42553.4894
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.32298 | 0.0062589 | 4 | 489944.9175 | 1136900.008 | 9988.1898 | 23177.2444 | 82.3362 | 0 | 82.9507 | 139232.1856 | 7894.0698 | 142106.8986 | 105458.764 | 0 | 64235.5793 | 0 | 178981.724 | 465673.7316 | 317831.8905 | 1421414.8435 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12266007.7493 | 28462841.0464 | 2371.3737 | 0.025035 | 489944.9175 | 1136900.008 | 9988.1898 | 23177.2444
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.805 | 0.45354 | 0.01031 | 4 | 307056.6394 | 699807.0341 | 6259.7649 | 14266.5129 | 84.3467 | 0 | 88.2864 | 179506.7791 | 10319.2819 | 186153.0928 | 135568.8023 | 0 | 75511.5038 | 0 | 228953.1893 | 595689.2339 | 406570.1423 | 1818272.0255 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12662864.9314 | 28859698.2284 | 3162.2777 | 0.04124 | 307056.6394 | 699807.0341 | 6259.7649 | 14266.5129
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0781 | 0.62507 | 0.01581 | 4 | 207917.8721 | 464033.0051 | 4238.6871 | 9459.9405 | 85.8646 | 0 | 99.0406 | 227298.8602 | 13201.3921 | 240333.2642 | 174592.4736 | 0 | 88531.3287 | 0 | 290143.3544 | 754893.4915 | 515230.3194 | 2304224.4841 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13148817.39 | 29345650.687 | 4216.965 | 0.06324 | 207917.8721 | 464033.0051 | 4238.6871 | 9459.9405
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6593 | 0.83878 | 0.023192 | 4 | 147867.23 | 322464.815 | 3014.4735 | 6573.8814 | 86.9521 | 0 | 81.5979 | 281578.4451 | 16478.2229 | 303818.2752 | 223546.7734 | 0 | 102030.5473 | 0 | 361706.3829 | 941085.8122 | 642310.4042 | 2872554.8633 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13717147.7692 | 29913981.0662 | 5623.4133 | 0.092767 | 147867.23 | 322464.815 | 3014.4735 | 6573.8814
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2197 | 1.1857 | 0.033374 | 4 | 109361.8803 | 230690.6677 | 2229.4899 | 4702.9413 | 87.9597 | 0 | 86.5336 | 361436.7753 | 21296.1526 | 400448.4914 | 302489.7173 | 0 | 126600.761 | 0 | 472786.04 | 1230092.2944 | 839563.2668 | 3754713.4987 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 14599306.4046 | 30796139.7016 | 7498.9421 | 0.1335 | 109361.8803 | 230690.6677 | 2229.4899 | 4702.9413
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3929 | 1.4813 | 0.046233 | 4 | 82649.3101 | 170232.0094 | 1684.918 | 3470.4098 | 88.4851 | 0 | 77.8729 | 424080.2141 | 25076.186 | 478304.5764 | 369989.445 | 0 | 136045.1933 | 0 | 559063.2898 | 1454568.0003 | 992772.5486 | 4439899.4535 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 15284492.3594 | 31481325.6564 | 10000 | 0.18493 | 82649.3101 | 170232.0094 | 1684.918 | 3470.4098
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.6862 | 1.9289 | 0.063358 | 4 | 64302.6014 | 128212.2792 | 1310.8955 | 2613.7807 | 88.9716 | 0 | 98.4979 | 512097.9589 | 30378.1085 | 590564.9551 | 472267.0191 | 0 | 154903.0922 | 0 | 686482.3422 | 1786086.2375 | 1219040.5575 | 5451820.271 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 16296413.1768 | 32493246.4739 | 13335.2143 | 0.25343 | 64302.6014 | 128212.2792 | 1310.8955 | 2613.7807
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.7787 | 2.4853 | 0.085493 | 4 | 51158.4301 | 98521.3644 | 1042.9338 | 2008.4913 | 89.3419 | 0 | 87.9475 | 613318.9288 | 36464.9865 | 723094.6169 | 599224.9882 | 0 | 175023.3859 | 0 | 837379.4934 | 2178689.6717 | 1487000.4685 | 6650196.5398 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 17494789.4457 | 33691622.7428 | 17782.7941 | 0.34197 | 51158.4301 | 98521.3644 | 1042.9338 | 2008.4913
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.8166 | 3.1704 | 0.11377 | 4 | 41542.5409 | 77132.7768 | 846.9009 | 1572.456 | 89.6255 | 0 | 121.3258 | 729057.0366 | 43413.1402 | 878393.1536 | 755513.3313 | 0 | 196279.7802 | 0 | 1015036.0123 | 2640915.4915 | 1802479.0884 | 8061087.0341 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 18905679.94 | 35102513.237 | 23713.7371 | 0.45509 | 41542.5409 | 77132.7768 | 846.9009 | 1572.456
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8628 | 3.9929 | 0.14919 | 4 | 34401.6024 | 61543.7214 | 701.3232 | 1254.652 | 89.8418 | 0 | 119.3092 | 858571.707 | 51174.8746 | 1056218.7112 | 943108.5166 | 0 | 217656.4473 | 0 | 1219424.8001 | 3172693.1915 | 2165428.2955 | 9684276.5437 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 20528869.4496 | 36725702.7467 | 31622.7766 | 0.59674 | 34401.6024 | 61543.7214 | 701.3232 | 1254.652
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.9151 | 4.9525 | 0.19238 | 4 | 29042.5931 | 50090.6288 | 592.0725 | 1021.1652 | 90.0068 | 0 | 107.295 | 1000053.6437 | 59638.9934 | 1254657.7261 | 1161934.375 | 0 | 238035.8303 | 0 | 1448585.0217 | 3768921.0809 | 2572366.0813 | 11504192.7524 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 22348785.6583 | 38545618.9553 | 42169.6503 | 0.76952 | 29042.5931 | 50090.6288 | 592.0725 | 1021.1652
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8151 | 6.0273 | 0.24316 | 4 | 24997.3075 | 41650.0379 | 509.6039 | 849.0924 | 90.1307 | 0 | 114.0954 | 1149216.9761 | 68546.7716 | 1467993.4623 | 1406916.4694 | 0 | 255814.3803 | 0 | 1695910.3433 | 4412410.8342 | 3011561.0603 | 13468370.2975 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 24312963.2034 | 40509796.5004 | 56234.1325 | 0.97262 | 24997.3075 | 41650.0379 | 509.6039 | 849.0924
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.2 | 7.1676 | 0.3 | 4 | 21938.8236 | 35436.0877 | 447.2526 | 722.4126 | 90.2184 | 0 | 133.2289 | 1299088.9999 | 77480.3054 | 1686149.9664 | 1666887.7709 | 0 | 269074.6056 | 0 | 1949485.8427 | 5072162.2683 | 3461854.9706 | 15482184.7297 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 26326777.6356 | 42523610.9327 | 74989.4209 | 1.2 | 21938.8236 | 35436.0877 | 447.2526 | 722.4126
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.5749 | 8.305 | 0.36004 | 4 | 19632.1561 | 30878.5591 | 400.2281 | 629.5012 | 90.2727 | 0 | 147.8657 | 1441624.8414 | 85959.2034 | 1896921.2735 | 1926391.4321 | 0 | 276419.6169 | 0 | 2194653.3832 | 5710037.9178 | 3897218.2085 | 17429225.8767 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 28273818.7826 | 44470652.0796 | 100000 | 1.4402 | 19632.1561 | 30878.5591 | 400.2281 | 629.5012
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4165 | 9.3674 | 0.4196 | 4 | 17899.3123 | 27549.5892 | 364.9017 | 561.6356 | 90.2978 | 0 | 143.9676 | 1569492.6288 | 93548.6877 | 2088637.8426 | 2169117.7728 | 0 | 277358.0132 | 0 | 2417280.4286 | 6289267.8227 | 4292554.5205 | 19197257.7169 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 30041850.6227 | 46238683.9198 | 133352.1432 | 1.6784 | 17899.3123 | 27549.5892 | 364.9017 | 561.6356
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.7512 | 10.3578 | 0.47743 | 4 | 16575.1234 | 25056.3782 | 337.9063 | 510.8082 | 90.301 | 0 | 125.4543 | 1684719.5783 | 100372.0145 | 2263511.181 | 2395834.2675 | 0 | 274184.23 | 0 | 2620262.2958 | 6817385.004 | 4653005.3485 | 20809273.9197 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 31653866.8256 | 47850700.1226 | 177827.941 | 1.9097 | 16575.1234 | 25056.3782 | 337.9063 | 510.8082
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.7 | 11.1582 | 0.52715 | 4 | 15614.9943 | 23296.2925 | 318.3328 | 474.9264 | 90.2903 | 0 | 145.6992 | 1775316.9903 | 105724.9068 | 2402413.9849 | 2579426.5321 | 0 | 266427.7255 | 0 | 2780430.9544 | 7234110.9986 | 4937429.4026 | 22081281.4952 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 32925874.4011 | 49122707.6981 | 237137.3706 | 2.1086 | 15614.9943 | 23296.2925 | 318.3328 | 474.9264
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.6138 | 11.8172 | 0.56978 | 4 | 14898.1546 | 22004.808 | 303.719 | 448.5978 | 90.2731 | 0 | 123.3602 | 1848343.0057 | 110031.1984 | 2515285.8616 | 2730856.7905 | 0 | 256905.0514 | 0 | 2909954.544 | 7571104.8097 | 5167434.6033 | 23109915.8646 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 33954508.7705 | 50151342.0675 | 316227.766 | 2.2791 | 14898.1546 | 22004.808 | 303.719 | 448.5978
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.565 | 12.3454 | 0.60515 | 4 | 14362.901 | 21054.1942 | 292.8072 | 429.2182 | 90.254 | 0 | 147.9927 | 1905929.8162 | 113421.3814 | 2604872.3943 | 2852461.1978 | 0 | 246934.3205 | 0 | 3012211.453 | 7837156.3111 | 5349020.2198 | 23922007.0941 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 34766600 | 50963433.2971 | 421696.5034 | 2.4206 | 14362.901 | 21054.1942 | 292.8072 | 429.2182
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6661 | 12.7589 | 0.63371 | 4 | 13963.0242 | 20352.7581 | 284.6551 | 414.9185 | 90.236 | 0 | 112.5402 | 1950444.8429 | 116038.4083 | 2674476.2325 | 2947797.7843 | 0 | 237354.3887 | 0 | 3091183.5461 | 8042625.498 | 5489257.1618 | 24549177.8626 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 35393770.7685 | 51590604.0655 | 562341.3252 | 2.5348 | 13963.0242 | 20352.7581 | 284.6551 | 414.9185
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6 | 13.5473 | 0.6715 | 4 | 13653.0232 | 19683.0989 | 278.3353 | 401.2666 | 90.1943 | 0 | 170.2276 | 2034017.7239 | 120942.8072 | 2805986.2726 | 3129950.622 | 0 | 247955.0568 | 0 | 3252152.4682 | 8461433.6139 | 5775102.3066 | 25827540.8711 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36672133.777 | 52868967.074 | 749894.2093 | 2.686 | 13653.0232 | 19683.0989 | 278.3353 | 401.2666
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9554 | 13.3291 | 0.67421 | 4 | 13440.4541 | 19446.3017 | 274.0018 | 396.4392 | 90.2066 | 0 | 153.0351 | 2011057.3941 | 119596.5042 | 2769750.0757 | 3079501.0896 | 0 | 221623.2932 | 0 | 3198596.0591 | 8322090.8236 | 5679997.9889 | 25402213.2283 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36246806.1342 | 52443639.4312 | 1000000 | 2.6968 | 13440.4541 | 19446.3017 | 274.0018 | 396.4392
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.3929 | 13.5198 | 0.68803 | 4 | 13273.0675 | 19158.315 | 270.5894 | 390.5682 | 90.1957 | 0 | 127.121 | 2031127.1191 | 120773.2487 | 2801424.8562 | 3123594.7161 | 0 | 215689.3966 | 0 | 3234117.6413 | 8414510.6939 | 5743076.4495 | 25684314.1213 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36528907.0272 | 52725740.3243 | 1333521.4322 | 2.7521 | 13273.0675 | 19158.315 | 270.5894 | 390.5682
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.4723 | 13.6628 | 0.69858 | 4 | 13147.721 | 18944.0714 | 268.0341 | 386.2005 | 90.1872 | 0 | 150.257 | 2046118.9142 | 121651.7947 | 2825127.4091 | 3156690.532 | 0 | 210815.3214 | 0 | 3260557.5488 | 8483301.9097 | 5790027.8678 | 25894291.2977 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36738884.2035 | 52935717.5006 | 1778279.41 | 2.7943 | 13147.721 | 18944.0714 | 268.0341 | 386.2005
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2929 | 13.7715 | 0.70665 | 4 | 13053.8226 | 18784.0012 | 266.1198 | 382.9373 | 90.1805 | 0 | 143.7385 | 2057469.934 | 122316.7172 | 2843097.7091 | 3181839.4516 | 0 | 206966.5436 | 0 | 3280559.2386 | 8535342.2037 | 5825546.4378 | 26053138.2357 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36897731.1415 | 53094564.4386 | 2371373.7057 | 2.8266 | 13053.8226 | 18784.0012 | 266.1198 | 382.9373
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9191 | 13.8543 | 0.7128 | 4 | 12983.4633 | 18664.1386 | 264.6855 | 380.4937 | 90.1753 | 0 | 143.0136 | 2066107.0252 | 122822.5068 | 2856785.3249 | 3201027.843 | 0 | 203991.6535 | 0 | 3295786.3979 | 8574960.1485 | 5852586.4991 | 26174067.3989 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37018660.3048 | 53215493.6018 | 3162277.6602 | 2.8512 | 12983.4633 | 18664.1386 | 264.6855 | 380.4937
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.3749 | 13.9146 | 0.7174 | 4 | 12930.7314 | 18575.0388 | 263.6104 | 378.6773 | 90.1714 | 0 | 129.2317 | 2072379.759 | 123189.7535 | 2866733.5835 | 3214992.0166 | 0 | 201594.2804 | 0 | 3306766.8632 | 8603529.0669 | 5872085.373 | 26261270.6961 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37105863.6019 | 53302696.899 | 4216965.0343 | 2.8696 | 12930.7314 | 18575.0388 | 263.6104 | 378.6773
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.7233 | 13.9607 | 0.72089 | 4 | 12891.2049 | 18508.168 | 262.8046 | 377.314 | 90.1684 | 0 | 140.7662 | 2077166.1826 | 123469.9336 | 2874328.885 | 3225663.5118 | 0 | 199783.3111 | 0 | 3315160.6114 | 8625367.8779 | 5886990.8103 | 26327931.1237 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37172524.0295 | 53369357.3266 | 5623413.2519 | 2.8836 | 12891.2049 | 18508.168 | 262.8046 | 377.314
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.9861 | 13.9954 | 0.72353 | 4 | 12861.5735 | 18458.0645 | 262.2006 | 376.2926 | 90.1662 | 0 | 126.7886 | 2080772.6852 | 123681.0177 | 2880054.2804 | 3233713.5601 | 0 | 198405.1888 | 0 | 3321484.4255 | 8641821.1451 | 5898220.5032 | 26378152.806 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37222745.7119 | 53419579.009 | 7498942.0933 | 2.8941 | 12861.5735 | 18458.0645 | 262.2006 | 376.2926
1 | 3100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1908 | 14.0224 | 0.72554 | 4 | 12839.3582 | 18420.2914 | 261.7477 | 375.5226 | 90.1644 | 0 | 122.5427 | 2083578.3269 | 123845.212 | 2884509.7356 | 3239981.4746 | 0 | 197398.2559 | 0 | 3326432.072 | 8654693.9062 | 5907006.4272 | 26417445.4103 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37262038.3162 | 53458871.6133 | 10000000 | 2.9022 | 12839.3582 | 18420.2914 | 261.7477 | 375.5226
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.0583 | [19 empty] | 100 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8886 | [19 empty] | 133.3521 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4945 | [19 empty] | 177.8279 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1549 | [19 empty] | 237.1374 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9372 | [19 empty] | 316.2278 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4652 | [19 empty] | 421.6965 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5558 | [19 empty] | 562.3413 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2982 | [19 empty] | 749.8942 | 0
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.16641 | 4.301e-05 | 4 | 70651074.1232 | 167951732.9911 | 1440317.7087 | 3423923.2486 | 78.2971 | 0 | 30.751 | 84645.4291 | 4662.2382 | 83871.7944 | 68419.3884 | 0 | 56253.7705 | 0 | 116162.522 | 302231.0541 | 206278.9046 | 922525.1013 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12154905.3342 | 28894640.8891 | 1000 | 0.00017204 | 70651074.1232 | 167951732.9911 | 1440317.7087 | 3423923.2486
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.17072 | 0.0021516 | 4 | 1411029.9911 | 3356050.3021 | 28765.7549 | 68417.6248 | 78.5501 | 0 | 259.1539 | 86365.2292 | 4764.7952 | 85586.9212 | 69373.6984 | 0 | 48231.422 | 0 | 114785.6057 | 298648.6004 | 203833.8064 | 911590.0785 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12143970.3114 | 28883705.8663 | 1333.5214 | 0.0086065 | 1411029.9911 | 3356050.3021 | 28765.7549 | 68417.6248
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3321 | 0.26686 | 0.0046385 | 4 | 672585.7445 | 1574810.0051 | 13711.5701 | 32104.632 | 82.4946 | 0 | 379.9718 | 122211.7957 | 6922.9127 | 121967.1178 | 91165.1784 | 0 | 60243.22 | 0 | 156978.9876 | 408427.1248 | 278759.905 | 1246676.2419 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12479056.4748 | 29218792.0297 | 1778.2794 | 0.018554 | 672585.7445 | 1574810.0051 | 13711.5701 | 32104.632
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1808 | 0.38533 | 0.0082181 | 4 | 391039.1115 | 900271.9844 | 7971.8612 | 18353.2621 | 85.1192 | 0 | 90.6584 | 161455.5355 | 9308.113 | 163299.8817 | 117721.7821 | 0 | 71916.0791 | 0 | 204243.5427 | 531399.8019 | 362691.284 | 1622036.02 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12854416.253 | 29594151.8078 | 2371.3737 | 0.032872 | 391039.1115 | 900271.9844 | 7971.8612 | 18353.2621
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.53849 | 0.013202 | 4 | 251934.3404 | 568916.0416 | 5136.0223 | 11598.123 | 87.0387 | 0 | 94.2361 | 207148.0744 | 12098.1813 | 213111.886 | 152002.3406 | 0 | 84689.7281 | 0 | 260929.5821 | 678885.2485 | 463353.1318 | 2072218.1728 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13304598.4057 | 30044333.9606 | 3162.2777 | 0.05281 | 251934.3404 | 568916.0416 | 5136.0223 | 11598.123
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6628 | 0.73595 | 0.019958 | 4 | 173448.3232 | 383136.226 | 3535.9787 | 7810.7502 | 88.4627 | 0 | 111.9131 | 260529.4229 | 15362.3533 | 273317.9512 | 195971.2071 | 0 | 98885.9364 | 0 | 329186.0796 | 856474.6539 | 584561.5501 | 2614289.1544 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13846669.3873 | 30586404.9422 | 4216.965 | 0.079832 | 173448.3232 | 383136.226 | 3535.9787 | 7810.7502
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3413 | 0.97369 | 0.028879 | 4 | 125164.5124 | 270078.1794 | 2551.6479 | 5505.909 | 89.4468 | 0 | 114.2074 | 319239.1386 | 18951.4885 | 341657.1255 | 249149.1993 | 0 | 112579.7497 | 0 | 406214.9137 | 1056887.8792 | 721347.6944 | 3226027.189 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 14458407.4219 | 31198142.9768 | 5623.4133 | 0.11552 | 125164.5124 | 270078.1794 | 2551.6479 | 5505.909
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6996 | 1.3101 | 0.041118 | 4 | 92919.7387 | 194698.3299 | 1894.2946 | 3969.1888 | 90.343 | 0 | 93.5776 | 395541.1162 | 23620.5561 | 432909.5244 | 323922.5255 | 0 | 131720.1562 | 0 | 510008.4126 | 1326937.2725 | 905661.9543 | 4050321.5178 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 15282701.7508 | 32022437.3056 | 7498.9421 | 0.16447 | 92919.7387 | 194698.3299 | 1894.2946 | 3969.1888
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5696 | 1.7187 | 0.05698 | 4 | 71193.6328 | 144638.6653 | 1451.3785 | 2948.6548 | 90.9577 | 0 | 101.7316 | 480476.4334 | 28806.7232 | 537659.7165 | 414700.8663 | 0 | 150820.8988 | 0 | 628861.2089 | 1636167.8684 | 1116718.1901 | 4994211.9057 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 16226592.1386 | 32966327.6935 | 10000 | 0.22792 | 71193.6328 | 144638.6653 | 1451.3785 | 2948.6548
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1723 | 2.232 | 0.077668 | 4 | 55859.6014 | 109741.9225 | 1138.7735 | 2237.2375 | 91.4253 | 0 | 116.4662 | 578959.0489 | 34810.677 | 662440.0101 | 528691.7789 | 0 | 171572.4809 | 0 | 770824.8584 | 2005528.1635 | 1368814.1811 | 6121641.1988 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 17354021.4317 | 34093756.9866 | 13335.2143 | 0.31067 | 55859.6014 | 109741.9225 | 1138.7735 | 2237.2375
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6204 | 2.866 | 0.10431 | 4 | 44775.0006 | 84895.9983 | 912.7989 | 1730.7198 | 91.7805 | 0 | 99.8459 | 691650.7359 | 41669.2112 | 808898.2539 | 669449.972 | 0 | 193414.4909 | 0 | 937982.2389 | 2440437.3791 | 1665648.6572 | 7449150.9392 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 18681531.1721 | 35421266.727 | 17782.7941 | 0.41723 | 44775.0006 | 84895.9983 | 912.7989 | 1730.7198
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.0844 | 3.6451 | 0.13822 | 4 | 36613.1364 | 66890.3593 | 746.4083 | 1363.6505 | 92.0536 | 0 | 127.5393 | 820410.6355 | 49492.087 | 980282.4855 | 842472.0371 | 0 | 216490.6037 | 0 | 1134567.661 | 2951912.3222 | 2014740.8156 | 9010368.6476 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 20242748.8805 | 36982484.4354 | 23713.7371 | 0.55288 | 36613.1364 | 66890.3593 | 746.4083 | 1363.6505
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.5862 | 4.5727 | 0.18042 | 4 | 30519.1743 | 53714.1887 | 622.1746 | 1095.0364 | 92.2616 | 0 | 108.326 | 963522.0284 | 58172.6242 | 1175033.6523 | 1048738.3277 | 0 | 239287.7204 | 0 | 1359054.1977 | 3535980.242 | 2413379.1723 | 10793167.9651 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 22025548.198 | 38765283.7529 | 31622.7766 | 0.7217 | 30519.1743 | 53714.1887 | 622.1746 | 1095.0364
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.0823 | 5.6423 | 0.2314 | 4 | 25931.8497 | 44017.5052 | 528.6558 | 897.3564 | 92.4196 | 0 | 104.2096 | 1118281.731 | 67542.4377 | 1390046.8437 | 1286576.7659 | 0 | 260444.1999 | 0 | 1607927.8715 | 4183498.4903 | 2855323.6819 | 12769642.022 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 24002022.2549 | 40741757.8098 | 42169.6503 | 0.92558 | 25931.8497 | 44017.5052 | 528.6558 | 897.3564
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.3714 | 6.8251 | 0.29059 | 4 | 22462.6148 | 36864.3358 | 457.9308 | 751.5293 | 92.5366 | 0 | 111.8523 | 1279624.6834 | 77292.4441 | 1618488.6481 | 1549563.2746 | 0 | 278278.7185 | 0 | 1873266.6298 | 4873855.511 | 3326506.534 | 14876876.4437 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 26109256.6766 | 42848992.2315 | 56234.1325 | 1.1623 | 22462.6148 | 36864.3358 | 457.9308 | 751.5293
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.007 | 8.0563 | 0.35573 | 4 | 19839.1873 | 31603.4934 | 404.4487 | 644.28 | 92.6156 | 0 | 142.5231 | 1438972.0309 | 86902.118 | 1848002.9729 | 1823420.3009 | 0 | 290568.5641 | 0 | 2140267.7349 | 5568537.6169 | 3800641.3455 | 16997312.6841 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 28229692.917 | 44969428.4719 | 74989.4209 | 1.4229 | 19839.1873 | 31603.4934 | 404.4487 | 644.28
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4601 | 9.259 | 0.42323 | 4 | 17861.7442 | 27749.923 | 364.1358 | 565.7197 | 92.6596 | 0 | 159.2112 | 1587697.165 | 95850.6018 | 2065525.9162 | 2091195.6119 | 0 | 296081.4543 | 0 | 2393176.7922 | 6226555.1052 | 4249751.8022 | 19005834.4488 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 30238214.6817 | 46977950.2366 | 100000 | 1.6929 | 17861.7442 | 27749.923 | 364.1358 | 565.7197
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.2675 | 10.3663 | 0.48906 | 4 | 16377.0281 | 24934.1205 | 333.8679 | 508.3158 | 92.6745 | 0 | 162.2921 | 1719475.868 | 103759.7939 | 2260874.9266 | 2338106.9515 | 0 | 295034.9751 | 0 | 2619728.4809 | 6815996.1271 | 4652057.4114 | 20805034.5345 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 32037414.7674 | 48777150.3223 | 133352.1432 | 1.9562 | 16377.0281 | 24934.1205 | 333.8679 | 508.3158
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1204 | 11.3347 | 0.54982 | 4 | 15265.5505 | 22877.0518 | 311.2089 | 466.3796 | 92.669 | 0 | 135.8937 | 1831138.7231 | 110444.9495 | 2428321.5717 | 2554397.8365 | 0 | 288753.4097 | 0 | 2813092.0313 | 7319088.4208 | 4995428.2394 | 22340665.182 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 33573045.4149 | 50312780.9698 | 177827.941 | 2.1993 | 15265.5505 | 22877.0518 | 311.2089 | 466.3796
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.2714 | 12.2004 | 0.60557 | 4 | 14417.4827 | 21328.2645 | 293.9199 | 434.8055 | 92.6506 | 0 | 120.7023 | 1928409.8539 | 116254.4907 | 2575631.3655 | 2748120.4186 | 0 | 280477.7765 | 0 | 2983068.623 | 7761332.6454 | 5297269.01 | 23690564.1834 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 34922944.4163 | 51662679.9712 | 237137.3706 | 2.4223 | 14417.4827 | 21328.2645 | 293.9199 | 434.8055
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.9971 | 12.863 | 0.65082 | 4 | 13803.2081 | 20233.4752 | 281.3971 | 412.4868 | 92.6282 | 0 | 140.8579 | 2001346.2805 | 120601.2688 | 2686982.7816 | 2896651.5846 | 0 | 269589.3724 | 0 | 3110316.8023 | 8092406.3058 | 5523233.586 | 24701127.9819 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 35933508.2148 | 52673243.7697 | 316227.766 | 2.6033 | 13803.2081 | 20233.4752 | 281.3971 | 412.4868
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7755 | 13.391 | 0.68807 | 4 | 13344.243 | 19426.412 | 272.0404 | 396.0337 | 92.6055 | 0 | 132.3598 | 2058588.2627 | 124006.7124 | 2774917.1873 | 3015204.1507 | 0 | 258608.7103 | 0 | 3210216.7591 | 8352325.5012 | 5700633.7777 | 25494501.0613 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 36726881.2942 | 53466616.8491 | 421696.5034 | 2.7523 | 13344.243 | 19426.412 | 272.0404 | 396.0337
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7445 | 13.8048 | 0.71803 | 4 | 13001.1399 | 18829.5033 | 265.0458 | 383.8649 | 92.5847 | 0 | 144.2846 | 2102917.777 | 126640.1631 | 2843347.935 | 3108222.5157 | 0 | 248404.6512 | 0 | 3287517.8864 | 8553447.1777 | 5837903.4545 | 26108401.5605 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 37340781.7934 | 54080517.3483 | 562341.3252 | 2.8721 | 13001.1399 | 18829.5033 | 265.0458 | 383.8649
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2455 | 14.0136 | 0.73901 | 4 | 12725.4928 | 18388.3563 | 259.4264 | 374.8715 | 92.5732 | 0 | 138.7841 | 2125115.5245 | 127957.5456 | 2877724.7562 | 3155201.306 | 0 | 232798.1424 | 0 | 3322330.9371 | 8644023.5946 | 5899723.7202 | 26384875.5266 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 37617255.7596 | 54356991.3144 | 749894.2093 | 2.9561 | 12725.4928 | 18388.3563 | 259.4264 | 374.8715
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.813 | 14.3701 | 0.76016 | 4 | 12552.4097 | 18057.7201 | 255.8979 | 368.131 | 92.5523 | 0 | 135.103 | 2162762.6212 | 130189.8197 | 2936195.2297 | 3235486.6727 | 0 | 231823.4857 | 0 | 3391618.5533 | 8824295.7591 | 6022763.1767 | 26935135.3181 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38167515.551 | 54907251.1059 | 1000000 | 3.0407 | 12552.4097 | 18057.7201 | 255.8979 | 368.131
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.1749 | 14.5589 | 0.77448 | 4 | 12408.5771 | 17812.1246 | 252.9656 | 363.1243 | 92.5404 | 0 | 150.8956 | 2182567.0826 | 131363.07 | 2967040.2362 | 3278033.082 | 0 | 225665.5661 | 0 | 3426020.9244 | 8913803.6718 | 6083854.1663 | 27208347.7994 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38440728.0323 | 55180463.5872 | 1333521.4322 | 3.0979 | 12408.5771 | 17812.1246 | 252.9656 | 363.1243
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1908 | 14.6995 | 0.78536 | 4 | 12300.8346 | 17629.4851 | 250.7692 | 359.4009 | 92.5313 | 0 | 123.2154 | 2197267.1805 | 132233.4542 | 2989973.9468 | 3309753.2201 | 0 | 220607.1872 | 0 | 3451435.6457 | 8979927.5632 | 6128985.0809 | 27410183.2787 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38642563.5116 | 55382299.0665 | 1778279.41 | 3.1415 | 12300.8346 | 17629.4851 | 250.7692 | 359.4009
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.9749 | 14.808 | 0.79373 | 4 | 12220.1034 | 17492.5687 | 249.1233 | 356.6097 | 92.524 | 0 | 151.3886 | 2208570.2862 | 132902.4272 | 3007630.4248 | 3334224.3029 | 0 | 216704.4289 | 0 | 3471012.4293 | 9030862.3386 | 6163749.1117 | 27565655.7497 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38798035.9826 | 55537771.5375 | 2371373.7057 | 3.1749 | 12220.1034 | 17492.5687 | 249.1233 | 356.6097
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.5519 | 14.8878 | 0.80002 | 4 | 12159.5988 | 17390.6674 | 247.8899 | 354.5323 | 92.5186 | 0 | 158.0675 | 2216863.7872 | 133393.1213 | 3020598.1163 | 3352224.6548 | 0 | 213570.0133 | 0 | 3485293.3803 | 9068018.4434 | 6189108.9168 | 27679070.4335 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38911450.6664 | 55651186.2213 | 3162277.6602 | 3.2001 | 12159.5988 | 17390.6674 | 247.8899 | 354.5323
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9929 | 14.9487 | 0.8048 | 4 | 12114.2461 | 17314.2272 | 246.9653 | 352.9739 | 92.5143 | 0 | 157.5775 | 2223189.5168 | 133767.3016 | 3030496.1033 | 3365979.7316 | 0 | 211186.657 | 0 | 3496201.531 | 9096399.2141 | 6208479.3759 | 27765699.4312 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 38998079.6641 | 55737815.219 | 4216965.0343 | 3.2192 | 12114.2461 | 17314.2272 | 246.9653 | 352.9739
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.3218 | 14.9942 | 0.80839 | 4 | 12080.2471 | 17257.0918 | 246.2722 | 351.8092 | 92.5112 | 0 | 171.1067 | 2227900.3276 | 134045.9056 | 3037871.2064 | 3376237.6714 | 0 | 209341.3252 | 0 | 3504304.6101 | 9117481.7638 | 6222868.6493 | 27830051.4594 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 39062431.6923 | 55802167.2472 | 5623413.2519 | 3.2336 | 12080.2471 | 17257.0918 | 246.2722 | 351.8092
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5756 | 15.0292 | 0.81114 | 4 | 12054.7573 | 17214.1038 | 245.7525 | 350.9328 | 92.5087 | 0 | 154.4308 | 2231529.9542 | 134260.5378 | 3043555.962 | 3384149.6839 | 0 | 207972.3303 | 0 | 3510572.7026 | 9133790.0546 | 6233999.3929 | 27879830.6182 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 39112210.8511 | 55851946.406 | 7498942.0933 | 3.2445 | 12054.7573 | 17214.1038 | 245.7525 | 350.9328
1 | 3200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.7628 | 15.0551 | 0.81318 | 4 | 12035.6459 | 17182.0023 | 245.3629 | 350.2784 | 92.5069 | 0 | 168.7597 | 2234205.8741 | 134418.7576 | 3047748.3225 | 3389987.4754 | 0 | 206912.0896 | 0 | 3515176.2825 | 9145767.6252 | 6242174.3309 | 27916390.7578 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 39148770.9907 | 55888506.5456 | 10000000 | 3.2527 | 12035.6459 | 17182.0023 | 245.3629 | 350.2784
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1656 | [19 empty] | 100 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.264 | [19 empty] | 133.3521 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6956 | [19 empty] | 177.8279 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6658 | [19 empty] | 237.1374 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5702 | [19 empty] | 316.2278 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1709 | [19 empty] | 421.6965 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9211 | [19 empty] | 562.3413 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0172 | [19 empty] | 749.8942 | 0
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.17238 | 0.0008609 | 4 | 3648842.9016 | 8669997.8853 | 74386.598 | 176749.6339 | 79.8346 | 0 | 31.5452 | 88080.3899 | 4894.3184 | 86164.7621 | 68960.6816 | 0 | 55111.1882 | 0 | 118252.4227 | 307668.5469 | 209990.1052 | 939122.415 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12565150.0658 | 29855992.0057 | 1000 | 0.0034436 | 3648842.9016 | 8669997.8853 | 74386.598 | 176749.6339
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.21294 | 0.0031064 | 4 | 1021688.5739 | 2413226.581 | 20828.5035 | 49196.888 | 81.9155 | 0 | 325.5009 | 104012.5048 | 5860.3449 | 101861.5203 | 78048.6446 | 0 | 55417.6583 | 0 | 134628.2624 | 350275.1228 | 239069.9687 | 1069174.0268 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12695201.6776 | 29986043.6176 | 1333.5214 | 0.012426 | 1021688.5739 | 2413226.581 | 20828.5035 | 49196.888
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6238 | 0.31977 | 0.0061951 | 4 | 526674.9283 | 1224433.7978 | 10736.9808 | 24961.7391 | 85.3992 | 0 | 446.9782 | 142275.327 | 8202.2678 | 140636.5127 | 101520.2924 | 0 | 67535.1361 | 0 | 179466.1191 | 466934.0283 | 318692.0688 | 1425261.7523 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13051289.4031 | 30342131.3431 | 1778.2794 | 0.024781 | 526674.9283 | 1224433.7978 | 10736.9808 | 24961.7391
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.45576 | 0.010597 | 4 | 317720.3373 | 725642.7827 | 6477.1588 | 14793.2096 | 87.8585 | 0 | 76.8394 | 185843.4172 | 10889.7494 | 186374.7202 | 131229.3915 | 0 | 80178.4425 | 0 | 231861.1311 | 603255.1019 | 411734.0027 | 1841365.9565 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13467393.6073 | 30758235.5473 | 2371.3737 | 0.042388 | 317720.3373 | 725642.7827 | 6477.1588 | 14793.2096
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.63306 | 0.016695 | 4 | 209239.3611 | 468167.3443 | 4265.6274 | 9544.2246 | 89.6852 | 0 | 65.0413 | 237151.9266 | 14067.3858 | 242064.0844 | 170033.0616 | 0 | 94347.9678 | 0 | 295489.1262 | 768802.0933 | 524723.226 | 2346678.8718 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13972706.5226 | 31263548.4626 | 3162.2777 | 0.066779 | 209239.3611 | 468167.3443 | 4265.6274 | 9544.2246
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2307 | 0.85263 | 0.024857 | 4 | 146398.3987 | 320301.6592 | 2984.5294 | 6529.7826 | 90.9979 | 0 | 95.7972 | 294890.6966 | 17645.1928 | 306862.3737 | 217774.3067 | 0 | 108847.0595 | 0 | 368947.6554 | 959926.1179 | 655169.3 | 2930062.7026 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14556090.3534 | 31846932.2934 | 4216.965 | 0.099428 | 146398.3987 | 320301.6592 | 2984.5294 | 6529.7826
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0212 | 1.1174 | 0.035466 | 4 | 107261.2369 | 229142.7726 | 2186.6654 | 4671.3854 | 91.8965 | 0 | 101.5955 | 358597.7915 | 21585.1789 | 380721.139 | 275373.7044 | 0 | 123036.8298 | 0 | 452132.711 | 1176356.569 | 802887.53 | 3590691.4537 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 15216719.1045 | 32507561.0445 | 5623.4133 | 0.14187 | 107261.2369 | 229142.7726 | 2186.6654 | 4671.3854
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.713 | 1.5207 | 0.05051 | 4 | 80097.7674 | 165679.475 | 1632.9013 | 3377.6002 | 92.8386 | 0 | 91.6868 | 448032.7237 | 27133.6896 | 486805.8362 | 363019.8766 | 0 | 146261.1636 | 0 | 573788.783 | 1492880.7131 | 1018921.7623 | 4556844.5483 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 16182872.1991 | 33473714.139 | 7498.9421 | 0.20204 | 80097.7674 | 165679.475 | 1632.9013 | 3377.6002
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8265 | 1.9851 | 0.069604 | 4 | 61871.9336 | 123976.3367 | 1261.3431 | 2527.4253 | 93.4234 | 0 | 100.757 | 542236.9623 | 32958.6101 | 602225.3711 | 463816.3073 | 0 | 166845.6068 | 0 | 705152.3145 | 1834661.6756 | 1252194.2921 | 5600091.1399 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 17226118.7907 | 34516960.7306 | 10000 | 0.27842 | 61871.9336 | 123976.3367 | 1261.3431 | 2527.4253
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7434 | 2.5696 | 0.094435 | 4 | 48910.7091 | 94684.9485 | 997.111 | 1930.2807 | 93.872 | 0 | 107.9768 | 651803.8014 | 39721.3524 | 740066.0512 | 590487.937 | 0 | 189425.2319 | 0 | 862486.7058 | 2244013.4882 | 1531585.3155 | 6849589.8834 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 18475617.5342 | 35766459.4742 | 13335.2143 | 0.37774 | 48910.7091 | 94684.9485 | 997.111 | 1930.2807
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6233 | 3.2982 | 0.12658 | 4 | 39425.7463 | 73575.4458 | 803.7472 | 1499.935 | 94.2168 | 0 | 54.3846 | 778454.2505 | 47525.0249 | 903406.1654 | 748504.4435 | 0 | 213593.9372 | 0 | 1049678.6904 | 2731048.6338 | 1863996.81 | 8336207.9558 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 19962235.6066 | 37253077.5466 | 17782.7941 | 0.50632 | 39425.7463 | 73575.4458 | 803.7472 | 1499.935
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.4887 | 4.1742 | 0.16689 | 4 | 32463.9214 | 58364.8246 | 661.8209 | 1189.8459 | 94.4776 | 0 | 52.7764 | 920188.9608 | 56241.91 | 1090532.6774 | 938555.6175 | 0 | 238042.4886 | 0 | 1264989.0452 | 3291242.0106 | 2246340.3005 | 10046133.0105 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 21672160.6613 | 38963002.6013 | 23713.7371 | 0.66758 | 32463.9214 | 58364.8246 | 661.8209 | 1189.8459
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4265 | 5.2107 | 0.21667 | 4 | 27244.8421 | 47195.064 | 555.423 | 962.1352 | 94.677 | 0 | 69.8011 | 1076948.5125 | 65864.3437 | 1302061.7294 | 1163383.373 | 0 | 261963.06 | 0 | 1509386.1972 | 3927113.2676 | 2680335.4992 | 11987055.9826 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 23613083.6334 | 40903925.5734 | 31622.7766 | 0.8667 | 27244.8421 | 47195.064 | 555.423 | 962.1352
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.3607 | 6.3963 | 0.27626 | 4 | 23301.6105 | 38949.0306 | 475.0348 | 794.0287 | 94.8281 | 0 | 62.7799 | 1245359.0308 | 76182.0341 | 1533933.8331 | 1420523.0117 | 0 | 283819.6286 | 0 | 1778328.8399 | 4626846.8561 | 3157918.0515 | 14122911.2859 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 25748938.9367 | 43039780.8766 | 42169.6503 | 1.105 | 23301.6105 | 38949.0306 | 475.0348 | 794.0287
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.977 | 7.6834 | 0.34441 | 4 | 20313.5642 | 32864.4852 | 414.1195 | 669.987 | 94.9369 | 0 | 77.9855 | 1418046.2429 | 86740.3307 | 1776104.5161 | 1699718.0614 | 0 | 301186.3599 | 0 | 2059900.2493 | 5359437.9049 | 3657926.4956 | 16359060.1607 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 27985087.8115 | 45275929.7514 | 56234.1325 | 1.3777 | 20313.5642 | 32864.4852 | 414.1195 | 669.987
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8003 | 8.9996 | 0.41817 | 4 | 18052.778 | 28389.8638 | 368.0303 | 578.7658 | 95.0059 | 0 | 66.8514 | 1585931.0883 | 96981.7505 | 2015492.5813 | 1985415.5453 | 0 | 312088.2733 | 0 | 2338404.6031 | 6084049.1045 | 4152488.5286 | 18570851.4749 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 30196879.1257 | 47487721.0657 | 74989.4209 | 1.6727 | 18052.778 | 28389.8638 | 368.0303 | 578.7658
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.3117 | 10.2658 | 0.49333 | 4 | 16348.9783 | 25111.3425 | 333.296 | 511.9287 | 95.0388 | 0 | 73.123 | 1740543.1857 | 106389.279 | 2239273.0882 | 2260563.8617 | 0 | 315758.6904 | 0 | 2598385.961 | 6760467.2682 | 4614157.8243 | 20635539.1585 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 32261566.8093 | 49552408.7492 | 100000 | 1.9733 | 16348.9783 | 25111.3425 | 333.296 | 511.9287
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0413 | 11.4116 | 0.56537 | 4 | 15069.7416 | 22715.4845 | 307.2171 | 463.0859 | 95.0433 | 0 | 72.2096 | 1875440.1847 | 114575.2805 | 2437072.8114 | 2510063.1346 | 0 | 312555.7015 | 0 | 2827385.7739 | 7356277.8072 | 5020810.7598 | 22454181.4536 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 34080209.1044 | 51371051.0444 | 133352.1432 | 2.2615 | 15069.7416 | 22715.4845 | 307.2171 | 463.0859
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.7692 | 12.4049 | 0.63104 | 4 | 14111.9209 | 20962.0543 | 287.6906 | 427.3398 | 95.0292 | 0 | 72.57 | 1988955.7215 | 121445.6825 | 2605370.3205 | 2726861.1899 | 0 | 304468.5249 | 0 | 3021369.5613 | 7860983.8304 | 5365282.9913 | 23994737.8222 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 35620765.473 | 52911607.413 | 177827.941 | 2.5242 | 14111.9209 | 20962.0543 | 287.6906 | 427.3398
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7324 | 13.2815 | 0.69061 | 4 | 13378.6993 | 19637.9253 | 272.7429 | 400.3457 | 95.0038 | 0 | 83.3383 | 2086739.9018 | 127349.277 | 2751712.3944 | 2918680.1659 | 0 | 294393.8558 | 0 | 3189761.482 | 8299105.0661 | 5664309.7371 | 25332051.88 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 36958079.5308 | 54248921.4707 | 237137.3706 | 2.7625 | 13378.6993 | 19637.9253 | 272.7429 | 400.3457
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2808 | 13.9475 | 0.73842 | 4 | 12849.2407 | 18703.2603 | 261.9492 | 381.2913 | 94.9768 | 0 | 73.5034 | 2159610.3357 | 131738.8715 | 2861614.3375 | 3064649.6681 | 0 | 282300.5884 | 0 | 3314966.3825 | 8624862.5341 | 5886645.9027 | 26326388.6205 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 37952416.2713 | 55243258.2113 | 316227.766 | 2.9537 | 12849.2407 | 18703.2603 | 261.9492 | 381.2913
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8908 | 14.4744 | 0.77744 | 4 | 12453.4662 | 18013.6357 | 253.8808 | 367.2323 | 94.9508 | 0 | 73.5397 | 2216437.0716 | 135155.8941 | 2947824.2609 | 3180306.3195 | 0 | 270407.3256 | 0 | 3412551.0399 | 8878757.7954 | 6059934.6356 | 27101374.3426 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 38727401.9934 | 56018243.9334 | 421696.5034 | 3.1098 | 12453.4662 | 18013.6357 | 253.8808 | 367.2323
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.7265 | 14.8871 | 0.80871 | 4 | 12157.4702 | 17502.6654 | 247.8465 | 356.8155 | 94.9278 | 0 | 81.7397 | 2260467.892 | 137799.6565 | 3014928.8076 | 3271035.482 | 0 | 259634.5418 | 0 | 3488107.8882 | 9075341.2157 | 6194106.8594 | 27701422.3432 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39327449.994 | 56618291.934 | 562341.3252 | 3.2348 | 12157.4702 | 17502.6654 | 247.8465 | 356.8155
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9191 | 15.2055 | 0.83331 | 4 | 11935.9757 | 17123.3435 | 243.331 | 349.0825 | 94.9085 | 0 | 76.2478 | 2294155.3375 | 139820.0304 | 3066452.3686 | 3341114.4385 | 0 | 250278.5315 | 0 | 3545810.0755 | 9225470.4709 | 6296573.1608 | 28159674.4137 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 39785702.0646 | 57076544.0045 | 749894.2093 | 3.3333 | 11935.9757 | 17123.3435 | 243.331 | 349.0825
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.5922 | 15.4481 | 0.8524 | 4 | 11770.1473 | 16841.356 | 239.9504 | 343.3338 | 94.8928 | 0 | 79.6629 | 2319655.2049 | 141347.9808 | 3105559.5325 | 3394546.0255 | 0 | 242393.1903 | 0 | 3589365.7543 | 9338793.4124 | 6373918.397 | 28505579.4977 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40131607.1485 | 57422449.0884 | 1000000 | 3.4096 | 11770.1473 | 16841.356 | 239.9504 | 343.3338
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8567 | 15.6311 | 0.86705 | 4 | 11645.9434 | 16631.4719 | 237.4183 | 339.055 | 94.8805 | 0 | 82.6328 | 2338809.2669 | 142494.8932 | 3134995.1872 | 3434900.2439 | 0 | 235901.9249 | 0 | 3621969.5913 | 9423621.9084 | 6431815.5885 | 28764508.6043 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40390536.2551 | 57681378.1951 | 1333521.4322 | 3.4682 | 11645.9434 | 16631.4719 | 237.4183 | 339.055
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.8313 | 15.7721 | 0.87834 | 4 | 11552.8861 | 16474.3513 | 235.5212 | 335.8519 | 94.8707 | 0 | 83.7678 | 2353504.2167 | 143374.3324 | 3157613.498 | 3465987.9615 | 0 | 230815.1898 | 0 | 3647005.1273 | 9488759.2377 | 6476273.1542 | 28963332.7176 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40589360.3684 | 57880202.3084 | 1778279.41 | 3.5134 | 11552.8861 | 16474.3513 | 235.5212 | 335.8519
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5593 | 15.8773 | 0.88688 | 4 | 11483.1477 | 16357.203 | 234.0995 | 333.4637 | 94.8633 | 0 | 83.2413 | 2364441.0483 | 144028.5936 | 3174467.389 | 3489197.745 | 0 | 226755.7332 | 0 | 3665567.2986 | 9537054.1997 | 6509235.4582 | 29110747.4656 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40736775.1164 | 58027617.0564 | 2371373.7057 | 3.5475 | 11483.1477 | 16357.203 | 234.0995 | 333.4637
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.1077 | 15.9565 | 0.89336 | 4 | 11430.8757 | 16269.6077 | 233.0339 | 331.678 | 94.8576 | 0 | 77.2512 | 2372659.4469 | 144520.0817 | 3187143.3926 | 3506679.3621 | 0 | 223594.8947 | 0 | 3679492.8994 | 9573285.7565 | 6533964.2401 | 29221340.074 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40847367.7248 | 58138209.6647 | 3162277.6602 | 3.5734 | 11430.8757 | 16269.6077 | 233.0339 | 331.678
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5144 | 16.0152 | 0.89822 | 4 | 11391.6906 | 16204.23 | 232.235 | 330.3451 | 94.8533 | 0 | 84.3128 | 2378742.5317 | 144883.7862 | 3196532.1612 | 3519641.5105 | 0 | 221119.6204 | 0 | 3689758.6479 | 9599995.1283 | 6552193.9352 | 29302867.3214 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40928894.9722 | 58219736.9121 | 4216965.0343 | 3.5929 | 11391.6906 | 16204.23 | 232.235 | 330.3451
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8239 | 16.0598 | 0.90191 | 4 | 11362.3131 | 16155.179 | 231.6361 | 329.3452 | 94.85 | 0 | 80.7846 | 2383364.5018 | 145160.0834 | 3203669.3625 | 3529503.0904 | 0 | 219246.9318 | 0 | 3697568.1483 | 9620313.8463 | 6566061.8778 | 29364887.8425 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 40990915.4933 | 58281757.4332 | 5623413.2519 | 3.6076 | 11362.3131 | 16155.179 | 231.6361 | 329.3452
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.0675 | 16.095 | 0.90474 | 4 | 11340.2871 | 16118.1347 | 231.1871 | 328.59 | 94.8474 | 0 | 86.5 | 2386997.7954 | 145377.2499 | 3209281.9934 | 3537262.9493 | 0 | 217888.3432 | 0 | 3703755.2491 | 9636411.4135 | 6577048.7982 | 29414023.7919 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 41040051.4428 | 58330893.3827 | 7498942.0933 | 3.619 | 11340.2871 | 16118.1347 | 231.1871 | 328.59
1 | 3300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2332 | 16.1189 | 0.90678 | 4 | 11323.7721 | 16090.8556 | 230.8504 | 328.0339 | 94.8456 | 0 | 80.8298 | 2389468.5101 | 145524.9118 | 3213099.8228 | 3542543.8329 | 0 | 216750.5081 | 0 | 3707881.1584 | 9647146.1832 | 6584375.4991 | 29446790.4263 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 41072818.0771 | 58363660.0171 | 10000000 | 3.6271 | 11323.7721 | 16090.8556 | 230.8504 | 328.0339
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.705 | [19 empty] | 100 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5654 | [19 empty] | 133.3521 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.264 | [19 empty] | 177.8279 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4974 | [19 empty] | 237.1374 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0117 | [19 empty] | 316.2278 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3648 | [19 empty] | 421.6965 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9322 | [19 empty] | 562.3413 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6222 | [19 empty] | 749.8942 | 0
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.17848 | 0.0016989 | 4 | 1910402.6463 | 4537175.3194 | 38946.142 | 92496.4559 | 81.35 | 0 | 30.1529 | 91592.7505 | 5134.669 | 88486.9487 | 69652.7034 | 0 | 53970.0649 | 0 | 120446.4833 | 313377.0425 | 213886.2708 | 956546.9331 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 12982082.0927 | 30832234.5449 | 1000 | 0.0067955 | 1910402.6463 | 4537175.3194 | 38946.142 | 92496.4559
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0987 | 0.25273 | 0.0042817 | 4 | 772822.6849 | 1815054.4734 | 15755.0358 | 37002.3405 | 84.837 | 0 | 339.5916 | 120320.5266 | 6900.6702 | 116558.3911 | 85741.2299 | 0 | 61305.012 | 0 | 152422.0737 | 396570.9696 | 270667.8355 | 1210486.7087 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13236021.8682 | 31086174.3204 | 1333.5214 | 0.017127 | 772822.6849 | 1815054.4734 | 15755.0358 | 37002.3405
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9445 | 0.38119 | 0.0080979 | 4 | 421451.672 | 972525.2591 | 8591.8624 | 19826.2428 | 88.2772 | 0 | 79.774 | 164816.592 | 9667.2596 | 161498.9312 | 113281.8872 | 0 | 75702.584 | 0 | 204737.229 | 532684.2726 | 363567.9616 | 1625956.7172 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13651491.8768 | 31501644.329 | 1778.2794 | 0.032392 | 421451.672 | 972525.2591 | 8591.8624 | 19826.2428
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9339 | 0.53346 | 0.013467 | 4 | 261775.849 | 593134.5127 | 5336.6548 | 12091.8493 | 90.5425 | 0 | 67.8477 | 212111.3545 | 12628.3831 | 210946.1403 | 145895.0363 | 0 | 88761.4181 | 0 | 261433.5096 | 680196.3645 | 464247.9954 | 2076220.2017 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14101755.3612 | 31951907.8134 | 2371.3737 | 0.05387 | 261775.849 | 593134.5127 | 5336.6548 | 12091.8493
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2561 | 0.7381 | 0.020825 | 4 | 176083.219 | 390374.4276 | 3589.6946 | 7958.3107 | 92.2983 | 0 | 82.1768 | 269610.8621 | 16236.9024 | 273146.2913 | 189417.2372 | 0 | 104585.107 | 0 | 332668.596 | 865535.4471 | 590745.7277 | 2641946.1709 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14667481.3305 | 32517633.7827 | 3162.2777 | 0.083299 | 176083.219 | 390374.4276 | 3589.6946 | 7958.3107
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8567 | 0.98642 | 0.03063 | 4 | 124947.7904 | 270640.4252 | 2547.2297 | 5517.3711 | 93.5269 | 0 | 88.3305 | 333182.9223 | 20228.3771 | 344145.7837 | 242336.337 | 0 | 120069.6694 | 0 | 413385.6049 | 1075544.5469 | 734081.2535 | 3282974.4949 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 15308509.6544 | 33158662.1066 | 4216.965 | 0.12252 | 124947.7904 | 270640.4252 | 2547.2297 | 5517.3711
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3124 | 1.3691 | 0.044252 | 4 | 91810.7756 | 192653.6193 | 1871.6868 | 3927.5046 | 94.6538 | 0 | 46.8065 | 422449.6014 | 25834.0163 | 446960.9265 | 323494.936 | 0 | 145648.1262 | 0 | 532111.1665 | 1384444.1043 | 944911.5486 | 4225854.4258 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 16251389.5854 | 34101542.0376 | 5623.4133 | 0.17701 | 91810.7756 | 192653.6193 | 1871.6868 | 3927.5046
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7265 | 1.7457 | 0.061391 | 4 | 69663.9076 | 142354.3902 | 1420.193 | 2902.0868 | 95.3103 | 0 | 54.9224 | 503110.9814 | 30892.6357 | 542606.0303 | 403268.1885 | 0 | 160736.9303 | 0 | 639839.7589 | 1664731.8033 | 1136213.6626 | 5081399.9911 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 17106935.1506 | 34957087.6029 | 7498.9421 | 0.24556 | 69663.9076 | 142354.3902 | 1420.193 | 2902.0868
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1124 | 2.2738 | 0.084108 | 4 | 54282.0899 | 107339.1402 | 1106.6138 | 2188.2536 | 95.8754 | 0 | 50.0881 | 607810.496 | 37446.1277 | 670069.3604 | 514940.9048 | 0 | 183375.5408 | 0 | 785320.5476 | 2043242.9733 | 1394555.3137 | 6236761.2643 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 18262296.4238 | 36112448.876 | 10000 | 0.33643 | 54282.0899 | 107339.1402 | 1106.6138 | 2188.2536
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3318 | 2.9322 | 0.11355 | 4 | 43228.589 | 82529.8994 | 881.2733 | 1682.4836 | 96.3067 | 0 | 48.7841 | 728633.2663 | 44995.2916 | 820992.7236 | 654191.4356 | 0 | 207665.8305 | 0 | 958026.6336 | 2492588.7824 | 1701243.0615 | 7608337.0252 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 19633872.1848 | 37484024.637 | 13335.2143 | 0.45419 | 43228.589 | 82529.8994 | 881.2733 | 1682.4836
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.523 | 3.7426 | 0.15121 | 4 | 35126.3178 | 64638.9017 | 716.0975 | 1317.7514 | 96.6369 | 0 | 65.9753 | 866725.1723 | 53606.7765 | 997738.2874 | 825560.4088 | 0 | 233194.6023 | 0 | 1160961.8465 | 3020584.5785 | 2061611.0416 | 9219982.714 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 21245517.8736 | 39095670.3258 | 17782.7941 | 0.60483 | 35126.3178 | 64638.9017 | 716.0975 | 1317.7514
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.7861 | 4.7207 | 0.19854 | 4 | 29096.1666 | 51572.6987 | 593.1647 | 1051.3792 | 96.8897 | 0 | 55.5166 | 1022053.8264 | 63273.8395 | 1201150.8674 | 1032342.8886 | 0 | 259097.4434 | 0 | 1395388.3575 | 3630514.2726 | 2477900.5907 | 11081722.0861 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 23107257.2457 | 40957409.6979 | 23713.7371 | 0.79417 | 29096.1666 | 51572.6987 | 593.1647 | 1051.3792
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.2723 | 5.89 | 0.25727 | 4 | 24530.6667 | 41876.1693 | 500.0908 | 853.7024 | 97.0857 | 0 | 125.081 | 1195761.0388 | 74062.6073 | 1433583.7341 | 1279467.7307 | 0 | 285043.5747 | 0 | 1664488.2874 | 4330657.0903 | 2955762.4502 | 13218826.5135 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 25244361.6731 | 43094514.1253 | 31622.7766 | 1.0291 | 24530.6667 | 41876.1693 | 500.0908 | 853.7024
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.6056 | 7.1917 | 0.32617 | 4 | 21101.9285 | 34783.6658 | 430.1914 | 709.1121 | 97.23 | 0 | 107.6802 | 1377541.1146 | 85329.3324 | 1681689.9294 | 1554480.1419 | 0 | 307174.7964 | 0 | 1952423.9727 | 5079806.6798 | 3467072.4385 | 15505518.4057 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 27531053.5652 | 45381206.0175 | 42169.6503 | 1.3047 | 21101.9285 | 34783.6658 | 430.1914 | 709.1121
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.5339 | 8.5853 | 0.40392 | 4 | 18502.155 | 29550.2786 | 377.1915 | 602.4224 | 97.3302 | 0 | 110.5122 | 1561672.9974 | 96716.7827 | 1937552.7469 | 1849046.7596 | 0 | 323957.9693 | 0 | 2249889.4298 | 5853750.7806 | 3995305.1903 | 17867892.6565 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 29893427.8161 | 47743580.2683 | 56234.1325 | 1.6157 | 18502.155 | 29550.2786 | 377.1915 | 602.4224
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5003 | 9.9821 | 0.48658 | 4 | 16535.8275 | 25706.9964 | 337.1052 | 524.0719 | 97.3882 | 0 | 135.1389 | 1737443.7755 | 107560.0242 | 2185795.6383 | 2144632.8062 | 0 | 333139.8625 | 0 | 2538343.1216 | 6604248.1167 | 4507535.0434 | 20158698.3884 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 32184233.5479 | 50034386.0001 | 74989.4209 | 1.9463 | 16535.8275 | 25706.9964 | 337.1052 | 524.0719
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0117 | 11.3037 | 0.56941 | 4 | 15054.6472 | 22891.8004 | 306.9093 | 466.6803 | 97.4093 | 0 | 157.2392 | 1896958.4525 | 117373.0885 | 2414366.217 | 2424844.2769 | 0 | 334572.6081 | 0 | 2803364.7107 | 7293779.9282 | 4978154.6732 | 22263413.9551 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 34288949.1146 | 52139101.5668 | 100000 | 2.2776 | 15054.6472 | 22891.8004 | 306.9093 | 466.6803
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.6487 | 12.4847 | 0.64766 | 4 | 13942.9002 | 20833.182 | 284.2449 | 424.7126 | 97.4031 | 0 | 154.6524 | 2034630.4028 | 125817.9354 | 2614141.6957 | 2675838.4594 | 0 | 329148.6303 | 0 | 3034035.0782 | 7893936.9073 | 5387774.1434 | 24095323.2526 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 36120858.4121 | 53971010.8643 | 133352.1432 | 2.5906 | 13942.9002 | 20833.182 | 284.2449 | 424.7126
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.2265 | 13.4972 | 0.71807 | 4 | 13110.344 | 19324.9718 | 267.2721 | 393.9657 | 97.3803 | 0 | 133.2223 | 2149400.3863 | 132838.3047 | 2782471.6686 | 2891623.6018 | 0 | 319076.9896 | 0 | 3227410.2709 | 8397059.4919 | 5731165.6455 | 25631046.3592 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 37656581.5188 | 55506733.971 | 177827.941 | 2.8723 | 13110.344 | 19324.9718 | 267.2721 | 393.9657
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.028 | 14.2333 | 0.77633 | 4 | 12471.6889 | 18219.9617 | 254.2522 | 371.4386 | 97.354 | 0 | 191.2034 | 2231081.7544 | 137822.714 | 2903274.5432 | 3048870.4995 | 0 | 300423.9172 | 0 | 3362374.637 | 8748209.0876 | 5970832.46 | 26702889.613 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 38728424.7725 | 56578577.2247 | 237137.3706 | 3.1053 | 12471.6889 | 18219.9617 | 254.2522 | 371.4386
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.4427 | 15.0601 | 0.83198 | 4 | 12010.3037 | 17374.0679 | 244.8463 | 354.1939 | 97.3155 | 0 | 154.9899 | 2321178.1847 | 143308.2589 | 3037502.8529 | 3225908.6651 | 0 | 294203.8674 | 0 | 3518619.7133 | 9154726.726 | 6248289.1013 | 27943737.3697 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 39969272.5293 | 57819424.9815 | 316227.766 | 3.3279 | 12010.3037 | 17374.0679 | 244.8463 | 354.1939
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9265 | 15.5899 | 0.87292 | 4 | 11665.7598 | 16777.9393 | 237.8223 | 342.041 | 97.2858 | 0 | 125.507 | 2378051.3158 | 146763.8608 | 3122773.154 | 3339635.9658 | 0 | 281534.4691 | 0 | 3614815.9186 | 9405009.5195 | 6419112.2506 | 28707696.4543 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 40733231.6139 | 58583384.0661 | 421696.5034 | 3.4917 | 11665.7598 | 16777.9393 | 237.8223 | 342.041
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.6307 | 16.0001 | 0.90545 | 4 | 11407.9084 | 16336.4389 | 232.5656 | 333.0404 | 97.2603 | 0 | 136.5538 | 2421624.8278 | 149407.4851 | 3188388.7899 | 3427813.7514 | 0 | 270056.189 | 0 | 3688343.5069 | 9596313.2216 | 6549680.9582 | 29291628.7299 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41317163.8895 | 59167316.3417 | 562341.3252 | 3.6218 | 11407.9084 | 16336.4389 | 232.5656 | 333.0404
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.7176 | 16.3159 | 0.93096 | 4 | 11214.8472 | 16008.3151 | 228.6298 | 326.3512 | 97.2391 | 0 | 134.6786 | 2454917.4687 | 151425.0143 | 3238691.5614 | 3495803.9897 | 0 | 260205.3466 | 0 | 3744406.9185 | 9742178.7184 | 6649237.157 | 29736866.1746 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41762401.3341 | 59612553.7863 | 749894.2093 | 3.7238 | 11214.8472 | 16008.3151 | 228.6298 | 326.3512
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.0903 | 16.0697 | 0.93334 | 4 | 11061.4536 | 15842.7106 | 225.5027 | 322.9751 | 97.2555 | 0 | 144.9014 | 2428971.8831 | 149852.726 | 3199483.1388 | 3442786.9503 | 0 | 229487.9527 | 0 | 3685727.2339 | 9589506.2159 | 6545035.037 | 29270851.1377 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 41296386.2973 | 59146538.7495 | 1000000 | 3.7334 | 11061.4536 | 15842.7106 | 225.5027 | 322.9751
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6 | 17.0524 | 0.97762 | 4 | 10960.8834 | 15525.5953 | 223.4524 | 316.5103 | 97.1851 | 0 | 110.1265 | 2531696.8778 | 156069.941 | 3355258.5342 | 3654653.8083 | 0 | 258441.4168 | 0 | 3882887.0255 | 10102475.5507 | 6895147.1484 | 30836630.3027 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42862165.4623 | 60712317.9145 | 1333521.4322 | 3.9105 | 10960.8834 | 15525.5953 | 223.4524 | 316.5103
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.4501 | 16.8793 | 0.97756 | 4 | 10880.6808 | 15445.6679 | 221.8174 | 314.8808 | 97.1983 | 0 | 141.7445 | 2513746.335 | 154984.8971 | 3327939.0879 | 3617266.4558 | 0 | 240095.4799 | 0 | 3843072.5797 | 9998886.5298 | 6824445.5132 | 30520436.8784 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42545972.038 | 60396124.4902 | 1778279.41 | 3.9102 | 10880.6808 | 15445.6679 | 221.8174 | 314.8808
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1493 | 16.9845 | 0.98641 | 4 | 10819.8107 | 15343.8434 | 220.5765 | 312.805 | 97.1902 | 0 | 136.8408 | 2524666.2541 | 155644.9496 | 3344556.6198 | 3639999.9949 | 0 | 235974.2981 | 0 | 3861328.4254 | 10046384.4956 | 6856863.8508 | 30665418.8884 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42690954.0479 | 60541106.5001 | 2371373.7057 | 3.9456 | 10819.8107 | 15343.8434 | 220.5765 | 312.805
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6681 | 17.0626 | 0.99306 | 4 | 10774.1778 | 15267.8856 | 219.6462 | 311.2565 | 97.1841 | 0 | 132.01 | 2532748.2145 | 156133.3098 | 3356865.8815 | 3656863.4766 | 0 | 232721.7615 | 0 | 3874779.7311 | 10081382.0337 | 6880750.3897 | 30772244.7984 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42797779.9579 | 60647932.4101 | 3162277.6602 | 3.9723 | 10774.1778 | 15267.8856 | 219.6462 | 311.2565
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0749 | 17.1238 | 0.99819 | 4 | 10739.9649 | 15210.6143 | 218.9487 | 310.0889 | 97.1793 | 0 | 146.4192 | 2539072.5165 | 156515.3723 | 3366504.2833 | 3670082.0331 | 0 | 230323.3947 | 0 | 3885374.064 | 10108946.3146 | 6899563.5778 | 30856381.5563 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42881916.7159 | 60732069.1681 | 4216965.0343 | 3.9927 | 10739.9649 | 15210.6143 | 218.9487 | 310.0889
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3675 | 17.1678 | 1.002 | 4 | 10714.3126 | 15168.0638 | 218.4258 | 309.2215 | 97.1758 | 0 | 120.2531 | 2543616.3039 | 156789.8205 | 3373432.5291 | 3679591.4744 | 0 | 228403.1372 | 0 | 3892914.9733 | 10128566.214 | 6912954.5622 | 30916269.0145 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42941804.1741 | 60791956.6263 | 5623413.2519 | 4.0079 | 10714.3126 | 15168.0638 | 218.4258 | 309.2215
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.587 | 17.2008 | 1.0048 | 4 | 10695.078 | 15136.1987 | 218.0336 | 308.5719 | 97.1732 | 0 | 149.7091 | 2547020.5632 | 156995.4131 | 3378625.0987 | 3686722.8077 | 0 | 226939.221 | 0 | 3898558.2104 | 10143248.7593 | 6922975.7011 | 30961085.7744 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 42986620.934 | 60836773.3862 | 7498942.0933 | 4.0193 | 10695.078 | 15136.1987 | 218.0336 | 308.5719
1 | 3400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7593 | 17.2267 | 1.007 | 4 | 10680.6552 | 15112.1347 | 217.7396 | 308.0813 | 97.1711 | 0 | 135.8643 | 2549690.1792 | 157156.6229 | 3382698.1922 | 3692319.1864 | 0 | 225877.0263 | 0 | 3903019.0708 | 10154855.0028 | 6930897.2008 | 30996512.4815 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 43022047.6411 | 60872200.0933 | 10000000 | 4.028 | 10680.6552 | 15112.1347 | 217.7396 | 308.0813
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.9895 | [19 empty] | 100 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4663 | [19 empty] | 133.3521 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7864 | [19 empty] | 177.8279 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7537 | [19 empty] | 237.1374 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3156 | [19 empty] | 316.2278 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0173 | [19 empty] | 421.6965 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.318 | [19 empty] | 562.3413 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6673 | [19 empty] | 749.8942 | 0
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.20145 | 0.00257 | 4 | 1310473.5459 | 3102106.9978 | 26715.7758 | 63240.6471 | 83.8066 | 0 | 275.4687 | 101939.0175 | 5800.8353 | 97294.5188 | 73957.4969 | 0 | 56959.8677 | 0 | 131021.1771 | 340890.2267 | 232664.5843 | 1040527.7243 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13471430.4835 | 31889097.5752 | 1000 | 0.01028 | 1310473.5459 | 3102106.9978 | 26715.7758 | 63240.6471
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.30471 | 0.0057353 | 4 | 602448.6737 | 1405264.8132 | 12281.7311 | 28648.224 | 87.9251 | 0 | 386.8395 | 140725.7953 | 8222.8634 | 135045.5154 | 95655.2645 | 0 | 69157.4977 | 0 | 175034.7051 | 455404.3982 | 310822.8594 | 1390068.899 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13820971.6582 | 32238638.7499 | 1333.5214 | 0.022941 | 602448.6737 | 1405264.8132 | 12281.7311 | 28648.224
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2493 | 0.44473 | 0.01039 | 4 | 343065.9852 | 786241.6646 | 6993.8641 | 16028.5998 | 91.0073 | 0 | 73.9071 | 187697.2371 | 11189.7638 | 182311.1236 | 125099.5383 | 0 | 83375.317 | 0 | 229972.4621 | 598341.1726 | 408380.145 | 1826366.7594 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14257269.5186 | 32674936.6103 | 1778.2794 | 0.041558 | 343065.9852 | 786241.6646 | 6993.8641 | 16028.5998
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 0.62367 | 0.016882 | 4 | 218753.6732 | 491493.403 | 4459.5895 | 10019.7578 | 93.2302 | 0 | 86.1826 | 241668.4349 | 14617.0298 | 238536.3191 | 162524.3668 | 0 | 98541.0574 | 0 | 294796.0111 | 766998.75 | 523492.4071 | 2341174.3762 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14772077.1354 | 33189744.2271 | 2371.3737 | 0.067528 | 218753.6732 | 491493.403 | 4459.5895 | 10019.7578
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7554 | 0.84943 | 0.025707 | 4 | 149537.3111 | 328650.1972 | 3048.5204 | 6699.9788 | 94.8543 | 0 | 68.2159 | 303423.9872 | 18545.7416 | 305040.1953 | 209477.5444 | 0 | 114546.1583 | 0 | 370903.1145 | 965013.8211 | 658641.762 | 2945592.3244 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 15376495.0836 | 33794162.1752 | 3162.2777 | 0.10283 | 149537.3111 | 328650.1972 | 3048.5204 | 6699.9788
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4487 | 1.1232 | 0.037198 | 4 | 107954.2636 | 231735.2977 | 2200.7937 | 4724.2375 | 95.9937 | 0 | 54.9389 | 371809.8993 | 22891.4466 | 381108.937 | 266243.7533 | 0 | 130553.354 | 0 | 457316.8822 | 1189844.7188 | 812093.4695 | 3631862.4606 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 16062765.2198 | 34480432.3115 | 4216.965 | 0.14879 | 107954.2636 | 231735.2977 | 2200.7937 | 4724.2375
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9165 | 1.5257 | 0.053277 | 4 | 79888.8397 | 166313.5569 | 1628.6421 | 3390.5268 | 97.0694 | 0 | 93.5691 | 464093.4358 | 28763.952 | 486522.4749 | 349313.8423 | 0 | 154532.1122 | 0 | 578458.0687 | 1505029.2367 | 1027213.3793 | 4593926.502 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 17024829.2612 | 35442496.3529 | 5623.4133 | 0.21311 | 79888.8397 | 166313.5569 | 1628.6421 | 3390.5268
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8324 | 2.0004 | 0.07395 | 4 | 61153.5676 | 123417.4552 | 1246.6982 | 2516.0318 | 97.7807 | 0 | 95.984 | 563724.216 | 35086.7958 | 603941.7117 | 447220.538 | 0 | 176913.4644 | 0 | 712485.8232 | 1853741.9609 | 1265216.9789 | 5658331.489 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 18089234.2482 | 36506901.3399 | 7498.9421 | 0.2958 | 61153.5676 | 123417.4552 | 1246.6982 | 2516.0318
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5324 | 2.6033 | 0.10103 | 4 | 47943.5842 | 93517.7041 | 977.3948 | 1906.4849 | 98.3281 | 0 | 111.609 | 680581.8335 | 42491.9509 | 745333.839 | 571784.9002 | 0 | 201898.8068 | 0 | 874415.6188 | 2275050.0729 | 1552768.4224 | 6944325.4444 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 19375228.2036 | 37792895.2953 | 10000 | 0.40413 | 47943.5842 | 93517.7041 | 977.3948 | 1906.4849
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1151 | 3.3506 | 0.13601 | 4 | 38404.6889 | 72259.3878 | 782.9315 | 1473.1054 | 98.7442 | 0 | 94.3396 | 814720.9115 | 50976.8181 | 911775.5506 | 726288.4816 | 0 | 228353.6911 | 0 | 1065525.0266 | 2772277.5501 | 1892136.3925 | 8462054.4222 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 20892957.1814 | 39310624.2731 | 13335.2143 | 0.54402 | 38404.6889 | 72259.3878 | 782.9315 | 1473.1054
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6982 | 4.2612 | 0.18047 | 4 | 31388.62 | 56902.398 | 639.8995 | 1160.0323 | 99.0612 | 0 | 103.4517 | 966671.5225 | 60568.213 | 1104889.7467 | 914496.443 | 0 | 255539.8448 | 0 | 1287844.6503 | 3350707.6068 | 2286926.7918 | 10227644.8189 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 22658547.578 | 41076214.6697 | 17782.7941 | 0.72187 | 31388.62 | 56902.398 | 639.8995 | 1160.0323
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4339 | 5.36 | 0.2361 | 4 | 26152.7628 | 45654.4416 | 533.1594 | 930.7275 | 99.3054 | 0 | 109.9891 | 1137712.759 | 71340.9996 | 1327231.2535 | 1141353.1968 | 0 | 283336.8244 | 0 | 1544780.263 | 4019201.3663 | 2743187.5188 | 12268144.1813 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 24699046.9405 | 43116714.0322 | 23713.7371 | 0.94441 | 26152.7628 | 45654.4416 | 533.1594 | 930.7275
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.2413 | 6.634 | 0.30367 | 4 | 22203.1404 | 37365.816 | 452.641 | 761.7527 | 99.4907 | 0 | 125.2844 | 1323538.1285 | 83020.5179 | 1573877.9542 | 1404330.3286 | 0 | 309267.4692 | 0 | 1830673.4154 | 4763036.7041 | 3250870.4211 | 14538614.939 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 26969517.6982 | 45387184.7899 | 31622.7766 | 1.2147 | 22203.1404 | 37365.816 | 452.641 | 761.7527
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.965 | 8.0572 | 0.3828 | 4 | 19208.225 | 31236.4314 | 391.5856 | 636.7969 | 99.6273 | 0 | 151.4112 | 1519091.1811 | 95284.8558 | 1838458.0415 | 1698146.9101 | 0 | 331571.3742 | 0 | 2138195.4214 | 5563145.8823 | 3796961.3759 | 16980855.0423 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 29411757.8015 | 47829424.8932 | 42169.6503 | 1.5312 | 19208.225 | 31236.4314 | 391.5856 | 636.7969
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.1413 | 9.5524 | 0.47069 | 4 | 16936.8512 | 26719.1244 | 345.2806 | 544.7055 | 99.7172 | 0 | 134.2217 | 1713788.5027 | 107465.9499 | 2106543.7624 | 2007045.7419 | 0 | 347209.7334 | 0 | 2450000.9392 | 6374399.8796 | 4350658.8986 | 19457113.4077 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 31888016.1669 | 50305683.2586 | 56234.1325 | 1.8828 | 16936.8512 | 26719.1244 | 345.2806 | 544.7055
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.2056 | 11.0256 | 0.56258 | 4 | 15219.7858 | 23404.2576 | 310.2759 | 477.1274 | 99.7628 | 0 | 140.5851 | 1896800.6701 | 118884.0447 | 2362578.2392 | 2311813.4728 | 0 | 354377.6216 | 0 | 2747337.0789 | 7148007.5229 | 4878662.0112 | 21818460.6613 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 34249363.4205 | 52667030.5122 | 74989.4209 | 2.2503 | 15219.7858 | 23404.2576 | 310.2759 | 477.1274
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6781 | 12.3972 | 0.65314 | 4 | 13927.0404 | 20976.7064 | 283.9216 | 427.6385 | 99.7717 | 0 | 152.6306 | 2060526.7238 | 129067.4968 | 2594896.8274 | 2596181.3079 | 0 | 353376.2323 | 0 | 3016278.9493 | 7847739.1023 | 5356243.1922 | 23954309.832 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 36385212.5912 | 54802879.6829 | 100000 | 2.6126 | 13927.0404 | 20976.7064 | 283.9216 | 427.6385
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.1908 | 13.6077 | 0.73749 | 4 | 12956.8924 | 19200.2454 | 264.1438 | 391.423 | 99.7548 | 0 | 146.3023 | 2200331.6777 | 137735.8012 | 2795723.584 | 2847802.6042 | 0 | 345611.1297 | 0 | 3247609.8707 | 8449614.7072 | 5767035.6599 | 25791465.0345 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 38222367.7937 | 56640034.8854 | 133352.1432 | 2.95 | 12956.8924 | 19200.2454 | 264.1438 | 391.423
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6 | 14.6353 | 0.81249 | 4 | 12230.2345 | 17897.2554 | 249.3299 | 364.8598 | 99.7236 | 0 | 179.7943 | 2315897.0058 | 144879.8114 | 2963458.1464 | 3061994.2525 | 0 | 333530.9265 | 0 | 3439706.4557 | 8949410.6168 | 6108156.638 | 27317033.8531 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 39747936.6123 | 58165603.704 | 177827.941 | 3.25 | 12230.2345 | 17897.2554 | 249.3299 | 364.8598
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.8841 | 15.4786 | 0.87657 | 4 | 11686.4028 | 16939.1407 | 238.2431 | 345.3273 | 99.687 | 0 | 122.5573 | 2408751.792 | 150604.5663 | 3099381.9787 | 3238219.9897 | 0 | 319307.7453 | 0 | 3594343.7681 | 9351745.1833 | 6382758.2467 | 28545113.2701 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 40976016.0292 | 59393683.1209 | 237137.3706 | 3.5063 | 11686.4028 | 16939.1407 | 238.2431 | 345.3273
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4977 | 16.2118 | 0.93259 | 4 | 11268.0377 | 16205.2911 | 229.7142 | 330.3668 | 99.6476 | 0 | 162.0772 | 2488114.9435 | 155485.9546 | 3216382.417 | 3391797.3803 | 0 | 305972.0918 | 0 | 3727523.587 | 9698251.7533 | 6619256.1008 | 29602784.2284 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42033686.9876 | 60451354.0792 | 316227.766 | 3.7303 | 11268.0377 | 16205.2911 | 229.7142 | 330.3668
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8204 | 16.7379 | 0.97511 | 4 | 10967.0117 | 15688.9402 | 223.5774 | 319.8403 | 99.6151 | 0 | 147.9809 | 2544310.1957 | 158935.4806 | 3299697.9899 | 3502220.0791 | 0 | 292363.6827 | 0 | 3821035.6969 | 9941551.0812 | 6785312.8913 | 30345427.0974 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42776329.8566 | 61193996.9483 | 421696.5034 | 3.9005 | 10967.0117 | 15688.9402 | 223.5774 | 319.8403
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4144 | 17.1475 | 1.0089 | 4 | 10741.6178 | 15305.4959 | 218.9824 | 312.0232 | 99.5873 | 0 | 169.8682 | 2587639.6199 | 161591.2123 | 3364207.659 | 3588321.8872 | 0 | 280379.4671 | 0 | 3893034.5398 | 10128877.3013 | 6913166.8857 | 30917218.5723 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43348121.3315 | 61765788.4232 | 562341.3252 | 4.0355 | 10741.6178 | 15305.4959 | 218.9824 | 312.0232
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4024 | 17.4607 | 1.0352 | 4 | 10572.7877 | 15020.5424 | 215.5406 | 306.2141 | 99.5647 | 0 | 165.1532 | 2620527.9131 | 163604.5749 | 3413330.5716 | 3654239.6701 | 0 | 270121.7547 | 0 | 3947511.5489 | 10270615.3043 | 7009905.9852 | 31349857.3227 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43780760.0819 | 62198427.1736 | 749894.2093 | 4.1409 | 10572.7877 | 15020.5424 | 215.5406 | 306.2141
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.9176 | 17.699 | 1.0556 | 4 | 10446.2847 | 14808.3005 | 212.9616 | 301.8872 | 99.5467 | 0 | 143.1404 | 2645414.2208 | 165126.6533 | 3450593.0404 | 3704445.3192 | 0 | 261633.8038 | 0 | 3988613.0846 | 10377553.0692 | 7082893.2071 | 31676272.3984 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44107175.1576 | 62524842.2492 | 1000000 | 4.2223 | 10446.2847 | 14808.3005 | 212.9616 | 301.8872
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3829 | 17.4576 | 1.0555 | 4 | 10342.6549 | 14704.8833 | 210.849 | 299.7789 | 99.5647 | 0 | 150.3573 | 2620197.2223 | 163584.161 | 3412842.1658 | 3653589.3377 | 0 | 235040.8993 | 0 | 3933248.9766 | 10233507.0167 | 6984578.8164 | 31236588.5957 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 43667491.3549 | 62085158.4466 | 1333521.4322 | 4.2221 | 10342.6549 | 14704.8833 | 210.849 | 299.7789
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9593 | 18.0195 | 1.0832 | 4 | 10280.4011 | 14531.1442 | 209.5799 | 296.237 | 99.5214 | 0 | 130.7824 | 2678699.1641 | 167160.4573 | 3500555.129 | 3772036.9375 | 0 | 249486.4107 | 0 | 4043495.8585 | 10520346.7888 | 7180352.8548 | 32112133.6009 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44543036.36 | 62960703.4517 | 1778279.41 | 4.3328 | 10280.4011 | 14531.1442 | 209.5799 | 296.237
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.6165 | 18.1225 | 1.0922 | 4 | 10227.1176 | 14442.6899 | 208.4936 | 294.4338 | 99.513 | 0 | 168.2444 | 2689354.1853 | 167811.0305 | 3516579.043 | 3793781.7995 | 0 | 245236.3724 | 0 | 4060977.348 | 10565830.0384 | 7211396.1073 | 32250965.9244 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44681868.6836 | 63099535.7753 | 2371373.7057 | 4.369 | 10227.1176 | 14442.6899 | 208.4936 | 294.4338
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.1159 | 18.2008 | 1.0991 | 4 | 10187.1672 | 14376.4053 | 207.6792 | 293.0825 | 99.5066 | 0 | 199.0525 | 2697430.2983 | 168303.985 | 3528734.3949 | 3810298.5377 | 0 | 241973.1192 | 0 | 4074228.7307 | 10600307.418 | 7234927.6273 | 32356204.111 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44787106.8702 | 63204773.9619 | 3162277.6602 | 4.3964 | 10187.1672 | 14376.4053 | 207.6792 | 293.0825
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.4861 | 18.2588 | 1.1043 | 4 | 10157.2118 | 14326.9095 | 207.0685 | 292.0734 | 99.5018 | 0 | 168.4194 | 2703408.0078 | 168668.7681 | 3537736.9301 | 3822543.2614 | 0 | 239428.79 | 0 | 4083996.4454 | 10625721.008 | 7252272.9247 | 32433776.1355 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44864678.8947 | 63282345.9864 | 4216965.0343 | 4.417 | 10157.2118 | 14326.9095 | 207.0685 | 292.0734
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7614 | 18.3018 | 1.1081 | 4 | 10134.7501 | 14289.9113 | 206.6106 | 291.3192 | 99.4982 | 0 | 169.7127 | 2707845.4703 | 168939.5109 | 3544422.8522 | 3831643.6971 | 0 | 237464.7549 | 0 | 4091223.3513 | 10644523.9348 | 7265106.3086 | 32491169.8801 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44922072.6393 | 63339739.731 | 5623413.2519 | 4.4325 | 10134.7501 | 14289.9113 | 206.6106 | 291.3192
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.966 | 18.3339 | 1.111 | 4 | 10117.907 | 14262.2407 | 206.2672 | 290.7551 | 99.4955 | 0 | 165.9718 | 2711142.0323 | 169140.617 | 3549391.4533 | 3838410.2927 | 0 | 235957.6447 | 0 | 4096576.3956 | 10658451.458 | 7274612.1294 | 32533682.023 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44964584.7822 | 63382251.8738 | 7498942.0933 | 4.4441 | 10117.907 | 14262.2407 | 206.2672 | 290.7551
1 | 3500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.1272 | 18.3591 | 1.1132 | 4 | 10105.2769 | 14241.3326 | 206.0097 | 290.3288 | 99.4933 | 0 | 158.8542 | 2713735.5999 | 169298.8218 | 3553301.4718 | 3843737.4022 | 0 | 234865.7004 | 0 | 4100826.2085 | 10669508.5994 | 7282158.8556 | 32567432.6596 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 44998335.4188 | 63416002.5105 | 10000000 | 4.453 | 10105.2769 | 14241.3326 | 206.0097 | 290.3288
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2787 | [19 empty] | 100 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2707 | [19 empty] | 133.3521 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3911 | [19 empty] | 177.8279 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2365 | [19 empty] | 237.1374 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7932 | [19 empty] | 316.2278 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9685 | [19 empty] | 421.6965 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7469 | [19 empty] | 562.3413 | 0
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.19058 | 0.00082982 | 4 | 4177080.7544 | 9899236.8562 | 85155.4411 | 201809.333 | 84.313 | 0 | 28.5398 | 98574.5773 | 5621.6524 | 93035.5776 | 70950.4517 | 0 | 62023.789 | 0 | 128780.3588 | 335060.077 | 228685.3874 | 1022731.8712 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13864862.3209 | 32858248.1793 | 749.8942 | 0.0033193 | 4177080.7544 | 9899236.8562 | 85155.4411 | 201809.333
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.23627 | 0.0036104 | 4 | 970033.6031 | 2285229.9791 | 19775.4471 | 46587.5041 | 86.7247 | 0 | 299.6724 | 116821.3642 | 6765.5734 | 110280.2732 | 80408.4155 | 0 | 62378.4376 | 0 | 146895.0849 | 382190.8786 | 260853.1279 | 1166593.1553 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14008723.605 | 33002109.4634 | 1000 | 0.014441 | 970033.6031 | 2285229.9791 | 19775.4471 | 46587.5041
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.36073 | 0.0075132 | 4 | 479795.8094 | 1111794.2002 | 9781.2865 | 22665.4286 | 90.8605 | 0 | 431.3356 | 162167.1816 | 9644.9277 | 154213.727 | 106152.9665 | 0 | 77022.6741 | 0 | 198588.576 | 516686.7387 | 352649.316 | 1577126.1076 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14419256.5573 | 33412642.4156 | 1333.5214 | 0.030053 | 479795.8094 | 1111794.2002 | 9781.2865 | 22665.4286
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.53711 | 0.013204 | 4 | 283123.1596 | 642725.1515 | 5771.8486 | 13102.8216 | 93.9961 | 0 | 49.5918 | 219179.6158 | 13300.9279 | 211538.7636 | 142311.26 | 0 | 95503.1027 | 0 | 265915.1313 | 691856.625 | 472206.3628 | 2111811.7893 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14953942.239 | 33947328.0974 | 1778.2794 | 0.052818 | 283123.1596 | 642725.1515 | 5771.8486 | 13102.8216
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.7137 | 0.020821 | 4 | 185367.9597 | 413423.5196 | 3778.9766 | 8428.1976 | 95.8048 | 0 | 36.2227 | 270795.4821 | 16624.3691 | 265190.3374 | 178269.1767 | 0 | 107301.942 | 0 | 326890.7098 | 850502.5724 | 580485.4818 | 2596060.0712 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15438190.5208 | 34431576.3792 | 2371.3737 | 0.083284 | 185367.9597 | 413423.5196 | 3778.9766 | 8428.1976
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3085 | 0.97673 | 0.031293 | 4 | 128823.5879 | 280560.0651 | 2626.2431 | 5719.5964 | 97.4119 | 0 | 104.8967 | 340932.8594 | 21143.1502 | 340443.0597 | 231516.1298 | 0 | 125990.6428 | 0 | 413410.0783 | 1075608.2218 | 734124.7129 | 3283168.8549 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16125299.3046 | 35118685.1629 | 3162.2777 | 0.12517 | 128823.5879 | 280560.0651 | 2626.2431 | 5719.5964
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1332 | 1.2839 | 0.044866 | 4 | 94025.6091 | 199859.2918 | 1916.8392 | 4074.402 | 98.4622 | 0 | 95.9145 | 415717.2424 | 25951.8556 | 423360.0568 | 293858.7646 | 0 | 142951.1468 | 0 | 507717.2358 | 1320976.1005 | 901593.3319 | 4032125.7345 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16874256.1841 | 35867642.0425 | 4216.965 | 0.17946 | 94025.6091 | 199859.2918 | 1916.8392 | 4074.402
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.825 | 1.7433 | 0.064061 | 4 | 70032.902 | 144154.6142 | 1427.7154 | 2938.7868 | 99.5536 | 0 | 96.4598 | 518799.2895 | 32602.1836 | 540286.9357 | 386551.4688 | 0 | 169514.9186 | 0 | 642624.3705 | 1671976.7916 | 1141158.516 | 5103514.4742 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 17945644.9239 | 36939030.7823 | 5623.4133 | 0.25625 | 70032.902 | 144154.6142 | 1427.7154 | 2938.7868
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9922 | 2.2814 | 0.088528 | 4 | 54002.8234 | 107639.5043 | 1100.9206 | 2194.3769 | 100.2415 | 0 | 93.1841 | 629271.2309 | 39702.4009 | 669697.2679 | 495190.9267 | 0 | 194035.0071 | 0 | 790879.7651 | 2057706.9169 | 1404427.2525 | 6280910.768 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 19123041.2176 | 38116427.076 | 7498.9421 | 0.35411 | 54002.8234 | 107639.5043 | 1100.9206 | 2194.3769
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.9823 | 2.9597 | 0.12042 | 4 | 42630.4541 | 82063.4377 | 869.0795 | 1672.9742 | 100.7688 | 0 | 104.2508 | 757916.5454 | 47954.6847 | 824415.6663 | 632024.5723 | 0 | 220971.398 | 0 | 968480.318 | 2519787.1248 | 1719806.4891 | 7691356.7987 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 20533487.2484 | 39526873.1067 | 10000 | 0.48166 | 42630.4541 | 82063.4377 | 869.0795 | 1672.9742
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8861 | 3.7938 | 0.16137 | 4 | 34369.7156 | 63795.4909 | 700.6731 | 1300.5574 | 101.1689 | 0 | 85.8746 | 904569.587 | 57342.0048 | 1005248.2795 | 800191.3483 | 0 | 249001.3882 | 0 | 1176377.517 | 3060692.9912 | 2088985.8574 | 9342408.9734 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 22184539.4231 | 41177925.2815 | 13335.2143 | 0.64547 | 34369.7156 | 63795.4909 | 700.6731 | 1300.5574
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8862 | 4.8146 | 0.21334 | 4 | 28259.8995 | 50517.0176 | 576.1163 | 1029.8577 | 101.4767 | 0 | 96.097 | 1071592.8921 | 68009.7202 | 1216094.2788 | 1005930.0317 | 0 | 278308.4192 | 0 | 1419574.7834 | 3693442.3916 | 2520850.3249 | 11273802.8419 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 24115933.2916 | 43109319.1499 | 17782.7941 | 0.85336 | 28259.8995 | 50517.0176 | 576.1163 | 1029.8577
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.0332 | 6.0309 | 0.27789 | 4 | 23679.0702 | 40766.4209 | 482.7299 | 831.0786 | 101.7123 | 0 | 119.424 | 1257487.8002 | 79857.0739 | 1455973.8546 | 1251032.9509 | 0 | 307328.9335 | 0 | 1697155.4391 | 4415650.3182 | 3013772.0747 | 13478258.4451 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 26320388.8948 | 45313774.7531 | 23713.7371 | 1.1115 | 23679.0702 | 40766.4209 | 482.7299 | 831.0786
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.2692 | 7.4328 | 0.3557 | 4 | 20213.9755 | 33563.2393 | 412.0892 | 684.232 | 101.8907 | 0 | 104.8489 | 1458525.4886 | 92641.6261 | 1720727.7678 | 1533497.5137 | 0 | 334126.9043 | 0 | 2004412.5272 | 5215070.2342 | 3559392.5938 | 15918394.6557 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 28760525.1054 | 47753910.9638 | 31622.7766 | 1.4228 | 20213.9755 | 33563.2393 | 412.0892 | 684.232
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.3413 | 8.9763 | 0.44572 | 4 | 17582.9261 | 28236.2384 | 358.4517 | 575.6339 | 102.0185 | 0 | 119.7816 | 1667325.9808 | 105889.2714 | 2000901.5265 | 1844608.7149 | 0 | 356180.9333 | 0 | 2330213.5065 | 6062737.5513 | 4137942.9556 | 18505800.4402 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 31347930.8899 | 50341316.7483 | 42169.6503 | 1.7829 | 17582.9261 | 28236.2384 | 358.4517 | 575.6339
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.7151 | 10.5683 | 0.54411 | 4 | 15587.1597 | 24313.965 | 317.7653 | 495.6731 | 102.0966 | 0 | 125.8098 | 1871779.5854 | 118827.6438 | 2279962.2558 | 2165978.1255 | 0 | 370263.1522 | 0 | 2654656.1975 | 6906870.8811 | 4714081.2983 | 21082419.1398 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 33924549.5894 | 52917935.4478 | 56234.1325 | 2.1764 | 15587.1597 | 24313.965 | 317.7653 | 495.6731
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8527 | 12.115 | 0.64543 | 4 | 14079.3771 | 21436.2133 | 287.0271 | 437.0062 | 102.1292 | 0 | 144.1857 | 2061622.916 | 130803.9601 | 2543162.1091 | 2478743.3642 | 0 | 375314.2032 | 0 | 2959962.1555 | 7701214.3569 | 5256237.0427 | 23507060.1078 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 36349190.5575 | 55342576.4159 | 74989.4209 | 2.5817 | 14079.3771 | 21436.2133 | 287.0271 | 437.0062
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.2466 | 13.5295 | 0.74361 | 4 | 12944.7231 | 19330.2605 | 263.8957 | 394.0735 | 102.1255 | 0 | 167.1784 | 2228706.4025 | 141308.7597 | 2778044.8699 | 2765411.6781 | 0 | 371657.6746 | 0 | 3231200.4601 | 8406920.7868 | 5737896.182 | 25661146.8138 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 38503277.2635 | 57496663.1218 | 100000 | 2.9744 | 12944.7231 | 19330.2605 | 263.8957 | 394.0735
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.6332 | 14.7677 | 0.83399 | 4 | 12093.2893 | 17786.8178 | 246.5381 | 362.6083 | 102.0981 | 0 | 155.3141 | 2370450.0225 | 150190.1145 | 2979708.6248 | 3017043.7816 | 0 | 361636.3724 | 0 | 3462821.2772 | 9009550.641 | 6149203.4402 | 27500604.2744 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 40342734.7241 | 59336120.5824 | 133352.1432 | 3.336 | 12093.2893 | 17786.8178 | 246.5381 | 362.6083
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8741 | 15.8084 | 0.91344 | 4 | 11455.3981 | 16653.7033 | 233.5338 | 339.5083 | 102.0588 | 0 | 148.8597 | 2486601.0905 | 157444.7223 | 3146635.4405 | 3229102.5121 | 0 | 347613.0315 | 0 | 3653284.7508 | 9505097.5299 | 6487424.3744 | 29013203.452 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 41855333.9017 | 60848719.76 | 177827.941 | 3.6538 | 11455.3981 | 16653.7033 | 233.5338 | 339.5083
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9897 | 16.6573 | 0.98076 | 4 | 10977.7934 | 15819.3033 | 223.7972 | 322.4979 | 102.0164 | 0 | 161.5666 | 2579472.6405 | 163228.9766 | 3281212.9098 | 3402520.4293 | 0 | 331912.2206 | 0 | 3805755.3989 | 9901794.8802 | 6758178.4673 | 30224075.923 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 43066206.3727 | 62059592.2311 | 237137.3706 | 3.923 | 10977.7934 | 15819.3033 | 223.7972 | 322.4979
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4675 | 17.3972 | 1.0395 | 4 | 10608.8379 | 15176.5974 | 216.2755 | 309.3955 | 101.9721 | 0 | 133.5063 | 2659125.7652 | 168178.3835 | 3397409.2248 | 3554105.497 | 0 | 317515.8617 | 0 | 3937570.5456 | 10244750.8528 | 6992252.9656 | 31270909.0963 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 44113039.546 | 63106425.4044 | 316227.766 | 4.1581 | 10608.8379 | 15176.5974 | 216.2755 | 309.3955
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.6534 | 17.9217 | 1.0837 | 4 | 10344.2799 | 14726.0383 | 210.8821 | 300.2102 | 101.9366 | 0 | 149.5981 | 2714888.0644 | 171636.5289 | 3479187.8448 | 3661827.1162 | 0 | 303127.3571 | 0 | 4028960.0955 | 10482527.7151 | 7154540.5599 | 31996695.2819 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 44838825.7316 | 63832211.59 | 421696.5034 | 4.3346 | 10344.2799 | 14726.0383 | 210.8821 | 300.2102
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1212 | 18.3268 | 1.1185 | 4 | 10146.1058 | 14391.4546 | 206.8421 | 293.3893 | 101.907 | 0 | 153.7129 | 2757573.4421 | 174279.6511 | 3542037.5587 | 3745171.6984 | 0 | 290512.8327 | 0 | 4098734.3214 | 10664065.9381 | 7278444.1274 | 32550819.5699 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45392950.0195 | 64386335.8779 | 562341.3252 | 4.4739 | 10146.1058 | 14391.4546 | 206.8421 | 293.3893
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0165 | 18.6372 | 1.1456 | 4 | 9997.6105 | 14142.4248 | 203.8148 | 288.3125 | 101.8831 | 0 | 150.4999 | 2790059.1627 | 176288.7811 | 3590015.773 | 3809120.9393 | 0 | 279874.227 | 0 | 4151689.9644 | 10801845.6587 | 7372481.6178 | 32971376.124 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45813506.5737 | 64806892.432 | 749894.2093 | 4.5824 | 9997.6105 | 14142.4248 | 203.8148 | 288.3125
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.4728 | 18.8753 | 1.1666 | 4 | 9886.3114 | 13956.514 | 201.5458 | 284.5224 | 101.8639 | 0 | 161.7777 | 2814846.3081 | 177820.3449 | 3626709.8068 | 3858220.0052 | 0 | 271222.849 | 0 | 4192039.5325 | 10906826.958 | 7444133.5117 | 33291819.3162 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46133949.7659 | 65127335.6243 | 1000000 | 4.6664 | 9886.3114 | 13956.514 | 201.5458 | 284.5224
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5593 | 19.0527 | 1.1826 | 4 | 9802.8754 | 13818.1479 | 199.8449 | 281.7016 | 101.8493 | 0 | 144.8124 | 2833242.0666 | 178956.1746 | 3653990.7199 | 3894830.7145 | 0 | 264141.9913 | 0 | 4221813.0501 | 10984291.5434 | 7497004.683 | 33528270.9433 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46370401.393 | 65363787.2513 | 1333521.4322 | 4.7303 | 9802.8754 | 13818.1479 | 199.8449 | 281.7016
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.1592 | 18.6604 | 1.1739 | 4 | 9733.8884 | 13778.7853 | 198.4385 | 280.8992 | 101.881 | 0 | 169.4114 | 2792479.8607 | 176438.1317 | 3593604.9637 | 3813926.2107 | 0 | 234474.0934 | 0 | 4138260.0715 | 10766903.8321 | 7348633.1032 | 32864720.267 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 45706850.7167 | 64700236.575 | 1778279.41 | 4.6956 | 9733.8884 | 13778.7853 | 198.4385 | 280.8992
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.5461 | 19.2136 | 1.2021 | 4 | 9682.9194 | 13633.0889 | 197.3994 | 277.929 | 101.8356 | 0 | 170.2309 | 2849878.3501 | 179982.7513 | 3678698.3261 | 3928067.134 | 0 | 249058.4105 | 0 | 4245417.1391 | 11045704.5411 | 7538920.3159 | 33715726.9682 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46557857.4178 | 65551243.2762 | 2371373.7057 | 4.8082 | 9682.9194 | 13633.0889 | 197.3994 | 277.929
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6606 | 19.8829 | 1.2317 | 4 | 9662.033 | 13517.0606 | 196.9736 | 275.5636 | 101.7763 | 0 | 128.8902 | 2918539.0215 | 184213.7776 | 3781019.7708 | 4066491.3456 | 0 | 273184.6707 | 0 | 4377144.9486 | 11388433.2803 | 7772839.7227 | 34761866.5378 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 47603996.9874 | 66597382.8458 | 3162277.6602 | 4.9269 | 9662.033 | 13517.0606 | 196.9736 | 275.5636
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.8419 | 19.4247 | 1.2163 | 4 | 9631.8669 | 13535.6599 | 196.3586 | 275.9427 | 101.8173 | 0 | 158.7112 | 2871621.7996 | 181323.6179 | 3711041.6403 | 3971687.4301 | 0 | 248391.307 | 0 | 4283785.66 | 11145531.5619 | 7607054.3088 | 34020437.3255 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46862567.7751 | 65855953.6335 | 4216965.0343 | 4.8654 | 9631.8669 | 13535.6599 | 196.3586 | 275.9427
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1197 | 19.4699 | 1.2204 | 4 | 9612.089 | 13502.8962 | 195.9554 | 275.2748 | 101.8134 | 0 | 148.4914 | 2876268.6478 | 181610.0465 | 3717961.4306 | 3981036.6126 | 0 | 246515.0884 | 0 | 4291322.8121 | 11165141.6856 | 7620438.6212 | 34080294.9446 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46922425.3943 | 65915811.2526 | 5623413.2519 | 4.8816 | 9612.089 | 13502.8962 | 195.9554 | 275.2748
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.3024 | 19.4996 | 1.2233 | 4 | 9597.2576 | 13478.9042 | 195.6531 | 274.7857 | 101.8107 | 0 | 166.5865 | 2879319.984 | 181798.101 | 3722506.8338 | 3987181.1102 | 0 | 244908.2968 | 0 | 4296128.587 | 11177645.3262 | 7628972.6128 | 34118460.8516 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46960591.3013 | 65953977.1597 | 7498942.0933 | 4.8931 | 9597.2576 | 13478.9042 | 195.6531 | 274.7857
1 | 3600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4681 | 19.5266 | 1.2256 | 4 | 9586.1357 | 13460.314 | 195.4263 | 274.4067 | 101.8083 | 0 | 155.1109 | 2882088.0403 | 181968.6829 | 3726631.14 | 3992758.4367 | 0 | 243890.9071 | 0 | 4300661.5107 | 11189439.064 | 7637022.0811 | 34154459.8629 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 46996590.3126 | 65989976.1709 | 10000000 | 4.9026 | 9586.1357 | 13460.314 | 195.4263 | 274.4067
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.9361 | [19 empty] | 100 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.936 | [19 empty] | 133.3521 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6733 | [19 empty] | 177.8279 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4623 | [19 empty] | 237.1374 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6655 | [19 empty] | 316.2278 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5069 | [19 empty] | 421.6965 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5738 | [19 empty] | 562.3413 | 0
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.19653 | 0.0017336 | 4 | 2061893.7177 | 4885127.0419 | 42034.4924 | 99589.9224 | 85.7642 | 0 | 28.4934 | 101996.7552 | 5864.5314 | 95244.2935 | 71458.2861 | 0 | 60794.4092 | 0 | 130789.7274 | 340288.0421 | 232253.5809 | 1038689.6258 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14297907.8568 | 33875216.6091 | 749.8942 | 0.0069344 | 2061893.7177 | 4885127.0419 | 42034.4924 | 99589.9224
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.28363 | 0.0049138 | 4 | 742500.6681 | 1738539.1917 | 15136.8804 | 35442.473 | 89.9132 | 0 | 343.7693 | 136244.0018 | 8044.7649 | 127320.8725 | 89308.5467 | 0 | 70031.4463 | 0 | 168070.3566 | 437284.5918 | 298455.7192 | 1334760.2997 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14593978.5307 | 34171287.283 | 1000 | 0.019655 | 742500.6681 | 1738539.1917 | 15136.8804 | 35442.473
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9056 | 0.41897 | 0.0096299 | 4 | 390031.6593 | 898272.1143 | 7951.3229 | 18312.4921 | 93.6469 | 0 | 62.6606 | 183995.988 | 11126.048 | 173459.5158 | 116657.5753 | 0 | 84528.2709 | 0 | 222209.2852 | 578142.9787 | 394594.4626 | 1764714.1244 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15023932.3554 | 34601241.1077 | 1333.5214 | 0.03852 | 390031.6593 | 898272.1143 | 7951.3229 | 18312.4921
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 0.59203 | 0.016262 | 4 | 238742.1126 | 539712.7561 | 4867.0809 | 11002.7745 | 96.3553 | 0 | 53.2861 | 238814.8637 | 14690.774 | 228265.7992 | 151235.1728 | 0 | 99996.5027 | 0 | 285871.2138 | 743778.2582 | 507643.9443 | 2270296.5288 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15529514.7598 | 35106823.512 | 1778.2794 | 0.065047 | 238742.1126 | 539712.7561 | 4867.0809 | 11002.7745
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2567 | 0.8301 | 0.02551 | 4 | 158547.0935 | 350406.1119 | 3232.197 | 7143.5025 | 98.4805 | 0 | 83.1265 | 306847.0658 | 19128.9102 | 298663.5962 | 198473.2662 | 0 | 119315.3797 | 0 | 367547.0051 | 956281.9129 | 652682.0552 | 2918939.1912 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16178157.4222 | 35755466.1745 | 2371.3737 | 0.10204 | 158547.0935 | 350406.1119 | 3232.197 | 7143.5025
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8808 | 1.1158 | 0.037805 | 4 | 111768.0366 | 241228.8117 | 2278.5426 | 4917.7756 | 99.938 | 0 | 103.4546 | 381056.0259 | 23973.0046 | 377995.1265 | 255200.2258 | 0 | 137837.0122 | 0 | 458663.9441 | 1193349.4975 | 814485.5529 | 3642560.3895 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16901778.6205 | 36479087.3728 | 3162.2777 | 0.15122 | 111768.0366 | 241228.8117 | 2278.5426 | 4917.7756
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3272 | 1.5484 | 0.054795 | 4 | 81870.2835 | 171190.3723 | 1669.0365 | 3489.9473 | 101.2501 | 0 | 83.9587 | 483367.8373 | 30652.9985 | 490784.2934 | 340572.7243 | 0 | 167327.2122 | 0 | 589954.9756 | 1534941.8301 | 1047629.3389 | 4685231.2102 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 17944449.4413 | 37521758.1935 | 4216.965 | 0.21918 | 81870.2835 | 171190.3723 | 1669.0365 | 3489.9473
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7996 | 1.9861 | 0.07645 | 4 | 61858.9804 | 125879.1954 | 1261.079 | 2566.2177 | 102.0328 | 0 | 99.0831 | 578353.4309 | 36844.4206 | 598623.1445 | 426847.1139 | 0 | 185849.2367 | 0 | 712341.7651 | 1853367.1515 | 1264961.1638 | 5657187.4268 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 18916405.6578 | 38493714.4101 | 5623.4133 | 0.3058 | 61858.9804 | 125879.1954 | 1261.079 | 2566.2177
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2218 | 2.5924 | 0.10521 | 4 | 48022.84 | 94540.7244 | 979.0105 | 1927.3405 | 102.696 | 0 | 124.6136 | 700114.9769 | 44769.4414 | 740435.2941 | 546642.8058 | 0 | 212432.1194 | 0 | 875313.9087 | 2277387.2388 | 1554363.5861 | 6951459.3711 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 20210677.6021 | 39787986.3543 | 7498.9421 | 0.42086 | 48022.84 | 94540.7244 | 979.0105 | 1927.3405
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.495 | 3.3499 | 0.14255 | 4 | 38141.7648 | 72476.5866 | 777.5715 | 1477.5332 | 103.2024 | 0 | 108.4225 | 840845.5453 | 53909.5808 | 908641.1146 | 696285.7058 | 0 | 241057.2413 | 0 | 1068888.2833 | 2781028.0539 | 1898108.7912 | 8488764.3163 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 21747982.5473 | 41325291.2996 | 10000 | 0.57019 | 38141.7648 | 72476.5866 | 777.5715 | 1477.5332
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7614 | 4.284 | 0.19041 | 4 | 30926.8913 | 56631.3233 | 630.4865 | 1154.5061 | 103.5897 | 0 | 119.042 | 1001909.8539 | 64346.8086 | 1105922.1124 | 880765.2424 | 0 | 271188.2974 | 0 | 1296411.6028 | 3372997.0598 | 2302139.8015 | 10295680.7789 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 23554899.0099 | 43132207.7622 | 13335.2143 | 0.76163 | 30926.8913 | 56631.3233 | 630.4865 | 1154.5061
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.1734 | 5.4217 | 0.25089 | 4 | 25568.2516 | 45076.1547 | 521.2434 | 918.9384 | 103.8878 | 0 | 105.7046 | 1184627.4607 | 76160.5875 | 1334937.4831 | 1105417.726 | 0 | 302403.8655 | 0 | 1561383.3779 | 4062399.2656 | 2772670.9727 | 12400000.7391 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 25659218.9702 | 45236527.7224 | 17782.7941 | 1.0036 | 25568.2516 | 45076.1547 | 521.2434 | 918.9384
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.725 | 6.7618 | 0.32537 | 4 | 21539.0289 | 36581.1439 | 439.1022 | 745.7561 | 104.1149 | 0 | 107.3634 | 1385880.2754 | 89143.0786 | 1592677.9221 | 1369833.3395 | 0 | 332440.3916 | 0 | 1860290.2528 | 4840093.6398 | 3303463.3632 | 14773822.263 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 28033040.494 | 47610349.2463 | 23713.7371 | 1.3015 | 21539.0289 | 36581.1439 | 439.1022 | 745.7561
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3755 | 8.2966 | 0.41446 | 4 | 18485.3348 | 30294.1926 | 376.8486 | 617.5881 | 104.2858 | 0 | 121.2599 | 1602449.8227 | 103081.2095 | 1875621.8617 | 1672545.9317 | 0 | 359882.3184 | 0 | 2189296.6462 | 5696100.7869 | 3887705.8302 | 17386684.4073 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 30645902.6383 | 50223211.3905 | 31622.7766 | 1.6578 | 18485.3348 | 30294.1926 | 376.8486 | 617.5881
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.7318 | 9.9551 | 0.51601 | 4 | 16164.9674 | 25649.9521 | 329.5447 | 522.909 | 104.4031 | 0 | 133.8901 | 1823545.475 | 117274.5921 | 2169837.6719 | 1999830.6656 | 0 | 381000.1424 | 0 | 2531680.5333 | 6586913.4287 | 4495703.7626 | 20105786.2716 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 33365004.5027 | 52942313.2549 | 42169.6503 | 2.064 | 16164.9674 | 25649.9521 | 329.5447 | 522.909
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.2714 | 11.6421 | 0.62539 | 4 | 14405.5509 | 22231.5794 | 293.6766 | 453.2208 | 104.4683 | 0 | 127.46 | 2037361.9068 | 130959.8824 | 2459208.2209 | 2333178.3502 | 0 | 393285.8508 | 0 | 2868057.7423 | 7462097.926 | 5093035.1653 | 22777185.0447 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 36036403.2757 | 55613712.0279 | 56234.1325 | 2.5016 | 14405.5509 | 22231.5794 | 293.6766 | 453.2208
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.4212 | 13.2537 | 0.73621 | 4 | 13076.8356 | 19724.8255 | 266.589 | 402.1172 | 104.4868 | 0 | 148.5691 | 2232914.1567 | 143433.5282 | 2727937.2716 | 2652351.22 | 0 | 395764.7325 | 0 | 3179436.3545 | 8272241.2024 | 5645974.5982 | 25250053.0642 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 38509271.2953 | 58086580.0475 | 74989.4209 | 2.9448 | 13076.8356 | 19724.8255 | 266.589 | 402.1172
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.7498 | 14.7131 | 0.84224 | 4 | 12077.1219 | 17888.2316 | 246.2085 | 364.6758 | 104.4704 | 0 | 135.5727 | 2403641.489 | 154284.1556 | 2965744.7208 | 2942228.7393 | 0 | 389669.1113 | 0 | 3453671.6043 | 8985745.0689 | 6132955.6481 | 27427940.5373 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 40687158.7684 | 60264467.5206 | 100000 | 3.3689 | 12077.1219 | 17888.2316 | 246.2085 | 364.6758
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.9971 | 15.976 | 0.93862 | 4 | 11326.8539 | 16541.2564 | 230.9132 | 337.2159 | 104.4326 | 0 | 171.3009 | 2547011.8522 | 163363.5303 | 3167780.6697 | 3193858.2148 | 0 | 377355.668 | 0 | 3685254.2746 | 9588275.673 | 6544195.1662 | 29267095.0488 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 42526313.2798 | 62103622.0321 | 133352.1432 | 3.7545 | 11326.8539 | 16541.2564 | 230.9132 | 337.2159
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.0749 | 17.0292 | 1.0225 | 4 | 10764.5561 | 15551.0717 | 219.45 | 317.0296 | 104.3855 | 0 | 161.6366 | 2663752.0914 | 170732.1025 | 3333895.4911 | 3404384.7541 | 0 | 361472.1185 | 0 | 3874352.2575 | 10080269.835 | 6879991.2912 | 30768849.9414 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 44028068.1724 | 63605376.9247 | 177827.941 | 4.0901 | 10764.5561 | 15551.0717 | 219.45 | 317.0296
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0176 | 17.8815 | 1.093 | 4 | 10343.3505 | 14821.2569 | 210.8632 | 302.1514 | 104.3374 | 0 | 155.7071 | 2756449.2699 | 176566.2221 | 3466846.6345 | 3575227.2211 | 0 | 344273.6455 | 0 | 4024551.5673 | 10471057.629 | 7146711.9905 | 31961684.1797 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 45220902.4107 | 64798211.163 | 237137.3706 | 4.372 | 10343.3505 | 14821.2569 | 210.8632 | 302.1514
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9493 | 18.5566 | 1.1506 | 4 | 10027.8392 | 14281.6922 | 204.4311 | 291.1516 | 104.2933 | 0 | 177.0442 | 2828801.0558 | 181108.827 | 3571274.7931 | 3710874.8847 | 0 | 327489.4505 | 0 | 4141624.1143 | 10775656.3815 | 7354606.898 | 32891436.4049 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 46150654.6359 | 65727963.3882 | 316227.766 | 4.6023 | 10027.8392 | 14281.6922 | 204.4311 | 291.1516
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.377 | 19.1429 | 1.1999 | 4 | 9783.2614 | 13862.169 | 199.445 | 282.5991 | 104.2508 | 0 | 164.7774 | 2890907.378 | 185000.1533 | 3661380.9247 | 3828945.3921 | 0 | 313393.3141 | 0 | 4243054.5933 | 11039557.6815 | 7534724.9579 | 33696964.3949 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 46956182.6259 | 66533491.3782 | 421696.5034 | 4.7996 | 9783.2614 | 13862.169 | 199.445 | 282.5991
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7593 | 19.5492 | 1.236 | 4 | 9608.3622 | 13568.2738 | 195.8795 | 276.6076 | 104.2191 | 0 | 149.6579 | 2933546.6865 | 187667.2087 | 3723499.3499 | 3910899.0735 | 0 | 300416.6864 | 0 | 4311851.312 | 11218552.6314 | 7656892.6892 | 34243325.6376 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47502543.8687 | 67079852.6209 | 562341.3252 | 4.9439 | 9608.3622 | 13568.2738 | 195.8795 | 276.6076
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5593 | 19.8555 | 1.2638 | 4 | 9477.262 | 13349.9642 | 193.2068 | 272.1571 | 104.194 | 0 | 146.1421 | 2965484.335 | 189662.4162 | 3770164.4711 | 3972763.1848 | 0 | 289352.1632 | 0 | 4363096.3624 | 11351881.7409 | 7747892.546 | 34650297.2197 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47909515.4507 | 67486824.203 | 749894.2093 | 5.0552 | 9477.262 | 13349.9642 | 193.2068 | 272.1571
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9406 | 20.0901 | 1.2853 | 4 | 9378.9736 | 13186.8913 | 191.2031 | 268.8326 | 104.174 | 0 | 156.5291 | 2989831.5285 | 191181.9871 | 3805818.5495 | 4020202.3325 | 0 | 280405.4116 | 0 | 4402101.5256 | 11453365.1743 | 7817157.0746 | 34960063.5836 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48219281.8146 | 67796590.5669 | 1000000 | 5.1412 | 9378.9736 | 13186.8913 | 191.2031 | 268.8326
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9734 | 20.2653 | 1.3016 | 4 | 9305.275 | 13065.3984 | 189.7006 | 266.3558 | 104.1587 | 0 | 158.8589 | 3007943.9031 | 192311.6001 | 3832387.4298 | 4055650.5337 | 0 | 273145.1045 | 0 | 4430961.0428 | 11528451.7182 | 7868405.1837 | 35189256.5158 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48448474.7468 | 68025783.4991 | 1333521.4322 | 5.2066 | 9305.275 | 13065.3984 | 189.7006 | 266.3558
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7628 | 20.3991 | 1.3141 | 4 | 9250.0101 | 12974.3877 | 188.574 | 264.5004 | 104.1468 | 0 | 163.8344 | 3021735.6864 | 193171.2748 | 3852644.3475 | 4082733.0835 | 0 | 267493.2674 | 0 | 4452933.2872 | 11585618.9911 | 7907423.0221 | 35363752.96 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48622971.191 | 68200279.9433 | 1778279.41 | 5.2565 | 9250.0101 | 12974.3877 | 188.574 | 264.5004
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.365 | 20.501 | 1.3237 | 4 | 9208.5663 | 12906.1604 | 187.7291 | 263.1095 | 104.1377 | 0 | 153.2245 | 3032225.7388 | 193824.8666 | 3868066.829 | 4103384.5822 | 0 | 263143.078 | 0 | 4469651.5869 | 11629116.5775 | 7937111.0186 | 35496524.2775 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48755742.5085 | 68333051.2607 | 2371373.7057 | 5.2946 | 9208.5663 | 12906.1604 | 187.7291 | 263.1095
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7982 | 20.5743 | 1.3307 | 4 | 9177.4867 | 12855.4901 | 187.0955 | 262.0766 | 104.131 | 0 | 145.4037 | 3039757.0459 | 194293.9592 | 3879147.4916 | 4118239.54 | 0 | 259641.805 | 0 | 4481521.1382 | 11659998.7152 | 7958188.7122 | 35590788.4072 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 48850006.6382 | 68427315.3904 | 3162277.6602 | 5.3228 | 9177.4867 | 12855.4901 | 187.0955 | 262.0766
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.7337 | 20.7326 | 1.3404 | 4 | 9154.298 | 12805.6701 | 186.6227 | 261.0609 | 104.1164 | 0 | 125.4803 | 3055978.6196 | 195303.9886 | 3903034.2848 | 4150308.9952 | 0 | 261345.427 | 0 | 4510728.8129 | 11735991.0935 | 8010055.0718 | 35822746.2935 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 49081964.5246 | 68659273.2768 | 4216965.0343 | 5.3616 | 9154.298 | 12805.6701 | 186.6227 | 261.0609
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.7461 | 20.7347 | 1.3439 | 4 | 9127.9667 | 12769.907 | 186.0859 | 260.3318 | 104.1163 | 0 | 141.8483 | 3056193.6492 | 195317.3854 | 3903350.7664 | 4150733.9411 | 0 | 255716.026 | 0 | 4508911.5896 | 11731263.0511 | 8006828.0857 | 35808314.4946 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 49067532.7256 | 68644841.4779 | 5623413.2519 | 5.3755 | 9127.9667 | 12769.907 | 186.0859 | 260.3318
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120 | 20.9464 | 1.3543 | 4 | 9117.2412 | 12731.0806 | 185.8673 | 259.5403 | 104.0964 | 0 | 148.4026 | 3077837.5361 | 196664.137 | 3935270.6628 | 4193693.4163 | 0 | 262274.3547 | 0 | 4549638.6417 | 11837226.4864 | 8079150.3076 | 36131755.5425 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 49390973.7735 | 68968282.5258 | 7498942.0933 | 5.4173 | 9117.2412 | 12731.0806 | 185.8673 | 259.5403
1 | 3700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.7339 | 20.7326 | 1.3456 | 4 | 9113.7623 | 12750.9944 | 185.7964 | 259.9463 | 104.1164 | 0 | 138.595 | 3055977.5192 | 195303.8403 | 3903035.1168 | 4150312.7916 | 0 | 252504.4574 | 0 | 4507282.1529 | 11727023.5912 | 8003934.5672 | 35795374.0367 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 49054592.2677 | 68631901.02 | 10000000 | 5.3825 | 9113.7623 | 12750.9944 | 185.7964 | 259.9463
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.8856 | [19 empty] | 100 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8884 | [19 empty] | 133.3521 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3039 | [19 empty] | 177.8279 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5533 | [19 empty] | 237.1374 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6983 | [19 empty] | 316.2278 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4235 | [19 empty] | 421.6965 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5754 | [19 empty] | 562.3413 | 0
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.20255 | 0.0026556 | 4 | 1387388.0302 | 3286140.3913 | 28283.7816 | 66992.4167 | 87.1947 | 0 | 29.4536 | 105483.5609 | 6115.3813 | 97462.7186 | 72099.6228 | 0 | 59565.9152 | 0 | 132883.6076 | 345735.8887 | 235971.8482 | 1055318.5433 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14737484.6466 | 34906920.4199 | 749.8942 | 0.010622 | 1387388.0302 | 3286140.3913 | 28283.7816 | 66992.4167
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.33444 | 0.0064926 | 4 | 584931.82 | 1361565.3119 | 11924.6263 | 27757.3505 | 92.9349 | 0 | 383.7492 | 156529.4098 | 9411.9319 | 144924.8879 | 98552.6988 | 0 | 77693.9421 | 0 | 189974.0195 | 494273.4297 | 337351.772 | 1508712.0917 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15190878.1949 | 35360313.9682 | 1000 | 0.02597 | 584931.82 | 1361565.3119 | 11924.6263 | 27757.3505
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1808 | 0.48326 | 0.012089 | 4 | 323589.6189 | 740681.8196 | 6596.8121 | 15099.8007 | 96.3952 | 0 | 63.7579 | 207497.0176 | 12751.3542 | 194042.8123 | 127829.6697 | 0 | 92551.4431 | 0 | 247522.1958 | 644001.9797 | 439544.5841 | 1965741.0566 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15647907.1598 | 35817342.9331 | 1333.5214 | 0.048357 | 323589.6189 | 740681.8196 | 6596.8121 | 15099.8007
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3166 | 0.68962 | 0.020066 | 4 | 202284.8953 | 453579.5331 | 4123.8512 | 9246.8323 | 99.1142 | 0 | 83.2937 | 270993.5511 | 16939.1031 | 257372.0919 | 168101.8426 | 0 | 111080.22 | 0 | 321549.8554 | 836606.7647 | 571001.3075 | 2553644.7363 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16235810.8395 | 36405246.6128 | 1778.2794 | 0.080262 | 202284.8953 | 453579.5331 | 4123.8512 | 9246.8323
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7218 | 0.94648 | 0.030882 | 4 | 136921.8196 | 300201.2022 | 2791.3365 | 6120.0076 | 101.0497 | 0 | 94.0573 | 342463.1218 | 21665.0341 | 331088.5789 | 217941.6559 | 0 | 130151.4605 | 0 | 406890.842 | 1058646.5061 | 722547.9934 | 3231395.1928 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16913561.296 | 37082997.0694 | 2371.3737 | 0.12353 | 136921.8196 | 300201.2022 | 2791.3365 | 6120.0076
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4487 | 1.2624 | 0.045198 | 4 | 97859.6165 | 209421.5626 | 1995.0006 | 4269.3418 | 102.4182 | 0 | 87.2483 | 422583.086 | 26958.9913 | 416451.8882 | 279178.2277 | 0 | 149525.4374 | 0 | 504932.076 | 1313729.6858 | 896647.505 | 4010006.8975 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 17692173.0007 | 37861608.774 | 3162.2777 | 0.18079 | 97859.6165 | 209421.5626 | 1995.0006 | 4269.3418
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8823 | 1.7118 | 0.065034 | 4 | 72060.4017 | 149594.5064 | 1469.0488 | 3049.6864 | 103.6592 | 0 | 114.2326 | 527220.0468 | 33886.7487 | 530875.9199 | 366188.5634 | 0 | 176619.2267 | 0 | 637568.2971 | 1658821.9259 | 1132180.0498 | 5063360.7784 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 18745526.8817 | 38914962.655 | 4216.965 | 0.26014 | 72060.4017 | 149594.5064 | 1469.0488 | 3049.6864
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7935 | 2.2485 | 0.090683 | 4 | 54929.0262 | 110533.2911 | 1119.8025 | 2253.3706 | 104.4957 | 0 | 85.7187 | 641602.7704 | 41437.2964 | 659905.6525 | 469934.5555 | 0 | 202563.0447 | 0 | 786022.8946 | 2045070.3364 | 1395802.5266 | 6242339.0771 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 19924505.1804 | 40093940.9537 | 5623.4133 | 0.36273 | 54929.0262 | 110533.2911 | 1119.8025 | 2253.3706
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4935 | 2.9311 | 0.12429 | 4 | 42939.4894 | 83509.2948 | 875.3796 | 1702.4499 | 105.1402 | 0 | 100.4527 | 775826.6433 | 50280.1142 | 815424.9728 | 601758.5074 | 0 | 231601.4527 | 0 | 965207.7593 | 2511272.5983 | 1713995.1498 | 7665367.1978 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 21347533.301 | 41516969.0743 | 7498.9421 | 0.49715 | 42939.4894 | 83509.2948 | 875.3796 | 1702.4499
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.0808 | 3.7781 | 0.16779 | 4 | 34309.1665 | 64360.7818 | 699.4388 | 1312.0816 | 105.6301 | 0 | 108.7339 | 930066.3383 | 60422.3094 | 998663.8435 | 765607.3759 | 0 | 262354.0086 | 0 | 1176674.4115 | 3061465.4497 | 2089513.0762 | 9344766.8131 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 23026932.9163 | 43196368.6897 | 10000 | 0.67116 | 34309.1665 | 64360.7818 | 699.4388 | 1312.0816
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6982 | 4.8157 | 0.22331 | 4 | 27975.3597 | 50555.6568 | 570.3155 | 1030.6454 | 106.0044 | 0 | 98.7073 | 1105633.2505 | 71940.2186 | 1212301.5154 | 966290.1329 | 0 | 294265.7734 | 0 | 1423668.0474 | 3704092.2249 | 2528119.055 | 11306310.218 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 24988476.3213 | 45157912.0946 | 13335.2143 | 0.89323 | 27975.3597 | 50555.6568 | 570.3155 | 1030.6454
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4922 | 6.0707 | 0.29302 | 4 | 23254.7196 | 40462.8562 | 474.0789 | 824.8901 | 106.2925 | 0 | 117.5438 | 1303607.3028 | 84895.4733 | 1458755.8609 | 1208597.4074 | 0 | 326862.833 | 0 | 1709260.3622 | 4447144.8449 | 3035267.7363 | 13574391.8209 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 27256557.9241 | 47425993.6975 | 17782.7941 | 1.1721 | 23254.7196 | 40462.8562 | 474.0789 | 824.8901
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.4971 | 7.5496 | 0.37857 | 4 | 19692.356 | 33011.8317 | 401.4553 | 672.9908 | 106.5131 | 0 | 128.777 | 1522038.9911 | 99156.2313 | 1736465.2551 | 1494119.018 | 0 | 358515.3601 | 0 | 2032014.9937 | 5286886.19 | 3608408.4593 | 16137604.4987 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 29819770.6019 | 49989206.3752 | 23713.7371 | 1.5143 | 19692.356 | 33011.8317 | 401.4553 | 672.9908
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.5297 | 9.2181 | 0.47976 | 4 | 16987.0608 | 27497.2591 | 346.3042 | 560.5688 | 106.6753 | 0 | 118.5826 | 1753841.5419 | 114253.0854 | 2036992.4039 | 1816269.9749 | 0 | 386180.9377 | 0 | 2381939.7981 | 6197318.7516 | 4229797.3901 | 18916593.8835 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 32598759.9867 | 52768195.7601 | 31622.7766 | 1.919 | 16987.0608 | 27497.2591 | 346.3042 | 560.5688
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1398 | 10.9908 | 0.59345 | 4 | 14930.7017 | 23427.393 | 304.3825 | 477.5991 | 106.7807 | 0 | 135.5743 | 1986850.494 | 129386.2768 | 2344587.1657 | 2158803.7884 | 0 | 406053.3399 | 0 | 2740015.6153 | 7128958.5764 | 4865660.7138 | 21760315.9703 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 35442482.0735 | 55611917.8468 | 42169.6503 | 2.3738 | 14930.7017 | 23427.393 | 304.3825 | 477.5991
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.8038 | 12.7679 | 0.71413 | 4 | 13372.1582 | 20433.0426 | 272.6095 | 416.5552 | 106.8316 | 0 | 149.5451 | 2209296.1625 | 143785.6993 | 2643151.854 | 2502780.6729 | 0 | 416204.5828 | 0 | 3086935.3989 | 8031572.6903 | 5481713.3935 | 24515440.4541 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 38197606.5574 | 58367042.3307 | 56234.1325 | 2.8565 | 13372.1582 | 20433.0426 | 272.6095 | 416.5552
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.9413 | 14.4402 | 0.83453 | 4 | 12195.7385 | 18237.8633 | 248.6266 | 371.8035 | 106.8357 | 0 | 155.7929 | 2410029.0025 | 156730.9593 | 2916650.6154 | 2827332.151 | 0 | 415979.1094 | 0 | 3403421.5167 | 8855004.6487 | 6043722.6249 | 27028870.6279 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 40711036.7312 | 60880472.5045 | 74989.4209 | 3.3381 | 12195.7385 | 18237.8633 | 248.6266 | 371.8035
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.1682 | 15.9373 | 0.94822 | 4 | 11310.7933 | 16628.4903 | 230.5858 | 338.9943 | 106.8065 | 0 | 138.7085 | 2583541.7418 | 167877.0147 | 3156209.3971 | 3118799.9306 | 0 | 407226.3523 | 0 | 3679125.2302 | 9572329.1568 | 6533311.3412 | 29218420.1647 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 42900586.2679 | 63070022.0413 | 100000 | 3.7929 | 11310.7933 | 16628.4903 | 230.5858 | 338.9943
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2567 | 17.2194 | 1.0504 | 4 | 10646.5761 | 15447.1272 | 217.0449 | 314.9106 | 106.7587 | 0 | 150.0522 | 2727964.0053 | 177119.2038 | 3357873.9502 | 3369268.9225 | 0 | 392541.1903 | 0 | 3909659.2361 | 10172131.351 | 6942688.6634 | 31049246.5225 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 44731412.6258 | 64900848.3991 | 133352.1432 | 4.2015 | 10646.5761 | 15447.1272 | 217.0449 | 314.9106
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.154 | 18.28 | 1.1384 | 4 | 10148.5982 | 14577.7642 | 206.8929 | 297.1874 | 106.7042 | 0 | 180.8597 | 2844732.7914 | 184565.9747 | 3522466.3924 | 3577116.1499 | 0 | 374711.4572 | 0 | 4096401.1786 | 10657995.5792 | 7274300.9827 | 32532290.5061 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 46214456.6094 | 66383892.3827 | 177827.941 | 4.5538 | 10148.5982 | 14577.7642 | 206.8929 | 297.1874
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.9212 | 19.1329 | 1.2119 | 4 | 9775.405 | 13936.2659 | 199.2849 | 284.1096 | 106.651 | 0 | 186.2983 | 2936978.4437 | 190431.262 | 3653489.0418 | 3744758.0964 | 0 | 356021.1867 | 0 | 4243854.432 | 11041638.6978 | 7536145.2942 | 33703316.4547 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 47385482.558 | 67554918.3313 | 237137.3706 | 4.8474 | 9775.405 | 13936.2659 | 199.2849 | 284.1096
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.7191 | 19.8095 | 1.2716 | 4 | 9495.7262 | 13460.9677 | 193.5832 | 274.42 | 106.603 | 0 | 167.6829 | 3009138.2117 | 195007.9799 | 3756608.5038 | 3878058.1751 | 0 | 338317.6174 | 0 | 4359080.8903 | 11341434.3061 | 7740761.9571 | 34618407.6414 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 48300573.7446 | 68470009.5179 | 316227.766 | 5.0866 | 9495.7262 | 13460.9677 | 193.5832 | 274.42
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0371 | 20.3983 | 1.3229 | 4 | 9277.8415 | 13089.3644 | 189.1413 | 266.8444 | 106.5573 | 0 | 146.209 | 3071243.9867 | 198938.7001 | 3845805.9252 | 3994324.5037 | 0 | 323489.8219 | 0 | 4459183.1457 | 11601879.8408 | 7918521.3861 | 35413387.3101 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49095553.4133 | 69264989.1867 | 421696.5034 | 5.2917 | 9277.8415 | 13089.3644 | 189.1413 | 266.8444
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.3 | 20.7987 | 1.3599 | 4 | 9122.7494 | 12830.6856 | 185.9796 | 261.5709 | 106.5241 | 0 | 167.112 | 3113103.256 | 201583.3744 | 3906164.7408 | 4073511.3779 | 0 | 309890.6352 | 0 | 4525658.8199 | 11774835.909 | 8036567.4566 | 35941315.5696 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49623481.6729 | 69792917.4462 | 562341.3252 | 5.4395 | 9122.7494 | 12830.6856 | 185.9796 | 261.5709
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.0271 | 21.1035 | 1.3885 | 4 | 9006.4602 | 12637.9979 | 183.6089 | 257.6427 | 106.4977 | 0 | 150.1803 | 3144786.0058 | 203582.5883 | 3951978.4314 | 4133890.3242 | 0 | 298545.7356 | 0 | 4575785.4033 | 11905254.9966 | 8125581.1637 | 36339404.6489 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50021570.7522 | 70191006.5255 | 749894.2093 | 5.554 | 9006.4602 | 12637.9979 | 183.6089 | 257.6427
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3307 | 21.3332 | 1.4104 | 4 | 8919.2542 | 12494.3902 | 181.8311 | 254.715 | 106.4772 | 0 | 155.1842 | 3168547.6809 | 205080.5279 | 3986411.7341 | 4179426.8265 | 0 | 289261.3402 | 0 | 4613203.9627 | 12002610.4128 | 8192028.2357 | 36636570.7209 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50318736.8242 | 70488172.5975 | 1000000 | 5.6416 | 8919.2542 | 12494.3902 | 181.8311 | 254.715
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.3318 | 21.5094 | 1.4272 | 4 | 8853.8528 | 12386.8281 | 180.4978 | 252.5222 | 106.461 | 0 | 139.7542 | 3186709.1298 | 206224.583 | 4012772.448 | 4214378.1816 | 0 | 281969.2386 | 0 | 4641800.8966 | 12077013.7687 | 8242810.055 | 36863678.3013 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50545844.4045 | 70715280.1779 | 1333521.4322 | 5.7089 | 8853.8528 | 12386.8281 | 180.4978 | 252.5222
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.0823 | 21.6413 | 1.44 | 4 | 8804.8024 | 12306.4995 | 179.4978 | 250.8846 | 106.4487 | 0 | 136.8038 | 3200274.4135 | 207078.6238 | 4032486.3568 | 4240568.0106 | 0 | 276198.947 | 0 | 4663076.4771 | 12132368.465 | 8280590.7726 | 37032642.0663 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50714808.1696 | 70884243.9429 | 1778279.41 | 5.7599 | 8804.8024 | 12306.4995 | 179.4978 | 250.8846
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.6398 | 21.7393 | 1.4496 | 4 | 8768.0148 | 12246.5397 | 178.7478 | 249.6623 | 106.4395 | 0 | 149.3354 | 3210324.1347 | 207711.0617 | 4047104.7542 | 4260016.9209 | 0 | 271656.409 | 0 | 4678757.1794 | 12173166.4357 | 8308436.2259 | 37157173.1216 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50839339.2248 | 71008774.9981 | 2371373.7057 | 5.7983 | 8768.0148 | 12246.5397 | 178.7478 | 249.6623
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.0755 | 21.8158 | 1.4569 | 4 | 8740.4244 | 12201.3494 | 178.1854 | 248.741 | 106.4322 | 0 | 165.0836 | 3218162.2274 | 208204.1623 | 4058514.0165 | 4275212.999 | 0 | 268278.4558 | 0 | 4691065.0257 | 12205188.9272 | 8330292.2344 | 37254918.0481 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50937084.1514 | 71106519.9247 | 3162277.6602 | 5.8278 | 8740.4244 | 12201.3494 | 178.1854 | 248.741
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3922 | 21.8713 | 1.4624 | 4 | 8719.7323 | 12167.7029 | 177.7635 | 248.0551 | 106.4269 | 0 | 159.9062 | 3223850.8703 | 208561.9494 | 4066798.9447 | 4286257.0442 | 0 | 265611.8255 | 0 | 4699921.4473 | 12228231.5194 | 8346019.277 | 37325252.8779 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 51007418.9811 | 71176854.7544 | 4216965.0343 | 5.8497 | 8719.7323 | 12167.7029 | 177.7635 | 248.0551
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.624 | 21.912 | 1.4665 | 4 | 8704.2138 | 12142.6082 | 177.4472 | 247.5435 | 106.423 | 0 | 169.3387 | 3228007.5996 | 208823.3383 | 4072855.1806 | 4294335.1434 | 0 | 263534.952 | 0 | 4706346.9234 | 12244949.2902 | 8357429.4991 | 37376281.9267 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 51058448.0299 | 71227883.8032 | 5623413.2519 | 5.8659 | 8704.2138 | 12142.6082 | 177.4472 | 247.5435
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.9172 | 21.4363 | 1.4478 | 4 | 8687.1401 | 12169.9542 | 177.0991 | 248.101 | 106.4674 | 0 | 157.1865 | 3179177.0125 | 205749.8023 | 4001846.7333 | 4199894.5477 | 0 | 238714.2809 | 0 | 4611899.1269 | 11999215.4977 | 8189711.1364 | 36626208.1379 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 50308374.2411 | 70477810.0144 | 7498942.0933 | 5.7911 | 8687.1401 | 12169.9542 | 177.0991 | 248.101
1 | 3800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9451 | 21.9683 | 1.472 | 4 | 8683.8479 | 12109.4055 | 177.032 | 246.8666 | 106.4175 | 0 | 151.5629 | 3233763.1662 | 209185.2046 | 4081244.059 | 4305531.4055 | 0 | 260891.9444 | 0 | 4715340.1541 | 12268347.8317 | 8373399.4845 | 37447703.2499 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 51129869.3532 | 71299305.1265 | 10000000 | 5.8879 | 8683.8479 | 12109.4055 | 177.032 | 246.8666
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.2133 | [19 empty] | 100 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1563 | [19 empty] | 133.3521 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9444 | [19 empty] | 177.8279 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9071 | [19 empty] | 237.1374 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.6229 | [19 empty] | 316.2278 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9497 | [19 empty] | 421.6965 | 0
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.20854 | 0.0003679 | 4 | 10342301.2641 | 24456133.1 | 210841.8003 | 498571.3526 | 88.6011 | 0 | 28.9039 | 108946.7494 | 6367.3742 | 99653.2922 | 72715.7469 | 0 | 70262.3464 | 0 | 139598.7486 | 363207.3082 | 247896.451 | 1108648.0169 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15219622.0832 | 35989389.0049 | 562.3413 | 0.0014716 | 10342301.2641 | 24456133.1 | 210841.8003 | 498571.3526
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.24922 | 0.0037525 | 4 | 1021965.1923 | 2405709.235 | 20834.1428 | 49043.6367 | 90.8533 | 0 | 290.8709 | 125574.3634 | 7444.555 | 114722.4561 | 80786.4206 | 0 | 68130.9564 | 0 | 154696.9131 | 402489.6352 | 274707.4464 | 1228552.7463 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15339526.8126 | 36109293.7343 | 749.8942 | 0.01501 | 1021965.1923 | 2405709.235 | 20834.1428 | 49043.6367
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.38138 | 0.0083489 | 4 | 472331.6832 | 1094263.4184 | 9629.1202 | 22308.0399 | 95.6399 | 0 | 380.3463 | 175094.5074 | 10697.9597 | 160652.1864 | 106620.7709 | 0 | 83801.6031 | 0 | 209378.1408 | 544758.9729 | 371809.1927 | 1662813.334 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15773787.4003 | 36543554.3219 | 1000 | 0.033396 | 472331.6832 | 1094263.4184 | 9629.1202 | 22308.0399
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5124 | 0.56234 | 0.015064 | 4 | 270807.801 | 615502.104 | 5520.7833 | 12547.8429 | 99.2314 | 0 | 63.7997 | 235380.5821 | 14706.4944 | 218590.9776 | 141380.4715 | 0 | 102416.6473 | 0 | 277865.3175 | 722948.558 | 493427.2459 | 2206716.2943 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16317690.3606 | 37087457.2823 | 1333.5214 | 0.060256 | 270807.801 | 615502.104 | 5520.7833 | 12547.8429
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7085 | 0.78868 | 0.024393 | 4 | 173642.8311 | 386509.4231 | 3539.944 | 7879.5174 | 101.7568 | 0 | 96.0625 | 303116.5721 | 19235.9827 | 285992.2915 | 184457.3634 | 0 | 121447.0055 | 0 | 356557.1939 | 927688.6787 | 633166.5853 | 2831661.6731 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16942635.7394 | 37712402.6611 | 1778.2794 | 0.097572 | 173642.8311 | 386509.4231 | 3539.944 | 7879.5174
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2313 | 1.0786 | 0.037096 | 4 | 119211.3763 | 259184.1039 | 2430.2852 | 5283.8185 | 103.6189 | 0 | 93.2211 | 381853.5354 | 24513.4618 | 366892.8 | 239722.4112 | 0 | 142277.5798 | 0 | 450551.3174 | 1172242.1071 | 800079.3252 | 3578132.5379 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 17689106.6042 | 38458873.5258 | 2371.3737 | 0.14838 | 119211.3763 | 259184.1039 | 2430.2852 | 5283.8185
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0166 | 1.4178 | 0.053602 | 4 | 86291.4745 | 183161.0119 | 1759.1684 | 3733.985 | 104.8587 | 0 | 93.6873 | 465935.0359 | 30136.8046 | 456174.0199 | 304214.0936 | 0 | 161168.1502 | 0 | 552874.9606 | 1438467.2373 | 981783.447 | 4390753.7491 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 18501727.8154 | 39271494.7371 | 3162.2777 | 0.21441 | 86291.4745 | 183161.0119 | 1759.1684 | 3733.985
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6935 | 1.9332 | 0.076991 | 4 | 63918.8323 | 131361.2211 | 1303.0719 | 2677.9762 | 106.1368 | 0 | 85.6221 | 583626.3254 | 38035.8844 | 584061.1889 | 401836.8001 | 0 | 191991.3398 | 0 | 701825.1 | 1826004.9461 | 1246285.8963 | 5573667.4809 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 19684641.5472 | 40454408.4688 | 4216.965 | 0.30796 | 63918.8323 | 131361.2211 | 1303.0719 | 2677.9762
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8413 | 2.5368 | 0.10687 | 4 | 49078.8847 | 97664.5675 | 1000.5394 | 1991.0243 | 106.9517 | 0 | 80.9611 | 709630.4396 | 46458.2941 | 725480.0389 | 516017.247 | 0 | 220388.7873 | 0 | 865010.1747 | 2250579.0367 | 1536066.4373 | 6869630.4558 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 20980604.5221 | 41750371.4437 | 5623.4133 | 0.42749 | 49078.8847 | 97664.5675 | 1000.5394 | 1991.0243
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8165 | 3.3002 | 0.14598 | 4 | 38596.3057 | 74165.7645 | 786.8379 | 1511.9694 | 107.5766 | 0 | 106.5331 | 856811.9169 | 56279.3255 | 895000.4598 | 660742.9682 | 0 | 251715.3789 | 0 | 1061014.5192 | 2760542.135 | 1884126.7306 | 8426233.4342 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 22537207.5005 | 43306974.4221 | 7498.9421 | 0.58392 | 38596.3057 | 74165.7645 | 786.8379 | 1511.9694
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.7035 | 4.2391 | 0.19632 | 4 | 31017.4333 | 57466.9422 | 632.3323 | 1171.5413 | 108.0495 | 0 | 64.2689 | 1024560.5354 | 67446.5547 | 1093107.6825 | 838689.4926 | 0 | 284225.0149 | 0 | 1290131.4192 | 3356657.3105 | 2290987.5868 | 10245805.5966 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 24356779.6629 | 45126546.5846 | 10000 | 0.78526 | 31017.4333 | 57466.9422 | 632.3323 | 1171.5413
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.7009 | 5.3912 | 0.26036 | 4 | 25432.7424 | 45376.4165 | 518.4809 | 925.0596 | 108.4135 | 0 | 97.5262 | 1215954.0649 | 80154.5698 | 1324587.7776 | 1056549.5595 | 0 | 318302.0255 | 0 | 1558263.7189 | 4054282.5528 | 2767131.1495 | 12375225.4184 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 26486199.4847 | 47255966.4064 | 13335.2143 | 1.0414 | 25432.7424 | 45376.4165 | 518.4809 | 925.0596
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9166 | 6.7778 | 0.34045 | 4 | 21249.7473 | 36501.2531 | 433.2048 | 744.1274 | 108.6935 | 0 | 113.2514 | 1430953.3827 | 94395.6923 | 1590438.6785 | 1318703.4394 | 0 | 352750.8804 | 0 | 1867024.4086 | 4857614.5319 | 3315421.732 | 14827302.7458 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 28938276.8121 | 49708043.7338 | 17782.7941 | 1.3618 | 21249.7473 | 36501.2531 | 433.2048 | 744.1274
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.3204 | 8.393 | 0.43791 | 4 | 18084.4766 | 29941.8624 | 368.6765 | 610.4054 | 108.906 | 0 | 115.5914 | 1665686.7959 | 109906.3847 | 1886747.3588 | 1624050.089 | 0 | 385201.4891 | 0 | 2211920.9258 | 5754964.5216 | 3927881.5387 | 17566359.1035 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 31677333.1698 | 52447100.0915 | 23713.7371 | 1.7516 | 18084.4766 | 29941.8624 | 368.6765 | 610.4054
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.7091 | 10.1967 | 0.55206 | 4 | 15677.1716 | 25082.7813 | 319.6003 | 511.3464 | 109.0585 | 0 | 121.3059 | 1912605.0075 | 126180.6069 | 2204451.1331 | 1965292.2417 | 0 | 412774.3238 | 0 | 2582308.2921 | 6718636.4717 | 4585607.4461 | 20507855.5229 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 34618829.5892 | 55388596.5108 | 31622.7766 | 2.2082 | 15677.1716 | 25082.7813 | 319.6003 | 511.3464
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.5628 | 12.0861 | 0.67863 | 4 | 13847.1144 | 21498.4911 | 282.2922 | 438.2758 | 109.1509 | 0 | 140.2649 | 2157672.1405 | 142283.9662 | 2525413.9288 | 2323303.8257 | 0 | 431334.4293 | 0 | 2956203.2333 | 7691434.4123 | 5249562.0296 | 23477207.9655 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 37588182.0318 | 58357948.9535 | 42169.6503 | 2.7145 | 13847.1144 | 21498.4911 | 282.2922 | 438.2758
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.2823 | 13.9425 | 0.81067 | 4 | 12461.0551 | 18866.1556 | 254.0355 | 384.6121 | 109.1863 | 0 | 138.6748 | 2387319.7999 | 157318.1975 | 2831157.65 | 2675708.7105 | 0 | 438723.0549 | 0 | 3311188.691 | 8615033.7558 | 5879937.5596 | 26296387.4193 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 40407361.4856 | 61177128.4072 | 56234.1325 | 3.2427 | 12461.0551 | 18866.1556 | 254.0355 | 384.6121
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.3855 | 15.6716 | 0.94072 | 4 | 11415.4121 | 16935.0551 | 232.7186 | 345.244 | 109.1755 | 0 | 151.4609 | 2592755.5863 | 170711.6734 | 3108749.9759 | 3004812.1663 | 0 | 435697.8432 | 0 | 3631963.6256 | 9449624.3356 | 6449562.7794 | 28843877.9856 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 42954852.0519 | 63724618.9735 | 74989.4209 | 3.7629 | 11415.4121 | 16935.0551 | 232.7186 | 345.244
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.4855 | 17.2004 | 1.0619 | 4 | 10628.9833 | 15518.8143 | 216.6862 | 316.372 | 109.1338 | 0 | 137.5221 | 2768388.9228 | 182113.3807 | 3349183.9486 | 3296671.4583 | 0 | 424161.4305 | 0 | 3908002.465 | 10167820.7724 | 6939746.605 | 31036088.9834 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 45147063.0497 | 65916829.9714 | 100000 | 4.2475 | 10628.9833 | 15518.8143 | 216.6862 | 316.372
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.4085 | 18.4986 | 1.1696 | 4 | 10038.6182 | 14478.0887 | 204.6508 | 295.1554 | 109.0763 | 0 | 176.6088 | 2913513.5035 | 191496.2198 | 3550071.0168 | 3545272.7281 | 0 | 407119.1173 | 0 | 4136914.3083 | 10763402.4325 | 7346243.326 | 32854032.6522 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 46965006.7185 | 67734773.6402 | 133352.1432 | 4.6784 | 10038.6182 | 14478.0887 | 204.6508 | 295.1554
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.1313 | 19.5652 | 1.2617 | 4 | 9595.8459 | 13711.3011 | 195.6243 | 279.5234 | 109.0148 | 0 | 156.2048 | 3030190.7823 | 199012.2299 | 3713074.6577 | 3750129.2634 | 0 | 387434.4014 | 0 | 4321138.1205 | 11242715.0023 | 7673384.0038 | 34317078.4614 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 48428052.5277 | 69197819.4493 | 177827.941 | 5.0468 | 9595.8459 | 13711.3011 | 195.6243 | 279.5234
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7593 | 20.4235 | 1.3382 | 4 | 9263.8145 | 13144.1179 | 188.8554 | 267.9606 | 108.9563 | 0 | 142.7985 | 3122503.2231 | 204941.2411 | 3842973.6905 | 3915610.0068 | 0 | 367554.7651 | 0 | 4466897.3414 | 11621950.5957 | 7932220.0887 | 35474650.9524 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 49585625.0187 | 70355391.9404 | 237137.3706 | 5.3526 | 9263.8145 | 13144.1179 | 188.8554 | 267.9606
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4038 | 21.0964 | 1.3999 | 4 | 9014.8576 | 12724.0421 | 183.7801 | 259.3968 | 108.9051 | 0 | 170.4153 | 3193943.5819 | 209518.2434 | 3944086.6991 | 4045749.7098 | 0 | 348774.9295 | 0 | 4579408.5338 | 11914681.6392 | 8132015.041 | 36368178.3778 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 50479152.4441 | 71248919.3657 | 316227.766 | 5.5996 | 9014.8576 | 12724.0421 | 183.7801 | 259.3968
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.528 | 21.1192 | 1.4277 | 4 | 8823.2375 | 12460.042 | 179.8736 | 254.0148 | 108.903 | 0 | 531.2021 | 3196341.9299 | 209671.3648 | 3947499.7478 | 4050172.0769 | 0 | 309426.9454 | 0 | 4568113.7053 | 11885294.8122 | 8111957.9277 | 36278478.5102 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 50389452.5765 | 71159219.4981 | 421696.5034 | 5.711 | 8823.2375 | 12460.042 | 179.8736 | 254.0148
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7823 | 22.0845 | 1.491 | 4 | 8681.8213 | 12164.3543 | 176.9907 | 247.9868 | 108.8216 | 0 | 173.2386 | 3297391.8046 | 216126.8608 | 4091437.0137 | 4237392.8676 | 0 | 319154.3152 | 0 | 4742986.1161 | 12340276.9539 | 8422492.5884 | 37667258.5203 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51778232.5866 | 72547999.5082 | 562341.3252 | 5.964 | 8681.8213 | 12164.3543 | 176.9907 | 247.9868
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4218 | 22.3845 | 1.5202 | 4 | 8578.2465 | 11993.8788 | 174.8792 | 244.5114 | 108.7942 | 0 | 156.6912 | 3328462.9321 | 218107.134 | 4135916.4771 | 4295710.2242 | 0 | 307398.1524 | 0 | 4791382.0187 | 12466193.1651 | 8508432.9898 | 38051603.0934 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52162577.1597 | 72932344.0813 | 749894.2093 | 6.0808 | 8578.2465 | 11993.8788 | 174.8792 | 244.5114
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.6741 | 22.6132 | 1.5427 | 4 | 8500.558 | 11866.4717 | 173.2954 | 241.9141 | 108.7728 | 0 | 138.8769 | 3352051.5694 | 219609.057 | 4169753.6598 | 4340219.5171 | 0 | 297953.1714 | 0 | 4828038.9201 | 12561566.9031 | 8573527.5258 | 38342720.3236 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52453694.3899 | 73223461.3116 | 1000000 | 6.1706 | 8500.558 | 11866.4717 | 173.2954 | 241.9141
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.624 | 22.7865 | 1.5598 | 4 | 8442.2844 | 11771.2088 | 172.1074 | 239.972 | 108.7562 | 0 | 184.2152 | 3369862.0758 | 220742.228 | 4195342.154 | 4373961.9027 | 0 | 290469.853 | 0 | 4855647.5032 | 12633398.7732 | 8622554.2531 | 38561978.7429 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52672952.8093 | 73442719.7309 | 1333521.4322 | 6.2392 | 8442.2844 | 11771.2088 | 172.1074 | 239.972
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.3324 | 22.9156 | 1.5727 | 4 | 8398.5739 | 11700.0997 | 171.2163 | 238.5224 | 108.7437 | 0 | 164.6791 | 3383100.1514 | 221584.0032 | 4214383.8022 | 4399117.9671 | 0 | 284541.8559 | 0 | 4876063.8341 | 12686517.8781 | 8658809.1337 | 38724118.6257 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52835092.692 | 73604859.6136 | 1778279.41 | 6.291 | 8398.5739 | 11700.0997 | 171.2163 | 238.5224
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.866 | 23.0128 | 1.5825 | 4 | 8365.7879 | 11646.8778 | 170.5479 | 237.4374 | 108.7341 | 0 | 166.3696 | 3393045.1183 | 222216.1072 | 4228701.24 | 4418059.089 | 0 | 279946.1761 | 0 | 4891367.4149 | 12726334.6563 | 8685984.9029 | 38845654.7048 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 52956628.7711 | 73726395.6927 | 2371373.7057 | 6.3301 | 8365.7879 | 11646.8778 | 170.5479 | 237.4374
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.283 | 23.0886 | 1.5901 | 4 | 8341.1968 | 11606.7595 | 170.0466 | 236.6195 | 108.7266 | 0 | 160.7843 | 3400800.1103 | 222708.8567 | 4239873.2838 | 4432854.6094 | 0 | 276530.8437 | 0 | 4903379.4045 | 12757587.3892 | 8707315.5353 | 38941050.0329 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 53052024.0992 | 73821791.0209 | 3162277.6602 | 6.3602 | 8341.1968 | 11606.7595 | 170.0466 | 236.6195
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.5823 | 23.1431 | 1.5956 | 4 | 8322.7529 | 11576.9487 | 169.6706 | 236.0118 | 108.7211 | 0 | 179.8379 | 3406358.9681 | 223061.974 | 4247885.6606 | 4443474.2119 | 0 | 273810.8976 | 0 | 4911890.7678 | 12779732.2104 | 8722429.8309 | 39008644.5214 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 53119618.5877 | 73889385.5093 | 4216965.0343 | 6.3825 | 8322.7529 | 11576.9487 | 169.6706 | 236.0118
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8017 | 23.183 | 1.5998 | 4 | 8308.9201 | 11554.7022 | 169.3886 | 235.5582 | 108.7171 | 0 | 159.3578 | 3410430.9001 | 223320.589 | 4253757.015 | 4451260.6234 | 0 | 271700.7591 | 0 | 4918083.2557 | 12795843.7939 | 8733426.3176 | 39057823.2537 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 53168797.3201 | 73938564.2417 | 5623413.2519 | 6.399 | 8308.9201 | 11554.7022 | 169.3886 | 235.5582
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.9797 | 23.2153 | 1.603 | 4 | 8298.5457 | 11537.8064 | 169.1771 | 235.2138 | 108.7139 | 0 | 165.4969 | 3413730.3423 | 223530.1154 | 4258515.7802 | 4457574.2617 | 0 | 270202.739 | 0 | 4923185.763 | 12809119.4711 | 8742487.2401 | 39098345.7128 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 53209319.7791 | 73979086.7007 | 7498942.0933 | 6.4119 | 8298.5457 | 11537.8064 | 169.1771 | 235.2138
1 | 3900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.0964 | 23.2365 | 1.6053 | 4 | 8290.7656 | 11525.4279 | 169.0185 | 234.9614 | 108.7118 | 0 | 163.2136 | 3415891.9952 | 223667.3711 | 4261634.2479 | 4461713.0904 | 0 | 268940.059 | 0 | 4926420.2378 | 12817534.911 | 8748230.9507 | 39124032.863 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 53235006.9293 | 74004773.851 | 10000000 | 6.421 | 8290.7656 | 11525.4279 | 169.0185 | 234.9614
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.8564 | [19 empty] | 100 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9788 | [19 empty] | 133.3521 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4621 | [19 empty] | 177.8279 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5676 | [19 empty] | 237.1374 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9482 | [19 empty] | 316.2278 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0068 | [19 empty] | 421.6965 | 0
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.21459 | 0.0013711 | 4 | 2857393.891 | 6755508.6416 | 58251.8394 | 137720.1812 | 89.9911 | 0 | 28.4403 | 112444.4803 | 6624.9149 | 101848.1535 | 73387.7958 | 0 | 68941.9471 | 0 | 141666.4437 | 368587.0268 | 251568.2195 | 1125068.9816 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15670711.1018 | 37049013.299 | 562.3413 | 0.0054843 | 2857393.891 | 6755508.6416 | 58251.8394 | 137720.1812
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.29334 | 0.0051083 | 4 | 779639.5867 | 1825891.7669 | 15894.0075 | 37223.2734 | 93.9917 | 0 | 321.0196 | 144155.5246 | 8709.1205 | 130388.9352 | 88653.7627 | 0 | 75232.6612 | 0 | 174384.6016 | 453712.9622 | 309668.4195 | 1384905.9874 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15930548.1076 | 37308850.3048 | 749.8942 | 0.020433 | 779639.5867 | 1825891.7669 | 15894.0075 | 37223.2734
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.449 | 0.010578 | 4 | 388234.5564 | 893484.4621 | 7914.6866 | 18214.8893 | 98.6902 | 0 | 77.7781 | 200556.536 | 12475.5851 | 182646.6267 | 118226.3193 | 0 | 93558.1596 | 0 | 236910.6584 | 616392.9361 | 420700.8445 | 1881467.6658 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16427109.786 | 37805411.9832 | 1000 | 0.042312 | 388234.5564 | 893484.4621 | 7914.6866 | 18214.8893
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8413 | 0.64588 | 0.018469 | 4 | 230099.2064 | 519477.1518 | 4690.8836 | 10590.2444 | 101.9724 | 0 | 70.2616 | 264202.6644 | 16770.4488 | 243718.4194 | 155131.7738 | 0 | 112278.2776 | 0 | 308919.6177 | 803745.4772 | 548572.8035 | 2453339.4825 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16998981.6027 | 38377283.7999 | 1333.5214 | 0.073877 | 230099.2064 | 519477.1518 | 4690.8836 | 10590.2444
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1176 | 0.89756 | 0.029422 | 4 | 150192.5463 | 331845.4378 | 3061.8782 | 6765.1181 | 104.3728 | 0 | 74.4402 | 337680.7499 | 21754.8181 | 316555.7451 | 202264.765 | 0 | 132370.2142 | 0 | 394144.254 | 1025482.4987 | 699912.8769 | 3130165.9218 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 17675808.042 | 39054110.2392 | 1778.2794 | 0.11769 | 150192.5463 | 331845.4378 | 3061.8782 | 6765.1181
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7307 | 1.2167 | 0.044166 | 4 | 104585.2328 | 225597.4533 | 2132.1114 | 4599.1092 | 106.1349 | 0 | 77.1993 | 422376.8465 | 27506.2379 | 403272.6712 | 261842.1618 | 0 | 154071.5462 | 0 | 494937.0908 | 1287724.7847 | 878898.6257 | 3930629.9648 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 18476272.0851 | 39854574.2822 | 2371.3737 | 0.17666 | 104585.2328 | 225597.4533 | 2132.1114 | 4599.1092
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2781 | 1.7235 | 0.064696 | 4 | 76076.2561 | 158687.2363 | 1550.9174 | 3235.054 | 107.7443 | 0 | 88.1073 | 544302.7455 | 35788.5813 | 532187.5082 | 356114.3931 | 0 | 191653.521 | 0 | 647418.2322 | 1684449.4364 | 1149671.3523 | 5141585.7699 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 19687227.8902 | 41065530.0873 | 3162.2777 | 0.25878 | 76076.2561 | 158687.2363 | 1550.9174 | 3235.054
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5561 | 2.1777 | 0.090603 | 4 | 57035.6654 | 116024.846 | 1162.7492 | 2365.3234 | 108.6093 | 0 | 82.1341 | 644610.7265 | 42594.9276 | 641317.5894 | 440369.811 | 0 | 208563.8613 | 0 | 771208.1971 | 2006525.5324 | 1369494.9058 | 6124685.5512 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 20670327.6714 | 42048629.8685 | 4216.965 | 0.36241 | 57035.6654 | 116024.846 | 1162.7492 | 2365.3234
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9466 | 2.854 | 0.1253 | 4 | 44076.5873 | 86731.8233 | 898.5608 | 1768.1455 | 109.4017 | 0 | 94.1001 | 782955.0046 | 51961.5884 | 795759.9796 | 565928.5565 | 0 | 239431.9437 | 0 | 950054.4584 | 2471846.8178 | 1687086.2445 | 7545024.5935 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 22090666.7137 | 43468968.9109 | 5623.4133 | 0.50119 | 44076.5873 | 86731.8233 | 898.5608 | 1768.1455
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1855 | 3.7004 | 0.17049 | 4 | 34868.3142 | 66217.3227 | 710.8377 | 1349.9297 | 110.005 | 0 | 100.7434 | 943019.6821 | 62776.2561 | 979122.3751 | 723315.1856 | 0 | 272676.1876 | 0 | 1162554.7778 | 3024729.059 | 2064439.7347 | 9232633.258 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 23778275.3782 | 45156577.5754 | 7498.9421 | 0.68195 | 34868.3142 | 66217.3227 | 710.8377 | 1349.9297
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.413 | 4.7446 | 0.22857 | 4 | 28174.1116 | 51556.7824 | 574.3674 | 1051.0547 | 110.465 | 0 | 100.0884 | 1126176.6917 | 75122.6688 | 1194129.3875 | 917430.0917 | 0 | 307567.1368 | 0 | 1411966.1308 | 3673646.2383 | 2507339.0435 | 11213377.3891 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 25759019.5094 | 47137321.7065 | 10000 | 0.91428 | 28174.1116 | 51556.7824 | 574.3674 | 1051.0547
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.8056 | 6.0221 | 0.3023 | 4 | 23215.6837 | 40895.3721 | 473.2831 | 833.7075 | 110.8191 | 0 | 90.5851 | 1334728.7117 | 89145.9308 | 1444695.7752 | 1154867.2767 | 0 | 343913.0273 | 0 | 1703266.7814 | 4431550.7773 | 3024624.4647 | 13526792.7451 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 28072434.8653 | 49450737.0625 | 13335.2143 | 1.2092 | 23215.6837 | 40895.3721 | 473.2831 | 833.7075
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4233 | 7.5448 | 0.3939 | 4 | 19491.3462 | 33059.7121 | 397.3575 | 673.9669 | 111.0902 | 0 | 103.4849 | 1566960.6217 | 104721.9705 | 1729867.3745 | 1437771.3355 | 0 | 379786.8006 | 0 | 2035452.1601 | 5295828.9919 | 3614512.1054 | 16164901.3603 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 30710543.4805 | 52088845.6777 | 17782.7941 | 1.5756 | 19491.3462 | 33059.7121 | 397.3575 | 673.9669
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.2318 | 9.3054 | 0.50451 | 4 | 16668.0807 | 27261.7416 | 339.8014 | 555.7675 | 111.2943 | 0 | 96.5307 | 1818901.9966 | 121575.8364 | 2045605.9386 | 1764737.4988 | 0 | 413029.1557 | 0 | 2403901.6662 | 6254459.0275 | 4268796.8025 | 19091007.9225 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 33636650.0427 | 55014952.2399 | 23713.7371 | 2.018 | 16668.0807 | 27261.7416 | 339.8014 | 555.7675
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.9144 | 11.2389 | 0.63235 | 4 | 14519.6478 | 22971.5177 | 296.0027 | 468.3055 | 111.4352 | 0 | 139.7674 | 2079850.0977 | 138982.6122 | 2378862.2318 | 2123977.5274 | 0 | 439704.2436 | 0 | 2792936.9179 | 7266648.9503 | 4959637.2233 | 22180599.8042 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 36726241.9244 | 58104544.1216 | 31622.7766 | 2.5294 | 14519.6478 | 22971.5177 | 296.0027 | 468.3055
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.9487 | 13.2372 | 0.77218 | 4 | 12886.9697 | 19808.3373 | 262.7183 | 403.8197 | 111.5128 | 0 | 127.448 | 2335741.79 | 155993.4602 | 2711450.4708 | 2495756.8041 | 0 | 456298.9514 | 0 | 3180544.1759 | 8275123.5263 | 5647941.8435 | 25258851.0222 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 39804493.1424 | 61182795.3396 | 42169.6503 | 3.0887 | 12886.9697 | 19808.3373 | 262.7183 | 403.8197
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.7318 | 15.1763 | 0.91609 | 4 | 11650.907 | 17485.0229 | 237.5195 | 356.4558 | 111.532 | 0 | 127.3761 | 2572936.2951 | 171697.1853 | 3024763.3502 | 2857381.8514 | 0 | 461103.9715 | 0 | 3544274.2348 | 9221474.5284 | 6293845.848 | 28147477.2647 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 42693119.385 | 64071421.5821 | 56234.1325 | 3.6644 | 11650.907 | 17485.0229 | 237.5195 | 356.4558
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.7696 | 16.9566 | 1.0558 | 4 | 10718.6532 | 15780.762 | 218.5142 | 321.7122 | 111.506 | 0 | 150.3124 | 2782405.5344 | 185503.4064 | 3305508.2544 | 3190431.2659 | 0 | 455062.6394 | 0 | 3868375.3292 | 10064719.0936 | 6869377.5907 | 30721383.1138 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 45267025.2341 | 66645327.4312 | 74989.4209 | 4.2232 | 10718.6532 | 15780.762 | 218.5142 | 321.7122
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7427 | 18.5165 | 1.1845 | 4 | 10017.4729 | 14529.4917 | 204.2197 | 296.2033 | 111.4518 | 0 | 146.2168 | 2960126.2317 | 197164.2616 | 3546749.4313 | 3483251.6482 | 0 | 440813.645 | 0 | 4144961.035 | 10784338.3646 | 7360532.5298 | 32917937.1473 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 47463579.2675 | 68841881.4647 | 100000 | 4.7381 | 10017.4729 | 14529.4917 | 204.2197 | 296.2033
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4977 | 19.8291 | 1.2978 | 4 | 9490.9569 | 13609.148 | 193.486 | 277.4409 | 111.3849 | 0 | 161.1051 | 3105830.8389 | 206683.8924 | 3746675.8432 | 3730501.5422 | 0 | 421432.5043 | 0 | 4372338.6022 | 11375928.1529 | 7764304.7163 | 34723696.0923 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 49269338.2125 | 70647640.4097 | 133352.1432 | 5.1912 | 9490.9569 | 13609.148 | 193.486 | 277.4409
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.0466 | 20.9006 | 1.3939 | 4 | 9095.9122 | 12930.2806 | 185.4325 | 263.6013 | 111.3167 | 0 | 155.6351 | 3222342.587 | 214267.4952 | 3907974.9716 | 3932980.7402 | 0 | 399907.9911 | 0 | 4554214.7761 | 11849132.6496 | 8087276.5087 | 36168097.7194 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 50713739.8397 | 72092042.0368 | 177827.941 | 5.5754 | 9095.9122 | 12930.2806 | 185.4325 | 263.6013
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.5024 | 21.7563 | 1.473 | 4 | 8799.5909 | 12427.9421 | 179.3916 | 253.3604 | 111.2537 | 0 | 160.2021 | 3313904.2389 | 220207.9593 | 4035647.7018 | 4095141.2823 | 0 | 378570.709 | 0 | 4696954.0376 | 12220510.9281 | 8340749.8148 | 37301686.6718 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 51847328.792 | 73225630.9892 | 237137.3706 | 5.892 | 8799.5909 | 12427.9421 | 179.3916 | 253.3604
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.0003 | 22.4251 | 1.5366 | 4 | 8577.3222 | 12055.5268 | 174.8603 | 245.7682 | 111.1994 | 0 | 153.2519 | 3384569.9805 | 224780.5459 | 4134746.3999 | 4222160.9168 | 0 | 358751.015 | 0 | 4806753.4547 | 12506186.4883 | 8535729.2547 | 38173678.0558 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 52719320.1761 | 74097622.3732 | 316227.766 | 6.1464 | 8577.3222 | 12055.5268 | 174.8603 | 245.7682
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7265 | 22.9444 | 1.5869 | 4 | 8410.584 | 11778.4554 | 171.4611 | 240.1197 | 111.1542 | 0 | 149.672 | 3438920.7913 | 228289.9308 | 4211305.821 | 4320980.2638 | 0 | 341414.8455 | 0 | 4890955.5444 | 12725263.0536 | 8685253.5121 | 38842383.7626 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53388025.8828 | 74766328.0799 | 421696.5034 | 6.3477 | 8410.584 | 11778.4554 | 171.4611 | 240.1197
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1749 | 23.4094 | 1.6304 | 4 | 8279.0425 | 11557.2043 | 168.7795 | 235.6092 | 111.1117 | 0 | 145.5561 | 3487206.6029 | 231402.1883 | 4279570.5079 | 4409597.0301 | 0 | 327878.3587 | 0 | 4966905.3283 | 12922868.8119 | 8820123.5025 | 39445552.3307 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 53991194.4509 | 75369496.6481 | 562341.3252 | 6.5214 | 8279.0425 | 11557.2043 | 168.7795 | 235.6092
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7601 | 23.7096 | 1.6604 | 4 | 8186.5153 | 11405.4566 | 166.8932 | 232.5157 | 111.083 | 0 | 175.1742 | 3518198.2666 | 233396.77 | 4323514.7702 | 4466898.5488 | 0 | 315945.5918 | 0 | 5014602.0394 | 13046965.8702 | 8904822.2948 | 39824344.1516 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54369986.2719 | 75748288.469 | 749894.2093 | 6.6414 | 8186.5153 | 11405.4566 | 166.8932 | 232.5157
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9392 | 23.9326 | 1.6831 | 4 | 8117.0987 | 11292.5119 | 165.478 | 230.2131 | 111.0612 | 0 | 159.3394 | 3541116.3843 | 234870.27 | 4356075.7303 | 4509484.9658 | 0 | 306148.5785 | 0 | 5049601.4122 | 13138027.059 | 8966973.4272 | 40102297.8273 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54647939.9476 | 76026242.1447 | 1000000 | 6.7324 | 8117.0987 | 11292.5119 | 165.478 | 230.2131
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8406 | 24.1028 | 1.7005 | 4 | 8065.021 | 11207.9039 | 164.4164 | 228.4883 | 111.0442 | 0 | 173.1079 | 3558561.0841 | 235991.0113 | 4380897.2422 | 4542022.2778 | 0 | 298475.2688 | 0 | 5076219.2848 | 13207281.3034 | 9014240.8721 | 40313688.3445 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54859330.4647 | 76237632.6619 | 1333521.4322 | 6.8021 | 8065.021 | 11207.9039 | 164.4164 | 228.4883
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.525 | 24.2319 | 1.7138 | 4 | 8025.9528 | 11144.5297 | 163.6199 | 227.1963 | 111.0311 | 0 | 173.3143 | 3571761.129 | 236838.5592 | 4399700.513 | 4566712.8329 | 0 | 292513.0458 | 0 | 5096335.1712 | 13259618.7133 | 9049962.2297 | 40473442.194 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55019084.3143 | 76397386.5114 | 1778279.41 | 6.8551 | 8025.9528 | 11144.5297 | 163.6199 | 227.1963
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0346 | 24.3279 | 1.7238 | 4 | 7996.646 | 11097.1815 | 163.0224 | 226.2311 | 111.0213 | 0 | 165.197 | 3581563.8531 | 237467.6927 | 4413676.3526 | 4585088.1612 | 0 | 287851.8453 | 0 | 5111202.6829 | 13298300.929 | 9076363.6368 | 40591515.1536 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55137157.2738 | 76515459.471 | 2371373.7057 | 6.895 | 7996.646 | 11097.1815 | 163.0224 | 226.2311
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.4265 | 24.4018 | 1.7314 | 4 | 7974.6628 | 11061.5829 | 162.5743 | 225.5053 | 111.0137 | 0 | 164.9083 | 3589089.6066 | 237950.5318 | 4424412.7828 | 4599217.9817 | 0 | 284340.8379 | 0 | 5122654.5789 | 13328096.4134 | 9096699.6671 | 40682462.4001 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55228104.5204 | 76606406.7175 | 3162277.6602 | 6.9254 | 7974.6628 | 11061.5829 | 162.5743 | 225.5053
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6971 | 24.4527 | 1.7369 | 4 | 7958.1739 | 11035.2929 | 162.2381 | 224.9694 | 111.0084 | 0 | 159.6315 | 3594278.2295 | 238283.3367 | 4431818.6744 | 4608971.6836 | 0 | 281469.3502 | 0 | 5130380.297 | 13348197.1471 | 9110418.8309 | 40743817.5495 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55289459.6697 | 76667761.8668 | 4216965.0343 | 6.9475 | 7958.1739 | 11035.2929 | 162.2381 | 224.9694
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.9212 | 24.4949 | 1.7412 | 4 | 7945.8068 | 11015.2622 | 161.986 | 224.561 | 111.004 | 0 | 160.1645 | 3598571.356 | 238558.658 | 4437948.4306 | 4617048.8417 | 0 | 279453.1963 | 0 | 5136916.3883 | 13365202.7158 | 9122025.481 | 40795725.0677 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55341367.188 | 76719669.3851 | 5623413.2519 | 6.9649 | 7945.8068 | 11015.2622 | 161.986 | 224.561
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0844 | 24.5256 | 1.7444 | 4 | 7936.5314 | 11000.3298 | 161.7969 | 224.2566 | 111.0008 | 0 | 169.9274 | 3601694.4051 | 238758.9111 | 4442408.8142 | 4622928.744 | 0 | 277884.8645 | 0 | 5141633.5382 | 13377475.7722 | 9130402.0942 | 40833187.1434 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55378829.2637 | 76757131.4608 | 7498942.0933 | 6.9777 | 7936.5314 | 11000.3298 | 161.7969 | 224.2566
1 | 4000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.1964 | 24.5467 | 1.7467 | 4 | 7929.5756 | 10989.3014 | 161.6551 | 224.0318 | 110.9986 | 0 | 169.4356 | 3603837.057 | 238896.2573 | 4445470.3264 | 4626961.8815 | 0 | 276617.0231 | 0 | 5144795.1927 | 13385701.7487 | 9136016.4921 | 40858295.9787 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 55403938.099 | 76782240.2961 | 10000000 | 6.987 | 7929.5756 | 10989.3014 | 161.6551 | 224.0318
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5408 | [19 empty] | 100 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8847 | [19 empty] | 133.3521 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1139 | [19 empty] | 177.8279 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4878 | [19 empty] | 237.1374 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3986 | [19 empty] | 316.2278 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.187 | [19 empty] | 421.6965 | 0
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.22054 | 0.0023705 | 4 | 1700791.6181 | 4020430.1221 | 34672.9376 | 81961.9061 | 91.3614 | 0 | 29.9876 | 115890.1745 | 6881.6333 | 103993.0783 | 73973.316 | 0 | 67621.6855 | 0 | 143660.3562 | 373774.778 | 255108.9663 | 1140903.9881 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16127074.2531 | 38122115.853 | 562.3413 | 0.0094821 | 1700791.6181 | 4020430.1221 | 34672.9376 | 81961.9061
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.34033 | 0.0066664 | 4 | 619990.5519 | 1444839.221 | 12639.346 | 29455.0018 | 96.9877 | 0 | 331.5805 | 163465.0543 | 10053.086 | 146513.8922 | 96691.3582 | 0 | 82498.7008 | 0 | 194696.6157 | 506560.6563 | 345738.0567 | 1546217.4204 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16532387.6854 | 38527429.2853 | 749.8942 | 0.026666 | 619990.5519 | 1444839.221 | 12639.346 | 29455.0018
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0862 | 0.51446 | 0.013166 | 4 | 324155.722 | 741800.6533 | 6608.3528 | 15122.6097 | 101.4846 | 0 | 61.6912 | 224836.0763 | 14215.6749 | 203234.5852 | 128983.5206 | 0 | 102008.3406 | 0 | 262578.497 | 683175.387 | 466281.2395 | 2085313.321 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17071483.586 | 39066525.1859 | 1000 | 0.052664 | 324155.722 | 741800.6533 | 6608.3528 | 15122.6097
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1749 | 0.73577 | 0.022436 | 4 | 197209.9827 | 442299.432 | 4020.3922 | 9016.8722 | 104.6554 | 0 | 95.3478 | 294613.9584 | 18994.3654 | 269964.4556 | 169745.6525 | 0 | 122305.1972 | 0 | 341493.2154 | 888495.2965 | 606416.2966 | 2712028.4376 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17698198.7026 | 39693240.3025 | 1333.5214 | 0.089743 | 197209.9827 | 442299.432 | 4020.3922 | 9016.8722
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5586 | 1.0193 | 0.035188 | 4 | 131024.5004 | 287291.9886 | 2671.1117 | 5856.8358 | 106.9829 | 0 | 73.5699 | 375395.0122 | 24549.3074 | 349809.5206 | 221685.4714 | 0 | 144341.8986 | 0 | 435154.672 | 1132183.194 | 772738.2939 | 3455857.3701 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 18442027.6352 | 40437069.235 | 1778.2794 | 0.14075 | 131024.5004 | 287291.9886 | 2671.1117 | 5856.8358
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2519 | 1.3671 | 0.052177 | 4 | 92433.0958 | 197819.5933 | 1884.3737 | 4032.82 | 108.6289 | 0 | 55.8822 | 465603.1698 | 30754.3268 | 441868.219 | 285354.1683 | 0 | 166486.5574 | 0 | 542125.9121 | 1410500.4181 | 962695.5182 | 4305388.2898 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 19291558.5549 | 41286600.1548 | 2371.3737 | 0.20871 | 92433.0958 | 197819.5933 | 1884.3737 | 4032.82
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6413 | 1.8622 | 0.075666 | 4 | 67530.3497 | 140202.2674 | 1376.6975 | 2858.2129 | 110.0893 | 0 | 78.0608 | 583217.3318 | 38857.6186 | 565229.912 | 375725.2069 | 0 | 197469.3452 | 0 | 686594.7716 | 1786378.7557 | 1219240.2072 | 5452713.1489 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 20438883.4139 | 42433925.0138 | 3162.2777 | 0.30266 | 67530.3497 | 140202.2674 | 1376.6975 | 2858.2129
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.477 | 2.4495 | 0.10618 | 4 | 51122.2246 | 102910.5114 | 1042.1957 | 2097.97 | 111.078 | 0 | 96.7456 | 710981.7693 | 47640.3277 | 703329.5555 | 483092.3395 | 0 | 226553.3008 | 0 | 846922.9442 | 2203519.773 | 1503947.5229 | 6725987.5328 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 21712157.7978 | 43707199.3977 | 4216.965 | 0.42471 | 51122.2246 | 102910.5114 | 1042.1957 | 2097.97
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1038 | 3.2014 | 0.14624 | 4 | 39757.2096 | 77357.0528 | 810.5045 | 1577.0282 | 111.8445 | 0 | 116.9896 | 861765.0803 | 57979.8547 | 870825.3243 | 620221.1968 | 0 | 259600.4559 | 0 | 1041452.8457 | 2709646.6731 | 1849389.5321 | 8270880.9629 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 23257051.2279 | 45252092.8278 | 5623.4133 | 0.58498 | 39757.2096 | 77357.0528 | 810.5045 | 1577.0282
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6035 | 4.1345 | 0.19813 | 4 | 31640.3174 | 59393.5779 | 645.0307 | 1210.8184 | 112.4265 | 0 | 70.2228 | 1034883.007 | 69821.8845 | 1068122.7808 | 790162.0802 | 0 | 294556.0776 | 0 | 1270442.8738 | 3305431.7539 | 2256025.0919 | 10089445.5498 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 25075615.8148 | 47070657.4147 | 7498.9421 | 0.79252 | 31640.3174 | 59393.5779 | 645.0307 | 1210.8184
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1723 | 5.2897 | 0.26472 | 4 | 25705.9735 | 46477.5694 | 524.051 | 947.5081 | 112.8741 | 0 | 116.3779 | 1233875.8748 | 83399.333 | 1300457.4831 | 1000447.3649 | 0 | 331733.3717 | 0 | 1540466.2368 | 4007977.155 | 2735526.764 | 12233883.5832 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 27220053.8483 | 49215095.4481 | 10000 | 1.0589 | 25705.9735 | 46477.5694 | 524.051 | 947.5081
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.9392 | 6.6942 | 0.3489 | 4 | 21288.2623 | 37048.4349 | 433.99 | 755.2825 | 113.2181 | 0 | 109.1377 | 1459288.3189 | 98742.5746 | 1569655.7462 | 1256272.7443 | 0 | 369905.1106 | 0 | 1854007.1529 | 4823746.3027 | 3292305.9697 | 14723923.9198 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 29710094.1849 | 51705135.7847 | 13335.2143 | 1.3956 | 21288.2623 | 37048.4349 | 433.99 | 755.2825
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.9829 | 8.3643 | 0.45307 | 4 | 17958.0647 | 30094.6547 | 366.0994 | 613.5202 | 113.4818 | 0 | 127.4526 | 1709953.2201 | 115762.3053 | 1875455.2983 | 1560554.9818 | 0 | 407516.6632 | 0 | 2211004.5628 | 5752580.3329 | 3926254.2809 | 17559081.6452 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 32545251.9102 | 54540293.5101 | 17782.7941 | 1.8123 | 17958.0647 | 30094.6547 | 366.0994 | 613.5202
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.1741 | 10.2723 | 0.57771 | 4 | 15428.3606 | 24946.4857 | 314.528 | 508.5679 | 113.6767 | 0 | 114.7768 | 1978936.5969 | 133976.7627 | 2210217.8692 | 1908209.8753 | 0 | 441212.3057 | 0 | 2602295.8298 | 6770639.9449 | 4621100.8852 | 20666590.0697 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 35652760.3347 | 57647801.9346 | 23713.7371 | 2.3109 | 15428.3606 | 24946.4857 | 314.528 | 508.5679
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1398 | 12.3379 | 0.72002 | 4 | 13502.4756 | 21139.4524 | 275.2662 | 430.9563 | 113.8048 | 0 | 129.8562 | 2253944.8699 | 152540.9436 | 2558914.2491 | 2284868.0228 | 0 | 466868.5791 | 0 | 3009683.2992 | 7830578.5735 | 5344530.7787 | 23901929.316 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 38888099.581 | 60883141.1809 | 31622.7766 | 2.8801 | 13502.4756 | 21139.4524 | 275.2662 | 430.9563
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.323 | 14.4413 | 0.87348 | 4 | 12039.5347 | 18334.7807 | 245.4422 | 373.7793 | 113.8662 | 0 | 130.4615 | 2520018.2701 | 170433.0095 | 2902198.562 | 2669038.4418 | 0 | 481191.5562 | 0 | 3409723.1374 | 8871400.1732 | 6054912.9072 | 27078916.0573 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 42065086.3224 | 64060127.9222 | 42169.6503 | 3.4939 | 12039.5347 | 18334.7807 | 245.4422 | 373.7793
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1151 | 16.4527 | 1.0291 | 4 | 10932.5833 | 16275.7101 | 222.8755 | 331.8024 | 113.8685 | 0 | 149.4766 | 2763429.4762 | 186727.4162 | 3221309.9548 | 3037391.3522 | 0 | 482932.1883 | 0 | 3779798.2512 | 9834259.7064 | 6712084.3235 | 30017932.6688 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 45004102.9338 | 66999144.5337 | 56234.1325 | 4.1165 | 10932.5833 | 16275.7101 | 222.8755 | 331.8024
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.0675 | 18.2792 | 1.1783 | 4 | 10097.9415 | 14764.4552 | 205.8602 | 300.9934 | 113.8274 | 0 | 174.4854 | 2976327.3375 | 200910.0162 | 3504452.6391 | 3372957.8349 | 0 | 473790.1525 | 0 | 4106090.8123 | 10683206.0185 | 7291507.6256 | 32609242.4367 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 47595412.7017 | 69590454.3016 | 74989.4209 | 4.7134 | 10097.9415 | 14764.4552 | 205.8602 | 300.9934
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.8897 | 19.8634 | 1.3143 | 4 | 9470.1546 | 13654.051 | 193.0619 | 278.3563 | 113.7611 | 0 | 169.3427 | 3155375.8653 | 212780.1415 | 3745571.4367 | 3665044.7277 | 0 | 456700.2064 | 0 | 4381834.2272 | 11400633.8215 | 7781166.8428 | 34799107.269 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 49785277.5341 | 71780319.1339 | 100000 | 5.2571 | 9470.1546 | 13654.051 | 193.0619 | 278.3563
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4797 | 21.1886 | 1.4329 | 4 | 8998.6236 | 12836.1796 | 183.4491 | 261.6829 | 113.6853 | 0 | 168.2903 | 3301467.3737 | 222421.9391 | 3944397.1474 | 3910216.5829 | 0 | 435076.4709 | 0 | 4607296.0105 | 11987239.1328 | 8181537.0213 | 36589651.6786 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 51575821.9436 | 73570863.5435 | 133352.1432 | 5.7315 | 8998.6236 | 12836.1796 | 183.4491 | 261.6829
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8628 | 22.2642 | 1.5327 | 4 | 8644.6967 | 12232.2482 | 176.2338 | 249.3709 | 113.6106 | 0 | 178.7129 | 3417720.166 | 230064.0915 | 4103995.539 | 4109821.3034 | 0 | 411819.3057 | 0 | 4786633.9582 | 12453839.6856 | 8500001.4862 | 38013895.5357 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 53000065.8007 | 74995107.4006 | 177827.941 | 6.1309 | 8644.6967 | 12232.2482 | 176.2338 | 249.3709
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.165 | 23.119 | 1.6145 | 4 | 8379.1048 | 11784.9494 | 170.8194 | 240.2521 | 113.5433 | 0 | 185.921 | 3508703.616 | 236025.0742 | 4229781.0034 | 4268891.5905 | 0 | 389186.2996 | 0 | 4926709.1576 | 12818286.6212 | 8748744.0084 | 39126327.3709 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 54112497.6359 | 76107539.2358 | 237137.3706 | 6.458 | 8379.1048 | 11784.9494 | 170.8194 | 240.2521
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.5218 | 23.783 | 1.6798 | 4 | 8179.8048 | 11453.2125 | 166.7564 | 233.4892 | 113.4861 | 0 | 156.6044 | 3578538.1804 | 240587.882 | 4326863.7466 | 4392720.7804 | 0 | 368361.3568 | 0 | 5033758.059 | 13096805.9038 | 8938839.1418 | 39976475.0507 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 54962645.3158 | 76957686.9156 | 316227.766 | 6.7193 | 8179.8048 | 11453.2125 | 166.7564 | 233.4892
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1406 | 24.2991 | 1.7314 | 4 | 8030.243 | 11206.066 | 163.7074 | 228.4508 | 113.4389 | 0 | 170.5616 | 3632326.108 | 244094.5171 | 4401962.1894 | 4489140.7459 | 0 | 350388.7553 | 0 | 5115985.8032 | 13310745.6269 | 9084857.3988 | 40629501.1448 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 55615671.4098 | 77610713.0097 | 421696.5034 | 6.9258 | 8030.243 | 11206.066 | 163.7074 | 228.4508
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.0948 | 24.093 | 1.7437 | 4 | 7914.7025 | 11068.2036 | 161.3519 | 225.6403 | 113.4576 | 0 | 169.9306 | 3610890.3324 | 242697.2253 | 4372014.8994 | 4450638.3841 | 0 | 308585.9115 | 0 | 5064082.4335 | 13175703.7059 | 8992688.5129 | 40217301.4049 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 55203471.6699 | 77198513.2698 | 562341.3252 | 6.9748 | 7914.7025 | 11068.2036 | 161.3519 | 225.6403
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.0233 | 25.0611 | 1.8068 | 4 | 7828.4885 | 10871.9045 | 159.5943 | 221.6385 | 113.3648 | 0 | 186.4934 | 3710982.171 | 249209.992 | 4512294.5032 | 4631795.6041 | 0 | 324072.8916 | 0 | 5237058.5132 | 13625751.9828 | 9299855.7095 | 41591021.3675 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56577191.6325 | 78572233.2324 | 749894.2093 | 7.2271 | 7828.4885 | 10871.9045 | 159.5943 | 221.6385
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.1512 | 25.2817 | 1.83 | 4 | 7766.203 | 10771.0477 | 158.3246 | 219.5824 | 113.3423 | 0 | 160.0734 | 3733588.1431 | 250677.2831 | 4544121.4364 | 4673169.6711 | 0 | 314077.7186 | 0 | 5271097.3584 | 13714314.0757 | 9360301.1577 | 41861346.844 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56847517.109 | 78842558.7089 | 1000000 | 7.3199 | 7766.203 | 10771.0477 | 158.3246 | 219.5824
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0138 | 25.4502 | 1.8477 | 4 | 7719.4681 | 10695.4621 | 157.3718 | 218.0415 | 113.3248 | 0 | 155.4054 | 3750801.5682 | 251793.6907 | 4568391.1796 | 4704786.4144 | 0 | 306273.7445 | 0 | 5296998.173 | 13781702.6824 | 9406295.2664 | 42067042.7192 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57053212.9842 | 79048254.5841 | 1333521.4322 | 7.3908 | 7719.4681 | 10695.4621 | 157.3718 | 218.0415
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.6593 | 25.5762 | 1.8611 | 4 | 7684.404 | 10638.9698 | 156.657 | 216.8898 | 113.3116 | 0 | 139.6392 | 3763642.0081 | 252625.9838 | 4586515.196 | 4728434.7764 | 0 | 300147.2934 | 0 | 5316232.4505 | 13831746.3271 | 9440451.0822 | 42219795.1175 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57205965.3826 | 79201006.9824 | 1778279.41 | 7.4444 | 7684.404 | 10638.9698 | 156.657 | 216.8898
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1586 | 25.6736 | 1.8714 | 4 | 7658.0985 | 10596.4708 | 156.1207 | 216.0234 | 113.3013 | 0 | 152.2789 | 3773551.2112 | 253267.9922 | 4600513.3819 | 4746721.7522 | 0 | 295523.8921 | 0 | 5331135.5096 | 13870521.0296 | 9466915.6134 | 42338150.3822 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57324320.6472 | 79319362.2471 | 2371373.7057 | 7.4855 | 7658.0985 | 10596.4708 | 156.1207 | 216.0234
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.507 | 25.7415 | 1.8788 | 4 | 7638.3653 | 10565.0409 | 155.7184 | 215.3826 | 113.294 | 0 | 152.2362 | 3780452.0329 | 253714.9315 | 4610267.9984 | 4759476.5791 | 0 | 291754.1831 | 0 | 5341309.6327 | 13896992.0111 | 9484982.6022 | 42418949.9711 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57405120.2362 | 79400161.836 | 3162277.6602 | 7.5154 | 7638.3653 | 10565.0409 | 155.7184 | 215.3826
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.7971 | 25.798 | 1.8847 | 4 | 7623.5634 | 10541.0735 | 155.4167 | 214.894 | 113.288 | 0 | 151.5599 | 3786189.7768 | 254086.4569 | 4618382.1059 | 4770093.2743 | 0 | 289111.1685 | 0 | 5349966.4851 | 13919515.3653 | 9500355.2542 | 42487699.887 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57473870.152 | 79468911.7519 | 4216965.0343 | 7.539 | 7623.5634 | 10541.0735 | 155.4167 | 214.894
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0017 | 25.8378 | 1.8891 | 4 | 7612.4611 | 10523.3065 | 155.1903 | 214.5318 | 113.2837 | 0 | 151.5173 | 3790234.1502 | 254348.2791 | 4624103.6623 | 4777583.4775 | 0 | 286994.646 | 0 | 5355973.0439 | 13935143.1992 | 9511021.572 | 42535402.0303 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57521572.2953 | 79516613.8952 | 5623413.2519 | 7.5562 | 7612.4611 | 10523.3065 | 155.1903 | 214.5318
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1527 | 25.8672 | 1.8923 | 4 | 7604.1342 | 10510.0288 | 155.0206 | 214.2612 | 113.2805 | 0 | 156.1875 | 3793214.8162 | 254541.2114 | 4628321.5091 | 4783107.2276 | 0 | 285369.9391 | 0 | 5360376.3343 | 13946599.6575 | 9518840.8402 | 42570371.5353 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57556541.8004 | 79551583.4002 | 7498942.0933 | 7.5691 | 7604.1342 | 10510.0288 | 155.0206 | 214.2612
1 | 4100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.2575 | 25.8876 | 1.8946 | 4 | 7597.889 | 10500.1994 | 154.8932 | 214.0608 | 113.2783 | 0 | 162.17 | 3795283.4131 | 254675.0909 | 4631249.3255 | 4786942.6247 | 0 | 284073.4284 | 0 | 5363367.3142 | 13954381.5736 | 9524152.1578 | 42594124.9281 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 57580295.1931 | 79575336.793 | 10000000 | 7.5785 | 7597.889 | 10500.1994 | 154.8932 | 214.0608
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5512 | [19 empty] | 100 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1555 | [19 empty] | 133.3521 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0205 | [19 empty] | 177.8279 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3133 | [19 empty] | 237.1374 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5188 | [19 empty] | 316.2278 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8421 | [19 empty] | 421.6965 | 0
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.22655 | 0.0033811 | 4 | 1226645.3811 | 2899174.853 | 25006.8253 | 59103.6008 | 92.7123 | 0 | 29.4516 | 119369.5275 | 7143.8539 | 106143.3914 | 74630.7363 | 0 | 66302.981 | 0 | 145700.2912 | 379082.2704 | 258731.4389 | 1157104.4906 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16589662.9913 | 39209648.1211 | 562.3413 | 0.013524 | 1226645.3811 | 2899174.853 | 25006.8253 | 59103.6008
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4293 | 0.39434 | 0.0085485 | 4 | 501808.2849 | 1163328.2856 | 10230.0406 | 23716.0206 | 99.9926 | 0 | 369.8078 | 185030.215 | 11582.8708 | 164471.3723 | 105713.5806 | 0 | 90551.0284 | 0 | 217366.1362 | 565542.0985 | 385994.1029 | 1726251.4048 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17158809.9055 | 39778795.0353 | 749.8942 | 0.034194 | 501808.2849 | 1163328.2856 | 10230.0406 | 23716.0206
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.364 | 0.58912 | 0.016201 | 4 | 273822.1284 | 622869.1479 | 5582.2345 | 12698.0301 | 104.2865 | 0 | 80.9337 | 251817.9024 | 16184.4932 | 226043.1174 | 141130.7758 | 0 | 111446.1578 | 0 | 291182.7542 | 757597.7966 | 517076.0633 | 2312479.0607 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17745037.5613 | 40365022.6911 | 1000 | 0.064805 | 273822.1284 | 622869.1479 | 5582.2345 | 12698.0301
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5381 | 0.83725 | 0.027008 | 4 | 170592.8769 | 379972.3884 | 3477.7665 | 7746.2511 | 107.3408 | 0 | 80.6209 | 328084.7731 | 21484.1174 | 298778.2273 | 185907.917 | 0 | 133432.5215 | 0 | 377398.1469 | 981912.5632 | 670175.5007 | 2997173.7669 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 18429732.2676 | 41049717.3974 | 1333.5214 | 0.10803 | 170592.8769 | 379972.3884 | 3477.7665 | 7746.2511
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0191 | 1.1525 | 0.041788 | 4 | 115083.6477 | 250409.2621 | 2346.1358 | 5104.9315 | 109.5682 | 0 | 80.3658 | 415791.2273 | 27598.9182 | 385201.4973 | 242605.1261 | 0 | 156967.3418 | 0 | 478984.0032 | 1246218.1231 | 850569.4762 | 3803935.7132 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 19236494.2139 | 41856479.3437 | 1778.2794 | 0.16715 | 115083.6477 | 250409.2621 | 2346.1358 | 5104.9315
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7829 | 1.5282 | 0.061256 | 4 | 82162.6248 | 174479.563 | 1674.9962 | 3557.0019 | 111.0898 | 0 | 76.6278 | 511194.8881 | 34246.5783 | 482223.9416 | 310430.0158 | 0 | 179172.3133 | 0 | 591734.4175 | 1539571.5729 | 1050789.2335 | 4699362.961 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 20131921.4617 | 42751906.5915 | 2371.3737 | 0.24503 | 82162.6248 | 174479.563 | 1674.9962 | 3557.0019
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3575 | 2.083 | 0.088499 | 4 | 60425.197 | 124324.2912 | 1231.8494 | 2534.5188 | 112.5625 | 0 | 90.4269 | 640504.2413 | 43277.4616 | 617146.4571 | 409579.4809 | 0 | 213029.7245 | 0 | 750179.5725 | 1951813.3647 | 1332152.7272 | 5957683.0299 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 21390241.5306 | 44010226.6604 | 3162.2777 | 0.354 | 60425.197 | 124324.2912 | 1231.8494 | 2534.5188
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4346 | 2.7443 | 0.12367 | 4 | 46078.6749 | 91804.305 | 939.3761 | 1871.5549 | 113.5367 | 0 | 78.1097 | 781536.1287 | 53094.6092 | 768939.9568 | 527979.3321 | 0 | 245418.4372 | 0 | 927017.701 | 2411909.9005 | 1646178.0669 | 7362074.1324 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 22794632.633 | 45414617.7628 | 4216.965 | 0.49469 | 46078.6749 | 91804.305 | 939.3761 | 1871.5549
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.2829 | 3.5724 | 0.16964 | 4 | 36045.7905 | 69380.6997 | 734.8422 | 1414.4194 | 114.2759 | 0 | 99.4656 | 944524.0461 | 64416.7868 | 949042.6818 | 676324.3769 | 0 | 280191.104 | 0 | 1136654.6083 | 2957342.1309 | 2018446.7716 | 9026942.5064 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 24459501.0071 | 47079486.1369 | 5623.4133 | 0.67857 | 36045.7905 | 69380.6997 | 734.8422 | 1414.4194
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.0897 | 4.6073 | 0.22919 | 4 | 28836.5649 | 53510.0991 | 587.8724 | 1090.8757 | 114.8434 | 0 | 92.1281 | 1133157.0727 | 77488.0999 | 1162784.6791 | 861644.2756 | 0 | 317742.2265 | 0 | 1385598.378 | 3605042.7543 | 2460515.7561 | 11003973.2424 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 26436531.7431 | 49056516.8728 | 7498.9421 | 0.91677 | 28836.5649 | 53510.0991 | 587.8724 | 1090.8757
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0017 | 5.8805 | 0.3053 | 4 | 23544.4348 | 42067.1755 | 479.9851 | 857.5963 | 115.2785 | 0 | 101.7147 | 1348737.7391 | 92385.4363 | 1412995.184 | 1089344.0213 | 0 | 357097.1059 | 0 | 1677218.1998 | 4363777.7111 | 2978367.9545 | 13319923.3519 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 28752481.8526 | 51372466.9824 | 10000 | 1.2212 | 23544.4348 | 42067.1755 | 479.9851 | 857.5963
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.1512 | 7.4206 | 0.40102 | 4 | 19592.2587 | 33693.6722 | 399.4147 | 686.8911 | 115.6129 | 0 | 106.5037 | 1591878.3656 | 109141.9995 | 1701612.8331 | 1364600.5316 | 0 | 397101.4504 | 0 | 2014090.7203 | 5240250.9073 | 3576578.9206 | 15995255.7284 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 31427814.2291 | 54047799.3589 | 13335.2143 | 1.6041 | 19592.2587 | 33693.6722 | 399.4147 | 686.8911
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5971 | 9.2404 | 0.51877 | 4 | 16604.4781 | 27505.3506 | 338.5047 | 560.7338 | 115.8684 | 0 | 122.4605 | 1860796.0118 | 127626.0345 | 2027606.1114 | 1689804.7155 | 0 | 435982.9448 | 0 | 2395308.169 | 6232100.5106 | 4253536.6553 | 19022761.1529 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 34455319.6536 | 57075304.7834 | 17782.7941 | 2.0751 | 16604.4781 | 27505.3506 | 338.5047 | 560.7338
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.1561 | 11.2991 | 0.65842 | 4 | 14330.7528 | 22919.4717 | 292.1518 | 467.2444 | 116.0532 | 0 | 120.461 | 2146884.2722 | 147235.1385 | 2381273.5602 | 2057918.2602 | 0 | 469889.19 | 0 | 2809248.1642 | 7309087.4673 | 4988602.3832 | 22310138.4359 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 37742696.9366 | 60362682.0664 | 23713.7371 | 2.6337 | 14330.7528 | 22919.4717 | 292.1518 | 467.2444
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.3756 | 13.4955 | 0.81588 | 4 | 12598.9423 | 19530.1081 | 256.8465 | 398.1477 | 116.1668 | 0 | 121.8682 | 2435517.87 | 166952.4092 | 2744677.9507 | 2451292.8173 | 0 | 494169.4143 | 0 | 3234118.08 | 8414511.8353 | 5743077.2286 | 25684317.6055 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 41116876.1062 | 63736861.236 | 31622.7766 | 3.2635 | 12598.9423 | 19530.1081 | 256.8465 | 398.1477
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.6501 | 15.6943 | 0.98312 | 4 | 11284.0782 | 17036.1451 | 230.0412 | 347.3049 | 116.2106 | 0 | 150.9715 | 2710447.866 | 185653.1151 | 3096844.0745 | 2845858.0939 | 0 | 505618.5227 | 0 | 3644324.4522 | 9481784.6708 | 6471512.869 | 28942043.6643 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 44374602.1649 | 66994587.2947 | 42169.6503 | 3.9325 | 11284.0782 | 17036.1451 | 230.0412 | 347.3049
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.4332 | 17.7748 | 1.1506 | 4 | 10289.6458 | 15204.3187 | 209.7683 | 309.9606 | 116.1956 | 0 | 149.2111 | 2959662.4488 | 202520.6994 | 3421165.2899 | 3220269.3205 | 0 | 504211.7814 | 0 | 4020053.5206 | 10459354.6343 | 7138724.4561 | 31925962.1511 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 47358520.6518 | 69978505.7816 | 56234.1325 | 4.6025 | 10289.6458 | 15204.3187 | 209.7683 | 309.9606
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.2929 | 19.6449 | 1.3093 | 4 | 9539.9791 | 13858.9555 | 194.4854 | 282.5336 | 116.1395 | 0 | 162.3139 | 3175725.6588 | 217067.6978 | 3706357.8532 | 3557967.7227 | 0 | 491996.4442 | 0 | 4348154.9969 | 11313007.3727 | 7721359.9909 | 34531637.7372 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 49964196.2379 | 72584181.3677 | 74989.4209 | 5.2373 | 9539.9791 | 13858.9555 | 194.4854 | 282.5336
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.9714 | 21.2531 | 1.4524 | 4 | 8976.0462 | 12869.5255 | 182.9888 | 262.3627 | 116.0614 | 0 | 142.3552 | 3356100.1684 | 229149.387 | 3947389.16 | 3849419.2608 | 0 | 472207.0372 | 0 | 4623163.3552 | 12028522.7091 | 8209713.9104 | 36715664.9881 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 52148223.4888 | 74768208.6186 | 100000 | 5.8097 | 8976.0462 | 12869.5255 | 182.9888 | 262.3627
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4 | 22.5897 | 1.5763 | 4 | 8552.3252 | 12139.8875 | 174.3507 | 247.488 | 115.9768 | 0 | 178.9258 | 3502484.4926 | 238908.8118 | 4145019.3857 | 4092575.1478 | 0 | 448414.9419 | 0 | 4846687.0842 | 12610085.6008 | 8606642.5339 | 38490817.9987 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 53923376.4994 | 76543361.6292 | 133352.1432 | 6.3051 | 8552.3252 | 12139.8875 | 174.3507 | 247.488
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.6233 | 23.6688 | 1.6799 | 4 | 8234.1096 | 11600.426 | 167.8635 | 236.4904 | 115.896 | 0 | 163.5928 | 3618487.641 | 246613.0606 | 4302918.5991 | 4289769.5965 | 0 | 423492.3295 | 0 | 5023699.6784 | 13070636.0607 | 8920977.6862 | 39896594.652 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 55329153.1527 | 77949138.2825 | 177827.941 | 6.7195 | 8234.1096 | 11600.426 | 167.8635 | 236.4904
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7714 | 24.521 | 1.7642 | 4 | 7995.2246 | 11200.6745 | 162.9935 | 228.3409 | 115.8245 | 0 | 155.8683 | 3708768.9435 | 252588.6155 | 4426638.1545 | 4445968.9271 | 0 | 399552.5908 | 0 | 5161071.7202 | 13428049.9346 | 9164919.9992 | 40987558.8854 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 56420117.3861 | 79040102.5159 | 237137.3706 | 7.0567 | 7995.2246 | 11200.6745 | 162.9935 | 228.3409
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.0091 | 25.1831 | 1.8314 | 4 | 7815.9016 | 10903.7733 | 159.3377 | 222.2882 | 115.7645 | 0 | 164.0811 | 3778131.401 | 257166.8542 | 4522197.6302 | 4567634.7099 | 0 | 377888.7228 | 0 | 5266177.534 | 13701513.702 | 9351564.6396 | 41822275.1936 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 57254833.6943 | 79874818.8241 | 316227.766 | 7.3254 | 7815.9016 | 10903.7733 | 159.3377 | 222.2882
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.5176 | 25.6942 | 1.8842 | 4 | 7681.2896 | 10682.6207 | 156.5935 | 217.7797 | 115.7155 | 0 | 174.0381 | 3831215.1621 | 260662.8646 | 4595633.511 | 4661738.2953 | 0 | 359231.0154 | 0 | 5346307.5309 | 13909995.517 | 9493857.7621 | 42458641.6585 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 57891200.1592 | 80511185.289 | 421696.5034 | 7.5367 | 7681.2896 | 10682.6207 | 156.5935 | 217.7797
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4324 | 26.0833 | 1.9251 | 4 | 7580.2422 | 10517.7999 | 154.5335 | 214.4196 | 115.6766 | 0 | 172.7862 | 3871354.3772 | 263301.7668 | 4651339.4372 | 4733474.076 | 0 | 343569.5401 | 0 | 5406585.287 | 14066825.8735 | 9600897.7031 | 42937348.0609 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58369906.5616 | 80989891.6914 | 562341.3252 | 7.7003 | 7580.2422 | 10517.7999 | 154.5335 | 214.4196
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.628 | 26.1229 | 1.9449 | 4 | 7499.6399 | 10407.173 | 152.8903 | 212.1643 | 115.6724 | 0 | 285.0659 | 3875424.2193 | 263568.8252 | 4657002.7335 | 4740790.563 | 0 | 318402.8913 | 0 | 5403523.8006 | 14058860.5141 | 9595461.1816 | 42913034.7288 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58345593.2295 | 80965578.3593 | 749894.2093 | 7.7798 | 7499.6399 | 10407.173 | 152.8903 | 212.1643
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3366 | 26.6715 | 1.985 | 4 | 7442.9275 | 10291.7304 | 151.7341 | 209.8108 | 115.6154 | 0 | 147.5358 | 3931621.6839 | 267256.5135 | 4735266.5668 | 4842122.7694 | 0 | 321889.2748 | 0 | 5498281.1553 | 14305399.7135 | 9763729.2511 | 43665566.9284 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59098125.429 | 81718110.5588 | 1000000 | 7.9402 | 7442.9275 | 10291.7304 | 151.7341 | 209.8108
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1675 | 26.8393 | 2.0032 | 4 | 7400.8507 | 10223.8925 | 150.8764 | 208.4279 | 115.5974 | 0 | 138.4965 | 3948724.7606 | 268377.0451 | 4759150.0674 | 4873169.6751 | 0 | 313999.5427 | 0 | 5523734.2255 | 14371623.3809 | 9808928.2648 | 43867706.9621 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59300265.4628 | 81920250.5926 | 1333521.4322 | 8.0126 | 7400.8507 | 10223.8925 | 150.8764 | 208.4279
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7781 | 26.9625 | 2.0167 | 4 | 7369.2785 | 10173.336 | 150.2327 | 207.3972 | 115.584 | 0 | 175.7268 | 3961254.1374 | 269197.4318 | 4776665.076 | 4895973.8949 | 0 | 307724.626 | 0 | 5542217.9148 | 14419714.149 | 9841751.2022 | 44014498.432 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59447056.9327 | 82067042.0624 | 1778279.41 | 8.0669 | 7369.2785 | 10173.336 | 150.2327 | 207.3972
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2339 | 27.0544 | 2.0269 | 4 | 7345.5909 | 10135.5263 | 149.7498 | 206.6264 | 115.5739 | 0 | 161.9862 | 3970586.5859 | 269808.2218 | 4789721.1844 | 4912992.4644 | 0 | 302853.7547 | 0 | 5555925.2624 | 14455377.8557 | 9866092.4148 | 44123357.7441 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59555916.2448 | 82175901.3746 | 2371373.7057 | 8.1077 | 7345.5909 | 10135.5263 | 149.7498 | 206.6264
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5823 | 27.1246 | 2.0347 | 4 | 7327.8206 | 10107.122 | 149.3875 | 206.0474 | 115.5661 | 0 | 167.5088 | 3977707.4436 | 270274.1139 | 4799689.0492 | 4925996.8287 | 0 | 299170.6124 | 0 | 5566406.8386 | 14482648.7671 | 9884705.3722 | 44206599.0256 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59639157.5263 | 82259142.6561 | 3162277.6602 | 8.1387 | 7327.8206 | 10107.122 | 149.3875 | 206.0474
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8575 | 27.1801 | 2.0407 | 4 | 7314.4906 | 10085.6518 | 149.1158 | 205.6097 | 115.56 | 0 | 201.9528 | 3983325.6614 | 270641.603 | 4807556.9544 | 4936268.3588 | 0 | 296477.0103 | 0 | 5574765.1393 | 14504395.3508 | 9899547.8625 | 44272977.9405 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59705536.4412 | 82325521.571 | 4216965.0343 | 8.1626 | 7314.4906 | 10085.6518 | 149.1158 | 205.6097
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0427 | 27.2174 | 2.0449 | 4 | 7304.4919 | 10069.8568 | 148.9119 | 205.2877 | 115.5558 | 0 | 184.1685 | 3987102.5479 | 270888.5953 | 4812848.148 | 4943179.6153 | 0 | 294250.1795 | 0 | 5580224.9435 | 14518600.6415 | 9909243.2652 | 44316337.9361 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59748896.4368 | 82368881.5666 | 5623413.2519 | 8.1797 | 7304.4919 | 10069.8568 | 148.9119 | 205.2877
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1935 | 27.2478 | 2.0483 | 4 | 7296.9925 | 10057.8554 | 148.7591 | 205.043 | 115.5524 | 0 | 168.9802 | 3990175.1424 | 271089.5061 | 4817153.6196 | 4948805.2838 | 0 | 292664.3818 | 0 | 5584756.2941 | 14530390.2863 | 9917289.9401 | 44352324.4542 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59784882.9549 | 82404868.0847 | 7498942.0933 | 8.1931 | 7296.9925 | 10057.8554 | 148.7591 | 205.043
1 | 4200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.301 | 27.2694 | 2.0507 | 4 | 7291.368 | 10048.9371 | 148.6444 | 204.8612 | 115.55 | 0 | 163.2072 | 3992363.0171 | 271232.5494 | 4820220.0004 | 4952813.0829 | 0 | 291418.4013 | 0 | 5587938.3499 | 14538669.3427 | 9922940.5662 | 44377595.3098 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 59810153.8105 | 82430138.9402 | 10000000 | 8.2029 | 7291.368 | 10048.9371 | 148.6444 | 204.8612
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1486 | [19 empty] | 100 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6102 | [19 empty] | 133.3521 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5313 | [19 empty] | 177.8279 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9236 | [19 empty] | 237.1374 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1428 | [19 empty] | 316.2278 | 0
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.23246 | 0.00045322 | 4 | 9432310.6058 | 22258893.9802 | 192290.4098 | 453777.6612 | 94.0392 | 0 | 26.161 | 122795.2983 | 7405.0913 | 108242.946 | 75225.7978 | 0 | 78580.4863 | 0 | 152977.3517 | 398015.6892 | 271653.8863 | 1214896.5469 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17099703.3742 | 40352836.1611 | 421.6965 | 0.0018129 | 9432310.6058 | 22258893.9802 | 192290.4098 | 453777.6612
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.28705 | 0.004689 | 4 | 920511.1632 | 2160292.1613 | 18765.8651 | 44040.4777 | 97.0806 | 0 | 269.7828 | 145399.0503 | 8934.1604 | 127847.0943 | 85260.737 | 0 | 78164.1678 | 0 | 173786.0318 | 452155.6064 | 308605.4922 | 1380152.3401 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17264959.1674 | 40518091.9543 | 562.3413 | 0.018756 | 920511.1632 | 2160292.1613 | 18765.8651 | 44040.4777
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6822 | 0.46002 | 0.01077 | 4 | 413775.4254 | 953566.4559 | 8435.3717 | 19439.742 | 103.0968 | 0 | 405.6172 | 210387.048 | 13412.9005 | 185621.4688 | 116476.0214 | 0 | 100406.5478 | 0 | 244258.5548 | 635510.6552 | 433749.0806 | 1939822.2771 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17824629.1043 | 41077761.8912 | 749.8942 | 0.043078 | 413775.4254 | 953566.4559 | 8435.3717 | 19439.742
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.67127 | 0.019703 | 4 | 233985.0928 | 529034.2405 | 4770.1026 | 10785.0786 | 107.056 | 0 | 72.0912 | 280814.6986 | 18341.4906 | 250423.8079 | 154130.05 | 0 | 121473.8369 | 0 | 321821.7148 | 837314.0872 | 571484.0696 | 2555803.7557 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 18440610.5829 | 41693743.3698 | 1000 | 0.078811 | 233985.0928 | 529034.2405 | 4770.1026 | 10785.0786
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9207 | 0.94907 | 0.032258 | 4 | 148713.4653 | 328925.5728 | 3031.7251 | 6705.5927 | 110.0036 | 0 | 91.0313 | 364148.146 | 24217.0466 | 329666.702 | 203416.9128 | 0 | 145300.2743 | 0 | 416032.1418 | 1082430.2931 | 738780.9168 | 3303992.4334 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 19188799.2606 | 42441932.0475 | 1333.5214 | 0.12903 | 148713.4653 | 328925.5728 | 3031.7251 | 6705.5927
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4749 | 1.2926 | 0.049277 | 4 | 101700.8637 | 219671.384 | 2073.3097 | 4478.2983 | 112.1041 | 0 | 65.259 | 457619.5417 | 30824.1034 | 421460.8533 | 264258.1102 | 0 | 169420.9301 | 0 | 523997.5801 | 1363334.2167 | 930503.6166 | 4161418.9521 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 20046225.7793 | 43299358.5662 | 1778.2794 | 0.19711 | 101700.8637 | 219671.384 | 2073.3097 | 4478.2983
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3183 | 1.6986 | 0.071341 | 4 | 73555.7993 | 155042.0314 | 1499.5345 | 3160.7415 | 113.5143 | 0 | 63.1037 | 558551.1836 | 37939.7662 | 523869.8284 | 336020.5906 | 0 | 191942.1993 | 0 | 642846.1915 | 1672553.9244 | 1141552.4209 | 5105276.1047 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 20990082.9319 | 44243215.7188 | 2371.3737 | 0.28536 | 73555.7993 | 155042.0314 | 1499.5345 | 3160.7415
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1345 | 2.3295 | 0.10305 | 4 | 54334.8354 | 110749.4994 | 1107.6891 | 2257.7783 | 115.0379 | 0 | 80.5608 | 703098.2404 | 48183.0775 | 673743.2454 | 446925.4697 | 0 | 230253.4034 | 0 | 819859.3402 | 2133105.8269 | 1455888.5578 | 6511057.1614 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 22395863.9886 | 45648996.7755 | 3162.2777 | 0.41218 | 54334.8354 | 110749.4994 | 1107.6891 | 2257.7783
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4092 | 3.0594 | 0.14331 | 4 | 41714.4583 | 82278.9728 | 850.4057 | 1677.3682 | 115.9816 | 0 | 81.9084 | 855779.972 | 58947.7497 | 837354.1501 | 575071.0466 | 0 | 264665.1055 | 0 | 1010809.0293 | 2629917.7489 | 1794972.903 | 8027517.7052 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 23912324.5324 | 47165457.3193 | 4216.965 | 0.57324 | 41714.4583 | 82278.9728 | 850.4057 | 1677.3682
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5204 | 3.9772 | 0.19595 | 4 | 32815.3619 | 62482.4732 | 668.9855 | 1273.7897 | 116.7024 | 0 | 94.0151 | 1033175.1041 | 71430.9944 | 1032378.305 | 736657.2161 | 0 | 302052.5385 | 0 | 1238520.7217 | 3222376.8622 | 2199338.4217 | 9835930.1637 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 25720736.9909 | 48973869.7779 | 5623.4133 | 0.7838 | 32815.3619 | 62482.4732 | 668.9855 | 1273.7897
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.6313 | 5.1187 | 0.26393 | 4 | 26387.488 | 48413.2833 | 537.9446 | 986.9703 | 117.2545 | 0 | 109.4368 | 1237626.4672 | 85780.3674 | 1262804.648 | 937496.0409 | 0 | 341995.9569 | 0 | 1507624.3573 | 3922529.3214 | 2677206.8618 | 11973064.0208 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 27857870.848 | 51111003.635 | 7498.9421 | 1.0557 | 26387.488 | 48413.2833 | 537.9446 | 986.9703
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8971 | 6.5185 | 0.35056 | 4 | 21647.0146 | 38229.6634 | 441.3037 | 779.3634 | 117.6781 | 0 | 102.4203 | 1470743.6312 | 102097.4234 | 1531780.2386 | 1183618.0914 | 0 | 383598.7981 | 0 | 1822016.8912 | 4740514.204 | 3235498.352 | 14469867.6299 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 30354674.4571 | 53607807.244 | 10000 | 1.4023 | 21647.0146 | 38229.6634 | 441.3037 | 779.3634
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.4487 | 8.2063 | 0.45914 | 4 | 18094.3264 | 30755.6203 | 368.8773 | 626.9949 | 118.0038 | 0 | 97.4038 | 1733026.9097 | 120406.1823 | 1841168.2999 | 1480317.789 | 0 | 425647.8064 | 0 | 2184221.1251 | 5682895.322 | 3878692.8291 | 17346376.2635 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 33231183.0907 | 56484315.8776 | 13335.2143 | 1.8366 | 18094.3264 | 30755.6203 | 368.8773 | 626.9949
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.287 | 10.1815 | 0.59169 | 4 | 15402.9219 | 25227.739 | 314.0094 | 514.3016 | 118.2503 | 0 | 121.2829 | 2020619.8638 | 140425.3955 | 2187519.8878 | 1827411.5841 | 0 | 465534.776 | 0 | 2590189.4878 | 6739141.7263 | 4599602.7037 | 20570445.4251 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 36455252.2523 | 59708385.0392 | 17782.7941 | 2.3668 | 15402.9219 | 25227.739 | 314.0094 | 514.3016
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.1593 | 12.3858 | 0.74719 | 4 | 13352.8682 | 21133.0528 | 272.2163 | 430.8259 | 118.4229 | 0 | 114.0644 | 2322777.572 | 161393.2658 | 2558531.0693 | 2214940.3333 | 0 | 498829.3891 | 0 | 3025023.9355 | 7870491.7625 | 5371772.3503 | 24023759.6779 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 39908566.5051 | 63161699.292 | 23713.7371 | 2.9888 | 13352.8682 | 21133.0528 | 272.2163 | 430.8259
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.5808 | 14.7063 | 0.92027 | 4 | 11791.7364 | 18108.6606 | 240.3905 | 369.1695 | 118.5203 | 0 | 120.4998 | 2623926.1827 | 182211.011 | 2935101.3169 | 2623451.911 | 0 | 521108.8967 | 0 | 3465461.7341 | 9016420.5682 | 6153892.3067 | 27521573.9273 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 43406380.7545 | 66659513.5415 | 31622.7766 | 3.6811 | 11791.7364 | 18108.6606 | 240.3905 | 369.1695
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.9487 | 17.003 | 1.1018 | 4 | 10606.893 | 15882.9329 | 216.2359 | 323.7951 | 118.5459 | 0 | 132.7544 | 2907937.099 | 201751.6068 | 3296347.5505 | 3028812.5083 | 0 | 529797.7424 | 0 | 3886212.1377 | 10111126.8107 | 6901051.8112 | 30863037.2666 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 46747844.0938 | 70000976.8807 | 42169.6503 | 4.4073 | 10606.893 | 15882.9329 | 216.2359 | 323.7951
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.7124 | 19.1507 | 1.2814 | 4 | 9711.0532 | 14247.7546 | 197.973 | 290.4597 | 118.513 | 0 | 128.3416 | 3162726.6538 | 219187.8319 | 3625531.8599 | 3409213.3254 | 0 | 525219.1465 | 0 | 4267332.7388 | 11102724.4361 | 7577837.5658 | 33889773.5582 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 49774580.3854 | 73027713.1724 | 56234.1325 | 5.1256 | 9711.0532 | 14247.7546 | 197.973 | 290.4597
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.4601 | 21.0597 | 1.4495 | 4 | 9035.7343 | 13046.2715 | 184.2057 | 265.9659 | 118.442 | 0 | 153.9978 | 3381444.4631 | 234072.1063 | 3912072.3362 | 3748673.9301 | 0 | 509813.1314 | 0 | 4596569.6272 | 11959331.2839 | 8162489.3409 | 36504466.2192 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 52389273.0464 | 75642405.8333 | 74989.4209 | 5.798 | 9035.7343 | 13046.2715 | 184.2057 | 265.9659
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9728 | 22.686 | 1.5995 | 4 | 8527.6342 | 12161.9885 | 173.8474 | 247.9386 | 118.3526 | 0 | 147.0801 | 3562543.5957 | 246330.1089 | 4152193.233 | 4039036.7038 | 0 | 487168.6924 | 0 | 4870036.2102 | 12670835.2371 | 8648105.409 | 38676249.1901 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 54561056.0173 | 77814188.8042 | 100000 | 6.3981 | 8527.6342 | 12161.9885 | 173.8474 | 247.9386
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2138 | 24.0268 | 1.7283 | 4 | 8145.7638 | 11509.4136 | 166.0624 | 234.635 | 118.26 | 0 | 159.9805 | 3708490.3954 | 256160.5664 | 4347660.5424 | 4279347.3146 | 0 | 461000.3313 | 0 | 5090537.0685 | 13244533.2396 | 9039666.084 | 40427395.5422 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 56312202.3694 | 79565335.1563 | 133352.1432 | 6.9131 | 8145.7638 | 11509.4136 | 166.0624 | 234.635
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2755 | 25.1069 | 1.8354 | 4 | 7858.9155 | 11026.269 | 160.2146 | 224.7854 | 118.1735 | 0 | 177.7051 | 3823977.4367 | 263906.4242 | 4503610.8763 | 4473610.6064 | 0 | 434415.1632 | 0 | 5264812.9976 | 13697963.4582 | 9349141.5252 | 41811438.4878 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 57696245.315 | 80949378.1019 | 177827.941 | 7.3415 | 7858.9155 | 11026.269 | 160.2146 | 224.7854
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.2735 | 25.9553 | 1.922 | 4 | 7643.4911 | 10668.0398 | 155.8229 | 217.4824 | 118.0983 | 0 | 150.0415 | 3913420.8981 | 269884.2557 | 4625191.6261 | 4626623.8588 | 0 | 409199.2458 | 0 | 5399284.7549 | 14047831.3868 | 9587933.5755 | 42879369.6017 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 58764176.4289 | 82017309.2158 | 237137.3706 | 7.6881 | 7643.4911 | 10668.0398 | 155.8229 | 217.4824
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.401 | 26.616 | 1.991 | 4 | 7481.7205 | 10401.5303 | 152.525 | 212.0493 | 118.0355 | 0 | 176.1268 | 3982323.925 | 274476.0497 | 4719338.8695 | 4746054.2446 | 0 | 386763.7873 | 0 | 5502493.1817 | 14316358.5422 | 9771208.8768 | 43699017.4768 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 59583824.304 | 82836957.0909 | 316227.766 | 7.9639 | 7481.7205 | 10401.5303 | 152.525 | 212.0493
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8003 | 27.1209 | 2.0448 | 4 | 7360.247 | 10203.1792 | 150.0486 | 208.0056 | 117.9849 | 0 | 191.1153 | 4034553.1874 | 277948.5869 | 4790994.5959 | 4837482.989 | 0 | 367407.0526 | 0 | 5580270.7006 | 14518719.692 | 9909324.5196 | 44316701.3239 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60201508.1511 | 83454640.9381 | 421696.5034 | 8.1793 | 7360.247 | 10203.1792 | 150.0486 | 208.0056
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.625 | 27.5037 | 2.0864 | 4 | 7269.0397 | 10055.3375 | 148.1892 | 204.9917 | 117.9451 | 0 | 172.0583 | 4073905.5631 | 280560.0851 | 4845155.9501 | 4906862.8196 | 0 | 351222.6968 | 0 | 5638505.7747 | 14670235.4092 | 10012737.11 | 44779185.4084 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60663992.2356 | 83917125.0226 | 562341.3252 | 8.3455 | 7269.0397 | 10055.3375 | 148.1892 | 204.9917
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0157 | 27.7948 | 2.1183 | 4 | 7200.5628 | 9944.8427 | 146.7932 | 202.7391 | 117.914 | 0 | 186.1481 | 4103690.0155 | 282533.9002 | 4886245.7512 | 4959678.8127 | 0 | 338111.9564 | 0 | 5682401.57 | 14784443.2644 | 10090686.3179 | 45127791.5883 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61012598.4155 | 84265731.2024 | 749894.2093 | 8.4733 | 7200.5628 | 9944.8427 | 146.7932 | 202.7391
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0365 | 28.0081 | 2.1436 | 4 | 7144.5271 | 9856.5118 | 145.6508 | 200.9383 | 117.8908 | 0 | 168.5833 | 4125441.7509 | 283973.9726 | 4916304.9777 | 4998413.2914 | 0 | 325582.1568 | 0 | 5713389.2982 | 14865066.9767 | 10145713.6582 | 45373886.0824 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61258692.9096 | 84511825.6965 | 1000000 | 8.5742 | 7144.5271 | 9856.5118 | 145.6508 | 200.9383
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2324 | 28.2577 | 2.1662 | 4 | 7106.5074 | 9790.0917 | 144.8758 | 199.5843 | 117.8633 | 0 | 177.1834 | 4150806.9514 | 285651.664 | 4951414.4721 | 5043761.0017 | 0 | 321032.1476 | 0 | 5753539.8324 | 14969530.4305 | 10217012.1119 | 45692748.6116 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61577555.4388 | 84830688.2257 | 1333521.4322 | 8.665 | 7106.5074 | 9790.0917 | 144.8758 | 199.5843
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8197 | 28.3801 | 2.18 | 4 | 7078.0038 | 9744.6094 | 144.2947 | 198.657 | 117.8495 | 0 | 168.434 | 4163212.5871 | 286471.4568 | 4968610.3373 | 5066014.6621 | 0 | 314694.4324 | 0 | 5771611.3556 | 15016548.8269 | 10249103.1336 | 45836266.7918 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61721073.619 | 84974206.4059 | 1778279.41 | 8.7201 | 7078.0038 | 9744.6094 | 144.2947 | 198.657
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2607 | 28.4719 | 2.1904 | 4 | 7056.6168 | 9710.5551 | 143.8587 | 197.9628 | 117.8391 | 0 | 168.2232 | 4172506.899 | 287085.3638 | 4981503.3049 | 5082717.8445 | 0 | 309804.2957 | 0 | 5785110.9061 | 15051671.8882 | 10273075.3446 | 45943475.8469 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61828282.6741 | 85081415.461 | 2371373.7057 | 8.7617 | 7056.6168 | 9710.5551 | 143.8587 | 197.9628
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5897 | 28.5404 | 2.1983 | 4 | 7040.5714 | 9685.0739 | 143.5316 | 197.4433 | 117.8313 | 0 | 167.5502 | 4179427.9926 | 287542.3563 | 4991109.6684 | 5095173.2109 | 0 | 306039.308 | 0 | 5795124.0891 | 15077724.1366 | 10290856.5395 | 46022997.3014 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61907804.1286 | 85160936.9156 | 3162277.6602 | 8.793 | 7040.5714 | 9685.0739 | 143.5316 | 197.4433
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8332 | 28.591 | 2.2041 | 4 | 7028.5347 | 9666.0241 | 143.2862 | 197.055 | 117.8255 | 0 | 165.117 | 4184546.3225 | 287880.2258 | 4998216.873 | 5104393.7859 | 0 | 303141.3842 | 0 | 5802489.6506 | 15096887.8166 | 10303936.1449 | 46081492.2035 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 61966299.0307 | 85219431.8176 | 4216965.0343 | 8.8164 | 7028.5347 | 9666.0241 | 143.2862 | 197.055
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.0112 | 28.628 | 2.2084 | 4 | 7019.506 | 9651.8087 | 143.1021 | 196.7652 | 117.8212 | 0 | 167.0031 | 4188283.123 | 288126.8491 | 5003407.3845 | 5111130.7396 | 0 | 300900.4732 | 0 | 5807820.942 | 15110758.7432 | 10313403.3373 | 46123831.5919 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 62008638.4191 | 85261771.206 | 5623413.2519 | 8.8338 | 7019.506 | 9651.8087 | 143.1021 | 196.7652
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1498 | 28.6568 | 2.2118 | 4 | 7012.7339 | 9641.0883 | 142.9641 | 196.5466 | 117.8179 | 0 | 154.5993 | 4191190.3471 | 288318.6965 | 5007446.4913 | 5116374.9344 | 0 | 299248.7297 | 0 | 5812005.8876 | 15121647.1132 | 10320834.8735 | 46157067.0733 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 62041873.9005 | 85295006.6874 | 7498942.0933 | 8.847 | 7012.7339 | 9641.0883 | 142.9641 | 196.5466
1 | 4300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2546 | 28.6786 | 2.2143 | 4 | 7007.6547 | 9633.0404 | 142.8605 | 196.3826 | 117.8154 | 0 | 152.5563 | 4193388.5614 | 288463.7408 | 5010501.0893 | 5120341.8888 | 0 | 298009.2367 | 0 | 5815174.7617 | 15129891.8735 | 10326462.0918 | 46182233.2441 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 62067040.0713 | 85320172.8582 | 10000000 | 8.857 | 7007.6547 | 9633.0404 | 142.8605 | 196.3826
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2099 | [19 empty] | 100 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2118 | [19 empty] | 133.3521 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7043 | [19 empty] | 177.8279 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5292 | [19 empty] | 237.1374 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5541 | [19 empty] | 316.2278 | 0
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.23838 | 0.0015216 | 4 | 2887236.2403 | 6812989.7957 | 58860.216 | 138892.0122 | 95.3522 | 0 | 24.9385 | 126231.0846 | 7670.0846 | 110333.3768 | 75832.2858 | 0 | 77230.8559 | 0 | 154946.0982 | 403137.9636 | 275149.9438 | 1230531.6933 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17573446.9379 | 41467931.5092 | 421.6965 | 0.0060866 | 2887236.2403 | 6812989.7957 | 58860.216 | 138892.0122
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.33669 | 0.006205 | 4 | 721055.0708 | 1683760.2088 | 14699.6829 | 34325.7293 | 100.3802 | 0 | 309.1794 | 166300.2693 | 10420.5266 | 144893.6171 | 93505.3891 | 0 | 86543.5909 | 0 | 195648.7233 | 509037.8449 | 347428.7888 | 1553778.7501 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17896693.9947 | 41791178.5659 | 562.3413 | 0.02482 | 721055.0708 | 1683760.2088 | 14699.6829 | 34325.7293
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9155 | 0.52562 | 0.013362 | 4 | 345919.3327 | 792970.6044 | 7052.0335 | 16165.7783 | 105.9741 | 0 | 470.5829 | 235274.0859 | 15255.243 | 206077.1837 | 126943.3987 | 0 | 109373.3331 | 0 | 270240.0653 | 703109.216 | 479886.4874 | 2146159.0131 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 18489074.2577 | 42383558.8289 | 749.8942 | 0.053449 | 345919.3327 | 792970.6044 | 7052.0335 | 16165.7783
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9682 | 0.76289 | 0.023751 | 4 | 201714.3896 | 453221.1547 | 4112.2207 | 9239.5263 | 109.811 | 0 | 68.7775 | 312405.9612 | 20736.3758 | 276864.6886 | 168453.9953 | 0 | 132354.9345 | 0 | 355218.2226 | 924204.9499 | 630788.8688 | 2821027.9968 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19163943.2414 | 43058427.8126 | 1000 | 0.095005 | 201714.3896 | 453221.1547 | 4112.2207 | 9239.5263
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3003 | 1.0667 | 0.038224 | 4 | 130554.6538 | 286832.7136 | 2661.5332 | 5847.4728 | 112.6084 | 0 | 84.9639 | 401447.4328 | 27104.7991 | 361295.5442 | 221417.1718 | 0 | 157038.3029 | 0 | 455638.2678 | 1185477.3086 | 809112.6223 | 3618531.4496 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19961446.6942 | 43855931.2655 | 1333.5214 | 0.1529 | 130554.6538 | 286832.7136 | 2661.5332 | 5847.4728
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9502 | 1.4445 | 0.057695 | 4 | 90489.3947 | 194028.0612 | 1844.7487 | 3955.5245 | 114.6194 | 0 | 74.3879 | 502082.8618 | 34314.464 | 459809.5978 | 287116.6747 | 0 | 182516.8614 | 0 | 571677.7793 | 1487388.3146 | 1015173.0875 | 4540079.6412 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 20882994.8858 | 44777479.457 | 1778.2794 | 0.23078 | 90489.3947 | 194028.0612 | 1844.7487 | 3955.5245
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3829 | 2.0055 | 0.084696 | 4 | 65471.3019 | 136001.2122 | 1334.721 | 2772.5687 | 116.4026 | 0 | 86.0208 | 638189.8808 | 44076.9898 | 597092.6372 | 384159.8051 | 0 | 221307.9456 | 0 | 735082.6308 | 1912534.2191 | 1305343.9032 | 5837788.0115 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 22180703.2561 | 46075187.8273 | 2371.3737 | 0.33879 | 65471.3019 | 136001.2122 | 1334.721 | 2772.5687
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9628 | 2.6015 | 0.11944 | 4 | 49087.1458 | 99100.2691 | 1000.7079 | 2020.293 | 117.5102 | 0 | 97.2569 | 770717.561 | 53570.0815 | 734697.6941 | 487422.2661 | 0 | 248906.6403 | 0 | 895172.5547 | 2329055.3623 | 1589628.1421 | 7109170.302 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 23452085.5466 | 47346570.1179 | 3162.2777 | 0.47776 | 49087.1458 | 99100.2691 | 1000.7079 | 2020.293
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.442 | 3.4057 | 0.16546 | 4 | 37907.5525 | 74010.0684 | 772.7967 | 1508.7954 | 118.423 | 0 | 76.5802 | 935856.2005 | 65370.65 | 910784.5177 | 626492.549 | 0 | 285363.8064 | 0 | 1101308.4122 | 2865378.5791 | 1955679.7579 | 8746234.4727 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 25089149.7173 | 48983634.2885 | 4216.965 | 0.66185 | 37907.5525 | 74010.0684 | 772.7967 | 1508.7954
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8117 | 4.4167 | 0.22542 | 4 | 29988.8914 | 56488.6748 | 611.3641 | 1151.598 | 119.1233 | 0 | 91.244 | 1127761.6111 | 79048.5054 | 1120771.0539 | 801233.4272 | 0 | 325099.9429 | 0 | 1347026.6708 | 3504687.0842 | 2392020.9491 | 10697649.2445 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 27040564.4891 | 50935049.0603 | 5623.4133 | 0.90169 | 29988.8914 | 56488.6748 | 611.3641 | 1151.598
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.2218 | 5.6695 | 0.30268 | 4 | 24233.3735 | 43968.9092 | 494.0301 | 896.3657 | 119.6595 | 0 | 114.3349 | 1348367.2302 | 94732.4056 | 1368082.2745 | 1018007.3018 | 0 | 367191.3257 | 0 | 1636588.4097 | 4258067.3317 | 2906218.4484 | 12997254.7277 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 29340169.9723 | 53234654.5435 | 7498.9421 | 1.2107 | 24233.3735 | 43968.9092 | 494.0301 | 896.3657
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.8534 | 7.2058 | 0.40095 | 4 | 19970.9409 | 34869.7709 | 407.1346 | 710.8674 | 120.0727 | 0 | 85.5684 | 1600112.9913 | 112580.536 | 1656905.0961 | 1283763.2962 | 0 | 411167.6599 | 0 | 1975166.536 | 5138978.1644 | 3507458.1926 | 15686132.4725 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 32029047.7171 | 55923532.2884 | 10000 | 1.6038 | 19970.9409 | 34869.7709 | 407.1346 | 710.8674
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.7922 | 9.0452 | 0.52343 | 4 | 16766.994 | 28179.5121 | 341.8179 | 574.4775 | 120.3895 | 0 | 100.2468 | 1881615.8351 | 132484.0175 | 1986947.6755 | 1601770.9165 | 0 | 454896.8169 | 0 | 2362508.952 | 6146763.6758 | 4195292.5121 | 18762280.4014 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 35105195.646 | 58999680.2173 | 13335.2143 | 2.0937 | 16766.994 | 28179.5121 | 341.8179 | 574.4775
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.0144 | 11.1816 | 0.67196 | 4 | 14334.4254 | 23224.2774 | 292.2267 | 473.4583 | 120.6265 | 0 | 134.8435 | 2188268.1182 | 154102.7259 | 2353880.2911 | 1971171.4544 | 0 | 495601.4447 | 0 | 2793579.3734 | 7268320.4876 | 4960778.0819 | 22185701.9772 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 38528617.2218 | 62423101.7931 | 17782.7941 | 2.6878 | 14334.4254 | 23224.2774 | 292.2267 | 473.4583
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.1996 | 13.5378 | 0.84439 | 4 | 12480.3463 | 19554.8219 | 254.4287 | 398.6515 | 120.7858 | 0 | 129.0866 | 2507004.8738 | 176496.9584 | 2742659.5103 | 2378841.6682 | 0 | 528262.4708 | 0 | 3249973.5378 | 8455764.4842 | 5771233.009 | 25810236.5126 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 42153151.7572 | 66047636.3284 | 23713.7371 | 3.3776 | 12480.3463 | 19554.8219 | 254.4287 | 398.6515
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.8038 | 15.9821 | 1.0338 | 4 | 11068.9023 | 16847.2716 | 225.6545 | 343.4544 | 120.8654 | 0 | 150.3419 | 2820437.6832 | 198423.9932 | 3131956.4101 | 2802451.2884 | 0 | 548300.7763 | 0 | 3705612.359 | 9641243.2324 | 6580346.6138 | 29428772.3563 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 45771687.6009 | 69666172.1722 | 31622.7766 | 4.1352 | 11068.9023 | 16847.2716 | 225.6545 | 343.4544
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.2271 | 18.3703 | 1.2298 | 4 | 9998.2586 | 14855.4543 | 203.828 | 302.8485 | 120.8715 | 0 | 143.6691 | 3112616.1296 | 218757.1057 | 3501061.1065 | 3217486.1591 | 0 | 553832.1041 | 0 | 4135463.516 | 10759627.7684 | 7343667.0402 | 32842510.9296 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 49185426.1742 | 73079910.7454 | 42169.6503 | 4.9194 | 9998.2586 | 14855.4543 | 203.828 | 302.8485
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.9176 | 20.5734 | 1.4212 | 4 | 9189.0337 | 13392.3884 | 187.3309 | 273.022 | 120.8209 | 0 | 149.0558 | 3371525.9512 | 236669.617 | 3833248.8375 | 3601729.2781 | 0 | 545567.6799 | 0 | 4519609.1318 | 11759095.8617 | 8025824.5509 | 35893270.908 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 52236186.1526 | 76130670.7238 | 56234.1325 | 5.6846 | 9189.0337 | 13392.3884 | 187.3309 | 273.022
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5339 | 22.5155 | 1.5984 | 4 | 8579.0238 | 12316.237 | 174.895 | 251.0832 | 120.7353 | 0 | 174.8624 | 3592239.9083 | 251848.1194 | 4120350.6794 | 3941808.0852 | 0 | 526857.9263 | 0 | 4848910.8402 | 12615871.3579 | 8610591.432 | 38508478.3486 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 54851393.5932 | 78745878.1644 | 74989.4209 | 6.3937 | 8579.0238 | 12316.237 | 174.895 | 251.0832
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8808 | 24.1575 | 1.7552 | 4 | 8119.9647 | 11523.4037 | 165.5365 | 234.9202 | 120.635 | 0 | 179.2669 | 3773810.446 | 264263.4532 | 4359344.338 | 4230475.7562 | 0 | 501423.1283 | 0 | 5120433.6774 | 13322318.0832 | 9092755.8381 | 40664824.7203 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 57007739.9649 | 80902224.5362 | 100000 | 7.0207 | 8119.9647 | 11523.4037 | 165.5365 | 234.9202
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9586 | 25.5053 | 1.8888 | 4 | 7774.8324 | 10937.542 | 158.5005 | 222.9766 | 120.5345 | 0 | 174.6454 | 3919620.1783 | 274182.32 | 4553173.495 | 4468288.9913 | 0 | 473141.5914 | 0 | 5338478.5646 | 13889626.1527 | 9479955.2525 | 42396466.5458 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 58739381.7904 | 82633866.3617 | 133352.1432 | 7.5551 | 7774.8324 | 10937.542 | 158.5005 | 222.9766
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8554 | 26.5838 | 1.9992 | 4 | 7515.4772 | 10503.5524 | 153.2132 | 214.1291 | 120.4427 | 0 | 177.6861 | 4034302.9231 | 281949.1827 | 4706859.5256 | 4659200.3662 | 0 | 444866.5058 | 0 | 5509599.6163 | 14334848.0274 | 9783828.3304 | 43755454.4774 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 60098369.722 | 83992854.2933 | 177827.941 | 7.9966 | 7515.4772 | 10503.5524 | 153.2132 | 214.1291
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7212 | 27.4304 | 2.0882 | 4 | 7320.6232 | 10181.316 | 149.2408 | 207.5599 | 120.3638 | 0 | 180.8377 | 4123125.4389 | 287942.493 | 4826660.6238 | 4809463.0283 | 0 | 418525.4543 | 0 | 5641629.6449 | 14678363.0787 | 10018284.4114 | 44803994.1733 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61146909.4179 | 85041393.9892 | 237137.3706 | 8.3527 | 7320.6232 | 10181.316 | 149.2408 | 207.5599
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.7297 | 28.0861 | 2.1587 | 4 | 7174.2459 | 9941.5254 | 146.2567 | 202.6714 | 120.2985 | 0 | 169.559 | 4191224.9761 | 292523.7945 | 4918978.4112 | 4926119.1573 | 0 | 395221.27 | 0 | 5742386.3676 | 14940511.403 | 10197206.0294 | 45604171.4091 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61947086.6537 | 85841571.225 | 316227.766 | 8.6346 | 7174.2459 | 9941.5254 | 146.2567 | 202.6714
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0271 | 28.5851 | 2.2135 | 4 | 7064.2957 | 9763.0265 | 144.0152 | 199.0325 | 120.2465 | 0 | 168.571 | 4242632.7424 | 295973.9989 | 4988942.7771 | 5015031.6497 | 0 | 375200.7774 | 0 | 5817934.9587 | 15137073.3401 | 10331363.5904 | 46204153.8346 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62547069.0792 | 86441553.6505 | 421696.5034 | 8.854 | 7064.2957 | 9763.0265 | 144.0152 | 199.0325
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7929 | 28.9674 | 2.256 | 4 | 6981.7177 | 9629.6238 | 142.3318 | 196.3129 | 120.2053 | 0 | 169.6571 | 4281797.0864 | 298597.6476 | 5042405.1784 | 5083265.9459 | 0 | 358740.2098 | 0 | 5875274.3665 | 15286258.7172 | 10433185.6757 | 46659524.8276 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 63002440.0722 | 86896924.6434 | 562341.3252 | 9.0239 | 6981.7177 | 9629.6238 | 142.3318 | 196.3129
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.1157 | 29.2532 | 2.2883 | 4 | 6919.7072 | 9530.1658 | 141.0676 | 194.2853 | 120.1737 | 0 | 184.3243 | 4310940.6371 | 300547.209 | 5082280.1543 | 5134324.3322 | 0 | 345253.3093 | 0 | 5917604.8004 | 15396393.8229 | 10508355.1484 | 46995699.4137 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 63338614.6583 | 87233099.2296 | 749894.2093 | 9.1534 | 6919.7072 | 9530.1658 | 141.0676 | 194.2853
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1144 | 29.4687 | 2.313 | 4 | 6873.1498 | 9455.7984 | 140.1185 | 192.7692 | 120.1494 | 0 | 181.9561 | 4332832.3898 | 302010.0755 | 5112284.9636 | 5172837.853 | 0 | 334513.2414 | 0 | 5949246.6241 | 15478719.3576 | 10564544.0175 | 47246988.5225 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 63589903.7671 | 87484388.3384 | 1000000 | 9.2519 | 6873.1498 | 9455.7984 | 140.1185 | 192.7692
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.646 | 29.5832 | 2.3304 | 4 | 6834.0741 | 9397.4715 | 139.3218 | 191.5802 | 120.1364 | 0 | 165.71 | 4344447.4849 | 302785.7028 | 5128222.1381 | 5193326.5863 | 0 | 322283.973 | 0 | 5963515.6952 | 15515844.5537 | 10589882.7266 | 47360308.8607 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 63703224.1053 | 87597708.6765 | 1333521.4322 | 9.3214 | 6834.0741 | 9397.4715 | 139.3218 | 191.5802
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.8077 | 29.8332 | 2.3512 | 4 | 6808.1942 | 9348.8642 | 138.7942 | 190.5892 | 120.1077 | 0 | 158.3701 | 4369745.4007 | 304473.903 | 5162973.0982 | 5238077.1257 | 0 | 321199.2693 | 0 | 6004622.8309 | 15622796.8884 | 10662879.8927 | 47686768.4091 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64029683.6537 | 87924168.225 | 1778279.41 | 9.4048 | 6808.1942 | 9348.8642 | 138.7942 | 190.5892
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2339 | 29.9248 | 2.3618 | 4 | 6788.8277 | 9318.1025 | 138.3994 | 189.9621 | 120.097 | 0 | 177.868 | 4378990.3441 | 305090.2686 | 5175689.9572 | 5254482.1747 | 0 | 316282.5405 | 0 | 6017908.7612 | 15657364.1538 | 10686472.7616 | 47792280.9618 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64135196.2064 | 88029680.7777 | 2371373.7057 | 9.4472 | 6788.8277 | 9318.1025 | 138.3994 | 189.9621
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5387 | 29.9903 | 2.3696 | 4 | 6774.2974 | 9295.2414 | 138.1032 | 189.4961 | 120.0893 | 0 | 178.7803 | 4385592.7857 | 305530.2952 | 5184777.0773 | 5266213.7943 | 0 | 312384.2587 | 0 | 6027254.3023 | 15681679.3348 | 10703068.3723 | 47866500.2206 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64209415.4652 | 88103900.0364 | 3162277.6602 | 9.4784 | 6774.2974 | 9295.2414 | 138.1032 | 189.4961
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.7823 | 30.0426 | 2.3756 | 4 | 6763.3968 | 9277.9302 | 137.881 | 189.1432 | 120.0831 | 0 | 162.6359 | 4390861.6813 | 305881.3618 | 5192031.6254 | 5275584.712 | 0 | 309548.799 | 0 | 6034824.19 | 15701374.6298 | 10716510.8158 | 47926617.8151 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64269533.0597 | 88164017.6309 | 4216965.0343 | 9.5026 | 6763.3968 | 9277.9302 | 137.881 | 189.1432
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.9527 | 30.0792 | 2.38 | 4 | 6755.2201 | 9265.1055 | 137.7143 | 188.8817 | 120.0788 | 0 | 176.3775 | 4394544.3524 | 306126.683 | 5197103.8687 | 5282139.5984 | 0 | 307286.7101 | 0 | 6040008.4729 | 15714863.0703 | 10725716.9537 | 47967789.7094 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64310704.954 | 88205189.5253 | 5623413.2519 | 9.5201 | 6755.2201 | 9265.1055 | 137.7143 | 188.8817
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.077 | 30.1059 | 2.3833 | 4 | 6749.0869 | 9255.535 | 137.5893 | 188.6866 | 120.0756 | 0 | 177.1273 | 4397228.3152 | 306305.4478 | 5200801.4244 | 5286919.4596 | 0 | 305543.9595 | 0 | 6043751.4565 | 15724601.5459 | 10732363.6633 | 47997515.2721 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64340430.5167 | 88234915.088 | 7498942.0933 | 9.5332 | 6749.0869 | 9255.535 | 137.5893 | 188.6866
1 | 4400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.187 | 30.1295 | 2.3859 | 4 | 6744.4868 | 9248.1571 | 137.4955 | 188.5362 | 120.0728 | 0 | 175.4404 | 4399603.7856 | 306463.6573 | 5204074.3652 | 5291151.2742 | 0 | 304379.3326 | 0 | 6047212.2418 | 15733605.7993 | 10738509.2513 | 48024999.7072 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 64367914.9518 | 88262399.5231 | 10000000 | 9.5438 | 6744.4868 | 9248.1571 | 137.4955 | 188.5362
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9731 | [19 empty] | 100 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7812 | [19 empty] | 133.3521 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3532 | [19 empty] | 177.8279 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5277 | [19 empty] | 237.1374 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0819 | [19 empty] | 316.2278 | 0
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.24423 | 0.002588 | 4 | 1743869.7355 | 4114812.057 | 35551.1433 | 83886.0095 | 96.6467 | 0 | 25.0978 | 129622.1797 | 7934.3969 | 112386.6127 | 76373.9548 | 0 | 75874.4193 | 0 | 156854.7097 | 408103.7793 | 278539.2151 | 1245689.2675 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18052573.0203 | 42596613.5031 | 421.6965 | 0.010352 | 1743869.7355 | 4114812.057 | 35551.1433 | 83886.0095
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.38951 | 0.0079996 | 4 | 579386.6013 | 1346424.9394 | 11811.5795 | 27448.6936 | 103.5153 | 0 | 355.1851 | 188000.1426 | 12000.3669 | 162436.251 | 102020.3555 | 0 | 94938.9197 | 0 | 218164.454 | 567619.1575 | 387411.7384 | 1732591.3857 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18539475.1385 | 43083515.6213 | 562.3413 | 0.031998 | 579386.6013 | 1346424.9394 | 11811.5795 | 27448.6936
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1489 | 0.59493 | 0.016345 | 4 | 293122.6636 | 668518.0328 | 5975.702 | 13628.6443 | 108.765 | 0 | 510.0408 | 261064.7279 | 17206.174 | 227089.6058 | 137638.973 | 0 | 118325.2453 | 0 | 296916.6431 | 772516.1994 | 527258.1797 | 2358015.7482 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19164899.501 | 43708939.9838 | 749.8942 | 0.065382 | 293122.6636 | 668518.0328 | 5975.702 | 13628.6443
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2823 | 0.86039 | 0.028382 | 4 | 175312.8155 | 391505.3174 | 3573.9889 | 7981.3654 | 112.5042 | 0 | 61.2344 | 345391.9411 | 23290.4514 | 304241.3554 | 183393.6516 | 0 | 143323.5651 | 0 | 389859.9762 | 1014335.6868 | 692304.9487 | 3096141.5763 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19903025.3291 | 44447065.8119 | 1000 | 0.11353 | 175312.8155 | 391505.3174 | 3573.9889 | 7981.3654
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6977 | 1.195 | 0.044989 | 4 | 115367.6019 | 251756.4368 | 2351.9246 | 5132.3955 | 115.196 | 0 | 67.1364 | 441343.8462 | 30252.3756 | 394939.2544 | 240704.827 | 0 | 169455.8661 | 0 | 497911.5061 | 1295463.6031 | 884180.5282 | 3954251.8068 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 20761135.5596 | 45305176.0424 | 1333.5214 | 0.17996 | 115367.6019 | 251756.4368 | 2351.9246 | 5132.3955
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4345 | 1.6066 | 0.067127 | 4 | 80975.695 | 172384.6396 | 1650.7991 | 3514.294 | 117.1032 | 0 | 73.0619 | 548755.3438 | 38049.272 | 499781.7508 | 311095.2534 | 0 | 195905.9562 | 0 | 621499.1548 | 1617013.3137 | 1103644.8129 | 4935744.8576 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 21742628.6104 | 46286669.0932 | 1778.2794 | 0.26851 | 80975.695 | 172384.6396 | 1650.7991 | 3514.294
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8628 | 2.1879 | 0.097803 | 4 | 58930.5861 | 121669.0789 | 1201.3797 | 2480.3887 | 118.8004 | 0 | 96.4156 | 687739.4389 | 48164.7056 | 639076.3179 | 409963.3439 | 0 | 232152.4362 | 0 | 786667.5346 | 2046747.5573 | 1396947.2643 | 6247458.5988 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 23054342.3517 | 47598382.8345 | 2371.3737 | 0.39121 | 58930.5861 | 121669.0789 | 1201.3797 | 2480.3887
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8083 | 2.8929 | 0.13781 | 4 | 44524.3614 | 89049.2895 | 907.6893 | 1815.3902 | 119.9677 | 0 | 76.7992 | 841974.7604 | 59358.932 | 798441.471 | 530161.9764 | 0 | 268032.122 | 0 | 974208.0121 | 2534689.4099 | 1729977.6049 | 7736844.2887 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 24543728.0416 | 49087768.5244 | 3162.2777 | 0.55124 | 44524.3614 | 89049.2895 | 907.6893 | 1815.3902
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5092 | 3.7793 | 0.19023 | 4 | 34581.2024 | 66837.0544 | 704.9846 | 1362.5638 | 120.8558 | 0 | 78.1026 | 1020790.8865 | 72309.2842 | 988199.8587 | 681133.4206 | 0 | 306916.8984 | 0 | 1197046.6359 | 3114469.7986 | 2125689.6335 | 9506556.4163 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 26313440.1692 | 50857480.652 | 4216.965 | 0.76092 | 34581.2024 | 66837.0544 | 704.9846 | 1362.5638
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1493 | 4.8919 | 0.25842 | 4 | 27495.3161 | 51239.9055 | 560.5292 | 1044.5948 | 121.5377 | 0 | 87.1569 | 1228433.2701 | 87309.4967 | 1214197.1494 | 870700.716 | 0 | 349186.5672 | 0 | 1462432.6077 | 3804949.6592 | 2596956.3263 | 11614165.7926 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 28421049.5454 | 52965090.0282 | 5623.4133 | 1.0337 | 27495.3161 | 51239.9055 | 560.5292 | 1044.5948
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8297 | 6.2546 | 0.34571 | 4 | 22326.2055 | 40075.2883 | 455.1499 | 816.989 | 122.0566 | 0 | 94.2836 | 1464519.5025 | 104314.7587 | 1477437.7507 | 1102678.8821 | 0 | 392672.2966 | 0 | 1771233.0444 | 4608385.0516 | 3145317.4906 | 14066558.7773 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 30873442.5302 | 55417483.013 | 7498.9421 | 1.3828 | 22326.2055 | 40075.2883 | 455.1499 | 816.989
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8166 | 7.9296 | 0.45629 | 4 | 18489.5254 | 31937.2017 | 376.934 | 651.0831 | 122.4601 | 0 | 109.4541 | 1734639.3624 | 123699.9521 | 1785813.9782 | 1386234.7787 | 0 | 438745.2283 | 0 | 2132961.9869 | 5549529.5592 | 3787667.9556 | 16939292.8015 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 33746176.5543 | 58290217.0371 | 10000 | 1.8252 | 18489.5254 | 31937.2017 | 376.934 | 651.0831
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.1498 | 9.928 | 0.59357 | 4 | 15593.1552 | 25930.5596 | 317.8876 | 528.6295 | 122.769 | 0 | 96.8999 | 2035878.0081 | 145256.8964 | 2137153.8743 | 1724488.0474 | 0 | 484249.571 | 0 | 2545540.2949 | 6622973.6853 | 4520315.6287 | 20215856.0061 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 37022739.759 | 61566780.2418 | 13335.2143 | 2.3743 | 15593.1552 | 25930.5596 | 317.8876 | 528.6295
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.7406 | 12.2272 | 0.75877 | 4 | 13388.4243 | 21475.2139 | 272.9411 | 437.8013 | 122.996 | 0 | 126.7091 | 2361225.1545 | 168468.3294 | 2524309.4059 | 2113757.0056 | 0 | 525518.387 | 0 | 3000378.5301 | 7806369.4732 | 5328007.5703 | 23828033.856 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 40634917.6088 | 65178958.0916 | 17782.7941 | 3.0351 | 13388.4243 | 21475.2139 | 272.9411 | 437.8013
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2398 | 14.7401 | 0.94898 | 4 | 11704.9119 | 18170.7923 | 238.6205 | 370.4362 | 123.1409 | 0 | 130.1061 | 2696888.8227 | 192341.5738 | 2931147.2103 | 2540936.408 | 0 | 557607.8426 | 0 | 3478379.5244 | 9050030.0088 | 6176831.4405 | 27624162.8313 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 44431046.5841 | 68975087.067 | 23713.7371 | 3.7959 | 11704.9119 | 18170.7923 | 238.6205 | 370.4362
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.9922 | 17.3022 | 1.1549 | 4 | 10423.9597 | 15736.9292 | 212.5065 | 320.8186 | 123.2014 | 0 | 143.9884 | 3021652.813 | 215327.9651 | 3331959.0864 | 2977307.0004 | 0 | 575018.2849 | 0 | 3947293.4084 | 10270047.7475 | 7009518.6161 | 31348124.9218 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 48155008.6747 | 72699049.1575 | 31622.7766 | 4.6196 | 10423.9597 | 15736.9292 | 212.5065 | 320.8186
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.4332 | 19.773 | 1.3653 | 4 | 9452.8752 | 13947.1843 | 192.7096 | 284.3322 | 123.1876 | 0 | 153.1403 | 3320839.2148 | 236380.3811 | 3707508.796 | 3399336.7449 | 0 | 577044.9945 | 0 | 4384032.9512 | 11406354.4503 | 7785071.2894 | 34816568.8222 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 51623452.5751 | 76167493.0579 | 42169.6503 | 5.4611 | 9452.8752 | 13947.1843 | 192.7096 | 284.3322
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.0434 | 22.0281 | 1.5681 | 4 | 8719.1315 | 12632.0853 | 177.7513 | 257.5221 | 123.1193 | 0 | 165.2301 | 3583447.9726 | 254740.436 | 4042277.2273 | 3785864.0651 | 0 | 565136.7186 | 0 | 4770271.9037 | 12411268.976 | 8470946.1022 | 37883953.4015 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 54690837.1544 | 79234877.6372 | 56234.1325 | 6.2725 | 8719.1315 | 12632.0853 | 177.7513 | 257.5221
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5112 | 23.9972 | 1.7541 | 4 | 8166.0322 | 11664.1604 | 166.4756 | 237.7897 | 123.0197 | 0 | 158.8108 | 3805437.9851 | 270160.1575 | 4329158.0643 | 4124658.0697 | 0 | 543049.3619 | 0 | 5098260.819 | 13264628.854 | 9053381.7537 | 40488735.0652 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 57295618.818 | 81839659.3008 | 74989.4209 | 7.0163 | 8166.0322 | 11664.1604 | 166.4756 | 237.7897
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.7728 | 25.6719 | 1.9184 | 4 | 7749.4655 | 10948.0468 | 157.9833 | 223.1907 | 122.9076 | 0 | 154.809 | 3989472.1896 | 282878.4111 | 4569553.0223 | 4415216.358 | 0 | 515719.5398 | 0 | 5371407.4131 | 13975300.2618 | 9538429.5924 | 42657976.788 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 59464860.5409 | 84008901.0237 | 100000 | 7.6734 | 7749.4655 | 10948.0468 | 157.9833 | 223.1907
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.6971 | 27.0277 | 2.0569 | 4 | 7436.159 | 10419.2274 | 151.5962 | 212.41 | 122.7993 | 0 | 175.6401 | 4135408.846 | 292914.5877 | 4761952.5377 | 4651890.4909 | 0 | 485437.1106 | 0 | 5587765.3934 | 14538219.3454 | 9922633.4338 | 44376221.7456 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 61183105.4984 | 85727145.9812 | 133352.1432 | 8.2278 | 7436.159 | 10419.2274 | 151.5962 | 212.41
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4519 | 28.1085 | 2.1709 | 4 | 7200.6621 | 10027.1426 | 146.7952 | 204.4169 | 122.7021 | 0 | 162.8898 | 4249866.4369 | 300751.7777 | 4914008.6709 | 4841421.9058 | 0 | 455681.883 | 0 | 5757074.963 | 14978728.1152 | 10223289.7207 | 45720823.4732 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 62527707.226 | 87071747.7088 | 177827.941 | 8.6836 | 7200.6621 | 10027.1426 | 146.7952 | 204.4169
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.1696 | 28.9489 | 2.2622 | 4 | 7023.6912 | 9736.1511 | 143.1874 | 198.4846 | 122.6199 | 0 | 184.6792 | 4337741.7378 | 306747.2665 | 5031461.6179 | 4989339.604 | 0 | 428045.0195 | 0 | 5886400.7458 | 15315207.2737 | 10452943.6604 | 46747886.9255 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 63554770.6783 | 88098811.1611 | 237137.3706 | 9.0486 | 7023.6912 | 9736.1511 | 143.1874 | 198.4846
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.064 | 29.6002 | 2.3343 | 4 | 6890.7198 | 9519.3582 | 140.4766 | 194.065 | 122.5524 | 0 | 170.2792 | 4405194.175 | 311336.1101 | 5122046.8271 | 5104332.688 | 0 | 403889.9635 | 0 | 5985251.9078 | 15572397.7202 | 10628481.4248 | 47532930.8164 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64339814.5693 | 88883855.0521 | 316227.766 | 9.3372 | 6890.7198 | 9519.3582 | 140.4766 | 194.065
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2728 | 30.0955 | 2.3903 | 4 | 6790.8214 | 9357.8648 | 138.4401 | 190.7727 | 122.4988 | 0 | 180.5204 | 4456108.6671 | 314791.9738 | 5190674.381 | 5191985.1309 | 0 | 383296.2715 | 0 | 6059374.0055 | 15765248.2137 | 10760105.8493 | 48121584.4927 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64928468.2456 | 89472508.7284 | 421696.5034 | 9.5612 | 6790.8214 | 9357.8648 | 138.4401 | 190.7727
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.9512 | 30.4708 | 2.4334 | 4 | 6715.7817 | 9237.3351 | 136.9103 | 188.3156 | 122.4569 | 0 | 180.6051 | 4494477.2177 | 317391.6703 | 5242536.7648 | 5258531.9339 | 0 | 366278.884 | 0 | 6114894.4236 | 15909700.9529 | 10858697.812 | 48562509.6593 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65369393.4122 | 89913433.895 | 562341.3252 | 9.7337 | 6715.7817 | 9237.3351 | 136.9103 | 188.3156
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2204 | 30.7539 | 2.4664 | 4 | 6659.4252 | 9147.2822 | 135.7614 | 186.4797 | 122.4245 | 0 | 183.7453 | 4523305.8537 | 319342.3272 | 5281587.4427 | 5308814.9901 | 0 | 352518.1456 | 0 | 6156371.8161 | 16017616.62 | 10932352.4723 | 48891909.6677 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65698793.4205 | 90242833.9033 | 749894.2093 | 9.8655 | 6659.4252 | 9147.2822 | 135.7614 | 186.4797
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1755 | 30.9667 | 2.4914 | 4 | 6617.109 | 9079.9588 | 134.8987 | 185.1072 | 122.3998 | 0 | 181.016 | 4544899.7223 | 320801.9374 | 5310885.3275 | 5346639.4241 | 0 | 341566.4114 | 0 | 6187269.2008 | 16098005.2772 | 10987219.3826 | 49137286.6833 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65944170.4361 | 90488210.9189 | 1000000 | 9.9657 | 6617.109 | 9079.9588 | 134.8987 | 185.1072
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8944 | 31.1266 | 2.5104 | 4 | 6585.3415 | 9029.5771 | 134.2511 | 184.0801 | 122.381 | 0 | 168.4701 | 4561092.4596 | 321895.6038 | 5332881.8995 | 5375093.8755 | 0 | 332979.8852 | 0 | 6210338.0522 | 16158025.6963 | 11028184.552 | 49320492.024 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 66127375.7769 | 90671416.2597 | 1333521.4322 | 10.0416 | 6585.3415 | 9029.5771 | 134.2511 | 184.0801
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.305 | 30.9954 | 2.5121 | 4 | 6558.0016 | 9000.6094 | 133.6937 | 183.4896 | 122.3962 | 0 | 267.2199 | 4547803.6739 | 320997.675 | 5314837.2015 | 5351759.3733 | 0 | 314076.6465 | 0 | 6181295.0824 | 16082461.8465 | 10976610.6718 | 49089842.171 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 65896725.9238 | 90440766.4066 | 1778279.41 | 10.0483 | 6558.0016 | 9000.6094 | 133.6937 | 183.4896
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.846 | 31.5608 | 2.5491 | 4 | 6539.8814 | 8947.0288 | 133.3243 | 182.3973 | 122.3307 | 0 | 166.6272 | 4604926.7358 | 324855.7933 | 5392478.1242 | 5452344.7038 | 0 | 328636.8686 | 0 | 6280264.468 | 16339959.8864 | 11152358.3751 | 49875824.9552 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 66682708.708 | 91226749.1908 | 2371373.7057 | 10.1963 | 6539.8814 | 8947.0288 | 133.3243 | 182.3973
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.0802 | 31.8367 | 2.5687 | 4 | 6526.365 | 8915.0904 | 133.0488 | 181.7462 | 122.3027 | 0 | 189.0926 | 4632782.0484 | 326742.9555 | 5430263.7335 | 5501279.8942 | 0 | 333371.8102 | 0 | 6327531.7723 | 16462939.7164 | 11236294.636 | 50251206.5666 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 67058090.3194 | 91602130.8022 | 3162277.6602 | 10.275 | 6526.365 | 8915.0904 | 133.0488 | 181.7462
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3313 | 31.8928 | 2.5752 | 4 | 6516.334 | 8899.0816 | 132.8443 | 181.4198 | 122.2969 | 0 | 198.2175 | 4638432.0052 | 327125.4504 | 5437936.3982 | 5511234.1653 | 0 | 330669.1079 | 0 | 6335704.8795 | 16484204.4648 | 11250808.2637 | 50316114.7351 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 67122998.4879 | 91667038.9707 | 4216965.0343 | 10.3007 | 6516.334 | 8899.0816 | 132.8443 | 181.4198
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5017 | 31.9308 | 2.5798 | 4 | 6508.8094 | 8887.2879 | 132.6909 | 181.1794 | 122.293 | 0 | 189.5803 | 4642262.1441 | 327384.6979 | 5443139.2573 | 5517987.4094 | 0 | 328452.0007 | 0 | 6341097.9487 | 16498236.1244 | 11260385.1597 | 50358944.7421 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 67165828.4949 | 91709868.9777 | 5623413.2519 | 10.3192 | 6508.8094 | 8887.2879 | 132.6909 | 181.1794
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.6332 | 31.9602 | 2.5833 | 4 | 6503.1653 | 8878.4053 | 132.5758 | 180.9983 | 122.2899 | 0 | 189.4014 | 4645216.4164 | 327584.6409 | 5447153.0561 | 5523198.8886 | 0 | 326809.7374 | 0 | 6345285.4684 | 16509131.1917 | 11267821.2671 | 50392200.6666 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 67199084.4195 | 91743124.9023 | 7498942.0933 | 10.3333 | 6503.1653 | 8878.4053 | 132.5758 | 180.9983
1 | 4500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7381 | 31.9836 | 2.586 | 4 | 6498.9321 | 8871.6762 | 132.4895 | 180.8611 | 122.2875 | 0 | 196.36 | 4647570.3866 | 327743.945 | 5450351.6701 | 5527352.9027 | 0 | 325627.6617 | 0 | 6348672.1608 | 16517942.6706 | 11273835.2825 | 50419096.68 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 67225980.4329 | 91770020.9157 | 10000000 | 10.3442 | 6498.9321 | 8871.6762 | 132.4895 | 180.8611
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3182 | [19 empty] | 100 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1445 | [19 empty] | 133.3521 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0465 | [19 empty] | 177.8279 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8864 | [19 empty] | 237.1374 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0786 | [19 empty] | 316.2278 | 0
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.25007 | 0.0036889 | 4 | 1256259.7327 | 2964194.8651 | 25610.5539 | 60429.1217 | 97.9232 | 0 | 29.1566 | 132992.3152 | 8199.6179 | 114421.8422 | 76893.3439 | 0 | 74400.3529 | 0 | 158693.9141 | 412889.0119 | 281805.2346 | 1260295.6326 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18537007.9845 | 43738808.5061 | 421.6965 | 0.014756 | 1256259.7327 | 2964194.8651 | 25610.5539 | 60429.1217
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.44557 | 0.010105 | 4 | 474854.9195 | 1098357.2332 | 9680.5598 | 22391.4978 | 106.5206 | 0 | 398.4729 | 210533.0061 | 13678.8961 | 180490.5067 | 110830.595 | 0 | 103337.6488 | 0 | 241359.5545 | 627968.0513 | 428601.0985 | 1916799.357 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19193511.7089 | 44395312.2305 | 562.3413 | 0.04042 | 474854.9195 | 1098357.2332 | 9680.5598 | 22391.4978
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4212 | 0.67784 | 0.019832 | 4 | 250654.2097 | 568345.2588 | 5109.9251 | 11586.4868 | 111.6393 | 0 | 561.8511 | 291046.8753 | 19511.2571 | 251552.5417 | 150513.9897 | 0 | 129149.7165 | 0 | 328292.0083 | 854148.4635 | 582973.8774 | 2607188.7293 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19883901.0813 | 45085701.6028 | 749.8942 | 0.079328 | 250654.2097 | 568345.2588 | 5109.9251 | 11586.4868
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5648 | 0.9555 | 0.033592 | 4 | 153558.9544 | 341117.1022 | 3130.507 | 6954.1335 | 115.0698 | 0 | 75.487 | 377326.8618 | 25830.2319 | 330259.2149 | 197469.9164 | 0 | 152876.1251 | 0 | 422667.3165 | 1099693.6566 | 750563.517 | 3356686.8401 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 20633399.1921 | 45835199.7136 | 1000 | 0.13437 | 153558.9544 | 341117.1022 | 3130.507 | 6954.1335
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.058 | 1.3211 | 0.052528 | 4 | 102573.145 | 222517.3894 | 2091.0923 | 4536.318 | 117.6926 | 0 | 78.1072 | 480295.0113 | 33407.6034 | 427198.1445 | 259059.8403 | 0 | 180359.3121 | 0 | 538324.7656 | 1400610.6144 | 955945.524 | 4275200.8156 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 21551913.1676 | 46753713.6892 | 1333.5214 | 0.21011 | 102573.145 | 222517.3894 | 2091.0923 | 4536.318
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9144 | 1.7759 | 0.077609 | 4 | 72855.3192 | 154037.4981 | 1485.2542 | 3140.2627 | 119.5453 | 0 | 73.5891 | 596849.5197 | 41979.851 | 540566.4995 | 335659.6968 | 0 | 209097.199 | 0 | 672419.5787 | 1749497.8117 | 1194068.2051 | 5340138.3615 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 22616850.7135 | 47818651.235 | 1778.2794 | 0.31044 | 72855.3192 | 154037.4981 | 1485.2542 | 3140.2627
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5622 | 2.4337 | 0.11293 | 4 | 53300.6325 | 109091.2521 | 1086.6055 | 2223.9727 | 121.2846 | 0 | 80.3809 | 751465.5252 | 53400.1978 | 694700.546 | 445970.656 | 0 | 250056.1084 | 0 | 856281.2831 | 2227868.2511 | 1520565.8595 | 6800308.4271 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 24077020.779 | 49278821.3006 | 2371.3737 | 0.45172 | 53300.6325 | 109091.2521 | 1086.6055 | 2223.9727
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6413 | 3.1961 | 0.15813 | 4 | 40555.2228 | 80398.7258 | 826.7731 | 1639.0368 | 122.4039 | 0 | 92.3187 | 915247.7205 | 65443.4545 | 863274.4809 | 573406.3106 | 0 | 286722.0616 | 0 | 1054596.6709 | 2743844.2102 | 1872730.0538 | 8375264.963 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 25651977.315 | 50853777.8365 | 3162.2777 | 0.63252 | 40555.2228 | 80398.7258 | 826.7731 | 1639.0368
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6197 | 4.1816 | 0.21755 | 4 | 31694.6354 | 60655.0187 | 646.138 | 1236.5346 | 123.2822 | 0 | 68.4278 | 1110499.8123 | 79759.2922 | 1069723.6079 | 737466.7054 | 0 | 329523.6386 | 0 | 1297519.492 | 3375879.5603 | 2304107.1673 | 10304479.2759 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 27581191.6279 | 52782992.1494 | 4216.965 | 0.87022 | 31694.6354 | 60655.0187 | 646.138 | 1236.5346
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.5307 | 5.4004 | 0.29467 | 4 | 25321.2222 | 46702.4287 | 516.2074 | 952.0922 | 123.9458 | 0 | 89.5328 | 1334200.3943 | 96135.6669 | 1311984.7179 | 941641.204 | 0 | 374195.4862 | 0 | 1582681.413 | 4117812.3841 | 2810491.5648 | 12569142.8313 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 29845855.1832 | 55047655.7048 | 5623.4133 | 1.1787 | 25321.2222 | 46702.4287 | 516.2074 | 952.0922
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5741 | 6.9009 | 0.39338 | 4 | 20652.445 | 36668.4975 | 421.028 | 747.5369 | 124.4546 | 0 | 80.0726 | 1589996.448 | 114803.4255 | 1595735.3798 | 1192752.5657 | 0 | 420939.6662 | 0 | 1916548.7192 | 4986466.6293 | 3403365.9361 | 15220608.7698 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 32497321.1218 | 57699121.6434 | 7498.9421 | 1.5735 | 20652.445 | 36668.4975 | 421.028 | 747.5369
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9406 | 8.7308 | 0.51814 | 4 | 17168.6831 | 29328.4282 | 350.0068 | 597.8997 | 124.8476 | 0 | 113.2104 | 1880737.9436 | 135958.8108 | 1925584.8999 | 1498917.4351 | 0 | 469331.6035 | 0 | 2305106.9702 | 5997415.494 | 4093359.3092 | 18306412.4663 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 35583124.8182 | 60784925.3398 | 10000 | 2.0726 | 17168.6831 | 29328.4282 | 350.0068 | 597.8997
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.6862 | 10.904 | 0.67238 | 4 | 14534.0386 | 23904.464 | 296.296 | 487.3248 | 125.1473 | 0 | 94.197 | 2203785.5522 | 159400.9686 | 2299826.915 | 1862890.9428 | 0 | 516673.1723 | 0 | 2746605.2449 | 7146103.4409 | 4877362.4362 | 21812648.6729 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 39089361.0249 | 64291161.5464 | 13335.2143 | 2.6895 | 14534.0386 | 23904.464 | 296.296 | 487.3248
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.6176 | 13.3702 | 0.85617 | 4 | 12527.535 | 19886.42 | 255.3907 | 405.4116 | 125.3613 | 0 | 111.6217 | 2548310.0007 | 184323.4703 | 2706898.8448 | 2276439.3027 | 0 | 557823.7364 | 0 | 3226780.1884 | 8395420.1467 | 5730046.7588 | 25626042.4489 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 42902754.8009 | 68104555.3224 | 17782.7941 | 3.4247 | 12527.535 | 19886.42 | 255.3907 | 405.4116
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3091 | 16.0179 | 1.0646 | 4 | 10997.9668 | 16916.1224 | 224.2084 | 344.858 | 125.4881 | 0 | 141.2527 | 2897657.6077 | 209487.7214 | 3127562.4612 | 2720805.9243 | 0 | 587422.2332 | 0 | 3721745.0197 | 9683217.1063 | 6608994.6453 | 29556892.719 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 46833605.071 | 72035405.5926 | 23713.7371 | 4.2584 | 10997.9668 | 16916.1224 | 224.2084 | 344.858
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1593 | 18.6902 | 1.2876 | 4 | 9834.8753 | 14728.0683 | 200.4972 | 300.2516 | 125.528 | 0 | 124.4902 | 3232709.0036 | 233490.7926 | 3538349.9316 | 3170101.9896 | 0 | 601549.2484 | 0 | 4202718.3767 | 10934611.1201 | 7463096.7732 | 33376627.2359 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 50653339.5878 | 75855140.1094 | 31622.7766 | 5.1504 | 9834.8753 | 14728.0683 | 200.4972 | 300.2516
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6003 | 21.2416 | 1.5127 | 4 | 8953.5789 | 13118.5664 | 182.5308 | 267.4397 | 125.4937 | 0 | 130.0385 | 3538658.1387 | 255266.929 | 3919852.5822 | 3600158.1096 | 0 | 599921.1287 | 0 | 4646404.1864 | 12088990.5844 | 8250984.4778 | 36900236.1368 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 54176948.4888 | 79378749.0103 | 42169.6503 | 6.0509 | 8953.5789 | 13118.5664 | 182.5308 | 267.4397
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1197 | 23.5461 | 1.7273 | 4 | 8287.7893 | 11935.4003 | 168.9578 | 243.3193 | 125.4076 | 0 | 156.7033 | 3804739.3872 | 274072.5722 | 4256794.6118 | 3989793.8435 | 0 | 584313.785 | 0 | 5034788.5378 | 13099486.9983 | 8940669.0439 | 39984658.7797 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 57261371.1316 | 82463171.6532 | 56234.1325 | 6.9091 | 8287.7893 | 11935.4003 | 168.9578 | 243.3193
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4413 | 25.5412 | 1.922 | 4 | 7785.8441 | 11063.8826 | 158.725 | 225.5522 | 125.2942 | 0 | 162.2376 | 4027964.3773 | 289739.0532 | 4543333.5395 | 4328177.8477 | 0 | 558909.3215 | 0 | 5361768.4143 | 13950221.5641 | 9521312.8659 | 42581426.9834 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 59858139.3354 | 85059939.8569 | 74989.4209 | 7.6881 | 7785.8441 | 11063.8826 | 158.725 | 225.5522
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4723 | 27.2111 | 2.0917 | 4 | 7407.9094 | 10420.0871 | 151.0203 | 212.4276 | 125.1732 | 0 | 170.1296 | 4210113.3302 | 302439.2247 | 4779882.1364 | 4612309.2445 | 0 | 528230.961 | 0 | 5628860.2097 | 14645139.6277 | 9995608.7234 | 44702583.4576 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 61979295.8096 | 87181096.3311 | 100000 | 8.3666 | 7407.9094 | 10420.0871 | 151.0203 | 212.4276
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2038 | 28.5611 | 2.234 | 4 | 7123.5584 | 9943.8418 | 145.2234 | 202.7187 | 125.0586 | 0 | 193.5544 | 4354392.3214 | 312440.6606 | 4969073.9622 | 4842637.8511 | 0 | 495614.7467 | 0 | 5839922.2214 | 15194279.6873 | 10370408.0978 | 46378769.5484 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 63655481.9004 | 88857282.422 | 133352.1432 | 8.9359 | 7123.5584 | 9943.8418 | 145.2234 | 202.7187
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.842 | 29.6459 | 2.3511 | 4 | 6909.6698 | 9589.5005 | 140.863 | 195.4949 | 124.956 | 0 | 174.722 | 4468534.7025 | 320317.6337 | 5119866.3546 | 5028500.6022 | 0 | 464670.5159 | 0 | 6006737.0255 | 15628297.5891 | 10666634.234 | 47703558.6575 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 64980271.0095 | 90182071.531 | 177827.941 | 9.4043 | 6909.6698 | 9589.5005 | 140.863 | 195.4949
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.4398 | 30.4826 | 2.4443 | 4 | 6748.8197 | 9326.4617 | 137.5838 | 190.1325 | 124.8706 | 0 | 183.3158 | 4555540.9002 | 326302.0225 | 5235452.11 | 5172556.7943 | 0 | 436018.3371 | 0 | 6133089.364 | 15957040.4555 | 10891007.9953 | 48707007.979 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 65983720.3309 | 91185520.8525 | 237137.3706 | 9.7771 | 6748.8197 | 9326.4617 | 137.5838 | 190.1325
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2191 | 31.1259 | 2.5175 | 4 | 6627.9099 | 9130.5616 | 135.1189 | 186.1388 | 124.8013 | 0 | 192.756 | 4621810.3405 | 330845.795 | 5323912.3729 | 5283547.3791 | 0 | 411000.8282 | 0 | 6228735.5191 | 16205892.1315 | 11060854.3775 | 49466598.7439 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 66743311.0959 | 91945111.6174 | 316227.766 | 10.07 | 6627.9099 | 9130.5616 | 135.1189 | 186.1388
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.3339 | 31.6136 | 2.5742 | 4 | 6537.0405 | 8984.5744 | 133.2664 | 183.1627 | 124.7466 | 0 | 174.2013 | 4671693.0984 | 334257.5616 | 5390745.2877 | 5367830.0582 | 0 | 389777.7508 | 0 | 6300178.4651 | 16391772.0219 | 11187721.2222 | 50033975.466 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67310687.8179 | 92512488.3395 | 421696.5034 | 10.2968 | 6537.0405 | 8984.5744 | 133.2664 | 183.1627
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.9586 | 31.9872 | 2.618 | 4 | 6468.763 | 8875.3357 | 131.8745 | 180.9357 | 124.7035 | 0 | 179.6003 | 4709700.6022 | 336852.1281 | 5441812.045 | 5432478.8405 | 0 | 372505.0495 | 0 | 6354405.9794 | 16532860.8906 | 11284017.2742 | 50464632.8095 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67741345.1614 | 92943145.683 | 562341.3252 | 10.4721 | 6468.763 | 8875.3357 | 131.8745 | 180.9357
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1696 | 32.265 | 2.6512 | 4 | 6417.473 | 8793.8805 | 130.8289 | 179.2751 | 124.6707 | 0 | 187.9003 | 4737850.4632 | 338770.9158 | 5479715.9539 | 5480603.8426 | 0 | 358419.069 | 0 | 6394190.4954 | 16636372.0401 | 11354665.7607 | 50780588.5407 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 68057300.8926 | 93259101.4142 | 749894.2093 | 10.605 | 6417.473 | 8793.8805 | 130.8289 | 179.2751
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6396 | 32.8325 | 2.6965 | 4 | 6378.8187 | 8715.3599 | 130.0408 | 177.6744 | 124.6073 | 0 | 343.3399 | 4795185.4122 | 342682.6968 | 5556927.8766 | 5578842.8048 | 0 | 362023.4071 | 0 | 6487908.257 | 16880206.4317 | 11521087.7432 | 51524864.6294 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 68801576.9814 | 94003377.5029 | 1000000 | 10.7859 | 6378.8187 | 8715.3599 | 130.0408 | 177.6744
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3702 | 33.0008 | 2.7165 | 4 | 6349.5192 | 8668.8779 | 129.4435 | 176.7268 | 124.59 | 0 | 192.4445 | 4812170.4999 | 343843.797 | 5579779.2891 | 5607950.3876 | 0 | 353695.3109 | 0 | 6512001.3209 | 16942891.6419 | 11563871.6872 | 51716203.9346 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 68992916.2865 | 94194716.8081 | 1333521.4322 | 10.8658 | 6349.5192 | 8668.8779 | 129.4435 | 176.7268
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9233 | 33.1282 | 2.7316 | 4 | 6327.5255 | 8634.0277 | 128.9952 | 176.0163 | 124.5768 | 0 | 199.0718 | 4824995.6739 | 344720.0699 | 5597048.3022 | 5629973.7074 | 0 | 347276.7325 | 0 | 6530165.6495 | 16990151.4988 | 11596127.5106 | 51860459.1447 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69137171.4967 | 94338972.0182 | 1778279.41 | 10.9264 | 6327.5255 | 8634.0277 | 128.9952 | 176.0163
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3325 | 33.2223 | 2.7429 | 4 | 6311.0195 | 8607.9888 | 128.6587 | 175.4855 | 124.5669 | 0 | 174.7675 | 4834466.3822 | 345366.8938 | 5609808.5263 | 5646261.626 | 0 | 342280.8159 | 0 | 6543491.8553 | 17024823.5527 | 11619791.8998 | 51966291.5521 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69243003.904 | 94444804.4256 | 2371373.7057 | 10.9718 | 6311.0195 | 8607.9888 | 128.6587 | 175.4855
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6466 | 33.2946 | 2.7516 | 4 | 6298.634 | 8588.4023 | 128.4062 | 175.0862 | 124.5594 | 0 | 200.2115 | 4841727.3648 | 345862.6567 | 5619596.0041 | 5658763.3342 | 0 | 338529.0314 | 0 | 6553746.5726 | 17051504.2237 | 11638002.006 | 52047731.1936 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69324443.5456 | 94526244.0671 | 3162277.6602 | 11.0063 | 6298.634 | 8588.4023 | 128.4062 | 175.0862
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.446 | 33.0182 | 2.7405 | 4 | 6286.2924 | 8585.2749 | 128.1546 | 175.0224 | 124.5879 | 0 | 356.9126 | 4813908.9701 | 343962.0179 | 5582130.1511 | 5610955.6229 | 0 | 320133.2861 | 0 | 6501725.1188 | 16916155.0718 | 11545623.4287 | 51634593.6674 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 68911306.0194 | 94113106.5409 | 4216965.0343 | 10.9622 | 6286.2924 | 8585.2749 | 128.1546 | 175.0224
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.328 | 33.2213 | 2.7547 | 4 | 6279.1066 | 8566.3074 | 128.0081 | 174.6358 | 124.567 | 0 | 237.2454 | 4834355.754 | 345359.1199 | 5609663.4919 | 5646079.6393 | 0 | 324677.2754 | 0 | 6536452.7594 | 17006509.2691 | 11607292.025 | 51910389.3341 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69187101.686 | 94388902.2076 | 5623413.2519 | 11.0186 | 6279.1066 | 8566.3074 | 128.0081 | 174.6358
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.3849 | 33.4644 | 2.7704 | 4 | 6273.7694 | 8548.0085 | 127.8993 | 174.2627 | 124.5417 | 0 | 179.9857 | 4858767.5832 | 347025.8898 | 5642576.0863 | 5688141.029 | 0 | 331842.1986 | 0 | 6578657.5869 | 17116317.573 | 11682238.4487 | 52245566.3956 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69522278.7475 | 94724079.2691 | 7498942.0933 | 11.0814 | 6273.7694 | 8548.0085 | 127.8993 | 174.2627
1 | 4600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7092 | 33.5389 | 2.776 | 4 | 6269.9058 | 8539.5194 | 127.8205 | 174.0897 | 124.5338 | 0 | 177.8349 | 4866237.9111 | 347535.6239 | 5652657.2814 | 5701041.5165 | 0 | 332775.7454 | 0 | 6591096.7506 | 17148681.7251 | 11704327.6476 | 52344354.2016 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 69621066.5536 | 94822867.0751 | 10000000 | 11.104 | 6269.9058 | 8539.5194 | 127.8205 | 174.0897
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0443 | [19 empty] | 100 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7386 | [19 empty] | 133.3521 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.0494 | [19 empty] | 177.8279 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1387 | [19 empty] | 237.1374 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.538 | [19 empty] | 316.2278 | 0
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.25593 | 0.0047831 | 4 | 994538.0918 | 2346582.2603 | 20275.0042 | 47838.2534 | 99.1817 | 0 | 26.8852 | 136395.493 | 8470.8067 | 116453.3179 | 77491.3253 | 0 | 72985.1402 | 0 | 160600.4724 | 417849.4854 | 285190.8597 | 1275436.9005 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19027837.9424 | 44895602.6299 | 421.6965 | 0.019132 | 994538.0918 | 2346582.2603 | 20275.0042 | 47838.2534
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.50488 | 0.012549 | 4 | 395627.7765 | 910967.7498 | 8065.4074 | 18571.3098 | 109.4215 | 0 | 422.1157 | 233909.0782 | 15459.902 | 199053.8015 | 119918.9421 | 0 | 111727.2604 | 0 | 265226.9039 | 690065.9984 | 470984.2233 | 2106346.1098 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19858747.1517 | 45726511.8393 | 562.3413 | 0.050196 | 395627.7765 | 910967.7498 | 8065.4074 | 18571.3098
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.499 | 0.71671 | 0.023524 | 4 | 217493.5631 | 492407.024 | 4433.9005 | 10038.3832 | 113.7071 | 0 | 553.6904 | 306352.546 | 20785.32 | 262642.5237 | 155504.0046 | 0 | 130486.2464 | 0 | 341550.5498 | 888644.4691 | 606518.1099 | 2712483.7695 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 20464884.8114 | 46332649.4989 | 749.8942 | 0.094094 | 217493.5631 | 492407.024 | 4433.9005 | 10038.3832
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6379 | 1.0027 | 0.038976 | 4 | 136145.1629 | 302065.1981 | 2775.5033 | 6158.0076 | 117.1345 | 0 | 66.8051 | 394961.4482 | 27365.3401 | 342763.9012 | 203173.8786 | 0 | 153152.1229 | 0 | 437352.5095 | 1137901.5163 | 776641.1664 | 3473311.8831 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 21225712.9251 | 47093477.6126 | 1000 | 0.15591 | 136145.1629 | 302065.1981 | 2775.5033 | 6158.0076
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1654 | 1.3897 | 0.060263 | 4 | 92042.5074 | 199354.154 | 1876.411 | 4064.1041 | 119.8361 | 0 | 57.0655 | 503657.4773 | 35476.4051 | 444174.0123 | 267409.7326 | 0 | 181097.983 | 0 | 558408.0881 | 1452863.2999 | 991609.0556 | 4434696.054 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 22187097.0959 | 48054861.7834 | 1333.5214 | 0.24105 | 92042.5074 | 199354.154 | 1876.411 | 4064.1041
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1922 | 1.903 | 0.088697 | 4 | 65905.5319 | 138815.8008 | 1343.5734 | 2829.9479 | 121.8182 | 0 | 62.3391 | 634455.5933 | 45230.8117 | 570383.7094 | 352812.7373 | 0 | 214908.152 | 0 | 708938.4914 | 1844512.5314 | 1258917.7037 | 5630159.7302 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 23382560.7721 | 49250325.4597 | 1778.2794 | 0.35479 | 65905.5319 | 138815.8008 | 1343.5734 | 2829.9479
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8984 | 2.5982 | 0.1283 | 4 | 48517.328 | 98923.5526 | 989.0914 | 2016.6904 | 123.5859 | 0 | 84.7211 | 796547.8636 | 57365.0825 | 730873.6871 | 466508.2009 | 0 | 255913.2543 | 0 | 899811.1545 | 2341124.0473 | 1597865.2676 | 7146008.5577 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 24898409.5996 | 50766174.2871 | 2371.3737 | 0.51319 | 48517.328 | 98923.5526 | 989.0914 | 2016.6904
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4721 | 3.5144 | 0.1806 | 4 | 37077.2648 | 72886.0101 | 755.8702 | 1485.8799 | 124.8248 | 0 | 82.6693 | 991214.2372 | 71887.6254 | 929842.2924 | 617833.5187 | 0 | 305265.5563 | 0 | 1137256.8597 | 2958909.0654 | 2019516.2366 | 9031725.3916 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 26784126.4335 | 52651891.121 | 3162.2777 | 0.72239 | 37077.2648 | 72886.0101 | 755.8702 | 1485.8799
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.7964 | 4.6251 | 0.24862 | 4 | 29092.1837 | 55103.1775 | 593.0835 | 1123.3528 | 125.7058 | 0 | 92.0331 | 1208049.7156 | 88031.9196 | 1157589.4083 | 801933.4422 | 0 | 353911.6954 | 0 | 1407711.3106 | 3662576.0689 | 2499783.4254 | 11179586.986 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 28931988.0279 | 54799752.7154 | 4216.965 | 0.99449 | 29092.1837 | 55103.1775 | 593.0835 | 1123.3528
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9682 | 5.9543 | 0.3357 | 4 | 23352.5891 | 42616.7396 | 476.0741 | 868.7999 | 126.349 | 0 | 76.7587 | 1448094.9409 | 105850.7615 | 1416187.0016 | 1021995.672 | 0 | 400566.5168 | 0 | 1713151.0082 | 4457267.5077 | 3042176.6617 | 13605290.0703 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 31357691.1122 | 57225455.7998 | 5623.4133 | 1.3428 | 23352.5891 | 42616.7396 | 476.0741 | 868.7999
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3575 | 7.5969 | 0.44706 | 4 | 19131.5758 | 33597.1982 | 390.023 | 684.9243 | 126.8462 | 0 | 107.2046 | 1723836.7189 | 126254.9465 | 1720339.074 | 1293595.4611 | 0 | 450078.6945 | 0 | 2072500.909 | 5392222.237 | 3680302.4758 | 16459130.5168 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 34211531.5587 | 60079296.2463 | 7498.9421 | 1.7882 | 19131.5758 | 33597.1982 | 390.023 | 684.9243
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.0749 | 9.5811 | 0.58695 | 4 | 15972.387 | 26990.2122 | 325.6187 | 550.232 | 127.2282 | 0 | 94.3541 | 2034526.1571 | 149174.6601 | 2070731.7896 | 1621343.4582 | 0 | 500109.769 | 0 | 2486595.4752 | 6469611.3557 | 4415642.6875 | 19747735.3523 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 37500136.3942 | 63367901.0817 | 10000 | 2.3478 | 15972.387 | 26990.2122 | 325.6187 | 550.232
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.1781 | 11.9214 | 0.75875 | 4 | 13578.4771 | 22101.6374 | 276.8156 | 450.5718 | 127.5175 | 0 | 111.468 | 2377639.0944 | 174407.0687 | 2465844.331 | 2007711.3138 | 0 | 548280.5124 | 0 | 2953814.1049 | 7685218.3904 | 5245319.4669 | 23458234.2824 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 41210635.3244 | 67078400.0119 | 13335.2143 | 3.035 | 13578.4771 | 22101.6374 | 276.8156 | 450.5718
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4286 | 14.5536 | 0.96167 | 4 | 11753.1254 | 18477.8257 | 239.6034 | 376.6955 | 127.7182 | 0 | 132.649 | 2740616.374 | 201004.1882 | 2892144.3306 | 2442511.0798 | 0 | 589030.3253 | 0 | 3457469.4562 | 8995626.3006 | 6139699.7918 | 27458101.8465 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 45210502.8884 | 71078267.576 | 17782.7941 | 3.8467 | 11753.1254 | 18477.8257 | 239.6034 | 376.6955
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.3519 | 17.3488 | 1.1893 | 4 | 10361.0078 | 15798.4087 | 211.2232 | 322.0719 | 127.8264 | 0 | 113.3242 | 3105107.3811 | 227587.9477 | 3328339.5476 | 2904972.5702 | 0 | 616826.0472 | 0 | 3971305.0626 | 10332521.1462 | 7052157.9943 | 31538817.6969 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 49291218.7389 | 75158983.4264 | 23713.7371 | 4.7574 | 10361.0078 | 15798.4087 | 211.2232 | 322.0719
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.3117 | 20.1359 | 1.43 | 4 | 9302.5017 | 13824.776 | 189.6441 | 281.8368 | 127.8448 | 0 | 134.214 | 3450871.7736 | 252656.6578 | 3749585.8466 | 3367390.0423 | 0 | 627909.3662 | 0 | 4464881.3377 | 11616705.3677 | 7928640.1129 | 35458640.5048 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 53211041.5467 | 79078806.2343 | 31622.7766 | 5.7201 | 9302.5017 | 13824.776 | 189.6441 | 281.8368
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7324 | 22.7634 | 1.67 | 4 | 8500.5117 | 12372.8998 | 173.2944 | 252.2383 | 127.7896 | 0 | 158.5906 | 3763053.0369 | 275134.4225 | 4136309.3494 | 3805017.9344 | 0 | 622450.7077 | 0 | 4914766.5259 | 12787214.3431 | 8727536.5402 | 39031482.8601 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 56783883.9021 | 82651648.5896 | 42169.6503 | 6.6801 | 8500.5117 | 12372.8998 | 173.2944 | 252.2383
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.1555 | 25.1163 | 1.8965 | 4 | 7894.5949 | 11304.576 | 160.942 | 230.4591 | 127.6858 | 0 | 153.3017 | 4032575.869 | 294398.6088 | 4475262.9466 | 4198651.2009 | 0 | 603157.4529 | 0 | 5305577.9705 | 13804025.5555 | 9421531.086 | 42135180.69 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 59887581.7319 | 85755346.4194 | 56234.1325 | 7.5859 | 7894.5949 | 11304.576 | 160.942 | 230.4591
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.3501 | 27.1421 | 2.1004 | 4 | 7437.7016 | 10516.5606 | 151.6276 | 214.3943 | 127.5584 | 0 | 175.2115 | 4257739.423 | 310376.4257 | 4762201.9483 | 4539133.6335 | 0 | 574704.1997 | 0 | 5633220.6958 | 14656484.718 | 10003351.9807 | 44737213.0247 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 62489614.0666 | 88357378.7541 | 74989.4209 | 8.4017 | 7437.7016 | 10516.5606 | 151.6276 | 214.3943
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2024 | 28.8203 | 2.2765 | 4 | 7093.598 | 9934.381 | 144.6126 | 202.5258 | 127.4276 | 0 | 184.7662 | 4439755.9317 | 323206.6335 | 4996783.7061 | 4822409.7323 | 0 | 541206.9582 | 0 | 5898111.5551 | 15345676.3973 | 10473739.4633 | 46840890.3774 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 64593291.4193 | 90461056.1068 | 100000 | 9.1059 | 7093.598 | 9934.381 | 144.6126 | 202.5258
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7808 | 30.1752 | 2.4235 | 4 | 6834.6257 | 9503.023 | 139.3331 | 193.732 | 127.3059 | 0 | 166.4265 | 4583886.3665 | 333306.9484 | 5184277.8496 | 5052009.8665 | 0 | 506613.3689 | 0 | 6107436.816 | 15890297.7876 | 10845454.753 | 48503283.7566 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 66255684.7985 | 92123449.486 | 133352.1432 | 9.6941 | 6834.6257 | 9503.023 | 139.3331 | 193.732
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.2218 | 31.2462 | 2.5432 | 4 | 6639.8039 | 9182.6601 | 135.3614 | 187.2009 | 127.1999 | 0 | 187.6192 | 4696100.6008 | 341131.7925 | 5331359.399 | 5234110.5149 | 0 | 473626.597 | 0 | 6269768.2727 | 16312650.9391 | 11133719.4574 | 49792467.5735 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 67544868.6154 | 93412633.3029 | 177827.941 | 10.1727 | 6639.8039 | 9182.6601 | 135.3614 | 187.2009
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7003 | 32.0803 | 2.6386 | 4 | 6493.2838 | 8944.2058 | 132.3744 | 182.3397 | 127.1113 | 0 | 174.3441 | 4782465.2949 | 347129.7196 | 5445239.8862 | 5376311.3894 | 0 | 443914.9543 | 0 | 6394073.8853 | 16636068.6447 | 11354458.6871 | 50779662.4616 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 68532063.5035 | 94399828.191 | 237137.3706 | 10.5543 | 6493.2838 | 8944.2058 | 132.3744 | 182.3397
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.3682 | 32.717 | 2.7131 | 4 | 6383.1172 | 8766.6749 | 130.1285 | 178.7205 | 127.0403 | 0 | 180.8786 | 4847807.6217 | 351652.9723 | 5531804.1988 | 5485110.696 | 0 | 418014.5674 | 0 | 6487412.1219 | 16878915.5901 | 11520206.7172 | 51520924.4855 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69273325.5274 | 95141090.2149 | 316227.766 | 10.8526 | 6383.1172 | 8766.6749 | 130.1285 | 178.7205
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.3996 | 33.2 | 2.7708 | 4 | 6300.3028 | 8634.2731 | 128.4402 | 176.0213 | 126.9843 | 0 | 176.6258 | 4897026.215 | 355051.1487 | 5597247.9576 | 5567700.0685 | 0 | 396211.0027 | 0 | 6557162.1931 | 17060390.9676 | 11644067.3914 | 52074856.9447 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69827257.9866 | 95695022.6741 | 421696.5034 | 11.0832 | 6300.3028 | 8634.2731 | 128.4402 | 176.0213
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.9484 | 33.5668 | 2.8151 | 4 | 6238.0644 | 8535.3025 | 127.1714 | 174.0037 | 126.9407 | 0 | 168.311 | 4934209.8748 | 357612.7788 | 5646835.5735 | 5630364.1753 | 0 | 378427.573 | 0 | 6609505.4904 | 17196577.4901 | 11737017.4913 | 52490550.4474 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 70242951.4893 | 96110716.1768 | 562341.3252 | 11.2604 | 6238.0644 | 8535.3025 | 127.1714 | 174.0037
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7723 | 34.2383 | 2.8716 | 4 | 6190.6458 | 8442.6727 | 126.2047 | 172.1153 | 126.8689 | 0 | 200.4938 | 5002150.9916 | 362306.572 | 5737318.4235 | 5744904.3292 | 0 | 380213.4667 | 0 | 6718488.5754 | 17480129.1216 | 11930547.3063 | 53356058.7863 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71108459.8282 | 96976224.5157 | 749894.2093 | 11.4864 | 6190.6458 | 8442.6727 | 126.2047 | 172.1153
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7003 | 34.4589 | 2.8983 | 4 | 6155.0423 | 8386.324 | 125.4789 | 170.9666 | 126.8459 | 0 | 177.249 | 5024388.8174 | 363842.6954 | 5766967.5439 | 5782538.164 | 0 | 369346.9314 | 0 | 6749762.8193 | 17561498.2891 | 11986083.435 | 53604428.6954 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71356829.7373 | 97224594.4248 | 1000000 | 11.5932 | 6155.0423 | 8386.324 | 125.4789 | 170.9666
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4165 | 34.629 | 2.9188 | 4 | 6128.3077 | 8343.9504 | 124.9338 | 170.1027 | 126.828 | 0 | 189.8624 | 5041498.6461 | 365023.7616 | 5789803.9821 | 5811567.9868 | 0 | 361031.2055 | 0 | 6773880.977 | 17624248.7881 | 12028911.94 | 53795967.2872 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71548368.3291 | 97416133.0166 | 1333521.4322 | 11.6751 | 6128.3077 | 8343.9504 | 124.9338 | 170.1027
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.9307 | 34.7511 | 2.9339 | 4 | 6108.2381 | 8312.4626 | 124.5247 | 169.4608 | 126.815 | 0 | 189.5791 | 5053751.7364 | 365869.1078 | 5806171.554 | 5832398.0113 | 0 | 354355.9171 | 0 | 6790893.0674 | 17668510.7576 | 12059121.6437 | 53931071.7953 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71683472.8372 | 97551237.5247 | 1778279.41 | 11.7355 | 6108.2381 | 8312.4626 | 124.5247 | 169.4608
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3445 | 34.8492 | 2.9457 | 4 | 6093.1753 | 8288.5888 | 124.2176 | 168.9741 | 126.8046 | 0 | 177.2174 | 5063595.8097 | 366547.997 | 5819328.8651 | 5849156.4206 | 0 | 349501.0332 | 0 | 6804770.749 | 17704617.6384 | 12083765.3317 | 54041283.8447 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71793684.8866 | 97661449.5741 | 2371373.7057 | 11.7826 | 6093.1753 | 8288.5888 | 124.2176 | 168.9741
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6345 | 34.918 | 2.9542 | 4 | 6081.8724 | 8270.908 | 123.9872 | 168.6136 | 126.7972 | 0 | 175.4543 | 5070486.1884 | 367023.0282 | 5828542.8103 | 5860899.8185 | 0 | 345589.6324 | 0 | 6814291.1763 | 17729387.8375 | 12100671.5016 | 54116891.9933 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71869293.0352 | 97737057.7227 | 3162277.6602 | 11.817 | 6081.8724 | 8270.908 | 123.9872 | 168.6136
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8586 | 34.9711 | 2.9608 | 4 | 6073.392 | 8257.5904 | 123.8143 | 168.3421 | 126.7915 | 0 | 183.0564 | 5075805.1922 | 367389.6485 | 5835657.8021 | 5869972.215 | 0 | 342679.6691 | 0 | 6821686.7655 | 17748629.6434 | 12113804.4295 | 54175625.3653 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71928026.4073 | 97795791.0948 | 4216965.0343 | 11.8431 | 6073.392 | 8257.5904 | 123.8143 | 168.3421
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0218 | 35.0097 | 2.9656 | 4 | 6067.0302 | 8247.6576 | 123.6846 | 168.1397 | 126.7874 | 0 | 191.1259 | 5079674.7491 | 367656.315 | 5840835.3014 | 5876576.4454 | 0 | 340425.7167 | 0 | 6827015.7258 | 17762494.505 | 12123267.4824 | 54217946.2408 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 71970347.2827 | 97838111.9703 | 5623413.2519 | 11.8625 | 6067.0302 | 8247.6576 | 123.6846 | 168.1397
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.1487 | 35.0398 | 2.9693 | 4 | 6062.2581 | 8240.1661 | 123.5873 | 167.9869 | 126.7842 | 0 | 174.2065 | 5082682.0045 | 367863.5334 | 5844859.7463 | 5881711.1894 | 0 | 338766.2467 | 0 | 6831194.2609 | 17773366.1963 | 12130687.6351 | 54251130.8126 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 72003531.8545 | 97871296.542 | 7498942.0933 | 11.8773 | 6062.2581 | 8240.1661 | 123.5873 | 167.9869
1 | 4700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2413 | 35.0617 | 2.9721 | 4 | 6058.6787 | 8234.5751 | 123.5144 | 167.873 | 126.7818 | 0 | 169.6364 | 5084876.0992 | 368014.7039 | 5847796.433 | 5885458.8375 | 0 | 337489.2646 | 0 | 6834217.7819 | 17781232.7777 | 12136056.7386 | 54275142.6363 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 72027543.6782 | 97895308.3658 | 10000000 | 11.8883 | 6058.6787 | 8234.5751 | 123.5144 | 167.873
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2214 | [19 empty] | 100 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3225 | [19 empty] | 133.3521 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5387 | [19 empty] | 177.8279 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3773 | [19 empty] | 237.1374 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6388 | [19 empty] | 316.2278 | 0
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.36801 | 0.0067059 | 4 | 742526.4902 | 1732024.9784 | 15137.4068 | 35309.6719 | 106.0013 | 0 | 308.4758 | 183774.6315 | 11890.4906 | 154944.5028 | 96082.8328 | 0 | 96788.9504 | 0 | 211957.7492 | 551470.5848 | 376390.0057 | 1683299.7479 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19917249.5706 | 46459182.5513 | 421.6965 | 0.026824 | 742526.4902 | 1732024.9784 | 15137.4068 | 35309.6719
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7016 | 0.5332 | 0.015185 | 4 | 336235.3824 | 773223.7588 | 6854.6131 | 15763.2122 | 111.4016 | 0 | 420.9993 | 245972.8769 | 16447.5547 | 207638.9555 | 123727.7536 | 0 | 112779.8474 | 0 | 275561.1253 | 716953.5228 | 489335.5112 | 2188417.1474 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20422366.9701 | 46964299.9508 | 562.3413 | 0.060738 | 336235.3824 | 773223.7588 | 6854.6131 | 15763.2122
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5573 | 0.75196 | 0.027421 | 4 | 191813.22 | 433795.1332 | 3910.3719 | 8843.5005 | 115.6972 | 0 | 582.9322 | 320514.8153 | 22000.9081 | 272545.7012 | 159822.5231 | 0 | 130821.5459 | 0 | 353225.1425 | 919019.3643 | 627249.6001 | 2805199.6003 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 21039149.4231 | 47581082.4037 | 749.8942 | 0.10969 | 191813.22 | 433795.1332 | 3910.3719 | 8843.5005
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7279 | 1.0558 | 0.044728 | 4 | 122064.7222 | 270415.8289 | 2488.4545 | 5512.7924 | 119.2359 | 0 | 81.7899 | 414369.6759 | 29067.8202 | 356685.6309 | 209718.4372 | 0 | 154095.6609 | 0 | 453935.5178 | 1181047.1025 | 806088.9155 | 3605008.7611 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 21838958.5838 | 48380891.5645 | 1000 | 0.17891 | 122064.7222 | 270415.8289 | 2488.4545 | 5512.7924
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2775 | 1.4618 | 0.068503 | 4 | 83339.4918 | 180203.1307 | 1698.9883 | 3673.6846 | 121.9829 | 0 | 63.0838 | 528097.3538 | 37677.7796 | 461838.9898 | 276336.2865 | 0 | 181942.1046 | 0 | 579498.0806 | 1507735.1342 | 1029060.2099 | 4602185.9389 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 22836135.7617 | 49378068.7424 | 1333.5214 | 0.27401 | 83339.4918 | 180203.1307 | 1698.9883 | 3673.6846
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3238 | 1.9962 | 0.099945 | 4 | 60190.0253 | 126581.7011 | 1227.0551 | 2580.5392 | 123.9839 | 0 | 67.3024 | 663730.6648 | 47921.5377 | 591766.8819 | 363176.914 | 0 | 215296.8994 | 0 | 733938.2302 | 1909556.7235 | 1303311.7012 | 5828699.5527 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 24062649.3755 | 50604582.3561 | 1778.2794 | 0.39978 | 60190.0253 | 126581.7011 | 1227.0551 | 2580.5392
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0912 | 2.7338 | 0.14452 | 4 | 44386.5867 | 90300.8996 | 904.8806 | 1840.906 | 125.8185 | 0 | 78.3009 | 835627.0745 | 61004.6792 | 760026.6898 | 483592.264 | 0 | 256983.4847 | 0 | 934921.335 | 2432473.5349 | 1660213.1699 | 7424842.232 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 25658792.0548 | 52200725.0354 | 2371.3737 | 0.57808 | 44386.5867 | 90300.8996 | 904.8806 | 1840.906
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7279 | 3.6985 | 0.20291 | 4 | 34033.8777 | 66735.367 | 693.8266 | 1360.4907 | 127.0861 | 0 | 89.2933 | 1040157.9051 | 76492.9566 | 967070.9839 | 641239.765 | 0 | 306565.0516 | 0 | 1182295.3983 | 3076090.1042 | 2099494.7034 | 9389406.868 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 27623356.6908 | 54165289.6715 | 3162.2777 | 0.81164 | 34033.8777 | 66735.367 | 693.8266 | 1360.4907
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5838 | 4.9873 | 0.28073 | 4 | 26806.4254 | 50443.1814 | 546.4852 | 1028.3525 | 128.0585 | 0 | 71.777 | 1289976.6296 | 95348.6418 | 1227546.2571 | 851028.1932 | 0 | 367634.9064 | 0 | 1494298.505 | 3887858.1871 | 2653543.1002 | 11867234.4204 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 30101184.2432 | 56643117.2238 | 4216.965 | 1.1229 | 26806.4254 | 50443.1814 | 546.4852 | 1028.3525
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4271 | 6.54 | 0.38059 | 4 | 21617.411 | 39052.0829 | 440.7002 | 796.1295 | 128.7443 | 0 | 77.1019 | 1566760.0769 | 116173.4251 | 1524058.4348 | 1103934.5153 | 0 | 427348.2877 | 0 | 1847927.1485 | 4807927.3785 | 3281509.2289 | 14675638.4958 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 32909588.3185 | 59451521.2992 | 5623.4133 | 1.5224 | 21617.411 | 39052.0829 | 440.7002 | 796.1295
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.148 | 8.3267 | 0.50543 | 4 | 17786.8456 | 30915.2805 | 362.6089 | 630.2498 | 129.2301 | 0 | 102.4028 | 1862279.2485 | 138340.3316 | 1848301.0763 | 1394963.2353 | 0 | 479236.2548 | 0 | 2232016.8572 | 5807250.0127 | 3963567.4607 | 17725954.4771 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 35959904.2999 | 62501837.2806 | 7498.9421 | 2.0217 | 17786.8456 | 30915.2805 | 362.6089 | 630.2498
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.2675 | 10.4859 | 0.662 | 4 | 14909.3128 | 24932.7249 | 303.9465 | 508.2873 | 129.6042 | 0 | 87.3326 | 2195634.4547 | 163271.6473 | 2222096.598 | 1746662.2688 | 0 | 531901.938 | 0 | 2675231.0936 | 6960402.5403 | 4750617.7557 | 21245818.2965 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 39479768.1193 | 66021701.0999 | 10000 | 2.648 | 14909.3128 | 24932.7249 | 303.9465 | 508.2873
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.7339 | 13.0028 | 0.85279 | 4 | 12724.1994 | 20505.0887 | 259.4 | 418.024 | 129.8827 | 0 | 91.2452 | 2559774.998 | 190416.2747 | 2638914.8559 | 2156688.5245 | 0 | 580905.7608 | 0 | 3169413.1614 | 8246162.9099 | 5628175.6277 | 25170452.1129 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 43404401.9357 | 69946334.9164 | 13335.2143 | 3.4112 | 12724.1994 | 20505.0887 | 259.4 | 418.024
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.301 | 15.8074 | 1.0762 | 4 | 11057.0954 | 17222.9443 | 225.4138 | 351.113 | 130.0682 | 0 | 118.8333 | 2941776.8715 | 218780.1256 | 3084806.9195 | 2613882.4462 | 0 | 621144.7976 | 0 | 3697352.5526 | 9619752.9106 | 6565679.0276 | 29363175.6513 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 47597125.474 | 74139058.4547 | 17782.7941 | 4.3047 | 11057.0954 | 17222.9443 | 225.4138 | 351.113
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.4117 | 18.7433 | 1.3237 | 4 | 9786.0824 | 14799.0675 | 199.5025 | 301.699 | 130.1559 | 0 | 133.5837 | 3320300.9722 | 246739.08 | 3535003.097 | 3093311.2501 | 0 | 646443.4826 | 0 | 4228301.174 | 11001172.3108 | 7508526.1536 | 33579797.5204 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 51813747.3432 | 78355680.3239 | 23713.7371 | 5.2946 | 9786.0824 | 14799.0675 | 199.5025 | 301.699
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.4197 | 21.6312 | 1.5819 | 4 | 8820.1742 | 13014.8272 | 179.8112 | 265.3249 | 130.1516 | 0 | 141.1774 | 3674948.7584 | 272760.611 | 3964420.1804 | 3566305.2508 | 0 | 653688.6197 | 0 | 4731528.134 | 12310465.6347 | 8402145.7504 | 37576262.9395 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 55810212.7623 | 82352145.7429 | 31622.7766 | 6.3276 | 8820.1742 | 13014.8272 | 179.8112 | 265.3249
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7876 | 24.326 | 1.8364 | 4 | 8088.5789 | 11701.7997 | 164.8966 | 238.557 | 130.0756 | 0 | 156.7045 | 3992239.4655 | 295864.0294 | 4355062.5177 | 4009361.4614 | 0 | 644087.9657 | 0 | 5185680.0214 | 13492075.6865 | 9208618.8905 | 41182990.038 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 59416939.8608 | 85958872.8414 | 42169.6503 | 7.3458 | 8088.5789 | 11701.7997 | 164.8966 | 238.557
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.1102 | 26.7239 | 2.0745 | 4 | 7535.859 | 10734.4768 | 153.6287 | 218.8368 | 129.9544 | 0 | 147.6819 | 4264736.4974 | 315548.4433 | 4695639.3959 | 4405300.8569 | 0 | 621169.1513 | 0 | 5577933.7945 | 14512639.5417 | 9905174.6921 | 44298142.373 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 62532092.1958 | 89074025.1765 | 56234.1325 | 8.2979 | 7535.859 | 10734.4768 | 153.6287 | 218.8368
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1345 | 28.7661 | 2.2866 | 4 | 7118.9974 | 10020.8504 | 145.1304 | 204.2886 | 129.8142 | 0 | 153.4917 | 4490130.5448 | 331706.093 | 4981054.9742 | 4743925.8158 | 0 | 589266.08 | 0 | 5903072.568 | 15358583.9352 | 10482549.1231 | 46880289.134 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 65114238.9568 | 91656171.9375 | 74989.4209 | 9.1465 | 7118.9974 | 10020.8504 | 145.1304 | 204.2886
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8313 | 30.4539 | 2.4687 | 4 | 6804.942 | 9492.7542 | 138.7279 | 193.5226 | 129.6739 | 0 | 179.9586 | 4672068.807 | 344656.7099 | 5214026.1998 | 5024924.3014 | 0 | 553269.4238 | 0 | 6165488.7223 | 16041336.9399 | 10948542.078 | 48964313.1821 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 67198263.0048 | 93740195.9855 | 100000 | 9.8749 | 6804.942 | 9492.7542 | 138.7279 | 193.5226
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2487 | 31.8076 | 2.6198 | 4 | 6568.4949 | 9101.2772 | 133.9077 | 185.5418 | 129.546 | 0 | 179.3858 | 4815283.5331 | 354788.1703 | 5399110.6071 | 5251107.5508 | 0 | 516654.731 | 0 | 6371408.391 | 16577097.6778 | 11314209.7904 | 50599660.4515 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 68833610.2742 | 95375543.2549 | 133352.1432 | 10.4794 | 6568.4949 | 9101.2772 | 133.9077 | 185.5418
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.5406 | 32.8724 | 2.7421 | 4 | 6390.5513 | 8810.3737 | 130.28 | 179.6114 | 129.4359 | 0 | 209.1719 | 4926296.4289 | 362600.9238 | 5543649.8939 | 5429559.7879 | 0 | 482116.0395 | 0 | 6530246.9989 | 16990363.1532 | 11596271.9691 | 51861105.1951 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 70095055.0178 | 96636987.9985 | 177827.941 | 10.9685 | 6390.5513 | 8810.3737 | 130.28 | 179.6114
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8929 | 33.6992 | 2.8393 | 4 | 6256.6757 | 8593.7005 | 127.5508 | 175.1942 | 129.3447 | 0 | 170.1017 | 5011526.1779 | 368573.7604 | 5655275.7711 | 5568471.2195 | 0 | 451274.139 | 0 | 6651497.2165 | 17305831.3477 | 11811585.4941 | 52824035.1264 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71057984.9491 | 97599917.9298 | 237137.3706 | 11.3571 | 6256.6757 | 8593.7005 | 127.5508 | 175.1942
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4682 | 34.3314 | 2.9152 | 4 | 6155.9822 | 8432.1851 | 125.498 | 171.9015 | 129.2717 | 0 | 180.4282 | 5076132.9389 | 373086.0463 | 5740282.24 | 5674899.3691 | 0 | 424660.8794 | 0 | 6742733.9747 | 17543210.6772 | 11973601.7641 | 53548607.8897 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71782557.7124 | 98324490.6931 | 316227.766 | 11.6606 | 6155.9822 | 8432.1851 | 125.498 | 171.9015
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9 | 35.1726 | 2.9946 | 4 | 6080.0383 | 8295.8326 | 123.9498 | 169.1218 | 129.1762 | 0 | 181.2655 | 5161528.2162 | 379044.2295 | 5852925.7967 | 5816613.9337 | 0 | 417085.269 | 0 | 6874607.0036 | 17886317.2476 | 12207779.0486 | 54595900.7449 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72829850.5677 | 99371783.5484 | 421696.5034 | 11.9785 | 6080.0383 | 8295.8326 | 123.9498 | 169.1218
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.642 | 35.6008 | 3.0439 | 4 | 6022.3157 | 8202.2581 | 122.7731 | 167.2141 | 129.1317 | 0 | 190.6115 | 5204841.5494 | 382072.3405 | 5910040.1099 | 5888661.3121 | 0 | 401393.133 | 0 | 6936933.2935 | 18048477.4691 | 12318456.7318 | 55090875.9392 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 73324825.762 | 99866758.7427 | 562341.3252 | 12.1755 | 6022.3157 | 8202.2581 | 122.7731 | 167.2141
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.8381 | 35.8943 | 3.0797 | 4 | 5978.941 | 8133.5124 | 121.8888 | 165.8127 | 129.1008 | 0 | 194.4802 | 5234411.4285 | 384136.787 | 5949108.8411 | 5938079.755 | 0 | 387529.2983 | 0 | 6978373.7829 | 18156297.1217 | 12392045.8602 | 55419982.8747 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 73653932.6974 | 100195865.6781 | 749894.2093 | 12.3189 | 5978.941 | 8133.5124 | 121.8888 | 165.8127
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7271 | 36.1121 | 3.1068 | 4 | 5946.3581 | 8082.1815 | 121.2246 | 164.7662 | 129.0775 | 0 | 180.0563 | 5256301.2079 | 385663.5728 | 5978070.3741 | 5974783.8489 | 0 | 376456.779 | 0 | 7008797.5552 | 18235453.5366 | 12446071.7398 | 55661598.6142 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 73895548.437 | 100437481.4177 | 1000000 | 12.427 | 5946.3581 | 8082.1815 | 121.2246 | 164.7662
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4117 | 36.2797 | 3.1274 | 4 | 5921.89 | 8043.5894 | 120.7257 | 163.9794 | 129.0595 | 0 | 183.6511 | 5273105.1219 | 386834.7881 | 6000325.9296 | 6003029.7016 | 0 | 367978.0254 | 0 | 7032196.691 | 18296333.288 | 12487623.4211 | 55847426.9666 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74081376.7893 | 100623309.77 | 1333521.4322 | 12.5098 | 5921.89 | 8043.5894 | 120.7257 | 163.9794
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.9038 | 36.4 | 3.1427 | 4 | 5903.521 | 8014.8979 | 120.3513 | 163.3945 | 129.0465 | 0 | 204.8796 | 5285156.9327 | 387674.3135 | 6016300.3604 | 6023325.7809 | 0 | 361198.1532 | 0 | 7048725.6609 | 18339338.2772 | 12516975.2099 | 55978694.6887 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74212644.5114 | 100754577.4921 | 1778279.41 | 12.5709 | 5903.521 | 8014.8979 | 120.3513 | 163.3945
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2935 | 36.4953 | 3.1545 | 4 | 5889.7341 | 7993.2041 | 120.0702 | 162.9523 | 129.0361 | 0 | 170.7076 | 5294685.2173 | 388337.795 | 6028937.0172 | 6039393.8128 | 0 | 356200.3456 | 0 | 7061946.1333 | 18373735.2345 | 12540451.84 | 56083687.3957 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74317637.2185 | 100859570.1992 | 2371373.7057 | 12.6182 | 5889.7341 | 7993.2041 | 120.0702 | 162.9523
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.5714 | 36.5632 | 3.1632 | 4 | 5879.3883 | 7977.0875 | 119.8593 | 162.6237 | 129.0287 | 0 | 158.8072 | 5301468.932 | 388810.0079 | 6037937.8905 | 6050845.8623 | 0 | 352237.4968 | 0 | 7071207.0739 | 18397830.3023 | 12556897.2189 | 56157234.7847 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74391184.6075 | 100933117.5882 | 3162277.6602 | 12.6529 | 5879.3883 | 7977.0875 | 119.8593 | 162.6237
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7929 | 36.6173 | 3.1699 | 4 | 5871.6258 | 7964.8821 | 119.701 | 162.3749 | 129.0228 | 0 | 183.4074 | 5306872.6655 | 389186.0825 | 6045109.9687 | 6059975.1141 | 0 | 349358.0267 | 0 | 7078695.7244 | 18417314.2349 | 12570195.4033 | 56216707.2201 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74450657.0429 | 100992590.0236 | 4216965.0343 | 12.6797 | 5871.6258 | 7964.8821 | 119.701 | 162.3749
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9392 | 36.653 | 3.1747 | 4 | 5865.8025 | 7955.9221 | 119.5823 | 162.1922 | 129.0189 | 0 | 168.8243 | 5310439.1744 | 389434.2376 | 6049844.9936 | 6066004.457 | 0 | 346976.382 | 0 | 7083452.7055 | 18429690.9237 | 12578642.7477 | 56254485.6215 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74488435.4443 | 101030368.425 | 5623413.2519 | 12.6988 | 5865.8025 | 7955.9221 | 119.5823 | 162.1922
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0707 | 36.6851 | 3.1786 | 4 | 5861.4342 | 7948.9973 | 119.4933 | 162.0511 | 129.0153 | 0 | 170.9785 | 5313643.3565 | 389657.1716 | 6054099.4612 | 6071423.0295 | 0 | 345396.7429 | 0 | 7087945.7071 | 18441380.7922 | 12586621.3231 | 56290167.5841 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74524117.4068 | 101066050.3875 | 7498942.0933 | 12.7143 | 5861.4342 | 7948.9973 | 119.4933 | 162.0511
1 | 4800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1561 | 36.706 | 3.1813 | 4 | 5858.1577 | 7943.9317 | 119.4265 | 161.9478 | 129.0131 | 0 | 173.1057 | 5315722.4454 | 389801.8023 | 6056860.5957 | 6074940.4665 | 0 | 344071.3102 | 0 | 7090744.6819 | 18448663.1505 | 12591591.6823 | 56312396.1348 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 74546345.9575 | 101088278.9382 | 10000000 | 12.7252 | 5858.1577 | 7943.9317 | 119.4265 | 161.9478
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2165 | [19 empty] | 100 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4896 | [19 empty] | 133.3521 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1769 | [19 empty] | 177.8279 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3476 | [19 empty] | 237.1374 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7263 | [19 empty] | 316.2278 | 0
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.38675 | 0.0084811 | 4 | 603161.4156 | 1405664.5196 | 12296.2613 | 28656.3725 | 107.822 | 0 | 325.8883 | 192466.5353 | 12585.5364 | 161012.2087 | 98539.3012 | 0 | 97323.9427 | 0 | 219151.7345 | 570187.859 | 389164.93 | 1740432.0479 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20461790.7423 | 47686096.1434 | 421.6965 | 0.033924 | 603161.4156 | 1405664.5196 | 12296.2613 | 28656.3725
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7405 | 0.55728 | 0.017921 | 4 | 292623.5997 | 672409.341 | 5965.5279 | 13707.9739 | 113.2548 | 0 | 413.9113 | 256490.6546 | 17336.2441 | 214828.801 | 126625.8844 | 0 | 112742.2429 | 0 | 283929.2925 | 738725.7772 | 504195.5223 | 2254874.419 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20976233.1134 | 48200538.5145 | 562.3413 | 0.071683 | 292623.5997 | 672409.341 | 5965.5279 | 13707.9739
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 0.7936 | 0.03164 | 4 | 170963.5108 | 386070.2348 | 3485.3224 | 7870.5639 | 117.7615 | 0 | 572.5973 | 336781.7415 | 23401.8373 | 284139.3459 | 165157.7553 | 0 | 132030.8251 | 0 | 367189.487 | 955351.7242 | 652047.1823 | 2916099.8985 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 21637458.593 | 48861763.994 | 749.8942 | 0.12656 | 170963.5108 | 386070.2348 | 3485.3224 | 7870.5639
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8205 | 1.1117 | 0.050878 | 4 | 110382.4058 | 244153.806 | 2250.2946 | 4977.4056 | 121.3412 | 0 | 80.7757 | 434646.2289 | 30876.4685 | 371152.1291 | 216720.9512 | 0 | 155083.6315 | 0 | 471306.9696 | 1226244.0566 | 836936.7654 | 3742967.2009 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 22464325.8953 | 49688631.2964 | 1000 | 0.20351 | 110382.4058 | 244153.806 | 2250.2946 | 4977.4056
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 1.5349 | 0.07709 | 4 | 76174.4701 | 164462.4108 | 1552.9196 | 3352.7887 | 124.1235 | 0 | 77.5369 | 552705.7781 | 39933.5764 | 479520.7947 | 284578.1492 | 0 | 182580.0939 | 0 | 600334.173 | 1561946.3727 | 1066060.4941 | 4767659.4321 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 23489018.1265 | 50713323.5276 | 1333.5214 | 0.30836 | 76174.4701 | 164462.4108 | 1552.9196 | 3352.7887
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4869 | 2.1028 | 0.11226 | 4 | 55192.1289 | 115820.6753 | 1125.1662 | 2361.1611 | 126.168 | 0 | 77.9469 | 696596.9335 | 50975.0023 | 615948.0144 | 376868.5902 | 0 | 216767.3087 | 0 | 763290.7811 | 1985926.0401 | 1355435.329 | 6061807.9993 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 24783166.6938 | 52007472.0949 | 1778.2794 | 0.44903 | 55192.1289 | 115820.6753 | 1125.1662 | 2361.1611
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.281 | 2.8724 | 0.16157 | 4 | 40890.9768 | 83015.319 | 833.6179 | 1692.3796 | 128.0471 | 0 | 77.4317 | 875466.7995 | 64792.436 | 789488.1038 | 500388.1939 | 0 | 257824.0843 | 0 | 970304.2508 | 2524532.6238 | 1723045.3897 | 7705841.8817 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 26427200.5761 | 53651505.9772 | 2371.3737 | 0.64628 | 40890.9768 | 83015.319 | 833.6179 | 1692.3796
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9863 | 3.8881 | 0.22627 | 4 | 31456.5318 | 61535.3615 | 641.2839 | 1254.4816 | 129.3454 | 0 | 81.1631 | 1090157.4012 | 81284.449 | 1004949.9792 | 663761.6383 | 0 | 307765.3492 | 0 | 1227688.3386 | 3194193.2236 | 2180102.5092 | 9749902.8883 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 28471261.5827 | 55695566.9838 | 3162.2777 | 0.9051 | 31456.5318 | 61535.3615 | 641.2839 | 1254.4816
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9025 | 5.2371 | 0.31247 | 4 | 24831.6282 | 46613.2842 | 506.2263 | 950.2748 | 130.3359 | 0 | 90.3765 | 1351119.1709 | 101278.1878 | 1274485.0386 | 880766.7 | 0 | 368462.1404 | 0 | 1550683.3827 | 4034560.0728 | 2753670.1516 | 12315024.8448 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 31036383.5392 | 58260688.9403 | 4216.965 | 1.2499 | 24831.6282 | 46613.2842 | 506.2263 | 950.2748
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4212 | 7.0274 | 0.42677 | 4 | 20069.1284 | 36017.0541 | 409.1363 | 734.2564 | 131.0903 | 0 | 73.5383 | 1668477.6484 | 125509.597 | 1611637.3321 | 1168602.1428 | 0 | 442523.884 | 0 | 1956532.7357 | 5090496.8381 | 3474368.6913 | 15538148.8694 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 34259507.5638 | 61483812.9649 | 5623.4133 | 1.7071 | 20069.1284 | 36017.0541 | 409.1363 | 734.2564
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0265 | 9.1173 | 0.57008 | 4 | 16577.3422 | 28516.1126 | 337.9515 | 581.3395 | 131.6112 | 0 | 70.0344 | 2010113.1654 | 151500.3684 | 1984133.1835 | 1504422.8241 | 0 | 510258.9076 | 0 | 2402567.0951 | 6250986.7472 | 4266426.8999 | 19080409.1911 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 37801767.8855 | 65026073.2866 | 7498.9421 | 2.2803 | 16577.3422 | 28516.1126 | 337.9515 | 581.3395
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.4964 | 11.4457 | 0.7443 | 4 | 13950.5624 | 23094.7675 | 284.4011 | 470.8181 | 131.9747 | 0 | 115.8007 | 2364656.3604 | 178383.823 | 2379491.6874 | 1878538.0689 | 0 | 564335.113 | 0 | 2872507.9705 | 7473676.507 | 5100937.7847 | 22812527.3149 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 41533886.0093 | 68758191.4104 | 10000 | 2.9772 | 13950.5624 | 23094.7675 | 284.4011 | 470.8181
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.313 | 14.1413 | 0.95507 | 4 | 11953.351 | 19079.5944 | 243.6852 | 388.9633 | 132.2415 | 0 | 113.0831 | 2749566.8506 | 207462.4306 | 2817622.5038 | 2310786.8898 | 0 | 613845.81 | 0 | 3392720.9491 | 8827163.9667 | 6024720.7874 | 26943890.1879 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 45665248.8823 | 72889554.2834 | 13335.2143 | 3.8203 | 11953.351 | 19079.5944 | 243.6852 | 388.9633
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1561 | 17.1117 | 1.1994 | 4 | 10428.1909 | 16102.6588 | 212.5928 | 328.2745 | 132.41 | 0 | 118.517 | 3149297.6551 | 237528.9424 | 3281545.4142 | 2787639.4494 | 0 | 652882.8806 | 0 | 3942468.7933 | 10257495.0886 | 7000951.1684 | 31309809.392 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 50031168.0864 | 77255473.4875 | 17782.7941 | 4.7977 | 10428.1909 | 16102.6588 | 212.5928 | 328.2745
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.4271 | 20.1837 | 1.4671 | 4 | 9265.2844 | 13904.5212 | 188.8854 | 283.4625 | 132.4758 | 0 | 136.6648 | 3541050.3252 | 266826.0764 | 3744765.5167 | 3282164.5812 | 0 | 675343.687 | 0 | 4488958.5727 | 11679349.3942 | 7971395.9482 | 35649854.1015 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 54371212.796 | 81595518.197 | 23713.7371 | 5.8683 | 9265.2844 | 13904.5212 | 188.8854 | 283.4625
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 23.1763 | 1.7434 | 4 | 8381.6597 | 12285.6735 | 170.8715 | 250.4601 | 132.4483 | 0 | 144.1506 | 3905001.1144 | 293850.3188 | 4182800.2988 | 3765999.9834 | 0 | 679010.7595 | 0 | 5002398.3652 | 13015214.4133 | 8883151.273 | 39727426.5263 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 58448785.2208 | 85673090.6218 | 31622.7766 | 6.9734 | 8381.6597 | 12285.6735 | 170.8715 | 250.4601
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.8297 | 25.9435 | 2.013 | 4 | 7712.4281 | 11093.5601 | 157.2283 | 226.1572 | 132.351 | 0 | 164.237 | 4228079.4426 | 317647.6215 | 4578076.4245 | 4215826.6252 | 0 | 665621.0292 | 0 | 5462047.9457 | 14211128.3347 | 9699387.0979 | 43377814.5213 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 62099173.2157 | 89323478.6168 | 42169.6503 | 8.0518 | 7712.4281 | 11093.5601 | 157.2283 | 226.1572
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0332 | 28.3814 | 2.2626 | 4 | 7206.7973 | 10214.9381 | 146.9203 | 208.2453 | 132.2126 | 0 | 167.8421 | 4503121.3548 | 337739.5014 | 4919578.229 | 4614482.696 | 0 | 638917.914 | 0 | 5855397.4811 | 15234543.1387 | 10397888.7307 | 46501669.0457 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 65223027.7401 | 92447333.1412 | 56234.1325 | 9.0502 | 7206.7973 | 10214.9381 | 146.9203 | 208.2453
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.9092 | 30.4459 | 2.4834 | 4 | 6825.3891 | 9566.0287 | 139.1448 | 195.0164 | 132.0595 | 0 | 175.2644 | 4729565.8647 | 354150.4419 | 5204365.2414 | 4954054.0419 | 0 | 603854.14 | 0 | 6179935.9947 | 16078925.779 | 10974197.233 | 49079048.7366 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 67800407.4311 | 95024712.8321 | 74989.4209 | 9.9336 | 6825.3891 | 9566.0287 | 139.1448 | 195.0164
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.3982 | 32.129 | 2.6709 | 4 | 6538.0354 | 9086.3021 | 133.2867 | 185.2366 | 131.9112 | 0 | 188.3422 | 4910006.8243 | 367129.2251 | 5433826.6806 | 5231606.2279 | 0 | 564791.0165 | 0 | 6437870.39 | 16750018.166 | 11432231.5767 | 51127480.107 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 69848838.8015 | 97073144.2025 | 100000 | 10.6835 | 6538.0354 | 9086.3021 | 133.2867 | 185.2366
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6628 | 33.4818 | 2.826 | 4 | 6321.654 | 8730.0113 | 128.8755 | 177.9731 | 131.7771 | 0 | 188.7261 | 5052438.9651 | 377306.7917 | 5616624.3228 | 5455124.7593 | 0 | 526246.6691 | 0 | 6640819.1881 | 17278049.3082 | 11792623.6812 | 52739233.6855 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 71460592.38 | 98684897.781 | 133352.1432 | 11.3041 | 6321.654 | 8730.0113 | 128.8755 | 177.9731
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8233 | 34.5432 | 2.9511 | 4 | 6158.7573 | 8465.0297 | 125.5546 | 172.5711 | 131.6629 | 0 | 209.1965 | 5162619.8927 | 385137.9052 | 5759061.1878 | 5631029.879 | 0 | 490319.6808 | 0 | 6796985.7328 | 17684362.6232 | 12069940.8676 | 53979457.7692 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 72700816.4637 | 99925121.8647 | 177827.941 | 11.8045 | 6158.7573 | 8465.0297 | 125.5546 | 172.5711
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0512 | 35.3618 | 3.05 | 4 | 6036.1651 | 8267.6903 | 123.0554 | 168.548 | 131.5694 | 0 | 177.5111 | 5246685.7187 | 391086.9997 | 5868363.1331 | 5767052.8153 | 0 | 458339.2653 | 0 | 6915295.8935 | 17992181.3927 | 12280033.5029 | 54919038.7212 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 73640397.4156 | 100864702.8167 | 237137.3706 | 12.1999 | 6036.1651 | 8267.6903 | 123.0554 | 168.548
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1922 | 36.4091 | 3.1518 | 4 | 5943.6876 | 8103.1313 | 121.1701 | 165.1933 | 131.4503 | 0 | 188.3623 | 5353306.1361 | 398617.7948 | 6007495.7835 | 5941292.4021 | 0 | 448029.4859 | 0 | 7078009.225 | 18415528.104 | 12568976.3323 | 56211255.2637 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 74932613.9582 | 102156919.3592 | 316227.766 | 12.6071 | 5943.6876 | 8103.1313 | 121.1701 | 165.1933
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2191 | 36.9229 | 3.2143 | 4 | 5873.3031 | 7990.7584 | 119.7352 | 162.9024 | 131.3967 | 0 | 188.6935 | 5405353.3104 | 402299.891 | 6075435.8376 | 6026681.5127 | 0 | 426540.3673 | 0 | 7151161.2584 | 18605854.6895 | 12698878.1377 | 56792205.0046 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 75513563.699 | 102737869.1001 | 421696.5034 | 12.8571 | 5873.3031 | 7990.7584 | 119.7352 | 162.9024
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.742 | 37.308 | 3.262 | 4 | 5820.3806 | 7906.8776 | 118.6563 | 161.1924 | 131.3557 | 0 | 180.4306 | 5444188.0226 | 405042.6364 | 6126248.3719 | 6090755.6573 | 0 | 408878.6277 | 0 | 7205294.1932 | 18746697.4816 | 12795006.2373 | 57222111.228 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 75943469.9224 | 103167775.3235 | 562341.3252 | 13.0479 | 5820.3806 | 7906.8776 | 118.6563 | 161.1924
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8844 | 37.5963 | 3.2982 | 4 | 5780.6059 | 7844.1902 | 117.8455 | 159.9144 | 131.3245 | 0 | 200.8601 | 5473169.3435 | 407086.8604 | 6164235.5255 | 6138775.3744 | 0 | 394675.3671 | 0 | 7245397.5637 | 18851038.2252 | 12866220.9388 | 57540599.1986 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76261957.893 | 103486263.2941 | 749894.2093 | 13.1927 | 5780.6059 | 7844.1902 | 117.8455 | 159.9144
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7493 | 37.8144 | 3.3257 | 4 | 5750.7245 | 7797.2192 | 117.2363 | 158.9569 | 131.3007 | 0 | 180.113 | 5495026.991 | 408627.1234 | 6192923.4326 | 6175106.8875 | 0 | 383530.0382 | 0 | 7275533.6443 | 18929446.1254 | 12919735.9418 | 57779930.1842 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76501288.8787 | 103725594.2798 | 1000000 | 13.3029 | 5750.7245 | 7797.2192 | 117.2363 | 158.9569
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3996 | 37.9782 | 3.3465 | 4 | 5728.2837 | 7762.0433 | 116.7788 | 158.2398 | 131.2827 | 0 | 178.4356 | 5511411.2778 | 409780.8429 | 6214449.2362 | 6202405.939 | 0 | 374844.9949 | 0 | 7298027.9934 | 18987971.8074 | 12959680.9224 | 57958573.014 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76679931.7084 | 103904237.1095 | 1333521.4322 | 13.3862 | 5728.2837 | 7762.0433 | 116.7788 | 158.2398
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8749 | 38.0978 | 3.3621 | 4 | 5711.4357 | 7735.8123 | 116.4353 | 157.705 | 131.2695 | 0 | 175.034 | 5523359.0332 | 410621.6869 | 6230158.1958 | 6222348.7201 | 0 | 368002.181 | 0 | 7314251.0286 | 19030180.8173 | 12988489.4389 | 58087411.1018 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76808769.7963 | 104033075.1973 | 1778279.41 | 13.4482 | 5711.4357 | 7735.8123 | 116.4353 | 157.705
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2445 | 38.1908 | 3.3739 | 4 | 5698.7899 | 7716.0386 | 116.1775 | 157.3019 | 131.2592 | 0 | 175.805 | 5532635.7595 | 411274.295 | 6242361.9369 | 6237853.3929 | 0 | 362889.2083 | 0 | 7326935.6911 | 19063183.7071 | 13011014.5894 | 58188148.5802 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76909507.2747 | 104133812.6757 | 2371373.7057 | 13.4958 | 5698.7899 | 7716.0386 | 116.1775 | 157.3019
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.5197 | 38.26 | 3.3828 | 4 | 5689.3001 | 7701.2381 | 115.9841 | 157.0002 | 131.2514 | 0 | 199.4308 | 5539534.9002 | 411759.4876 | 6251441.826 | 6249396.0645 | 0 | 358967.0416 | 0 | 7336328.7348 | 19087622.4799 | 13027694.554 | 58262745.0886 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 76984103.7831 | 104208409.1841 | 3162277.6602 | 13.5314 | 5689.3001 | 7701.2381 | 115.9841 | 157.0002
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.7218 | 38.3108 | 3.3895 | 4 | 5682.1799 | 7690.1841 | 115.8389 | 156.7748 | 131.2458 | 0 | 216.2782 | 5544595.3172 | 412115.2837 | 6258103.9374 | 6257868.8835 | 0 | 355942.1829 | 0 | 7343163.9858 | 19105406.4011 | 13039832.4456 | 58317028.4372 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 77038387.1317 | 104262692.5327 | 4216965.0343 | 13.5579 | 5682.1799 | 7690.1841 | 115.8389 | 156.7748
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.8681 | 38.3475 | 3.3944 | 4 | 5676.8383 | 7681.9446 | 115.73 | 156.6068 | 131.2417 | 0 | 193.2259 | 5548257.1757 | 412372.7003 | 6262925.9934 | 6264003.5181 | 0 | 353597.7777 | 0 | 7348051.2945 | 19118122.1756 | 13048511.223 | 58355841.8583 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 77077200.5528 | 104301505.9538 | 5623413.2519 | 13.5775 | 5676.8383 | 7681.9446 | 115.73 | 156.6068
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.9802 | 38.3757 | 3.3981 | 4 | 5672.8314 | 7675.7463 | 115.6483 | 156.4805 | 131.2385 | 0 | 195.0205 | 5551060.1404 | 412569.7159 | 6266617.6419 | 6268701.1331 | 0 | 351851.0354 | 0 | 7351811.87 | 19127906.4217 | 13055189.172 | 58385707.1302 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 77107065.8247 | 104331371.2257 | 7498942.0933 | 13.5923 | 5672.8314 | 7675.7463 | 115.6483 | 156.4805
1 | 4900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.0682 | 38.3978 | 3.4009 | 4 | 5669.8259 | 7671.0636 | 115.5871 | 156.385 | 131.236 | 0 | 192.868 | 5553260.0658 | 412724.3334 | 6269515.385 | 6272389.1336 | 0 | 350574.7989 | 0 | 7354800.8495 | 19135683.1332 | 13060496.9374 | 58409444.6367 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 77130803.3311 | 104355108.7322 | 10000000 | 13.6037 | 5669.8259 | 7671.0636 | 115.5871 | 156.385
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2004 | [19 empty] | 100 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.445 | [19 empty] | 133.3521 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6137 | [19 empty] | 177.8279 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7264 | [19 empty] | 237.1374 | 0
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.27321 | 0.0034113 | 4 | 1508310.1451 | 3554063.5434 | 30748.9424 | 72454.3926 | 102.846 | 0 | 26.4001 | 146401.9954 | 9284.5558 | 122371.5081 | 79076.4257 | 0 | 84124.0421 | 0 | 172090.8256 | 447745.0275 | 305595.1815 | 1366689.5617 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20581317.2188 | 48496199.1674 | 316.2278 | 0.013645 | 1508310.1451 | 3554063.5434 | 30748.9424 | 72454.3926
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.40607 | 0.010368 | 4 | 506699.0587 | 1179817.2381 | 10329.7457 | 24052.1702 | 109.6413 | 0 | 325.9351 | 201384.969 | 13308.994 | 167198.5811 | 101028.5084 | 0 | 97815.1992 | 0 | 226487.1382 | 589273.0746 | 402190.9818 | 1798687.4463 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21013315.1033 | 48928197.0519 | 421.6965 | 0.041471 | 506699.0587 | 1179817.2381 | 10329.7457 | 24052.1702
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7989 | 0.58734 | 0.020899 | 4 | 257847.8696 | 591779.4066 | 5256.5776 | 12064.2236 | 115.232 | 0 | 440.7827 | 269183.2378 | 18407.9473 | 223736.7817 | 130517.2803 | 0 | 113684.9357 | 0 | 294656.7713 | 766636.4765 | 523245.148 | 2340068.5786 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21554696.2356 | 49469578.1843 | 562.3413 | 0.083595 | 257847.8696 | 591779.4066 | 5256.5776 | 12064.2236
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7124 | 0.83659 | 0.036134 | 4 | 153896.8754 | 347029.5152 | 3137.396 | 7074.6661 | 119.8219 | 0 | 51.6302 | 353482.9567 | 24864.8991 | 295961.31 | 170577.5844 | 0 | 133147.6217 | 0 | 381433.405 | 992411.4772 | 677341.2252 | 3029220.4793 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22243848.1363 | 50158730.0849 | 749.8942 | 0.14454 | 153896.8754 | 347029.5152 | 3137.396 | 7074.6661
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9131 | 1.1688 | 0.05731 | 4 | 100749.0652 | 222521.3855 | 2053.906 | 4536.3994 | 123.4444 | 0 | 79.6098 | 455224.8054 | 32740.8512 | 385789.9354 | 223283.9376 | 0 | 155979.8132 | 0 | 488677.5437 | 1271438.7272 | 867783.0568 | 3880918.6705 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 23095546.3275 | 51010428.2761 | 1000 | 0.22924 | 100749.0652 | 222521.3855 | 2053.906 | 4536.3994
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5138 | 1.6167 | 0.086504 | 4 | 69856.8874 | 150532.0952 | 1424.1271 | 3068.8004 | 126.2845 | 0 | 61.6874 | 579915.329 | 42464.0899 | 499080.5239 | 295126.009 | 0 | 183846.9107 | 0 | 624168.8163 | 1623959.2255 | 1108385.5404 | 4956946.4447 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 24171574.1017 | 52086456.0504 | 1333.5214 | 0.34602 | 69856.8874 | 150532.0952 | 1424.1271 | 3068.8004
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 2.2076 | 0.1251 | 4 | 50960.6976 | 106745.8955 | 1038.9027 | 2176.1595 | 128.3407 | 0 | 64.6513 | 729069.3694 | 54069.0703 | 639431.2802 | 389483.7376 | 0 | 217511.3828 | 0 | 791530.2877 | 2059399.4435 | 1405582.4366 | 6286077.0082 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 25500704.6652 | 53415586.6138 | 1778.2794 | 0.5004 | 50960.6976 | 106745.8955 | 1038.9027 | 2176.1595
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4831 | 3.0192 | 0.17968 | 4 | 37868.016 | 76708.0576 | 771.9907 | 1563.7975 | 130.2787 | 0 | 92.1131 | 917240.7581 | 68831.4754 | 820332.5286 | 518120.9265 | 0 | 258939.1805 | 0 | 1007551.299 | 2621441.8027 | 1789187.8956 | 8001645.8664 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 27216273.5234 | 55131155.472 | 2371.3737 | 0.71871 | 37868.016 | 76708.0576 | 771.9907 | 1563.7975
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2421 | 4.0835 | 0.25102 | 4 | 29215.2944 | 57016.6121 | 595.5933 | 1162.3608 | 131.6013 | 0 | 88.0381 | 1141656.3322 | 86333.7444 | 1043533.5217 | 687139.2176 | 0 | 308750.2665 | 0 | 1274291.1022 | 3315444.0548 | 2262858.6929 | 10120006.9323 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 29334634.5893 | 57249516.538 | 3162.2777 | 1.0041 | 29215.2944 | 57016.6121 | 595.5933 | 1162.3608
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2527 | 5.5028 | 0.34601 | 4 | 23121.4328 | 43290.8312 | 471.3617 | 882.5421 | 132.6153 | 0 | 85.2298 | 1415314.4192 | 107598.6459 | 1323879.3972 | 911420.6963 | 0 | 369938.8379 | 0 | 1609979.2786 | 4188835.8308 | 2858966.5265 | 12785933.6324 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 32000561.2894 | 59915443.238 | 4216.965 | 1.384 | 23121.4328 | 43290.8312 | 471.3617 | 882.5421
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8622 | 7.3771 | 0.47178 | 4 | 18724.079 | 33516.2465 | 381.7157 | 683.274 | 133.3839 | 0 | 78.1791 | 1746685.9237 | 133268.3597 | 1672885.0091 | 1208084.2752 | 0 | 443790.5693 | 0 | 2029838.5134 | 5281223.4348 | 3604543.5125 | 16120319.5977 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 35334947.2547 | 63249829.2034 | 5623.4133 | 1.8871 | 18724.079 | 33516.2465 | 381.7157 | 683.274
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5199 | 9.8356 | 0.63712 | 4 | 15494.9953 | 26448.5938 | 315.8864 | 539.1904 | 133.9654 | 0 | 87.5809 | 2146042.092 | 164103.8803 | 2104855.1168 | 1598287.4799 | 0 | 532463.1061 | 0 | 2552843.1533 | 6641974.2247 | 4533283.8873 | 20273852.9403 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 39488480.5973 | 67403362.5459 | 7498.9421 | 2.5485 | 15494.9953 | 26448.5938 | 315.8864 | 539.1904
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8035 | 12.4713 | 0.83419 | 4 | 13087.722 | 21453.5539 | 266.8109 | 437.3597 | 134.3412 | 0 | 63.4859 | 2542756.2618 | 194620.855 | 2544456.872 | 2016018.7668 | 0 | 598216.8373 | 0 | 3079467.1412 | 8012141.8159 | 5468451.4224 | 24456129.9723 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 43670757.6293 | 71585639.578 | 10000 | 3.3368 | 13087.722 | 21453.5539 | 266.8109 | 437.3597
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.9855 | 15.3595 | 1.0669 | 4 | 11254.9087 | 17796.1919 | 229.4465 | 362.7994 | 134.5951 | 0 | 114.101 | 2950120.5174 | 225836.3308 | 3005331.3851 | 2473907.7004 | 0 | 648407.4159 | 0 | 3628405.3064 | 9440366.3189 | 6443243.9928 | 28815618.9678 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 48030246.6248 | 75945128.5734 | 13335.2143 | 4.2675 | 11254.9087 | 17796.1919 | 229.4465 | 362.7994
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.0675 | 18.4933 | 1.3334 | 4 | 9855.6156 | 15089.4746 | 200.9201 | 307.6193 | 134.7439 | 0 | 105.2202 | 3367022.7315 | 257625.0827 | 3486247.6693 | 2971348.0583 | 0 | 685514.3668 | 0 | 4199425.5844 | 10926043.9499 | 7457249.5036 | 33350476.9464 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 52565104.6035 | 80479986.5521 | 17782.7941 | 5.3335 | 9855.6156 | 15089.4746 | 200.9201 | 307.6193
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.448 | 21.6916 | 1.6216 | 4 | 8789.5252 | 13093.0224 | 179.1864 | 266.919 | 134.786 | 0 | 148.195 | 3770643.2934 | 288199.078 | 3960651.5765 | 3480258.5448 | 0 | 704328.1496 | 0 | 4759591.4505 | 12383480.6277 | 8451979.9835 | 37799132.7038 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 57013760.3609 | 84928642.3095 | 23713.7371 | 6.4866 | 8789.5252 | 13093.0224 | 179.1864 | 266.919
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.5144 | 24.7734 | 1.9157 | 4 | 7979.9904 | 11622.9477 | 162.6829 | 236.9495 | 134.7348 | 0 | 187.471 | 4141936.611 | 316098.1804 | 4404917.119 | 3972400.3506 | 0 | 703619.397 | 0 | 5280198.9466 | 13737994.5413 | 9376463.562 | 41933628.7078 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 61148256.3648 | 89063138.3135 | 31622.7766 | 7.6627 | 7979.9904 | 11622.9477 | 162.6829 | 236.9495
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7682 | 27.5979 | 2.1995 | 4 | 7367.0419 | 10539.8393 | 150.1871 | 214.8689 | 134.6167 | 0 | 172.8706 | 4468922.244 | 340448.6884 | 4802697.4998 | 4425405.869 | 0 | 685899.7533 | 0 | 5742115.8812 | 14939807.6531 | 10196725.7056 | 45602023.2943 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 64816650.9513 | 92731532.9 | 42169.6503 | 8.7982 | 7367.0419 | 10539.8393 | 150.1871 | 214.8689
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.8176 | 30.062 | 2.4596 | 4 | 6903.9087 | 9741.2411 | 140.7455 | 198.5884 | 134.4624 | 0 | 162.822 | 4744809.1781 | 360807.0299 | 5143339.0369 | 4822453.4878 | 0 | 655091.7885 | 0 | 6133335.2032 | 15957680.0788 | 10891444.5513 | 48708960.3544 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 67923588.0114 | 95838469.96 | 56234.1325 | 9.8384 | 6903.9087 | 9741.2411 | 140.7455 | 198.5884
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5324 | 32.1394 | 2.6881 | 4 | 6554.4653 | 9150.6512 | 133.6216 | 186.5484 | 134.2973 | 0 | 194.0074 | 4971105.9643 | 377361.4824 | 5426380.2767 | 5158710.3849 | 0 | 616823.6174 | 0 | 6454648.873 | 16793672.337 | 11462026.4455 | 51260729.3812 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 70475357.0382 | 98390238.9868 | 74989.4209 | 10.7523 | 6554.4653 | 9150.6512 | 133.6216 | 186.5484
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9003 | 33.8368 | 2.8815 | 4 | 6291.0438 | 8712.9082 | 128.2514 | 177.6244 | 134.1397 | 0 | 192.1258 | 5151974.1578 | 390489.2696 | 5655082.2997 | 5434617.3966 | 0 | 575718.0696 | 0 | 6711073.6654 | 17460837.0468 | 11917380.0688 | 53297171.9743 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 72511799.6313 | 100426681.5799 | 100000 | 11.5262 | 6291.0438 | 8712.9082 | 128.2514 | 177.6244
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0035 | 35.1853 | 3.0404 | 4 | 6092.5877 | 8387.9537 | 124.2056 | 170.9998 | 134.0002 | 0 | 177.439 | 5293180.4301 | 400669.3604 | 5835238.2726 | 5654612.9816 | 0 | 535163.2493 | 0 | 6910357.0746 | 17979331.599 | 12271263.2547 | 54879816.2222 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 74094443.8792 | 102009325.8279 | 133352.1432 | 12.1614 | 6092.5877 | 8387.9537 | 124.2056 | 170.9998
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.0159 | 36.2364 | 3.1676 | 4 | 5943.1443 | 8146.3089 | 121.159 | 166.0735 | 133.8828 | 0 | 225.7457 | 5401740.5509 | 408450.5393 | 5974763.0804 | 5826040.0611 | 0 | 497673.0554 | 0 | 7062380.242 | 18374864.6963 | 12541222.7209 | 56087134.9464 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 75301762.6034 | 103216644.552 | 177827.941 | 12.6704 | 5943.1443 | 8146.3089 | 121.159 | 166.0735
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.131 | 37.0475 | 3.268 | 4 | 5830.6382 | 7966.136 | 118.8654 | 162.4005 | 133.787 | 0 | 200.5197 | 5484647.264 | 414365.8278 | 6081925.2794 | 5958617.6049 | 0 | 464662.3575 | 0 | 7177645.1501 | 18674760.3432 | 12745907.6622 | 57002531.4891 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 76217159.1461 | 104132041.0947 | 237137.3706 | 13.0718 | 5830.6382 | 7966.136 | 118.8654 | 162.4005
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.3628 | 38.1523 | 3.3758 | 4 | 5744.6979 | 7811.9983 | 117.1134 | 159.2582 | 133.6689 | 0 | 209.8261 | 5596931.0591 | 422394.0242 | 6227105.8675 | 6139038.1247 | 0 | 455859.9442 | 0 | 7348118.3177 | 19118296.5563 | 13048630.2414 | 58356374.1351 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77571001.7921 | 105485883.7408 | 316227.766 | 13.5031 | 5744.6979 | 7811.9983 | 117.1134 | 159.2582
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2996 | 38.6567 | 3.4389 | 4 | 5680.0259 | 7709.4008 | 115.795 | 157.1666 | 133.6149 | 0 | 189.5329 | 5647831.0917 | 426026.8056 | 6293122.6425 | 6221488.3417 | 0 | 433691.2201 | 0 | 7418642.4397 | 19301785.8552 | 13173865.4582 | 58916453.8548 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 78131081.5118 | 106045963.4604 | 421696.5034 | 13.7554 | 5680.0259 | 7709.4008 | 115.795 | 157.1666
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7734 | 39.0397 | 3.4872 | 4 | 5631.3914 | 7632.6061 | 114.8035 | 155.601 | 133.5732 | 0 | 195.6089 | 5686301.2493 | 428767.6522 | 6343133.1784 | 6284134.5744 | 0 | 415757.3162 | 0 | 7471656.6485 | 19439717.9519 | 13268006.9485 | 59337475.5195 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 78552103.1765 | 106466985.1251 | 562341.3252 | 13.949 | 5631.3914 | 7632.6061 | 114.8035 | 155.601
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8749 | 39.3254 | 3.5239 | 4 | 5594.8349 | 7575.2316 | 114.0583 | 154.4313 | 133.5416 | 0 | 179.9609 | 5714906.7985 | 430802.9528 | 6380384.9688 | 6330903.1083 | 0 | 401333.2741 | 0 | 7510749.13 | 19541428.5697 | 13337426.535 | 59647935.3372 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 78862562.9942 | 106777444.9429 | 749894.2093 | 14.0956 | 5594.8349 | 7575.2316 | 114.0583 | 154.4313
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.7024 | 39.5398 | 3.5517 | 4 | 5567.3689 | 7532.2879 | 113.4983 | 153.5559 | 133.5177 | 0 | 216.8122 | 5736313.8653 | 432324.5413 | 6408298.9908 | 6366006.8948 | 0 | 389968.7971 | 0 | 7539836.1048 | 19617106.9117 | 13389078.5585 | 59878934.6643 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79093562.3213 | 107008444.2699 | 1000000 | 14.2066 | 5567.3689 | 7532.2879 | 113.4983 | 153.5559
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.324 | 39.7006 | 3.5726 | 4 | 5546.7404 | 7500.125 | 113.0778 | 152.9002 | 133.4997 | 0 | 206.2323 | 5752348.9162 | 433463.4257 | 6429228.6791 | 6392360.3077 | 0 | 381123.5766 | 0 | 7561524.7131 | 19673536.2215 | 13427592.7219 | 60051178.5619 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79265806.2189 | 107180688.1675 | 1333521.4322 | 14.2905 | 5546.7404 | 7500.125 | 113.0778 | 152.9002
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.787 | 39.8204 | 3.5884 | 4 | 5531.2523 | 7476.0596 | 112.7621 | 152.4096 | 133.4862 | 0 | 220.9726 | 5764268.4349 | 434309.5176 | 6444798.107 | 6411982.7249 | 0 | 374261.6168 | 0 | 7577551.9565 | 19715235.8212 | 13456053.5555 | 60178461.7345 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79393089.3915 | 107307971.3401 | 1778279.41 | 14.3535 | 5531.2523 | 7476.0596 | 112.7621 | 152.4096
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.1445 | 39.9128 | 3.6004 | 4 | 5519.6267 | 7457.9389 | 112.5251 | 152.0402 | 133.4757 | 0 | 204.2999 | 5773455.7341 | 434961.394 | 6456805.2103 | 6427126.0519 | 0 | 369109.8722 | 0 | 7589968.7224 | 19747541.699 | 13478102.981 | 60277071.6649 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79491699.3219 | 107406581.2705 | 2371373.7057 | 14.4016 | 5519.6267 | 7457.9389 | 112.5251 | 152.0402
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.4003 | 39.9788 | 3.6093 | 4 | 5510.9022 | 7444.464 | 112.3472 | 151.7655 | 133.4682 | 0 | 209.9804 | 5780021.0552 | 435427.0658 | 6465389.3567 | 6437958.155 | 0 | 365050.5005 | 0 | 7598699.992 | 19770258.6714 | 13493607.7814 | 60346412.5781 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79561040.2351 | 107475922.1837 | 3162277.6602 | 14.437 | 5510.9022 | 7444.464 | 112.3472 | 151.7655
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6003 | 40.0305 | 3.616 | 4 | 5504.356 | 7434.2927 | 112.2137 | 151.5581 | 133.4623 | 0 | 190.8602 | 5785151.2142 | 435790.8639 | 6472098.9778 | 6446428.0731 | 0 | 362055.683 | 0 | 7605594.6766 | 19788197.2266 | 13505851.214 | 60401167.9292 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79615795.5862 | 107530677.5348 | 4216965.0343 | 14.4641 | 5504.356 | 7434.2927 | 112.2137 | 151.5581
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.7318 | 40.0644 | 3.6208 | 4 | 5499.4449 | 7426.8258 | 112.1136 | 151.4059 | 133.4584 | 0 | 192.5677 | 5788521.0581 | 436029.7698 | 6476507.6069 | 6451995.0694 | 0 | 359591.9693 | 0 | 7609931.7347 | 19799481.3621 | 13513552.8683 | 60435611.4387 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79650239.0957 | 107565121.0443 | 5623413.2519 | 14.4833 | 5499.4449 | 7426.8258 | 112.1136 | 151.4059
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8561 | 40.0965 | 3.6248 | 4 | 5495.7608 | 7421.0085 | 112.0385 | 151.2873 | 133.4548 | 0 | 193.5207 | 5791704.8307 | 436255.4845 | 6480673.0719 | 6457255.8966 | 0 | 358004.3566 | 0 | 7614318.5198 | 19810894.8769 | 13521342.8267 | 60470449.8638 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79685077.5208 | 107599959.4694 | 7498942.0933 | 14.4994 | 5495.7608 | 7421.0085 | 112.0385 | 151.2873
1 | 5000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.9339 | 40.1166 | 3.6276 | 4 | 5492.9974 | 7416.7783 | 111.9822 | 151.2011 | 133.4525 | 0 | 205.0253 | 5793696.5845 | 436396.6606 | 6483279.5457 | 6460548.4704 | 0 | 356643.3739 | 0 | 7616920.2076 | 19817663.9351 | 13525962.848 | 60491111.6257 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 79705739.2827 | 107620621.2313 | 10000000 | 14.5104 | 5492.9974 | 7416.7783 | 111.9822 | 151.2011
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.1564 | [19 empty] | 100 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8238 | [19 empty] | 133.3521 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9117 | [19 empty] | 177.8279 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0392 | [19 empty] | 237.1374 | 0
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.279 | 0.0045907 | 4 | 1148776.6555 | 2707013.6275 | 23419.366 | 55186.1343 | 104.0359 | 0 | 29.9432 | 149745.5788 | 9561.9046 | 124331.8795 | 79646.915 | 0 | 82608.7389 | 0 | 173899.0565 | 452449.6735 | 308806.1991 | 1381049.9458 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21094806.6562 | 49708469.2796 | 316.2278 | 0.018363 | 1148776.6555 | 2707013.6275 | 23419.366 | 55186.1343
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1765 | 0.43138 | 0.012463 | 4 | 433107.4172 | 1007090.982 | 8829.4805 | 20530.9119 | 111.6608 | 0 | 343.8491 | 212667.7194 | 14223.6513 | 175231.2182 | 104528.5158 | 0 | 99397.7944 | 0 | 236359.0706 | 614957.8178 | 419721.3468 | 1877087.1341 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21590843.8445 | 50204506.4679 | 421.6965 | 0.049851 | 433107.4172 | 1007090.982 | 8829.4805 | 20530.9119
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8572 | 0.61844 | 0.02407 | 4 | 229968.2612 | 527166.3021 | 4688.2141 | 10746.9981 | 117.2075 | 0 | 449.9003 | 282233.4606 | 19527.4341 | 232840.7017 | 134474.2881 | 0 | 114570.1436 | 0 | 305621.951 | 795165.6247 | 542716.8779 | 2427150.4817 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22140907.1921 | 50754569.8156 | 562.3413 | 0.096278 | 229968.2612 | 527166.3021 | 4688.2141 | 10746.9981
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7754 | 0.87707 | 0.040829 | 4 | 139895.4474 | 315097.5968 | 2851.9579 | 6423.6907 | 121.8246 | 0 | 64.1608 | 369422.4146 | 26301.7938 | 306933.108 | 175581.9947 | 0 | 133523.6141 | 0 | 394587.5408 | 1026635.8402 | 700700.0562 | 3133686.3624 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22847443.0729 | 51461105.6963 | 749.8942 | 0.16332 | 139895.4474 | 315097.5968 | 2851.9579 | 6423.6907
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0058 | 1.2288 | 0.064268 | 4 | 92351.0536 | 203656.8852 | 1882.7011 | 4151.8211 | 125.5454 | 0 | 79.5883 | 476832.5871 | 34742.5376 | 400943.9077 | 230893.8101 | 0 | 156821.2583 | 0 | 507091.2993 | 1319347.542 | 900481.8073 | 4027154.7493 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 23740911.4597 | 52354574.0831 | 1000 | 0.25707 | 92351.0536 | 203656.8852 | 1882.7011 | 4151.8211
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 1.6963 | 0.096265 | 4 | 64537.3987 | 138846.8488 | 1315.6822 | 2830.5808 | 128.4228 | 0 | 68.5354 | 606550.3121 | 45005.2951 | 517888.4285 | 304711.9605 | 0 | 184433.1445 | 0 | 646849.7649 | 1682970.4011 | 1148661.8803 | 5137071.1869 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 24850827.8974 | 53464490.5208 | 1333.5214 | 0.38506 | 64537.3987 | 138846.8488 | 1315.6822 | 2830.5808
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7944 | 2.3207 | 0.13888 | 4 | 47238.3752 | 98747.3176 | 963.0182 | 2013.0976 | 130.5336 | 0 | 57.8012 | 763706.3628 | 57420.6437 | 664489.9806 | 403254.1578 | 0 | 218663.3902 | 0 | 821938.4686 | 2138515.2927 | 1459580.6293 | 6527568.9257 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 26241325.6361 | 54854988.2595 | 1778.2794 | 0.55551 | 47238.3752 | 98747.3176 | 963.0182 | 2013.0976
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6754 | 3.1674 | 0.19862 | 4 | 35254.8255 | 71270.3172 | 718.7173 | 1452.9418 | 132.5031 | 0 | 71.108 | 959403.1993 | 73004.7228 | 851094.5996 | 535259.222 | 0 | 259601.5087 | 0 | 1044561.6684 | 2717735.1921 | 1854910.1125 | 8295570.2252 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 28009326.9357 | 56622989.5591 | 2371.3737 | 0.79448 | 35254.8255 | 71270.3172 | 718.7173 | 1452.9418
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5199 | 4.2911 | 0.2772 | 4 | 27256.8194 | 53062.6686 | 555.6671 | 1081.7543 | 133.8603 | 0 | 82.0738 | 1195677.6005 | 91711.6358 | 1084099.1004 | 711221.7344 | 0 | 310215.0322 | 0 | 1323240.7903 | 3442801.1025 | 2349782.4949 | 10508749.4912 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 30222506.2016 | 58836168.825 | 3162.2777 | 1.1088 | 27256.8194 | 53062.6686 | 555.6671 | 1081.7543
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6011 | 5.7784 | 0.38168 | 4 | 21607.9022 | 40349.9051 | 440.5063 | 822.5874 | 134.8916 | 0 | 89.9703 | 1481869.8393 | 114310.2888 | 1374514.6176 | 944238.9222 | 0 | 371222.379 | 0 | 1671600.8583 | 4349162.5407 | 2968392.8004 | 13275312.2462 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 32989068.9566 | 61602731.58 | 4216.965 | 1.5267 | 21607.9022 | 40349.9051 | 440.5063 | 822.5874
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3032 | 7.7419 | 0.51991 | 4 | 17526.0754 | 31285.1271 | 357.2928 | 637.7896 | 135.6746 | 0 | 82.5827 | 1828340.5589 | 141579.5301 | 1735973.688 | 1252009.9922 | 0 | 444915.3761 | 0 | 2107099.4667 | 5482240.5867 | 3741741.8492 | 16733901.0478 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 36447657.7583 | 65061320.3817 | 5623.4133 | 2.0796 | 17526.0754 | 31285.1271 | 357.2928 | 637.7896
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.1117 | 10.324 | 0.70154 | 4 | 14526.8483 | 24723.5795 | 296.1495 | 504.0236 | 136.2694 | 0 | 81.0862 | 2246875.7093 | 174396.8457 | 2184555.1035 | 1656667.5312 | 0 | 534142.0311 | 0 | 2650688.5161 | 6896547.7879 | 4707035.5752 | 21050909.1 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 40764665.8104 | 69378328.4338 | 7498.9421 | 2.8062 | 14526.8483 | 24723.5795 | 296.1495 | 504.0236
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.1569 | 13.562 | 0.93303 | 4 | 12300.0481 | 19966.9365 | 250.7531 | 407.053 | 136.7023 | 0 | 112.2745 | 2730592.6243 | 212172.6501 | 2716523.809 | 2164026.6376 | 0 | 633002.7012 | 0 | 3297964.1847 | 8580626.3031 | 5856453.7661 | 26191362.6763 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 45905119.3867 | 74518782.0101 | 10000 | 3.7321 | 12300.0481 | 19966.9365 | 250.7531 | 407.053
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.6534 | 16.6353 | 1.1885 | 4 | 10616.9528 | 16635.7671 | 216.4409 | 339.1426 | 136.941 | 0 | 97.1486 | 3158923.7683 | 245472.3848 | 3198200.5114 | 2645818.6921 | 0 | 682842.3157 | 0 | 3873190.4922 | 10077247.1601 | 6877928.2535 | 30759623.578 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 50473380.2885 | 79087042.9119 | 13335.2143 | 4.754 | 10616.9528 | 16635.7671 | 216.4409 | 339.1426
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.9297 | 19.9219 | 1.4774 | 4 | 9332.6863 | 14174.5364 | 190.2594 | 288.9671 | 137.0685 | 0 | 104.5401 | 3591301.0413 | 278887.3105 | 3694104.4192 | 3160576.935 | 0 | 717266.1565 | 0 | 4462432.9864 | 11610335.2597 | 7924292.3833 | 35439196.4918 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 55152953.2022 | 83766615.8256 | 17782.7941 | 5.9097 | 9332.6863 | 14174.5364 | 190.2594 | 288.9671
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.4512 | 23.2568 | 1.7872 | 4 | 8354.1577 | 12356.6527 | 170.3108 | 251.9071 | 137.086 | 0 | 142.5072 | 4007987.5527 | 310858.7617 | 4181000.8251 | 3684946.2452 | 0 | 733023.3296 | 0 | 5037948.5186 | 13107708.6201 | 8946280.4697 | 40009754.3228 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 59723511.0332 | 88337173.6566 | 23713.7371 | 7.149 | 8354.1577 | 12356.6527 | 170.3108 | 251.9071
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.587 | 26.4512 | 2.1008 | 4 | 7610.8452 | 11015.9289 | 155.1574 | 224.5746 | 137.0098 | 0 | 169.0381 | 4389511.3611 | 339890.5641 | 4634648.1678 | 4191150.0915 | 0 | 729016.2895 | 0 | 5570844.4249 | 14494194.4562 | 9892585.5423 | 44241840.8974 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 63955597.6078 | 92569260.2312 | 31622.7766 | 8.4032 | 7610.8452 | 11015.9289 | 155.1574 | 224.5746
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6692 | 29.3077 | 2.398 | 4 | 7048.4425 | 10031.4819 | 143.692 | 204.5053 | 136.8719 | 0 | 139.2229 | 4717568.4601 | 364599.375 | 5031390.7149 | 4644605.9325 | 0 | 705770.6401 | 0 | 6030934.6978 | 15691254.9688 | 10709603.9393 | 47895728.7284 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 67609485.4388 | 96223148.0623 | 42169.6503 | 9.5921 | 7048.4425 | 10031.4819 | 143.692 | 204.5053
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.5755 | 31.8006 | 2.6689 | 4 | 6623.4895 | 9303.8243 | 135.0288 | 189.671 | 136.7016 | 0 | 156.1662 | 4994709.607 | 385267.4179 | 5371572.1403 | 5041893.4381 | 0 | 671041.6708 | 0 | 6421148.8669 | 16706512.193 | 11402537.8562 | 50994683.1903 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 70708439.9007 | 99322102.5242 | 56234.1325 | 10.6754 | 6623.4895 | 9303.8243 | 135.0288 | 189.671
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.1271 | 33.89 | 2.905 | 4 | 6302.767 | 8765.1793 | 128.4904 | 178.69 | 136.5249 | 0 | 158.6176 | 5220900.9682 | 401979.7092 | 5652809.3895 | 5376348.9065 | 0 | 629562.0469 | 0 | 6739824.3979 | 17535640.5553 | 11968435.0004 | 53525500.9739 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 73239257.6844 | 101852920.3078 | 74989.4209 | 11.6202 | 6302.767 | 8765.1793 | 128.4904 | 178.69
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3144 | 35.5843 | 3.1036 | 4 | 6060.9148 | 8365.7899 | 123.5599 | 170.5479 | 136.3597 | 0 | 189.8918 | 5400438.6168 | 415134.8933 | 5878472.2112 | 5648643.3333 | 0 | 585748.9954 | 0 | 6992090.8395 | 18191986.0894 | 12416404.3139 | 55528919.2929 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 75242676.0033 | 103856338.6267 | 100000 | 12.4144 | 6060.9148 | 8365.7899 | 123.5599 | 170.5479
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2667 | 36.9286 | 3.266 | 4 | 5878.6427 | 8068.9283 | 119.8441 | 164.496 | 136.2149 | 0 | 172.967 | 5540489.8564 | 425323.7202 | 6056075.7075 | 5865416.1423 | 0 | 543285.8561 | 0 | 7187930.6002 | 18701520.9744 | 12764172.3428 | 57084215.1998 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 76797971.9103 | 105411634.5337 | 133352.1432 | 13.0639 | 5878.6427 | 8068.9283 | 119.8441 | 164.496
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.165 | 37.979 | 3.396 | 4 | 5741.3342 | 7847.7591 | 117.0449 | 159.9872 | 136.0935 | 0 | 200.0406 | 5648502.9805 | 433135.3592 | 6194030.6488 | 6035303.4479 | 0 | 504564.964 | 0 | 7338059.5861 | 19092125.8001 | 13030768.1625 | 58276490.9491 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 77990247.6595 | 106603910.2829 | 177827.941 | 13.584 | 5741.3342 | 7847.7591 | 117.0449 | 159.9872
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.0339 | 39.2897 | 3.5293 | 4 | 5636.9018 | 7663.7747 | 114.9159 | 156.2364 | 135.9494 | 0 | 209.15 | 5782075.06 | 442792.3138 | 6365089.0873 | 6247277.4979 | 0 | 490603.0722 | 0 | 7537856.4422 | 19611956.2356 | 13385563.1162 | 59863212.8251 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 79576969.5355 | 108190632.159 | 237137.3706 | 14.1171 | 5636.9018 | 7663.7747 | 114.9159 | 156.2364
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.4971 | 39.9514 | 3.6126 | 4 | 5557.8269 | 7537.9673 | 113.3038 | 153.6717 | 135.8786 | 0 | 186.5558 | 5849015.4272 | 447628.6586 | 6451031.0335 | 6354311.3645 | 0 | 463290.0591 | 0 | 7630457.8517 | 19852886.1081 | 13550002.7048 | 60598623.2076 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 80312379.9181 | 108926042.5415 | 316227.766 | 14.4503 | 5557.8269 | 7537.9673 | 113.3038 | 153.6717
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3607 | 40.4507 | 3.6765 | 4 | 5498.3207 | 7444.0086 | 112.0907 | 151.7562 | 135.824 | 0 | 180.8519 | 5899227.2729 | 451247.9062 | 6515686.7476 | 6435145.6029 | 0 | 440572.5828 | 0 | 7699333.2439 | 20032085.7501 | 13672310.1427 | 61145609.2491 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 80859365.9595 | 109473028.5829 | 421696.5034 | 14.7062 | 5498.3207 | 7444.0086 | 112.0907 | 151.7562
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.7755 | 40.8288 | 3.7255 | 4 | 5453.5655 | 7373.6782 | 111.1783 | 150.3224 | 135.7819 | 0 | 206.0768 | 5937097.0906 | 453972.6617 | 6564559.4758 | 6496424.5617 | 0 | 422225.902 | 0 | 7750969.0798 | 20166431.6032 | 13764003.9479 | 61555684.3225 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 81269441.033 | 109883103.6564 | 562341.3252 | 14.9021 | 5453.5655 | 7373.6782 | 111.1783 | 150.3224
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8427 | 41.1135 | 3.7628 | 4 | 5419.9218 | 7321.0315 | 110.4924 | 149.2491 | 135.7498 | 0 | 219.0076 | 5965522.9788 | 456015.122 | 6601306.7594 | 6542600.5108 | 0 | 407622.5837 | 0 | 7789496.5023 | 20266672.0537 | 13832420.1151 | 61861656.6258 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 81575413.3362 | 110189075.9597 | 749894.2093 | 15.051 | 5419.9218 | 7321.0315 | 110.4924 | 149.2491
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6346 | 41.3245 | 3.7908 | 4 | 5394.6422 | 7281.7004 | 109.9771 | 148.4473 | 135.7259 | 0 | 201.921 | 5986535.2204 | 457523.3237 | 6628504.9493 | 6576832.9195 | 0 | 396031.1082 | 0 | 7817716.7333 | 20340095.3057 | 13882532.9933 | 62085772.5535 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 81799529.2639 | 110413191.8873 | 1000000 | 15.1631 | 5394.6422 | 7281.7004 | 109.9771 | 148.4473
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2239 | 41.4814 | 3.8118 | 4 | 5375.6548 | 7252.2824 | 109.59 | 147.8476 | 135.7079 | 0 | 211.2378 | 6002131.6265 | 458641.9207 | 6648712.1382 | 6602296.9331 | 0 | 386964.8149 | 0 | 7838511.499 | 20394199.0206 | 13919459.8904 | 62250917.8434 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 81964674.5538 | 110578337.1772 | 1333521.4322 | 15.2474 | 5375.6548 | 7252.2824 | 109.59 | 147.8476
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6649 | 41.5987 | 3.8277 | 4 | 5361.3982 | 7230.2504 | 109.2994 | 147.3984 | 135.6944 | 0 | 215.8498 | 6013778.157 | 459476.7422 | 6663812.456 | 6621342.6058 | 0 | 379964.1742 | 0 | 7853965.9127 | 20434408.2349 | 13946903.5054 | 62373651.788 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82087408.4985 | 110701071.1219 | 1778279.41 | 15.3108 | 5361.3982 | 7230.2504 | 109.2994 | 147.3984
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.0009 | 41.688 | 3.8397 | 4 | 5350.6966 | 7213.6963 | 109.0812 | 147.061 | 135.6841 | 0 | 196.1958 | 6022638.1788 | 460111.5559 | 6675305.9713 | 6635848.826 | 0 | 374660.4025 | 0 | 7865740.3244 | 20465042.8389 | 13967812.2521 | 62467160.3499 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82180917.0603 | 110794579.6837 | 2371373.7057 | 15.3589 | 5350.6966 | 7213.6963 | 109.0812 | 147.061
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.2593 | 41.7567 | 3.8489 | 4 | 5342.6653 | 7201.2362 | 108.9175 | 146.8069 | 135.6762 | 0 | 181.7166 | 6029443.6469 | 460599.0069 | 6684137.7491 | 6647001.2833 | 0 | 370688.5403 | 0 | 7874829.3884 | 20488690.7189 | 13983952.4162 | 62539342.7501 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82253099.4605 | 110866762.084 | 3162277.6602 | 15.3955 | 5342.6653 | 7201.2362 | 108.9175 | 146.8069
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.4445 | 41.8059 | 3.8556 | 4 | 5336.6391 | 7191.9655 | 108.7946 | 146.6179 | 135.6704 | 0 | 172.4632 | 6034317.5389 | 460948.0081 | 6690464.9077 | 6654994.1544 | 0 | 367580.4296 | 0 | 7881238.9651 | 20505367.1227 | 13995334.4044 | 62590245.5308 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82304002.2412 | 110917664.8647 | 4216965.0343 | 15.4224 | 5336.6391 | 7191.9655 | 108.7946 | 146.6179
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.5734 | 41.8401 | 3.8605 | 4 | 5332.118 | 7185.0962 | 108.7024 | 146.4779 | 135.6665 | 0 | 193.3435 | 6037707.0736 | 461190.6638 | 6694866.2459 | 6660555.8279 | 0 | 365119.8661 | 0 | 7885581.4741 | 20516665.4405 | 14003045.7385 | 62624732.3304 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82338489.0409 | 110952151.6643 | 5623413.2519 | 15.442 | 5332.118 | 7185.0962 | 108.7024 | 146.4779
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.6855 | 41.8699 | 3.8644 | 4 | 5328.7265 | 7179.8209 | 108.6333 | 146.3704 | 135.663 | 0 | 199.7097 | 6040652.7966 | 461401.5399 | 6698691.6249 | 6665390.5254 | 0 | 363430.1172 | 0 | 7889530.9756 | 20526941.2331 | 14010059.178 | 62656097.9907 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82369854.7012 | 110983517.3246 | 7498942.0933 | 15.4577 | 5328.7265 | 7179.8209 | 108.6333 | 146.3704
1 | 5100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.7586 | 41.8893 | 3.8672 | 4 | 5326.1825 | 7175.9537 | 108.5814 | 146.2915 | 135.6607 | 0 | 199.6987 | 6042574.9809 | 461539.1162 | 6701188.317 | 6668546.5815 | 0 | 362037.869 | 0 | 7891995.8772 | 20533354.4015 | 14014436.2973 | 62675673.4406 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 82389430.151 | 111003092.7744 | 10000000 | 15.4688 | 5326.1825 | 7175.9537 | 108.5814 | 146.2915
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5946 | [19 empty] | 100 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.538 | [19 empty] | 133.3521 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6461 | [19 empty] | 177.8279 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.709 | [19 empty] | 237.1374 | 0
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.28468 | 0.0057611 | 4 | 937910.9531 | 2210262.9637 | 19120.5834 | 45059.2001 | 105.2093 | 0 | 27.5463 | 153035.1868 | 9837.7329 | 126247.0069 | 80150.5843 | 0 | 81093.8448 | 0 | 175642.0988 | 456984.7118 | 311901.4559 | 1394892.6223 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21613638.477 | 50934285.9025 | 316.2278 | 0.023044 | 937910.9531 | 2210262.9637 | 19120.5834 | 45059.2001
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.45212 | 0.014613 | 4 | 379072.251 | 880705.5233 | 7727.9006 | 17954.3733 | 113.4779 | 0 | 348.8336 | 222124.2359 | 15014.9568 | 181705.0543 | 107131.5362 | 0 | 99793.2023 | 0 | 244049.9044 | 634967.7896 | 433378.5637 | 1938165.2432 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22156911.0979 | 51477558.5234 | 421.6965 | 0.05845 | 379072.251 | 880705.5233 | 7727.9006 | 17954.3733
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9155 | 0.65056 | 0.027441 | 4 | 207128.5119 | 474257.4794 | 4222.5949 | 9668.3802 | 119.1814 | 0 | 458.7772 | 295646.5718 | 20697.4266 | 242129.9278 | 138502.0423 | 0 | 115396.3501 | 0 | 316825.2043 | 824314.1917 | 562611.3738 | 2516123.0884 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22734868.9432 | 52055516.3686 | 562.3413 | 0.10976 | 207128.5119 | 474257.4794 | 4222.5949 | 9668.3802
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8459 | 0.92058 | 0.045775 | 4 | 128143.4749 | 288278.3535 | 2612.3781 | 5876.9442 | 123.8551 | 0 | 73.8852 | 386262.7925 | 27833.9596 | 318615.9486 | 180577.3366 | 0 | 134181.5998 | 0 | 408513.9385 | 1062869.4702 | 725430.2532 | 3244285.299 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 23463031.1537 | 52783678.5791 | 749.8942 | 0.1831 | 128143.4749 | 288278.3535 | 2612.3781 | 5876.9442
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0984 | 1.2907 | 0.071628 | 4 | 85146.4602 | 187482.9738 | 1735.8258 | 3822.094 | 127.6443 | 0 | 77.7046 | 499048.7438 | 36840.7647 | 416403.5783 | 238654.7044 | 0 | 157583.5596 | 0 | 525927.2268 | 1368354.7616 | 933930.2417 | 4176743.5809 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 24395489.4356 | 53716136.861 | 1000 | 0.28651 | 85146.4602 | 187482.9738 | 1735.8258 | 3822.094
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7379 | 1.7786 | 0.10658 | 4 | 59908.5296 | 128682.6918 | 1221.3164 | 2623.3707 | 130.558 | 0 | 67.6384 | 633995.904 | 47678.1733 | 537102.8939 | 314647.3924 | 0 | 184935.3919 | 0 | 670160.3046 | 1743619.6438 | 1190056.2347 | 5322195.9386 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 25540941.7933 | 54861589.2188 | 1333.5214 | 0.42633 | 59908.5296 | 128682.6918 | 1221.3164 | 2623.3707
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9474 | 2.4355 | 0.15342 | 4 | 43974.8186 | 91752.6154 | 896.4862 | 1870.5012 | 132.7481 | 0 | 86.0207 | 798869.9546 | 60904.1527 | 689622.1422 | 416419.559 | 0 | 219365.4436 | 0 | 852220.6883 | 2217303.4165 | 1513355.1428 | 6768060.4997 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 26986806.3544 | 56307453.7798 | 1778.2794 | 0.61369 | 43974.8186 | 91752.6154 | 896.4862 | 1870.5012
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8922 | 3.3285 | 0.21897 | 4 | 32920.45 | 66395.3415 | 671.1279 | 1353.5588 | 134.7363 | 0 | 73.8645 | 1004671.343 | 77555.2214 | 884187.9724 | 554556.0987 | 0 | 260934.745 | 0 | 1084943.0984 | 2822799.3897 | 1926618.5862 | 8616266.455 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 28835012.3098 | 58155659.7352 | 2371.3737 | 0.8759 | 32920.45 | 66395.3415 | 671.1279 | 1353.5588
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7757 | 4.5003 | 0.30488 | 4 | 25517.8571 | 49560.5916 | 520.216 | 1010.3597 | 136.1106 | 0 | 89.7483 | 1250530.3902 | 97342.3344 | 1124419.6695 | 736315.5226 | 0 | 310912.1708 | 0 | 1372612.8341 | 3571257.0328 | 2437456.3069 | 10900846.2612 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 31119592.1159 | 60440239.5413 | 3162.2777 | 1.2195 | 25517.8571 | 49560.5916 | 520.216 | 1010.3597
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9495 | 6.0619 | 0.41927 | 4 | 20269.6432 | 37752.913 | 413.2241 | 769.6442 | 137.165 | 0 | 98.2833 | 1550294.4885 | 121386.3251 | 1425963.5042 | 977491.2627 | 0 | 372301.9084 | 0 | 1734500.6206 | 4512814.8199 | 3080088.8437 | 13774841.773 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 33993587.6277 | 63314235.0532 | 4216.965 | 1.6771 | 20269.6432 | 37752.913 | 413.2241 | 769.6442
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.7831 | 8.1191 | 0.56952 | 4 | 16488.1114 | 29358.8612 | 336.1325 | 598.5201 | 137.9659 | 0 | 93.7639 | 1911689.8346 | 150199.0493 | 1800554.3573 | 1290318.111 | 0 | 446571.8206 | 0 | 2183739.9374 | 5681643.3705 | 3877838.3464 | 17342554.8271 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 37561300.6818 | 66881948.1073 | 5623.4133 | 2.2781 | 16488.1114 | 29358.8612 | 336.1325 | 598.5201
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.7185 | 10.8152 | 0.76692 | 4 | 13692.7574 | 23250.6286 | 279.1454 | 473.9955 | 138.5711 | 0 | 80.4224 | 2347152.6338 | 184806.9213 | 2263919.6907 | 1702630.0287 | 0 | 535618.2694 | 0 | 2743309.7421 | 7137529.2188 | 4871510.3534 | 21786476.8583 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 42005222.7131 | 71325870.1385 | 7498.9421 | 3.0677 | 13692.7574 | 23250.6286 | 279.1454 | 473.9955
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.2849 | 14.3067 | 1.0223 | 4 | 11611.482 | 18781.7832 | 236.7158 | 382.8921 | 139.0219 | 0 | 79.8153 | 2866432.7533 | 225907.2966 | 2830984.092 | 2236996.2864 | 0 | 641892.7135 | 0 | 3432863.1254 | 8931605.6751 | 6096004.3994 | 27262686.3418 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 47481432.1965 | 76802079.622 | 10000 | 4.0892 | 11611.482 | 18781.7832 | 236.7158 | 382.8921
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3381 | 17.943 | 1.315 | 4 | 10051.6061 | 15625.865 | 204.9156 | 318.5544 | 139.2794 | 0 | 111.5328 | 3369344.7814 | 265573.7592 | 3392648.7702 | 2797816.7817 | 0 | 717111.9502 | 0 | 4111573.4567 | 10697470.7346 | 7301243.5874 | 32652783.8214 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 52871529.6761 | 82192177.1016 | 13335.2143 | 5.26 | 10051.6061 | 15625.865 | 204.9156 | 318.5544
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8332 | 21.393 | 1.6274 | 4 | 8865.0867 | 13369.3682 | 180.7268 | 272.5527 | 139.3843 | 0 | 121.252 | 3818518.7142 | 300760.6349 | 3904870.056 | 3330357.5774 | 0 | 749309.32 | 0 | 4720488.358 | 12281742.4021 | 8382541.554 | 37488588.6165 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 57707334.4713 | 87027981.8967 | 17782.7941 | 6.5095 | 8865.0867 | 13369.3682 | 180.7268 | 272.5527
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.3944 | 24.8332 | 1.9574 | 4 | 7962.4921 | 11707.4047 | 162.3262 | 238.6713 | 139.3762 | 0 | 135.2996 | 4244169.2729 | 333818.6484 | 4399655.9533 | 3862116.8629 | 0 | 760441.7283 | 0 | 5304078.9617 | 13800125.4422 | 9418869.1786 | 42123276.0485 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 62342021.9032 | 91662669.3287 | 23713.7371 | 7.8295 | 7962.4921 | 11707.4047 | 162.3262 | 238.6713
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.4077 | 28.0736 | 2.2861 | 4 | 7277.8193 | 10484.2762 | 148.3682 | 213.7362 | 139.2773 | 0 | 143.2915 | 4627586.2392 | 363292.3676 | 4853580.2621 | 4363890.3402 | 0 | 750536.527 | 0 | 5833965.4371 | 15178781.3564 | 10359830.1685 | 46331462.6982 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 66550208.5529 | 95870855.9783 | 31622.7766 | 9.1443 | 7277.8193 | 10484.2762 | 148.3682 | 213.7362
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4607 | 30.9938 | 2.5971 | 4 | 6759.5863 | 9582.0672 | 137.8033 | 195.3434 | 139.119 | 0 | 163.569 | 4960165.6333 | 388575.8148 | 5254055.6876 | 4817043.9349 | 0 | 723993.4809 | 0 | 6296095.4751 | 16381148.9195 | 11180470.7365 | 50001549.6828 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 70220295.5375 | 99540942.9629 | 42169.6503 | 10.3883 | 6759.5863 | 9582.0672 | 137.8033 | 195.3434
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3593 | 33.5472 | 2.8796 | 4 | 6367.7733 | 8913.2951 | 129.8157 | 181.7096 | 138.9305 | 0 | 189.7427 | 5241988.2342 | 409790.3615 | 5598305.594 | 5216110.4026 | 0 | 687256.426 | 0 | 6689845.8971 | 17405606.7483 | 11879684.2552 | 53128587.9189 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 73347333.7737 | 102667981.1991 | 56234.1325 | 11.5185 | 6367.7733 | 8913.2951 | 129.8157 | 181.7096
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7601 | 35.6492 | 3.1236 | 4 | 6071.7005 | 8418.4037 | 123.7798 | 171.6205 | 138.7423 | 0 | 199.877 | 5468466.3746 | 426719.3698 | 5877923.5241 | 5549521.5542 | 0 | 642804.6614 | 0 | 7006519.8388 | 18229527.3857 | 12442027.0201 | 55643509.7286 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 75862255.5834 | 105182903.0088 | 74989.4209 | 12.4944 | 6071.7005 | 8418.4037 | 123.7798 | 171.6205
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.777 | 37.3408 | 3.3274 | 4 | 5848.4333 | 8051.435 | 119.2282 | 164.1394 | 138.5697 | 0 | 212.9003 | 5647065.6711 | 439961.7872 | 6100699.5212 | 5819533.3557 | 0 | 596457.9696 | 0 | 7255450.1389 | 18877192.964 | 12884072.0854 | 57620433.4932 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 77839179.3479 | 107159826.7733 | 100000 | 13.3094 | 5848.4333 | 8051.435 | 119.2282 | 164.1394
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5908 | 38.6826 | 3.4936 | 4 | 5680.1618 | 7778.3531 | 115.7978 | 158.5722 | 138.4196 | 0 | 169.2851 | 5786483.0466 | 450227.9874 | 6276060.6726 | 6034860.4611 | 0 | 552271.801 | 0 | 7448962.5478 | 19380672.557 | 13227707.2532 | 59157246.3267 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 79375992.1814 | 108696639.6069 | 133352.1432 | 13.9742 | 5680.1618 | 7778.3531 | 115.7978 | 158.5722
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1667 | 40.2295 | 3.6573 | 4 | 5552.8528 | 7557.09 | 113.2024 | 154.0615 | 138.2446 | 0 | 176.0161 | 5945152.137 | 461868.1813 | 6476781.7303 | 6283857.3099 | 0 | 532300.5783 | 0 | 7682984.3753 | 19989549.3478 | 13643278.1741 | 61015771.834 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 81234517.6887 | 110555165.1141 | 177827.941 | 14.6293 | 5552.8528 | 7557.09 | 113.2024 | 154.0615
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2756 | 41.0919 | 3.7665 | 4 | 5455.838 | 7401.9667 | 111.2246 | 150.8991 | 138.1528 | 0 | 184.5097 | 6032884.0249 | 468304.8304 | 6588020.3379 | 6422703.4541 | 0 | 499258.7562 | 0 | 7804356.8474 | 20305335.6231 | 13858808.7957 | 61979672.6697 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82198418.5244 | 111519065.9498 | 237137.3706 | 15.0661 | 5455.838 | 7401.9667 | 111.2246 | 150.8991
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.6554 | 41.7498 | 3.8513 | 4 | 5382.7819 | 7286.0681 | 109.7353 | 148.5364 | 138.0807 | 0 | 194.5805 | 6099324.6939 | 473165.1866 | 6672570.2348 | 6528851.5941 | 0 | 471278.6599 | 0 | 7895624.244 | 20542794.6677 | 14020879.4729 | 62704488.754 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82923234.6087 | 112243882.0341 | 316227.766 | 15.4053 | 5382.7819 | 7286.0681 | 109.7353 | 148.5364
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4601 | 42.2472 | 3.9164 | 4 | 5327.8019 | 7199.4365 | 108.6144 | 146.7703 | 138.0251 | 0 | 216.8892 | 6149296.5628 | 476812.5419 | 6736339.6077 | 6609263.8549 | 0 | 448158.7416 | 0 | 7963749.8104 | 20720043.4171 | 14141855.3865 | 63245519.9228 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 83464265.7776 | 112784913.203 | 421696.5034 | 15.6658 | 5327.8019 | 7199.4365 | 108.6144 | 146.7703
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8024 | 42.6169 | 3.9659 | 4 | 5286.4491 | 7134.763 | 107.7714 | 145.4518 | 137.9831 | 0 | 216.5361 | 6186308.7274 | 479511.7862 | 6783638.1035 | 6669382.0508 | 0 | 429238.0167 | 0 | 8013750.687 | 20850135.4413 | 14230645.8661 | 63642610.679 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 83861356.5337 | 113182003.9592 | 562341.3252 | 15.8635 | 5286.4491 | 7134.763 | 107.7714 | 145.4518
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.8307 | 42.9003 | 4.0038 | 4 | 5255.3635 | 7086.1702 | 107.1377 | 144.4612 | 137.9506 | 0 | 202.9468 | 6214618.7435 | 481576.6095 | 6819834.9528 | 6715830.1928 | 0 | 414398.0902 | 0 | 8052040.8496 | 20949758.59 | 14298640.7122 | 63946698.7406 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84165444.5953 | 113486092.0207 | 749894.2093 | 16.0152 | 5255.3635 | 7086.1702 | 107.1377 | 144.4612
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.5929 | 43.11 | 4.0323 | 4 | 5232.0067 | 7049.8692 | 106.6615 | 143.7211 | 137.9264 | 0 | 203.9667 | 6235530.2469 | 483100.3565 | 6846603.398 | 6750252.392 | 0 | 402635.2112 | 0 | 8080067.4258 | 21022677.9923 | 14348409.7026 | 64169276.7253 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84388022.58 | 113708670.0054 | 1000000 | 16.1292 | 5232.0067 | 7049.8692 | 106.6615 | 143.7211
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1607 | 43.2662 | 4.0537 | 4 | 5214.4638 | 7022.7104 | 106.3039 | 143.1675 | 137.9082 | 0 | 184.4409 | 6251071.2425 | 484231.9673 | 6866514.4132 | 6775896.6238 | 0 | 393455.5102 | 0 | 8100756.2052 | 21076505.9524 | 14385148.3914 | 64333580.306 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84552326.1607 | 113872973.5861 | 1333521.4322 | 16.215 | 5214.4638 | 7022.7104 | 106.3039 | 143.1675
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.5823 | 43.382 | 4.0698 | 4 | 5201.292 | 7002.3957 | 106.0354 | 142.7533 | 137.8947 | 0 | 188.551 | 6262586.006 | 485069.961 | 6881276.6157 | 6794931.7223 | 0 | 386337.2669 | 0 | 8115978.613 | 21116111.5349 | 14412180.0153 | 64454471.735 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84673217.5897 | 113993865.0151 | 1778279.41 | 16.2793 | 5201.292 | 7002.3957 | 106.0354 | 142.7533
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.8964 | 43.4683 | 4.0819 | 4 | 5191.4047 | 6987.1866 | 105.8338 | 142.4432 | 137.8845 | 0 | 202.0648 | 6271154.3186 | 485693.2764 | 6892266.6912 | 6809115.1665 | 0 | 380868.3927 | 0 | 8127248.1597 | 21145432.5837 | 14432192.2336 | 64543970.8224 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84762716.6771 | 114083364.1026 | 2371373.7057 | 16.3275 | 5191.4047 | 6987.1866 | 105.8338 | 142.4432
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1398 | 43.5351 | 4.0911 | 4 | 5183.9847 | 6975.7243 | 105.6825 | 142.2096 | 137.8767 | 0 | 193.7634 | 6277786.4723 | 486175.6092 | 6900776.3146 | 6820104.3836 | 0 | 376791.4532 | 0 | 8136037.3508 | 21168300.2561 | 14447799.8899 | 64613771.7297 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84832517.5844 | 114153165.0098 | 3162277.6602 | 16.3643 | 5183.9847 | 6975.7243 | 105.6825 | 142.2096
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3056 | 43.5807 | 4.0977 | 4 | 5178.4171 | 6967.2633 | 105.569 | 142.0371 | 137.8713 | 0 | 179.6017 | 6282299.5329 | 486503.7336 | 6906568.7933 | 6827588.7804 | 0 | 373511.977 | 0 | 8141824.3987 | 21183356.9676 | 14458076.4048 | 64659730.5883 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84878476.443 | 114199123.8684 | 4216965.0343 | 16.3908 | 5178.4171 | 6967.2633 | 105.569 | 142.0371
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.4519 | 43.6208 | 4.1031 | 4 | 5174.2401 | 6960.7468 | 105.4839 | 141.9042 | 137.8666 | 0 | 163.6178 | 6286281.5869 | 486793.2343 | 6911680.3444 | 6834195.0953 | 0 | 371276.9435 | 0 | 8147188.6097 | 21197313.5443 | 14467602.0552 | 64702331.4136 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84921077.2683 | 114241724.6937 | 5623413.2519 | 16.4123 | 5174.2401 | 6960.7468 | 105.4839 | 141.9042
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5419 | 43.6455 | 4.1067 | 4 | 5171.1067 | 6956.0156 | 105.42 | 141.8078 | 137.8637 | 0 | 195.3683 | 6288729.3438 | 486971.1424 | 6914823.2062 | 6838258.6679 | 0 | 369369.7266 | 0 | 8150279.3139 | 21205354.9226 | 14473090.4611 | 64726876.7844 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84945622.6391 | 114266270.0646 | 7498942.0933 | 16.427 | 5171.1067 | 6956.0156 | 105.42 | 141.8078
1 | 5200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.6151 | 43.6656 | 4.1096 | 4 | 5168.7564 | 6952.4237 | 105.3721 | 141.7346 | 137.8613 | 0 | 189.8836 | 6290718.573 | 487115.7196 | 6917377.4877 | 6841561.6839 | 0 | 367995.8941 | 0 | 8152860.0497 | 21212069.4678 | 14477673.2762 | 64747372.1521 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 84966118.0068 | 114286765.4322 | 10000000 | 16.4384 | 5168.7564 | 6952.4237 | 105.3721 | 141.7346
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5265 | [19 empty] | 100 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2956 | [19 empty] | 133.3521 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3655 | [19 empty] | 177.8279 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.5669 | [19 empty] | 237.1374 | 0
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.32556 | 0.0074639 | 4 | 745910.3029 | 1751945.0533 | 15206.3904 | 35715.7696 | 108.5532 | 0 | 260.347 | 171613.605 | 11254.1547 | 140216.0989 | 86344.4934 | 0 | 87803.4331 | 0 | 193920.3962 | 504541.0923 | 344359.6627 | 1540052.9362 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22269648.026 | 52305484.3807 | 316.2278 | 0.029856 | 745910.3029 | 1751945.0533 | 15206.3904 | 35715.7696
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.47353 | 0.016896 | 4 | 336329.8166 | 780753.4634 | 6856.5382 | 15916.7154 | 115.2938 | 0 | 355.9651 | 231860.3829 | 15842.785 | 188313.2552 | 109846.7929 | 0 | 100144.6126 | 0 | 251943.0531 | 655504.1436 | 447395.0473 | 2000850.0726 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22730445.1625 | 52766281.5171 | 421.6965 | 0.067584 | 336329.8166 | 780753.4634 | 6856.5382 | 15916.7154
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9739 | 0.68388 | 0.031038 | 4 | 187976.9872 | 429907.9186 | 3832.1651 | 8764.2544 | 121.1537 | 0 | 462.6378 | 309502.9833 | 21927.0165 | 251653.7042 | 142731.9158 | 0 | 116167.1915 | 0 | 328373.2964 | 854359.9586 | 583118.2271 | 2607834.2934 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23337429.3833 | 53373265.7379 | 562.3413 | 0.12415 | 187976.9872 | 429907.9186 | 3832.1651 | 8764.2544
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 0.96708 | 0.051156 | 4 | 117745.5919 | 264530.1151 | 2400.4032 | 5392.8042 | 125.894 | 0 | 70.6978 | 404228.3906 | 29501.1895 | 330952.1063 | 186572.6732 | 0 | 134914.1808 | 0 | 423605.7308 | 1102135.218 | 752229.9329 | 3364139.4222 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 24093734.5121 | 54129570.8667 | 749.8942 | 0.20463 | 117745.5919 | 264530.1151 | 2400.4032 | 5392.8042
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1884 | 1.3536 | 0.079343 | 4 | 78949.8251 | 173589.435 | 1609.499 | 3538.8554 | 129.7348 | 0 | 89.4037 | 521575.0225 | 39010.9589 | 431952.3139 | 246275.5683 | 0 | 158153.9948 | 0 | 544817.4647 | 1417503.2858 | 967475.1194 | 4326763.7283 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 25056358.8182 | 55092195.1728 | 1000 | 0.31737 | 78949.8251 | 173589.435 | 1609.499 | 3538.8554
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8622 | 1.8668 | 0.11751 | 4 | 55840.7767 | 119739.838 | 1138.3898 | 2441.0586 | 132.7064 | 0 | 70.1578 | 662979.1655 | 50537.0997 | 557492.5101 | 324905.7198 | 0 | 185804.0601 | 0 | 694870.2366 | 1807909.8181 | 1233935.5997 | 5518434.2097 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 26248029.2996 | 56283865.6542 | 1333.5214 | 0.47005 | 55840.7767 | 119739.838 | 1138.3898 | 2441.0586
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1131 | 2.5611 | 0.16947 | 4 | 40955.6354 | 85264.9569 | 834.936 | 1738.2415 | 135.0311 | 0 | 77.4248 | 837153.0621 | 64777.1743 | 716809.1008 | 431607.2432 | 0 | 220338.4877 | 0 | 885567.1765 | 2304064.1385 | 1572571.1183 | 7032887.5014 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 27762482.5913 | 57798318.9459 | 1778.2794 | 0.67787 | 40955.6354 | 85264.9569 | 834.936 | 1738.2415
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0969 | 3.4914 | 0.24043 | 4 | 30850.2608 | 62081.9157 | 628.9243 | 1265.6238 | 136.9612 | 0 | 72.1149 | 1050682.5528 | 82316.1647 | 917225.6303 | 574272.4113 | 0 | 261753.8804 | 0 | 1125637.7494 | 2928678.5239 | 1998883.2709 | 8939450.1837 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 29669045.2736 | 59704881.6282 | 2371.3737 | 0.96171 | 30850.2608 | 62081.9157 | 628.9243 | 1265.6238
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0682 | 4.7202 | 0.33342 | 4 | 24012.661 | 46533.8695 | 489.5306 | 948.6559 | 138.3681 | 0 | 60.1912 | 1307056.3186 | 103204.8519 | 1166433.0634 | 757838.9463 | 0 | 312357.4245 | 0 | 1422287.3358 | 3700499.8964 | 2525667.217 | 11295345.0537 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 32024940.1436 | 62060776.4982 | 3162.2777 | 1.3337 | 24012.661 | 46533.8695 | 489.5306 | 948.6559
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3199 | 6.3543 | 0.45792 | 4 | 19106.589 | 35504.4635 | 389.5137 | 723.8065 | 139.439 | 0 | 93.2187 | 1619757.1494 | 128669.6416 | 1478513.8544 | 1006010.0824 | 0 | 373636.4272 | 0 | 1796568.9904 | 4674303.9862 | 3190308.5179 | 14267768.6495 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 34997363.7394 | 65033200.094 | 4216.965 | 1.8317 | 19106.589 | 35504.4635 | 389.5137 | 723.8065
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2506 | 8.5146 | 0.623 | 4 | 15539.6292 | 27592.5614 | 316.7964 | 562.5117 | 140.2531 | 0 | 85.9494 | 1999240.8735 | 159505.7529 | 1867446.1017 | 1335936.3165 | 0 | 447879.5154 | 0 | 2265903.3384 | 5895415.6858 | 4023742.3442 | 17995069.9284 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 38724665.0182 | 68760501.3729 | 5623.4133 | 2.492 | 15539.6292 | 27592.5614 | 316.7964 | 562.5117
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.3226 | 11.3382 | 0.83849 | 4 | 12920.8853 | 21876.1923 | 263.4097 | 445.9758 | 140.8697 | 0 | 89.8438 | 2454592.6477 | 196315.629 | 2347313.9709 | 1763670.7437 | 0 | 537049.0265 | 0 | 2846587.3869 | 7406236.4654 | 5054908.5706 | 22606674.4408 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 43336269.5306 | 73372105.8852 | 7498.9421 | 3.354 | 12920.8853 | 21876.1923 | 263.4097 | 445.9758
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.0548 | 14.9941 | 1.1174 | 4 | 10968.7182 | 17688.9611 | 223.6122 | 360.6134 | 141.3277 | 0 | 81.5774 | 2997719.1844 | 240055.0402 | 2934493.8026 | 2319632.0074 | 0 | 643489.6369 | 0 | 3562801.9719 | 9269679.8997 | 6326747.0044 | 28294618.5475 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 49024213.6374 | 79060049.992 | 10000 | 4.4695 | 10968.7182 | 17688.9611 | 223.6122 | 360.6134
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.0519 | 19.3469 | 1.4569 | 4 | 9517.9933 | 14671.9111 | 194.0372 | 299.1068 | 141.6099 | 0 | 78.2657 | 3595639.78 | 287929.9091 | 3597488.7716 | 2982815.5021 | 0 | 752211.4506 | 0 | 4374273.3112 | 11380961.8689 | 7767740.3309 | 34739060.9245 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 55468656.0143 | 85504492.3689 | 13335.2143 | 5.8278 | 9517.9933 | 14671.9111 | 194.0372 | 299.1068
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.7102 | 22.9493 | 1.7935 | 4 | 8425.4891 | 12612.3119 | 171.765 | 257.119 | 141.6901 | 0 | 105.7874 | 4059850.9765 | 324804.222 | 4123841.2519 | 3532664.2555 | 0 | 781166.4641 | 0 | 5000707.5963 | 13010815.3793 | 8880148.8419 | 39713998.9875 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 60443594.0773 | 90479430.432 | 17782.7941 | 7.1739 | 8425.4891 | 12612.3119 | 171.765 | 257.119
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.3419 | 26.5097 | 2.1454 | 4 | 7594.4315 | 11094.3822 | 154.8228 | 226.174 | 141.6555 | 0 | 141.7499 | 4496361.248 | 359156.6528 | 4628295.8757 | 4077532.1746 | 0 | 788208.7834 | 0 | 5596326.3464 | 14560493.189 | 9937835.7897 | 44444210.0596 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 65173805.1494 | 95209641.504 | 23713.7371 | 8.5818 | 7594.4315 | 11094.3822 | 154.8228 | 226.174
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.3501 | 29.839 | 2.4929 | 4 | 6964.0064 | 9976.1353 | 141.9707 | 203.377 | 141.5316 | 0 | 168.9985 | 4887159.1423 | 389578.2368 | 5088177.4815 | 4588758.1167 | 0 | 774101.1281 | 0 | 6133831.9011 | 15958972.3847 | 10892326.5767 | 48712904.9678 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 69442500.0577 | 99478336.4123 | 31622.7766 | 9.9716 | 6964.0064 | 9976.1353 | 141.9707 | 203.377
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.2964 | 32.8074 | 2.8184 | 4 | 6486.7768 | 9151.0871 | 132.2417 | 186.5573 | 141.3529 | 0 | 188.4846 | 5222922.8798 | 415414.3083 | 5489944.3974 | 5046327.7048 | 0 | 743099.6063 | 0 | 6597906.4697 | 17166399.2174 | 11716420.2001 | 52398434.7839 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 73128029.8737 | 103163866.2284 | 42169.6503 | 11.2734 | 6486.7768 | 9151.0871 | 132.2417 | 186.5573
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9151 | 35.3459 | 3.1092 | 4 | 6126.0495 | 8541.118 | 124.8878 | 174.1222 | 141.1522 | 0 | 167.6137 | 5501311.405 | 436591.8033 | 5828046.4774 | 5439146.9634 | 0 | 700812.8185 | 0 | 6983304.6924 | 18169126.3368 | 12400802.0631 | 55459142.5598 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 76188737.6497 | 106224574.0043 | 56234.1325 | 12.4368 | 6126.0495 | 8541.118 | 124.8878 | 174.1222
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.189 | 37.4633 | 3.3603 | 4 | 5853.6503 | 8088.2389 | 119.3346 | 164.8897 | 140.9525 | 0 | 197.5794 | 5727784.6949 | 453645.0991 | 6106568.5382 | 5768793.0935 | 0 | 653731.8857 | 0 | 7297104.0914 | 18985568.0041 | 12958040.2772 | 57951235.6841 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 78680830.774 | 108716667.1286 | 74989.4209 | 13.4413 | 5853.6503 | 8088.2389 | 119.3346 | 164.8897
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0692 | 39.1605 | 3.5693 | 4 | 5648.0161 | 7751.7993 | 115.1424 | 158.0309 | 140.7721 | 0 | 177.8837 | 5905896.5485 | 466957.3718 | 6327676.3447 | 6036357.5494 | 0 | 605235.8337 | 0 | 7543428.2228 | 19626452.8658 | 13395457.3642 | 59907462.1009 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 80637057.1907 | 110672893.5453 | 100000 | 14.2771 | 5648.0161 | 7751.7993 | 115.1424 | 158.0309
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.7218 | 40.4919 | 3.7383 | 4 | 5492.9753 | 7501.6194 | 111.9817 | 152.9307 | 140.618 | 0 | 216.6564 | 6043436.3185 | 477159.5324 | 6499877.17 | 6247252.1179 | 0 | 559018.8253 | 0 | 7732430.146 | 20118197.1005 | 13731082.9087 | 61408454.1194 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 82138049.2093 | 112173885.5639 | 133352.1432 | 14.9533 | 5492.9753 | 7501.6194 | 111.9817 | 152.9307
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3445 | 42.0998 | 3.9098 | 4 | 5374.5775 | 7295.1113 | 109.568 | 148.7207 | 140.443 | 0 | 192.9597 | 6207836.2223 | 489349.2315 | 6706357.6995 | 6502087.5448 | 0 | 539941.3219 | 0 | 7973773.0878 | 20746121.9287 | 14159654.5065 | 63325121.5429 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 84054716.6328 | 114090552.9874 | 177827.941 | 15.6393 | 5374.5775 | 7295.1113 | 109.568 | 148.7207
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3607 | 42.9596 | 4.0209 | 4 | 5285.0622 | 7152.5599 | 107.7431 | 145.8146 | 140.3495 | 0 | 176.6083 | 6294867.4258 | 495784.3613 | 6816140.6782 | 6638610.6113 | 0 | 506053.5394 | 0 | 8093068.0802 | 21056503.0281 | 14371495.9846 | 64272523.7088 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 85002118.7986 | 115037955.1533 | 237137.3706 | 16.0835 | 5285.0622 | 7152.5599 | 107.7431 | 145.8146
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.6233 | 43.6023 | 4.1061 | 4 | 5217.6444 | 7046.3705 | 106.3687 | 143.6498 | 140.2777 | 0 | 223.9882 | 6359471.262 | 500546.2522 | 6897930.4429 | 6740861.5964 | 0 | 476995.8214 | 0 | 8180564.0962 | 21284149.7139 | 14526869.5253 | 64967388.7104 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 85696983.8003 | 115732820.1549 | 316227.766 | 16.4245 | 5217.6444 | 7046.3705 | 106.3687 | 143.6498
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.3554 | 44.0931 | 4.1718 | 4 | 5166.9119 | 6966.8282 | 105.3345 | 142.0282 | 140.222 | 0 | 218.2778 | 6408558.7273 | 504156.4408 | 6960239.4316 | 6819060.9694 | 0 | 453324.1866 | 0 | 8246682.5047 | 21456176.25 | 14644281.171 | 65492479.6814 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 86222074.7712 | 116257911.1258 | 421696.5034 | 16.6874 | 5166.9119 | 6966.8282 | 105.3345 | 142.0282
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.6466 | 44.4582 | 4.2216 | 4 | 5128.7526 | 6907.435 | 104.5566 | 140.8174 | 140.18 | 0 | 195.5594 | 6444931.2414 | 506826.5842 | 7006505.3918 | 6877300.0974 | 0 | 434061.9223 | 0 | 8295153.8425 | 21582288.728 | 14730355.5286 | 65877423.3361 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 86607018.426 | 116642854.7806 | 562341.3252 | 16.8866 | 5128.7526 | 6907.435 | 104.5566 | 140.8174
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6212 | 44.7333 | 4.2595 | 4 | 5100.0653 | 6862.945 | 103.9717 | 139.9104 | 140.148 | 0 | 195.8996 | 6472264.4628 | 508830.3772 | 7041327.7417 | 6921232.0931 | 0 | 418821.2678 | 0 | 8331365.6176 | 21676504.3389 | 14794659.6189 | 66165005.5181 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 86894600.6079 | 116930436.9626 | 749894.2093 | 17.0379 | 5100.0653 | 6862.945 | 103.9717 | 139.9104
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3593 | 44.9415 | 4.2882 | 4 | 5078.5087 | 6829.5779 | 103.5323 | 139.2302 | 140.1236 | 0 | 175.715 | 6492895.4674 | 510341.2521 | 7067642.5519 | 6954486.8116 | 0 | 406952.7896 | 0 | 8358604.3603 | 21747373.96 | 14843029.5915 | 66381326.7844 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87110921.8742 | 117146758.2289 | 1000000 | 17.1529 | 5078.5087 | 6829.5779 | 103.5323 | 139.2302
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8929 | 45.0918 | 4.3095 | 4 | 5062.3168 | 6804.733 | 103.2022 | 138.7237 | 140.1058 | 0 | 175.7706 | 6507772.5696 | 511429.8612 | 7086635.4178 | 6978518.9799 | 0 | 397517.4445 | 0 | 8377930.9665 | 21797657.8249 | 14877349.3625 | 66534812.4269 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87264407.5168 | 117300243.8714 | 1333521.4322 | 17.238 | 5062.3168 | 6804.733 | 103.2022 | 138.7237
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.2996 | 45.2063 | 4.3257 | 4 | 5050.1587 | 6786.0651 | 102.9543 | 138.3431 | 140.0922 | 0 | 194.0562 | 6519091.6838 | 512257.6485 | 7101095.2659 | 6996832.1615 | 0 | 390334.5441 | 0 | 8392648.4085 | 21835949.59 | 14903484.2791 | 66651693.5813 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87381288.6712 | 117417125.0258 | 1778279.41 | 17.3027 | 5050.1587 | 6786.0651 | 102.9543 | 138.3431
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.6091 | 45.2934 | 4.3379 | 4 | 5041.0321 | 6772.0396 | 102.7683 | 138.0572 | 140.0819 | 0 | 188.7849 | 6527692.731 | 512886.3863 | 7112088.2285 | 7010764.2732 | 0 | 384893.3294 | 0 | 8403846.7299 | 21865085.3252 | 14923370.017 | 66740627.0205 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87470222.1104 | 117506058.465 | 2371373.7057 | 17.3516 | 5041.0321 | 6772.0396 | 102.7683 | 138.0572
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8324 | 45.3562 | 4.3469 | 4 | 5034.1826 | 6761.5913 | 102.6286 | 137.8442 | 140.0744 | 0 | 217.7065 | 6533891.163 | 513339.3272 | 7120013.5388 | 7020813.9619 | 0 | 380651.5974 | 0 | 8411796.7395 | 21885769.6194 | 14937487.4728 | 66803763.4201 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87533358.51 | 117569194.8646 | 3162277.6602 | 17.3878 | 5034.1826 | 6761.5913 | 102.6286 | 137.8442
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.9982 | 45.4029 | 4.3537 | 4 | 5029.0431 | 6753.7704 | 102.5238 | 137.6847 | 140.0688 | 0 | 208.7549 | 6538489.4079 | 513675.2522 | 7125894.4786 | 7028274.163 | 0 | 377416.5031 | 0 | 8417662.4239 | 21901030.9271 | 14947903.6289 | 66850346.7848 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87579941.8747 | 117615778.2293 | 4216965.0343 | 17.4148 | 5029.0431 | 6753.7704 | 102.5238 | 137.6847
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.1251 | 45.4385 | 4.3588 | 4 | 5025.1872 | 6747.8874 | 102.4452 | 137.5648 | 140.0646 | 0 | 187.8878 | 6542006.819 | 513932.1746 | 7130393.9403 | 7033983.4874 | 0 | 374999.6784 | 0 | 8422173.2789 | 21912767.2464 | 14955913.908 | 66886170.5329 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87615765.6228 | 117651601.9774 | 5623413.2519 | 17.4353 | 5025.1872 | 6747.8874 | 102.4452 | 137.5648
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2345 | 45.4693 | 4.3629 | 4 | 5022.2946 | 6743.3704 | 102.3863 | 137.4727 | 140.0609 | 0 | 217.8739 | 6545040.4895 | 514153.7558 | 7134274.9226 | 7038908.8745 | 0 | 373339.4506 | 0 | 8426229.8223 | 21923321.5401 | 14963117.4303 | 66918386.2857 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87647981.3756 | 117683817.7302 | 7498942.0933 | 17.4518 | 5022.2946 | 6743.3704 | 102.3863 | 137.4727
1 | 5300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3077 | 45.4899 | 4.3659 | 4 | 5020.1249 | 6740.0496 | 102.342 | 137.405 | 140.0584 | 0 | 218.7972 | 6547067.1843 | 514301.7561 | 7136868.1792 | 7042200.7448 | 0 | 371986.1282 | 0 | 8428845.3571 | 21930126.6254 | 14967762.0408 | 66939158.016 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 87668753.1059 | 117704589.4605 | 10000000 | 17.4635 | 5020.1249 | 6740.0496 | 102.342 | 137.405
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7381 | [19 empty] | 100 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5242 | [19 empty] | 133.3521 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2076 | [19 empty] | 177.8279 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.419 | [19 empty] | 237.1374 | 0
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.33766 | 0.0089299 | 4 | 638938.2048 | 1500069.0008 | 13025.6195 | 30580.9356 | 110.0735 | 0 | 288.8805 | 177695.9871 | 11757.3923 | 144209.438 | 87847.044 | 0 | 87424.6358 | 0 | 198484.4539 | 516415.8343 | 352464.4182 | 1576299.2036 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 22822603.6195 | 53581833.0305 | 316.2278 | 0.03572 | 638938.2048 | 1500069.0008 | 13025.6195 | 30580.9356
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.50135 | 0.019461 | 4 | 299699.4364 | 694830.1846 | 6109.7784 | 14165.0531 | 117.308 | 0 | 403.9526 | 244073.2177 | 16878.931 | 196836.0468 | 113505.8273 | 0 | 101562.6623 | 0 | 262414.1072 | 682747.6784 | 465989.3196 | 2084007.7902 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23330312.2061 | 54089541.6171 | 421.6965 | 0.077846 | 299699.4364 | 694830.1846 | 6109.7784 | 14165.0531
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 0.71794 | 0.034791 | 4 | 172070.0963 | 393100.7996 | 3507.8817 | 8013.8915 | 123.1244 | 0 | 513.8975 | 323537.314 | 23189.9516 | 261283.4153 | 146676.8508 | 0 | 116870.0135 | 0 | 339907.4426 | 884369.4411 | 603600.3155 | 2699434.7443 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23945739.1602 | 54704968.5712 | 562.3413 | 0.13916 | 172070.0963 | 393100.7996 | 3507.8817 | 8013.8915
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 1.0148 | 0.056811 | 4 | 108833.9707 | 244192.182 | 2218.7277 | 4978.1879 | 127.931 | 0 | 73.2411 | 422580.9541 | 31235.5974 | 343473.7703 | 192481.4046 | 0 | 135571.1939 | 0 | 438883.739 | 1141885.4613 | 779360.2907 | 3485472.4114 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 24731776.8273 | 55491006.2383 | 749.8942 | 0.22724 | 108833.9707 | 244192.182 | 2218.7277 | 4978.1879
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2958 | 1.4241 | 0.087713 | 4 | 73368.0758 | 161038.1669 | 1495.7075 | 3282.9809 | 131.8637 | 0 | 80.9639 | 546346.3789 | 41422.1968 | 449192.7564 | 254960.5613 | 0 | 159374.8024 | 0 | 566005.7113 | 1472630.7572 | 1005100.7513 | 4495033.9156 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 25741338.3314 | 56500567.7425 | 1000 | 0.35085 | 73368.0758 | 161038.1669 | 1495.7075 | 3282.9809
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9937 | 1.9608 | 0.12926 | 4 | 52173.1554 | 111665.9479 | 1063.6203 | 2276.4614 | 134.8612 | 0 | 87.4231 | 693688.2186 | 53626.0801 | 578981.825 | 336375.062 | 0 | 186868.5176 | 0 | 721320.4843 | 1876727.937 | 1280905.3799 | 5728493.5045 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 26974797.9204 | 57734027.3314 | 1333.5214 | 0.51702 | 52173.1554 | 111665.9479 | 1063.6203 | 2276.4614
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 2.6892 | 0.18621 | 4 | 38325.4372 | 79622.6826 | 781.3159 | 1623.2161 | 137.2946 | 0 | 77.4451 | 876098.9151 | 68813.9475 | 744193.9678 | 446454.9034 | 0 | 221186.6008 | 0 | 919131.8505 | 2391392.5351 | 1632174.5434 | 7299447.2636 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 28545751.6794 | 59304981.0905 | 1778.2794 | 0.74483 | 38325.4372 | 79622.6826 | 781.3159 | 1623.2161
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 3.6572 | 0.26217 | 4 | 29080.9749 | 58412.5944 | 592.855 | 1190.8197 | 139.1891 | 0 | 77.1696 | 1096662.3521 | 87129.6321 | 950530.988 | 589538.0536 | 0 | 262681.9981 | 0 | 1164751.7793 | 3030445.2063 | 2068341.1227 | 9250081.1323 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 30496385.5481 | 61255614.9592 | 2371.3737 | 1.0487 | 29080.9749 | 58412.5944 | 592.855 | 1190.8197
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.348 | 4.9504 | 0.36443 | 4 | 22615.9687 | 43717.0696 | 461.0571 | 891.2316 | 140.6193 | 0 | 82.5654 | 1366653.4283 | 109587.0813 | 1209820.7987 | 784891.1576 | 0 | 313419.1947 | 0 | 1475904.9476 | 3840001.924 | 2620880.2173 | 11721158.7495 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 32967463.1653 | 63726692.5764 | 3162.2777 | 1.4577 | 22615.9687 | 43717.0696 | 461.0571 | 891.2316
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6754 | 6.6598 | 0.49997 | 4 | 18025.4471 | 33405.97 | 367.4731 | 681.0259 | 141.7077 | 0 | 83.56 | 1693169.9443 | 136646.5323 | 1532672.8231 | 1042185.9 | 0 | 374546.334 | 0 | 1863896.3981 | 4849476.0902 | 3309867.0783 | 14802461.1004 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 36048765.5162 | 66807994.9273 | 4216.965 | 1.9999 | 18025.4471 | 33405.97 | 367.4731 | 681.0259
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.7259 | 8.9258 | 0.67983 | 4 | 14681.0319 | 25992.3754 | 299.2927 | 529.8897 | 142.538 | 0 | 81.3209 | 2090433.1039 | 169486.3485 | 1936145.025 | 1384700.0529 | 0 | 449160.0654 | 0 | 2351670.5923 | 6118564.4872 | 4176045.9864 | 18676205.6616 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 39922510.0775 | 70681739.4885 | 5623.4133 | 2.7193 | 14681.0319 | 25992.3754 | 299.2927 | 529.8897
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.9365 | 11.887 | 0.91506 | 4 | 12218.8925 | 20622.5345 | 249.0987 | 420.4183 | 143.1657 | 0 | 76.1198 | 2567391.8476 | 208750.4351 | 2433780.9757 | 1831678.7195 | 0 | 538534.1533 | 0 | 2956253.0912 | 7691564.1324 | 5249650.5662 | 23477603.921 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 44723908.3368 | 75483137.7479 | 7498.9421 | 3.6602 | 12218.8925 | 20622.5345 | 249.0987 | 420.4183
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8396 | 15.711 | 1.2181 | 4 | 10388.7486 | 16701.9282 | 211.7887 | 340.4914 | 143.6306 | 0 | 93.4413 | 3134295.8499 | 255168.9115 | 3041237.5429 | 2406748.424 | 0 | 645148.1846 | 0 | 3698213.576 | 9621993.1169 | 6567208.0145 | 29370013.6204 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 50616318.0362 | 81375547.4473 | 10000 | 4.8722 | 10388.7486 | 16701.9282 | 211.7887 | 340.4914
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.8548 | 20.522 | 1.5973 | 4 | 9029.6159 | 13843.8655 | 184.0809 | 282.2259 | 143.9218 | 0 | 102.0919 | 3792371.5049 | 308703.7132 | 3765091.3563 | 3131166.5248 | 0 | 769790.5089 | 0 | 4589178.2072 | 11940100.3252 | 8149363.8165 | 36445765.957 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 57692070.3728 | 88451299.7839 | 13335.2143 | 6.3892 | 9029.6159 | 13843.8655 | 184.0809 | 282.2259
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.5996 | 24.5753 | 1.9718 | 4 | 8021.3124 | 11921.1815 | 163.5253 | 243.0294 | 143.9859 | 0 | 113.8381 | 4310675.3978 | 350484.4634 | 4348915.8556 | 3743502.7546 | 0 | 813203.4121 | 0 | 5291044.9346 | 13766213.5772 | 9395723.6338 | 42019764.0291 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 63266068.4449 | 94025297.856 | 17782.7941 | 7.8872 | 8021.3124 | 11921.1815 | 163.5253 | 243.0294
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.2728 | 28.2493 | 2.3461 | 4 | 7254.9824 | 10532.7186 | 147.9026 | 214.7237 | 143.9238 | 0 | 125.7617 | 4757187.3614 | 386103.6632 | 4861894.8904 | 4301056.1819 | 0 | 815722.7711 | 0 | 5897566.2985 | 15344257.7516 | 10472771.2084 | 46836560.1265 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 68082864.5423 | 98842093.9534 | 23713.7371 | 9.3843 | 7254.9824 | 10532.7186 | 147.9026 | 214.7237
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.242 | 31.6589 | 2.7123 | 4 | 6673.6512 | 9508.8609 | 136.0514 | 193.851 | 143.775 | 0 | 150.6271 | 5154388.762 | 417424.1637 | 5326480.1037 | 4821354.3404 | 0 | 796994.8664 | 0 | 6441490.4721 | 16759436.877 | 11438660.0405 | 51156229.6257 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 72402534.0416 | 103161763.4526 | 31622.7766 | 10.849 | 6673.6512 | 9508.8609 | 136.0514 | 193.851
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.0808 | 34.6764 | 3.0524 | 4 | 6233.5528 | 8752.8361 | 127.0794 | 178.4384 | 143.576 | 0 | 171.1485 | 5493483.6634 | 443839.5882 | 5729675.7476 | 5284615.8911 | 0 | 761612.0278 | 0 | 6908158.498 | 17973611.3537 | 12267359.0697 | 54862355.8394 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 76108660.2552 | 106867889.6663 | 42169.6503 | 12.2095 | 6233.5528 | 8752.8361 | 127.0794 | 178.4384
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5487 | 37.2395 | 3.3541 | 4 | 5900.8537 | 8193.49 | 120.2969 | 167.0354 | 143.3602 | 0 | 158.2708 | 5773029.6609 | 465359.3263 | 6066943.9133 | 5680512.3729 | 0 | 715462.3962 | 0 | 7293509.9912 | 18976216.8924 | 12951657.9513 | 57922692.5045 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 79168996.9204 | 109928226.3314 | 56234.1325 | 13.4165 | 5900.8537 | 8193.49 | 120.2969 | 167.0354
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.6056 | 39.3499 | 3.612 | 4 | 5649.5944 | 7778.5498 | 115.1746 | 158.5763 | 143.1516 | 0 | 167.4694 | 5997673.6955 | 482464.8568 | 6341385.8861 | 6008352.9828 | 0 | 664571.1325 | 0 | 7602834.936 | 19781016.9475 | 13500950.5259 | 60379250.9631 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 81625555.379 | 112384784.79 | 74989.4209 | 14.448 | 5649.5944 | 7778.5498 | 115.1746 | 158.5763
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2398 | 41.0166 | 3.8239 | 4 | 5459.9904 | 7470.9828 | 111.3093 | 152.3061 | 142.9676 | 0 | 189.0743 | 6171634.2549 | 495578.7669 | 6556202.209 | 6268009.4604 | 0 | 612592.9612 | 0 | 7840566.8844 | 20399546.7119 | 13923109.7996 | 62267241.0483 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 83513545.4642 | 114272774.8752 | 100000 | 15.2955 | 5459.9904 | 7470.9828 | 111.3093 | 152.3061
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6808 | 42.905 | 4.0315 | 4 | 5316.3755 | 7223.811 | 108.3815 | 147.2672 | 142.7532 | 0 | 178.3937 | 6365350.8584 | 510058.2606 | 6797647.8746 | 6559901.845 | 0 | 587215.0856 | 0 | 8119867.8305 | 21126230.4809 | 14419086.4039 | 64485358.6395 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 85731663.0554 | 116490892.4664 | 133352.1432 | 16.126 | 5316.3755 | 7223.811 | 108.3815 | 147.2672
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4787 | 44.0174 | 4.1751 | 4 | 5206.7055 | 7048.5397 | 106.1457 | 143.694 | 142.6336 | 0 | 174.4798 | 6478292.6214 | 518494.4329 | 6938883.6309 | 6731910.9964 | 0 | 547137.7546 | 0 | 8273740.5801 | 21526575.8118 | 14692330.3185 | 65707366.1465 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 86953670.5623 | 117712899.9734 | 177827.941 | 16.7003 | 5206.7055 | 7048.5397 | 106.1457 | 143.694
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4017 | 44.8694 | 4.2873 | 4 | 5124.0162 | 6917.6257 | 104.46 | 141.0252 | 142.5387 | 0 | 204.5261 | 6564017.5275 | 524868.6967 | 7046611.1859 | 6863826.2592 | 0 | 512386.0088 | 0 | 8389566.7744 | 21827931.8103 | 14898011.9797 | 66627220.2425 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87873524.6583 | 118632754.0694 | 237137.3706 | 17.1493 | 5124.0162 | 6917.6257 | 104.46 | 141.0252
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6138 | 45.5117 | 4.3738 | 4 | 5061.7184 | 6819.8834 | 103.19 | 139.0325 | 142.4653 | 0 | 204.2594 | 6628207.5167 | 529624.8321 | 7127581.042 | 6963382.9366 | 0 | 482984.6181 | 0 | 8475394.5687 | 22051238.1254 | 15050423.1282 | 67308836.7679 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 88555141.1838 | 119314370.5948 | 316227.766 | 17.4951 | 5061.7184 | 6819.8834 | 103.19 | 139.0325
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.2922 | 45.9977 | 4.44 | 4 | 5014.8164 | 6746.7368 | 102.2338 | 137.5414 | 142.4088 | 0 | 196.1046 | 6676523.914 | 533195.1129 | 7188702.4554 | 7038765.9477 | 0 | 458912.0955 | 0 | 8539478.8149 | 22217972.1885 | 15164222.5523 | 67817773.0811 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 89064077.497 | 119823306.908 | 421696.5034 | 17.7602 | 5014.8164 | 6746.7368 | 102.2338 | 137.5414
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5567 | 46.363 | 4.4905 | 4 | 4979.5282 | 6691.9938 | 101.5144 | 136.4253 | 142.3656 | 0 | 196.0848 | 6712703.3772 | 535862.9926 | 7234569.95 | 7095466.3321 | 0 | 439533.3425 | 0 | 8587073.0378 | 22341802.5935 | 15248739.3482 | 68195750.974 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 89442055.3899 | 120201284.8009 | 562341.3252 | 17.962 | 4979.5282 | 6691.9938 | 101.5144 | 136.4253
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4971 | 46.6342 | 4.5285 | 4 | 4952.9932 | 6651.0762 | 100.9735 | 135.5912 | 142.3333 | 0 | 197.8597 | 6739486.0034 | 537834.8214 | 7268580.101 | 7137581.2629 | 0 | 424060.4675 | 0 | 8621941.6359 | 22432523.5332 | 15310658.2537 | 68472666.0789 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 89718970.4948 | 120478199.9058 | 749894.2093 | 18.1141 | 4952.9932 | 6651.0762 | 100.9735 | 135.5912
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2003 | 46.8368 | 4.5572 | 4 | 4933.0514 | 6620.4449 | 100.5669 | 134.9667 | 142.309 | 0 | 231.2665 | 6759447.1709 | 539302.7486 | 7293958.2986 | 7169047.0845 | 0 | 411925.4421 | 0 | 8647735.4904 | 22499633.8516 | 15356462.425 | 68677512.5118 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 89923816.9276 | 120683046.3387 | 1000000 | 18.2288 | 4933.0514 | 6620.4449 | 100.5669 | 134.9667
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.7144 | 46.9848 | 4.5786 | 4 | 4918.0711 | 6597.5873 | 100.2615 | 134.5007 | 142.2911 | 0 | 227.0103 | 6774006.1272 | 540372.4664 | 7312484.9395 | 7192039.4352 | 0 | 402370.6547 | 0 | 8666296.713 | 22547926.3452 | 15389423.0442 | 68824919.7254 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90071224.1413 | 120830453.5523 | 1333521.4322 | 18.3143 | 4918.0711 | 6597.5873 | 100.2615 | 134.5007
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.1165 | 47.1005 | 4.595 | 4 | 4906.8217 | 6580.3386 | 100.0322 | 134.1491 | 142.2771 | 0 | 220.9154 | 6785371.3615 | 541207.009 | 7326956.9161 | 7210012.3281 | 0 | 395219.6377 | 0 | 8680919.2284 | 22585971.131 | 15415389.3922 | 68941047.004 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90187351.4198 | 120946580.8309 | 1778279.41 | 18.38 | 4906.8217 | 6580.3386 | 100.0322 | 134.1491
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4092 | 47.1846 | 4.6072 | 4 | 4898.3766 | 6567.4717 | 99.86 | 133.8868 | 142.2668 | 0 | 207.7852 | 6793630.6192 | 541813.1566 | 7337479.5473 | 7223087.5575 | 0 | 389650.2555 | 0 | 8691407.843 | 22613260.3547 | 15434014.8481 | 69024344.1819 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90270648.5978 | 121029878.0088 | 2371373.7057 | 18.4287 | 4898.3766 | 6567.4717 | 99.86 | 133.8868
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.6307 | 47.2482 | 4.6164 | 4 | 4892.0383 | 6557.8108 | 99.7308 | 133.6898 | 142.2591 | 0 | 205.1595 | 6799875.7873 | 542271.3231 | 7345439.141 | 7232981.897 | 0 | 385437.9973 | 0 | 8699342.3968 | 22633904.436 | 15448104.8578 | 69087357.8362 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90333662.2521 | 121092891.6631 | 3162277.6602 | 18.4654 | 4892.0383 | 6557.8108 | 99.7308 | 133.6898
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.7887 | 47.2936 | 4.6231 | 4 | 4887.2821 | 6550.6241 | 99.6339 | 133.5433 | 142.2535 | 0 | 203.0728 | 6804326.7636 | 542597.7533 | 7351113.8178 | 7240038.0512 | 0 | 382150.3299 | 0 | 8704888.4191 | 22648334.0485 | 15457953.3648 | 69131402.5482 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90377706.964 | 121136936.3751 | 4216965.0343 | 18.4924 | 4887.2821 | 6550.6241 | 99.6339 | 133.5433
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.913 | 47.3293 | 4.6283 | 4 | 4883.7137 | 6545.195 | 99.5611 | 133.4327 | 142.2492 | 0 | 205.0887 | 6807825.6288 | 542854.3173 | 7355575.4012 | 7245586.9387 | 0 | 379732.7846 | 0 | 8709314.2776 | 22659849.2242 | 15465812.7089 | 69166551.2813 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90412855.6972 | 121172085.1082 | 5623413.2519 | 18.5131 | 4883.7137 | 6545.195 | 99.5611 | 133.4327
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.0056 | 47.3559 | 4.6322 | 4 | 4881.0367 | 6541.1282 | 99.5065 | 133.3497 | 142.2459 | 0 | 205.4024 | 6810431.8212 | 543045.392 | 7358899.2446 | 7249721.5082 | 0 | 377901.915 | 0 | 8712599.9536 | 22668397.8794 | 15471647.3417 | 69192645.0558 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90438949.4716 | 121198178.8827 | 7498942.0933 | 18.5286 | 4881.0367 | 6541.1282 | 99.5065 | 133.3497
1 | 5400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.0787 | 47.3769 | 4.6351 | 4 | 4879.0287 | 6538.0529 | 99.4656 | 133.2871 | 142.2433 | 0 | 195.5639 | 6812490.1916 | 543196.293 | 7361524.6416 | 7252987.6538 | 0 | 376566.0859 | 0 | 8715238.2976 | 22675262.3093 | 15476332.4561 | 69213597.9288 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 90459902.3447 | 121219131.7557 | 10000000 | 18.5406 | 4879.0287 | 6538.0529 | 99.4656 | 133.2871
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0447 | [19 empty] | 100 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5487 | [19 empty] | 133.3521 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4381 | [19 empty] | 177.8279 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7943 | [19 empty] | 237.1374 | 0
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.3557 | 0.010581 | 4 | 552962.4619 | 1297036.6425 | 11272.8877 | 26441.8463 | 111.9045 | 0 | 267.2265 | 186320.8601 | 12462.6791 | 150146.9491 | 90282.4218 | 0 | 88251.8108 | 0 | 205711.2412 | 535218.4524 | 365297.5914 | 1633692.0059 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23402565.8386 | 54893392.4333 | 316.2278 | 0.042322 | 552962.4619 | 1297036.6425 | 11272.8877 | 26441.8463
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.52423 | 0.02203 | 4 | 271425.0304 | 628781.868 | 5533.3664 | 12818.5689 | 119.1217 | 0 | 375.8738 | 254359.2682 | 17781.975 | 203729.503 | 116320.1534 | 0 | 101814.7715 | 0 | 270662.2117 | 704207.5544 | 480636.1259 | 2149511.563 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23918385.3958 | 55409211.9904 | 421.6965 | 0.088122 | 271425.0304 | 628781.868 | 5533.3664 | 12818.5689
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0906 | 0.75353 | 0.038841 | 4 | 158108.857 | 360796.8848 | 3223.2629 | 7355.3325 | 125.0935 | 0 | 489.2143 | 338223.7913 | 24539.9992 | 271221.5358 | 151183.4764 | 0 | 117523.0663 | 0 | 352049.8289 | 915961.4395 | 625162.5036 | 2795865.641 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 24564739.4737 | 56055566.0683 | 562.3413 | 0.15537 | 158108.857 | 360796.8848 | 3223.2629 | 7355.3325
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0849 | 1.0704 | 0.063043 | 4 | 100708.6413 | 225586.1611 | 2053.0819 | 4598.879 | 130.0419 | 0 | 68.9256 | 443432.8698 | 33216.8866 | 357922.0239 | 199475.0552 | 0 | 137054.2911 | 0 | 456729.4394 | 1188316.3132 | 811050.3012 | 3627197.1803 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 25396071.0131 | 56886897.6077 | 749.8942 | 0.25217 | 100708.6413 | 225586.1611 | 2053.0819 | 4598.879
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3884 | 1.4919 | 0.096314 | 4 | 68583.7931 | 150323.5916 | 1398.1734 | 3064.5497 | 133.9559 | 0 | 68.5773 | 570335.5918 | 43824.9658 | 465552.9106 | 262864.9589 | 0 | 159884.9329 | 0 | 585960.7104 | 1524549.5714 | 1040536.4089 | 4653510.0507 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 26422383.8835 | 57913210.4781 | 1000 | 0.38526 | 68583.7931 | 150323.5916 | 1398.1734 | 3064.5497
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1354 | 2.0612 | 0.14183 | 4 | 48862.3374 | 104369.3138 | 996.1248 | 2127.7096 | 137.0259 | 0 | 62.1353 | 726211.1493 | 56961.5488 | 601655.7743 | 348735.23 | 0 | 188217.3653 | 0 | 749494.6164 | 1950031.2493 | 1330936.3968 | 5952243.3302 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 27721117.1629 | 59211943.7576 | 1333.5214 | 0.56733 | 48862.3374 | 104369.3138 | 996.1248 | 2127.7096
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4421 | 2.817 | 0.20315 | 4 | 36088.2297 | 74840.9435 | 735.7074 | 1525.7339 | 139.5111 | 0 | 80.6047 | 914568.601 | 72874.7085 | 771227.2205 | 459325.2807 | 0 | 221832.6104 | 0 | 951533.0843 | 2475693.899 | 1689711.9565 | 7556767.3609 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 29325641.1936 | 60816467.7882 | 1778.2794 | 0.81261 | 36088.2297 | 74840.9435 | 735.7074 | 1525.7339
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5379 | 3.837 | 0.28633 | 4 | 27391.9407 | 54886.7676 | 558.4218 | 1118.941 | 141.4177 | 0 | 76.6563 | 1146929.8807 | 92563.7778 | 986205.4139 | 611314.5141 | 0 | 263834.6805 | 0 | 1209330.8241 | 3146430.7365 | 2147503.6304 | 9604113.4581 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 31372987.2908 | 62863813.8855 | 2371.3737 | 1.1453 | 27391.9407 | 54886.7676 | 558.4218 | 1118.941
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6259 | 5.1891 | 0.39744 | 4 | 21345.4332 | 41153.7851 | 435.1555 | 838.9756 | 142.8672 | 0 | 70.5746 | 1428623.2307 | 116426.411 | 1254257.024 | 814252.524 | 0 | 314296.9825 | 0 | 1531863.9072 | 3985595.6581 | 2720250.9324 | 12165566.67 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 33934440.5027 | 65425267.0974 | 3162.2777 | 1.5898 | 21345.4332 | 41153.7851 | 435.1555 | 838.9756
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.058 | 6.9849 | 0.54486 | 4 | 17041.2267 | 31490.2019 | 347.4085 | 641.9704 | 143.9778 | 0 | 72.326 | 1770759.0649 | 145274.6725 | 1589689.3616 | 1081276.4773 | 0 | 375989.7347 | 0 | 1935565.8313 | 5035945.2538 | 3437136.114 | 15371636.51 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 37140510.3427 | 68631336.9374 | 4216.965 | 2.1795 | 17041.2267 | 31490.2019 | 347.4085 | 641.9704
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2058 | 9.3547 | 0.74027 | 4 | 13899.7897 | 24534.7409 | 283.366 | 500.1739 | 144.8204 | 0 | 84.5268 | 2185514.5016 | 180198.9699 | 2006956.1103 | 1437132.1795 | 0 | 450378.4757 | 0 | 2441470.2924 | 6352204.8865 | 4335510.3598 | 19389365.7758 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 41158239.6085 | 72649066.2032 | 5623.4133 | 2.9611 | 13899.7897 | 24534.7409 | 283.366 | 500.1739
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5601 | 12.453 | 0.99523 | 4 | 11587.9003 | 19498.3122 | 236.235 | 397.4995 | 145.4591 | 0 | 85.2171 | 2683285.4249 | 221870.2261 | 2521976.2872 | 1898559.3527 | 0 | 539919.25 | 0 | 3067588.111 | 7981235.0159 | 5447356.8963 | 24361790.5641 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 46130664.3968 | 77621490.9915 | 7498.9421 | 3.9809 | 11587.9003 | 19498.3122 | 236.235 | 397.4995
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6205 | 16.4457 | 1.3232 | 4 | 9866.6589 | 15816.3584 | 201.1452 | 322.4379 | 145.93 | 0 | 101.2921 | 3273913.542 | 271057.2025 | 3149378.5378 | 2491785.3019 | 0 | 646384.5643 | 0 | 3834682.4679 | 9977057.18 | 6809546.5334 | 30453805.3299 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 52222679.1626 | 83713505.7573 | 10000 | 5.2928 | 9866.6589 | 15816.3584 | 201.1452 | 322.4379
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.817 | 21.464 | 1.7338 | 4 | 8586.1093 | 13126.7918 | 175.0395 | 267.6074 | 146.2194 | 0 | 77.5242 | 3959728.8257 | 327875.4595 | 3896333.4499 | 3242346.3351 | 0 | 770989.7779 | 0 | 4756936.8007 | 12376573.7736 | 8447265.9137 | 37778050.3361 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 59546924.1688 | 91037750.7635 | 13335.2143 | 6.9353 | 8586.1093 | 13126.7918 | 175.0395 | 267.6074
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.465 | 26.2589 | 2.1624 | 4 | 7648.6196 | 11289.3505 | 155.9275 | 230.1487 | 146.2712 | 0 | 112.3369 | 4569775.0564 | 377849.8688 | 4578171.6336 | 3961024.3354 | 0 | 844760.711 | 0 | 5589316.8261 | 14542255.8549 | 9925388.4344 | 44388542.7206 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 66157416.5534 | 97648243.148 | 17782.7941 | 8.6496 | 7648.6196 | 11289.3505 | 155.9275 | 230.1487
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.1085 | 30.0231 | 2.5578 | 4 | 6941.4858 | 10019.3793 | 141.5116 | 204.2586 | 146.1819 | 0 | 144.8451 | 5023188.3277 | 414479.9047 | 5096419.5371 | 4525910.6257 | 0 | 841667.8143 | 0 | 6201649.8217 | 16135420.7028 | 11012756.1794 | 49251492.9134 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 71020366.7462 | 102511193.3408 | 23713.7371 | 10.2313 | 6941.4858 | 10019.3793 | 141.5116 | 204.2586
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9339 | 33.4757 | 2.9398 | 4 | 6405.328 | 9083.2708 | 130.5813 | 185.1748 | 146.0105 | 0 | 144.6046 | 5421858.364 | 446228.7484 | 5560874.4752 | 5044780.0617 | 0 | 816907.6911 | 0 | 6743353.2428 | 17544821.8858 | 11974701.4471 | 53553525.9161 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 75322399.7489 | 106813226.3435 | 31622.7766 | 11.7593 | 6405.328 | 9083.2708 | 130.5813 | 185.1748
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.7823 | 36.5756 | 3.2962 | 4 | 5998.779 | 8387.1887 | 122.2932 | 170.9842 | 145.7895 | 0 | 177.3323 | 5768043.0222 | 473519.435 | 5970047.7897 | 5517443.8788 | 0 | 778999.2584 | 0 | 7218140.8198 | 18780121.7689 | 12817819.0002 | 57324134.973 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 79093008.8057 | 110583835.4003 | 42169.6503 | 13.1849 | 5998.779 | 8387.1887 | 122.2932 | 170.9842
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.089 | 39.1555 | 3.6081 | 4 | 5691.3738 | 7873.3442 | 116.0264 | 160.5088 | 145.5596 | 0 | 208.0913 | 6047893.4161 | 495310.8628 | 6305589.1035 | 5913950.1314 | 0 | 728936.2926 | 0 | 7601755.1245 | 19778207.4997 | 13499033.02 | 60370675.4508 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 82139549.2835 | 113630375.8782 | 56234.1325 | 14.4323 | 5691.3738 | 7873.3442 | 116.0264 | 160.5088
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9755 | 41.2686 | 3.873 | 4 | 5459.1781 | 7491.8995 | 111.2927 | 152.7325 | 145.3413 | 0 | 206.7092 | 6271777.8112 | 512547.2 | 6577347.0843 | 6240925.0683 | 0 | 674872.5449 | 0 | 7908213.1864 | 20575548.5134 | 14043234.6456 | 62804466.0541 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 84573339.8868 | 116064166.4815 | 74989.4209 | 15.492 | 5459.1781 | 7491.8995 | 111.2927 | 152.7325
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5392 | 42.9581 | 4.0915 | 4 | 5283.9027 | 7208.0826 | 107.7195 | 146.9465 | 145.1478 | 0 | 217.2707 | 6447458.9437 | 525939.3143 | 6792782.8964 | 6503924.2779 | 0 | 621516.4588 | 0 | 8147732.5375 | 21198728.7328 | 14468567.9505 | 64706651.1118 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 86475524.9446 | 117966351.5392 | 100000 | 16.3658 | 5283.9027 | 7208.0826 | 107.7195 | 146.9465
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.9512 | 44.8975 | 4.3082 | 4 | 5149.9801 | 6977.3515 | 104.9893 | 142.2427 | 144.9351 | 0 | 194.8114 | 6646323.2877 | 541043.4852 | 7038064.7843 | 6804239.1525 | 0 | 595935.2542 | 0 | 8433986.3259 | 21943502.3716 | 14976891.2625 | 66979985.9241 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 88748859.7568 | 120239686.3515 | 133352.1432 | 17.2329 | 5149.9801 | 6977.3515 | 104.9893 | 142.2427
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.6318 | 46.0016 | 4.454 | 4 | 5048.5121 | 6816.0688 | 102.9207 | 138.9548 | 144.8135 | 0 | 219.9995 | 6757941.9931 | 549454.5566 | 7176833.0231 | 6972826.9422 | 0 | 554549.1457 | 0 | 8584526.2077 | 22335176.264 | 15244216.7421 | 68175524.8746 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 89944398.7073 | 121435225.302 | 177827.941 | 17.816 | 5048.5121 | 6816.0688 | 102.9207 | 138.9548
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.448 | 46.8422 | 4.5675 | 4 | 4971.9892 | 6695.6321 | 101.3607 | 136.4995 | 144.7177 | 0 | 224.5961 | 6842188.1413 | 555772.6541 | 7282080.6237 | 7101312.5605 | 0 | 518723.5567 | 0 | 8697030.2391 | 22627888.676 | 15443998.978 | 69068995.4293 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90837869.2621 | 122328695.8567 | 237137.3706 | 18.2699 | 4971.9892 | 6695.6321 | 101.3607 | 136.4995
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6017 | 47.4827 | 4.6552 | 4 | 4914.3255 | 6605.4907 | 100.1852 | 134.6619 | 144.643 | 0 | 206.3069 | 6905945.9936 | 560536.4378 | 7362030.107 | 7199271.5687 | 0 | 488852.0316 | 0 | 8781488.0941 | 22847630.6899 | 15593977.4178 | 69739732.3405 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 91508606.1732 | 122999432.7679 | 316227.766 | 18.6208 | 4914.3255 | 6605.4907 | 100.1852 | 134.6619
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.2265 | 47.9644 | 4.7222 | 4 | 4870.9053 | 6538.071 | 99.3 | 133.2874 | 144.5858 | 0 | 214.5952 | 6953663.1755 | 564091.4481 | 7422036.2913 | 7272997.056 | 0 | 464361.3128 | 0 | 8844088.2207 | 23010503.3782 | 15705141.3742 | 70236882.2569 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 92005756.0896 | 123496582.6843 | 421696.5034 | 18.8888 | 4870.9053 | 6538.071 | 99.3 | 133.2874
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.4346 | 48.3218 | 4.7729 | 4 | 4838.2323 | 6487.7067 | 98.6339 | 132.2607 | 144.5428 | 0 | 207.1647 | 6988931.981 | 566713.2555 | 7466483.9109 | 7327718.5299 | 0 | 444509.7549 | 0 | 8889799.3986 | 23129434.4865 | 15786314.2994 | 70599905.6167 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 92368779.4494 | 123859606.044 | 562341.3252 | 19.0914 | 4838.2323 | 6487.7067 | 98.6339 | 132.2607
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3406 | 48.5894 | 4.8112 | 4 | 4813.6613 | 6449.9961 | 98.133 | 131.4919 | 144.5103 | 0 | 221.8732 | 7015266.4732 | 568667.6773 | 7499725.491 | 7368705.8096 | 0 | 428792.665 | 0 | 8923651.6653 | 23217511.1405 | 15846428.4256 | 70868749.3477 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 92637623.1804 | 124128449.7751 | 749894.2093 | 19.2447 | 4813.6613 | 6449.9961 | 98.133 | 131.4919
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.023 | 48.7907 | 4.8402 | 4 | 4795.193 | 6421.7261 | 97.7565 | 130.9156 | 144.4856 | 0 | 206.0096 | 7035032.6625 | 570132.8084 | 7524706.19 | 7399542.2409 | 0 | 416540.637 | 0 | 8948922.2701 | 23283260.0704 | 15891303.4212 | 71069440.3002 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 92838314.133 | 124329140.7276 | 1000000 | 19.3607 | 4795.193 | 6421.7261 | 97.7565 | 130.9156
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.5346 | 48.9414 | 4.862 | 4 | 4781.3182 | 6400.5418 | 97.4736 | 130.4837 | 144.4671 | 0 | 197.5663 | 7049813.9384 | 571227.4095 | 7543403.965 | 7422642.5764 | 0 | 407054.5219 | 0 | 8967715.5404 | 23332156.3046 | 15924676.1058 | 71218690.362 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 92987564.1947 | 124478390.7894 | 1333521.4322 | 19.4481 | 4781.3182 | 6400.5418 | 97.4736 | 130.4837
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.907 | 49.0511 | 4.8782 | 4 | 4770.8983 | 6384.7374 | 97.2612 | 130.1615 | 144.4535 | 0 | 212.7924 | 7060555.5969 | 572022.2775 | 7557001.289 | 7439452.116 | 0 | 399634.0527 | 0 | 8981179.4795 | 23367186.7124 | 15948585.0789 | 71325616.6029 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93094490.4357 | 124585317.0303 | 1778279.41 | 19.513 | 4770.8983 | 6384.7374 | 97.2612 | 130.1615
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1971 | 49.1365 | 4.8907 | 4 | 4763.0756 | 6372.8173 | 97.1017 | 129.9185 | 144.4429 | 0 | 207.9301 | 7068909.1709 | 572640.1341 | 7567580.7071 | 7452536.8809 | 0 | 394095.8186 | 0 | 8991747.4575 | 23394682.4234 | 15967351.4666 | 71409544.059 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93178417.8918 | 124669244.4864 | 2371373.7057 | 19.5627 | 4763.0756 | 6372.8173 | 97.1017 | 129.9185
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4017 | 49.1967 | 4.8997 | 4 | 4757.2042 | 6363.9657 | 96.982 | 129.738 | 144.4354 | 0 | 205.6272 | 7074796.957 | 573075.4079 | 7575040.5177 | 7461766.5742 | 0 | 389731.0413 | 0 | 8999020.0943 | 23413604.3325 | 15980266.0584 | 71467300.9832 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93236174.816 | 124727001.4106 | 3162277.6602 | 19.5989 | 4757.2042 | 6363.9657 | 96.982 | 129.738
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.5481 | 49.2397 | 4.9064 | 4 | 4752.7983 | 6357.376 | 96.8922 | 129.6037 | 144.4301 | 0 | 191.4529 | 7079002.796 | 573386.231 | 7580370.9628 | 7468363.3765 | 0 | 386338.5869 | 0 | 9004110.1617 | 23426847.6438 | 15989304.8905 | 71507724.6492 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93276598.4819 | 124767425.0765 | 4216965.0343 | 19.6256 | 4752.7983 | 6357.376 | 96.8922 | 129.6037
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.6723 | 49.2763 | 4.9117 | 4 | 4749.4926 | 6352.3382 | 96.8248 | 129.501 | 144.4255 | 0 | 219.4122 | 7082573.681 | 573650.115 | 7584897.1421 | 7473965.8233 | 0 | 383949.1918 | 0 | 9008624.0217 | 23438591.7817 | 15997320.5059 | 71543572.2624 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93312446.0951 | 124803272.6898 | 5623413.2519 | 19.6468 | 4749.4926 | 6352.3382 | 96.8248 | 129.501
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.765 | 49.3035 | 4.9157 | 4 | 4747.0127 | 6348.5646 | 96.7743 | 129.4241 | 144.4221 | 0 | 212.4711 | 7085233.4906 | 573846.6361 | 7588269.0899 | 7478140.2192 | 0 | 382139.5576 | 0 | 9011975.3074 | 23447311.1395 | 16003271.6468 | 71570187.0871 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93339060.9198 | 124829887.5145 | 7498942.0933 | 19.6627 | 4747.0127 | 6348.5646 | 96.7743 | 129.4241
1 | 5500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.8233 | 49.3206 | 4.9184 | 4 | 4745.1525 | 6345.8083 | 96.7364 | 129.3679 | 144.42 | 0 | 201.6745 | 7086908.0398 | 573970.3167 | 7590392.5508 | 7480769.3579 | 0 | 380643.365 | 0 | 9013946.6158 | 23452440.0796 | 16006772.2538 | 71585842.5793 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 93354716.412 | 124845543.0067 | 10000000 | 19.6737 | 4745.1525 | 6345.8083 | 96.7364 | 129.3679
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.3713 | [19 empty] | 100 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7336 | [19 empty] | 133.3521 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3051 | [19 empty] | 177.8279 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7497 | [19 empty] | 237.1374 | 0
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.37428 | 0.012334 | 4 | 486252.9574 | 1139557.6463 | 9912.9242 | 23231.424 | 113.7339 | 0 | 273.1978 | 195140.572 | 13194.393 | 156184.5043 | 92696.4325 | 0 | 89031.9171 | 0 | 213036.6494 | 554277.6618 | 378305.8934 | 1691868.0235 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 23989171.3639 | 56219799.2694 | 316.2278 | 0.049335 | 486252.9574 | 1139557.6463 | 9912.9242 | 23231.424
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4099 | 0.55399 | 0.024961 | 4 | 245728.0565 | 568542.8643 | 5009.4988 | 11590.5153 | 121.1316 | 0 | 364.965 | 267302.5642 | 18916.3894 | 212633.8251 | 120210.9737 | 0 | 103122.148 | 0 | 281652.5012 | 732802.0332 | 500152.4453 | 2236792.8802 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 24534096.2207 | 56764724.1261 | 421.6965 | 0.099842 | 245728.0565 | 568542.8643 | 5009.4988 | 11590.5153
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1489 | 0.79048 | 0.04316 | 4 | 145927.3007 | 332618.6405 | 2974.9254 | 6780.8809 | 127.061 | 0 | 473.5622 | 353436.2022 | 25965.7157 | 281420.5237 | 156004.2338 | 0 | 118120.8316 | 0 | 364629.5278 | 948691.2354 | 647501.2618 | 2895769.5321 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25193072.8725 | 57423700.778 | 562.3413 | 0.17264 | 145927.3007 | 332618.6405 | 2974.9254 | 6780.8809
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 1.1214 | 0.069371 | 4 | 93885.8729 | 210039.1675 | 1913.9905 | 4281.9325 | 132.0752 | 0 | 55.5407 | 462865.8793 | 35126.8355 | 370991.1865 | 205647.0451 | 0 | 137566.0301 | 0 | 472756.8208 | 1230016.2721 | 839511.38 | 3754481.4494 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 26051784.7899 | 58282412.6954 | 749.8942 | 0.27748 | 93885.8729 | 210039.1675 | 1913.9905 | 4281.9325
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.481 | 1.5622 | 0.10546 | 4 | 64281.1711 | 140688.429 | 1310.4586 | 2868.1239 | 136.0458 | 0 | 66.801 | 595221.6664 | 46377.8009 | 482323.2367 | 271395.8111 | 0 | 160323.0195 | 0 | 606700.1985 | 1578509.4651 | 1077365.1451 | 4818216.3433 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 27115519.6838 | 59346147.5893 | 1000 | 0.42183 | 64281.1711 | 140688.429 | 1310.4586 | 2868.1239
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2495 | 2.1519 | 0.15405 | 4 | 46150.9313 | 98455.0985 | 940.8492 | 2007.1404 | 139.1509 | 0 | 80.5977 | 755768.3367 | 60080.6298 | 621904.2482 | 356829.7877 | 0 | 188337.1032 | 0 | 773338.8412 | 2012069.0311 | 1373278.4576 | 6141606.4355 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 28438909.776 | 60669537.6815 | 1333.5214 | 0.61622 | 46150.9313 | 98455.0985 | 940.8492 | 2007.1404
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6273 | 2.9587 | 0.22182 | 4 | 33978.185 | 70303.1174 | 692.6913 | 1433.2241 | 141.7248 | 0 | 77.1752 | 956979.3766 | 77452.7318 | 800859.2584 | 476355.5285 | 0 | 223207.4889 | 0 | 988593.2098 | 2572116.7435 | 1755522.5292 | 7851086.8665 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 30148390.207 | 62379018.1125 | 1778.2794 | 0.88729 | 33978.185 | 70303.1174 | 692.6913 | 1433.2241
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7548 | 4.0212 | 0.31183 | 4 | 25866.1529 | 51706.3161 | 527.3165 | 1054.1032 | 143.6402 | 0 | 76.0348 | 1198490.9888 | 98307.078 | 1022281.1334 | 633885.9164 | 0 | 264640.909 | 0 | 1254866.35 | 3264904.8341 | 2228364.6364 | 9965741.846 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 32263045.1864 | 64493673.0919 | 2371.3737 | 1.2473 | 25866.1529 | 51706.3161 | 527.3165 | 1054.1032
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9205 | 5.441 | 0.4325 | 4 | 20190.2437 | 38820.474 | 411.6054 | 791.4079 | 145.1167 | 0 | 84.0843 | 1493603.5663 | 123771.5397 | 1300665.5142 | 844981.2441 | 0 | 315486.7083 | 0 | 1590618.3433 | 4138462.6486 | 2824585.7946 | 12632175.359 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 34929478.6995 | 67160106.605 | 3162.2777 | 1.73 | 20190.2437 | 38820.474 | 411.6054 | 791.4079
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4453 | 7.3223 | 0.59238 | 4 | 16145.78 | 29747.8421 | 329.1536 | 606.45 | 146.2456 | 0 | 82.1742 | 1851254.7704 | 154498.6037 | 1648154.5115 | 1121933.8568 | 0 | 377357.7392 | 0 | 2009747.7978 | 5228951.5139 | 3568866.8525 | 15960765.6457 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 38258068.9862 | 70488696.8916 | 4216.965 | 2.3695 | 16145.78 | 29747.8421 | 329.1536 | 606.45
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7005 | 9.8001 | 0.80424 | 4 | 13188.1764 | 23207.1376 | 268.8588 | 473.1089 | 147.1011 | 0 | 79.5323 | 2284422.8665 | 191712.9898 | 2079586.2393 | 1491443.4636 | 0 | 451680.0324 | 0 | 2534549.7807 | 6594378.6219 | 4500798.9104 | 20128572.9046 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 42425876.2451 | 74656504.1506 | 5623.4133 | 3.217 | 13188.1764 | 23207.1376 | 268.8588 | 473.1089
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2058 | 13.0464 | 1.0811 | 4 | 11007.289 | 18460.8331 | 224.3985 | 376.3491 | 147.7506 | 0 | 86.5375 | 2805343.8237 | 236188.604 | 2613249.8076 | 1972335.0639 | 0 | 541550.0173 | 0 | 3185780.2535 | 8288746.7261 | 5657239.9573 | 25300434.2534 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 47597737.5939 | 79828365.4994 | 7498.9421 | 4.3242 | 11007.289 | 18460.8331 | 224.3985 | 376.3491
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.4442 | 17.2257 | 1.4372 | 4 | 9382.2758 | 14988.7084 | 191.2704 | 305.5651 | 148.2273 | 0 | 95.8006 | 3423341.4958 | 288732.4711 | 3262698.7363 | 2592467.6447 | 0 | 648306.9935 | 0 | 3984063.4631 | 10365715.8872 | 7074814.0872 | 31640140.7789 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 53937444.1193 | 86168072.0248 | 10000 | 5.7489 | 9382.2758 | 14988.7084 | 191.2704 | 305.5651
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.8085 | 22.4538 | 1.8806 | 4 | 8177.1565 | 12461.8715 | 166.7024 | 254.0521 | 148.5132 | 0 | 98.0748 | 4136925.8069 | 348972.1215 | 4032475.517 | 3369698.7972 | 0 | 772556.7207 | 0 | 4937645.2957 | 12846740.2091 | 8768164.1668 | 39213178.6349 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 61510481.9754 | 93741109.8809 | 13335.2143 | 7.5222 | 8177.1565 | 12461.8715 | 166.7024 | 254.0521
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.3271 | 28.0175 | 2.3688 | 4 | 7301.3853 | 10703.0035 | 148.8486 | 218.1952 | 148.5457 | 0 | 94.3494 | 4841295.369 | 407646.3405 | 4813628.4287 | 4198372.3133 | 0 | 876325.2937 | 0 | 5903534.4206 | 15359785.581 | 10483369.2711 | 46883957.0179 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 69181260.3584 | 101411888.2639 | 17782.7941 | 9.4751 | 7301.3853 | 10703.0035 | 148.8486 | 218.1952
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9855 | 31.8883 | 2.7873 | 4 | 6648.4424 | 9539.2762 | 135.5375 | 194.471 | 148.4279 | 0 | 129.7308 | 5303972.1445 | 445572.2859 | 5339168.9898 | 4776405.2575 | 0 | 868365.3405 | 0 | 6526058.7671 | 16979466.2333 | 11588834.5974 | 51827843.6159 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 74125146.9564 | 106355774.8619 | 23713.7371 | 11.1492 | 6648.4424 | 9539.2762 | 135.5375 | 194.471
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.7501 | 35.4117 | 3.1881 | 4 | 6153.2942 | 8680.7161 | 125.4432 | 176.9681 | 148.2317 | 0 | 154.4978 | 5708081.5094 | 478190.7753 | 5806992.3579 | 5303981.8247 | 0 | 838757.2507 | 0 | 7073041.45 | 18402602.9726 | 12560154.6645 | 56171802.8052 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 78469106.1456 | 110699734.0511 | 31622.7766 | 12.7524 | 6153.2942 | 8680.7161 | 125.4432 | 176.9681
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.3576 | 38.5102 | 3.5552 | 4 | 5778.3288 | 8044.7594 | 117.799 | 164.0033 | 147.9943 | 0 | 183.4554 | 6051161.6373 | 505447.5056 | 6211170.8231 | 5769357.6751 | 0 | 794695.7425 | 0 | 7539415.0196 | 19616011.3344 | 13388330.8045 | 59875590.5421 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 82172893.8826 | 114403521.7881 | 42169.6503 | 14.2209 | 5778.3288 | 8044.7594 | 117.799 | 164.0033
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.501 | 41.0975 | 3.8758 | 4 | 5494.4829 | 7573.4587 | 112.0125 | 154.3952 | 147.7514 | 0 | 174.0119 | 6329937.6432 | 527340.1684 | 6543960.5485 | 6161274.3192 | 0 | 740755.3488 | 0 | 7918274.531 | 20601726.0681 | 14061101.3646 | 62884369.9918 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 85181673.3323 | 117412301.2378 | 56234.1325 | 15.5031 | 5494.4829 | 7573.4587 | 112.0125 | 154.3952
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.2265 | 43.2071 | 4.1464 | 4 | 5279.9661 | 7223.2512 | 107.6393 | 147.2557 | 147.5241 | 0 | 190.0629 | 6551997.5589 | 544554.4056 | 6812444.9544 | 6482212.6976 | 0 | 683691.629 | 0 | 8219211.4857 | 21384702.2938 | 14595498.7272 | 65274313.7522 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 87571617.0926 | 119802244.9981 | 74989.4209 | 16.5856 | 5279.9661 | 7223.2512 | 107.6393 | 147.2557
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5929 | 45.4958 | 4.4083 | 4 | 5117.483 | 6945.313 | 104.3268 | 141.5896 | 147.2623 | 0 | 197.6459 | 6788231.8334 | 562691.9838 | 7100981.7551 | 6831597.6386 | 0 | 652278.9389 | 0 | 8554955.0384 | 22258238.1474 | 15191704.8966 | 67940680.2322 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 90237983.5726 | 122468611.4781 | 100000 | 17.6333 | 5117.483 | 6945.313 | 104.3268 | 141.5896
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.1755 | 46.9178 | 4.5963 | 4 | 4992.9333 | 6746.0094 | 101.7877 | 137.5265 | 147.109 | 0 | 192.5025 | 6933222.3084 | 573812.2537 | 7278789.8259 | 7048816.7351 | 0 | 604173.4373 | 0 | 8751137.6785 | 22768665.1344 | 15540081.8035 | 69498699.1768 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 91796002.5172 | 124026630.4227 | 133352.1432 | 18.3852 | 4992.9333 | 6746.0094 | 101.7877 | 137.5265
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6929 | 48.0025 | 4.7438 | 4 | 4898.9239 | 6597.4921 | 99.8712 | 134.4988 | 146.987 | 0 | 175.8525 | 7042577.5051 | 582143.3179 | 7413756.1417 | 7214585.6182 | 0 | 560902.147 | 0 | 8897446.2446 | 23149330.0114 | 15799893.4039 | 70660634.3899 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92957937.7303 | 125188565.6358 | 177827.941 | 18.9752 | 4898.9239 | 6597.4921 | 99.8712 | 134.4988
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.4165 | 48.8362 | 4.8586 | 4 | 4828.045 | 6486.4699 | 98.4262 | 132.2355 | 146.8901 | 0 | 199.5156 | 7125691.4855 | 588411.1742 | 7517154.9394 | 7340303.6469 | 0 | 524141.5791 | 0 | 9007324.1018 | 23435209.6566 | 15995012.136 | 71533248.7194 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 93830552.0598 | 126061179.9653 | 237137.3706 | 19.4345 | 4828.045 | 6486.4699 | 98.4262 | 132.2355
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4971 | 49.4706 | 4.9472 | 4 | 4774.6232 | 6403.3423 | 97.3372 | 130.5408 | 146.8147 | 0 | 194.5407 | 7188532.8997 | 593130.8183 | 7595631.1499 | 7436024.6123 | 0 | 493598.8934 | 0 | 9089698.1657 | 23649530.0736 | 16141290.2245 | 72187436.8371 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 94484740.1776 | 126715368.0831 | 316227.766 | 19.7889 | 4774.6232 | 6403.3423 | 97.3372 | 130.5408
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.0628 | 49.9468 | 5.0148 | 4 | 4734.3899 | 6341.1648 | 96.5169 | 129.2732 | 146.7571 | 0 | 227.9764 | 7235456.6071 | 596643.8097 | 7654400.0173 | 7507879.4828 | 0 | 468598.0292 | 0 | 9150561.399 | 23807883.7219 | 16249369.8433 | 72670792.9104 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 94968096.2509 | 127198724.1563 | 421696.5034 | 20.0592 | 4734.3899 | 6341.1648 | 96.5169 | 129.2732
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.2297 | 50.3008 | 5.0659 | 4 | 4704.1105 | 6294.6812 | 95.8997 | 128.3256 | 146.7137 | 0 | 200.2249 | 7270222.4333 | 599240.3002 | 7698037.6713 | 7561328.853 | 0 | 448422.7036 | 0 | 9195128.2649 | 23923837.5652 | 16328510.7239 | 73024728.5154 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 95322031.8558 | 127552659.7613 | 562341.3252 | 20.2636 | 4704.1105 | 6294.6812 | 95.8997 | 128.3256
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0922 | 50.5621 | 5.1043 | 4 | 4681.3367 | 6259.9489 | 95.4354 | 127.6175 | 146.6814 | 0 | 203.5669 | 7295808.5636 | 601147.7151 | 7730205.9754 | 7600781.7806 | 0 | 432324.9732 | 0 | 9227504.9131 | 24008074.9623 | 16386004.4784 | 73281853.3616 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 95579156.7021 | 127809784.6076 | 749894.2093 | 20.4171 | 4681.3367 | 6259.9489 | 95.4354 | 127.6175
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7501 | 50.7612 | 5.1335 | 4 | 4664.2178 | 6233.8519 | 95.0864 | 127.0855 | 146.6567 | 0 | 204.6315 | 7315260.6362 | 602595.9047 | 7754691.8528 | 7630841.9406 | 0 | 419895.3034 | 0 | 9252081.3987 | 24072017.9365 | 16429646.8722 | 73477031.8451 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 95774335.1855 | 128004963.091 | 1000000 | 20.5338 | 4664.2178 | 6233.8519 | 95.0864 | 127.0855
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.2371 | 50.9083 | 5.1553 | 4 | 4651.3556 | 6214.3328 | 94.8242 | 126.6876 | 146.6383 | 0 | 201.4796 | 7329622.9935 | 603664.0469 | 7772787.8517 | 7653073.8608 | 0 | 410205.0966 | 0 | 9270048.0013 | 24118763.351 | 16461551.5781 | 73619716.7799 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 95917020.1203 | 128147648.0258 | 1333521.4322 | 20.6213 | 4651.3556 | 6214.3328 | 94.8242 | 126.6876
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.6003 | 51.0181 | 5.1717 | 4 | 4641.6957 | 6199.7124 | 94.6272 | 126.3895 | 146.6245 | 0 | 190.3632 | 7340315.8682 | 604458.6685 | 7786269.7939 | 7669646.1666 | 0 | 402743.1571 | 0 | 9283339.1252 | 24153344.1291 | 16485153.6697 | 73725270.5784 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96022573.9188 | 128253201.8243 | 1778279.41 | 20.687 | 4641.6957 | 6199.7124 | 94.6272 | 126.3895
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.8561 | 51.0953 | 5.1837 | 4 | 4634.4432 | 6188.8558 | 94.4794 | 126.1682 | 146.6147 | 0 | 200.5866 | 7347835.0207 | 605017.0712 | 7795755.5329 | 7681310.8755 | 0 | 396845.3896 | 0 | 9292437.917 | 24177017.319 | 16501311.1083 | 73797530.2342 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96094833.5747 | 128325461.4802 | 2371373.7057 | 20.7349 | 4634.4432 | 6188.8558 | 94.4794 | 126.1682
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.0607 | 51.157 | 5.193 | 4 | 4628.9996 | 6180.6336 | 94.3684 | 126.0006 | 146.6069 | 0 | 198.9287 | 7353846.5378 | 605463.37 | 7803341.6856 | 7690642.3634 | 0 | 392521.562 | 0 | 9299868.0523 | 24196349.0068 | 16514505.3824 | 73856537.9603 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96153841.3008 | 128384469.2062 | 3162277.6602 | 20.7721 | 4628.9996 | 6180.6336 | 94.3684 | 126.0006
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.2071 | 51.2012 | 5.1998 | 4 | 4624.9146 | 6174.5134 | 94.2851 | 125.8758 | 146.6014 | 0 | 179.0017 | 7358140.6766 | 605782.0434 | 7808762.4101 | 7697311.7245 | 0 | 389158.5804 | 0 | 9305070.6196 | 24209885.0199 | 16523743.9894 | 73897855.0639 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96195158.4044 | 128425786.3099 | 4216965.0343 | 20.7993 | 4624.9146 | 6174.5134 | 94.2851 | 125.8758
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.3313 | 51.2387 | 5.2053 | 4 | 4621.8496 | 6169.8323 | 94.2227 | 125.7804 | 146.5966 | 0 | 206.0564 | 7361786.5518 | 606052.5934 | 7813365.2759 | 7702975.7922 | 0 | 386795.6364 | 0 | 9309680.5814 | 24221879.1947 | 16531930.2602 | 73934465.8859 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96231769.2264 | 128462397.1319 | 5623413.2519 | 20.8211 | 4621.8496 | 6169.8323 | 94.2227 | 125.7804
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.4091 | 51.2621 | 5.209 | 4 | 4619.5503 | 6166.4192 | 94.1758 | 125.7108 | 146.5936 | 0 | 205.6436 | 7364066.8972 | 606221.7317 | 7816245.151 | 7706520.1028 | 0 | 384824.5053 | 0 | 9312372.5713 | 24228883.2002 | 16536710.6379 | 73955844.7974 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96253148.1379 | 128483776.0434 | 7498942.0933 | 20.836 | 4619.5503 | 6166.4192 | 94.1758 | 125.7108
1 | 5600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.4823 | 51.2842 | 5.2121 | 4 | 4617.8254 | 6163.7664 | 94.1406 | 125.6567 | 146.5909 | 0 | 195.8747 | 7366211.844 | 606380.8612 | 7818953.786 | 7709853.9637 | 0 | 383521.779 | 0 | 9315119.6712 | 24236030.5908 | 16541588.8788 | 73977661.3749 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 96274964.7153 | 128505592.6208 | 10000000 | 20.8485 | 4617.8254 | 6163.7664 | 94.1406 | 125.6567
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9644 | [19 empty] | 100 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7549 | [19 empty] | 133.3521 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6068 | [19 empty] | 177.8279 | 0
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.26489 | 0.0054378 | 4 | 1111008.8692 | 2627193.0863 | 22649.4185 | 53558.8846 | 107.2871 | 0 | 55.5456 | 147587.6132 | 9593.6507 | 118997.8239 | 75300.4387 | 0 | 79238.1582 | 0 | 167979.897 | 437049.2346 | 298295.0831 | 1334041.8993 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24165634.8383 | 57144268.1819 | 237.1374 | 0.021751 | 1111008.8692 | 2627193.0863 | 22649.4185 | 53558.8846
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.39347 | 0.014206 | 4 | 432609.4293 | 1012963.847 | 8819.3284 | 20650.6382 | 115.5616 | 0 | 272.8648 | 204217.178 | 13959.3369 | 162349.8432 | 95186.803 | 0 | 89766.23 | 0 | 220536.9625 | 573791.9382 | 391624.788 | 1751433.0798 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24583026.0189 | 57561659.3624 | 316.2278 | 0.056825 | 432609.4293 | 1012963.847 | 8819.3284 | 20650.6382
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.57824 | 0.027804 | 4 | 226005.7685 | 522529.8081 | 4607.4333 | 10652.4769 | 122.9431 | 0 | 380.9412 | 278053.5379 | 19889.4303 | 219779.1193 | 122951.5147 | 0 | 103269.8354 | 0 | 290137.9406 | 754879.4061 | 515220.7059 | 2304181.4901 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25135774.4292 | 58114407.7727 | 421.6965 | 0.11122 | 226005.7685 | 522529.8081 | 4607.4333 | 10652.4769
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2267 | 0.8348 | 0.047955 | 4 | 134745.3308 | 306670.3144 | 2746.9658 | 6251.8892 | 129.1497 | 0 | 509.0917 | 371133.9559 | 27626.1459 | 293549.6887 | 161580.0233 | 0 | 119631.7174 | 0 | 379673.3972 | 987832.2977 | 674215.8411 | 3015243.0673 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25846836.0064 | 58825469.3499 | 562.3413 | 0.19182 | 134745.3308 | 306670.3144 | 2746.9658 | 6251.8892
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 1.179 | 0.076261 | 4 | 87624.5134 | 195735.5484 | 1786.3442 | 3990.3339 | 134.1637 | 0 | 68.6301 | 484353.3852 | 37257.5473 | 385591.6637 | 212573.2412 | 0 | 138677.0874 | 0 | 490796.6407 | 1276952.1828 | 871546.1035 | 3897747.8517 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 26729340.7908 | 59707974.1343 | 749.8942 | 0.30504 | 87624.5134 | 195735.5484 | 1786.3442 | 3990.3339
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5905 | 1.6381 | 0.11503 | 4 | 60468.4682 | 132143.9037 | 1232.7315 | 2693.9322 | 138.1724 | 0 | 90.595 | 621502.1397 | 49093.7719 | 500278.2899 | 279110.5931 | 0 | 161312.0942 | 0 | 628405.7867 | 1634982.9532 | 1115909.4611 | 4990595.0898 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 27822188.0288 | 60800821.3723 | 1000 | 0.46011 | 60468.4682 | 132143.9037 | 1232.7315 | 2693.9322
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3958 | 2.2602 | 0.16814 | 4 | 43435.2757 | 92470.7938 | 885.4868 | 1885.1422 | 141.3142 | 0 | 72.252 | 790658.7156 | 63825.8061 | 645827.3957 | 370123.4046 | 0 | 189654.5227 | 0 | 803435.0394 | 2090373.1655 | 1426722.6383 | 6380620.6879 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 29212213.627 | 62190846.9705 | 1333.5214 | 0.67255 | 43435.2757 | 92470.7938 | 885.4868 | 1885.1422
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7905 | 3.0976 | 0.24117 | 4 | 32104.0514 | 66290.6691 | 654.4845 | 1351.425 | 143.9126 | 0 | 84.6662 | 999009.4692 | 82160.186 | 829518.4919 | 493091.5332 | 0 | 223729.3041 | 0 | 1024728.5039 | 2666133.3665 | 1819690.8062 | 8138061.6611 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 30969654.6001 | 63948287.9436 | 1778.2794 | 0.96466 | 32104.0514 | 66290.6691 | 654.4845 | 1351.425
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9789 | 4.213 | 0.33866 | 4 | 24485.9766 | 48831.0746 | 499.1798 | 995.4875 | 145.8633 | 0 | 81.1384 | 1251864.0443 | 104399.7901 | 1059447.7897 | 656532.2402 | 0 | 265512.8046 | 0 | 1301725.1009 | 3386821.692 | 2311575.397 | 10337878.8588 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 33169471.7979 | 66148105.1414 | 2371.3737 | 1.3546 | 24485.9766 | 48831.0746 | 499.1798 | 995.4875
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.228 | 5.7043 | 0.46979 | 4 | 19131.7249 | 36681.5048 | 390.0261 | 747.8021 | 147.3669 | 0 | 81.3998 | 1561585.5876 | 131709.1459 | 1348556.5875 | 877239.5535 | 0 | 316838.9961 | 0 | 1652012.6495 | 4298198.0397 | 2933608.4813 | 13119749.0412 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 35951341.9802 | 68929975.3238 | 3162.2777 | 1.8791 | 19131.7249 | 36681.5048 | 390.0261 | 747.8021
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8326 | 7.6736 | 0.64337 | 4 | 15316.3906 | 28131.2877 | 312.2453 | 573.4943 | 148.5105 | 0 | 94.1927 | 1935780.4 | 164577.6402 | 1708203.0873 | 1167450.6332 | 0 | 378582.2025 | 0 | 2088291.6457 | 5433306.4946 | 3708343.3258 | 16584535.4294 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 39416128.3685 | 72394761.712 | 4216.965 | 2.5735 | 15316.3906 | 28131.2877 | 312.2453 | 573.4943
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2138 | 10.2697 | 0.87266 | 4 | 12531.998 | 21979.7387 | 255.4817 | 448.0867 | 149.3804 | 0 | 84.1336 | 2388646.9985 | 204252.77 | 2155257.3635 | 1550726.7157 | 0 | 453247.3901 | 0 | 2633331.1827 | 6851387.5669 | 4676212.7964 | 20913062.7838 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 43744655.7228 | 76723289.0664 | 5623.4133 | 3.4906 | 12531.998 | 21979.7387 | 255.4817 | 448.0867
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.8636 | 13.6654 | 1.1724 | 4 | 10473.5045 | 17505.8486 | 213.5166 | 356.8804 | 150.0395 | 0 | 91.6157 | 2933019.3071 | 251723.3794 | 2707301.2765 | 2051156.3602 | 0 | 543216.5389 | 0 | 3309702.5762 | 8611167.19 | 5877298.549 | 26284585.1774 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 49116178.1165 | 82094811.46 | 7498.9421 | 4.6896 | 10473.5045 | 17505.8486 | 213.5166 | 356.8804
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.2601 | 18.0192 | 1.5557 | 4 | 8943.4634 | 14243.139 | 182.3246 | 290.3657 | 150.5209 | 0 | 92.6158 | 3575386.0179 | 307355.1244 | 3376633.4513 | 2687934.3202 | 0 | 649651.2071 | 0 | 4132814.4472 | 10752735.4348 | 7338962.8808 | 32821472.8838 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 55653065.8228 | 88631699.1663 | 10000 | 6.2228 | 8943.4634 | 14243.139 | 182.3246 | 290.3657
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.822 | 23.4653 | 2.0322 | 4 | 7807.2778 | 11864.3201 | 159.1619 | 241.8702 | 150.803 | 0 | 113.4929 | 4317091.7853 | 371079.5776 | 4170159.6634 | 3486278.7647 | 0 | 774019.4178 | 0 | 5116265.3914 | 13311473.0581 | 9085353.8856 | 40631721.5439 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 63463314.4829 | 96441947.8264 | 13335.2143 | 8.1287 | 7807.2778 | 11864.3201 | 159.1619 | 241.8702
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.1823 | 29.8199 | 2.5846 | 4 | 6983.4744 | 10173.3328 | 142.3676 | 207.3971 | 150.8093 | 0 | 118.5824 | 5117664.9657 | 438892.4276 | 5051443.002 | 4423688.3681 | 0 | 907489.2996 | 0 | 6216279.4445 | 16173483.9804 | 11038735.1485 | 49367676.6364 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 72199269.5755 | 105177902.919 | 17782.7941 | 10.3386 | 6983.4744 | 10173.3328 | 142.3676 | 207.3971
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8554 | 33.7984 | 3.0269 | 4 | 6378.5656 | 9102.3743 | 130.0357 | 185.5642 | 150.6624 | 0 | 136.9918 | 5589982.0152 | 478219.7644 | 5584325.6799 | 5015733.738 | 0 | 894772.4384 | 0 | 6849583.118 | 17821210.2303 | 12163342.1714 | 54397169.1556 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 77228762.0946 | 110207395.4381 | 23713.7371 | 12.1075 | 6378.5656 | 9102.3743 | 130.0357 | 185.5642
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5681 | 37.3979 | 3.4475 | 4 | 5919.8014 | 8311.3071 | 120.6832 | 169.4372 | 150.4411 | 0 | 157.1077 | 6000665.7499 | 511896.7607 | 6056164.3031 | 5555865.6581 | 0 | 860580.2332 | 0 | 7404217.3549 | 19264254.7437 | 13148249.7034 | 58801894.5069 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 81633487.446 | 114612120.7895 | 31622.7766 | 13.7899 | 5919.8014 | 8311.3071 | 120.6832 | 169.4372
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.9808 | 40.5154 | 3.8286 | 4 | 5572.4254 | 7725.8897 | 113.6014 | 157.5027 | 150.186 | 0 | 180.0637 | 6344606.6921 | 539666.756 | 6457904.1265 | 6027758.2696 | 0 | 811095.6559 | 0 | 7870602.2851 | 20477692.6632 | 13976446.0171 | 62505772.4655 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 85337365.4046 | 118315998.7481 | 42169.6503 | 15.3142 | 5572.4254 | 7725.8897 | 113.6014 | 157.5027
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8755 | 43.0922 | 4.1578 | 4 | 5309.6949 | 7292.633 | 108.2453 | 148.6702 | 149.9327 | 0 | 202.4804 | 6620982.0565 | 561630.1194 | 6785662.1153 | 6419310.1969 | 0 | 752108.3065 | 0 | 8244480.1899 | 21450446.2787 | 14640370.3478 | 65474989.6109 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 88306582.55 | 121285215.8935 | 56234.1325 | 16.6312 | 5309.6949 | 7292.633 | 108.2453 | 148.6702
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4191 | 45.194 | 4.434 | 4 | 5111.2783 | 6970.6752 | 104.2003 | 142.1066 | 149.6976 | 0 | 186.1387 | 6840894.6121 | 578797.5879 | 7050409.6505 | 6735931.4133 | 0 | 691771.0667 | 0 | 8540143.6889 | 22219702.0542 | 15165403.2212 | 67823053.2949 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 90654646.234 | 123633279.5775 | 74989.4209 | 17.7362 | 5111.2783 | 6970.6752 | 104.2003 | 142.1066
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8346 | 47.5616 | 4.7074 | 4 | 4959.8685 | 6711.2785 | 101.1136 | 136.8185 | 149.4323 | 0 | 193.8965 | 7084346.194 | 597678.4874 | 7345843.7384 | 7093259.5414 | 0 | 660845.7905 | 0 | 8884969.7632 | 23116868.7659 | 15777737.9369 | 70561550.2177 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 93393143.1568 | 126371776.5003 | 100000 | 18.8298 | 4959.8685 | 6711.2785 | 101.1136 | 136.8185
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.2897 | 48.9782 | 4.8986 | 4 | 4844.4636 | 6527.5217 | 98.7609 | 133.0724 | 149.2758 | 0 | 212.0313 | 7228032.9539 | 608772.8898 | 7521255.8888 | 7307353.18 | 0 | 611050.0458 | 0 | 9077821.3337 | 23618628.9931 | 16120199.6021 | 72093114.8871 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 94924707.8261 | 127903341.1696 | 133352.1432 | 19.5945 | 4844.4636 | 6527.5217 | 98.7609 | 133.0724
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.7586 | 50.0748 | 5.0495 | 4 | 4757.3214 | 6390.0818 | 96.9844 | 130.2705 | 149.1498 | 0 | 192.3741 | 7338065.7957 | 617211.8362 | 7656409.1512 | 7473372.174 | 0 | 567247.2664 | 0 | 9224399.4271 | 23999995.1249 | 16380489.8234 | 73257190.5989 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 96088783.538 | 129067416.8815 | 177827.941 | 20.1981 | 4757.3214 | 6390.0818 | 96.9844 | 130.2705
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.3922 | 50.9035 | 5.1662 | 4 | 4691.5854 | 6287.4608 | 95.6443 | 128.1784 | 149.0518 | 0 | 191.5732 | 7420530.1372 | 623502.4259 | 7758187.6617 | 7599006.7023 | 0 | 529532.2124 | 0 | 9332996.0644 | 24282541.2989 | 16573333.3928 | 74119629.8958 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 96951222.8348 | 129929856.1783 | 237137.3706 | 20.6649 | 4691.5854 | 6287.4608 | 95.6443 | 128.1784
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4138 | 51.5368 | 5.2564 | 4 | 4642.0336 | 6210.541 | 94.6341 | 126.6103 | 148.9752 | 0 | 210.751 | 7483150.9726 | 628259.054 | 7835763.1381 | 7694937.3403 | 0 | 498446.3958 | 0 | 9414817.1913 | 24495423.0872 | 16718629.5876 | 74769426.7667 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 97601019.7058 | 130579653.0493 | 316227.766 | 21.0255 | 4642.0336 | 6210.541 | 94.6341 | 126.6103
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.9265 | 52.0084 | 5.3248 | 4 | 4604.7046 | 6153.0656 | 93.8731 | 125.4386 | 148.9172 | 0 | 216.0352 | 7529561.2971 | 631772.3074 | 7893425.1929 | 7766145.5207 | 0 | 472968.4614 | 0 | 9474610.384 | 24650992.7093 | 16824809.0514 | 75244284.9242 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 98075877.8633 | 131054511.2068 | 421696.5034 | 21.2991 | 4604.7046 | 6153.0656 | 93.8731 | 125.4386
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.0519 | 52.3586 | 5.3764 | 4 | 4576.6085 | 6110.0968 | 93.3004 | 124.5626 | 148.8735 | 0 | 210.3935 | 7563893.5472 | 634364.8448 | 7936171.7468 | 7819034.5499 | 0 | 452434.9975 | 0 | 9518300.8776 | 24764666.4116 | 16902393.6889 | 75591260.6644 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 98422853.6035 | 131401486.947 | 562341.3252 | 21.5056 | 4576.6085 | 6110.0968 | 93.3004 | 124.5626
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.8755 | 52.6144 | 5.415 | 4 | 4555.4753 | 6078.0341 | 92.8695 | 123.9089 | 148.8413 | 0 | 212.8024 | 7588914.3861 | 636250.7162 | 7967374.513 | 7857694.8566 | 0 | 435982.7509 | 0 | 9549624.7169 | 24846164.616 | 16958017.888 | 75840024.4437 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 98671617.3828 | 131650250.7263 | 749894.2093 | 21.66 | 4555.4753 | 6078.0341 | 92.8695 | 123.9089
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5017 | 52.8087 | 5.4443 | 4 | 4539.5885 | 6053.9512 | 92.5457 | 123.418 | 148.8168 | 0 | 199.9498 | 7607878.8893 | 637678.1825 | 7991052.0277 | 7887061.6782 | 0 | 423266.585 | 0 | 9573305.5715 | 24907777.342 | 17000069.8396 | 76028090.1159 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 98859683.0549 | 131838316.3984 | 1000000 | 21.7772 | 4539.5885 | 6053.9512 | 92.5457 | 123.418
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.9692 | 52.9536 | 5.4663 | 4 | 4527.6515 | 6035.9107 | 92.3023 | 123.0502 | 148.7983 | 0 | 188.5173 | 7622003.4663 | 638740.2329 | 8008702.5186 | 7908970.3548 | 0 | 413417.2717 | 0 | 9590815.1993 | 24953333.8018 | 17031163.0595 | 76167145.9048 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 98998738.8439 | 131977372.1874 | 1333521.4322 | 21.8654 | 4527.6515 | 6035.9107 | 92.3023 | 123.0502
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3176 | 53.0615 | 5.4829 | 4 | 4518.6861 | 6022.3982 | 92.1195 | 122.7747 | 148.7845 | 0 | 193.4013 | 7632510.6148 | 639529.6594 | 8021841.3407 | 7925288.3976 | 0 | 405835.0884 | 0 | 9603751.9893 | 24986992.6758 | 17054135.9326 | 76269885.6986 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99101478.6377 | 132080111.9812 | 1778279.41 | 21.9315 | 4518.6861 | 6022.3982 | 92.1195 | 122.7747
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5734 | 53.1407 | 5.4952 | 4 | 4511.9548 | 6012.2995 | 91.9823 | 122.5689 | 148.7744 | 0 | 203.9115 | 7640214.3179 | 640108.1005 | 8031479.4889 | 7937263.8771 | 0 | 399982.5653 | 0 | 9613128.8564 | 25011389.3605 | 17070787.1712 | 76344353.7378 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99175946.6769 | 132154580.0204 | 2371373.7057 | 21.9807 | 4511.9548 | 6012.2995 | 91.9823 | 122.5689
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7586 | 53.198 | 5.5043 | 4 | 4506.9023 | 6004.7666 | 91.8793 | 122.4153 | 148.767 | 0 | 195.7228 | 7645787.0989 | 640526.3353 | 8038454.385 | 7945933.0027 | 0 | 395454.515 | 0 | 9619800.5814 | 25028747.8203 | 17082634.6767 | 76397338.4151 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99228931.3542 | 132207564.6977 | 3162277.6602 | 22.0171 | 4506.9023 | 6004.7666 | 91.8793 | 122.4153
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.9024 | 53.2425 | 5.5112 | 4 | 4503.1106 | 5999.0885 | 91.802 | 122.2995 | 148.7613 | 0 | 210.4588 | 7650108.5995 | 640850.5796 | 8043864.4338 | 7952658.7051 | 0 | 392086.3694 | 0 | 9625031.788 | 25042358.3469 | 17091924.1408 | 76438882.963 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99270475.902 | 132249109.2455 | 4216965.0343 | 22.0449 | 4503.1106 | 5999.0885 | 91.802 | 122.2995
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.0144 | 53.2772 | 5.5165 | 4 | 4500.2657 | 5994.8047 | 91.744 | 122.2122 | 148.7569 | 0 | 211.6271 | 7653476.4646 | 641103.2273 | 8048081.3466 | 7957902.035 | 0 | 389595.4718 | 0 | 9629161.8327 | 25053103.8759 | 17099258.1851 | 76471682.4391 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99303275.3782 | 132281908.7217 | 5623413.2519 | 22.0661 | 4500.2657 | 5994.8047 | 91.744 | 122.2122
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.0876 | 53.2998 | 5.5203 | 4 | 4498.1315 | 5991.6578 | 91.7005 | 122.148 | 148.754 | 0 | 200.5041 | 7655673.6992 | 641267.9859 | 8050833.3322 | 7961324.3928 | 0 | 387580.8828 | 0 | 9631705.3142 | 25059721.4932 | 17103774.8449 | 76491881.9452 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99323474.8843 | 132302108.2278 | 7498942.0933 | 22.0811 | 4498.1315 | 5991.6578 | 91.7005 | 122.148
1 | 5700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1607 | 53.3224 | 5.5235 | 4 | 4496.5305 | 5989.1878 | 91.6679 | 122.0977 | 148.7511 | 0 | 197.3002 | 7657871.6774 | 641432.8591 | 8053585.789 | 7964747.5425 | 0 | 386293.2397 | 0 | 9634533.132 | 25067078.8949 | 17108796.4227 | 76514339.5571 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 99345932.4961 | 132324565.8396 | 10000000 | 22.0939 | 4496.5305 | 5989.1878 | 91.6679 | 122.0977
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8238 | [19 empty] | 100 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.0027 | [19 empty] | 133.3521 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2833 | [19 empty] | 177.8279 | 0
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.27508 | 0.0065634 | 4 | 942269.7824 | 2227221.0837 | 19209.444 | 45404.9143 | 108.7416 | 0 | 57.8355 | 152902.6429 | 10024.392 | 122517.4629 | 76596.4341 | 0 | 79127.7556 | 0 | 172055.7881 | 447653.8671 | 305532.9627 | 1366411.3054 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 24738153.9339 | 58472996.8426 | 237.1374 | 0.026254 | 942269.7824 | 2227221.0837 | 19209.444 | 45404.9143
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9042 | 0.41333 | 0.016203 | 4 | 388581.8161 | 909096.1418 | 7921.7659 | 18533.1545 | 117.3878 | 0 | 298.8207 | 213559.6836 | 14758.8061 | 168654.7702 | 97759.92 | 0 | 90454.9039 | 0 | 228223.3527 | 593790.3486 | 405274.1141 | 1812475.8991 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25184218.5276 | 58919061.4363 | 316.2278 | 0.064811 | 388581.8161 | 909096.1418 | 7921.7659 | 18533.1545
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.60996 | 0.031118 | 4 | 207014.6555 | 478041.5545 | 4220.2738 | 9745.5237 | 124.949 | 0 | 388.2067 | 291728.8807 | 21129.0841 | 229049.0778 | 127046.4635 | 0 | 104462.938 | 0 | 301632.4132 | 784785.6659 | 535632.3427 | 2395466.866 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25767209.4945 | 59502052.4032 | 421.6965 | 0.12447 | 207014.6555 | 478041.5545 | 4220.2738 | 9745.5237
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 0.87403 | 0.052757 | 4 | 125529.3888 | 285387.6533 | 2559.0864 | 5818.0133 | 131.1138 | 0 | 511.2061 | 387114.4895 | 29181.5223 | 304122.0929 | 166407.9872 | 0 | 120094.2519 | 0 | 392698.9341 | 1021722.073 | 697346.3091 | 3118687.6603 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 26490430.2888 | 60225273.1975 | 562.3413 | 0.21103 | 125529.3888 | 285387.6533 | 2559.0864 | 5818.0133
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3212 | 1.2342 | 0.083376 | 4 | 82175.6616 | 183328.3623 | 1675.262 | 3737.3966 | 136.201 | 0 | 66.1772 | 505233.9763 | 39397.7701 | 399413.3298 | 219320.7774 | 0 | 139136.2949 | 0 | 507975.838 | 1321648.9302 | 902052.552 | 4034179.4688 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 27405922.0973 | 61140765.006 | 749.8942 | 0.3335 | 82175.6616 | 183328.3623 | 1675.262 | 3737.3966
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7025 | 1.7198 | 0.12553 | 4 | 56862.4899 | 124046.5221 | 1159.2188 | 2528.8561 | 140.3022 | 0 | 90.0953 | 649772.2094 | 52088.7895 | 519378.9787 | 288960.3202 | 0 | 162373.9319 | 0 | 652303.9496 | 1697161.0709 | 1158347.304 | 5180386.5541 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 28552129.1827 | 62286972.0914 | 1000 | 0.50213 | 56862.4899 | 124046.5221 | 1159.2188 | 2528.8561
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5273 | 2.3674 | 0.18281 | 4 | 41009.8557 | 87143.4897 | 836.0414 | 1776.5379 | 143.4543 | 0 | 78.652 | 825496.6435 | 67696.551 | 669206.4933 | 383477.1588 | 0 | 190331.6183 | 0 | 833121.3013 | 2167610.7293 | 1479438.8627 | 6616379.3583 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 29988121.9868 | 63722964.8955 | 1333.5214 | 0.73124 | 41009.8557 | 87143.4897 | 836.0414 | 1776.5379
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9757 | 3.2487 | 0.26197 | 4 | 30367.0165 | 62560.4559 | 619.0727 | 1275.3795 | 146.1147 | 0 | 83.868 | 1044147.4728 | 87312.6855 | 860387.5865 | 511253.3969 | 0 | 224873.4636 | 0 | 1063910.0961 | 2768075.832 | 1889268.6336 | 8449229.1669 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 31820971.7955 | 65555814.7042 | 1778.2794 | 1.0479 | 30367.0165 | 62560.4559 | 619.0727 | 1275.3795
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2152 | 4.4171 | 0.36776 | 4 | 23189.7727 | 46122.1496 | 472.7549 | 940.2624 | 148.0894 | 0 | 85.2045 | 1308956.7956 | 111157.9698 | 1098482.4173 | 682901.6475 | 0 | 266652.5328 | 0 | 1352579.0316 | 3519133.188 | 2401880.7118 | 10741744.2944 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 34113486.9229 | 67848329.8316 | 2371.3737 | 1.4711 | 23189.7727 | 46122.1496 | 472.7549 | 940.2624
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5273 | 5.9754 | 0.50937 | 4 | 18158.2377 | 34715.5368 | 370.1802 | 707.7232 | 149.612 | 0 | 84.5859 | 1631999.5998 | 140253.9503 | 1397233.9357 | 911720.1224 | 0 | 317834.5911 | 0 | 1715626.4578 | 4463708.1197 | 3046572.5117 | 13624949.2886 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 36996691.9171 | 70731534.8259 | 3162.2777 | 2.0375 | 18158.2377 | 34715.5368 | 370.1802 | 707.7232
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.2152 | 8.029 | 0.69599 | 4 | 14572.842 | 26690.3781 | 297.0871 | 544.1195 | 150.7717 | 0 | 89.9343 | 2021114.6141 | 175090.2036 | 1768282.2154 | 1208980.8222 | 0 | 379385.646 | 0 | 2165612.8655 | 5634480.4477 | 3845648.6825 | 17198595.497 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 40570338.1255 | 74305181.0342 | 4216.965 | 2.784 | 14572.842 | 26690.3781 | 297.0871 | 544.1195
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.7326 | 10.7503 | 0.94474 | 4 | 11930.6076 | 20857.5884 | 243.2216 | 425.2102 | 151.6571 | 0 | 99.98 | 2496293.2272 | 217786.1175 | 2231690.0533 | 1610269.2074 | 0 | 454602.2717 | 0 | 2734149.9421 | 7113697.2981 | 4855244.5778 | 21713732.6953 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 45085475.3238 | 78820318.2326 | 5623.4133 | 3.779 | 11930.6076 | 20857.5884 | 243.2216 | 425.2102
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5279 | 14.2969 | 1.2686 | 4 | 9983.2002 | 16631.1922 | 203.521 | 339.0493 | 152.3257 | 0 | 105.296 | 3064884.509 | 268557.7001 | 2801929.3398 | 2130228.8186 | 0 | 544597.545 | 0 | 3435977.1859 | 8939707.8218 | 6101534.281 | 27287417.2013 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 50659159.8298 | 84394002.7386 | 7498.9421 | 5.0744 | 9983.2002 | 16631.1922 | 203.521 | 339.0493
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.1032 | 18.843 | 1.6821 | 4 | 8536.3101 | 13550.1542 | 174.0242 | 276.2382 | 152.8117 | 0 | 100.3565 | 3735139.708 | 327883.5925 | 3493321.1967 | 2790429.2717 | 0 | 651177.9349 | 0 | 4289201.1645 | 11159621.5939 | 7616671.0451 | 34063445.5074 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 57435188.1359 | 91170031.0446 | 10000 | 6.7283 | 8536.3101 | 13550.1542 | 174.0242 | 276.2382
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8379 | 24.5083 | 2.1945 | 4 | 7462.4956 | 11305.676 | 152.1331 | 230.4815 | 153.0886 | 0 | 90.3827 | 4506438.1545 | 395602.7697 | 4310057.5872 | 3616003.771 | 0 | 775204.0866 | 0 | 5305289.4839 | 13803274.9726 | 9421018.7977 | 42132889.6231 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 65504632.2517 | 99239475.1604 | 13335.2143 | 8.7778 | 7462.4956 | 11305.676 | 152.1331 | 230.4815
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.7831 | 31.2476 | 2.7941 | 4 | 6685.2777 | 9703.6871 | 136.2884 | 197.8228 | 153.0734 | 0 | 116.0724 | 5354252.8679 | 468830.6257 | 5234696.0119 | 4604035.4196 | 0 | 915889.7166 | 0 | 6465304.8103 | 16821396.9 | 11480949.0294 | 51345355.3813 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 74717098.0099 | 108451940.9186 | 17782.7941 | 11.1764 | 6685.2777 | 9703.6871 | 136.2884 | 197.8228
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6741 | 35.7551 | 3.283 | 4 | 6124.9021 | 8693.8019 | 124.8644 | 177.2349 | 152.8858 | 0 | 108.8893 | 5886890.7099 | 513889.335 | 5831318.1854 | 5270596.5369 | 0 | 920269.8334 | 0 | 7184956.1942 | 18693782.1802 | 12758890.4568 | 57060593.4317 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 80432336.0602 | 114167178.969 | 23713.7371 | 13.132 | 6124.9021 | 8693.8019 | 124.8644 | 177.2349
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2555 | 39.3964 | 3.7209 | 4 | 5700.2626 | 7966.8437 | 116.2076 | 162.4149 | 152.6416 | 0 | 156.7213 | 6299960.9786 | 548244.3302 | 6302820.1612 | 5814788.7202 | 0 | 880341.0875 | 0 | 7740000.5583 | 20137893.7603 | 13744526.2838 | 61468575.8802 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 84840318.5087 | 118575161.4175 | 31622.7766 | 14.8836 | 5700.2626 | 7966.8437 | 116.2076 | 162.4149
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.5165 | 42.5362 | 4.115 | 4 | 5378.6922 | 7428.2 | 109.6519 | 151.4339 | 152.369 | 0 | 203.6382 | 6644636.9668 | 576428.5828 | 6702832.983 | 6288381.5905 | 0 | 826160.3377 | 0 | 8204991.7797 | 21347705.5355 | 14570247.6795 | 65161385.4554 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 88533128.0839 | 122267970.9927 | 42169.6503 | 16.46 | 5378.6922 | 7428.2 | 109.6519 | 151.4339
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3628 | 45.16 | 4.4564 | 4 | 5135.3869 | 7027.8954 | 104.6918 | 143.2732 | 152.0993 | 0 | 231.9515 | 6924938.3504 | 598984.3569 | 7032914.5335 | 6687680.0054 | 0 | 764955.0798 | 0 | 8583694.2071 | 22333011.5692 | 15242739.2934 | 68168917.3957 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 91540660.0242 | 125275502.9329 | 56234.1325 | 17.8255 | 5135.3869 | 7027.8954 | 104.6918 | 143.2732
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4017 | 47.1464 | 4.7309 | 4 | 4951.738 | 6734.4336 | 100.9479 | 137.2905 | 151.8691 | 0 | 228.3254 | 7131381.6613 | 615162.2959 | 7280687.4831 | 6983721.854 | 0 | 697061.2338 | 0 | 8856125.6659 | 23041822.3416 | 15726517.2103 | 70332479.7459 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 93704222.3744 | 127439065.2832 | 74989.4209 | 18.9235 | 4951.738 | 6734.4336 | 100.9479 | 137.2905
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9003 | 49.5997 | 5.0146 | 4 | 4810.6376 | 6492.4609 | 98.0714 | 132.3576 | 151.6 | 0 | 193.4526 | 7381495.5877 | 634532.8687 | 7584056.5979 | 7341504.7694 | 0 | 667198.5645 | 0 | 9207427.4714 | 23955837.5775 | 16350351.3899 | 73122404.8271 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 96494147.4556 | 130228990.3643 | 100000 | 20.0585 | 4810.6376 | 6492.4609 | 98.0714 | 132.3576
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2387 | 51.0093 | 5.2076 | 4 | 4703.6986 | 6323.213 | 95.8913 | 128.9073 | 151.4407 | 0 | 232.126 | 7522912.3774 | 645377.3893 | 7757113.9181 | 7546896.5096 | 0 | 615923.1068 | 0 | 9394407.0875 | 24442320.1838 | 16682385.7649 | 74607336.3374 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 97979078.9659 | 131713921.8746 | 133352.1432 | 20.8302 | 4703.6986 | 6323.213 | 95.8913 | 128.9073
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5808 | 52.0888 | 5.3587 | 4 | 4622.9018 | 6196.7331 | 94.2441 | 126.3288 | 151.314 | 0 | 217.5551 | 7629989.9236 | 653516.8866 | 7889064.7231 | 7704055.7401 | 0 | 570668.5365 | 0 | 9534445.3658 | 24806671.0583 | 16931062.7234 | 75719474.9574 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 99091217.5859 | 132826060.4946 | 177827.941 | 21.4349 | 4622.9018 | 6196.7331 | 94.2441 | 126.3288
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.1554 | 52.9164 | 5.4763 | 4 | 4561.9163 | 6101.9638 | 93.0008 | 124.3968 | 151.2139 | 0 | 229.0694 | 7711373.2611 | 659659.2633 | 7989908.9708 | 7824477.636 | 0 | 532395.3128 | 0 | 9639947.6332 | 25081166.3164 | 17118411.3774 | 76557339.7709 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 99929082.3994 | 133663925.3082 | 237137.3706 | 21.9051 | 4561.9163 | 6101.9638 | 93.0008 | 124.3968
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0728 | 53.5306 | 5.5657 | 4 | 4515.9253 | 6031.2282 | 92.0632 | 122.9547 | 151.1381 | 0 | 198.2637 | 7771370.2143 | 664162.9683 | 8064564.863 | 7913799.4265 | 0 | 500198.5991 | 0 | 9716497.4678 | 25280333.2835 | 17254346.9249 | 77165273.7474 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 100537016.3759 | 134271859.2847 | 316227.766 | 22.2628 | 4515.9253 | 6031.2282 | 92.0632 | 122.9547
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5271 | 53.9952 | 5.634 | 4 | 4481.272 | 5978.1946 | 91.3568 | 121.8736 | 151.0799 | 0 | 195.77 | 7816534.2939 | 667539.3276 | 8120941.1121 | 7981346.868 | 0 | 474160.6886 | 0 | 9773603.6932 | 25428911.9678 | 17355754.9299 | 77618792.8811 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 100990535.5096 | 134725378.4183 | 421696.5034 | 22.5361 | 4481.272 | 5978.1946 | 91.3568 | 121.8736
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.6138 | 54.3416 | 5.6857 | 4 | 4455.1821 | 5938.4985 | 90.8249 | 121.0643 | 151.0359 | 0 | 197.3154 | 7850087.3591 | 670039.753 | 8162924.6139 | 8031702.6362 | 0 | 453283.1244 | 0 | 9815534.6198 | 25538007.6377 | 17430214.9663 | 77951794.7103 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 101323537.3388 | 135058380.2476 | 562341.3252 | 22.7429 | 4455.1821 | 5938.4985 | 90.8249 | 121.0643
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.642 | 54.6691 | 5.7297 | 4 | 4435.552 | 5907.4757 | 90.4247 | 120.4319 | 150.9942 | 0 | 199.3511 | 7881790.1712 | 672408.6188 | 8202560.7672 | 8079712.0066 | 0 | 439517.12 | 0 | 9857635.5867 | 25647545.7175 | 17504976.9565 | 78286146.9445 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 101657889.573 | 135392732.4818 | 749894.2093 | 22.9189 | 4435.552 | 5907.4757 | 90.4247 | 120.4319
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.2339 | 54.8581 | 5.7592 | 4 | 4420.7735 | 5885.1662 | 90.1234 | 119.9771 | 150.9699 | 0 | 195.7345 | 7900296.4099 | 673829.2181 | 8225372.0685 | 8108897.6993 | 0 | 426467.9841 | 0 | 9880596.7182 | 25707285.8717 | 17545750.8393 | 78468496.8093 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 101840239.4378 | 135575082.3465 | 1000000 | 23.0367 | 4420.7735 | 5885.1662 | 90.1234 | 119.9771
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6741 | 54.9985 | 5.7813 | 4 | 4409.6692 | 5868.4624 | 89.8971 | 119.6365 | 150.9518 | 0 | 222.8586 | 7914027.7077 | 674882.2703 | 8242311.1054 | 8130593.6074 | 0 | 416350.8297 | 0 | 9897484.553 | 25751224.5537 | 17575739.8926 | 78602614.5198 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 101974357.1484 | 135709200.0571 | 1333521.4322 | 23.1252 | 4409.6692 | 5868.4624 | 89.8971 | 119.6365
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.0102 | 55.1057 | 5.7981 | 4 | 4401.3291 | 5855.9015 | 89.727 | 119.3805 | 150.938 | 0 | 230.7286 | 7924498.3602 | 675684.7191 | 8255235.2136 | 8147160.2655 | 0 | 408674.0731 | 0 | 9910388.5263 | 25784798.0451 | 17598654.4904 | 78705093.6933 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102076836.3218 | 135811679.2305 | 1778279.41 | 23.1923 | 4401.3291 | 5855.9015 | 89.727 | 119.3805
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.2466 | 55.181 | 5.8103 | 4 | 4395.0672 | 5846.5756 | 89.5994 | 119.1904 | 150.9282 | 0 | 232.6787 | 7931849.4104 | 676247.727 | 8264313.2964 | 8158804.4194 | 0 | 402619.5613 | 0 | 9919195.4216 | 25807711.7803 | 17614293.5855 | 78775035.2018 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102146777.8303 | 135881620.7391 | 2371373.7057 | 23.2412 | 4395.0672 | 5846.5756 | 89.5994 | 119.1904
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4318 | 55.24 | 5.8197 | 4 | 4390.367 | 5839.5349 | 89.5036 | 119.0468 | 150.9205 | 0 | 225.3072 | 7937606.1964 | 676688.4965 | 8271424.5413 | 8167929.4784 | 0 | 398124.5321 | 0 | 9926191.5655 | 25825914.3115 | 17626717.1871 | 78830596.3088 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102202338.9373 | 135937181.846 | 3162277.6602 | 23.2788 | 4390.367 | 5839.5349 | 89.5036 | 119.0468
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5755 | 55.2858 | 5.8269 | 4 | 4386.8398 | 5834.2266 | 89.4317 | 118.9386 | 150.9146 | 0 | 222.8402 | 7942070.4885 | 677030.2231 | 8276940.3982 | 8175009.6037 | 0 | 394782.9734 | 0 | 9931675.1379 | 25840181.4421 | 17636454.7969 | 78874145.0638 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102245887.6923 | 135980730.6011 | 4216965.0343 | 23.3074 | 4386.8398 | 5834.2266 | 89.4317 | 118.9386
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6681 | 55.3152 | 5.8319 | 4 | 4384.1932 | 5830.335 | 89.3777 | 118.8593 | 150.9107 | 0 | 225.0123 | 7944944.6626 | 677250.1209 | 8280492.7864 | 8179571.0857 | 0 | 392065.0687 | 0 | 9934986.2525 | 25848796.2831 | 17642334.6029 | 78900440.8628 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102272183.4913 | 136007026.4001 | 5623413.2519 | 23.3275 | 4384.1932 | 5830.335 | 89.3777 | 118.8593
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7413 | 55.3385 | 5.8357 | 4 | 4382.2078 | 5827.3947 | 89.3372 | 118.7993 | 150.9077 | 0 | 210.8618 | 7947214.7812 | 677423.7947 | 8283298.7787 | 8183174.6203 | 0 | 390063.6873 | 0 | 9937658.5082 | 25855748.9444 | 17647079.9371 | 78921663.0519 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102293405.6804 | 136028248.5892 | 7498942.0933 | 23.3429 | 4382.2078 | 5827.3947 | 89.3372 | 118.7993
1 | 5800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7996 | 55.3571 | 5.8387 | 4 | 4380.7184 | 5825.1693 | 89.3069 | 118.754 | 150.9053 | 0 | 230.3066 | 7949024.9051 | 677562.2761 | 8285536.2756 | 8186048.335 | 0 | 388601.3395 | 0 | 9939841.5212 | 25861428.6963 | 17650956.4845 | 78938999.8333 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 102310742.4618 | 136045585.3706 | 10000000 | 23.3548 | 4380.7184 | 5825.1693 | 89.3069 | 118.754
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6523 | [19 empty] | 100 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8303 | [19 empty] | 133.3521 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6075 | [19 empty] | 177.8279 | 0
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4908 | 0.29012 | 0.0078586 | 4 | 805946.6776 | 1903440.6996 | 16430.3131 | 38804.2133 | 110.545 | 0 | 52.2714 | 160448.8791 | 10632.8314 | 127680.2099 | 78668.7281 | 0 | 80019.055 | 0 | 178405.3844 | 464174.2141 | 316808.439 | 1416837.7409 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25334590.1498 | 59833846.751 | 237.1374 | 0.031435 | 805946.6776 | 1903440.6996 | 16430.3131 | 38804.2133
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.43379 | 0.018318 | 4 | 352008.7553 | 822846.8136 | 7176.1746 | 16774.8453 | 119.2124 | 0 | 312.7901 | 223135.0294 | 15590.7384 | 175078.3947 | 100358.6627 | 0 | 91096.2594 | 0 | 236051.043 | 614156.3931 | 419174.358 | 1874640.8787 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25792393.2875 | 60291649.8887 | 316.2278 | 0.073272 | 352008.7553 | 822846.8136 | 7176.1746 | 16774.8453
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.63631 | 0.034379 | 4 | 191881.8166 | 442754.2178 | 3911.7704 | 9026.1436 | 126.7583 | 0 | 424.1948 | 303407.3547 | 22229.6974 | 236629.4971 | 130465.9322 | 0 | 104518.1403 | 0 | 310927.7424 | 808970.2057 | 552138.7881 | 2469287.3578 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 26387039.7667 | 60886296.3679 | 421.6965 | 0.13752 | 191881.8166 | 442754.2178 | 3911.7704 | 9026.1436
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3434 | 0.9142 | 0.057757 | 4 | 117475.8728 | 266804.3228 | 2394.9046 | 5439.167 | 133.0762 | 0 | 564.5959 | 403346.3522 | 30787.0522 | 314834.6246 | 171021.9868 | 0 | 120487.7739 | 0 | 405786.3379 | 1055772.8131 | 720586.6389 | 3222623.5794 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 27140375.9882 | 61639632.5894 | 562.3413 | 0.23103 | 117475.8728 | 266804.3228 | 2394.9046 | 5439.167
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4092 | 1.2938 | 0.090826 | 4 | 77330.3807 | 172289.7933 | 1576.4844 | 3512.3605 | 138.2852 | 0 | 67.2371 | 527275.3328 | 41672.4264 | 414208.3376 | 225337.5667 | 0 | 140050.643 | 0 | 525932.2795 | 1368367.9078 | 933939.2142 | 4176783.708 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 28094536.1168 | 62593792.718 | 749.8942 | 0.36331 | 77330.3807 | 172289.7933 | 1576.4844 | 3512.3605
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8124 | 1.8033 | 0.1366 | 4 | 53606.0322 | 116743.1578 | 1092.8315 | 2379.9672 | 142.4244 | 0 | 56.842 | 678724.6071 | 55246.0988 | 538651.2738 | 299065.2879 | 0 | 163251.0497 | 0 | 676625.9437 | 1760441.9105 | 1201537.7774 | 5373543.9487 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 29291296.3576 | 63790552.9587 | 1000 | 0.54642 | 53606.0322 | 116743.1578 | 1092.8315 | 2379.9672
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.671 | 2.482 | 0.19842 | 4 | 38785.3417 | 82252.247 | 790.6917 | 1676.8233 | 145.6059 | 0 | 91.4065 | 862289.4514 | 71865.1163 | 693928.2833 | 397305.0676 | 0 | 191347.9237 | 0 | 864526.9785 | 2249321.8592 | 1535208.3879 | 6865793.0679 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 30783545.4767 | 65282802.0779 | 1333.5214 | 0.79369 | 38785.3417 | 82252.247 | 790.6917 | 1676.8233
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1601 | 3.4058 | 0.28434 | 4 | 28747.1331 | 59079.6454 | 586.0492 | 1204.4185 | 148.3133 | 0 | 92.0207 | 1091558.8491 | 92949.0655 | 892042.6002 | 531789.1659 | 0 | 225894.845 | 0 | 1105351.465 | 2875897.7732 | 1962859.324 | 8778343.0879 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 32696095.4967 | 67195352.0979 | 1778.2794 | 1.1374 | 28747.1331 | 59079.6454 | 586.0492 | 1204.4185
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4588 | 4.6291 | 0.39847 | 4 | 22006.243 | 43651.1781 | 448.627 | 889.8883 | 150.3161 | 0 | 106.1589 | 1368158.9229 | 118399.9756 | 1138553.8508 | 709399.5046 | 0 | 267834.9166 | 0 | 1404915.3965 | 3655301.6739 | 2494818.5014 | 11157382.7422 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 35075135.1511 | 69574391.7523 | 2371.3737 | 1.5939 | 22006.243 | 43651.1781 | 448.627 | 889.8883
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8368 | 6.2559 | 0.55141 | 4 | 17259.184 | 32900.5807 | 351.8518 | 670.7228 | 151.8569 | 0 | 84.1331 | 1705545.578 | 149585.5957 | 1446939.0023 | 947533.475 | 0 | 318881.4735 | 0 | 1781709.1986 | 4635641.8559 | 3163920.8195 | 14149756.9985 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 38067509.4073 | 72566766.0085 | 3162.2777 | 2.2056 | 17259.184 | 32900.5807 | 351.8518 | 670.7228
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.6368 | 8.4101 | 0.75327 | 4 | 13869.1983 | 25319.0077 | 282.7424 | 516.1622 | 153.0359 | 0 | 92.592 | 2113315.9552 | 186967.1472 | 1831850.3627 | 1256949.6532 | 0 | 380974.119 | 0 | 2250322.3226 | 5854877.0788 | 3996073.912 | 17871330.5507 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 41789082.9595 | 76288339.5607 | 4216.965 | 3.0131 | 13869.1983 | 25319.0077 | 282.7424 | 516.1622
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.2468 | 11.2396 | 1.0195 | 4 | 11384.9651 | 19845.161 | 232.0979 | 404.5704 | 153.9304 | 0 | 99.8513 | 2605683.9279 | 232063.4289 | 2308621.9235 | 1665267.0334 | 0 | 455518.461 | 0 | 2834190.3621 | 7373981.9499 | 5032894.201 | 22508221.2876 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 46425973.6964 | 80925230.2976 | 5623.4133 | 4.0778 | 11384.9651 | 19845.161 | 232.0979 | 404.5704
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.1884 | 14.9347 | 1.3672 | 4 | 9540.7665 | 15849.2141 | 194.5014 | 323.1077 | 154.6083 | 0 | 92.0814 | 3197441.8775 | 286100.0336 | 2896510.9452 | 2198162.379 | 0 | 545420.7888 | 0 | 3558218.0494 | 9257753.4736 | 6318606.9735 | 28258214.5206 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 52175966.9294 | 86675223.5306 | 7498.9421 | 5.4687 | 9540.7665 | 15849.2141 | 194.5014 | 323.1077
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.9385 | 19.7009 | 1.8126 | 4 | 8167.6348 | 12925.8906 | 166.5083 | 263.5118 | 155.0987 | 0 | 97.8092 | 3897626.6693 | 349153.8702 | 3614008.35 | 2884283.9604 | 0 | 652400.5969 | 0 | 4445014.6443 | 11565016.3065 | 7893361.2665 | 35300865.6642 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 59218618.0731 | 93717874.6743 | 10000 | 7.2504 | 8167.6348 | 12925.8906 | 166.5083 | 263.5118
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.8831 | 25.7056 | 2.3636 | 4 | 7155.3459 | 10804.3883 | 145.8714 | 220.2621 | 155.3695 | 0 | 107.8944 | 4703920.0149 | 419797.8711 | 4471646.4099 | 3745971.3153 | 0 | 778031.1637 | 0 | 5506553.0422 | 14326921.4665 | 9778418.2897 | 43731259.5733 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 67649011.9821 | 102148268.5833 | 13335.2143 | 9.4543 | 7155.3459 | 10804.3883 | 145.8714 | 220.2621
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9816 | 32.7004 | 3.0037 | 4 | 6418.7106 | 9290.0606 | 130.8541 | 189.3905 | 155.3337 | 0 | 104.7066 | 5581145.8405 | 496959.3422 | 5421028.9909 | 4760424.3639 | 0 | 917925.184 | 0 | 6699218.6513 | 17429992.7321 | 11896328.1902 | 53203023.295 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 77120775.7038 | 111620032.305 | 17782.7941 | 12.015 | 6418.7106 | 9290.0606 | 130.8541 | 189.3905
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.7675 | 37.8938 | 3.5558 | 4 | 5890.526 | 8316.0866 | 120.0863 | 169.5347 | 155.0917 | 0 | 144.846 | 6201319.6421 | 551946.4907 | 6098942.6637 | 5525954.107 | 0 | 950069.2858 | 0 | 7538010.5538 | 19612357.2024 | 13385836.7843 | 59864436.7296 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 83782189.1385 | 118281445.7397 | 23713.7371 | 14.2232 | 5890.526 | 8316.0866 | 120.0863 | 169.5347
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.7887 | 41.371 | 3.9991 | 4 | 5496.1021 | 7652.764 | 112.0455 | 156.0119 | 154.8352 | 0 | 145.1949 | 6596605.2676 | 585840.394 | 6543319.3787 | 6040621.5222 | 0 | 897465.6167 | 0 | 8058902.3499 | 20967610.8062 | 14310825.2165 | 64001190.5517 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 87918942.9605 | 122418199.5617 | 31622.7766 | 15.9966 | 5496.1021 | 7652.764 | 112.0455 | 156.0119
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8406 | 44.5096 | 4.4028 | 4 | 5198.0982 | 7157.0387 | 105.9703 | 145.9059 | 154.5484 | 0 | 193.3581 | 6938305.2906 | 613901.964 | 6939084.6074 | 6505194.1295 | 0 | 837985.5357 | 0 | 8515443.8956 | 22155438.2586 | 15121541.8603 | 67626895.5417 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 91544647.9505 | 126043904.5517 | 42169.6503 | 17.6112 | 5198.0982 | 7157.0387 | 105.9703 | 145.9059
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4434 | 47.1097 | 4.7493 | 4 | 4972.573 | 6788.588 | 101.3726 | 138.3945 | 154.2704 | 0 | 208.4138 | 7213671.0925 | 636069.8371 | 7263129.0828 | 6892388.2309 | 0 | 772135.606 | 0 | 8883183.6012 | 23112221.5389 | 15774566.1089 | 70547365.0983 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 94465117.5072 | 128964374.1084 | 56234.1325 | 18.9972 | 4972.573 | 6788.588 | 101.3726 | 138.3945
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.8964 | 49.9709 | 5.0905 | 4 | 4801.1022 | 6495.388 | 97.877 | 132.4173 | 153.9454 | 0 | 217.8266 | 7509880.0025 | 659597.5111 | 7615905.4916 | 7320303.9348 | 0 | 735719.3326 | 0 | 9298148.4463 | 24191874.9448 | 16511451.7432 | 73842881.4069 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 97760633.8158 | 132259890.417 | 74989.4209 | 20.3621 | 4801.1022 | 6495.388 | 97.877 | 132.4173
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.2749 | 51.7786 | 5.3389 | 4 | 4669.4443 | 6284.9102 | 95.1929 | 128.1264 | 153.7465 | 0 | 227.1007 | 7694466.1496 | 674251.669 | 7836708.1242 | 7590659.2827 | 0 | 677555.6567 | 0 | 9544719.9441 | 24833403.4032 | 16949308.0981 | 75801072.3275 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 99718824.7363 | 134218081.3375 | 100000 | 21.3556 | 4669.4443 | 6284.9102 | 95.1929 | 128.1264
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.4749 | 53.1802 | 5.5365 | 4 | 4569.8968 | 6127.7118 | 93.1635 | 124.9217 | 153.5847 | 0 | 213.2366 | 7835687.1079 | 685355.2438 | 8006953.4081 | 7800938.9929 | 0 | 624413.9086 | 0 | 9731805.9779 | 25320162.8867 | 17281531.4475 | 77286848.9735 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101204601.3824 | 135703857.9835 | 133352.1432 | 22.1459 | 4569.8968 | 6127.7118 | 93.1635 | 124.9217
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.7144 | 54.2553 | 5.6913 | 4 | 4494.7073 | 6010.1567 | 91.6307 | 122.5252 | 153.4561 | 0 | 220.843 | 7942899.2916 | 693719.8195 | 8136990.6601 | 7962637.9141 | 0 | 577923.2802 | 0 | 9872526.6766 | 25686289.2787 | 17531420.2332 | 78404407.154 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 102322159.5628 | 136821416.164 | 177827.941 | 22.765 | 4494.7073 | 6010.1567 | 91.6307 | 122.5252
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1628 | 55.0644 | 5.8104 | 4 | 4437.9685 | 5922.3352 | 90.474 | 120.7348 | 153.3567 | 0 | 226.1688 | 8022949.9743 | 699927.3451 | 8234543.0894 | 8084563.8457 | 0 | 538206.7975 | 0 | 9976274.5103 | 25956219.8605 | 17715653.4018 | 79228338.8245 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 103146091.2334 | 137645347.8346 | 237137.3706 | 23.2417 | 4437.9685 | 5922.3352 | 90.474 | 120.7348
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.007 | 55.6718 | 5.9015 | 4 | 4395.1904 | 5856.6399 | 89.6019 | 119.3955 | 153.2806 | 0 | 212.4621 | 8082702.8301 | 704539.5992 | 8307618.6303 | 8176247.1691 | 0 | 505260.6822 | 0 | 10052783.8753 | 26155281.534 | 17851517.0842 | 79835951.4044 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 103753703.8133 | 138252960.4145 | 316227.766 | 23.6062 | 4395.1904 | 5856.6399 | 89.6019 | 119.3955
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3908 | 56.1264 | 5.9708 | 4 | 4362.9635 | 5807.4664 | 88.9449 | 118.3931 | 153.2229 | 0 | 188.3157 | 8127229.4164 | 707964.2985 | 8362221.0439 | 8244950.9371 | 0 | 478500.1779 | 0 | 10109137.6908 | 26301902.6022 | 17951588.976 | 80283495.1429 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 104201247.5517 | 138700504.1529 | 421696.5034 | 23.8831 | 4362.9635 | 5807.4664 | 88.9449 | 118.3931
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.4307 | 56.4674 | 6.0233 | 4 | 4338.7033 | 5770.6196 | 88.4503 | 117.6419 | 153.1792 | 0 | 230.6174 | 8160517.9223 | 710517.7059 | 8403126.0156 | 8296530.9969 | 0 | 457178.5393 | 0 | 10150869.7602 | 26410480.8864 | 18025695.8861 | 80614917.7128 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 104532670.1216 | 139031926.7228 | 562341.3252 | 24.0931 | 4338.7033 | 5770.6196 | 88.4503 | 117.6419
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.1929 | 56.717 | 6.0625 | 4 | 4320.4524 | 5743.1058 | 88.0783 | 117.081 | 153.1469 | 0 | 234.0581 | 8184821.6036 | 712378.0413 | 8433036.941 | 8334308.764 | 0 | 440179.4552 | 0 | 10180842.674 | 26488464.2597 | 18078921.1408 | 80852952.8795 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 104770705.2884 | 139269961.8896 | 749894.2093 | 24.2499 | 4320.4524 | 5743.1058 | 88.0783 | 117.081
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7607 | 56.9028 | 6.092 | 4 | 4306.7306 | 5722.4989 | 87.7985 | 116.6609 | 153.1227 | 0 | 218.8493 | 8202877.7305 | 713758.0441 | 8455284.2741 | 8362440.6754 | 0 | 426911.2064 | 0 | 10202896.0529 | 26545842.6279 | 18118083.0561 | 81028093.6675 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 104945846.0763 | 139445102.6775 | 1000000 | 24.3679 | 4306.7306 | 5722.4989 | 87.7985 | 116.6609
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.1823 | 57.0406 | 6.1141 | 4 | 4296.4192 | 5707.071 | 87.5883 | 116.3464 | 153.1047 | 0 | 210.9344 | 8216252.6789 | 714779.0908 | 8471777.9646 | 8383315.5108 | 0 | 416624.1065 | 0 | 10219072.2471 | 26587929.7669 | 18146808.3932 | 81156559.7586 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105074312.1675 | 139573568.7687 | 1333521.4322 | 24.4563 | 4296.4192 | 5707.071 | 87.5883 | 116.3464
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4964 | 57.1432 | 6.1306 | 4 | 4288.6739 | 5695.5124 | 87.4304 | 116.1107 | 153.0913 | 0 | 232.4253 | 8226203.3393 | 715538.0736 | 8484056.7232 | 8398866.0279 | 0 | 408718.0289 | 0 | 10231019.0552 | 26619012.9111 | 18168023.2778 | 81251437.4369 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105169189.8457 | 139668446.4469 | 1778279.41 | 24.5225 | 4288.6739 | 5695.5124 | 87.4304 | 116.1107
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.7204 | 57.2163 | 6.1428 | 4 | 4282.8583 | 5686.9092 | 87.3119 | 115.9353 | 153.0816 | 0 | 223.9137 | 8233288.1068 | 716078.0585 | 8492803.666 | 8409949.23 | 0 | 402541.5193 | 0 | 10239317.6265 | 26640604.0912 | 18182759.7019 | 81317342.0004 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105235094.4092 | 139734351.0104 | 2371373.7057 | 24.5712 | 4282.8583 | 5686.9092 | 87.3119 | 115.9353
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.901 | 57.2753 | 6.1523 | 4 | 4278.4928 | 5680.386 | 87.2229 | 115.8024 | 153.0739 | 0 | 228.3959 | 8238997.5289 | 716513.0928 | 8499854.3955 | 8418886.0568 | 0 | 398018.1495 | 0 | 10246184.9972 | 26658471.5811 | 18194954.6309 | 81371880.4327 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105289632.8416 | 139788889.4428 | 3162277.6602 | 24.609 | 4278.4928 | 5680.386 | 87.2229 | 115.8024
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.0176 | 57.3134 | 6.1589 | 4 | 4275.2166 | 5675.5987 | 87.1561 | 115.7048 | 153.0689 | 0 | 232.4456 | 8242682.7937 | 716793.6901 | 8504407.4858 | 8424659.0872 | 0 | 394349.846 | 0 | 10250328.2321 | 26669251.4285 | 18202312.0983 | 81404784.6618 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105322537.0706 | 139821793.6718 | 4216965.0343 | 24.6356 | 4275.2166 | 5675.5987 | 87.1561 | 115.7048
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.1297 | 57.3499 | 6.1645 | 4 | 4272.7584 | 5671.8713 | 87.106 | 115.6288 | 153.064 | 0 | 231.4611 | 8246222.4502 | 717063.2941 | 8508780.1846 | 8430203.8372 | 0 | 391900.661 | 0 | 10254726.4666 | 26680694.7324 | 18210122.3883 | 81439714.0143 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105357466.4231 | 139856723.0243 | 5623413.2519 | 24.658 | 4272.7584 | 5671.8713 | 87.106 | 115.6288
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.2003 | 57.373 | 6.1683 | 4 | 4270.9141 | 5669.1512 | 87.0684 | 115.5733 | 153.061 | 0 | 255.9523 | 8248449.3925 | 717232.8065 | 8511532.24 | 8433694.4072 | 0 | 389877.8563 | 0 | 10257306.814 | 26687408.2671 | 18214704.5137 | 81460206.2973 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105377958.7062 | 139877215.3073 | 7498942.0933 | 24.6734 | 4270.9141 | 5669.1512 | 87.0684 | 115.5733
1 | 5900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.2493 | 57.389 | 6.1712 | 4 | 4269.5307 | 5667.1326 | 87.0402 | 115.5322 | 153.0589 | 0 | 235.4767 | 8249997.7676 | 717350.6268 | 8513446.1166 | 8436122.2304 | 0 | 388304.9292 | 0 | 10259036.4515 | 26691908.4291 | 18217775.9667 | 81473942.5179 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 105391694.9267 | 139890951.5279 | 10000000 | 24.6846 | 4269.5307 | 5667.1326 | 87.0402 | 115.5322
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0921 | [19 empty] | 100 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0929 | [19 empty] | 133.3521 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4152 | [19 empty] | 177.8279 | 0
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5297 | 0.30709 | 0.0092816 | 4 | 698782.2718 | 1648834.5948 | 14245.6218 | 33613.7234 | 112.4529 | 0 | 59.296 | 168844.2933 | 11316.6597 | 133441.5718 | 80965.6688 | 0 | 81188.4234 | 0 | 185545.0806 | 482750.2393 | 329486.9578 | 1473538.8948 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 25943161.1748 | 61215035.5956 | 237.1374 | 0.037126 | 698782.2718 | 1648834.5948 | 14245.6218 | 33613.7234
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.45497 | 0.020571 | 4 | 320946.4618 | 749616.1716 | 6542.9277 | 15281.9396 | 121.0355 | 0 | 318.034 | 233006.7544 | 16462.2782 | 181654.1896 | 103078.0717 | 0 | 91691.7255 | 0 | 244098.2776 | 635093.6468 | 433464.4638 | 1938549.4076 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 26408171.6876 | 61680046.1085 | 316.2278 | 0.082282 | 320946.4618 | 749616.1716 | 6542.9277 | 15281.9396
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.67001 | 0.038089 | 4 | 177438.3895 | 408946.774 | 3617.3216 | 8336.9331 | 128.7602 | 0 | 400.269 | 317799.9811 | 23579.7284 | 246264.0303 | 134696.0208 | 0 | 105594.1376 | 0 | 322894.2203 | 840104.5265 | 573388.6018 | 2564321.2468 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 27033943.5269 | 62305817.9477 | 421.6965 | 0.15236 | 177438.3895 | 408946.774 | 3617.3216 | 8336.9331
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4212 | 0.96316 | 0.063496 | 4 | 109541.219 | 248416.2008 | 2233.1459 | 5064.3003 | 135.1579 | 0 | 521.272 | 422711.5761 | 32715.9969 | 327779.4426 | 177239.4277 | 0 | 121795.3108 | 0 | 422074.2841 | 1098150.7078 | 749510.4228 | 3351977.1688 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 27821599.4488 | 63093473.8696 | 562.3413 | 0.25398 | 109541.219 | 248416.2008 | 2233.1459 | 5064.3003
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4916 | 1.3554 | 0.098873 | 4 | 72811.8098 | 161996.3372 | 1484.3672 | 3302.5144 | 140.346 | 0 | 81.6621 | 550195.712 | 44113.2203 | 429271.6336 | 232766.4222 | 0 | 140682.1719 | 0 | 544841.3724 | 1417565.4886 | 967517.5741 | 4326953.5951 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 28796575.8751 | 64068450.296 | 749.8942 | 0.39549 | 72811.8098 | 161996.3372 | 1484.3672 | 3302.5144
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.907 | 1.884 | 0.14798 | 4 | 50730.3281 | 110318.3412 | 1034.2064 | 2248.9886 | 144.5094 | 0 | 64.8994 | 707074.238 | 58457.1327 | 557037.2668 | 308863.2521 | 0 | 163426.3845 | 0 | 699994.7269 | 1821242.6908 | 1243035.5593 | 5559131.2511 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 30028753.5312 | 65300627.952 | 1000 | 0.59193 | 50730.3281 | 110318.3412 | 1034.2064 | 2248.9886
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8025 | 2.596 | 0.2148 | 4 | 36761.1269 | 77812.4543 | 749.4253 | 1586.3121 | 147.7379 | 0 | 87.5455 | 899498.2637 | 76270.6718 | 718184.0425 | 411764.8788 | 0 | 191818.2422 | 0 | 896039.0786 | 2331309.8797 | 1591166.8965 | 7116051.9538 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 31585674.2339 | 66857548.6547 | 1333.5214 | 0.85921 | 36761.1269 | 77812.4543 | 749.4253 | 1586.3121
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3453 | 3.5666 | 0.30765 | 4 | 27286.3528 | 55948.5275 | 556.2692 | 1140.5864 | 150.5099 | 0 | 80.8221 | 1139941.2059 | 98887.3903 | 924058.4182 | 551379.2646 | 0 | 226776.7414 | 0 | 1147006.778 | 2984276.3528 | 2036829.9315 | 9109156.0828 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 33578778.3628 | 68850652.7836 | 1778.2794 | 1.2306 | 27286.3528 | 55948.5275 | 556.2692 | 1140.5864
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7022 | 4.8461 | 0.43101 | 4 | 20913.0748 | 41371.8496 | 426.3413 | 843.4211 | 152.5398 | 0 | 80.4578 | 1429559.5644 | 126285.8068 | 1179001.7385 | 736897.4611 | 0 | 268823.0391 | 0 | 1458821.3679 | 3795553.9539 | 2590543.5644 | 11585486.4962 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 36055108.7762 | 71326983.197 | 2371.3737 | 1.724 | 20913.0748 | 41371.8496 | 426.3413 | 843.4211
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.158 | 6.5449 | 0.59478 | 4 | 16451.0926 | 31276.6043 | 335.3778 | 637.6159 | 154.102 | 0 | 79.8888 | 1780360.6254 | 159343.8122 | 1497668.9548 | 979020.1975 | 0 | 319972.3027 | 0 | 1847182.6981 | 4805990.4713 | 3280187.2499 | 14669726.312 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 39139348.592 | 74411223.0129 | 3162.2777 | 2.3791 | 16451.0926 | 31276.6043 | 335.3778 | 637.6159
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0311 | 8.822 | 0.81217 | 4 | 13243.3821 | 24100.6245 | 269.9843 | 491.3238 | 155.2929 | 0 | 83.1946 | 2206644.91 | 198682.1191 | 1900575.0263 | 1302376.988 | 0 | 382219.6123 | 0 | 2336294.4758 | 6078558.9861 | 4148741.4099 | 18554093.5275 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 43023715.8076 | 78295590.2284 | 4216.965 | 3.2487 | 13243.3821 | 24100.6245 | 269.9843 | 491.3238
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.7802 | 11.9204 | 1.0992 | 4 | 10908.3084 | 18930.7016 | 222.3806 | 385.928 | 156.2023 | 0 | 77.2177 | 2725807.0006 | 244273.2019 | 2418564.1902 | 1736037.6844 | 0 | 459679.1471 | 0 | 2957900.8775 | 7695851.3343 | 5252576.6696 | 23490690.1055 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 47960312.3856 | 83232186.8064 | 5623.4133 | 4.3967 | 10908.3084 | 18930.7016 | 222.3806 | 385.928
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8728 | 15.8853 | 1.4718 | 4 | 9168.8811 | 15159.9717 | 186.92 | 309.0565 | 156.8891 | 0 | 77.9702 | 3343964.4494 | 299701.4293 | 3042589.9043 | 2290736.8935 | 0 | 551170.3929 | 0 | 3715983.597 | 9668227.0665 | 6598763.6351 | 29511137.3679 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 53980759.648 | 89252634.0688 | 7498.9421 | 5.8874 | 9168.8811 | 15159.9717 | 186.92 | 309.0565
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8011 | 20.9724 | 1.9471 | 4 | 7871.9504 | 12400.7463 | 160.4804 | 252.806 | 157.3825 | 0 | 97.8117 | 4072280.5092 | 364241.7555 | 3799720.4879 | 2998583.1009 | 0 | 659559.7457 | 0 | 4638810.3837 | 12069233.0675 | 8237499.5665 | 36839928.6168 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 61309550.8968 | 96581425.3176 | 10000 | 7.7884 | 7871.9504 | 12400.7463 | 160.4804 | 252.806
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.928 | 27.2721 | 2.533 | 4 | 6907.6585 | 10388.8679 | 140.822 | 211.7911 | 157.6442 | 0 | 105.6178 | 4906466.5692 | 437762.8907 | 4688219.0381 | 3878983.9603 | 0 | 785230.4056 | 0 | 5731698.5169 | 14912703.808 | 10178226.7744 | 45519291.9632 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 69988914.2432 | 105260788.664 | 13335.2143 | 10.1321 | 6907.6585 | 10388.8679 | 140.822 | 211.7911
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.1795 | 34.6358 | 3.2135 | 4 | 6206.4109 | 8950.4325 | 126.5261 | 182.4667 | 157.5822 | 0 | 120.8893 | 5814382.0778 | 517492.5965 | 5676149.6113 | 4923764.7929 | 0 | 925348.0626 | 0 | 6964283.485 | 18119637.0571 | 12367024.6128 | 55308082.2959 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 79777704.5759 | 115049578.9968 | 17782.7941 | 12.8541 | 6206.4109 | 8950.4325 | 126.5261 | 182.4667
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.287 | 40.6015 | 3.826 | 4 | 5707.557 | 8012.2798 | 116.3563 | 163.3412 | 157.2806 | 0 | 138.6005 | 6509844.9603 | 578383.5432 | 6445658.6788 | 5790226.2005 | 0 | 977682.1952 | 0 | 7917700.2755 | 20600231.9731 | 14060081.6141 | 62879809.4408 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 87349431.7208 | 122621306.1417 | 23713.7371 | 15.3042 | 5707.557 | 8012.2798 | 116.3563 | 163.3412
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.6197 | 44.3133 | 4.3009 | 4 | 5333.0113 | 7383.2775 | 108.7206 | 150.5181 | 156.9864 | 0 | 139.0245 | 6927640.7038 | 614865.5272 | 6912934.2862 | 6341410.748 | 0 | 924698.4693 | 0 | 8471404.3965 | 22040856.5157 | 15043337.4662 | 67277148.1129 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 91746770.393 | 127018644.8138 | 31622.7766 | 17.2036 | 5333.0113 | 7383.2775 | 108.7206 | 150.5181
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8297 | 47.5615 | 4.7268 | 4 | 5050.3977 | 6915.9048 | 102.9592 | 140.9901 | 156.6672 | 0 | 165.2424 | 7281213.2652 | 645029.5353 | 7316040.2585 | 6824614.5392 | 0 | 863167.998 | 0 | 8942725.5825 | 23267137.5604 | 15880299.4769 | 71020228.2159 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 95489850.4959 | 130761724.9168 | 42169.6503 | 18.9074 | 5050.3977 | 6915.9048 | 102.9592 | 140.9901
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5003 | 50.209 | 5.0898 | 4 | 4836.4998 | 6568.9674 | 98.5986 | 133.9173 | 156.3644 | 0 | 193.828 | 7563413.8474 | 668925.1968 | 7640662.9388 | 7223716.2198 | 0 | 794854.6851 | 0 | 9317713.4263 | 24242779.0094 | 16546194.8132 | 73998260.1368 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 98467882.4168 | 133739756.8377 | 56234.1325 | 20.3593 | 4836.4998 | 6568.9674 | 98.5986 | 133.9173
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.8 | 53.7216 | 5.4917 | 4 | 4672.1899 | 6277.8839 | 95.2489 | 127.9832 | 155.9735 | 0 | 203.2807 | 7931899.0797 | 700184.1415 | 8066081.0446 | 7756406.0638 | 0 | 781719.3595 | 0 | 9842152.9787 | 25607263.1475 | 17477483.2748 | 78163189.0901 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 102632811.3701 | 137904685.791 | 74989.4209 | 21.9667 | 4672.1899 | 6277.8839 | 95.2489 | 127.9832
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3936 | 55.5071 | 5.753 | 4 | 4545.8381 | 6078.5851 | 92.6731 | 123.9202 | 155.759 | 0 | 190.8177 | 8123134.9571 | 717515.418 | 8279173.7726 | 8030089.0854 | 0 | 724653.0982 | 0 | 10091080.8692 | 26254922.4564 | 17919524.0612 | 80140093.7182 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 104609715.9982 | 139881590.419 | 100000 | 23.0122 | 4545.8381 | 6078.5851 | 92.6731 | 123.9202
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6124 | 56.8305 | 5.9565 | 4 | 4450.5347 | 5930.9218 | 90.7302 | 120.9099 | 155.592 | 0 | 195.6497 | 8264075.1668 | 730336.6603 | 8436188.0471 | 8234411.8318 | 0 | 671007.9437 | 0 | 10271047.6634 | 26723159.1386 | 18239105.2181 | 81569331.6699 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 106038953.95 | 141310828.3708 | 133352.1432 | 23.8261 | 4450.5347 | 5930.9218 | 90.7302 | 120.9099
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.8307 | 57.8266 | 6.1145 | 4 | 4378.7165 | 5820.8589 | 89.2661 | 118.6661 | 155.4619 | 0 | 207.2289 | 8369721.0438 | 739975.2236 | 8553851.5176 | 8389057.1411 | 0 | 624220.5577 | 0 | 10403961.9387 | 27068974.8184 | 18475131.5254 | 82624893.7662 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 107094516.0462 | 142366390.467 | 177827.941 | 24.458 | 4378.7165 | 5820.8589 | 89.2661 | 118.6661
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4176 | 58.6166 | 6.2393 | 4 | 4324.6189 | 5737.9079 | 88.1632 | 116.975 | 155.3542 | 0 | 198.9213 | 8453296.2904 | 747623.6055 | 8646864.6454 | 8512403.4767 | 0 | 586647.4445 | 0 | 10509265.8304 | 27342953.9438 | 18662127.9082 | 83461183.145 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 107930805.425 | 143202679.8458 | 237137.3706 | 24.9573 | 4324.6189 | 5737.9079 | 88.1632 | 116.975
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3271 | 59.1896 | 6.3334 | 4 | 4283.8214 | 5676.1186 | 87.3315 | 115.7154 | 155.2705 | 0 | 228.0847 | 8513870.2476 | 753191.4635 | 8714152.5623 | 8602540.3404 | 0 | 554779.2626 | 0 | 10584028.2118 | 27537470.3244 | 18794889.3348 | 84054921.7475 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 108524544.0275 | 143796418.4484 | 316227.766 | 25.3336 | 4283.8214 | 5676.1186 | 87.3315 | 115.7154
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.7692 | 59.6192 | 6.405 | 4 | 4253.0851 | 5629.8157 | 86.7049 | 114.7714 | 155.2066 | 0 | 220.7369 | 8559210.339 | 757366.0789 | 8764497.5216 | 8670320.4712 | 0 | 529073.2193 | 0 | 10639382.3757 | 27681490.5042 | 18893186.0669 | 84494526.5769 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 108964148.8569 | 144236023.2777 | 421696.5034 | 25.62 | 4253.0851 | 5629.8157 | 86.7049 | 114.7714
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8487 | 59.9388 | 6.4591 | 4 | 4229.948 | 5595.1417 | 86.2332 | 114.0645 | 155.1583 | 0 | 230.9486 | 8592917.5791 | 760473.6435 | 8801913.1127 | 8720886.3151 | 0 | 508578.3119 | 0 | 10680059.8953 | 27787325.0661 | 18965420.33 | 84817574.2537 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109287196.5337 | 144559070.9546 | 562341.3252 | 25.8365 | 4229.948 | 5595.1417 | 86.2332 | 114.0645
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.6575 | 60.1773 | 6.5 | 4 | 4212.544 | 5569.1591 | 85.8784 | 113.5348 | 155.1219 | 0 | 243.3137 | 8618045.8083 | 762792.5611 | 8829798.6236 | 8758681.0995 | 0 | 492480.5839 | 0 | 10710101.4838 | 27865487.117 | 19018767.5359 | 85056154.8131 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109525777.0931 | 144797651.514 | 749894.2093 | 25.9999 | 4212.544 | 5569.1591 | 85.8784 | 113.5348
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2714 | 60.3577 | 6.5309 | 4 | 4199.4607 | 5549.6459 | 85.6117 | 113.137 | 155.0942 | 0 | 209.7493 | 8637042.6481 | 764546.938 | 8850875.8917 | 8787309.8723 | 0 | 480075.9079 | 0 | 10732741.9906 | 27924393.0715 | 19058972.0602 | 85235958.3802 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109705580.6602 | 144977455.0811 | 1000000 | 26.1237 | 4199.4607 | 5549.6459 | 85.6117 | 113.137
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.7124 | 60.487 | 6.5538 | 4 | 4189.6306 | 5535.1098 | 85.4113 | 112.8407 | 155.0742 | 0 | 196.8693 | 8650649.4359 | 765804.3011 | 8865970.0309 | 8807846.7285 | 0 | 470264.1078 | 0 | 10748608.4957 | 27965674.463 | 19087147.4581 | 85361965.021 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109831587.301 | 145103461.7219 | 1333521.4322 | 26.2151 | 4189.6306 | 5535.1098 | 85.4113 | 112.8407
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0413 | 60.5832 | 6.5709 | 4 | 4182.2478 | 5524.2181 | 85.2608 | 112.6187 | 155.0592 | 0 | 196.9448 | 8660777.1202 | 766740.5598 | 8877203.4408 | 8823149.0163 | 0 | 462734.4183 | 0 | 10760335.7766 | 27996186.4424 | 19107972.5111 | 85455099.2856 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109924721.5656 | 145196595.9864 | 1778279.41 | 26.2836 | 4182.2478 | 5524.2181 | 85.2608 | 112.6187
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.2971 | 60.658 | 6.584 | 4 | 4176.705 | 5516.0065 | 85.1478 | 112.4513 | 155.0475 | 0 | 211.0804 | 8668640.5838 | 767467.6967 | 8885924.9019 | 8835039.3932 | 0 | 457123.3769 | 0 | 10769536.4215 | 28020124.633 | 19124310.818 | 85528167.8248 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 109997790.1049 | 145269664.5257 | 2371373.7057 | 26.336 | 4176.705 | 5516.0065 | 85.1478 | 112.4513
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4823 | 60.712 | 6.5937 | 4 | 4172.5447 | 5509.8804 | 85.063 | 112.3264 | 155.0391 | 0 | 205.1116 | 8674327.2127 | 767993.6871 | 8892231.4213 | 8843643.7972 | 0 | 452778.4778 | 0 | 10776080.0925 | 28037149.9227 | 19135930.9281 | 85580135.5394 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 110049757.8194 | 145321632.2402 | 3162277.6602 | 26.3747 | 4172.5447 | 5509.8804 | 85.063 | 112.3264
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6332 | 60.756 | 6.6012 | 4 | 4169.4227 | 5505.2284 | 84.9993 | 112.2315 | 155.0322 | 0 | 211.5798 | 8678958.8425 | 768422.1295 | 8897367.9955 | 8850654.5137 | 0 | 449653.0914 | 0 | 10781572.0633 | 28051438.9043 | 19145683.4516 | 85623750.9919 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 110093373.2719 | 145365247.6927 | 4216965.0343 | 26.4049 | 4169.4227 | 5505.2284 | 84.9993 | 112.2315
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.7381 | 60.7866 | 6.6067 | 4 | 4167.0804 | 5501.7801 | 84.9516 | 112.1612 | 155.0274 | 0 | 210.9061 | 8682172.0274 | 768719.4283 | 8900931.1407 | 8855520.3406 | 0 | 447181.4515 | 0 | 10785264.5115 | 28061045.8971 | 19152240.4216 | 85653075.2187 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 110122697.4987 | 145394571.9196 | 5623413.2519 | 26.4268 | 4167.0804 | 5501.7801 | 84.9516 | 112.1612
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8159 | 60.8093 | 6.6108 | 4 | 4165.3232 | 5499.1981 | 84.9157 | 112.1086 | 155.0238 | 0 | 223.0195 | 8684555.2786 | 768939.9623 | 8903573.865 | 8859130.3366 | 0 | 445307.9057 | 0 | 10787987.8658 | 28068131.5063 | 19157076.4955 | 85674703.2158 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 110144325.4958 | 145416199.9167 | 7498942.0933 | 26.4432 | 4165.3232 | 5499.1981 | 84.9157 | 112.1086
1 | 6000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8696 | 60.8249 | 6.6137 | 4 | 4164.005 | 5497.2839 | 84.8889 | 112.0696 | 155.0214 | 0 | 218.7713 | 8686199.7476 | 769092.1602 | 8905397.2121 | 8861621.9852 | 0 | 443835.867 | 0 | 10789797.3191 | 28072839.3325 | 19160289.6836 | 85689073.3072 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 110158695.5872 | 145430570.0081 | 10000000 | 26.455 | 4164.005 | 5497.2839 | 84.8889 | 112.0696
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7295 | [19 empty] | 100 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.538 | [19 empty] | 133.3521 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7673 | [19 empty] | 177.8279 | 0
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.31834 | 0.010614 | 4 | 624997.2335 | 1474152.933 | 12741.414 | 30052.6015 | 113.9078 | 0 | 58.4421 | 174617.403 | 11804.9804 | 137196.1538 | 82363.2365 | 0 | 80973.3891 | 0 | 189912.5135 | 494113.4037 | 337242.5511 | 1508223.6312 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 26535575.8733 | 62588272.241 | 237.1374 | 0.042457 | 624997.2335 | 1474152.933 | 12741.414 | 30052.6015
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.48332 | 0.023206 | 4 | 291435.4014 | 679834.0064 | 5941.3049 | 13859.3358 | 123.1549 | 0 | 305.0244 | 245760.7095 | 17585.585 | 190379.0976 | 106596.0114 | 0 | 93430.567 | 0 | 254963.2685 | 663362.1244 | 452758.2806 | 2024835.6439 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 27052187.8859 | 63104884.2536 | 316.2278 | 0.092824 | 291435.4014 | 679834.0064 | 5941.3049 | 13859.3358
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6627 | 0.70489 | 0.04204 | 4 | 164661.5312 | 379057.7728 | 3356.848 | 7727.6054 | 130.7591 | 0 | 410.2304 | 332646.9786 | 25000.8287 | 256111.7003 | 139100.8321 | 0 | 106609.4678 | 0 | 335193.2249 | 872104.0137 | 595228.9093 | 2661995.9554 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 27689348.1975 | 63742044.5652 | 421.6965 | 0.16816 | 164661.5312 | 379057.7728 | 3356.848 | 7727.6054
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4795 | 1.0062 | 0.069129 | 4 | 103032.5662 | 233413.8079 | 2100.4582 | 4758.4562 | 137.1169 | 0 | 572.094 | 440082.6243 | 34515.3499 | 338995.815 | 182418.5281 | 0 | 122060.9513 | 0 | 436048.5747 | 1134508.9456 | 774325.6672 | 3462956.4562 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 28490308.6982 | 64543005.066 | 562.3413 | 0.27652 | 103032.5662 | 233413.8079 | 2100.4582 | 4758.4562
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5842 | 1.4226 | 0.10761 | 4 | 68576.8724 | 152333.4577 | 1398.0323 | 3105.5236 | 142.4432 | 0 | 85.4849 | 575023.7654 | 46807.7686 | 445570.7861 | 241000.4974 | 0 | 141686.9512 | 0 | 565535.0098 | 1471406.0882 | 1004264.8896 | 4491295.7562 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 29518647.9983 | 65571344.366 | 749.8942 | 0.43045 | 68576.8724 | 152333.4577 | 1398.0323 | 3105.5236
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0385 | 1.9812 | 0.16089 | 4 | 47877.9115 | 103900.0227 | 976.056 | 2118.1425 | 146.675 | 0 | 80.3562 | 740305.0048 | 62247.4554 | 579007.1157 | 320968.1101 | 0 | 164995.4781 | 0 | 728334.034 | 1894975.7547 | 1293359.8904 | 5784192.8434 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 30811545.0854 | 66864241.4531 | 1000 | 0.64354 | 47877.9115 | 103900.0227 | 976.056 | 2118.1425
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9559 | 2.7222 | 0.23268 | 4 | 34834.8828 | 73571.3459 | 710.1562 | 1499.8514 | 149.8923 | 0 | 69.6681 | 940211.126 | 81203.409 | 744769.2568 | 428121.0156 | 0 | 192995.978 | 0 | 931047.3063 | 2422394.1069 | 1653333.7532 | 7394075.9518 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 32421428.1939 | 68474124.5616 | 1333.5214 | 0.93072 | 34834.8828 | 73571.3459 | 710.1562 | 1499.8514
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5279 | 3.7307 | 0.33242 | 4 | 25930.0432 | 53043.9692 | 528.619 | 1081.3731 | 152.7016 | 0 | 101.5153 | 1190169.5135 | 105377.7329 | 956282.387 | 572209.1127 | 0 | 227427.6326 | 0 | 1190071.8876 | 3096322.9343 | 2113304.0258 | 9451165.2263 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 34478517.4684 | 70531213.8361 | 1778.2794 | 1.3297 | 25930.0432 | 53043.9692 | 528.619 | 1081.3731
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9385 | 5.063 | 0.46428 | 4 | 19937.8988 | 39351.0778 | 406.461 | 802.2249 | 154.7574 | 0 | 86.1005 | 1490895.7954 | 134480.9852 | 1218976.5732 | 760634.9077 | 0 | 269352.0518 | 0 | 1510992.7222 | 3931293.1159 | 2683188.3316 | 11999814.483 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 37027166.7251 | 73079863.0928 | 2371.3737 | 1.8571 | 19937.8988 | 39351.0778 | 406.461 | 802.2249
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.4675 | 6.9429 | 0.64073 | 4 | 15735.9536 | 29802.9511 | 320.7987 | 607.5735 | 156.3411 | 0 | 84.4039 | 1861290.45 | 167438.8366 | 1569422.2386 | 1019860.6398 | 0 | 322738.5256 | 0 | 1926892.7693 | 5013379.7257 | 3421734.6775 | 15302757.8631 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 40330110.1051 | 76382806.4728 | 3162.2777 | 2.5629 | 15735.9536 | 29802.9511 | 320.7987 | 607.5735
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.4527 | 9.3864 | 0.87244 | 4 | 12717.923 | 23048.9284 | 259.2721 | 469.8836 | 157.5511 | 0 | 88.0816 | 2305397.8265 | 207485.2634 | 1997259.6926 | 1352447.1037 | 0 | 386529.0124 | 0 | 2437156.3705 | 6340980.9464 | 4327849.7901 | 19355106.0055 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 44382458.2476 | 80435154.6153 | 4216.965 | 3.4898 | 12717.923 | 23048.9284 | 259.2721 | 469.8836
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3332 | 12.6164 | 1.1768 | 4 | 10501.8063 | 18161.1161 | 214.0935 | 370.2389 | 158.4728 | 0 | 91.686 | 2841380.8549 | 255206.7403 | 2530363.8608 | 1788639.877 | 0 | 464000.9818 | 0 | 3073041.0028 | 7995422.3218 | 5457040.0241 | 24405095.6635 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 49432447.9055 | 85485144.2733 | 5623.4133 | 4.707 | 10501.8063 | 18161.1161 | 214.0935 | 370.2389
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.5768 | 16.8163 | 1.5724 | 4 | 8849.5986 | 14581.6109 | 180.411 | 297.2659 | 159.1676 | 0 | 101.0045 | 3482269.0865 | 312066.7287 | 3184326.8354 | 2355631.8813 | 0 | 556422.2715 | 0 | 3857379.5533 | 10036110.3404 | 6849851.5288 | 30634058.2258 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 55661410.4679 | 91714106.8356 | 7498.9421 | 6.2897 | 8849.5986 | 14581.6109 | 180.411 | 297.2659
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6831 | 22.181 | 2.0773 | 4 | 7610.3893 | 11949.343 | 155.1481 | 243.6035 | 159.6631 | 0 | 112.3167 | 4237340.4301 | 378811.2549 | 3973910.6698 | 3080478.4299 | 0 | 665533.5126 | 0 | 4811068.9759 | 12517414.5894 | 8543392.6644 | 38207950.5271 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 63235302.7692 | 99287999.1369 | 10000 | 8.3091 | 7610.3893 | 11949.343 | 155.1481 | 243.6035
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9849 | 28.7983 | 2.6981 | 4 | 6687.6805 | 10028.1934 | 136.3374 | 204.4383 | 159.9146 | 0 | 91.6739 | 5099874.3206 | 454771.2442 | 4896962.8695 | 3980043.9314 | 0 | 791466.5349 | 0 | 5937016.3712 | 15446898.7484 | 10542825.7978 | 47149859.818 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 72177212.0601 | 108229908.4278 | 13335.2143 | 10.7926 | 6687.6805 | 10028.1934 | 136.3374 | 204.4383
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4099 | 36.5139 | 3.4174 | 4 | 6016.358 | 8653.8307 | 122.6516 | 176.42 | 159.8255 | 0 | 122.2433 | 6036754.891 | 536978.6827 | 5921067.4756 | 5045403.2194 | 0 | 931874.8248 | 0 | 7204110.8464 | 18743618.6561 | 12792904.8756 | 57212713.4715 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 82240065.7136 | 118292762.0813 | 17782.7941 | 13.6694 | 6016.358 | 8653.8307 | 122.6516 | 176.42
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5741 | 43.1046 | 4.0827 | 4 | 5541.0065 | 7748.6675 | 112.9609 | 157.9671 | 159.4671 | 0 | 111.6261 | 6792834.3642 | 603118.8623 | 6761645.9767 | 5978080.5496 | 0 | 999586.9813 | 0 | 8242754.0263 | 21445955.1551 | 14637305.0637 | 65461280.9793 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 90488633.2214 | 126541329.5891 | 23713.7371 | 16.3307 | 5541.0065 | 7748.6675 | 112.9609 | 157.9671
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.3823 | 47.12 | 4.5886 | 4 | 5185.8514 | 7150.1218 | 105.7206 | 145.7649 | 159.1287 | 0 | 169.4295 | 7237260.4854 | 641918.8729 | 7261023.4284 | 6560403.655 | 0 | 950114.0027 | 0 | 8833780.9733 | 22983686.0349 | 15686837.9864 | 70155025.439 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 95182377.6811 | 131235074.0488 | 31622.7766 | 18.3542 | 5185.8514 | 7150.1218 | 105.7206 | 145.7649
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6607 | 50.4744 | 5.0347 | 4 | 4916.5941 | 6706.8111 | 100.2314 | 136.7274 | 158.7795 | 0 | 168.1041 | 7600318.9229 | 673575.0772 | 7671676.0435 | 7056382.7306 | 0 | 885858.2433 | 0 | 9316246.2968 | 24238961.8394 | 16543589.5163 | 73986608.67 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 99013960.9121 | 135066657.2798 | 42169.6503 | 20.1387 | 4916.5941 | 6706.8111 | 100.2314 | 136.7274
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2922 | 53.8727 | 5.4616 | 4 | 4712.5339 | 6362.8266 | 96.0714 | 129.7148 | 158.3791 | 0 | 193.1361 | 7961216.4705 | 705008.5598 | 8082177.8763 | 7567779.7578 | 0 | 842819.9902 | 0 | 9812011.0353 | 25528839.9937 | 17423957.8609 | 77923811.5445 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 102951163.7865 | 139003860.1543 | 56234.1325 | 21.8462 | 4712.5339 | 6362.8266 | 96.0714 | 129.7148
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9935 | 56.2206 | 5.7919 | 4 | 4555.6917 | 6111.8505 | 92.8739 | 124.5983 | 158.1152 | 0 | 205.1782 | 8206798.0765 | 726379.3197 | 8362771.132 | 7923112.2856 | 0 | 777445.8026 | 0 | 10138637.5804 | 26378655.2636 | 18003974.2446 | 80517773.705 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 105545125.9471 | 141597822.3148 | 74989.4209 | 23.1677 | 4555.6917 | 6111.8505 | 92.8739 | 124.5983
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.2996 | 58.0518 | 6.0586 | 4 | 4437.1146 | 5924.776 | 90.4566 | 120.7846 | 157.8963 | 0 | 210.8321 | 8396312.547 | 742860.8524 | 8579978.7595 | 8203261.2305 | 0 | 715315.3735 | 0 | 10388714.2175 | 27029303.3757 | 18448054.9505 | 82503801.3066 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 107531153.5486 | 143583849.9163 | 100000 | 24.2345 | 4437.1146 | 5924.776 | 90.4566 | 120.7846
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4017 | 59.45 | 6.2689 | 4 | 4347.5766 | 5785.326 | 88.6312 | 117.9417 | 157.7213 | 0 | 238.2685 | 8539875.6617 | 755340.3151 | 8744903.16 | 8419018.1614 | 0 | 658935.6863 | 0 | 10576048.4639 | 27516708.6573 | 18780719.0704 | 83991549.1761 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 109018901.4182 | 145071597.7859 | 133352.1432 | 25.0758 | 4347.5766 | 5785.326 | 88.6312 | 117.9417
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5345 | 60.5076 | 6.4325 | 4 | 4280.03 | 5681.2336 | 87.2542 | 115.8196 | 157.5844 | 0 | 229.2212 | 8647839.0232 | 764721.9549 | 8869144.694 | 8583430.5256 | 0 | 609843.8573 | 0 | 10715242.2214 | 27878862.2618 | 19027896.347 | 85096980.8853 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 110124333.1273 | 146177029.495 | 177827.941 | 25.7298 | 4280.03 | 5681.2336 | 87.2542 | 115.8196
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.8922 | 61.2977 | 6.5578 | 4 | 4229.1125 | 5603.5297 | 86.2162 | 114.2355 | 157.4796 | 0 | 259.2216 | 8728144.5572 | 771698.432 | 8961675.9545 | 8706960.9766 | 0 | 568222.218 | 0 | 10817313.8339 | 28144431.6597 | 19209152.918 | 85907600.5499 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 110934952.7919 | 146987649.1596 | 237137.3706 | 26.2313 | 4229.1125 | 5603.5297 | 86.2162 | 114.2355
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6561 | 61.8855 | 6.6532 | 4 | 4190.7564 | 5545.4734 | 85.4342 | 113.052 | 157.4002 | 0 | 249.2043 | 8787693.1712 | 776870.6882 | 9030354.4951 | 8799259.1195 | 0 | 533808.1338 | 0 | 10891914.3871 | 28338526.9963 | 19341626.9735 | 86500053.9646 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 111527406.2067 | 147580102.5744 | 316227.766 | 26.6127 | 4190.7564 | 5545.4734 | 85.4342 | 113.052
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.001 | 62.3317 | 6.7261 | 4 | 4161.8801 | 5501.908 | 84.8456 | 112.1638 | 157.339 | 0 | 235.2333 | 8832791.2255 | 780787.2492 | 9082403.0943 | 8869566.3425 | 0 | 506316.3718 | 0 | 10948027.0705 | 28484520.6883 | 19441270.6681 | 86945682.7101 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 111973034.9522 | 148025731.3199 | 421696.5034 | 26.9044 | 4161.8801 | 5501.908 | 84.8456 | 112.1638
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.9802 | 62.6552 | 6.7805 | 4 | 4140.1483 | 5469.4267 | 84.4025 | 111.5017 | 157.2939 | 0 | 229.6987 | 8865435.0047 | 783621.9171 | 9120097.3077 | 8920711.456 | 0 | 484053.3858 | 0 | 10987828.4378 | 28588075.6817 | 19511949.0789 | 87261772.2697 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112289124.5118 | 148341820.8795 | 562341.3252 | 27.122 | 4140.1483 | 5469.4267 | 84.4025 | 111.5017
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.7159 | 62.8977 | 6.8216 | 4 | 4123.8052 | 5445.0756 | 84.0693 | 111.0052 | 157.2599 | 0 | 244.7978 | 8889868.0424 | 785743.4317 | 9148321.0624 | 8959115.1256 | 0 | 466624.7084 | 0 | 11017372.2245 | 28664942.5543 | 19564412.299 | 87496399.4484 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112523751.6904 | 148576448.0581 | 749894.2093 | 27.2864 | 4123.8052 | 5445.0756 | 84.0693 | 111.0052
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2519 | 63.074 | 6.8522 | 4 | 4111.521 | 5426.8989 | 83.8189 | 110.6347 | 157.235 | 0 | 207.4101 | 8907619.9484 | 787284.7385 | 9168832.8013 | 8987085.764 | 0 | 452889.5146 | 0 | 11038447.9791 | 28719777.3445 | 19601838.17 | 87663776.2603 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112691128.5024 | 148743824.8701 | 1000000 | 27.4086 | 4111.521 | 5426.8989 | 83.8189 | 110.6347
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.6339 | 63.1995 | 6.8746 | 4 | 4102.292 | 5413.3699 | 83.6308 | 110.3589 | 157.2171 | 0 | 239.3439 | 8920243.2904 | 788380.714 | 9183421.5545 | 9007012.2679 | 0 | 442046.5944 | 0 | 11053030.7243 | 28757718.6562 | 19627733.8949 | 87779587.6965 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112806939.9386 | 148859636.3063 | 1333521.4322 | 27.4985 | 4102.292 | 5413.3699 | 83.6308 | 110.3589
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.9286 | 63.2962 | 6.8917 | 4 | 4095.3609 | 5403.1823 | 83.4895 | 110.1512 | 157.2034 | 0 | 259.9363 | 8929967.4298 | 789224.9517 | 9194661.3504 | 9022380.772 | 0 | 433868.794 | 0 | 11064340.2862 | 28787143.8164 | 19647817.1714 | 87869404.572 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112896756.814 | 148949453.1817 | 1778279.41 | 27.567 | 4095.3609 | 5403.1823 | 83.4895 | 110.1512
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.1481 | 63.3682 | 6.9046 | 4 | 4090.1572 | 5395.5496 | 83.3834 | 109.9956 | 157.1931 | 0 | 236.1701 | 8937202.0316 | 789853.0366 | 9203024.5018 | 9033825.9301 | 0 | 427623.2972 | 0 | 11072696.231 | 28808884.2708 | 19662655.4782 | 87935764.7774 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 112963117.0195 | 149015813.3872 | 2371373.7057 | 27.6183 | 4090.1572 | 5395.5496 | 83.3834 | 109.9956
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.3112 | 63.4216 | 6.9142 | 4 | 4086.2515 | 5389.8325 | 83.3038 | 109.879 | 157.1854 | 0 | 245.0278 | 8942575.7275 | 790319.5559 | 9209236.9691 | 9042333.4276 | 0 | 422866.7453 | 0 | 11078859.6459 | 28824920.2121 | 19673600.3377 | 87984712.6212 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 113012064.8632 | 149064761.2309 | 3162277.6602 | 27.6567 | 4086.2515 | 5389.8325 | 83.3038 | 109.879
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4427 | 63.4647 | 6.9216 | 4 | 4083.3206 | 5385.4993 | 83.244 | 109.7907 | 157.1793 | 0 | 257.2579 | 8946904.7923 | 790695.3803 | 9214242.0671 | 9049189.7568 | 0 | 419395.3632 | 0 | 11083966.6702 | 28838207.6417 | 19682669.2814 | 88025270.9529 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 113052623.195 | 149105319.5627 | 4216965.0343 | 27.6864 | 4083.3206 | 5385.4993 | 83.244 | 109.7907
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5398 | 63.4965 | 6.9272 | 4 | 4081.1216 | 5382.2574 | 83.1992 | 109.7246 | 157.1747 | 0 | 259.5398 | 8950098.3766 | 790972.626 | 9217934.5472 | 9054250.0769 | 0 | 416753.4402 | 0 | 11087703.5361 | 28847930.2002 | 19689305.1273 | 88054947.9306 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 113082300.1727 | 149134996.5404 | 5623413.2519 | 27.7086 | 4081.1216 | 5382.2574 | 83.1992 | 109.7246
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5935 | 63.5141 | 6.9308 | 4 | 4079.4718 | 5379.9213 | 83.1656 | 109.677 | 157.1722 | 0 | 244.5754 | 8951863.1571 | 791125.8315 | 9219975.0843 | 9057049.4635 | 0 | 414498.4684 | 0 | 11089459.6819 | 28852499.3313 | 19692423.6532 | 88068894.6712 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 113096246.9133 | 149148943.281 | 7498942.0933 | 27.7233 | 4079.4718 | 5379.9213 | 83.1656 | 109.677
1 | 6100 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6519 | 63.5332 | 6.934 | 4 | 4078.2343 | 5378.0794 | 83.1403 | 109.6394 | 157.1694 | 0 | 256.6445 | 8953782.0139 | 791292.412 | 9222193.826 | 9060091.005 | 0 | 413051.656 | 0 | 11091760.256 | 28858484.9533 | 19696508.9632 | 88087165.0855 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 113114517.3276 | 149167213.6953 | 10000000 | 27.7361 | 4078.2343 | 5378.0794 | 83.1403 | 109.6394
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.6233 | [19 empty] | 100 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9684 | [19 empty] | 133.3521 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2848 | [19 empty] | 177.8279 | 0
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5834 | 0.33475 | 0.012174 | 4 | 557601.1335 | 1314185.6462 | 11367.4533 | 26791.452 | 115.7053 | 0 | 47.9962 | 182726.0317 | 12486.718 | 142645.0486 | 84502.6402 | 0 | 81739.931 | 0 | 196599.1441 | 511510.6449 | 349116.5256 | 1561326.6841 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 27152268.979 | 63993991.4208 | 237.1374 | 0.048695 | 557601.1335 | 1314185.6462 | 11367.4533 | 26791.452
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.50605 | 0.025763 | 4 | 268627.0413 | 626127.0303 | 5476.3256 | 12764.4464 | 124.9735 | 0 | 326.9725 | 256246.5959 | 18544.9838 | 197258.2426 | 109491.7509 | 0 | 93923.8241 | 0 | 263431.505 | 685394.7387 | 467795.9926 | 2092087.6336 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 27683029.9286 | 64524752.3703 | 316.2278 | 0.10305 | 268627.0413 | 626127.0303 | 5476.3256 | 12764.4464
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7016 | 0.73354 | 0.045795 | 4 | 154656.3017 | 355779.2427 | 3152.8779 | 7253.0411 | 132.5653 | 0 | 416.8097 | 345114.0181 | 26239.528 | 264081.0269 | 142407.4102 | 0 | 106495.0471 | 0 | 344891.4418 | 897336.7846 | 612450.7939 | 2739016.0505 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 28329958.3455 | 65171680.7873 | 421.6965 | 0.18318 | 154656.3017 | 355779.2427 | 3152.8779 | 7253.0411
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5573 | 1.0566 | 0.075246 | 4 | 96949.6145 | 219354.114 | 1976.449 | 4471.8303 | 139.1935 | 0 | 560.6237 | 459674.0222 | 36536.0011 | 352023.5813 | 187441.2574 | 0 | 123184.8231 | 0 | 451955.2772 | 1175894.9224 | 802572.4468 | 3589282.3314 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 29180224.6263 | 66021947.0681 | 562.3413 | 0.30098 | 96949.6145 | 219354.114 | 1976.449 | 4471.8303
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6574 | 1.4846 | 0.11636 | 4 | 64950.5015 | 144101.7654 | 1324.1038 | 2937.7094 | 144.4649 | 0 | 76.514 | 598325.6099 | 49447.1821 | 460367.9031 | 248501.8688 | 0 | 141748.7068 | 0 | 584372.5956 | 1520417.6224 | 1037716.2688 | 4640897.7575 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 30231840.0525 | 67073562.4942 | 749.8942 | 0.46546 | 64950.5015 | 144101.7654 | 1324.1038 | 2937.7094
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1506 | 2.0748 | 0.17417 | 4 | 45346.6186 | 98228.7231 | 924.4522 | 2002.5254 | 148.7937 | 0 | 71.6699 | 772835.8126 | 66137.7884 | 599824.838 | 333018.6214 | 0 | 165700.6723 | 0 | 755631.9158 | 1965999.2434 | 1341834.8808 | 6000983.7727 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 31591926.0677 | 68433648.5094 | 1000 | 0.69668 | 45346.6186 | 98228.7231 | 924.4522 | 2002.5254
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0996 | 2.8472 | 0.25132 | 4 | 33087.044 | 69735.4821 | 674.5241 | 1421.6521 | 152.0301 | 0 | 66.6483 | 981321.6303 | 86455.4249 | 770711.4321 | 444412.7619 | 0 | 193680.9369 | 0 | 965867.0526 | 2512987.9442 | 1715165.9087 | 7670603.0916 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 33261545.3866 | 70103267.8283 | 1333.5214 | 1.0053 | 33087.044 | 69735.4821 | 674.5241 | 1421.6521
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7326 | 3.9056 | 0.35856 | 4 | 24680.4436 | 50368.0162 | 503.1442 | 1026.8201 | 154.908 | 0 | 101.0781 | 1242972.7735 | 112396.9777 | 990289.3011 | 591879.1323 | 0 | 228599.6783 | 0 | 1234793.7665 | 3212680.0894 | 2192720.175 | 9806331.8938 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 35397274.1888 | 72238996.6305 | 1778.2794 | 1.4342 | 24680.4436 | 50368.0162 | 503.1442 | 1026.8201
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1969 | 5.3942 | 0.49994 | 4 | 19067.2979 | 37490.4022 | 388.7127 | 764.2926 | 156.9823 | 0 | 76.3923 | 1559694.2473 | 140781.7631 | 1282263.709 | 793106.5654 | 0 | 272582.4311 | 0 | 1578887.1992 | 4107940.6179 | 2803753.8815 | 12539010.4144 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 38129952.7094 | 74971675.1512 | 2371.3737 | 1.9998 | 19067.2979 | 37490.4022 | 388.7127 | 764.2926
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.799 | 7.3496 | 0.68573 | 4 | 15126.1377 | 28557.6473 | 308.3668 | 582.1863 | 158.583 | 0 | 71.8828 | 1939777.0704 | 174832.0138 | 1642269.7157 | 1050580.5553 | 0 | 325807.8099 | 0 | 2001974.1944 | 5208726.1924 | 3555062.6549 | 15899030.2068 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 41489972.5018 | 78331694.9436 | 3162.2777 | 2.7429 | 15126.1377 | 28557.6473 | 308.3668 | 582.1863
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8937 | 9.941 | 0.93176 | 4 | 12259.5837 | 22144.5414 | 249.9282 | 451.4464 | 159.8091 | 0 | 94.7019 | 2400811.2672 | 215992.6799 | 2091122.2592 | 1391428.729 | 0 | 390629.5441 | 0 | 2531093.947 | 6585387.2513 | 4494662.1152 | 20101127.793 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 45692070.0879 | 82533792.5297 | 4216.965 | 3.727 | 12259.5837 | 22144.5414 | 249.9282 | 451.4464
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.8863 | 13.3408 | 1.2546 | 4 | 10143.8001 | 17484.927 | 206.7951 | 356.4539 | 160.7402 | 0 | 102.9924 | 2955838.2423 | 265376.7872 | 2645928.8808 | 1838175.177 | 0 | 468406.4874 | 0 | 3187752.9742 | 8293879.3407 | 5660743.0722 | 25316100.9619 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 50907043.2568 | 87748765.6986 | 5623.4133 | 5.0185 | 10143.8001 | 17484.927 | 206.7951 | 356.4539
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.2884 | 17.7662 | 1.6747 | 4 | 8561.1083 | 14060.9839 | 174.5298 | 286.6522 | 161.4431 | 0 | 97.5582 | 3620490.8373 | 324303.7151 | 3327426.2848 | 2419427.026 | 0 | 561595.6562 | 0 | 3998764.9726 | 10403966.1992 | 7100920.7111 | 31756895.4025 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 57347837.6974 | 94189560.1392 | 7498.9421 | 6.6986 | 8561.1083 | 14060.9839 | 174.5298 | 286.6522
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.5721 | 23.4076 | 2.2096 | 4 | 7372.7682 | 11541.0623 | 150.3039 | 235.2802 | 161.9399 | 0 | 103.4078 | 4402254.8102 | 393356.8115 | 4148772.1791 | 3161344.0658 | 0 | 671307.7081 | 0 | 4983043.8741 | 12964857.9975 | 8848781.9845 | 39573719.4307 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 65164661.7257 | 102006384.1675 | 10000 | 8.8386 | 7372.7682 | 11541.0623 | 150.3039 | 235.2802
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0495 | 30.3433 | 2.8656 | 4 | 6487.6435 | 9701.7831 | 132.2594 | 197.784 | 162.1801 | 0 | 126.2817 | 5292706.8541 | 471715.7505 | 5106035.3676 | 4079246.3452 | 0 | 797459.2093 | 0 | 6141393.7754 | 15978646.8304 | 10905754.7901 | 48772958.9224 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 74363901.2173 | 111205623.6591 | 13335.2143 | 11.4624 | 6487.6435 | 9701.7831 | 132.2594 | 197.784
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.6279 | 38.4029 | 3.6231 | 4 | 5843.4904 | 8385.651 | 119.1275 | 170.9528 | 162.0629 | 0 | 134.2394 | 6257162.1127 | 556277.2195 | 6164883.0834 | 5163577.7288 | 0 | 937777.8285 | 0 | 7441074.4095 | 19360149.2392 | 13213699.6671 | 59094601.2888 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 84685543.5837 | 121527266.0255 | 17782.7941 | 14.4923 | 5843.4904 | 8385.651 | 119.1275 | 170.9528
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.825 | 45.6337 | 4.3428 | 4 | 5388.907 | 7509.7588 | 109.8602 | 153.0966 | 161.6432 | 0 | 123.2542 | 7074059.7536 | 627677.2575 | 7077210.6494 | 6161916.8384 | 0 | 1020783.3279 | 0 | 8565042.6524 | 22284484.0498 | 15209618.2644 | 68020792.7934 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 93611735.0884 | 130453457.5302 | 23713.7371 | 17.3712 | 5388.907 | 7509.7588 | 109.8602 | 153.0966
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.6091 | 49.773 | 4.8678 | 4 | 5051.4371 | 6943.5587 | 102.9804 | 141.5538 | 161.2759 | 0 | 157.133 | 7524983.8763 | 667009.2671 | 7586271.461 | 6748401.8553 | 0 | 967109.9016 | 0 | 9162572.7809 | 23839134.8739 | 16270699.3967 | 72766183.4129 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 98357125.7078 | 135198848.1496 | 31622.7766 | 19.4711 | 5051.4371 | 6943.5587 | 102.9804 | 141.5538
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8527 | 53.2257 | 5.3293 | 4 | 4795.5309 | 6523.7845 | 97.7634 | 132.9962 | 160.9018 | 0 | 203.314 | 7893015.9346 | 699070.9873 | 8004432.795 | 7247667.7758 | 0 | 899309.3215 | 0 | 9649963.7575 | 25107226.2173 | 17136197.7952 | 76636884.5842 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 102227826.8791 | 139069549.3209 | 42169.6503 | 21.3173 | 4795.5309 | 6523.7845 | 97.7634 | 132.9962
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.5749 | 56.7828 | 5.7751 | 4 | 4600.6889 | 6195.5322 | 93.7913 | 126.3043 | 160.4851 | 0 | 219.8429 | 8265162.5228 | 731456.0474 | 8429602.2744 | 7769516.0362 | 0 | 855536.527 | 0 | 10159996.629 | 26434227.1269 | 18041903.1831 | 80687400.3468 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 106278342.6417 | 143120065.0835 | 56234.1325 | 23.1005 | 4600.6889 | 6195.5322 | 93.7913 | 126.3043
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.223 | 59.191 | 6.1153 | 4 | 4451.4596 | 5957.58 | 90.749 | 121.4533 | 160.2075 | 0 | 198.5083 | 8513359.6199 | 753035.7376 | 8714417.1307 | 8125643.9049 | 0 | 787602.2505 | 0 | 10488682.871 | 27289401.3057 | 18625577.1323 | 83297719.9526 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 108888662.2476 | 145730384.6894 | 74989.4209 | 24.4613 | 4451.4596 | 5957.58 | 90.749 | 121.4533
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4675 | 61.0628 | 6.3891 | 4 | 4338.6183 | 5780.1978 | 88.4486 | 117.8372 | 159.9786 | 0 | 195.7939 | 8704298.1824 | 769626.9568 | 8934188.7883 | 8405605.8574 | 0 | 723238.324 | 0 | 10739413.6625 | 27941751.3931 | 19070819.4714 | 85288942.6359 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 110879884.9308 | 147721607.3726 | 100000 | 25.5565 | 4338.6183 | 5780.1978 | 88.4486 | 117.8372
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5166 | 62.4895 | 6.6046 | 4 | 4253.3955 | 5647.9441 | 86.7112 | 115.141 | 159.7961 | 0 | 197.7933 | 8848715.7029 | 782170.1043 | 9100789.2779 | 8620624.3267 | 0 | 665072.3468 | 0 | 10926774.9858 | 28429227.1234 | 19403531.6739 | 86776905.5417 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 112367847.8367 | 149209570.2784 | 133352.1432 | 26.4184 | 4253.3955 | 5647.9441 | 86.7112 | 115.141
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5903 | 63.5623 | 6.7715 | 4 | 4189.0935 | 5549.2762 | 85.4003 | 113.1295 | 159.6544 | 0 | 213.6781 | 8956700.7145 | 791545.7897 | 9225568.7767 | 8783504.689 | 0 | 614353.677 | 0 | 11064952.7222 | 28788737.2494 | 19648904.7221 | 87874268.3405 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 113465210.6355 | 150306933.0773 | 177827.941 | 27.0859 | 4189.0935 | 5549.2762 | 85.4003 | 113.1295
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.8996 | 64.3624 | 6.8992 | 4 | 4140.6138 | 5475.6099 | 84.412 | 111.6277 | 159.5461 | 0 | 210.7994 | 9036902.3041 | 798507.4672 | 9318357.4622 | 8905677.9498 | 0 | 571424.7524 | 0 | 11166039.2749 | 29051743.7237 | 19828412.0451 | 88677064.9795 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 114268007.2744 | 151109729.7162 | 237137.3706 | 27.5969 | 4140.6138 | 5475.6099 | 84.412 | 111.6277
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6318 | 64.9592 | 6.9965 | 4 | 4104.0883 | 5420.5267 | 83.6674 | 110.5048 | 159.4639 | 0 | 198.9415 | 9096542.348 | 803683.4014 | 9387419.8728 | 8997207.3378 | 0 | 536065.2053 | 0 | 11240158.0844 | 29244585.6623 | 19960030.6307 | 89265692.5426 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 114856634.8376 | 151698357.2794 | 316227.766 | 27.9859 | 4104.0883 | 5420.5267 | 83.6674 | 110.5048
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.9157 | 65.3997 | 7.0698 | 4 | 4076.5871 | 5379.367 | 83.1067 | 109.6657 | 159.4024 | 0 | 195.6621 | 9140463.1374 | 807494.6026 | 9438313.3306 | 9064990.1696 | 0 | 507341.4511 | 0 | 11293855.0497 | 29384294.151 | 20055384.5449 | 89692136.437 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 115283078.732 | 152124801.1738 | 421696.5034 | 28.2793 | 4076.5871 | 5379.367 | 83.1067 | 109.6657
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8554 | 65.7211 | 7.1247 | 4 | 4055.893 | 5348.6447 | 82.6849 | 109.0394 | 159.357 | 0 | 239.6017 | 9172452.7818 | 810270.2101 | 9475399.4397 | 9114565.7533 | 0 | 484238.113 | 0 | 11332201.2562 | 29484063.1145 | 20123478.9126 | 89996669.5813 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 115587611.8763 | 152429334.3181 | 562341.3252 | 28.4987 | 4055.893 | 5348.6447 | 82.6849 | 109.0394
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5593 | 65.9613 | 7.166 | 4 | 4040.3301 | 5325.6192 | 82.3676 | 108.57 | 159.3229 | 0 | 233.4102 | 9196328.9627 | 812341.6954 | 9503089.296 | 9151680.3655 | 0 | 466139.6522 | 0 | 11360536.189 | 29557784.7974 | 20173795.4759 | 90221696.4341 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 115812638.729 | 152654361.1708 | 749894.2093 | 28.6642 | 4040.3301 | 5325.6192 | 82.3676 | 108.57
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.0734 | 66.1364 | 7.1968 | 4 | 4028.6324 | 5308.4216 | 82.1291 | 108.2194 | 159.2979 | 0 | 224.6221 | 9213725.3015 | 813850.9119 | 9523269.574 | 9178783.2887 | 0 | 451919.1336 | 0 | 11380803.8018 | 29610516.9684 | 20209786.2662 | 90382655.2461 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 115973597.5411 | 152815319.9828 | 1000000 | 28.7873 | 4028.6324 | 5308.4216 | 82.1291 | 108.2194
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.4561 | 66.2666 | 7.2199 | 4 | 4019.8437 | 5295.5388 | 81.95 | 107.9567 | 159.2793 | 0 | 224.1287 | 9226646.9371 | 814971.8821 | 9538261.9316 | 9198948.6761 | 0 | 440940.0856 | 0 | 11395710.1099 | 29649300.1243 | 20236256.567 | 90501036.3137 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116091978.6087 | 152933701.0505 | 1333521.4322 | 28.8797 | 4019.8437 | 5295.5388 | 81.95 | 107.9567
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7339 | 66.361 | 7.237 | 4 | 4013.2432 | 5285.9212 | 81.8154 | 107.7607 | 159.2657 | 0 | 209.6069 | 9236014.4607 | 815784.5045 | 9549132.1505 | 9213586.6679 | 0 | 432416.7695 | 0 | 11406304.4757 | 29676864.4911 | 20255069.8137 | 90585173.3337 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116176115.6287 | 153017838.0704 | 1778279.41 | 28.9482 | 4013.2432 | 5285.9212 | 81.8154 | 107.7607
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.936 | 66.4296 | 7.2497 | 4 | 4008.2876 | 5278.7383 | 81.7144 | 107.6142 | 159.2558 | 0 | 234.8304 | 9242819.723 | 816374.8412 | 9557029.8865 | 9224231.122 | 0 | 425841.7149 | 0 | 11413855.9421 | 29696511.8577 | 20268479.5452 | 90645144.6325 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116236086.9275 | 153077809.3693 | 2371373.7057 | 28.9989 | 4008.2876 | 5278.7383 | 81.7144 | 107.6142
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.0823 | 66.4792 | 7.2591 | 4 | 4004.568 | 5273.3762 | 81.6385 | 107.5049 | 159.2486 | 0 | 213.9927 | 9247743.3616 | 816801.946 | 9562744.3565 | 9231938.1496 | 0 | 420782.2792 | 0 | 11419203.9363 | 29710426.2413 | 20277976.3979 | 90687616.6685 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116278558.9634 | 153120281.4052 | 3162277.6602 | 29.0365 | 4004.568 | 5273.3762 | 81.6385 | 107.5049
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.2092 | 66.5223 | 7.2666 | 4 | 4001.7767 | 5269.2719 | 81.5816 | 107.4212 | 159.2424 | 0 | 220.5103 | 9252012.1419 | 817172.2402 | 9567699.072 | 9238621.0679 | 0 | 417199.6946 | 0 | 11424154.6445 | 29723306.9686 | 20286767.759 | 90726933.5887 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116317875.8837 | 153159598.3255 | 4216965.0343 | 29.0666 | 4001.7767 | 5269.2719 | 81.5816 | 107.4212
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.2844 | 66.5478 | 7.2717 | 4 | 3999.6824 | 5266.29 | 81.5389 | 107.3604 | 159.2387 | 0 | 240.3746 | 9254538.769 | 817391.4099 | 9570631.8191 | 9242580.548 | 0 | 414211.9306 | 0 | 11426748.2458 | 29730054.9872 | 20291373.4203 | 90747531.1298 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116338473.4248 | 153180195.8666 | 5623413.2519 | 29.0869 | 3999.6824 | 5266.29 | 81.5389 | 107.3604
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3575 | 66.5726 | 7.276 | 4 | 3998.1113 | 5263.9729 | 81.5069 | 107.3132 | 159.2351 | 0 | 237.9017 | 9256998.6595 | 817604.7891 | 9573487.1921 | 9246433.8745 | 0 | 412199.4651 | 0 | 11429622.3523 | 29737532.8228 | 20296477.1968 | 90770356.3522 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116361298.6471 | 153203021.0889 | 7498942.0933 | 29.1041 | 3998.1113 | 5263.9729 | 81.5069 | 107.3132
1 | 6200 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3964 | 66.5858 | 7.2788 | 4 | 3996.9327 | 5262.312 | 81.4829 | 107.2793 | 159.2332 | 0 | 240.1686 | 9258304.5038 | 817718.062 | 9575003.0161 | 9248481.7933 | 0 | 410457.385 | 0 | 11430886.2564 | 29740821.242 | 20298721.6105 | 90780393.869 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 116371336.1639 | 153213058.6057 | 10000000 | 29.1152 | 3996.9327 | 5262.312 | 81.4829 | 107.2793
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7776 | [19 empty] | 100 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.5142 | [19 empty] | 133.3521 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2418 | [19 empty] | 177.8279 | 0
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.35663 | 0.014028 | 4 | 495342.4067 | 1166146.0383 | 10098.225 | 23773.4643 | 117.8244 | 0 | 238.9559 | 193273.9711 | 13378.152 | 149831.6957 | 87446.4485 | 0 | 83436.557 | 0 | 205673.0615 | 535119.1166 | 365229.7927 | 1633388.795 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 27793781.2337 | 65432733.8768 | 237.1374 | 0.05611 | 495342.4067 | 1166146.0383 | 10098.225 | 23773.4643
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.52963 | 0.02849 | 4 | 248527.2557 | 578809.3901 | 5066.5643 | 11799.8123 | 126.7907 | 0 | 312.1796 | 267107.522 | 19557.2838 | 204316.0505 | 112612.7977 | 0 | 94371.1785 | 0 | 272206.2847 | 708224.9155 | 483378.0574 | 2161774.0901 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 28322166.5289 | 65961119.1719 | 316.2278 | 0.11396 | 248527.2557 | 578809.3901 | 5066.5643 | 11799.8123
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.76 | 0.77059 | 0.050191 | 4 | 144456.0286 | 331935.6491 | 2944.9315 | 6766.9572 | 134.5604 | 0 | 407.2521 | 360757.2778 | 27792.6962 | 274320.6497 | 147008.6266 | 0 | 107391.1476 | 0 | 357735.4551 | 930754.2726 | 635258.9162 | 2841019.0418 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 29001411.4805 | 66640364.1235 | 421.6965 | 0.20076 | 144456.0286 | 331935.6491 | 2944.9315 | 6766.9572
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6157 | 1.1025 | 0.081513 | 4 | 91601.368 | 207040.1471 | 1867.4178 | 4220.7934 | 141.1491 | 0 | 573.0498 | 478117.0613 | 38537.1924 | 363704.1194 | 192980.9649 | 0 | 123315.544 | 0 | 466695.404 | 1214245.7087 | 828747.6465 | 3706343.6412 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 29866736.0799 | 67505688.7229 | 562.3413 | 0.32605 | 91601.368 | 207040.1471 | 1867.4178 | 4220.7934
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7622 | 1.561 | 0.12645 | 4 | 61264.7437 | 135679.9178 | 1248.9647 | 2766.0186 | 146.6028 | 0 | 79.6506 | 626258.9042 | 52626.624 | 478490.5969 | 258010.4852 | 0 | 143128.117 | 0 | 607820.7436 | 1581424.8937 | 1079354.985 | 4827115.3494 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 30987507.7882 | 68626460.4312 | 749.8942 | 0.5058 | 61264.7437 | 135679.9178 | 1248.9647 | 2766.0186
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.258 | 2.1677 | 0.18773 | 4 | 43109.5702 | 93233.9826 | 878.8469 | 1900.7008 | 150.8992 | 0 | 60.5142 | 805142.0464 | 70128.8302 | 620277.0272 | 343703.0852 | 0 | 166087.1783 | 0 | 782081.8853 | 2034816.6384 | 1388804.167 | 6211040.8582 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 32371433.2969 | 70010385.94 | 1000 | 0.75091 | 43109.5702 | 93233.9826 | 878.8469 | 1900.7008
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2608 | 2.9804 | 0.27072 | 4 | 31502.812 | 66261.4653 | 642.2274 | 1350.8296 | 154.1836 | 0 | 56.7215 | 1024006.5427 | 91989.2133 | 798143.0161 | 458768.1881 | 0 | 194826.3952 | 0 | 1001416.0086 | 2605479.0358 | 1778292.9792 | 7952921.3792 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 34113313.8179 | 71752266.461 | 1333.5214 | 1.0829 | 31502.812 | 66261.4653 | 642.2274 | 1350.8296
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.928 | 4.1612 | 0.38566 | 4 | 23596.3295 | 47995.5211 | 481.0431 | 978.4536 | 157.1043 | 0 | 84.6101 | 1299316.2022 | 117406.0885 | 1041861.0675 | 616412.8978 | 0 | 231171.5139 | 0 | 1289405.4303 | 3354768.4361 | 2289698.3912 | 10240040.0274 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 36400432.4662 | 74039385.1092 | 1778.2794 | 1.5426 | 23596.3295 | 47995.5211 | 481.0431 | 978.4536
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4527 | 5.7118 | 0.53404 | 4 | 18341.344 | 35961.2803 | 373.9131 | 733.1193 | 159.2031 | 0 | 79.9203 | 1623886.8852 | 146546.9578 | 1342304.8732 | 815654.2499 | 0 | 275202.3049 | 0 | 1639402.1557 | 4265388.1215 | 2911215.0379 | 13019600.586 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 39179993.0247 | 76818945.6678 | 2371.3737 | 2.1362 | 18341.344 | 35961.2803 | 373.9131 | 733.1193
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1326 | 7.7721 | 0.7311 | 4 | 14586.1208 | 27456.7588 | 297.3578 | 559.7432 | 160.8224 | 0 | 89.1422 | 2017800.8712 | 181807.5791 | 1717365.7502 | 1079883.7587 | 0 | 328933.346 | 0 | 2077058.6091 | 5404080.4375 | 3688395.9413 | 16495326.2931 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 42655718.7319 | 80294671.3749 | 3162.2777 | 2.9244 | 14586.1208 | 27456.7588 | 297.3578 | 559.7432
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3152 | 10.4952 | 0.99155 | 4 | 11847.8868 | 21337.8101 | 241.5352 | 435.0001 | 162.061 | 0 | 85.702 | 2494626.512 | 224352.274 | 2183870.0286 | 1428693.9361 | 0 | 394002.7333 | 0 | 2622962.7387 | 6824411.0026 | 4657800.7369 | 20830719.9622 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 46991112.4009 | 84630065.044 | 4216.965 | 3.9662 | 11847.8868 | 21337.8101 | 241.5352 | 435.0001
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4394 | 14.0751 | 1.3338 | 4 | 9818.3924 | 16873.0309 | 200.1612 | 343.9796 | 163.0043 | 0 | 98.3265 | 3070073.1846 | 275520.2273 | 2761823.6551 | 1886946.0624 | 0 | 472540.9402 | 0 | 3302092.5871 | 8591367.5593 | 5863784.8942 | 26224149.1102 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 52384541.5489 | 90023494.192 | 5623.4133 | 5.3353 | 9818.3924 | 16873.0309 | 200.1612 | 343.9796
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.0117 | 18.7344 | 1.779 | 4 | 8297.5365 | 13586.9148 | 169.1565 | 276.9876 | 163.7158 | 0 | 87.9745 | 3759218.7287 | 336576.7516 | 3471724.3264 | 2483066.8122 | 0 | 566711.5039 | 0 | 4140746.2679 | 10773372.4052 | 7353048.0372 | 32884464.8332 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 59044857.272 | 96683809.915 | 7498.9421 | 7.116 | 8297.5365 | 13586.9148 | 169.1565 | 276.9876
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.4736 | 24.6551 | 2.3444 | 4 | 7155.4468 | 11169.0977 | 145.8735 | 227.6972 | 164.2132 | 0 | 105.1245 | 4567446.215 | 407915.9852 | 4324725.042 | 3241591.4023 | 0 | 676964.0974 | 0 | 5155270.6693 | 13412956.7901 | 9154618.618 | 40941488.8192 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 67101881.258 | 104740833.901 | 10000 | 9.3777 | 7155.4468 | 11169.0977 | 145.8735 | 227.6972
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1432 | 31.9178 | 3.0362 | 4 | 6304.3634 | 9403.5568 | 128.523 | 191.7042 | 164.4408 | 0 | 101.0508 | 5486355.3703 | 488718.9962 | 5316914.0373 | 4178367.1878 | 0 | 803601.2914 | 0 | 6346843.1844 | 16513184.0492 | 11270587.4256 | 50404571.5422 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 76564963.9809 | 114203916.624 | 13335.2143 | 12.1448 | 6304.3634 | 9403.5568 | 128.523 | 191.7042
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8802 | 40.3227 | 3.832 | 4 | 5685.1619 | 8140.7258 | 115.8997 | 165.9597 | 164.2934 | 0 | 99.2261 | 6478019.2834 | 575600.2803 | 6410222.4049 | 5281309.4573 | 0 | 943881.6232 | 0 | 7678722.8892 | 19978461.835 | 13635710.7187 | 60981928.492 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 87142320.9308 | 124781273.5738 | 17782.7941 | 15.328 | 5685.1619 | 8140.7258 | 115.8997 | 165.9597
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.0371 | 48.1868 | 4.6063 | 4 | 5249.271 | 7292.0652 | 107.0135 | 148.6586 | 163.809 | 0 | 110.9782 | 7353497.1729 | 652057.7613 | 7392239.6362 | 6342064.7452 | 0 | 1041171.9236 | 0 | 8884602.1833 | 23115912.3984 | 15777085.1964 | 70558631.0174 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 96719023.4562 | 134357976.0992 | 23713.7371 | 18.4252 | 5249.271 | 7292.0652 | 107.0135 | 148.6586
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8017 | 52.4476 | 5.15 | 4 | 4927.8532 | 6754.9857 | 100.461 | 137.7095 | 163.4126 | 0 | 136.3196 | 7810689.7839 | 691902.0518 | 7910690.2522 | 6932370.8574 | 0 | 983463.7123 | 0 | 9488355.4964 | 24686754.6724 | 16849217.326 | 75353444.1522 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 101513836.591 | 139152789.234 | 31622.7766 | 20.6 | 4927.8532 | 6754.9857 | 100.461 | 137.7095
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0038 | 55.992 | 5.6263 | 4 | 4684.0779 | 6356.5428 | 95.4913 | 129.5867 | 163.014 | 0 | 191.1387 | 8183016.1525 | 724310.4501 | 8335555.1904 | 7433858.2856 | 0 | 912104.5009 | 0 | 9979649.386 | 25965000.5947 | 17721646.4333 | 79255140.9934 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 105415533.4322 | 143054486.0752 | 42169.6503 | 22.5051 | 4684.0779 | 6356.5428 | 95.4913 | 129.5867
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8035 | 59.7037 | 6.0906 | 4 | 4497.5741 | 6042.5364 | 91.6891 | 123.1853 | 162.5827 | 0 | 166.3598 | 8565824.0731 | 757595.3954 | 8774747.2827 | 7965011.7559 | 0 | 867518.7593 | 0 | 10502971.934 | 27326578.5164 | 18650951.3425 | 83411199.0593 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 109571591.498 | 147210544.1411 | 56234.1325 | 24.3624 | 4497.5741 | 6042.5364 | 91.6891 | 123.1853
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3787 | 62.1617 | 6.4397 | 4 | 4355.2708 | 5816.4888 | 88.7881 | 118.577 | 162.2926 | 0 | 176.2149 | 8815619.116 | 779295.9855 | 9062580.7437 | 8320407.8529 | 0 | 796817.8354 | 0 | 10832141.398 | 28183009.94 | 19235483.387 | 86025356.2584 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112185748.6971 | 149824701.3402 | 74989.4209 | 25.7586 | 4355.2708 | 5816.4888 | 88.7881 | 118.577
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.5649 | 64.0721 | 6.7202 | 4 | 4247.6546 | 5647.8706 | 86.5942 | 115.1395 | 162.0538 | 0 | 210.3017 | 9007841.8508 | 795985.1255 | 9284725.0381 | 8599854.5141 | 0 | 730333.9755 | 0 | 11083308.7965 | 28836495.9893 | 19681501.0435 | 88020046.3332 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 114180438.772 | 151819391.415 | 100000 | 26.8808 | 4247.6546 | 5647.8706 | 86.5942 | 115.1395
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.5692 | 65.529 | 6.9408 | 4 | 4166.3668 | 5522.0724 | 84.937 | 112.5749 | 161.8637 | 0 | 194.5628 | 9153331.6819 | 808611.1802 | 9453230.2277 | 8814712.3239 | 0 | 670548.4393 | 0 | 11271169.2027 | 29325270.2308 | 20015099.5065 | 89511972.7931 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 115672365.2319 | 153311317.8749 | 133352.1432 | 27.7634 | 4166.3668 | 5522.0724 | 84.937 | 112.5749
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6024 | 66.6218 | 7.1114 | 4 | 4105.0235 | 5428.2219 | 83.6865 | 110.6616 | 161.7165 | 0 | 214.1616 | 9261876.2958 | 818027.8879 | 9579149.2789 | 8977016.7741 | 0 | 618487.61 | 0 | 11409277.5602 | 29684599.847 | 20260349.3531 | 90608784.607 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 116769177.0457 | 154408129.6888 | 177827.941 | 28.4454 | 4105.0235 | 5428.2219 | 83.6865 | 110.6616
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8681 | 67.4323 | 7.2415 | 4 | 4058.7676 | 5358.1927 | 82.7435 | 109.234 | 161.6047 | 0 | 200.9183 | 9342050.3224 | 824981.6268 | 9672266.9563 | 9098076.21 | 0 | 574339.6925 | 0 | 11509568.7751 | 29945537.0157 | 20438444.3325 | 91405264.9314 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 117565657.3701 | 155204610.0132 | 237137.3706 | 28.9659 | 4058.7676 | 5358.1927 | 82.7435 | 109.234
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.566 | 68.0364 | 7.3404 | 4 | 4023.9124 | 5305.8198 | 82.0329 | 108.1663 | 161.5199 | 0 | 198.185 | 9401624.1501 | 830147.7188 | 9741518.897 | 9188691.8266 | 0 | 538016.2142 | 0 | 11582999.5346 | 30136588.7892 | 20568841.0936 | 91988428.2241 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 118148820.6628 | 155787773.3058 | 316227.766 | 29.3617 | 4023.9124 | 5305.8198 | 82.0329 | 108.1663
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8176 | 68.4798 | 7.4148 | 4 | 3997.665 | 5266.7078 | 81.4978 | 107.369 | 161.4569 | 0 | 224.1139 | 9445260.9784 | 833931.2948 | 9792277.175 | 9255432.7352 | 0 | 508450.1237 | 0 | 11635787.3998 | 30273931.9861 | 20662580.6476 | 92407652.3406 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 118568044.7793 | 156206997.4224 | 421696.5034 | 29.6593 | 3997.665 | 5266.7078 | 81.4978 | 107.369
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7339 | 68.8034 | 7.4705 | 4 | 3977.9119 | 5237.5047 | 81.0951 | 106.7736 | 161.4105 | 0 | 207.902 | 9477055.8222 | 836687.8342 | 9829278.0522 | 9304260.8824 | 0 | 484702.3731 | 0 | 11673474.136 | 30371985.1432 | 20729503.9421 | 92706948.1856 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 118867340.6243 | 156506293.2673 | 562341.3252 | 29.8818 | 3977.9119 | 5237.5047 | 81.0951 | 106.7736
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.4112 | 69.0421 | 7.5122 | 4 | 3963.0549 | 5215.6561 | 80.7922 | 106.3282 | 161.376 | 0 | 214.0005 | 9500478.2468 | 838718.3618 | 9856544.8553 | 9340339.5032 | 0 | 465980.3101 | 0 | 11700803.8981 | 30443091.5779 | 20778035.5449 | 92923992.2979 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119084384.7367 | 156723337.3797 | 749894.2093 | 30.0486 | 3963.0549 | 5215.6561 | 80.7922 | 106.3282
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.9176 | 69.2202 | 7.5435 | 4 | 3951.8864 | 5199.2784 | 80.5645 | 105.9943 | 161.3501 | 0 | 213.3824 | 9517945.2076 | 840232.522 | 9876883.7954 | 9367304.3494 | 0 | 451450.0719 | 0 | 11720988.2191 | 30495607.0407 | 20813878.4274 | 93084289.6335 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119244682.0723 | 156883634.7153 | 1000000 | 30.1741 | 3951.8864 | 5199.2784 | 80.5645 | 105.9943
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.2855 | 69.3494 | 7.5668 | 4 | 3943.4945 | 5187.0509 | 80.3935 | 105.745 | 161.3312 | 0 | 220.7685 | 9530607.5874 | 841330.1452 | 9891630.8802 | 9386885.6196 | 0 | 440103.1771 | 0 | 11735317.3897 | 30532888.6035 | 20839323.86 | 93198087.2627 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119358479.7014 | 156997432.3445 | 1333521.4322 | 30.2672 | 3943.4945 | 5187.0509 | 80.3935 | 105.745
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.5561 | 69.4444 | 7.5841 | 4 | 3937.1915 | 5177.904 | 80.265 | 105.5586 | 161.3173 | 0 | 230.665 | 9539909.1647 | 842136.4188 | 9902465.2977 | 9401287.6282 | 0 | 431352.9193 | 0 | 11745689.0572 | 30559873.5547 | 20857741.6437 | 93280455.6842 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119440848.1229 | 157079800.766 | 1778279.41 | 30.3366 | 3937.1915 | 5177.904 | 80.265 | 105.5586
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.7607 | 69.5162 | 7.5972 | 4 | 3932.459 | 5171.0352 | 80.1685 | 105.4185 | 161.3068 | 0 | 219.8815 | 9546937.477 | 842745.6301 | 9910652.6448 | 9412179.2885 | 0 | 424719.4003 | 0 | 11753521.4319 | 30580251.7869 | 20871650.2059 | 93342657.8654 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119503050.3041 | 157142002.9471 | 2371373.7057 | 30.3889 | 3932.459 | 5171.0352 | 80.1685 | 105.4185
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9117 | 69.5691 | 7.607 | 4 | 3928.9067 | 5165.8951 | 80.0961 | 105.3138 | 161.299 | 0 | 219.0721 | 9552116.9793 | 843194.5804 | 9916686.7438 | 9420211.5884 | 0 | 419652.2721 | 0 | 11759226.2439 | 30595094.5377 | 20881780.6883 | 93387963.6338 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119548356.0725 | 157187308.7156 | 3162277.6602 | 30.4279 | 3928.9067 | 5165.8951 | 80.0961 | 105.3138
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.0165 | 69.6058 | 7.6141 | 4 | 3926.2409 | 5162.0789 | 80.0417 | 105.236 | 161.2936 | 0 | 225.4849 | 9555710.9989 | 843506.1003 | 9920873.9853 | 9425788.706 | 0 | 415698.8178 | 0 | 11763015.6572 | 30604953.8138 | 20888509.8469 | 93418057.9262 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119578450.365 | 157217403.008 | 4216965.0343 | 30.4562 | 3926.2409 | 5162.0789 | 80.0417 | 105.236
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.0897 | 69.6314 | 7.6192 | 4 | 3924.2407 | 5159.242 | 80.001 | 105.1781 | 161.2898 | 0 | 216.1201 | 9558217.7643 | 843723.3783 | 9923794.6208 | 9429680.7512 | 0 | 412636.186 | 0 | 11765540.5532 | 30611523.0753 | 20892993.5028 | 93438109.8318 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119598502.2705 | 157237454.9136 | 5623413.2519 | 30.4769 | 3924.2407 | 5159.242 | 80.001 | 105.1781
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.148 | 69.6518 | 7.6232 | 4 | 3922.7401 | 5157.0982 | 79.9704 | 105.1344 | 161.2868 | 0 | 231.9026 | 9560216.7568 | 843896.6432 | 9926123.7133 | 9432784.5979 | 0 | 410379.3596 | 0 | 11767626.4177 | 30616950.0666 | 20896697.5359 | 93454675.0911 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119615067.5298 | 157254020.1729 | 7498942.0933 | 30.4927 | 3922.7401 | 5157.0982 | 79.9704 | 105.1344
1 | 6300 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2017 | 69.6706 | 7.6264 | 4 | 3921.6144 | 5155.4442 | 79.9474 | 105.1007 | 161.2841 | 0 | 217.4585 | 9562057.9889 | 844056.2333 | 9928269.0438 | 9435642.5006 | 0 | 408826.0488 | 0 | 11769752.208 | 30622480.9371 | 20900472.4686 | 93471557.4292 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 119631949.868 | 157270902.511 | 10000000 | 30.5058 | 3921.6144 | 5155.4442 | 79.9474 | 105.1007
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6808 | [19 empty] | 100 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.921 | [19 empty] | 133.3521 | 0
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.24152 | 0.0057909 | 4 | 1208124.4768 | 2867802.1734 | 24629.2516 | 58464.0263 | 108.9762 | 0 | 48.035 | 139950.7022 | 9177.211 | 110388.4755 | 70088.7899 | 0 | 73658.8167 | 0 | 157272.9582 | 409191.9761 | 279281.9318 | 1249010.8614 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 27984713.5348 | 66429100.5063 | 177.8279 | 0.023164 | 1208124.4768 | 2867802.1734 | 24629.2516 | 58464.0263
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.36905 | 0.015599 | 4 | 455267.3599 | 1071415.4848 | 9281.2409 | 21842.2539 | 119.2808 | 0 | 245.5443 | 199549.2253 | 13934.0869 | 153837.0272 | 88944.4605 | 0 | 83108.1269 | 0 | 210355.4415 | 547301.7088 | 373544.6622 | 1670574.7393 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 28406277.4127 | 66850664.3842 | 237.1374 | 0.062395 | 455267.3599 | 1071415.4848 | 9281.2409 | 21842.2539
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.5537 | 0.031325 | 4 | 231184.6114 | 538005.1121 | 4713.011 | 10967.9619 | 128.6065 | 0 | 325.7911 | 278107.3972 | 20597.5536 | 211447.2603 | 115578.9127 | 0 | 94765.913 | 0 | 280993.8444 | 731088.3433 | 498982.8167 | 2231562.0413 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 28967264.7147 | 67411651.6862 | 316.2278 | 0.1253 | 231184.6114 | 538005.1121 | 4713.011 | 10967.9619
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8183 | 0.80886 | 0.054855 | 4 | 135273.4916 | 310483.4206 | 2757.7331 | 6329.6245 | 136.5527 | 0 | 427.5989 | 376891.6753 | 29431.2665 | 284772.8409 | 151803.3785 | 0 | 108224.5178 | 0 | 370938.2348 | 965105.197 | 658704.1279 | 2945871.2385 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 29681573.9119 | 68125960.8834 | 421.6965 | 0.21942 | 135273.4916 | 310483.4206 | 2757.7331 | 6329.6245
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7022 | 1.1617 | 0.088943 | 4 | 85997.313 | 194055.7694 | 1753.1715 | 3956.0893 | 143.2732 | 0 | 75.4088 | 501152.7706 | 41038.3108 | 378664.981 | 200614.5706 | 0 | 124763.6258 | 0 | 486031.3609 | 1264553.9024 | 863084.0224 | 3859903.5445 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 30595606.2178 | 69039993.1894 | 562.3413 | 0.35577 | 85997.313 | 194055.7694 | 1753.1715 | 3956.0893
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8548 | 1.6355 | 0.13689 | 4 | 57976.1438 | 128187.9214 | 1181.9221 | 2613.2842 | 148.6924 | 0 | 76.0444 | 653885.4442 | 55913.45 | 495905.8704 | 267663.9982 | 0 | 143894.8328 | 0 | 630732.8023 | 1641037.3704 | 1120041.7252 | 5009075.4935 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 31744778.1668 | 70189165.1384 | 749.8942 | 0.54755 | 57976.1438 | 128187.9214 | 1181.9221 | 2613.2842
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 2.2728 | 0.20301 | 4 | 40872.8116 | 88214.7437 | 833.2475 | 1798.3769 | 153.0489 | 0 | 82.755 | 841774.6387 | 74832.0038 | 643135.1354 | 357244.9993 | 0 | 167241.7236 | 0 | 812849.1153 | 2114866.6597 | 1443439.9514 | 6455384.2273 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 33191086.9006 | 71635473.8722 | 1000 | 0.81206 | 40872.8116 | 88214.7437 | 833.2475 | 1798.3769
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4164 | 3.1633 | 0.29141 | 4 | 30052.9692 | 63034.2662 | 612.6704 | 1285.0388 | 156.3244 | 0 | 71.6382 | 1070271.5498 | 96568.877 | 836795.5452 | 477842.2456 | 0 | 196798.5181 | 0 | 1044527.927 | 2717647.4038 | 1854850.1952 | 8295302.2617 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 35031004.9351 | 73475391.9066 | 1333.5214 | 1.1656 | 30052.9692 | 63034.2662 | 612.6704 | 1285.0388
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1152 | 4.3995 | 0.41143 | 4 | 22698.3987 | 46058.6366 | 462.7376 | 938.9676 | 159.2914 | 0 | 90.9124 | 1351230.6684 | 122072.8268 | 1089322.6447 | 633113.0539 | 0 | 232938.0357 | 0 | 1337184.1195 | 3479078.7848 | 2374542.7586 | 10619482.8925 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 37355185.5659 | 75799572.5374 | 1778.2794 | 1.6457 | 22698.3987 | 46058.6366 | 462.7376 | 938.9676
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7085 | 6.0344 | 0.56876 | 4 | 17685.3337 | 34583.6381 | 360.5394 | 705.0342 | 161.4209 | 0 | 84.5745 | 1687987.2435 | 152292.3945 | 1402615.0364 | 837887.1189 | 0 | 277663.6624 | 0 | 1699793.7277 | 4422514.6039 | 3018457.0907 | 13499210.8779 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 40234913.5513 | 78679300.5228 | 2371.3737 | 2.275 | 17685.3337 | 34583.6381 | 360.5394 | 705.0342
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.481 | 8.2074 | 0.77776 | 4 | 14090.88 | 26448.2409 | 287.2616 | 539.1832 | 163.0626 | 0 | 87.4333 | 2096932.602 | 188878.0521 | 1793904.7578 | 1109594.9313 | 0 | 332275.4374 | 0 | 2153418.4544 | 5602753.0915 | 3823994.11 | 17101751.4364 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 43837454.1098 | 82281841.0813 | 3162.2777 | 3.1111 | 14090.88 | 26448.2409 | 287.2616 | 539.1832
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7562 | 11.0659 | 1.053 | 4 | 11469.2692 | 20596.6512 | 233.8166 | 419.8906 | 164.3127 | 0 | 89.4336 | 2589758.0174 | 232823.8985 | 2278365.7971 | 1466516.0442 | 0 | 397634.452 | 0 | 2716388.3016 | 7067485.1528 | 4823703.8391 | 21572675.5026 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 48308378.176 | 86752765.1475 | 4216.965 | 4.212 | 11469.2692 | 20596.6512 | 233.8166 | 419.8906
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0117 | 14.8277 | 1.4149 | 4 | 9519.2988 | 16311.8441 | 194.0638 | 332.539 | 165.2668 | 0 | 78.2572 | 3185372.0588 | 285751.3826 | 2879339.7912 | 1935809.1835 | 0 | 476826.4295 | 0 | 3417608.5497 | 8891916.3985 | 6068915.6526 | 27141539.4464 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 53877242.1198 | 92321629.0913 | 5623.4133 | 5.6598 | 9519.2988 | 16311.8441 | 194.0638 | 332.539
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.7279 | 19.712 | 1.8848 | 4 | 8056.3989 | 13155.6975 | 164.2406 | 268.1967 | 165.9846 | 0 | 98.4809 | 3897216.5611 | 348776.7209 | 3615910.4122 | 2545122.4156 | 0 | 571317.1048 | 0 | 4281553.8537 | 11139724.8599 | 7603091.1154 | 34002713.0437 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 60738415.7171 | 99182802.6886 | 7498.9421 | 7.5392 | 8056.3989 | 13155.6975 | 164.2406 | 268.1967
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.3775 | 25.9185 | 2.4813 | 4 | 6955.8709 | 10829.2076 | 141.8048 | 220.768 | 166.4825 | 0 | 75.8833 | 4732342.2628 | 422438.6163 | 4501132.5287 | 3320395.5182 | 0 | 682258.0376 | 0 | 5326841.1158 | 13859347.898 | 9459289.7215 | 42304045.6988 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 69039748.3722 | 107484135.3437 | 10000 | 9.9254 | 6955.8709 | 10829.2076 | 141.8048 | 220.768
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2421 | 33.5119 | 3.2093 | 4 | 6135.778 | 9130.5229 | 125.0861 | 186.1381 | 166.6963 | 0 | 103.8443 | 5679670.5494 | 505680.3606 | 5528320.3468 | 4276008.844 | 0 | 809400.2203 | 0 | 6551641.3252 | 17046026.8018 | 11634263.553 | 52031012.001 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 78766714.6744 | 117211101.6459 | 13335.2143 | 12.8373 | 6135.778 | 9130.5229 | 125.0861 | 186.1381
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.13 | 42.258 | 4.0432 | 4 | 5539.4879 | 7916.5704 | 112.93 | 161.39 | 166.5177 | 0 | 109.5056 | 6697660.2199 | 594802.5524 | 6655196.7585 | 5396343.07 | 0 | 949473.3128 | 0 | 7914455.6063 | 20591790.0095 | 14054319.8005 | 62854041.3299 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 89589744.0033 | 128034130.9748 | 17782.7941 | 16.1729 | 5539.4879 | 7916.5704 | 112.93 | 161.39
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.2102 | 50.759 | 4.8728 | 4 | 5120.457 | 7092.8548 | 104.3874 | 144.5974 | 165.9649 | 0 | 106.8739 | 7630811.1162 | 676232.1937 | 7706272.2909 | 6517284.4906 | 0 | 1060660.7682 | 0 | 9200591.7353 | 23938052.3943 | 16338212.6369 | 73068117.6261 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 99803820.2995 | 138248207.271 | 23713.7371 | 19.4912 | 5120.457 | 7092.8548 | 104.3874 | 144.5974
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9398 | 55.1321 | 5.4344 | 4 | 4813.6964 | 6582.2768 | 98.1337 | 134.1886 | 165.5399 | 0 | 151.7077 | 8093309.4876 | 716505.3019 | 8232978.795 | 7110288.1066 | 0 | 998771.727 | 0 | 9809222.833 | 25521585.6633 | 17419006.6314 | 77901668.5458 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 104637371.2192 | 143081758.1907 | 31622.7766 | 21.7374 | 4813.6964 | 6582.2768 | 98.1337 | 134.1886
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.0844 | 58.7583 | 5.9244 | 4 | 4581.0114 | 6203.3052 | 93.3901 | 126.4628 | 165.1179 | 0 | 193.6948 | 8468973.2764 | 749177.6282 | 8663410.0994 | 7612647.9232 | 0 | 923723.4641 | 0 | 10302993.6326 | 26806275.9975 | 18295834.1822 | 81823036.2036 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 108558738.877 | 147003125.8485 | 42169.6503 | 23.6975 | 4581.0114 | 6203.3052 | 93.3901 | 126.4628
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9935 | 62.6395 | 6.4082 | 4 | 4402.1041 | 5901.907 | 89.7428 | 120.3184 | 164.6713 | 0 | 196.1609 | 8863850.4849 | 783484.3288 | 9118267.267 | 8155325.2275 | 0 | 878945.3889 | 0 | 10841950.3519 | 28208530.8258 | 19252901.916 | 86103255.7909 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 112838958.4643 | 151283345.4358 | 56234.1325 | 25.633 | 4402.1041 | 5901.907 | 89.7428 | 120.3184
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.5124 | 65.1514 | 6.7663 | 4 | 4266.1495 | 5686.5824 | 86.9712 | 115.9287 | 164.3682 | 0 | 211.9909 | 9115716.466 | 805347.2784 | 9409634.4776 | 8511071.9528 | 0 | 805787.5927 | 0 | 11172547.5293 | 29068676.8667 | 19839969.2631 | 88728751.4266 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115464454.1 | 153908841.0715 | 74989.4209 | 27.0653 | 4266.1495 | 5686.5824 | 86.9712 | 115.9287
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.6332 | 67.0961 | 7.0532 | 4 | 4163.3249 | 5525.9855 | 84.875 | 112.6547 | 164.1201 | 0 | 226.0454 | 9308822.6236 | 822099.8612 | 9633663.5063 | 8789741.0554 | 0 | 737136.5315 | 0 | 11423670.7954 | 29722048.0925 | 20285908.5502 | 90723091.0161 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 117458793.6894 | 155903180.661 | 100000 | 28.2127 | 4163.3249 | 5525.9855 | 84.875 | 112.6547
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.589 | 68.58 | 7.2786 | 4 | 4085.645 | 5406.0956 | 83.2914 | 110.2106 | 163.9228 | 0 | 252.6375 | 9455111.5004 | 834785.3361 | 9803739.0595 | 9004179.4232 | 0 | 675723.6407 | 0 | 11611680.1944 | 30211209.9827 | 20619771.5915 | 92216200.7285 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 118951903.4018 | 157396290.3734 | 133352.1432 | 29.1146 | 4085.645 | 5406.0956 | 83.2914 | 110.2106
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5781 | 69.6899 | 7.4525 | 4 | 4027.0132 | 5316.6649 | 82.0961 | 108.3874 | 163.7705 | 0 | 234.6043 | 9563941.6539 | 844219.5006 | 9930463.8652 | 9165483.0813 | 0 | 622310.2069 | 0 | 11749303.1401 | 30569276.657 | 20864159.4542 | 93309157.5591 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 120044860.2325 | 158489247.204 | 177827.941 | 29.8099 | 4027.0132 | 5316.6649 | 82.0961 | 108.3874
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8165 | 70.5151 | 7.5852 | 4 | 3982.7957 | 5249.8832 | 81.1947 | 107.026 | 163.6547 | 0 | 257.9032 | 9644541.4632 | 851204.7885 | 10024424.6017 | 9286102.7572 | 0 | 577198.5669 | 0 | 11849554.1492 | 30830109.2185 | 21042183.037 | 94105318.5821 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 120841021.2555 | 159285408.227 | 237137.3706 | 30.3408 | 3982.7957 | 5249.8832 | 81.1947 | 107.026
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.4755 | 71.1234 | 7.6855 | 4 | 3949.4718 | 5200.0133 | 80.5153 | 106.0093 | 163.5678 | 0 | 251.0981 | 9703781.4012 | 856337.9947 | 10093542.856 | 9375401.3577 | 0 | 539865.2512 | 0 | 11921882.2557 | 31018292.115 | 21170621.7307 | 94679724.9622 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 121415427.6355 | 159859814.6071 | 316227.766 | 30.7422 | 3949.4718 | 5200.0133 | 80.5153 | 106.0093
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.6935 | 71.5681 | 7.7608 | 4 | 3924.3742 | 5162.7823 | 80.0037 | 105.2503 | 163.5035 | 0 | 225.4235 | 9747004.7451 | 860082.8662 | 10144004.6583 | 9440908.9958 | 0 | 509450.7265 | 0 | 11973566.2768 | 31152763.3361 | 21262401.1022 | 95090182.707 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 121825885.3804 | 160270272.3519 | 421696.5034 | 31.0434 | 3924.3742 | 5162.7823 | 80.0037 | 105.2503
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.595 | 71.8963 | 7.8174 | 4 | 3905.4841 | 5134.9306 | 79.6186 | 104.6825 | 163.4556 | 0 | 228.7917 | 9778848.4226 | 862841.5456 | 10181197.7016 | 9489362.6109 | 0 | 485193.2836 | 0 | 12011002.9901 | 31250165.9846 | 21328880.4112 | 95387492.9502 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122123195.6235 | 160567582.5951 | 562341.3252 | 31.2697 | 3905.4841 | 5134.9306 | 79.6186 | 104.6825
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2601 | 72.1379 | 7.8598 | 4 | 3891.2745 | 5114.0956 | 79.3289 | 104.2578 | 163.4201 | 0 | 235.557 | 9802263.6201 | 864869.9104 | 10208555.3462 | 9525097.2578 | 0 | 466058.8747 | 0 | 12038069.5536 | 31320587.6309 | 21376944.6318 | 95602446.8255 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122338149.4989 | 160782536.4704 | 749894.2093 | 31.4391 | 3891.2745 | 5114.0956 | 79.3289 | 104.2578
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.7398 | 72.3118 | 7.8911 | 4 | 3880.5916 | 5098.5554 | 79.1111 | 103.9409 | 163.3943 | 0 | 227.2042 | 9819108.3168 | 866329.0263 | 10228240.8956 | 9550862.2851 | 0 | 450954.9596 | 0 | 12057043.2385 | 31369953.2669 | 21410637.6928 | 95753129.6815 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122488832.3549 | 160933219.3264 | 1000000 | 31.5645 | 3880.5916 | 5098.5554 | 79.1111 | 103.9409
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.0908 | 72.4389 | 7.9144 | 4 | 3872.5639 | 5086.938 | 78.9475 | 103.7041 | 163.3755 | 0 | 211.2015 | 9831409.7522 | 867394.5589 | 10242619.4391 | 9569708.7363 | 0 | 439213.5085 | 0 | 12070634.938 | 31405316.0811 | 21434773.5401 | 95861070.5542 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122596773.2275 | 161041160.1991 | 1333521.4322 | 31.6578 | 3872.5639 | 5086.938 | 78.9475 | 103.7041
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.3466 | 72.5314 | 7.9318 | 4 | 3866.5341 | 5078.2569 | 78.8245 | 103.5271 | 163.3617 | 0 | 220.2288 | 9840361.5638 | 868169.9315 | 10253084.0837 | 9583440.1595 | 0 | 430129.1609 | 0 | 12080322.1107 | 31430520.1173 | 21451975.8127 | 95938002.94 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122673705.6134 | 161118092.5849 | 1778279.41 | 31.727 | 3866.5341 | 5078.2569 | 78.8245 | 103.5271
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.5512 | 72.6054 | 7.9452 | 4 | 3862.0064 | 5071.6869 | 78.7322 | 103.3932 | 163.3507 | 0 | 218.0136 | 9847519.1737 | 868789.8847 | 10261452.1054 | 9594426.8781 | 0 | 423407.2029 | 0 | 12088282.1455 | 31451230.4949 | 21466111.0709 | 96001218.9561 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122736921.6295 | 161181308.601 | 2371373.7057 | 31.7806 | 3862.0064 | 5071.6869 | 78.7322 | 103.3932
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.6903 | 72.6557 | 7.9548 | 4 | 3858.6077 | 5066.8238 | 78.6629 | 103.2941 | 163.3432 | 0 | 222.5664 | 9852378.0368 | 869210.7268 | 10267133.0449 | 9601892.0495 | 0 | 418095.9589 | 0 | 12093396.8286 | 31464537.8511 | 21475193.615 | 96041838.1116 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122777540.7849 | 161221927.7565 | 3162277.6602 | 31.8191 | 3858.6077 | 5066.8238 | 78.6629 | 103.2941
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.805 | 72.6971 | 7.9623 | 4 | 3856.057 | 5063.1296 | 78.6109 | 103.2187 | 163.337 | 0 | 226.7225 | 9856382.6891 | 869557.579 | 10271815.493 | 9608046.0419 | 0 | 414233.3922 | 0 | 12097813.7261 | 31476029.7126 | 21483037.0466 | 96076915.6805 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122812618.3539 | 161257005.3254 | 4216965.0343 | 31.8493 | 3856.057 | 5063.1296 | 78.6109 | 103.2187
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.8756 | 72.7225 | 7.9675 | 4 | 3854.1431 | 5060.4281 | 78.5719 | 103.1637 | 163.3332 | 0 | 222.6557 | 9858844.1502 | 869770.7702 | 10274693.6709 | 9611832.2303 | 0 | 411088.5693 | 0 | 12100229.4624 | 31482314.9629 | 21487326.859 | 96096100.6752 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122831803.3485 | 161276190.3201 | 5623413.2519 | 31.8701 | 3854.1431 | 5060.4281 | 78.5719 | 103.1637
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.9339 | 72.7436 | 7.9716 | 4 | 3852.7072 | 5058.3776 | 78.5426 | 103.1219 | 163.33 | 0 | 206.0686 | 9860879.7427 | 869947.0752 | 10277073.9452 | 9614963.1195 | 0 | 408800.0149 | 0 | 12102348.9201 | 31487829.3569 | 21491090.5463 | 96112932.7209 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122848635.3943 | 161293022.3658 | 7498942.0933 | 31.8863 | 3852.7072 | 5058.3776 | 78.5426 | 103.1219
1 | 6400 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.9728 | 72.7576 | 7.9745 | 4 | 3851.6301 | 5056.8616 | 78.5207 | 103.091 | 163.3279 | 0 | 215.8746 | 9862235.8371 | 870064.5277 | 10278659.6953 | 9617050.0822 | 0 | 407005.2109 | 0 | 12103655.9877 | 31491230.0788 | 21493411.6089 | 96123313.0286 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 122859015.702 | 161303402.6735 | 10000000 | 31.8979 | 3851.6301 | 5056.8616 | 78.5207 | 103.091
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4255 | [19 empty] | 100 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7229 | [19 empty] | 133.3521 | 0
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2934 | 0.25112 | 0.0067976 | 4 | 1051754.8978 | 2495569.0251 | 21441.4462 | 50875.5501 | 110.4068 | 0 | 50.9142 | 145075.2581 | 9594.9802 | 113766.8821 | 71381.4575 | 0 | 73730.5925 | 0 | 161284.1765 | 419628.3432 | 286404.9667 | 1280866.6568 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 28597739.6556 | 67855765.0828 | 177.8279 | 0.02719 | 1051754.8978 | 2495569.0251 | 21441.4462 | 50875.5501
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.38883 | 0.017556 | 4 | 413690.7607 | 972745.5554 | 8433.6457 | 19830.7339 | 121.1749 | 0 | 248.232 | 209105.3971 | 14771.8295 | 160185.3308 | 91530.9147 | 0 | 84056.705 | 0 | 218263.5691 | 567877.0348 | 387587.745 | 1733378.526 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 29050251.5249 | 68308276.9521 | 237.1374 | 0.070222 | 413690.7607 | 972745.5554 | 8433.6457 | 19830.7339
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.57854 | 0.034319 | 4 | 215767.3403 | 501742.5076 | 4398.7091 | 10228.6997 | 130.421 | 0 | 329.633 | 289426.0156 | 21687.5911 | 218726.7055 | 118668.0215 | 0 | 95111.8937 | 0 | 290011.8887 | 754551.4448 | 514996.8655 | 2303180.4265 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 29620053.4253 | 68878078.8526 | 316.2278 | 0.13728 | 215767.3403 | 501742.5076 | 4398.7091 | 10228.6997
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8766 | 0.84698 | 0.059555 | 4 | 127457.3937 | 292255.2787 | 2598.3914 | 5958.0192 | 138.5423 | 0 | 427.2519 | 392757.2624 | 31064.6918 | 295079.4463 | 155560.3372 | 0 | 108967.361 | 0 | 383537.3485 | 997885.5065 | 681077.3627 | 3045929.3163 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 30362802.3152 | 69620827.7424 | 421.6965 | 0.23822 | 127457.3937 | 292255.2787 | 2598.3914 | 5958.0192
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7754 | 1.217 | 0.096373 | 4 | 81241.3677 | 183080.2799 | 1656.2152 | 3732.3391 | 145.3136 | 0 | 64.7418 | 522899.9712 | 43487.8748 | 392467.3523 | 207448.7056 | 0 | 125477.953 | 0 | 503794.9242 | 1310771.0501 | 894628.1754 | 4000976.0065 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 31317849.0054 | 70575874.4326 | 562.3413 | 0.38549 | 81241.3677 | 183080.2799 | 1656.2152 | 3732.3391
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9474 | 1.7112 | 0.14769 | 4 | 55026.976 | 121481.6403 | 1121.7993 | 2476.5676 | 150.7793 | 0 | 64.1867 | 681857.0113 | 59340.9978 | 513411.0757 | 276602.52 | 0 | 144549.5407 | 0 | 653546.8467 | 1700394.8342 | 1160554.414 | 5190257.2403 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 32507130.2392 | 71765155.6664 | 749.8942 | 0.59075 | 55026.976 | 121481.6403 | 1121.7993 | 2476.5676
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5092 | 2.3825 | 0.21866 | 4 | 38890.2685 | 83774.6384 | 792.8307 | 1707.8593 | 155.1804 | 0 | 58.615 | 878464.4679 | 79533.0838 | 666879.6968 | 369695.8193 | 0 | 168124.7042 | 0 | 843452.1311 | 2194489.4293 | 1497784.1277 | 6698423.4602 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 34015296.459 | 73273321.8862 | 1000 | 0.87465 | 38890.2685 | 83774.6384 | 792.8307 | 1707.8593
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5601 | 3.3387 | 0.31108 | 4 | 28864.3187 | 60414.3536 | 588.4382 | 1231.6283 | 158.4485 | 0 | 71.6732 | 1112942.6384 | 100633.408 | 873569.1888 | 491181.1503 | 0 | 198097.4974 | 0 | 1082805.3143 | 2817237.3139 | 1922822.3552 | 8599288.8661 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 35916161.865 | 75174187.2922 | 1333.5214 | 1.2443 | 28864.3187 | 60414.3536 | 588.4382 | 1231.6283
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3199 | 4.6494 | 0.43825 | 4 | 21865.8188 | 44260.7026 | 445.7643 | 902.3143 | 161.4892 | 0 | 83.1787 | 1404795.6019 | 126885.5922 | 1138541.5525 | 650586.8604 | 0 | 235149.2629 | 0 | 1386823.9593 | 3608231.4653 | 2462692.1168 | 11013706.4113 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 38330579.4102 | 77588604.8374 | 1778.2794 | 1.753 | 21865.8188 | 44260.7026 | 445.7643 | 902.3143
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9863 | 6.3722 | 0.60487 | 4 | 17075.3495 | 33301.0501 | 348.1041 | 678.8869 | 163.6456 | 0 | 75.7153 | 1754057.612 | 158211.2336 | 1465086.2009 | 861136.6224 | 0 | 280632.9516 | 0 | 1762458.602 | 4585555.7523 | 3129736.0247 | 13996874.9995 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 41313747.9983 | 80571773.4255 | 2371.3737 | 2.4195 | 17075.3495 | 33301.0501 | 348.1041 | 678.8869
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8099 | 8.6399 | 0.82461 | 4 | 13645.1665 | 25547.156 | 278.1752 | 520.8133 | 165.2945 | 0 | 95.6741 | 2174353.24 | 195791.6889 | 1869143.0196 | 1137671.7676 | 0 | 334849.3607 | 0 | 2227605.54 | 5795772.6703 | 3955733.9387 | 17690921.226 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 45007794.2248 | 84265819.652 | 3162.2777 | 3.2984 | 13645.1665 | 25547.156 | 278.1752 | 520.8133
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2043 | 11.648 | 1.1158 | 4 | 11121.257 | 19917.4547 | 226.7219 | 406.0443 | 166.5623 | 0 | 77.267 | 2685340.1684 | 241330.4479 | 2373746.7348 | 1504151.7261 | 0 | 401185.5409 | 0 | 2810244.301 | 7311679.2109 | 4990371.3014 | 22318049.4314 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 49634922.4303 | 88892947.8575 | 4216.965 | 4.4631 | 11121.257 | 19917.4547 | 226.7219 | 406.0443
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.599 | 15.5985 | 1.498 | 4 | 9242.9922 | 15794.5166 | 188.4309 | 321.9926 | 167.5274 | 0 | 75.8002 | 3301737.0349 | 296070.427 | 2998475.9124 | 1985080.1943 | 0 | 481167.7056 | 0 | 3534387.1969 | 9195750.4838 | 6276288.659 | 28068957.6138 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 55385830.6127 | 94643856.0399 | 5623.4133 | 5.9922 | 9242.9922 | 15794.5166 | 188.4309 | 321.9926
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.481 | 20.7199 | 1.9936 | 4 | 7832.5362 | 12755.5455 | 159.6768 | 260.039 | 168.2518 | 0 | 85.6725 | 4037459.819 | 361166.7557 | 3763082.1003 | 2608392.6531 | 0 | 576361.3322 | 0 | 4425120.4375 | 11513255.6614 | 7858033.5626 | 35142872.3218 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 62459745.3207 | 101717770.7479 | 7498.9421 | 7.9744 | 7832.5362 | 12755.5455 | 159.6768 | 260.039
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.3178 | 27.2156 | 2.6217 | 4 | 6770.7745 | 10514.3365 | 138.0314 | 214.349 | 168.7485 | 0 | 96.1031 | 4899248.3581 | 437127.8555 | 4680447.3804 | 3400357.1351 | 0 | 687882.3264 | 0 | 5500974.5916 | 14312407.4824 | 9768512.1973 | 43686957.3269 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 71003830.3257 | 110261855.753 | 10000 | 10.4868 | 6770.7745 | 10514.3365 | 138.0314 | 214.349
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.348 | 35.1278 | 3.3852 | 4 | 5979.9136 | 8879.1523 | 121.9086 | 181.0135 | 168.9466 | 0 | 98.254 | 5872962.6652 | 522627.4262 | 5740562.7583 | 4372695.6357 | 0 | 814876.2112 | 0 | 6756252.6317 | 17578383.4497 | 11997607.9041 | 53655968.682 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 80972841.6809 | 120230867.1081 | 13335.2143 | 13.5408 | 5979.9136 | 8879.1523 | 121.9086 | 181.0135
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.3869 | 44.2149 | 4.2572 | 4 | 5404.7714 | 7710.1388 | 110.1836 | 157.1816 | 168.7353 | 0 | 109.9864 | 6916860.951 | 613952.406 | 6900630.3692 | 5510024.3846 | 0 | 954721.4857 | 0 | 8149513.9427 | 21203363.5837 | 14471731.3314 | 64720798.4544 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 92037671.4533 | 131295696.8805 | 17782.7941 | 17.029 | 5404.7714 | 7710.1388 | 110.1836 | 157.1816
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3445 | 53.3511 | 5.1424 | 4 | 5001.1033 | 6909.6455 | 101.9543 | 140.8625 | 168.1108 | 0 | 84.282 | 7906258.3996 | 700223.9753 | 8019522.3761 | 6688651.2222 | 0 | 1079220.8734 | 0 | 9513611.9702 | 24752466.8363 | 16894067.2281 | 75554022.8812 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 102870895.8801 | 142128921.3073 | 23713.7371 | 20.5696 | 5001.1033 | 6909.6455 | 101.9543 | 140.8625
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0593 | 57.8421 | 5.722 | 4 | 4707.8102 | 6423.0302 | 95.9751 | 130.9422 | 167.6565 | 0 | 150.9663 | 8374698.3692 | 740981.5724 | 8555176.9345 | 7285542.1957 | 0 | 1013601.8756 | 0 | 10128300.3695 | 26351759.9612 | 17985617.6481 | 80435678.9261 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 107752551.9249 | 147010577.3521 | 31622.7766 | 22.888 | 4707.8102 | 6423.0302 | 95.9751 | 130.9422
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.0675 | 62.3302 | 6.2799 | 4 | 4485.1094 | 6047.9418 | 91.435 | 123.2955 | 167.1244 | 0 | 182.6425 | 8832636.8457 | 780773.8428 | 9082224.8684 | 7895058.9521 | 0 | 965378.1727 | 0 | 10746868.3459 | 27961146.9502 | 19084057.3376 | 85348145.3154 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 112665018.3143 | 151923043.7415 | 42169.6503 | 25.1198 | 4485.1094 | 6047.9418 | 91.435 | 123.2955
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1519 | 65.5926 | 6.7283 | 4 | 4313.3598 | 5772.0545 | 87.9337 | 117.6711 | 166.7509 | 0 | 190.1594 | 9159663.3947 | 809160.5564 | 9460570.6882 | 8341314.6142 | 0 | 889874.9276 | 0 | 11177627.8306 | 29081894.7686 | 19848990.7527 | 88769097.533 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 116085970.5319 | 155343995.9591 | 56234.1325 | 26.9131 | 4313.3598 | 5772.0545 | 87.9337 | 117.6711
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6124 | 68.1533 | 7.0948 | 4 | 4183.243 | 5566.5878 | 85.2811 | 113.4824 | 166.4352 | 0 | 193.5072 | 9413141.0278 | 831146.3425 | 9754912.6534 | 8696394.2223 | 0 | 814302.2122 | 0 | 11508859.6187 | 29943691.9361 | 20437185.0277 | 91399633.0406 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 118716506.0395 | 157974531.4667 | 74989.4209 | 28.3791 | 4183.243 | 5566.5878 | 85.2811 | 113.4824
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6741 | 70.1307 | 7.3876 | 4 | 4084.826 | 5413.3318 | 83.2747 | 110.3581 | 166.1779 | 0 | 208.7734 | 9607026.1624 | 847953.6521 | 9980679.0488 | 8973817.6274 | 0 | 743633.7391 | 0 | 11759712.9896 | 30596360.9501 | 20882645.0408 | 93391829.2103 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 120708702.2092 | 159966727.6364 | 100000 | 29.5505 | 4084.826 | 5413.3318 | 83.2747 | 110.3581
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.577 | 71.6375 | 7.6175 | 4 | 4010.4693 | 5298.8928 | 81.7588 | 108.0251 | 165.9739 | 0 | 163.6324 | 9753737.154 | 860666.126 | 10151866.8598 | 9187181.3645 | 0 | 680584.5349 | 0 | 11947274.0553 | 31084356.369 | 21215711.9415 | 94881378.4051 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 122198251.404 | 161456276.8312 | 133352.1432 | 30.4698 | 4010.4693 | 5298.8928 | 81.7588 | 108.0251
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.5271 | 72.7649 | 7.7945 | 4 | 3954.3381 | 5213.4899 | 80.6145 | 106.284 | 165.8164 | 0 | 156.0046 | 9862936.9086 | 870125.2479 | 10279479.5037 | 9347707.9792 | 0 | 625934.8312 | 0 | 12084611.9435 | 31441681.3823 | 21459593.6053 | 95972071.4017 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 123288944.4005 | 162546969.8278 | 177827.941 | 31.1781 | 3954.3381 | 5213.4899 | 80.6145 | 106.284
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7191 | 73.5966 | 7.9291 | 4 | 3912.0008 | 5149.777 | 79.7514 | 104.9852 | 165.6976 | 0 | 207.8915 | 9943189.7893 | 877075.3044 | 10373368.9513 | 9466813.0321 | 0 | 579619.4758 | 0 | 12183625.9556 | 31699295.5312 | 21635420.5555 | 96758408.5953 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 124075281.5941 | 163333307.0213 | 237137.3706 | 31.7166 | 3912.0008 | 5149.777 | 79.7514 | 104.9852
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3392 | 74.208 | 8.0308 | 4 | 3880.0898 | 5102.2036 | 79.1009 | 104.0153 | 165.6089 | 0 | 201.8022 | 10002024.2151 | 882169.6128 | 10442256.3788 | 9554754.7773 | 0 | 541295.3999 | 0 | 12254775.1497 | 31884411.1396 | 21761765.7619 | 97323452.4352 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 124640325.4341 | 163898350.8613 | 316227.766 | 32.1231 | 3880.0898 | 5102.2036 | 79.1009 | 104.0153
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.5307 | 74.6559 | 8.107 | 4 | 3856.0532 | 5066.6674 | 78.6109 | 103.2909 | 165.543 | 0 | 231.7479 | 10045032.1919 | 885893.0909 | 10492642.8295 | 9619381.6635 | 0 | 510148.5923 | 0 | 12305708.3636 | 32016928.9141 | 21852211.866 | 97727947.5118 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125044820.5106 | 164302845.9378 | 421696.5034 | 32.4282 | 3856.0532 | 5066.6674 | 78.6109 | 103.2909
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.4197 | 74.9891 | 8.1646 | 4 | 3837.9594 | 5040.0454 | 78.242 | 102.7481 | 165.4936 | 0 | 210.4467 | 10076980.5894 | 888658.818 | 10530088.4987 | 9667577.6221 | 0 | 485432.8752 | 0 | 12343007.9774 | 32113974.858 | 21918447.7168 | 98024168.9556 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125341041.9545 | 164599067.3817 | 562341.3252 | 32.6583 | 3837.9594 | 5040.0454 | 78.242 | 102.7481
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0628 | 75.2295 | 8.2072 | 4 | 3824.3475 | 5020.1846 | 77.9645 | 102.3433 | 165.4577 | 0 | 228.4938 | 10100010.6369 | 890652.3635 | 10557089.7939 | 9702423.2211 | 0 | 465751.5343 | 0 | 12369211.7444 | 32182151.6846 | 21964979.8019 | 98232270.7805 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125549143.7794 | 164807169.2066 | 749894.2093 | 32.8289 | 3824.3475 | 5020.1846 | 77.9645 | 102.3433
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.5233 | 75.4014 | 8.2387 | 4 | 3814.1128 | 5005.3822 | 77.7558 | 102.0415 | 165.4319 | 0 | 234.5183 | 10116458.7794 | 892076.0928 | 10576378.5815 | 9727365.1277 | 0 | 450181.6275 | 0 | 12387359.4815 | 32229368.3741 | 21997206.1626 | 98376394.2271 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125693267.226 | 164951292.6532 | 1000000 | 32.9548 | 3814.1128 | 5005.3822 | 77.7558 | 102.0415
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8741 | 75.5321 | 8.2625 | 4 | 3806.4214 | 4994.2528 | 77.599 | 101.8146 | 165.4121 | 0 | 199.805 | 10128969.6245 | 893158.977 | 10591052.5203 | 9746364.674 | 0 | 438295.761 | 0 | 12401158.2071 | 32265269.8276 | 22021709.6424 | 98485979.2339 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125802852.2327 | 165060877.66 | 1333521.4322 | 33.0502 | 3806.4214 | 4994.2528 | 77.599 | 101.8146
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.1176 | 75.6228 | 8.2799 | 4 | 3800.6436 | 4985.9891 | 77.4813 | 101.6461 | 165.3984 | 0 | 205.578 | 10137641.8622 | 893909.589 | 10601225.3979 | 9759552.641 | 0 | 428915.8761 | 0 | 12410285.6928 | 32289017.6731 | 22037918.0349 | 98558466.767 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125875339.7658 | 165133365.1931 | 1778279.41 | 33.1195 | 3800.6436 | 4985.9891 | 77.4813 | 101.6461
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2956 | 75.6891 | 8.2927 | 4 | 3796.305 | 4979.8101 | 77.3928 | 101.5202 | 165.3884 | 0 | 204.2391 | 10143972.7626 | 894457.5402 | 10608652.4305 | 9769188.6037 | 0 | 421708.8349 | 0 | 12416812.267 | 32305998.4804 | 22049507.7848 | 98610298.7041 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125927171.703 | 165185197.1302 | 2371373.7057 | 33.171 | 3796.305 | 4979.8101 | 77.3928 | 101.5202
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4413 | 75.7433 | 8.3028 | 4 | 3793.0481 | 4975.1217 | 77.3264 | 101.4246 | 165.3801 | 0 | 240.8922 | 10149152.3085 | 894905.8333 | 10614729.1623 | 9777074.792 | 0 | 416429.282 | 0 | 12422393.6375 | 32320520.0614 | 22059419.0622 | 98654624.1392 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125971497.138 | 165229522.5653 | 3162277.6602 | 33.2112 | 3793.0481 | 4975.1217 | 77.3264 | 101.4246
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5339 | 75.7777 | 8.3098 | 4 | 3790.6037 | 4971.6774 | 77.2766 | 101.3544 | 165.3749 | 0 | 232.8375 | 10152441.2585 | 895190.4912 | 10618588.001 | 9782087.4203 | 0 | 412183.7659 | 0 | 12425591.4654 | 32328840.1536 | 22065097.6961 | 98680020.252 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 125996893.2508 | 165254918.678 | 4216965.0343 | 33.2393 | 3790.6037 | 4971.6774 | 77.2766 | 101.3544
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.6265 | 75.8121 | 8.3158 | 4 | 3788.7695 | 4968.9932 | 77.2392 | 101.2996 | 165.3697 | 0 | 235.8876 | 10155732.6927 | 895475.3619 | 10622449.8993 | 9787101.091 | 0 | 409332.3505 | 0 | 12429335.6442 | 32338581.7388 | 22071746.5281 | 98709755.3064 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 126026628.3053 | 165284653.7325 | 5623413.2519 | 33.2632 | 3788.7695 | 4968.9932 | 77.2392 | 101.2996
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.6823 | 75.8329 | 8.3199 | 4 | 3787.3934 | 4967.0397 | 77.2111 | 101.2598 | 165.3665 | 0 | 278.2517 | 10157711.503 | 895646.625 | 10624771.7424 | 9790118.1539 | 0 | 406974.6137 | 0 | 12431336.8288 | 32343788.4108 | 22075300.1888 | 98725648.0665 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 126042521.0653 | 165300546.4926 | 7498942.0933 | 33.2795 | 3787.3934 | 4967.0397 | 77.2111 | 101.2598
1 | 6500 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.7165 | 75.8456 | 8.3227 | 4 | 3786.3611 | 4965.6073 | 77.1901 | 101.2306 | 165.3646 | 0 | 267.6488 | 10158926.5135 | 895751.782 | 10626197.4045 | 9791972.352 | 0 | 405085.256 | 0 | 12432393.9902 | 32346538.9277 | 22077177.4731 | 98734043.6991 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 126050916.698 | 165308942.1252 | 10000000 | 33.2908 | 3786.3611 | 4965.6073 | 77.1901 | 101.2306
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4253 | [19 empty] | 100 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8039 | [19 empty] | 133.3521 | 0
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.26508 | 0.007986 | 4 | 915125.1709 | 2169810.9678 | 18656.0644 | 44234.5315 | 112.2348 | 0 | 54.0784 | 152299.1631 | 10183.2277 | 118642.2501 | 73275.1119 | 0 | 74686.8134 | 0 | 167343.7608 | 435394.1388 | 297165.4462 | 1328989.912 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 29232893.3272 | 69312761.3373 | 177.8279 | 0.031944 | 915125.1709 | 2169810.9678 | 18656.0644 | 44234.5315
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.40906 | 0.019602 | 4 | 378785.5481 | 889951.6019 | 7722.0557 | 18142.8672 | 123.0648 | 0 | 263.7124 | 218778.5478 | 15630.9944 | 166605.3482 | 93956.3281 | 0 | 84955.6761 | 0 | 226171.4889 | 588451.8199 | 401630.4586 | 1796180.6619 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 29700084.0772 | 69779952.0873 | 237.1374 | 0.078409 | 378785.5481 | 889951.6019 | 7722.0557 | 18142.8672
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.61171 | 0.037907 | 4 | 199855.2776 | 464182.9839 | 4074.3202 | 9462.998 | 132.5206 | 0 | 344.6801 | 304065.2675 | 23095.5079 | 228375.5097 | 122787.9222 | 0 | 96570.3267 | 0 | 302208.8683 | 786285.4838 | 536655.9992 | 2400044.8854 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 30303948.3006 | 70383816.3107 | 316.2278 | 0.15163 | 199855.2776 | 464182.9839 | 4074.3202 | 9462.998
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.935 | 0.88772 | 0.064749 | 4 | 119924.0917 | 274675.6166 | 2444.8148 | 5599.634 | 140.5291 | 0 | 435.3286 | 409819.1945 | 32873.8802 | 305955.4264 | 160592.844 | 0 | 109672.3991 | 0 | 397376.3602 | 1033891.7762 | 705652.3816 | 3155834.2622 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 31059737.6774 | 71139605.6875 | 421.6965 | 0.25899 | 119924.0917 | 274675.6166 | 2444.8148 | 5599.634
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8459 | 1.2729 | 0.10417 | 4 | 76914.9152 | 173108.1046 | 1568.0146 | 3529.0429 | 147.3362 | 0 | 75.8019 | 545032.587 | 46074.3692 | 406212.1444 | 214482.3454 | 0 | 125988.9459 | 0 | 521738.2528 | 1357455.9106 | 926491.5519 | 4143476.1073 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 32047379.5225 | 72127247.5326 | 562.3413 | 0.41666 | 76914.9152 | 173108.1046 | 1568.0146 | 3529.0429
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.04 | 1.7895 | 0.15931 | 4 | 52234.7179 | 115131.9685 | 1064.8754 | 2347.1209 | 152.8636 | 0 | 65.0354 | 711301.2779 | 63142.6561 | 531240.8695 | 286701.9374 | 0 | 145121.5314 | 0 | 677628.2262 | 1763049.6439 | 1203317.609 | 5381503.7515 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 33285407.1667 | 73365275.1768 | 749.8942 | 0.63723 | 52234.7179 | 115131.9685 | 1064.8754 | 2347.1209
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 2.5318 | 0.23459 | 4 | 37172.8431 | 79886.1473 | 757.8187 | 1628.5872 | 157.2962 | 0 | 70.083 | 916441.7529 | 82915.3282 | 700123.4352 | 383562.6667 | 0 | 169627.9719 | 0 | 878541.7505 | 2285785.421 | 1560095.518 | 6977093.8444 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 34880997.2597 | 74960865.2698 | 1000 | 0.93835 | 37172.8431 | 79886.1473 | 757.8187 | 1628.5872
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7259 | 3.5315 | 0.33165 | 4 | 27761.6323 | 57974.3211 | 565.9584 | 1181.885 | 160.601 | 0 | 68.0896 | 1157731.1555 | 104666.9304 | 913698.2685 | 505111.5091 | 0 | 200188.8466 | 0 | 1123744.7169 | 2923753.2417 | 1995521.6646 | 8924416.3332 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 36828319.7484 | 76908187.7586 | 1333.5214 | 1.3266 | 27761.6323 | 57974.3211 | 565.9584 | 1181.885
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5368 | 4.9091 | 0.46602 | 4 | 21095.0098 | 42596.1669 | 430.0503 | 868.3805 | 163.6933 | 0 | 88.2799 | 1459598.7057 | 131807.1944 | 1189150.0616 | 668592.6267 | 0 | 237625.2677 | 0 | 1437841.8039 | 3740969.4318 | 2553288.5065 | 11418873.5983 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 39322777.0136 | 79402645.0237 | 1778.2794 | 1.8641 | 21095.0098 | 42596.1669 | 430.0503 | 868.3805
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2421 | 6.7045 | 0.6409 | 4 | 16530.9572 | 32165.2385 | 337.0059 | 655.7319 | 165.8572 | 0 | 93.0645 | 1818066.1307 | 163942.3553 | 1525895.262 | 882753.3485 | 0 | 282732.52 | 0 | 1822621.9504 | 4742088.4438 | 3236572.803 | 14474672.8136 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 42378576.2288 | 82458444.2389 | 2371.3737 | 2.5636 | 16530.9572 | 32165.2385 | 337.0059 | 655.7319
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1795 | 9.0985 | 0.87376 | 4 | 13223.529 | 24691.2351 | 269.5795 | 503.3642 | 167.5339 | 0 | 97.0531 | 2255229.0149 | 203009.7898 | 1948100.5375 | 1167839.0201 | 0 | 338350.5166 | 0 | 2305886.2628 | 5999443.0534 | 4094743.1602 | 18312601.3553 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 46216504.7705 | 86296372.7806 | 3162.2777 | 3.495 | 13223.529 | 24691.2351 | 269.5795 | 503.3642
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6648 | 12.2448 | 1.1801 | 4 | 10798.7399 | 19289.1932 | 220.1469 | 393.2363 | 168.8105 | 0 | 92.8734 | 2781925.2771 | 249921.0804 | 2470559.1776 | 1542121.5122 | 0 | 404787.8123 | 0 | 2905232.7952 | 7558819.788 | 5159049.8235 | 23072417.2663 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 50976320.6815 | 91056188.6916 | 4216.965 | 4.7206 | 10798.7399 | 19289.1932 | 220.1469 | 393.2363
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.2032 | 16.3889 | 1.5833 | 4 | 8986.3908 | 15315.0337 | 183.1997 | 312.2177 | 169.7861 | 0 | 91.2764 | 3419352.559 | 306493.6812 | 3119418.9201 | 2034778.0198 | 0 | 485583.9336 | 0 | 3652594.5743 | 9503301.8323 | 6486198.7738 | 29007722.2942 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 56911625.7094 | 96991493.7195 | 5623.4133 | 6.3331 | 8986.3908 | 15315.0337 | 183.1997 | 312.2177
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2432 | 21.7468 | 2.1047 | 4 | 7624.9087 | 12385.6951 | 155.4441 | 252.4991 | 170.5159 | 0 | 97.3216 | 4178353.6075 | 373605.9017 | 3911564.5802 | 2671534.2972 | 0 | 581222.6782 | 0 | 4569349.6153 | 11888510.3964 | 8114152.63 | 36288293.7064 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 64192197.1216 | 104272065.1317 | 7498.9421 | 8.4187 | 7624.9087 | 12385.6951 | 155.4441 | 252.4991
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.2527 | 28.5274 | 2.7642 | 4 | 6599.2913 | 10224.1583 | 134.5355 | 208.4333 | 171.0101 | 0 | 111.7475 | 5065769.8222 | 451773.0593 | 4860083.8626 | 3479065.1298 | 0 | 692952.574 | 0 | 5674361.3347 | 14763524.2213 | 10076408.6411 | 45063938.6451 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 72967842.0603 | 113047710.0704 | 10000 | 11.0569 | 6599.2913 | 10224.1583 | 134.5355 | 208.4333
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.4884 | 36.7783 | 3.5648 | 4 | 5834.8521 | 8645.6789 | 118.9514 | 176.2539 | 171.1915 | 0 | 109.5947 | 6067795.3154 | 539697.4495 | 5955341.3876 | 4469832.7766 | 0 | 820520.7795 | 0 | 6962743.2063 | 18115629.5679 | 12364289.419 | 55295849.9018 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 83199753.317 | 123279621.3271 | 13335.2143 | 14.2591 | 5834.8521 | 8645.6789 | 118.9514 | 176.2539
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.671 | 46.2031 | 4.4747 | 4 | 5279.5489 | 7518.7766 | 107.6307 | 153.2804 | 170.9458 | 0 | 120.9314 | 7136753.574 | 633149.0642 | 7147764.0745 | 5623534.6826 | 0 | 959969.8566 | 0 | 8385456.7883 | 21817238.4693 | 14890713.5547 | 66594580.0643 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 94498483.4795 | 134578351.4896 | 17782.7941 | 17.899 | 5279.5489 | 7518.7766 | 107.6307 | 153.2804
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4569 | 55.9692 | 5.4156 | 4 | 4890.0559 | 6740.2692 | 99.6904 | 137.4095 | 170.2463 | 0 | 115.6514 | 8180645.8559 | 724104.2423 | 8332843.1392 | 6857278.6861 | 0 | 1097101.1352 | 0 | 9824869.4929 | 25562295.0628 | 17446791.633 | 78025929.2475 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 105929832.6627 | 146009700.6729 | 23713.7371 | 21.6623 | 4890.0559 | 6740.2692 | 99.6904 | 137.4095
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1398 | 60.5676 | 6.0123 | 4 | 4609.2067 | 6275.7921 | 93.9649 | 127.9405 | 169.7633 | 0 | 149.1158 | 8653945.7186 | 765252.5226 | 8876177.562 | 7456701.8766 | 0 | 1027563.0235 | 0 | 10444059.8743 | 27173301.4216 | 18546336.5757 | 82943338.5748 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 110847241.99 | 150927110.0001 | 31622.7766 | 24.0491 | 4609.2067 | 6275.7921 | 93.9649 | 127.9405
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2406 | 65.2283 | 6.5909 | 4 | 4395.1695 | 5915.4371 | 89.6015 | 120.5942 | 169.2118 | 0 | 172.9034 | 9123377.6592 | 806012.0722 | 9418512.0469 | 8075899.758 | 0 | 978456.5393 | 0 | 11076880.6495 | 28819771.2692 | 19670086.0783 | 87968996.0726 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 115872899.4878 | 155952767.4979 | 42169.6503 | 26.3637 | 4395.1695 | 5915.4371 | 89.6015 | 120.5942
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.2667 | 68.5566 | 7.0503 | 4 | 4230.5687 | 5651.7882 | 86.2459 | 115.2193 | 168.8221 | 0 | 175.35 | 9452812.0809 | 834585.9781 | 9801063.3734 | 8522287.3775 | 0 | 900085.7232 | 0 | 11509225.4679 | 29944643.8007 | 20437834.6949 | 91402538.4964 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 119306441.9116 | 159386309.9218 | 56234.1325 | 28.201 | 4230.5687 | 5651.7882 | 86.2459 | 115.2193
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.6781 | 71.168 | 7.4251 | 4 | 4105.8593 | 5455.3291 | 83.7035 | 111.2143 | 168.4937 | 0 | 203.3818 | 9708120.0803 | 856713.9162 | 10098606.9426 | 8877264.8535 | 0 | 822319.4052 | 0 | 11841579.8271 | 30809361.6681 | 21028022.4076 | 94041989.1005 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 121945892.5157 | 162025760.5258 | 74989.4209 | 29.7005 | 4105.8593 | 5455.3291 | 83.7035 | 111.2143
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6887 | 73.1794 | 7.7239 | 4 | 4011.5255 | 5308.7851 | 81.7804 | 108.2268 | 168.2271 | 0 | 205.8169 | 9902968.39 | 873592.2238 | 10326302.1082 | 9153944.0587 | 0 | 749813.6383 | 0 | 12092581.9634 | 31462417.7391 | 21473746.595 | 96035366.7164 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 123939270.1316 | 164019138.1417 | 100000 | 30.8958 | 4011.5255 | 5308.7851 | 81.7804 | 108.2268
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.5138 | 74.6973 | 7.9571 | 4 | 3940.2487 | 5199.4966 | 80.3273 | 105.9988 | 168.0179 | 0 | 206.8979 | 10049002.8012 | 886236.8326 | 10497295.9007 | 9364732.2223 | 0 | 684809.2114 | 0 | 12278010.0176 | 31944863.4996 | 21803025.7398 | 97507976.2251 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 125411879.6403 | 165491747.6504 | 133352.1432 | 31.8284 | 3940.2487 | 5199.4966 | 80.3273 | 105.9988
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.4218 | 75.8398 | 8.1372 | 4 | 3886.4363 | 5117.8185 | 79.2303 | 104.3337 | 167.8556 | 0 | 240.294 | 10158376.1696 | 895704.1507 | 10625551.6426 | 9524321.0545 | 0 | 628915.9627 | 0 | 12414818.9023 | 32300812.1542 | 22045968.0105 | 98594468.0471 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 126498371.4623 | 166578239.4724 | 177827.941 | 32.5487 | 3886.4363 | 5117.8185 | 79.2303 | 104.3337
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.5903 | 76.6858 | 8.2742 | 4 | 3845.8426 | 5056.8309 | 78.4027 | 103.0903 | 167.7328 | 0 | 223.358 | 10239055.8752 | 902686.1572 | 10720262.6155 | 9643137.0066 | 0 | 581759.9711 | 0 | 12513891.634 | 32558579.0796 | 22221899.2337 | 99381271.5729 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 127285174.9881 | 167365042.9983 | 237137.3706 | 33.0968 | 3845.8426 | 5056.8309 | 78.4027 | 103.0903
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1808 | 77.3029 | 8.3772 | 4 | 3815.2419 | 5011.3371 | 77.7789 | 102.1629 | 167.6418 | 0 | 217.2733 | 10297754.5584 | 907765.0826 | 10789224.1073 | 9730196.671 | 0 | 542599.5421 | 0 | 12584340.5849 | 32741872.7988 | 22347000.9634 | 99940754.3085 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 127844657.7238 | 167924525.7339 | 316227.766 | 33.5089 | 3815.2419 | 5011.3371 | 77.7789 | 102.1629
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3406 | 77.7511 | 8.4542 | 4 | 3792.1894 | 4977.3894 | 77.3089 | 101.4708 | 167.5748 | 0 | 220.4268 | 10340305.9353 | 911446.4122 | 10839243.57 | 9793638.9168 | 0 | 510659.0494 | 0 | 12634164.6146 | 32871504.7038 | 22435477.4022 | 100336440.6044 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 128240344.0196 | 168320212.0297 | 421696.5034 | 33.817 | 3792.1894 | 4977.3894 | 77.3089 | 101.4708
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2102 | 78.0862 | 8.5124 | 4 | 3774.8345 | 4951.9338 | 76.9551 | 100.9519 | 167.5244 | 0 | 203.6258 | 10372071.9824 | 914194.4071 | 10876600.3249 | 9841182.2089 | 0 | 485394.8116 | 0 | 12670883.0566 | 32967038.5578 | 22500681.2206 | 100628046.5698 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 128531949.985 | 168611817.9951 | 562341.3252 | 34.0497 | 3774.8345 | 4951.9338 | 76.9551 | 100.9519
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.824 | 78.3221 | 8.5551 | 4 | 3761.7769 | 4933.005 | 76.6889 | 100.566 | 167.4886 | 0 | 249.3308 | 10394413.8645 | 916127.019 | 10902882.2248 | 9874720.4774 | 0 | 465059.7761 | 0 | 12695749.3112 | 33031735.4513 | 22544838.1798 | 100825526.3043 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 128729429.7195 | 168809297.7296 | 749894.2093 | 34.2204 | 3761.7769 | 4933.005 | 76.6889 | 100.566
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.287 | 78.4999 | 8.5873 | 4 | 3751.9581 | 4918.7911 | 76.4887 | 100.2762 | 167.4615 | 0 | 234.4653 | 10411232.8155 | 917581.8204 | 10922671.5284 | 9900019.1454 | 0 | 449357.7977 | 0 | 12714336.6119 | 33080095.7951 | 22577845.1082 | 100973140.6226 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 128877044.0378 | 168956912.048 | 1000000 | 34.3493 | 3751.9581 | 4918.7911 | 76.4887 | 100.2762
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6056 | 78.622 | 8.6107 | 4 | 3744.5786 | 4908.2489 | 76.3383 | 100.0613 | 167.4428 | 0 | 234.7839 | 10422780.8613 | 918580.6669 | 10936261.1862 | 9917420.0601 | 0 | 436846.9704 | 0 | 12726437.0005 | 33111578.5241 | 22599332.7176 | 101069237.987 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 128973141.4022 | 169053009.4123 | 1333521.4322 | 34.4426 | 3744.5786 | 4908.2489 | 76.3383 | 100.0613
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8567 | 78.7182 | 8.6286 | 4 | 3739.0348 | 4900.2871 | 76.2253 | 99.899 | 167.428 | 0 | 246.2453 | 10431875.3973 | 919367.2783 | 10946964.7966 | 9931136.5595 | 0 | 427474.6741 | 0 | 12736159.2953 | 33136873.9408 | 22616597.3592 | 101146449.3011 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129050352.7163 | 169130220.7264 | 1778279.41 | 34.5143 | 3739.0348 | 4900.2871 | 76.2253 | 99.899
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0271 | 78.7834 | 8.6415 | 4 | 3734.8717 | 4894.3901 | 76.1404 | 99.7788 | 167.4179 | 0 | 232.0854 | 10438037.6882 | 919900.2621 | 10954217.98 | 9940441.2363 | 0 | 420065.7611 | 0 | 12742338.5418 | 33152951.0728 | 22627570.3322 | 101195522.8746 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129099426.2898 | 169179294.2999 | 2371373.7057 | 34.566 | 3734.8717 | 4894.3901 | 76.1404 | 99.7788
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1586 | 78.8337 | 8.6513 | 4 | 3731.7463 | 4889.9504 | 76.0767 | 99.6883 | 167.4102 | 0 | 239.0522 | 10442790.8866 | 920311.3666 | 10959812.9614 | 9947621.6786 | 0 | 414505.921 | 0 | 12747166.6975 | 33165512.9436 | 22636144.0671 | 101233866.5225 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129137769.9377 | 169217637.9478 | 3162277.6602 | 34.6052 | 3731.7463 | 4889.9504 | 76.0767 | 99.6883
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2512 | 78.8691 | 8.6585 | 4 | 3729.4005 | 4886.6454 | 76.0289 | 99.6209 | 167.4047 | 0 | 233.7914 | 10446135.6279 | 920600.6507 | 10963750.227 | 9952677.7371 | 0 | 410208.1225 | 0 | 12750415.2224 | 33173964.9389 | 22641912.7276 | 101259665.2542 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129163568.6694 | 169243436.6795 | 4216965.0343 | 34.6339 | 3729.4005 | 4886.6454 | 76.0289 | 99.6209
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3413 | 78.9035 | 8.6645 | 4 | 3727.6403 | 4884.0796 | 75.993 | 99.5686 | 167.3994 | 0 | 262.1205 | 10449388.6363 | 920881.9988 | 10967579.6489 | 9957592.6532 | 0 | 407284.2961 | 0 | 12754063.621 | 33183457.3236 | 22648391.4752 | 101288639.653 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129192543.0683 | 169272411.0784 | 5623413.2519 | 34.658 | 3727.6403 | 4884.0796 | 75.993 | 99.5686
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3903 | 78.9223 | 8.6684 | 4 | 3726.3196 | 4882.2329 | 75.9661 | 99.5309 | 167.3965 | 0 | 256.3034 | 10451159.6062 | 921035.1666 | 10969664.4819 | 9960271.9857 | 0 | 404794.1592 | 0 | 12755700.9058 | 33187717.2029 | 22651298.9304 | 101301642.4386 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129205545.8539 | 169285413.864 | 7498942.0933 | 34.6738 | 3726.3196 | 4882.2329 | 75.9661 | 99.5309
1 | 6600 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4339 | 78.9389 | 8.6716 | 4 | 3725.3289 | 4880.8195 | 75.9459 | 99.5021 | 167.3939 | 0 | 255.4167 | 10452730.9966 | 921171.0725 | 10971514.3989 | 9962648.3356 | 0 | 403024.7619 | 0 | 12757324.9306 | 33191942.5821 | 22654182.8385 | 101314539.9167 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 129218443.3319 | 169298311.3421 | 10000000 | 34.6865 | 3725.3289 | 4880.8195 | 75.9459 | 99.5021
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2036 | [19 empty] | 100 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0247 | [19 empty] | 133.3521 | 0
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.27521 | 0.0091013 | 4 | 820173.7587 | 1943913.8764 | 16720.3514 | 39629.3137 | 113.6649 | 0 | 51.7607 | 157646.3904 | 10630.7131 | 122132.5906 | 74559.6985 | 0 | 74692.8392 | 0 | 171468.2704 | 446125.2665 | 304489.6614 | 1361745.43 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 29858539.3525 | 70768454.0727 | 177.8279 | 0.036405 | 820173.7587 | 1943913.8764 | 16720.3514 | 39629.3137
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.43017 | 0.021821 | 4 | 347819.9462 | 816524.9316 | 7090.7801 | 16645.9652 | 124.9505 | 0 | 260.848 | 228882.1639 | 16547.2509 | 173220.7966 | 96695.0132 | 0 | 85809.3075 | 0 | 234450.2675 | 609991.5037 | 416331.7353 | 1861928.0385 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 30358721.9609 | 71268636.6812 | 237.1374 | 0.087283 | 347819.9462 | 816524.9316 | 7090.7801 | 16645.9652
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.63823 | 0.041251 | 4 | 187704.793 | 435638.8426 | 3826.6161 | 8881.0871 | 134.3312 | 0 | 337.7694 | 316033.4421 | 24293.3884 | 235968.4583 | 126023.0896 | 0 | 96808.94 | 0 | 311659.6542 | 810874.49 | 553438.5012 | 2475099.9637 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 30971893.8862 | 71881808.6064 | 316.2278 | 0.165 | 187704.793 | 435638.8426 | 3826.6161 | 8881.0871
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9933 | 0.92979 | 0.070241 | 4 | 113059.484 | 258665.1637 | 2304.8705 | 5273.2392 | 142.5133 | 0 | 442.7488 | 427414.6957 | 34786.84 | 317055.6868 | 165822.6511 | 0 | 110313.2897 | 0 | 411603.3337 | 1070907.4429 | 730916.3347 | 3268820.2747 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 31765614.1971 | 72675528.9173 | 421.6965 | 0.28096 | 113059.484 | 258665.1637 | 2304.8705 | 5273.2392
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 1.332 | 0.11251 | 4 | 72860.8528 | 163761.5041 | 1485.367 | 3338.4998 | 149.3718 | 0 | 72.6204 | 568379.0725 | 48884.2399 | 420578.6613 | 222084.9505 | 0 | 126557.6411 | 0 | 540728.9805 | 1406865.8884 | 960214.8771 | 4294294.3113 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 32791088.2338 | 73701002.954 | 562.3413 | 0.45005 | 72860.8528 | 163761.5041 | 1485.367 | 3338.4998
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.13 | 1.8674 | 0.17116 | 4 | 49754.3375 | 109507.6786 | 1014.3095 | 2232.4621 | 154.936 | 0 | 77.5433 | 740644.0693 | 67086.2954 | 548784.386 | 295537.4367 | 0 | 145455.8175 | 0 | 701028.1219 | 1823931.3727 | 1244870.6399 | 5567338.1395 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 34064132.0619 | 74974046.7822 | 749.8942 | 0.68465 | 49754.3375 | 109507.6786 | 1014.3095 | 2232.4621
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7574 | 2.6815 | 0.25054 | 4 | 35665.2518 | 76486.352 | 727.0844 | 1559.2777 | 159.44 | 0 | 72.5161 | 954138.5063 | 86317.1851 | 733046.7869 | 394591.157 | 0 | 171416.0347 | 0 | 912408.7712 | 2373900.462 | 1620235.8441 | 7246054.7472 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 35742848.6696 | 76652763.3899 | 1000 | 1.0022 | 35665.2518 | 76486.352 | 727.0844 | 1559.2777
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.889 | 3.7274 | 0.35269 | 4 | 26755.304 | 55753.7864 | 545.4431 | 1136.6163 | 162.7682 | 0 | 69.7267 | 1202516.3206 | 108698.3706 | 954028.0422 | 518767.6129 | 0 | 202032.8678 | 0 | 1164556.8535 | 3029938.0494 | 2067994.9777 | 9248533.0947 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 37745327.0172 | 78655241.7374 | 1333.5214 | 1.4108 | 26755.304 | 55753.7864 | 545.4431 | 1136.6163
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7459 | 5.169 | 0.49405 | 4 | 20399.3965 | 41100.8385 | 415.8693 | 837.8962 | 165.8885 | 0 | 83.3278 | 1513600.4229 | 136654.4867 | 1239259.1223 | 685874.7765 | 0 | 239675.7208 | 0 | 1487875.1664 | 3871145.9777 | 2642136.6739 | 11816222.3471 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 40313016.2696 | 81222930.9898 | 1778.2794 | 1.9762 | 20399.3965 | 41100.8385 | 415.8693 | 837.8962
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5199 | 7.0526 | 0.6784 | 4 | 16018.685 | 31094.6506 | 326.5626 | 633.9065 | 168.0757 | 0 | 81.5898 | 1884154.6609 | 169856.6709 | 1588967.2242 | 905426.2756 | 0 | 285319.5731 | 0 | 1885152.5178 | 4904780.1534 | 3347613.2378 | 14971270.3136 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 43468064.2361 | 84377978.9563 | 2371.3737 | 2.7136 | 16018.685 | 31094.6506 | 326.5626 | 633.9065
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5279 | 9.5539 | 0.92309 | 4 | 12841.0056 | 23920.5713 | 261.7813 | 487.6532 | 169.7645 | 0 | 98.1377 | 2334381.2777 | 210070.1208 | 2025721.3862 | 1196485.2819 | 0 | 341016.815 | 0 | 2381993.2038 | 6197457.7022 | 4229892.2268 | 18917018.0143 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 47413811.9367 | 88323726.657 | 3162.2777 | 3.6924 | 12841.0056 | 23920.5713 | 261.7813 | 487.6532
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.14 | 12.8581 | 1.2463 | 4 | 10498.1339 | 18704.4905 | 214.0187 | 381.3163 | 171.0575 | 0 | 72.3816 | 2879769.2216 | 258618.4929 | 2569060.5001 | 1580552.9615 | 0 | 408486.1953 | 0 | 3001630.0748 | 7809625.7357 | 5330230.0364 | 23837973.2182 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 52334767.1406 | 93244681.8608 | 4216.965 | 4.9851 | 10498.1339 | 18704.4905 | 214.0187 | 381.3163
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.8022 | 17.1885 | 1.6699 | 4 | 8748.8831 | 14873.5045 | 178.3578 | 303.2165 | 172.0409 | 0 | 87.1431 | 3536693.6861 | 316886.0778 | 3240590.3959 | 2083605.0656 | 0 | 489529.114 | 0 | 3770248.6924 | 9809413.7131 | 6695126.4225 | 29942093.1674 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 58438887.0898 | 99348801.81 | 5623.4133 | 6.6796 | 8748.8831 | 14873.5045 | 178.3578 | 303.2165
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.0131 | 22.7927 | 2.2181 | 4 | 7431.5711 | 12042.5116 | 151.5026 | 245.5029 | 172.7767 | 0 | 92.7486 | 4319900.2181 | 386094.4495 | 4061349.0008 | 2734535.6348 | 0 | 585850.8295 | 0 | 4714214.7517 | 12265419.7656 | 8371401.0192 | 37438765.6693 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 65935559.5917 | 106845474.3119 | 7498.9421 | 8.8724 | 7431.5711 | 12042.5116 | 151.5026 | 245.5029
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.2079 | 29.8668 | 2.9099 | 4 | 6439.1734 | 9953.9179 | 131.2713 | 202.9241 | 173.2678 | 0 | 103.1033 | 5233537.5233 | 466517.8319 | 5041784.0829 | 3558011.4505 | 0 | 697967.6208 | 0 | 5849149.2187 | 15218286.4415 | 10386793.2008 | 46452047.3703 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 74948841.2927 | 115858756.013 | 10000 | 11.6395 | 6439.1734 | 9953.9179 | 131.2713 | 202.9241
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.6138 | 38.4418 | 3.7466 | 4 | 5699.8125 | 8429.5978 | 116.1984 | 171.8488 | 173.4308 | 0 | 88.2093 | 6261672.9825 | 556672.0285 | 6169883.8271 | 4565077.6757 | 0 | 825369.0094 | 0 | 7167683.4541 | 18648842.0534 | 12728217.8968 | 56923418.9275 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 85420212.85 | 126330127.5702 | 13335.2143 | 14.9865 | 5699.8125 | 8429.5978 | 116.1984 | 171.8488
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9576 | 48.2123 | 4.6951 | 4 | 5162.7697 | 7341.0874 | 105.25 | 149.658 | 173.1494 | 0 | 98.4929 | 7356263.2851 | 652298.9944 | 7395365.2129 | 5735642.9807 | 0 | 964736.7748 | 0 | 8620679.8267 | 22429240.5644 | 15308417.56 | 68462645.199 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 96959439.1214 | 137869353.8416 | 17782.7941 | 18.7805 | 5162.7697 | 7341.0874 | 105.25 | 149.658
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2662 | 58.4858 | 5.6841 | 4 | 4786.3592 | 6585.6725 | 97.5764 | 134.2578 | 172.3836 | 0 | 128.7605 | 8440981.9523 | 746744.3477 | 8631259.6288 | 7007077.5149 | 0 | 1109108.9448 | 0 | 10114717.2315 | 26316419.4226 | 17961497.0043 | 80327806.0469 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 108824599.9693 | 149734514.6895 | 23713.7371 | 22.7364 | 4786.3592 | 6585.6725 | 97.5764 | 134.2578
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1841 | 63.3077 | 6.3051 | 4 | 4517.0501 | 6139.1509 | 92.0862 | 125.1549 | 171.8606 | 0 | 104.7531 | 8931123.1697 | 789325.2901 | 9195997.3251 | 7623695.962 | 0 | 1040645.9679 | 0 | 10756507.2087 | 27986225.2941 | 19101173.8227 | 85424694.0402 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 113921487.9626 | 154831402.6829 | 31622.7766 | 25.2203 | 4517.0501 | 6139.1509 | 92.0862 | 125.1549
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3944 | 68.1497 | 6.905 | 4 | 4311.0245 | 5792.2038 | 87.8861 | 118.0819 | 171.2896 | 0 | 156.3646 | 9412781.7494 | 831115.19 | 9754494.7953 | 8253535.3429 | 0 | 991064.0378 | 0 | 11404766.535 | 29672863.0848 | 20252338.7717 | 90572959.5068 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 119069753.4293 | 159979668.1495 | 42169.6503 | 27.6198 | 4311.0245 | 5792.2038 | 87.8861 | 118.0819
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3667 | 71.5431 | 7.375 | 4 | 4153.0714 | 5539.8413 | 84.666 | 112.9372 | 170.8838 | 0 | 177.5979 | 9744570.1254 | 859871.9414 | 10141161.6304 | 8700150.8638 | 0 | 909981.6284 | 0 | 11838737.1139 | 30801965.5115 | 21022974.3787 | 94019413.1937 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 122516207.1161 | 163426121.8364 | 56234.1325 | 29.5001 | 4153.0714 | 5539.8413 | 84.666 | 112.9372
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7197 | 74.1989 | 7.7576 | 4 | 4033.3933 | 5351.7669 | 82.2262 | 109.103 | 170.5433 | 0 | 190.0864 | 10001151.7222 | 882094.0714 | 10441234.4599 | 9054433.4812 | 0 | 829955.8902 | 0 | 12171459.1537 | 31667640.0084 | 21613815.0107 | 96661783.7977 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 125158577.7201 | 166068492.4404 | 74989.4209 | 31.0306 | 4033.3933 | 5351.7669 | 82.2262 | 109.103
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.665 | 76.2367 | 8.0617 | 4 | 3942.86 | 5211.5065 | 80.3805 | 106.2436 | 170.2683 | 0 | 214.9173 | 10196254.7124 | 898982.3211 | 10670006.9647 | 9329514.4603 | 0 | 755462.528 | 0 | 12421586.1847 | 32318419.235 | 22057985.205 | 98648211.6111 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 127145005.5335 | 168054920.2537 | 100000 | 32.2469 | 3942.86 | 5211.5065 | 80.3805 | 106.2436
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4498 | 77.7784 | 8.2991 | 4 | 3874.4495 | 5106.8132 | 78.9859 | 104.1093 | 170.0522 | 0 | 205.8665 | 10342893.6565 | 911670.2767 | 10842286.2246 | 9539649.9907 | 0 | 689103.6464 | 0 | 12606985.48 | 32800790.1708 | 22387213.2804 | 100120592.7262 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 128617386.6486 | 169527301.3689 | 133352.1432 | 33.1963 | 3874.4495 | 5106.8132 | 78.9859 | 104.1093
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3197 | 78.9361 | 8.482 | 4 | 3822.7949 | 5028.5761 | 77.9328 | 102.5143 | 169.8851 | 0 | 125.5258 | 10452463.4867 | 921147.9363 | 10971199.4709 | 9698368.0445 | 0 | 632069.4246 | 0 | 12743346.8615 | 33155574.5138 | 22629360.8846 | 101203530.6229 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 129700324.5454 | 170610239.2656 | 177827.941 | 33.9281 | 3822.7949 | 5028.5761 | 77.9328 | 102.5143
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.4392 | 79.7847 | 8.6205 | 4 | 3783.8234 | 4970.2346 | 77.1384 | 101.325 | 169.76 | 0 | 125.5282 | 10532497.8304 | 928069.2652 | 11065461.9141 | 9815305.6859 | 0 | 583729.0242 | 0 | 12840774.8508 | 33409062.1566 | 22802371.4095 | 101977272.1367 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 130474066.0591 | 171383980.7794 | 237137.3706 | 34.4821 | 3783.8234 | 4970.2346 | 77.1384 | 101.325
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0056 | 80.4087 | 8.725 | 4 | 3754.442 | 4926.6489 | 76.5394 | 100.4364 | 169.6665 | 0 | 125.5495 | 10591184.2645 | 933143.6137 | 11134633.9735 | 9901650.4869 | 0 | 543842.5763 | 0 | 12910737.4168 | 33591090.4021 | 22926609.4273 | 102532892.1612 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 131029686.0836 | 171939600.8038 | 316227.766 | 34.8999 | 3754.442 | 4926.6489 | 76.5394 | 100.4364
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.1381 | 80.858 | 8.8027 | 4 | 3732.3056 | 4894.1597 | 76.0881 | 99.7741 | 169.5983 | 0 | 157.3909 | 10633365.8617 | 936790.4354 | 11184379.6122 | 9964034.8263 | 0 | 511191.2028 | 0 | 12959607.156 | 33718239.4389 | 23013391.2576 | 102920999.7908 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 131417793.7133 | 172327708.4335 | 421696.5034 | 35.2109 | 3732.3056 | 4894.1597 | 76.0881 | 99.7741
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.9734 | 81.1884 | 8.861 | 4 | 3715.6384 | 4869.8509 | 75.7483 | 99.2785 | 169.5478 | 0 | 162.7398 | 10664347.3564 | 939468.7214 | 11220931.26 | 10010027.9618 | 0 | 485167.7917 | 0 | 12994777.8056 | 33809746.2547 | 23075846.5397 | 103200313.6912 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 131697107.6137 | 172607022.3339 | 562341.3252 | 35.444 | 3715.6384 | 4869.8509 | 75.7483 | 99.2785
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5802 | 81.4279 | 8.9043 | 4 | 3703.0969 | 4851.6956 | 75.4926 | 98.9084 | 169.5109 | 0 | 161.4472 | 10686779.3865 | 941407.8039 | 11247403.9937 | 10043423.6628 | 0 | 464528.3193 | 0 | 13019581.8348 | 33874281.2508 | 23119893.0005 | 103397299.2523 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 131894093.1747 | 172804007.895 | 749894.2093 | 35.6172 | 3703.0969 | 4851.6956 | 75.4926 | 98.9084
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0212 | 81.6017 | 8.9365 | 4 | 3693.6654 | 4838.131 | 75.3004 | 98.6318 | 169.484 | 0 | 172.6704 | 10703044.2567 | 942813.7182 | 11266602.6844 | 10067688.7835 | 0 | 448330.1241 | 0 | 13037107.031 | 33919878.2164 | 23151013.8665 | 103536478.6807 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132033272.6032 | 172943187.3234 | 1000000 | 35.7459 | 3693.6654 | 4838.131 | 75.3004 | 98.6318
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.3501 | 81.7312 | 8.9606 | 4 | 3686.5763 | 4827.9598 | 75.1558 | 98.4245 | 169.4639 | 0 | 177.846 | 10715155.9189 | 943860.6003 | 11280901.209 | 10085784.7031 | 0 | 435851.7916 | 0 | 13050006.1469 | 33953439.0699 | 23173919.8386 | 103638919.2782 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132135713.2006 | 173045627.9209 | 1333521.4322 | 35.8424 | 3686.5763 | 4827.9598 | 75.1558 | 98.4245
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5741 | 81.8192 | 8.978 | 4 | 3681.2504 | 4820.4219 | 75.0473 | 98.2708 | 169.4502 | 0 | 169.0446 | 10723388.0977 | 944572.1391 | 11290620.8422 | 10098101.5534 | 0 | 425957.1351 | 0 | 13058229.5093 | 33974834.5721 | 23188522.7085 | 103704226.5575 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132201020.48 | 173110935.2002 | 1778279.41 | 35.912 | 3681.2504 | 4820.4219 | 75.0473 | 98.2708
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.7398 | 81.8843 | 8.991 | 4 | 3677.2506 | 4814.7751 | 74.9657 | 98.1557 | 169.44 | 0 | 175.9293 | 10729476.4315 | 945098.3685 | 11297809.8178 | 10107218.0681 | 0 | 418395.0966 | 0 | 13064219.1352 | 33990418.35 | 23199158.9571 | 103751794.2248 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132248588.1472 | 173158502.8675 | 2371373.7057 | 35.964 | 3677.2506 | 4814.7751 | 74.9657 | 98.1557
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.8714 | 81.936 | 9.001 | 4 | 3674.2477 | 4810.5091 | 74.9045 | 98.0687 | 169.4319 | 0 | 206.9311 | 10734304.4593 | 945515.6613 | 11303510.9855 | 10114450.0434 | 0 | 412775.0674 | 0 | 13069116.9246 | 34003161.3932 | 23207856.346 | 103790690.8805 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132287484.803 | 173197399.5232 | 3162277.6602 | 36.004 | 3674.2477 | 4810.5091 | 74.9045 | 98.0687
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.9614 | 81.9713 | 9.0082 | 4 | 3671.9938 | 4807.3442 | 74.8586 | 98.0042 | 169.4263 | 0 | 161.375 | 10737605.9344 | 945801.0095 | 11307409.6968 | 10119399.1829 | 0 | 408388.331 | 0 | 13072255.6203 | 34011327.6357 | 23213429.9743 | 103815617.3849 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132312411.3073 | 173222326.0275 | 4216965.0343 | 36.0329 | 3671.9938 | 4807.3442 | 74.8586 | 98.0042
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.0345 | 82 | 9.0138 | 4 | 3670.3025 | 4804.947 | 74.8241 | 97.9553 | 169.4218 | 0 | 167.3864 | 10740289.5905 | 946032.9577 | 11310578.9276 | 10123422.1926 | 0 | 405167.6256 | 0 | 13074941.6046 | 34018316.016 | 23218199.6874 | 103836948.602 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132333742.5244 | 173243657.2446 | 5623413.2519 | 36.0553 | 3670.3025 | 4804.947 | 74.8241 | 97.9553
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.0929 | 82.0229 | 9.0181 | 4 | 3669.0335 | 4803.1347 | 74.7982 | 97.9184 | 169.4183 | 0 | 175.6198 | 10742429.7058 | 946217.9266 | 11313106.3361 | 10126630.4988 | 0 | 402795.9553 | 0 | 13077160.3648 | 34024088.7748 | 23222139.7139 | 103854569.2762 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132351363.1986 | 173261277.9188 | 7498942.0933 | 36.0725 | 3669.0335 | 4803.1347 | 74.7982 | 97.9184
1 | 6700 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.1271 | 82.0364 | 9.0211 | 4 | 3668.0815 | 4801.8144 | 74.7788 | 97.8915 | 169.4161 | 0 | 168.3425 | 10743684.8324 | 946326.4061 | 11314588.628 | 10128514.2275 | 0 | 400859.9107 | 0 | 13078249.8619 | 34026923.4226 | 23224074.4193 | 103863221.7086 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 132360015.631 | 173269930.3512 | 10000000 | 36.0843 | 3668.0815 | 4801.8144 | 74.7788 | 97.8915
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.4665 | [19 empty] | 100 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.676 | [19 empty] | 133.3521 | 0
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3834 | 0.29252 | 0.010544 | 4 | 723543.4458 | 1713382.0211 | 14750.4118 | 34929.61 | 115.7179 | 0 | 49.1667 | 166444.556 | 11363.5119 | 128055.3399 | 76873.7284 | 0 | 76108.1582 | 0 | 178949.6648 | 465590.3201 | 317774.9604 | 1421160.2396 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 30516704.7601 | 72264870.3176 | 177.8279 | 0.042177 | 723543.4458 | 1713382.0211 | 14750.4118 | 34929.61
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.4521 | 0.024198 | 4 | 320533.4751 | 751845.5923 | 6534.5084 | 15327.3893 | 126.8323 | 0 | 231.5327 | 239349.5289 | 17514.6037 | 180011.4288 | 99634.3466 | 0 | 86616.2744 | 0 | 243019.2111 | 632286.1373 | 431548.2809 | 1929979.8117 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 31025524.3322 | 72773689.8897 | 237.1374 | 0.096793 | 320533.4751 | 751845.5923 | 6534.5084 | 15327.3893
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.67368 | 0.04531 | 4 | 174756.6448 | 405103.4204 | 3562.6506 | 8258.5812 | 136.4207 | 0 | 334.4673 | 331597.4484 | 25854.6268 | 246037.8633 | 130528.0241 | 0 | 98150.821 | 0 | 324545.8256 | 844401.6647 | 576321.4869 | 2577437.7609 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 31672982.2814 | 73421147.8389 | 316.2278 | 0.18124 | 174756.6448 | 405103.4204 | 3562.6506 | 8258.5812
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0517 | 0.97314 | 0.076028 | 4 | 106803.3225 | 244082.6388 | 2177.3302 | 4975.9547 | 144.495 | 0 | 454.9768 | 445515.9338 | 36805.6928 | 328364.5135 | 171178.6104 | 0 | 110888.0857 | 0 | 426173.6061 | 1108816.3029 | 756789.9106 | 3384532.6558 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 32480077.1764 | 74228242.7339 | 421.6965 | 0.30411 | 106803.3225 | 244082.6388 | 2177.3302 | 4975.9547
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 1.3919 | 0.12119 | 4 | 69190.1058 | 155310.0386 | 1410.5339 | 3166.2052 | 151.405 | 0 | 64.8073 | 592133.6275 | 51846.567 | 434986.584 | 229335.0208 | 0 | 127030.1327 | 0 | 559779.4535 | 1456431.3115 | 994044.2967 | 4445586.9938 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 33541131.5143 | 75289297.0718 | 562.3413 | 0.48477 | 69190.1058 | 155310.0386 | 1410.5339 | 3166.2052
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2421 | 1.9954 | 0.18449 | 4 | 47318.799 | 103892.1193 | 964.6577 | 2117.9814 | 157.0843 | 0 | 79.2905 | 775529.2914 | 70186.6965 | 578701.4752 | 308188.464 | 0 | 147532.6839 | 0 | 733254.0583 | 1907776.6485 | 1302096.7635 | 5823266.0812 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 34918810.6017 | 76666976.1592 | 749.8942 | 0.73795 | 47318.799 | 103892.1193 | 964.6577 | 2117.9814
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8816 | 2.83 | 0.26656 | 4 | 34329.2718 | 73484.5045 | 699.8486 | 1498.081 | 161.5645 | 0 | 70.1603 | 990929.1433 | 89635.9628 | 765345.3189 | 405072.3455 | 0 | 172801.9462 | 0 | 945276.0395 | 2459414.352 | 1678600.8312 | 7507075.9393 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 36602620.4598 | 78350786.0174 | 1000 | 1.0662 | 34329.2718 | 73484.5045 | 699.8486 | 1498.081
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0548 | 3.9308 | 0.37463 | 4 | 25809.033 | 53668.9892 | 526.152 | 1094.1149 | 164.9882 | 0 | 67.9105 | 1248296.1869 | 112817.5409 | 995456.7413 | 532496.4879 | 0 | 203773.4597 | 0 | 1206207.7626 | 3138305.171 | 2141957.7649 | 9579311.1152 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 38674855.6358 | 80423021.1933 | 1333.5214 | 1.4985 | 25809.033 | 53668.9892 | 526.152 | 1094.1149
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9654 | 5.4384 | 0.52302 | 4 | 19750.2094 | 39705.6426 | 402.6347 | 809.4532 | 168.0883 | 0 | 65.9507 | 1568727.068 | 141600.4018 | 1290650.0833 | 703600.7296 | 0 | 241911.053 | 0 | 1539130.8409 | 4004502.729 | 2733155.3968 | 12223278.3025 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 41318822.823 | 83066988.3805 | 1778.2794 | 2.0921 | 19750.2094 | 39705.6426 | 402.6347 | 809.4532
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8022 | 7.4086 | 0.7168 | 4 | 15543.8536 | 30104.4571 | 316.8825 | 613.7201 | 170.2928 | 0 | 75.8156 | 1950743.6645 | 175812.7093 | 1652802.0192 | 928129.6397 | 0 | 287839.4515 | 0 | 1948177.7189 | 5068758.7983 | 3459532.0324 | 15471796.0338 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 44567340.5543 | 86315506.1119 | 2371.3737 | 2.8672 | 15543.8536 | 30104.4571 | 316.8825 | 613.7201
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8984 | 10.0274 | 0.9742 | 4 | 12480.7028 | 23194.1073 | 254.436 | 472.8432 | 171.9976 | 0 | 93.9759 | 2415530.8314 | 217304.6416 | 2105644.7648 | 1226104.7143 | 0 | 344054.8357 | 0 | 2460369.5173 | 6401376.7928 | 4369071.1962 | 19539457.2942 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 48635001.8147 | 90383167.3723 | 3162.2777 | 3.8968 | 12480.7028 | 23194.1073 | 254.436 | 472.8432
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6199 | 13.4833 | 1.3139 | 4 | 10218.2708 | 18161.8414 | 208.3133 | 370.2537 | 173.3019 | 0 | 85.3872 | 2978151.1982 | 267358.5877 | 2668523.1456 | 1618911.4017 | 0 | 412003.0827 | 0 | 3098529.4922 | 8061738.1429 | 5502301.9347 | 24607516.9856 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 53703061.5061 | 95451227.0637 | 4216.965 | 5.2556 | 10218.2708 | 18161.8414 | 208.3133 | 370.2537
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4166 | 18.0078 | 1.7587 | 4 | 8526.5219 | 14460.9695 | 173.8247 | 294.8064 | 174.2936 | 0 | 77.2752 | 3655314.4927 | 327385.3244 | 3363585.577 | 2132808.8385 | 0 | 493473.0541 | 0 | 3889301.2419 | 10119164.0259 | 6906537.3757 | 30887569.9304 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 59983114.4509 | 101731280.0084 | 5623.4133 | 7.0349 | 8526.5219 | 14460.9695 | 173.8247 | 294.8064
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.7831 | 23.8535 | 2.3335 | 4 | 7251.2034 | 11723.8305 | 147.8256 | 239.0061 | 175.0338 | 0 | 101.5455 | 4461580.2776 | 398586.7026 | 4211872.0102 | 2796784.3337 | 0 | 590041.7967 | 0 | 4858957.3971 | 12642010.4379 | 8628431.8912 | 38588264.8469 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 67683809.3674 | 109431974.925 | 7498.9421 | 9.3341 | 7251.2034 | 11723.8305 | 147.8256 | 239.0061
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.1869 | 31.2359 | 3.0589 | 4 | 6289.0002 | 9701.0521 | 128.2098 | 197.7691 | 175.5216 | 0 | 107.1371 | 5402837.8715 | 481387.3396 | 5225854.2043 | 3637262.7485 | 0 | 702967.0032 | 0 | 6025620.5752 | 15677428.712 | 10700167.2349 | 47853525.6893 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 76949070.2098 | 118697235.7673 | 10000 | 12.2355 | 6289.0002 | 9701.0521 | 128.2098 | 197.7691
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.771 | 40.1405 | 3.9323 | 4 | 5573.1286 | 8227.2896 | 113.6158 | 167.7244 | 175.6645 | 0 | 108.1866 | 6457190.1069 | 573778.5355 | 6387041.345 | 4660725.6097 | 0 | 830280.6257 | 0 | 7374516.3269 | 19186978.7612 | 13095507.2575 | 58566018.5683 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 87661563.0888 | 129409728.6463 | 13335.2143 | 15.7293 | 5573.1286 | 8227.2896 | 113.6158 | 167.7244
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.2527 | 50.2445 | 4.9186 | 4 | 5053.4255 | 7175.3995 | 103.0209 | 146.2802 | 175.346 | 0 | 114.3458 | 7575667.8283 | 671426.7809 | 7643718.993 | 5846222.9312 | 0 | 969086.8252 | 0 | 8855388.1098 | 23039903.3719 | 15725207.474 | 70326622.3142 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 99422166.8348 | 141170332.3923 | 17782.7941 | 19.6742 | 5053.4255 | 7175.3995 | 103.0209 | 146.2802
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.6085 | 60.8152 | 5.9422 | 4 | 4689.2988 | 6445.7263 | 95.5977 | 131.4048 | 174.5321 | 0 | 128.2621 | 8679135.7435 | 767441.0129 | 8905194.155 | 7128554.2702 | 0 | 1112085.2559 | 0 | 10371040.0706 | 26983318.8709 | 18416669.5811 | 82363438.9601 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 111458983.4806 | 153207149.0381 | 23713.7371 | 23.7688 | 4689.2988 | 6445.7263 | 95.5977 | 131.4048
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.2233 | 66.0766 | 6.6015 | 4 | 4430.6379 | 6011.6564 | 90.3245 | 122.5557 | 173.9466 | 0 | 142.5401 | 9207783.366 | 813335.4279 | 9516376.2504 | 7788900.3395 | 0 | 1053356.5231 | 0 | 11068103.2437 | 28796934.26 | 19654499.3503 | 87899288.761 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 116994833.2815 | 158742998.839 | 31622.7766 | 26.4059 | 4430.6379 | 6011.6564 | 90.3245 | 122.5557
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5138 | 71.0886 | 7.2217 | 4 | 4232.0531 | 5677.284 | 86.2761 | 115.7391 | 173.3586 | 0 | 159.7033 | 9700401.185 | 856045.1157 | 10089597.6651 | 8427717.05 | 0 | 1002928.5265 | 0 | 11729908.9215 | 30518816.8785 | 20829719.6186 | 93155134.9609 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 122250679.4814 | 163998845.0389 | 42169.6503 | 28.8868 | 4232.0531 | 5677.284 | 86.2761 | 115.7391
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.4324 | 74.5443 | 7.7021 | 4 | 4080.3069 | 5435.3941 | 83.1826 | 110.8079 | 172.937 | 0 | 186.5741 | 10034320.2229 | 884965.7231 | 10480090.7675 | 8874345.4283 | 0 | 919228.2548 | 0 | 12165250.6547 | 31651486.7674 | 21602790.0918 | 96612477.9105 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 125708022.431 | 167456187.9886 | 56234.1325 | 30.8085 | 4080.3069 | 5435.3941 | 83.1826 | 110.8079
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7413 | 77.2474 | 8.0925 | 4 | 3965.3235 | 5255.0443 | 80.8385 | 107.1312 | 172.5839 | 0 | 202.6638 | 10292483.6911 | 907309.0479 | 10783029.8253 | 9228225.2205 | 0 | 837240.0846 | 0 | 12498832.2691 | 32519397.7011 | 22195157.1378 | 99261674.9774 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 128357219.4979 | 170105385.0555 | 74989.4209 | 32.3699 | 3965.3235 | 5255.0443 | 80.8385 | 107.1312
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.6381 | 79.3155 | 8.4019 | 4 | 3878.3374 | 5120.5556 | 79.0652 | 104.3895 | 172.2999 | 0 | 204.3211 | 10488272.2699 | 924244.8222 | 11013363.8848 | 9502219.9675 | 0 | 761077.7878 | 0 | 12748779.7056 | 33169709.6596 | 22639008.412 | 101246676.5094 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 130342221.03 | 172090386.5875 | 100000 | 33.6078 | 3878.3374 | 5120.5556 | 79.0652 | 104.3895
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3723 | 80.8746 | 8.6428 | 4 | 3812.6029 | 5020.1956 | 77.7251 | 102.3435 | 172.0776 | 0 | 235.7487 | 10634924.3184 | 936925.1653 | 11186217.9698 | 9710778.1503 | 0 | 693265.357 | 0 | 12933223.2748 | 33649593.9921 | 22966539.3296 | 102711467.5574 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 131807012.0779 | 173555177.6355 | 133352.1432 | 34.5714 | 3812.6029 | 5020.1956 | 77.7251 | 102.3435
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1808 | 82.0362 | 8.8277 | 4 | 3762.9658 | 4945.2676 | 76.7131 | 100.816 | 171.9073 | 0 | 225.6776 | 10743670.8748 | 946325.1998 | 11314572.144 | 9867186.1807 | 0 | 634781.7492 | 0 | 13067549.0979 | 33999082.2298 | 23205072.2331 | 103778239.7093 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 132873784.2299 | 174621949.7874 | 177827.941 | 35.3109 | 3762.9658 | 4945.2676 | 76.7131 | 100.816
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2808 | 82.8985 | 8.9685 | 4 | 3725.5122 | 4889.2628 | 75.9496 | 99.6742 | 171.7782 | 0 | 217.1906 | 10824113.5576 | 953277.1356 | 11409615.7231 | 9983863.601 | 0 | 585736.096 | 0 | 13165076.3842 | 34252828.2231 | 23378259.0875 | 104552769.8079 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 133648314.3284 | 175396479.886 | 237137.3706 | 35.8738 | 3725.5122 | 4889.2628 | 75.9496 | 99.6742
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8102 | 83.5232 | 9.0738 | 4 | 3697.2721 | 4847.5094 | 75.3739 | 98.823 | 171.6832 | 0 | 237.358 | 10882245.6589 | 958300.1712 | 11478349.9781 | 10068766.9194 | 0 | 544957.3831 | 0 | 13233721.8432 | 34431429.6263 | 23500158.2151 | 105097929.7953 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 134193474.3158 | 175941639.8733 | 316227.766 | 36.2953 | 3697.2721 | 4847.5094 | 75.3739 | 98.823
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.924 | 83.9764 | 9.1525 | 4 | 3675.9932 | 4816.3444 | 74.9401 | 98.1877 | 171.6135 | 0 | 176.3199 | 10924334.2261 | 961936.5132 | 11528141.1254 | 10130552.3845 | 0 | 511746.5445 | 0 | 13282117.2095 | 34557344.4424 | 23586097.6643 | 105482270.11 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 134577814.6305 | 176325980.188 | 421696.5034 | 36.6099 | 3675.9932 | 4816.3444 | 74.9401 | 98.1877
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.725 | 84.3013 | 9.2108 | 4 | 3659.9698 | 4793.1057 | 74.6134 | 97.7139 | 171.563 | 0 | 172.9281 | 10954479.8833 | 964540.8051 | 11563817.3088 | 10174973.2389 | 0 | 484972.4073 | 0 | 13315685.6209 | 34644682.563 | 23645707.7263 | 105748859.5535 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 134844404.074 | 176592569.6316 | 562341.3252 | 36.843 | 3659.9698 | 4793.1057 | 74.6134 | 97.7139
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.3272 | 84.5451 | 9.2547 | 4 | 3647.9117 | 4775.6623 | 74.3676 | 97.3583 | 171.5249 | 0 | 182.5322 | 10977071.6367 | 966492.3963 | 11590561.1717 | 10208352.1126 | 0 | 464082.1333 | 0 | 13340558.1858 | 34709395.8746 | 23689875.8912 | 105946389.4022 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135041933.9227 | 176790099.4803 | 749894.2093 | 37.019 | 3647.9117 | 4775.6623 | 74.3676 | 97.3583
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.7534 | 84.7173 | 9.287 | 4 | 3638.8428 | 4762.6747 | 74.1827 | 97.0936 | 171.4979 | 0 | 209.4225 | 10993022.4154 | 967870.2459 | 11609447.3466 | 10231970.1992 | 0 | 447506.1842 | 0 | 13357428.3926 | 34753288.6922 | 23719833.6411 | 106080367.117 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135175911.6375 | 176924077.1951 | 1000000 | 37.148 | 3638.8428 | 4762.6747 | 74.1827 | 97.0936
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.048 | 84.8363 | 9.3105 | 4 | 3632.0257 | 4753.0284 | 74.0438 | 96.8969 | 171.4791 | 0 | 232.2893 | 11004030.0399 | 968821.0703 | 11622482.5293 | 10248296.5583 | 0 | 434369.3309 | 0 | 13368419.8162 | 34781886.1218 | 23739351.9744 | 106167657.441 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135263201.9615 | 177011367.5191 | 1333521.4322 | 37.2418 | 3632.0257 | 4753.0284 | 74.0438 | 96.8969
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.2797 | 84.9297 | 9.3284 | 4 | 3626.9038 | 4745.7465 | 73.9393 | 96.7485 | 171.4643 | 0 | 249.0264 | 11012677.4051 | 969568.0019 | 11632723.7572 | 10261132.8795 | 0 | 424502.5934 | 0 | 13377235.8084 | 34804823.5252 | 23755007.2235 | 106237671.1941 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135333215.7147 | 177081381.2722 | 1778279.41 | 37.3137 | 3626.9038 | 4745.7465 | 73.9393 | 96.7485
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4501 | 84.9984 | 9.3418 | 4 | 3623.057 | 4740.2961 | 73.8609 | 96.6373 | 171.4534 | 0 | 237.9197 | 11019030.933 | 970116.7899 | 11640248.9437 | 10270572.1783 | 0 | 416940.8717 | 0 | 13383594.7894 | 34821368.2893 | 23766299.365 | 106288172.1602 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135383716.6807 | 177131882.2382 | 2371373.7057 | 37.3673 | 3623.057 | 4740.2961 | 73.8609 | 96.6373
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.5692 | 85.0464 | 9.3516 | 4 | 3620.1688 | 4736.2416 | 73.802 | 96.5547 | 171.4458 | 0 | 217.958 | 11023467.9072 | 970500.0304 | 11645504.4401 | 10277169.6203 | 0 | 411066.987 | 0 | 13387806.5041 | 34832326.307 | 23773778.4373 | 106321620.2333 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135417164.7538 | 177165330.3114 | 3162277.6602 | 37.4063 | 3620.1688 | 4736.2416 | 73.802 | 96.5547
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.6593 | 85.0826 | 9.3589 | 4 | 3618.001 | 4733.1972 | 73.7578 | 96.4926 | 171.44 | 0 | 237.9408 | 11026819.2475 | 970789.4974 | 11649474.1892 | 10282154.6644 | 0 | 406635.9014 | 0 | 13390990.665 | 34840610.8404 | 23779432.8015 | 106346907.8069 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135442452.3274 | 177190617.885 | 4216965.0343 | 37.4357 | 3618.001 | 4733.1972 | 73.7578 | 96.4926
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.713 | 85.1042 | 9.364 | 4 | 3616.3742 | 4730.9685 | 73.7247 | 96.4472 | 171.4366 | 0 | 222.8516 | 11028815.9516 | 970961.9587 | 11651839.4029 | 10285128.6841 | 0 | 403068.4343 | 0 | 13392527.6283 | 34844609.7038 | 23782162.108 | 106359113.8717 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135454658.3923 | 177202823.9498 | 5623413.2519 | 37.4559 | 3616.3742 | 4730.9685 | 73.7247 | 96.4472
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.7667 | 85.1258 | 9.3682 | 4 | 3615.1536 | 4729.2431 | 73.6998 | 96.412 | 171.4331 | 0 | 212.3945 | 11030815.426 | 971134.6585 | 11654207.9475 | 10288103.5966 | 0 | 400598.2961 | 0 | 13394495.3706 | 34849729.3655 | 23785656.3823 | 106374741.043 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135470285.5635 | 177218451.1211 | 7498942.0933 | 37.4729 | 3615.1536 | 4729.2431 | 73.6998 | 96.412
1 | 6800 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.801 | 85.1396 | 9.3712 | 4 | 3614.2378 | 4727.973 | 73.6811 | 96.3861 | 171.4309 | 0 | 202.1537 | 11032089.623 | 971244.7138 | 11655717.3662 | 10290001.0229 | 0 | 398641.4344 | 0 | 13395600.7225 | 34852605.2645 | 23787619.2424 | 106383519.3897 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 135479063.9102 | 177227229.4677 | 10000000 | 37.4848 | 3614.2378 | 4727.973 | 73.6811 | 96.3861
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6862 | [19 empty] | 100 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7528 | [19 empty] | 133.3521 | 0
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.30879 | 0.012032 | 4 | 647765.3891 | 1532784.8401 | 13205.5736 | 31247.8922 | 117.6145 | 0 | 49.3687 | 174707.1441 | 12065.662 | 133543.7158 | 79031.2453 | 0 | 77136.7584 | 0 | 185828.965 | 483488.8481 | 329991.0736 | 1475793.4123 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 31175948.6218 | 73770569.1438 | 177.8279 | 0.048128 | 647765.3891 | 1532784.8401 | 13205.5736 | 31247.8922
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.47454 | 0.026683 | 4 | 296994.0846 | 696078.3584 | 6054.6261 | 14190.4989 | 128.7103 | 0 | 263.3755 | 249967.757 | 18510.8165 | 186882.2535 | 102447.3751 | 0 | 87372.5337 | 0 | 251620.487 | 654664.8926 | 446822.2412 | 1998288.3565 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 31698443.566 | 74293064.0881 | 237.1374 | 0.10673 | 296994.0846 | 696078.3584 | 6054.6261 | 14190.4989
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.70093 | 0.048878 | 4 | 165468.1603 | 383328.4739 | 3373.2923 | 7814.6694 | 138.2276 | 0 | 358.8969 | 343740.2145 | 27116.2891 | 253670.7788 | 133158.3469 | 0 | 98264.5902 | 0 | 333820.5856 | 868532.6877 | 592791.4059 | 2651094.8988 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 32351250.1083 | 74945870.6303 | 316.2278 | 0.19551 | 165468.1603 | 383328.4739 | 3373.2923 | 7814.6694
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.11 | 1.0177 | 0.082111 | 4 | 101091.2608 | 230777.2318 | 2060.8821 | 4704.706 | 146.4741 | 0 | 464.2881 | 464109.2062 | 38938.2067 | 339848.8278 | 176613.518 | 0 | 111393.8294 | 0 | 441052.3994 | 1147527.8709 | 783211.3513 | 3502695.2098 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 33202850.4192 | 75797470.9413 | 421.6965 | 0.32844 | 101091.2608 | 230777.2318 | 2060.8821 | 4704.706
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0654 | 1.4535 | 0.13034 | 4 | 65790.0319 | 147486.8705 | 1341.2188 | 3006.7193 | 153.4357 | 0 | 59.8055 | 616684.9481 | 55034.3121 | 449620.8393 | 236768.8103 | 0 | 127422.4597 | 0 | 579357.2341 | 1507368.6807 | 1028810.0979 | 4601067.3822 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 34301222.5917 | 76895843.1138 | 562.3413 | 0.52137 | 65790.0319 | 147486.8705 | 1341.2188 | 3006.7193
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3347 | 2.1067 | 0.19659 | 4 | 45440.9105 | 99608.6852 | 926.3744 | 2030.6578 | 159.1602 | 0 | 79.0072 | 805616.8754 | 72906.1665 | 604397.3408 | 316201.0605 | 0 | 148452.1739 | 0 | 759553.7106 | 1976202.9492 | 1348799.1197 | 6032129.3965 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 35732284.6059 | 78326905.128 | 749.8942 | 0.78635 | 45440.9105 | 99608.6852 | 926.3744 | 2030.6578
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0131 | 2.9845 | 0.28316 | 4 | 33087.2867 | 70693.8498 | 674.5291 | 1441.1897 | 163.7 | 0 | 80.1329 | 1028632.7397 | 93035.7721 | 798610.0612 | 415884.623 | 0 | 174371.0503 | 0 | 979108.3561 | 2547439.0998 | 1738679.5302 | 7775761.2324 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 37475916.4419 | 80070536.9639 | 1000 | 1.1326 | 33087.2867 | 70693.8498 | 674.5291 | 1441.1897
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2252 | 4.1445 | 0.39774 | 4 | 24904.0527 | 51677.0352 | 507.7028 | 1053.5063 | 167.2862 | 0 | 78.4032 | 1295643.8396 | 117075.8839 | 1038512.9015 | 546500.8129 | 0 | 205453.1545 | 0 | 1249242.771 | 3250273.4353 | 2218378.406 | 9921081.2046 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 39621236.4141 | 82215856.9361 | 1333.5214 | 1.591 | 24904.0527 | 51677.0352 | 507.7028 | 1053.5063
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1675 | 5.7029 | 0.55188 | 4 | 19168.2239 | 38463.5134 | 390.7702 | 784.1307 | 170.272 | 0 | 82.6589 | 1622096.8958 | 146386.4735 | 1340625.045 | 720139.5878 | 0 | 243381.5261 | 0 | 1588325.516 | 4132497.1823 | 2820514.2412 | 12613966.4677 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 42314121.6771 | 84908742.1992 | 1778.2794 | 2.2075 | 19168.2239 | 38463.5134 | 390.7702 | 784.1307
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0922 | 7.7742 | 0.75628 | 4 | 15100.2017 | 29180.5724 | 307.838 | 594.8854 | 172.5101 | 0 | 69.1975 | 2018199.963 | 181843.2486 | 1717750.8258 | 951089.3888 | 0 | 290384.9364 | 0 | 2012114.6614 | 5235109.6075 | 3573069.8779 | 15979562.5094 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 45679717.7188 | 88274338.2409 | 2371.3737 | 3.0251 | 15100.2017 | 29180.5724 | 307.838 | 594.8854
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.2662 | 10.507 | 1.0262 | 4 | 12146.5866 | 22523.1903 | 247.6246 | 459.1657 | 174.2266 | 0 | 101.4215 | 2496601.1376 | 224528.1711 | 2185826.9413 | 1255286.2137 | 0 | 346755.3744 | 0 | 2538509.1568 | 6604680.1063 | 4507829.8851 | 20160016.9863 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 49860172.1958 | 92454792.7179 | 3162.2777 | 4.1049 | 12146.5866 | 22523.1903 | 247.6246 | 459.1657
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0996 | 14.118 | 1.3828 | 4 | 9957.5055 | 17658.2909 | 202.9972 | 359.9881 | 175.5428 | 0 | 72.2162 | 3076681.1507 | 276106.7732 | 2768544.1675 | 1656815.9058 | 0 | 415190.1076 | 0 | 3195401.8609 | 8313780.1749 | 5674325.8005 | 25376845.9411 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 55077001.1506 | 97671621.6726 | 4216.965 | 5.5312 | 9957.5055 | 17658.2909 | 202.9972 | 359.9881
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0326 | 18.8402 | 1.8493 | 4 | 8318.6387 | 14076.8754 | 169.5867 | 286.9761 | 176.543 | 0 | 98.1938 | 3774256.9959 | 337906.6459 | 3487406.0061 | 2181559.0898 | 0 | 497067.0825 | 0 | 4008496.3699 | 10429285.2987 | 7118201.5168 | 31834179.0055 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 61534334.215 | 104128954.737 | 5623.4133 | 7.3972 | 8318.6387 | 14076.8754 | 169.5867 | 286.9761
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.5795 | 24.943 | 2.4502 | 4 | 7087.2504 | 11433.2193 | 144.4832 | 233.0816 | 177.2885 | 0 | 56.1329 | 4605228.43 | 411244.4365 | 4365077.9079 | 2859708.7929 | 0 | 596444.8166 | 0 | 5006704.7097 | 13026418.6383 | 8890798.3868 | 39761626.1186 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 69461781.3281 | 112056401.8501 | 7498.9421 | 9.8009 | 7087.2504 | 11433.2193 | 144.4832 | 233.0816
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1615 | 32.6216 | 3.2088 | 4 | 6151.5425 | 9470.1338 | 125.4075 | 193.0615 | 177.7706 | 0 | 70.3916 | 5572034.7311 | 496237.99 | 5410503.5128 | 3715362.7647 | 0 | 708925.1104 | 0 | 6202195.0025 | 16136839.1514 | 11013724.2997 | 49255822.5626 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 78955977.772 | 121550598.2941 | 10000 | 12.8352 | 6151.5425 | 9470.1338 | 125.4075 | 193.0615
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.9495 | 41.8704 | 4.1201 | 4 | 5456.3883 | 8040.9444 | 111.2359 | 163.9255 | 177.8917 | 0 | 74.6247 | 6653902.9139 | 590978.1634 | 6606315.5189 | 4756399.7829 | 0 | 836572.145 | 0 | 7583225.7244 | 19729997.8014 | 13466128.9104 | 60223520.9603 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 89923676.1698 | 132518296.6919 | 13335.2143 | 16.4804 | 5456.3883 | 8040.9444 | 111.2359 | 163.9255
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5562 | 52.2996 | 5.1422 | 4 | 4953.8747 | 7024.7041 | 100.9914 | 143.2081 | 177.5327 | 0 | 75.4315 | 7794988.5682 | 690534.5975 | 7892824.8346 | 5955635.7345 | 0 | 975520.7272 | 0 | 9090706.7402 | 23652154.1776 | 16143081.2294 | 72195446.6092 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 101895601.8186 | 144490222.3407 | 17782.7941 | 20.5689 | 4953.8747 | 7024.7041 | 100.9914 | 143.2081
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9728 | 63.1716 | 6.2035 | 4 | 4598.1543 | 6314.699 | 93.7396 | 128.7337 | 176.6718 | 0 | 91.739 | 8917440.4588 | 788137.3715 | 9180182.1236 | 7249046.3656 | 0 | 1114882.5948 | 0 | 10627378.6766 | 27650259.3413 | 18871870.1565 | 84399197.0887 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 114099352.2982 | 156693972.8202 | 23713.7371 | 24.8142 | 4598.1543 | 6314.699 | 93.7396 | 128.7337
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.2159 | 68.8534 | 6.9 | 4 | 4349.348 | 5892.6338 | 88.6673 | 120.1293 | 176.0238 | 0 | 149.2397 | 9481964.6923 | 837113.402 | 9834991.979 | 7949318.5189 | 0 | 1064923.318 | 0 | 11375641.645 | 29597086.0953 | 20200619.4193 | 90341659.0697 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 120041814.2792 | 162636434.8013 | 31622.7766 | 27.6 | 4349.348 | 5892.6338 | 88.6673 | 120.1293
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.6138 | 74.0485 | 7.5414 | 4 | 4157.6948 | 5569.7254 | 84.7602 | 113.5464 | 175.4183 | 0 | 107.7324 | 9986688.6505 | 880841.8197 | 10424295.9 | 8598359.4337 | 0 | 1014233.5378 | 0 | 12052723.5433 | 31358714.306 | 21402966.871 | 95718824.0619 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 125418979.2714 | 168013599.7935 | 42169.6503 | 30.1655 | 4157.6948 | 5569.7254 | 84.7602 | 113.5464
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.4935 | 77.57 | 8.0322 | 4 | 4011.7694 | 5337.5222 | 81.7853 | 108.8126 | 174.9802 | 0 | 120.4226 | 10323122.4632 | 909959.8301 | 10819041.3981 | 9045581.231 | 0 | 928248.9369 | 0 | 12490122.0051 | 32496735.381 | 22179689.6386 | 99192500.8839 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 128892656.0934 | 171487276.6154 | 56234.1325 | 32.1286 | 4011.7694 | 5337.5222 | 81.7853 | 108.8126
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.7339 | 80.3083 | 8.4292 | 4 | 3901.1957 | 5164.4974 | 79.5312 | 105.2853 | 174.6161 | 0 | 155.6848 | 10581755.0754 | 932328.3616 | 11123517.0597 | 9397874.6813 | 0 | 844001.7101 | 0 | 12822995.9863 | 33362805.1983 | 22770800.0849 | 101836078.1577 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 131536233.3671 | 174130853.8892 | 74989.4209 | 33.7169 | 3901.1957 | 5164.4974 | 79.5312 | 105.2853
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5741 | 82.402 | 8.7436 | 4 | 3817.5428 | 5035.4265 | 77.8258 | 102.654 | 174.3238 | 0 | 153.7266 | 10777825.3696 | 949277.0218 | 11354915.9169 | 9670497.1034 | 0 | 766118.3596 | 0 | 13072267.1708 | 34011357.6877 | 23213450.4853 | 103815709.115 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 133515864.3245 | 176110484.8465 | 100000 | 34.9743 | 3817.5428 | 5035.4265 | 77.8258 | 102.654
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2601 | 83.9784 | 8.9879 | 4 | 3754.3232 | 4939.0962 | 76.537 | 100.6902 | 174.0955 | 0 | 179.0525 | 10924521.5821 | 961952.6995 | 11528362.8187 | 9877751.2972 | 0 | 696944.2037 | 0 | 13255917.7144 | 34489178.7303 | 23539573.1652 | 105274202.2111 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 134974357.4205 | 177568977.9426 | 133352.1432 | 35.9517 | 3754.3232 | 4939.0962 | 76.537 | 100.6902
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0445 | 85.1582 | 9.1758 | 4 | 3706.5814 | 4867.1018 | 75.5637 | 99.2225 | 173.9199 | 0 | 186.2411 | 11033808.6703 | 971393.1913 | 11657753.7882 | 10033917.7923 | 0 | 637621.8569 | 0 | 13390453.1666 | 34839212.3799 | 23778478.3235 | 106342639.169 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 136042794.3784 | 178637414.9005 | 177827.941 | 36.703 | 3706.5814 | 4867.1018 | 75.5637 | 99.2225
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0855 | 86.0167 | 9.3173 | 4 | 3670.5538 | 4813.4479 | 74.8292 | 98.1286 | 173.7894 | 0 | 231.1093 | 11113063.1624 | 978237.9354 | 11751680.0575 | 10148102.0854 | 0 | 587302.6901 | 0 | 13485570.513 | 35086688.2039 | 23947385.6585 | 107098030.3061 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 136798185.5155 | 179392806.0376 | 237137.3706 | 37.2691 | 3670.5538 | 4813.4479 | 74.8292 | 98.1286
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5935 | 86.6478 | 9.4239 | 4 | 3643.386 | 4773.345 | 74.2754 | 97.3111 | 173.692 | 0 | 219.1237 | 11171181.0803 | 983256.4641 | 11820605.9978 | 10232403.9635 | 0 | 545895.6699 | 0 | 13553803.8385 | 35264217.3203 | 24068552.9283 | 107639917.2627 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 137340072.4721 | 179934692.9942 | 316227.766 | 37.6957 | 3643.386 | 4773.345 | 74.2754 | 97.3111
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.6802 | 87.1008 | 9.5031 | 4 | 3622.9129 | 4743.4524 | 73.858 | 96.7017 | 173.6213 | 0 | 222.5011 | 11212823.0077 | 986851.8769 | 11870017.3737 | 10293114.2875 | 0 | 512018.8828 | 0 | 13601181.9172 | 35387485.3625 | 24152685.9 | 108016178.6083 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 137716333.8178 | 180310954.3398 | 421696.5034 | 38.0126 | 3622.9129 | 4743.4524 | 73.858 | 96.7017
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4696 | 87.4289 | 9.5621 | 4 | 3607.4947 | 4721.1265 | 73.5437 | 96.2465 | 173.5696 | 0 | 233.581 | 11242948.3167 | 989452.7235 | 11905776.5696 | 10337197.2416 | 0 | 484858.799 | 0 | 13634491.1236 | 35474149.085 | 24211835.6714 | 108280709.5303 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 137980864.7397 | 180575485.2618 | 562341.3252 | 38.2484 | 3607.4947 | 4721.1265 | 73.5437 | 96.2465
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.0445 | 87.6674 | 9.6059 | 4 | 3595.8909 | 4704.4388 | 73.3071 | 95.9063 | 173.5318 | 0 | 203.5695 | 11264822.711 | 991341.1241 | 11931748.7221 | 10369293.846 | 0 | 463375.4993 | 0 | 13658026.942 | 35535384.4565 | 24253630.0707 | 108467623.3717 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138167778.5812 | 180762399.1032 | 749894.2093 | 38.4238 | 3595.8909 | 4704.4388 | 73.3071 | 95.9063
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4512 | 87.8358 | 9.6381 | 4 | 3587.1629 | 4692.01 | 73.1292 | 95.653 | 173.5049 | 0 | 211.1927 | 11280260.9493 | 992673.8409 | 11950082.5214 | 10391994.4812 | 0 | 446353.1371 | 0 | 13673932.3226 | 35576766.9943 | 24281874.5031 | 108593938.7499 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138294093.9594 | 180888714.4814 | 1000000 | 38.5525 | 3587.1629 | 4692.01 | 73.1292 | 95.653
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.7413 | 87.9557 | 9.6618 | 4 | 3580.6016 | 4682.7404 | 72.9954 | 95.464 | 173.4857 | 0 | 208.7355 | 11291250.8738 | 993622.5261 | 11963135.4517 | 10408179.3045 | 0 | 433028.9466 | 0 | 13684794.67 | 35605028.594 | 24301163.6256 | 108680203.9923 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138380359.2018 | 180974979.7238 | 1333521.4322 | 38.6472 | 3580.6016 | 4682.7404 | 72.9954 | 95.464
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9628 | 88.0473 | 9.6797 | 4 | 3575.6714 | 4675.768 | 72.8949 | 95.3219 | 173.4711 | 0 | 233.5545 | 11299635.6628 | 994346.3122 | 11973095.1996 | 10420538.8792 | 0 | 422912.2996 | 0 | 13693106.0578 | 35626653.1202 | 24315922.809 | 108746210.3404 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138446365.5498 | 181040986.0719 | 1778279.41 | 38.719 | 3575.6714 | 4675.768 | 72.8949 | 95.3219
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.124 | 88.1138 | 9.693 | 4 | 3571.9685 | 4670.5554 | 72.8194 | 95.2156 | 173.4604 | 0 | 228.0516 | 11305729.2354 | 994872.309 | 11980333.8938 | 10429528.8937 | 0 | 415132.9174 | 0 | 13698982.9272 | 35641943.5288 | 24326358.8271 | 108792882.5324 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138493037.7418 | 181087658.2639 | 2371373.7057 | 38.7722 | 3571.9685 | 4670.5554 | 72.8194 | 95.2156
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.2406 | 88.162 | 9.7029 | 4 | 3569.1882 | 4666.6606 | 72.7627 | 95.1362 | 173.4526 | 0 | 226.8321 | 11310138.3594 | 995252.8998 | 11985571.8731 | 10436038.2854 | 0 | 409165.5545 | 0 | 13703105.1192 | 35652668.6267 | 24333678.9268 | 108825619.6448 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138525774.8543 | 181120395.3763 | 3162277.6602 | 38.8116 | 3569.1882 | 4666.6606 | 72.7627 | 95.1362
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.3138 | 88.1921 | 9.7098 | 4 | 3567.1012 | 4663.7944 | 72.7202 | 95.0778 | 173.4477 | 0 | 223.1153 | 11312898.7362 | 995491.1707 | 11988851.2827 | 10440118.5719 | 0 | 404416.1699 | 0 | 13705292.6133 | 35658360.0377 | 24337563.4317 | 108842992.0141 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138543147.2236 | 181137767.7457 | 4216965.0343 | 38.8391 | 3567.1012 | 4663.7944 | 72.7202 | 95.0778
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.3797 | 88.2193 | 9.7153 | 4 | 3565.5351 | 4661.6012 | 72.6883 | 95.033 | 173.4433 | 0 | 240.0147 | 11315388.1991 | 995706.0556 | 11991808.9177 | 10443796.1614 | 0 | 401014.6336 | 0 | 13707608.4473 | 35664385.3628 | 24341675.84 | 108861383.6177 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138561538.8271 | 181156159.3492 | 5623413.2519 | 38.8614 | 3565.5351 | 4661.6012 | 72.6883 | 95.033
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4186 | 88.2354 | 9.7191 | 4 | 3564.3599 | 4659.9971 | 72.6643 | 95.0003 | 173.4407 | 0 | 220.003 | 11316854.4111 | 995832.6151 | 11993550.9027 | 10445965.1573 | 0 | 398276.9304 | 0 | 13708687.2065 | 35667192.0729 | 24343591.4773 | 108869950.7734 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138570105.9828 | 181164726.5049 | 7498942.0933 | 38.8766 | 3564.3599 | 4659.9971 | 72.6643 | 95.0003
1 | 6900 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4575 | 88.2514 | 9.7223 | 4 | 3563.4783 | 4658.7561 | 72.6463 | 94.975 | 173.4381 | 0 | 230.8329 | 11318322.9029 | 995959.3711 | 11995295.6223 | 10448134.8327 | 0 | 396377.5463 | 0 | 13710095.2074 | 35670855.4024 | 24346091.7749 | 108881132.66 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 138581287.8695 | 181175908.3915 | 10000000 | 38.8893 | 3563.4783 | 4658.7561 | 72.6463 | 94.975
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5548 | [19 empty] | 100 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.6231 | [19 empty] | 133.3521 | 0
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.31998 | 0.01336 | 4 | 595449.3184 | 1408479.8603 | 12139.0398 | 28713.7671 | 119.0439 | 0 | 37.4316 | 180520.8713 | 12575.1889 | 137266.4282 | 80411.7087 | 0 | 77033.7221 | 0 | 190245.0885 | 494978.6955 | 337833.1305 | 1510864.8336 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 31821490.8229 | 75270770.4367 | 177.8279 | 0.053441 | 595449.3184 | 1408479.8603 | 12139.0398 | 28713.7671
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.48969 | 0.028831 | 4 | 280534.1719 | 657293.4529 | 5719.0685 | 13399.8161 | 130.1703 | 0 | 194.4727 | 257420.0624 | 19242.6434 | 191446.6235 | 104258.0244 | 0 | 86802.6491 | 0 | 257076.301 | 668859.8017 | 456510.5584 | 2041616.6637 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 32352242.653 | 75801522.2668 | 237.1374 | 0.11532 | 280534.1719 | 657293.4529 | 5719.0685 | 13399.8161
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.73856 | 0.053394 | 4 | 154831.9717 | 358269.0282 | 3156.4592 | 7303.7987 | 140.3077 | 0 | 275.6481 | 360126.0878 | 28827.738 | 264127.1134 | 137826.9954 | 0 | 99484.8946 | 0 | 347253.2034 | 903481.6038 | 616644.7593 | 2757772.3956 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 33068398.3849 | 76517677.9987 | 316.2278 | 0.21358 | 154831.9717 | 358269.0282 | 3156.4592 | 7303.7987
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1878 | 1.073 | 0.089354 | 4 | 95023.8184 | 216589.3497 | 1937.1891 | 4415.4669 | 148.6272 | 0 | 436.7133 | 486842.9485 | 41590.1475 | 353981.8235 | 183911.2791 | 0 | 112867.3577 | 0 | 459885.487 | 1196527.7016 | 816654.7425 | 3652261.4874 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 33962887.4767 | 77412167.0905 | 421.6965 | 0.35741 | 95023.8184 | 216589.3497 | 1937.1891 | 4415.4669
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 1.5376 | 0.14083 | 4 | 62322.4118 | 139450.6974 | 1270.5267 | 2842.8911 | 155.5747 | 0 | 58.124 | 645723.421 | 58366.609 | 469846.9918 | 246255.2387 | 0 | 128904.3743 | 0 | 604147.6876 | 1571868.3554 | 1072832.4512 | 4797945.1291 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 35108571.1184 | 78557850.7322 | 562.3413 | 0.56334 | 62322.4118 | 139450.6974 | 1270.5267 | 2842.8911
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4468 | 2.2302 | 0.2097 | 4 | 43602.7574 | 95401.7513 | 888.9012 | 1944.8937 | 161.3012 | 0 | 78.423 | 838436.0252 | 75871.4957 | 632572.6497 | 325285.926 | 0 | 150143.4868 | 0 | 788700.7375 | 2052037.5343 | 1400557.7823 | 6263605.6375 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 36574231.6267 | 80023511.2405 | 749.8942 | 0.83881 | 43602.7574 | 95401.7513 | 888.9012 | 1944.8937
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.14 | 3.139 | 0.29989 | 4 | 31969.318 | 68189.9136 | 651.7378 | 1390.1436 | 165.8216 | 0 | 62.9053 | 1065733.1923 | 96379.9039 | 831499.9586 | 426260.3595 | 0 | 175629.9188 | 0 | 1012246.2999 | 2633657.2321 | 1797525.1771 | 8038932.0422 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 38349558.0315 | 81798837.6453 | 1000 | 1.1996 | 31969.318 | 68189.9136 | 651.7378 | 1390.1436
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4032 | 4.3634 | 0.42134 | 4 | 24076.7289 | 49857.132 | 490.8367 | 1016.4051 | 169.5518 | 0 | 71.5973 | 1343411.6302 | 121370.095 | 1082158.8992 | 560736.0717 | 0 | 207307.8734 | 0 | 1292843.9821 | 3363714.8426 | 2295804.4975 | 10267347.8916 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 40577973.8809 | 84027253.4946 | 1333.5214 | 1.6854 | 24076.7289 | 49857.132 | 490.8367 | 1016.4051
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4064 | 5.9912 | 0.5828 | 4 | 18595.7819 | 37233.8655 | 379.1002 | 759.0627 | 172.4799 | 0 | 70.5482 | 1679468.3627 | 151529.0072 | 1394582.7087 | 738696.8989 | 0 | 245917.3613 | 0 | 1641975.7921 | 4272084.1956 | 2915785.2461 | 13040039.5726 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 43350665.5619 | 86799945.1757 | 1778.2794 | 2.3312 | 18595.7819 | 37233.8655 | 379.1002 | 759.0627
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.3869 | 8.1483 | 0.79674 | 4 | 14685.6307 | 28319.0428 | 299.3864 | 577.322 | 174.7261 | 0 | 85.5379 | 2086264.1839 | 187925.0618 | 1783564.2577 | 974129.5973 | 0 | 292848.243 | 0 | 2076645.224 | 5403004.8944 | 3687661.8611 | 16492043.3231 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 46802669.3123 | 90251948.9261 | 2371.3737 | 3.187 | 14685.6307 | 28319.0428 | 299.3864 | 577.322
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6365 | 10.9952 | 1.0793 | 4 | 11834.4008 | 21898.2388 | 241.2603 | 446.4252 | 176.4528 | 0 | 72.0273 | 2578045.9488 | 231781.2001 | 2266708.2435 | 1284300.7366 | 0 | 349244.8903 | 0 | 2616931.5975 | 6808719.2102 | 4647090.7661 | 20782822.593 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 51093448.5823 | 94542728.1961 | 3162.2777 | 4.3174 | 11834.4008 | 21898.2388 | 241.2603 | 446.4252
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5795 | 14.7625 | 1.4524 | 4 | 9718.6615 | 17197.7098 | 198.1281 | 350.5986 | 177.7804 | 0 | 42.1419 | 3175444.9577 | 284870.7546 | 2869200.8337 | 1694363.6529 | 0 | 418957.9484 | 0 | 3292706.8774 | 8566947.868 | 5847117.9531 | 26149610.8457 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 56460236.835 | 99909516.4487 | 4216.965 | 5.8095 | 9718.6615 | 17197.7098 | 198.1281 | 350.5986
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.671 | 19.6975 | 1.9427 | 4 | 8121.1946 | 13712.5024 | 165.5615 | 279.5479 | 178.7907 | 0 | 47.9749 | 3895193.9585 | 348597.9688 | 3613792.5516 | 2231237.0023 | 0 | 500577.5749 | 0 | 4129865.6319 | 10745063.2223 | 7333726.4382 | 32798054.3485 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 63108680.3377 | 106557959.9515 | 5623.4133 | 7.7709 | 8121.1946 | 13712.5024 | 165.5615 | 279.5479
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3689 | 26.0451 | 2.5739 | 4 | 6918.0013 | 11138.2206 | 141.0328 | 227.0677 | 179.5388 | 0 | 50.5206 | 4748732.4851 | 423881.5632 | 4518707.9743 | 2921740.3264 | 0 | 596600.2339 | 0 | 5151768.4073 | 13403844.6229 | 9148399.3766 | 40913674.9897 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 71224300.9789 | 114673580.5927 | 7498.9421 | 10.2955 | 6918.0013 | 11138.2206 | 141.0328 | 227.0677
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.158 | 34.0385 | 3.3678 | 4 | 6010.404 | 9235.7941 | 122.5302 | 188.2842 | 180.0158 | 0 | 39.4593 | 5742944.8603 | 511229.3306 | 5597704.5567 | 3794038.9324 | 0 | 709094.4622 | 0 | 6378454.7355 | 16595430.8207 | 11326722.5371 | 50655620.2355 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 80966246.2248 | 124415525.8385 | 10000 | 13.471 | 6010.404 | 9235.7941 | 122.5302 | 188.2842
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.1164 | 43.6173 | 4.317 | 4 | 5337.2579 | 7853.4128 | 108.8072 | 160.1024 | 180.1155 | 0 | 51.9831 | 6850213.7376 | 608131.412 | 6825908.4284 | 4850420.9886 | 0 | 835860.7841 | 0 | 7788508.7868 | 20264102.2204 | 13830666.1511 | 61853812.5091 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 92164438.4983 | 135613718.1121 | 13335.2143 | 17.2681 | 5337.2579 | 7853.4128 | 108.8072 | 160.1024
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.8669 | 54.385 | 5.3782 | 4 | 4850.9014 | 6870.6136 | 98.8922 | 140.0668 | 179.72 | 0 | 58.7089 | 8015054.6277 | 709694.9046 | 8143605.8175 | 6064327.2708 | 0 | 973955.9166 | 0 | 9323589.0295 | 24258066.1237 | 16556628.5828 | 74044922.2732 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 104355548.2624 | 147804827.8762 | 17782.7941 | 21.5126 | 4850.9014 | 6870.6136 | 98.8922 | 140.0668
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3541 | 65.5558 | 6.4688 | 4 | 4511.8606 | 6191.0399 | 91.9804 | 126.2127 | 178.8038 | 0 | 65.4312 | 9156008.2977 | 808843.42 | 9456333.201 | 7368866.5443 | 0 | 1116980.3338 | 0 | 10883742.4008 | 28317265.1643 | 19327115.3363 | 86435154.6984 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 116745780.6876 | 160195060.3014 | 23713.7371 | 25.8753 | 4511.8606 | 6191.0399 | 91.9804 | 126.2127
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5996 | 71.3711 | 7.1809 | 4 | 4273.6432 | 5786.3042 | 87.124 | 117.9616 | 178.1218 | 0 | 68.3965 | 9727860.311 | 858424.2418 | 10121650.9643 | 8072794.1417 | 0 | 1066482.2006 | 0 | 11640412.6252 | 30285965.8737 | 20670794.0232 | 92444384.3814 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 122755010.3707 | 166204289.9845 | 31622.7766 | 28.7237 | 4273.6432 | 5786.3042 | 87.124 | 117.9616
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.0339 | 76.7137 | 7.839 | 4 | 4089.1806 | 5474.8645 | 83.3635 | 111.6125 | 177.4943 | 0 | 89.7454 | 10241712.6699 | 902916.0528 | 10723382.9348 | 8727799.2384 | 0 | 1015763.6689 | 0 | 12328514.0803 | 32076264.7108 | 21892709.7665 | 97909063.1223 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 128219689.1116 | 171668968.7254 | 42169.6503 | 31.3558 | 4089.1806 | 5474.8645 | 83.3635 | 111.6125
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5157 | 80.6055 | 8.3641 | 4 | 3947.0377 | 5245.7183 | 80.4657 | 106.9411 | 177.0154 | 0 | 163.8769 | 10609669.2337 | 934741.7809 | 11156430.8725 | 9212233.5136 | 0 | 936465.0252 | 0 | 12811320.7661 | 33332428.6701 | 22750067.4802 | 101743357.3422 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 132053983.3314 | 175503262.9452 | 56234.1325 | 33.4565 | 3947.0377 | 5245.7183 | 80.4657 | 106.9411
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.7024 | 83.3831 | 8.768 | 4 | 3840.6162 | 5079.4756 | 78.2962 | 103.552 | 176.6397 | 0 | 199.3832 | 10869215.2699 | 957174.309 | 11462939.4109 | 9563628.1524 | 0 | 850281.5056 | 0 | 13144263.0727 | 34198676.256 | 23341299.2573 | 104387477.2338 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 134698103.2231 | 178147382.8369 | 74989.4209 | 35.072 | 3840.6162 | 5079.4756 | 78.2962 | 103.552
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.487 | 85.5007 | 9.087 | 4 | 3760.1028 | 4955.4784 | 76.6548 | 101.0241 | 176.3393 | 0 | 225.1786 | 11065454.4161 | 974126.3945 | 11695248.5758 | 9834782.3874 | 0 | 770764.7236 | 0 | 13392746.834 | 34845180.0319 | 23782551.3686 | 106360854.732 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 136671480.7212 | 180120760.335 | 100000 | 36.3478 | 3760.1028 | 4955.4784 | 76.6548 | 101.0241
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.1313 | 87.0955 | 9.3347 | 4 | 3699.2525 | 4862.8999 | 75.4143 | 99.1368 | 176.1048 | 0 | 171.1808 | 11212337.2378 | 986809.9369 | 11869440.8479 | 10040983.0795 | 0 | 700391.4272 | 0 | 13575885.3864 | 35321668.9785 | 24107764.8655 | 107815281.7597 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 138125907.7489 | 181575187.3627 | 133352.1432 | 37.3389 | 3699.2525 | 4862.8999 | 75.4143 | 99.1368
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8808 | 88.2877 | 9.5249 | 4 | 3653.2962 | 4793.7047 | 74.4774 | 97.7262 | 175.9247 | 0 | 220.103 | 11321643.9642 | 996246.0339 | 11999241.4816 | 10196172.3009 | 0 | 640117.77 | 0 | 13709834.4047 | 35670176.8473 | 24345628.6471 | 108879061.4497 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 139189687.439 | 182638967.0528 | 177827.941 | 38.0998 | 3653.2962 | 4793.7047 | 74.4774 | 97.7262
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.8862 | 89.1508 | 9.6678 | 4 | 3618.6122 | 4742.1652 | 73.7703 | 96.6755 | 175.7916 | 0 | 208.8949 | 11400522.1727 | 1003053.9178 | 12092998.2856 | 10309052.7412 | 0 | 588919.949 | 0 | 13803873.3558 | 35914846.9082 | 24512620.9911 | 109625888.3214 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 139936514.3107 | 183385793.9244 | 237137.3706 | 38.6713 | 3618.6122 | 4742.1652 | 73.7703 | 96.6755
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.3575 | 89.7809 | 9.7751 | 4 | 3592.4551 | 4703.6747 | 73.2371 | 95.8908 | 175.6929 | 0 | 166.652 | 11457966.8483 | 1008011.1557 | 12161325.622 | 10391813.2374 | 0 | 546679.0132 | 0 | 13870660.3919 | 36088613.076 | 24631219.9712 | 110156289.3156 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 140466915.3049 | 183916194.9186 | 316227.766 | 39.1005 | 3592.4551 | 4703.6747 | 73.2371 | 95.8908
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4272 | 90.2372 | 9.8551 | 4 | 3572.7416 | 4674.9395 | 72.8352 | 95.305 | 175.6207 | 0 | 149.8385 | 11499498.0538 | 1011594.7385 | 12210749.3065 | 10451945.8496 | 0 | 512319.1868 | 0 | 13917581.7827 | 36210692.91 | 24714541.9664 | 110528923.7943 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 140839549.7836 | 184288829.3974 | 421696.5034 | 39.4206 | 3572.7416 | 4674.9395 | 72.8352 | 95.305
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.2017 | 90.5667 | 9.9146 | 4 | 3557.8941 | 4653.4841 | 72.5325 | 94.8676 | 175.5681 | 0 | 171.4499 | 11529449.8386 | 1014178.9717 | 12246405.796 | 10495472.5218 | 0 | 484746.8992 | 0 | 13950399.0706 | 36296076.7614 | 24772818.1994 | 110789548.0586 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141100174.0479 | 184549453.6616 | 562341.3252 | 39.6583 | 3557.8941 | 4653.4841 | 72.5325 | 94.8676
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.7593 | 90.8034 | 9.9586 | 4 | 3546.7187 | 4637.4703 | 72.3047 | 94.5411 | 175.53 | 0 | 147.2073 | 11550942.8721 | 1016033.2817 | 12271999.0223 | 10526792.1382 | 0 | 462838.6925 | 0 | 13973156.3427 | 36355286.5151 | 24813230.073 | 110970278.9375 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141280904.9268 | 184730184.5406 | 749894.2093 | 39.8343 | 3546.7187 | 4637.4703 | 72.3047 | 94.5411
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.1567 | 90.9718 | 9.9909 | 4 | 3538.3123 | 4625.5289 | 72.1333 | 94.2977 | 175.5028 | 0 | 141.9869 | 11566230.9432 | 1017352.2063 | 12290206.9085 | 10549115.7322 | 0 | 445545.7033 | 0 | 13988696.0825 | 36395717.7305 | 24840825.2083 | 111093690.5147 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141404316.504 | 184853596.1178 | 1000000 | 39.9638 | 3538.3123 | 4625.5289 | 72.1333 | 94.2977
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.4339 | 91.0891 | 10.0146 | 4 | 3531.9922 | 4616.6452 | 72.0044 | 94.1166 | 175.4838 | 0 | 257.1152 | 11576872.3963 | 1018270.2344 | 12302882.3693 | 10564679.6409 | 0 | 431911.692 | 0 | 13998900.3698 | 36422267.193 | 24858945.762 | 111174729.6576 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141485355.6469 | 184934635.2607 | 1333521.4322 | 40.0582 | 3531.9922 | 4616.6452 | 72.0044 | 94.1166
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.636 | 91.1746 | 10.0321 | 4 | 3527.2431 | 4609.9997 | 71.9076 | 93.9811 | 175.4698 | 0 | 283.7361 | 11584621.0125 | 1018938.6868 | 12312112.8991 | 10576024.6381 | 0 | 421397.1379 | 0 | 14006106.806 | 36441016.8617 | 24871742.7961 | 111231960.8382 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141542586.8274 | 184991866.4412 | 1778279.41 | 40.1284 | 3527.2431 | 4609.9997 | 71.9076 | 93.9811
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.8017 | 91.2446 | 10.0458 | 4 | 3523.6758 | 4604.9584 | 71.8349 | 93.8783 | 175.4584 | 0 | 237.991 | 11590975.9186 | 1019486.8992 | 12319683.7031 | 10585332.0427 | 0 | 413634.7346 | 0 | 14012354.1863 | 36457271.2636 | 24882836.7594 | 111281575.5075 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141592201.4967 | 185041481.1105 | 2371373.7057 | 40.1831 | 3523.6758 | 4604.9584 | 71.8349 | 93.8783
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.9092 | 91.29 | 10.0554 | 4 | 3520.9974 | 4601.2399 | 71.7803 | 93.8025 | 175.451 | 0 | 237.9848 | 11595088.3817 | 1019841.6609 | 12324583.2672 | 10591362.4082 | 0 | 407465.2358 | 0 | 14015952.972 | 36466634.5659 | 24889227.4056 | 111310155.8974 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141620781.8867 | 185070061.5005 | 3162277.6602 | 40.2218 | 3520.9974 | 4601.2399 | 71.7803 | 93.8025
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.9844 | 91.3217 | 10.0625 | 4 | 3518.9867 | 4598.4705 | 71.7393 | 93.746 | 175.4458 | 0 | 167.6208 | 11597964.3841 | 1020089.7575 | 12328009.8379 | 10595582.6746 | 0 | 402709.2334 | 0 | 14018298.7961 | 36472737.919 | 24893393.0695 | 111328785.6721 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141639411.6614 | 185088691.2751 | 4216965.0343 | 40.2501 | 3518.9867 | 4598.4705 | 71.7393 | 93.746
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.0381 | 91.3444 | 10.0677 | 4 | 3517.4778 | 4596.403 | 71.7085 | 93.7039 | 175.4421 | 0 | 172.3734 | 11600017.6721 | 1020266.8821 | 12330456.2574 | 10598597.2447 | 0 | 399074.8019 | 0 | 14019881.0147 | 36476854.5271 | 24896202.7392 | 111341351.1391 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141651977.1283 | 185101256.7421 | 5623413.2519 | 40.2709 | 3517.4778 | 4596.403 | 71.7085 | 93.7039
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.077 | 91.3608 | 10.0716 | 4 | 3516.3456 | 4594.8573 | 71.6855 | 93.6724 | 175.4394 | 0 | 176.3481 | 11601503.8739 | 1020395.0872 | 12332227.045 | 10600780.0698 | 0 | 396312.7598 | 0 | 14020975.3459 | 36479701.7525 | 24898146.029 | 111350041.9632 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141660667.9524 | 185109947.5662 | 7498942.0933 | 40.2863 | 3516.3456 | 4594.8573 | 71.6855 | 93.6724
1 | 7000 | 707 | 0.025 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.1159 | 91.3772 | 10.0748 | 4 | 3515.4962 | 4593.6611 | 71.6681 | 93.648 | 175.4367 | 0 | 192.4488 | 11602992.456 | 1020523.4972 | 12334000.6949 | 10602963.5735 | 0 | 394398.0586 | 0 | 14022402.5293 | 36483414.9909 | 24900680.3905 | 111361376.1909 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 141672002.1801 | 185121281.7939 | 10000000 | 40.2993 | 3515.4962 | 4593.6611 | 71.6681 | 93.648