## CO2
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028756 | 0.00013589 | 4 | 8792420.9611 | 31257875.1346 | 179245.3939 | 637234.064 | 28.0852 | 0.85587 | 22.8307 | 7897.1955 | 0 | 8264.2133 | 0 | 0 | 0 | 0 | 6302.9494 | 16398.9815 | 11192.6418 | 50055.9815 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779125.0359 | 16990234.4629 | 100 | 0.00054355 | 8792420.9611 | 31257875.1346 | 179245.3939 | 637234.064
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028756 | 0.00013589 | 4 | 8792049.7428 | 31256548.2068 | 179237.8261 | 637207.0128 | 28.0854 | 0.8559 | 22.8458 | 7897.4192 | 0 | 8264.4849 | 0 | 0 | 0 | 0 | 6303.1426 | 16399.4842 | 11192.9849 | 50057.5159 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779126.5703 | 16990235.9972 | 133.3521 | 0.00054357 | 8792049.7428 | 31256548.2068 | 179237.8261 | 637207.0128
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028756 | 0.00013589 | 4 | 8792055.3303 | 31256568.1794 | 179237.94 | 637207.42 | 28.0854 | 0.8559 | 23.3883 | 7897.4159 | 0 | 8264.4808 | 0 | 0 | 0 | 0 | 6303.1397 | 16399.4766 | 11192.9797 | 50057.4928 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779126.5472 | 16990235.9741 | 177.8279 | 0.00054357 | 8792055.3303 | 31256568.1794 | 179237.94 | 637207.42
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028756 | 0.00013589 | 4 | 8792288.0509 | 31257400.0439 | 179242.6844 | 637224.3787 | 28.0852 | 0.85588 | 24.3595 | 7897.2756 | 0 | 8264.3106 | 0 | 0 | 0 | 0 | 6303.0186 | 16399.1615 | 11192.7647 | 50056.5309 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779125.5853 | 16990235.0122 | 237.1374 | 0.00054356 | 8792288.0509 | 31257400.0439 | 179242.6844 | 637224.3787
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028757 | 0.00013588 | 4 | 8792624.3173 | 31258602.0355 | 179249.5396 | 637248.8829 | 28.0851 | 0.85586 | 26.0779 | 7897.0729 | 0 | 8264.0645 | 0 | 0 | 0 | 0 | 6302.8436 | 16398.7062 | 11192.4539 | 50055.1411 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779124.1955 | 16990233.6224 | 316.2278 | 0.00054354 | 8792624.3173 | 31258602.0355 | 179249.5396 | 637248.8829
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028757 | 0.00013588 | 4 | 8792983.0634 | 31259884.381 | 179256.8531 | 637275.0252 | 28.0849 | 0.85583 | 28.0095 | 7896.8567 | 0 | 8263.8021 | 0 | 0 | 0 | 0 | 6302.6569 | 16398.2204 | 11192.1224 | 50053.6585 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779122.7129 | 16990232.1399 | 421.6965 | 0.00054352 | 8792983.0634 | 31259884.381 | 179256.8531 | 637275.0252
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028758 | 0.00013587 | 4 | 8793319.1946 | 31261085.8893 | 179263.7056 | 637299.5196 | 28.0848 | 0.85581 | 29.4843 | 7896.6541 | 0 | 8263.5562 | 0 | 0 | 0 | 0 | 6302.482 | 16397.7654 | 11191.8118 | 50052.2695 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779121.3239 | 16990230.7509 | 562.3413 | 0.00054349 | 8793319.1946 | 31261085.8893 | 179263.7056 | 637299.5196
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028759 | 0.00013587 | 4 | 8793612.2281 | 31262133.3438 | 179269.6795 | 637320.8734 | 28.0846 | 0.85579 | 29.4693 | 7896.4775 | 0 | 8263.3418 | 0 | 0 | 0 | 0 | 6302.3296 | 16397.3687 | 11191.5411 | 50051.0587 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779120.1131 | 16990229.54 | 749.8942 | 0.00054348 | 8793612.2281 | 31262133.3438 | 179269.6795 | 637320.8734
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028759 | 0.00013587 | 4 | 8793856.4452 | 31263006.3029 | 179274.6582 | 637338.6698 | 28.0845 | 0.85577 | 29.7725 | 7896.3304 | 0 | 8263.1632 | 0 | 0 | 0 | 0 | 6302.2025 | 16397.0381 | 11191.3155 | 50050.0497 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779119.1041 | 16990228.531 | 1000 | 0.00054346 | 8793856.4452 | 31263006.3029 | 179274.6582 | 637338.6698
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028759 | 0.00013586 | 4 | 8794053.9732 | 31263712.3711 | 179278.6851 | 637353.064 | 28.0844 | 0.85575 | 28.7935 | 7896.2113 | 0 | 8263.0187 | 0 | 0 | 0 | 0 | 6302.0997 | 16396.7708 | 11191.133 | 50049.2336 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779118.288 | 16990227.7149 | 1333.5214 | 0.00054345 | 8794053.9732 | 31263712.3711 | 179278.6851 | 637353.064
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013586 | 4 | 8794210.4638 | 31264271.75 | 179281.8754 | 637364.4677 | 28.0843 | 0.85574 | 27.6651 | 7896.1171 | 0 | 8262.9043 | 0 | 0 | 0 | 0 | 6302.0183 | 16396.559 | 11190.9884 | 50048.587 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779117.6414 | 16990227.0684 | 1778.2794 | 0.00054344 | 8794210.4638 | 31264271.75 | 179281.8754 | 637364.4677
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013586 | 4 | 8794332.6375 | 31264708.4625 | 179284.366 | 637373.3707 | 28.0843 | 0.85573 | 28.362 | 7896.0434 | 0 | 8262.8149 | 0 | 0 | 0 | 0 | 6301.9548 | 16396.3936 | 11190.8755 | 50048.0823 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779117.1367 | 16990226.5636 | 2371.3737 | 0.00054343 | 8794332.6375 | 31264708.4625 | 179284.366 | 637373.3707
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013586 | 4 | 8794427.0167 | 31265045.8228 | 179286.2901 | 637380.2482 | 28.0842 | 0.85573 | 27.896 | 7895.9866 | 0 | 8262.7459 | 0 | 0 | 0 | 0 | 6301.9057 | 16396.2659 | 11190.7884 | 50047.6924 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779116.7468 | 16990226.1738 | 3162.2777 | 0.00054343 | 8794427.0167 | 31265045.8228 | 179286.2901 | 637380.2482
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013586 | 4 | 8794499.3653 | 31265304.4347 | 179287.765 | 637385.5204 | 28.0842 | 0.85572 | 27.1137 | 7895.943 | 0 | 8262.693 | 0 | 0 | 0 | 0 | 6301.868 | 16396.168 | 11190.7215 | 50047.3935 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779116.4479 | 16990225.8749 | 4216.965 | 0.00054342 | 8794499.3653 | 31265304.4347 | 179287.765 | 637385.5204
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013585 | 4 | 8794554.5142 | 31265501.5655 | 179288.8893 | 637389.5391 | 28.0842 | 0.85572 | 27.7488 | 7895.9098 | 0 | 8262.6527 | 0 | 0 | 0 | 0 | 6301.8394 | 16396.0933 | 11190.6706 | 50047.1657 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779116.2201 | 16990225.6471 | 5623.4133 | 0.00054342 | 8794554.5142 | 31265501.5655 | 179288.8893 | 637389.5391
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.02876 | 0.00013585 | 4 | 8794596.3771 | 31265651.2054 | 179289.7427 | 637392.5897 | 28.0841 | 0.85571 | 27.6446 | 7895.8845 | 0 | 8262.6221 | 0 | 0 | 0 | 0 | 6301.8176 | 16396.0367 | 11190.6319 | 50046.9928 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779116.0472 | 16990225.4741 | 7498.9421 | 0.00054342 | 8794596.3771 | 31265651.2054 | 179289.7427 | 637392.5897
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794628.057 | 31265764.4457 | 179290.3886 | 637394.8983 | 28.0841 | 0.85571 | 27.9454 | 7895.8655 | 0 | 8262.5989 | 0 | 0 | 0 | 0 | 6301.8011 | 16395.9938 | 11190.6027 | 50046.8619 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.9163 | 16990225.3433 | 10000 | 0.00054341 | 8794628.057 | 31265764.4457 | 179290.3886 | 637394.8983
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794651.9753 | 31265849.9421 | 179290.8762 | 637396.6413 | 28.0841 | 0.85571 | 28.8376 | 7895.8511 | 0 | 8262.5814 | 0 | 0 | 0 | 0 | 6301.7887 | 16395.9614 | 11190.5806 | 50046.7631 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.8175 | 16990225.2444 | 13335.2143 | 0.00054341 | 8794651.9753 | 31265849.9421 | 179290.8762 | 637396.6413
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794670.0024 | 31265914.3807 | 179291.2437 | 637397.9549 | 28.0841 | 0.85571 | 28.2546 | 7895.8402 | 0 | 8262.5682 | 0 | 0 | 0 | 0 | 6301.7793 | 16395.937 | 11190.5639 | 50046.6886 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.743 | 16990225.17 | 17782.7941 | 0.00054341 | 8794670.0024 | 31265914.3807 | 179291.2437 | 637397.9549
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794683.5726 | 31265962.8875 | 179291.5203 | 637398.9438 | 28.0841 | 0.85571 | 28.4858 | 7895.832 | 0 | 8262.5583 | 0 | 0 | 0 | 0 | 6301.7722 | 16395.9187 | 11190.5514 | 50046.6326 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.687 | 16990225.1139 | 23713.7371 | 0.00054341 | 8794683.5726 | 31265962.8875 | 179291.5203 | 637398.9438
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794693.778 | 31265999.3669 | 179291.7284 | 637399.6875 | 28.0841 | 0.85571 | 27.6078 | 7895.8259 | 0 | 8262.5508 | 0 | 0 | 0 | 0 | 6301.7669 | 16395.9048 | 11190.542 | 50046.5904 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.6448 | 16990225.0718 | 31622.7766 | 0.00054341 | 8794693.778 | 31265999.3669 | 179291.7284 | 637399.6875
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794701.4475 | 31266026.7818 | 179291.8847 | 637400.2464 | 28.0841 | 0.85571 | 27.5263 | 7895.8212 | 0 | 8262.5452 | 0 | 0 | 0 | 0 | 6301.7629 | 16395.8945 | 11190.5349 | 50046.5587 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.6131 | 16990225.0401 | 42169.6503 | 0.00054341 | 8794701.4475 | 31266026.7818 | 179291.8847 | 637400.2464
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794707.2075 | 31266047.3709 | 179292.0021 | 637400.6661 | 28.0841 | 0.85571 | 27.8077 | 7895.8178 | 0 | 8262.541 | 0 | 0 | 0 | 0 | 6301.7599 | 16395.8867 | 11190.5296 | 50046.5349 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5894 | 16990225.0163 | 56234.1325 | 0.00054341 | 8794707.2075 | 31266047.3709 | 179292.0021 | 637400.6661
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794711.5322 | 31266062.8297 | 179292.0903 | 637400.9813 | 28.0841 | 0.85571 | 27.8049 | 7895.8152 | 0 | 8262.5379 | 0 | 0 | 0 | 0 | 6301.7577 | 16395.8808 | 11190.5256 | 50046.5171 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5715 | 16990224.9984 | 74989.4209 | 0.00054341 | 8794711.5322 | 31266062.8297 | 179292.0903 | 637400.9813
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794714.7783 | 31266074.4329 | 179292.1565 | 637401.2178 | 28.0841 | 0.85571 | 27.3258 | 7895.8132 | 0 | 8262.5355 | 0 | 0 | 0 | 0 | 6301.756 | 16395.8764 | 11190.5226 | 50046.5037 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5581 | 16990224.985 | 100000 | 0.00054341 | 8794714.7783 | 31266074.4329 | 179292.1565 | 637401.2178
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794717.2142 | 31266083.1402 | 179292.2061 | 637401.3953 | 28.0841 | 0.85571 | 28.0188 | 7895.8117 | 0 | 8262.5337 | 0 | 0 | 0 | 0 | 6301.7547 | 16395.8731 | 11190.5203 | 50046.4936 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.548 | 16990224.975 | 133352.1432 | 0.00054341 | 8794717.2142 | 31266083.1402 | 179292.2061 | 637401.3953
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794719.042 | 31266089.6737 | 179292.2434 | 637401.5285 | 28.0841 | 0.85571 | 28.6975 | 7895.8106 | 0 | 8262.5324 | 0 | 0 | 0 | 0 | 6301.7538 | 16395.8707 | 11190.5186 | 50046.4861 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5405 | 16990224.9674 | 177827.941 | 0.00054341 | 8794719.042 | 31266089.6737 | 179292.2434 | 637401.5285
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794720.4127 | 31266094.5733 | 179292.2714 | 637401.6284 | 28.0841 | 0.8557 | 27.6559 | 7895.8098 | 0 | 8262.5314 | 0 | 0 | 0 | 0 | 6301.7531 | 16395.8688 | 11190.5174 | 50046.4804 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5348 | 16990224.9617 | 237137.3706 | 0.00054341 | 8794720.4127 | 31266094.5733 | 179292.2714 | 637401.6284
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794721.4411 | 31266098.249 | 179292.2923 | 637401.7033 | 28.0841 | 0.8557 | 28.0029 | 7895.8092 | 0 | 8262.5306 | 0 | 0 | 0 | 0 | 6301.7525 | 16395.8674 | 11190.5164 | 50046.4762 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5306 | 16990224.9575 | 316227.766 | 0.00054341 | 8794721.4411 | 31266098.249 | 179292.2923 | 637401.7033
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794722.2124 | 31266101.0061 | 179292.308 | 637401.7595 | 28.0841 | 0.8557 | 27.3017 | 7895.8087 | 0 | 8262.53 | 0 | 0 | 0 | 0 | 6301.7521 | 16395.8664 | 11190.5157 | 50046.473 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5274 | 16990224.9543 | 421696.5034 | 0.00054341 | 8794722.2124 | 31266101.0061 | 179292.308 | 637401.7595
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794722.7912 | 31266103.0752 | 179292.3198 | 637401.8017 | 28.0841 | 0.8557 | 27.6762 | 7895.8084 | 0 | 8262.5296 | 0 | 0 | 0 | 0 | 6301.7518 | 16395.8656 | 11190.5152 | 50046.4706 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.525 | 16990224.9519 | 562341.3252 | 0.00054341 | 8794722.7912 | 31266103.0752 | 179292.3198 | 637401.8017
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794723.2251 | 31266104.6261 | 179292.3287 | 637401.8333 | 28.0841 | 0.8557 | 27.7773 | 7895.8081 | 0 | 8262.5293 | 0 | 0 | 0 | 0 | 6301.7516 | 16395.865 | 11190.5148 | 50046.4688 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5232 | 16990224.9501 | 749894.2093 | 0.00054341 | 8794723.2251 | 31266104.6261 | 179292.3287 | 637401.8333
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794723.5501 | 31266105.788 | 179292.3353 | 637401.857 | 28.0841 | 0.8557 | 27.499 | 7895.8079 | 0 | 8262.5291 | 0 | 0 | 0 | 0 | 6301.7514 | 16395.8646 | 11190.5145 | 50046.4674 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5218 | 16990224.9488 | 1000000 | 0.00054341 | 8794723.5501 | 31266105.788 | 179292.3353 | 637401.857
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794723.7943 | 31266106.6607 | 179292.3403 | 637401.8748 | 28.0841 | 0.8557 | 27.3765 | 7895.8078 | 0 | 8262.5289 | 0 | 0 | 0 | 0 | 6301.7513 | 16395.8642 | 11190.5142 | 50046.4664 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5208 | 16990224.9478 | 1333521.4322 | 0.00054341 | 8794723.7943 | 31266106.6607 | 179292.3403 | 637401.8748
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794723.9772 | 31266107.3144 | 179292.344 | 637401.8881 | 28.0841 | 0.8557 | 27.6733 | 7895.8077 | 0 | 8262.5288 | 0 | 0 | 0 | 0 | 6301.7512 | 16395.864 | 11190.5141 | 50046.4657 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5201 | 16990224.947 | 1778279.41 | 0.00054341 | 8794723.9772 | 31266107.3144 | 179292.344 | 637401.8881
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.1147 | 31266107.8062 | 179292.3468 | 637401.8982 | 28.0841 | 0.8557 | 28.0534 | 7895.8076 | 0 | 8262.5287 | 0 | 0 | 0 | 0 | 6301.7511 | 16395.8638 | 11190.5139 | 50046.4651 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5195 | 16990224.9464 | 2371373.7057 | 0.00054341 | 8794724.1147 | 31266107.8062 | 179292.3468 | 637401.8982
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.2176 | 31266108.1739 | 179292.3489 | 637401.9057 | 28.0841 | 0.8557 | 27.6661 | 7895.8075 | 0 | 8262.5286 | 0 | 0 | 0 | 0 | 6301.7511 | 16395.8636 | 11190.5138 | 50046.4647 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5191 | 16990224.946 | 3162277.6602 | 0.00054341 | 8794724.2176 | 31266108.1739 | 179292.3489 | 637401.9057
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.2945 | 31266108.4489 | 179292.3505 | 637401.9113 | 28.0841 | 0.8557 | 27.1705 | 7895.8075 | 0 | 8262.5285 | 0 | 0 | 0 | 0 | 6301.751 | 16395.8635 | 11190.5138 | 50046.4644 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5188 | 16990224.9457 | 4216965.0343 | 0.00054341 | 8794724.2945 | 31266108.4489 | 179292.3505 | 637401.9113
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.3524 | 31266108.6556 | 179292.3517 | 637401.9155 | 28.0841 | 0.8557 | 27.6187 | 7895.8074 | 0 | 8262.5285 | 0 | 0 | 0 | 0 | 6301.751 | 16395.8635 | 11190.5137 | 50046.4641 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5185 | 16990224.9455 | 5623413.2519 | 0.00054341 | 8794724.3524 | 31266108.6556 | 179292.3517 | 637401.9155
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.3958 | 31266108.8108 | 179292.3526 | 637401.9187 | 28.0841 | 0.8557 | 27.7088 | 7895.8074 | 0 | 8262.5284 | 0 | 0 | 0 | 0 | 6301.751 | 16395.8634 | 11190.5137 | 50046.4639 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5184 | 16990224.9453 | 7498942.0933 | 0.00054341 | 8794724.3958 | 31266108.8108 | 179292.3526 | 637401.9187
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.27986 | 0.028761 | 0.00013585 | 4 | 8794724.4287 | 31266108.9284 | 179292.3532 | 637401.921 | 28.0841 | 0.8557 | 27.5048 | 7895.8074 | 0 | 8262.5284 | 0 | 0 | 0 | 0 | 6301.751 | 16395.8634 | 11190.5136 | 50046.4638 | 961560.8286 | 3767508.2258 | 3767508.2258 | 5798963.8404 | 2644637.3607 | 0 | 4779115.5182 | 16990224.9452 | 10000000 | 0.00054341 | 8794724.4287 | 31266108.9284 | 179292.3532 | 637401.921
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.55509 | 0.060843 | 0.00021981 | 4 | 6018155.1951 | 20586529.5494 | 122688.2338 | 419684.2502 | 31.0231 | 1.2193 | 31.4424 | 26449.1162 | 0 | 47895.021 | 0 | 0 | 0 | 0 | 28994.2135 | 75436.9961 | 51487.2999 | 230262.6467 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5291490.0227 | 18100798.6969 | 100 | 0.00087925 | 6018155.1951 | 20586529.5494 | 122688.2338 | 419684.2502
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75975 | 0.087602 | 0.0003473 | 4 | 3861168.7109 | 13081889.5845 | 78715.1468 | 266692.0137 | 31.579 | 1.2518 | 28.8134 | 33936.9474 | 0 | 63192.3644 | 0 | 0 | 0 | 589.2936 | 38110.2561 | 99155.069 | 67675.372 | 302659.3026 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5363886.6786 | 18173195.3528 | 133.3521 | 0.0013892 | 3861168.7109 | 13081889.5845 | 78715.1468 | 266692.0137
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.99609 | 0.11867 | 0.00051447 | 4 | 2642507.0168 | 8866983.271 | 53871.0798 | 180765.4475 | 31.9901 | 1.2732 | 33.7488 | 41816.8124 | 0 | 79829.7987 | 0 | 0 | 0 | 0 | 47442.1783 | 123434.8162 | 84246.7984 | 376770.404 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5437997.78 | 18247306.4542 | 177.8279 | 0.0020579 | 2642507.0168 | 8866983.271 | 53871.0798 | 180765.4475
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.16449 | 0.00075629 | 4 | 1832088.4514 | 6066321.6778 | 37349.6012 | 123670.1727 | 32.3689 | 1.2914 | 37.025 | 52419.6324 | 0 | 102932.8619 | 0 | 0 | 0 | 0 | 60587.4728 | 157636.176 | 107589.9292 | 481166.0723 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5542393.4483 | 18351702.1225 | 237.1374 | 0.0030252 | 1832088.4514 | 6066321.6778 | 37349.6012 | 123670.1727
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.22293 | 0.0010655 | 4 | 1329454.5335 | 4334852.3303 | 27102.7289 | 88371.8281 | 32.6605 | 1.3041 | 138.1961 | 64711.659 | 0 | 130636.2441 | 0 | 0 | 0 | 0 | 76185.6822 | 198219.5173 | 135288.8935 | 605041.9961 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5666269.3721 | 18475578.0463 | 316.2278 | 0.0042621 | 1329454.5335 | 4334852.3303 | 27102.7289 | 88371.8281
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.29992 | 0.0014765 | 4 | 985187.9201 | 3153995.239 | 20084.3883 | 64298.459 | 32.8907 | 1.3137 | 189.4145 | 79517.3695 | 0 | 165035.9298 | 0 | 0 | 0 | 0 | 95375.7867 | 248148.2328 | 169366.2678 | 757443.5867 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 5818670.9628 | 18627979.6369 | 421.6965 | 0.0059062 | 985187.9201 | 3153995.239 | 20084.3883 | 64298.459
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1684 | 0.40521 | 0.0020398 | 4 | 737008.8782 | 2306955.9043 | 15024.9229 | 47030.4165 | 33.0756 | 1.3211 | 261.8837 | 98020.5315 | 0 | 209374.4192 | 0 | 0 | 0 | 0 | 119884.0308 | 311913.6565 | 212887.4798 | 952080.1179 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 6013307.4939 | 18822616.1681 | 562.3413 | 0.0081591 | 737008.8782 | 2306955.9043 | 15024.9229 | 47030.4165
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2286 | 0.54526 | 0.0027882 | 4 | 560848.6569 | 1709358.0615 | 11433.6585 | 34847.5762 | 33.2168 | 1.3264 | 42.876 | 120513.7062 | 0 | 264959.9055 | 0 | 0 | 0 | 0 | 150334.7086 | 391140.0738 | 266961.1375 | 1193909.5317 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 6255136.9078 | 19064445.5819 | 749.8942 | 0.011153 | 560848.6569 | 1709358.0615 | 11433.6585 | 34847.5762
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6318 | 0.73066 | 0.0037744 | 4 | 434142.8077 | 1282581.7984 | 8850.5884 | 26147.1648 | 33.3216 | 1.33 | 33.3151 | 147755.1661 | 0 | 334363.6312 | 0 | 0 | 0 | 0 | 188026.3309 | 489205.9435 | 333893.1086 | 1493244.1803 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 6554471.5564 | 19363780.2305 | 1000 | 0.015098 | 434142.8077 | 1282581.7984 | 8850.5884 | 26147.1648
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5273 | 0.98106 | 0.005098 | 4 | 339965.723 | 968117.8002 | 6930.6611 | 19736.3908 | 33.3978 | 1.3323 | 40.4206 | 181427.9097 | 0 | 422775.3451 | 0 | 0 | 0 | 0 | 235639.2694 | 613085.0426 | 418443.1392 | 1871370.706 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 6932598.082 | 19741906.7562 | 1333.5214 | 0.020392 | 339965.723 | 968117.8002 | 6930.6611 | 19736.3908
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0286 | 1.3117 | 0.0068054 | 4 | 271827.2275 | 742382.347 | 5541.5657 | 15134.4683 | 33.4465 | 1.3325 | 49.3032 | 222048.4067 | 0 | 532933.6601 | 0 | 0 | 0 | 0 | 294443.0061 | 766080.3033 | 522865.5483 | 2338370.9246 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 7399598.3006 | 20208906.9748 | 1778.2794 | 0.027222 | 271827.2275 | 742382.347 | 5541.5657 | 15134.4683
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3616 | 1.7523 | 0.0090095 | 4 | 221482.527 | 576921.7412 | 4515.2209 | 11761.33 | 33.4671 | 1.3308 | 40.3572 | 271487.5339 | 0 | 671462.0105 | 0 | 0 | 0 | 0 | 367750.3223 | 956810.9027 | 653043.1016 | 2920553.8711 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 7981781.2472 | 20791089.9213 | 2371.3737 | 0.036038 | 221482.527 | 576921.7412 | 4515.2209 | 11761.33
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.805 | 2.3396 | 0.011768 | 4 | 184983.6746 | 457101.9313 | 3771.1424 | 9318.6411 | 33.4542 | 1.3258 | 29.5923 | 331477.6352 | 0 | 845833.6535 | 0 | 0 | 0 | 0 | 459151.4026 | 1194617.7646 | 815351.1713 | 3646431.6272 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 8707659.0032 | 21516967.6774 | 3162.2777 | 0.047073 | 184983.6746 | 457101.9313 | 3771.1424 | 9318.6411
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.717 | 3.1207 | 0.015028 | 4 | 159866.7179 | 372963.5864 | 3259.0993 | 7603.3672 | 33.3931 | 1.316 | 32.844 | 403665.8785 | 0 | 1064861.9087 | 0 | 0 | 0 | 0 | 572725.837 | 1490115.1457 | 1017034.2058 | 4548402.9757 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 9609630.3518 | 22418939.0259 | 4216.965 | 0.06011 | 159866.7179 | 372963.5864 | 3259.0993 | 7603.3672
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.5368 | 4.1549 | 0.018305 | 4 | 146442.1726 | 321383.4582 | 2985.4218 | 6551.8365 | 33.2585 | 1.2969 | 50.9241 | 488921.7062 | 0 | 1338942.4008 | 0 | 0 | 0 | 0 | 712867.0017 | 1854733.7093 | 1265893.8676 | 5661358.6856 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 10722586.0617 | 23531894.7358 | 5623.4133 | 0.073221 | 146442.1726 | 321383.4582 | 2985.4218 | 6551.8365
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.6813 | 0.019434 | 4 | 144866.8068 | 309649.2127 | 2953.3058 | 6312.618 | 33.1685 | 1.2851 | 54.4443 | 528583.875 | 0 | 1473172.9232 | 0 | 0 | 0 | 0 | 780685.1513 | 2031182.6231 | 1386323.8769 | 6199948.4495 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11261175.8256 | 24070484.4998 | 7498.9421 | 0.077735 | 144866.8068 | 309649.2127 | 2953.3058 | 6312.618
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.6812 | 0.019438 | 4 | 144836.5806 | 309586.2559 | 2952.6896 | 6311.3346 | 33.1682 | 1.2851 | 54.3299 | 528584.1631 | 0 | 1473136.1997 | 0 | 0 | 0 | 0 | 780670.9415 | 2031145.6522 | 1386298.6435 | 6199835.6001 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11261062.9762 | 24070371.6504 | 10000 | 0.07775 | 144836.5806 | 309586.2559 | 2952.6896 | 6311.3346
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.6811 | 0.01944 | 4 | 144813.8576 | 309539.0079 | 2952.2264 | 6310.3714 | 33.1681 | 1.2851 | 54.9406 | 528583.9791 | 0 | 1473107.2004 | 0 | 0 | 0 | 0 | 780659.56 | 2031116.0398 | 1386278.4325 | 6199745.2118 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11260972.5878 | 24070281.262 | 13335.2143 | 0.077762 | 144813.8576 | 309539.0079 | 2952.2264 | 6310.3714
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.681 | 0.019441 | 4 | 144806.1738 | 309523.2671 | 2952.0697 | 6310.0505 | 33.1679 | 1.2851 | 55.27 | 528582.7456 | 0 | 1473093.3533 | 0 | 0 | 0 | 0 | 780653.6786 | 2031100.7376 | 1386267.9884 | 6199698.5035 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11260925.8795 | 24070234.5537 | 17782.7941 | 0.077766 | 144806.1738 | 309523.2671 | 2952.0697 | 6310.0505
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.681 | 0.019441 | 4 | 144810.249 | 309532.1441 | 2952.1528 | 6310.2314 | 33.1679 | 1.2851 | 55.872 | 528580.7769 | 0 | 1473091.6519 | 0 | 0 | 0 | 0 | 780652.2472 | 2031097.0135 | 1386265.4466 | 6199687.1361 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11260914.5122 | 24070223.1864 | 23713.7371 | 0.077763 | 144810.249 | 309532.1441 | 2952.1528 | 6310.2314
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5191 | 4.681 | 0.019439 | 4 | 144821.004 | 309554.9815 | 2952.3721 | 6310.697 | 33.1678 | 1.2851 | 55.4064 | 528578.5097 | 0 | 1473097.2595 | 0 | 0 | 0 | 0 | 780653.55 | 2031100.403 | 1386267.76 | 6199697.4821 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11260924.8581 | 24070233.5323 | 31622.7766 | 0.077758 | 144821.004 | 309554.9815 | 2952.3721 | 6310.697
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6785 | 0.019433 | 4 | 144834.3964 | 309621.1924 | 2952.6451 | 6312.0468 | 33.1683 | 1.2852 | 54.3904 | 528388.3483 | 0 | 1472458.1726 | 0 | 0 | 0 | 0 | 780330.1432 | 2030258.9648 | 1385693.4611 | 6197129.09 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258356.4661 | 24067665.1403 | 42169.6503 | 0.077733 | 144834.3964 | 309621.1924 | 2952.6451 | 6312.0468
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6785 | 0.019431 | 4 | 144847.8795 | 309649.6607 | 2952.9199 | 6312.6272 | 33.1683 | 1.2852 | 54.4868 | 528386.3287 | 0 | 1472468.0326 | 0 | 0 | 0 | 0 | 780333.2009 | 2030266.9204 | 1385698.891 | 6197153.3735 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258380.7495 | 24067689.4237 | 56234.1325 | 0.077726 | 144847.8795 | 309649.6607 | 2952.9199 | 6312.6272
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6786 | 0.01943 | 4 | 144860.1319 | 309675.5087 | 2953.1697 | 6313.1541 | 33.1683 | 1.2851 | 54.4897 | 528384.6004 | 0 | 1472477.3587 | 0 | 0 | 0 | 0 | 780336.1641 | 2030274.6299 | 1385704.1529 | 6197176.906 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258404.282 | 24067712.9562 | 74989.4209 | 0.077719 | 144860.1319 | 309675.5087 | 2953.1697 | 6313.1541
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6786 | 0.019428 | 4 | 144870.6133 | 309697.6099 | 2953.3834 | 6313.6047 | 33.1683 | 1.2851 | 54.5347 | 528383.1756 | 0 | 1472485.5201 | 0 | 0 | 0 | 0 | 780338.7913 | 2030281.4655 | 1385708.8183 | 6197197.7708 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258425.1469 | 24067733.821 | 100000 | 0.077714 | 144870.6133 | 309697.6099 | 2953.3834 | 6313.6047
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6786 | 0.019427 | 4 | 144879.2395 | 309715.7935 | 2953.5593 | 6313.9754 | 33.1683 | 1.2851 | 53.567 | 528382.0311 | 0 | 1472492.3322 | 0 | 0 | 0 | 0 | 780341.0017 | 2030287.2164 | 1385712.7434 | 6197215.3246 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258442.7007 | 24067751.3748 | 133352.1432 | 0.077709 | 144879.2395 | 309715.7935 | 2953.5593 | 6313.9754
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4996 | 4.6786 | 0.019426 | 4 | 144886.1559 | 309730.3701 | 2953.7003 | 6314.2725 | 33.1683 | 1.2851 | 53.9952 | 528381.1283 | 0 | 1472497.8448 | 0 | 0 | 0 | 0 | 780342.7995 | 2030291.8941 | 1385715.936 | 6197229.6029 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11258456.9789 | 24067765.6531 | 177827.941 | 0.077706 | 144886.1559 | 309730.3701 | 2953.7003 | 6314.2725
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019421 | 4 | 144891.5992 | 309779.7678 | 2953.8112 | 6315.2796 | 33.1688 | 1.2852 | 51.4118 | 528192.4738 | 0 | 1471854.0477 | 0 | 0 | 0 | 0 | 780018.1434 | 2029447.2054 | 1385139.4186 | 6194651.2889 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255878.665 | 24065187.3391 | 237137.3706 | 0.077685 | 144891.5992 | 309779.7678 | 2953.8112 | 6315.2796
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019421 | 4 | 144895.826 | 309788.6745 | 2953.8974 | 6315.4612 | 33.1688 | 1.2851 | 50.7634 | 528191.9338 | 0 | 1471857.4554 | 0 | 0 | 0 | 0 | 780019.2618 | 2029450.1153 | 1385141.4047 | 6194660.1712 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255887.5472 | 24065196.2214 | 316227.766 | 0.077683 | 144895.826 | 309788.6745 | 2953.8974 | 6315.4612
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.01942 | 4 | 144899.0804 | 309795.5319 | 2953.9637 | 6315.6009 | 33.1688 | 1.2851 | 51.3965 | 528191.5205 | 0 | 1471860.0875 | 0 | 0 | 0 | 0 | 780020.1271 | 2029452.3667 | 1385142.9413 | 6194667.0432 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255894.4193 | 24065203.0934 | 421696.5034 | 0.077681 | 144899.0804 | 309795.5319 | 2953.9637 | 6315.6009
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.01942 | 4 | 144901.5692 | 309800.7756 | 2954.0145 | 6315.7078 | 33.1688 | 1.2851 | 52.4943 | 528191.2058 | 0 | 1471862.1049 | 0 | 0 | 0 | 0 | 780020.7912 | 2029454.0944 | 1385144.1205 | 6194672.3168 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255899.6928 | 24065208.367 | 562341.3252 | 0.07768 | 144901.5692 | 309800.7756 | 2954.0145 | 6315.7078
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.01942 | 4 | 144903.4629 | 309804.7654 | 2954.0531 | 6315.7892 | 33.1688 | 1.2851 | 49.8472 | 528190.9671 | 0 | 1471863.6425 | 0 | 0 | 0 | 0 | 780021.2977 | 2029455.4123 | 1385145.02 | 6194676.3396 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255903.7156 | 24065212.3898 | 749894.2093 | 0.077679 | 144903.4629 | 309804.7654 | 2954.0531 | 6315.7892
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144904.8984 | 309807.7899 | 2954.0824 | 6315.8508 | 33.1688 | 1.2851 | 49.6186 | 528190.7865 | 0 | 1471864.8095 | 0 | 0 | 0 | 0 | 780021.6824 | 2029456.4133 | 1385145.7032 | 6194679.3949 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255906.7709 | 24065215.4451 | 1000000 | 0.077678 | 144904.8984 | 309807.7899 | 2954.0824 | 6315.8508
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144905.9837 | 309810.0764 | 2954.1045 | 6315.8975 | 33.1688 | 1.2851 | 49.5257 | 528190.6503 | 0 | 1471865.6925 | 0 | 0 | 0 | 0 | 780021.9737 | 2029457.171 | 1385146.2204 | 6194681.7079 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255909.0839 | 24065217.7581 | 1333521.4322 | 0.077677 | 144905.9837 | 309810.0764 | 2954.1045 | 6315.8975
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144906.8025 | 309811.8013 | 2954.1212 | 6315.9326 | 33.1688 | 1.2851 | 50.4911 | 528190.5476 | 0 | 1471866.3592 | 0 | 0 | 0 | 0 | 780022.1936 | 2029457.7433 | 1385146.611 | 6194683.4547 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255910.8307 | 24065219.5049 | 1778279.41 | 0.077677 | 144906.8025 | 309811.8013 | 2954.1212 | 6315.9326
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144907.4193 | 309813.1007 | 2954.1337 | 6315.9591 | 33.1688 | 1.2851 | 49.9615 | 528190.4703 | 0 | 1471866.8616 | 0 | 0 | 0 | 0 | 780022.3595 | 2029458.1747 | 1385146.9054 | 6194684.7715 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255912.1476 | 24065220.8217 | 2371373.7057 | 0.077677 | 144907.4193 | 309813.1007 | 2954.1337 | 6315.9591
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144907.8834 | 309814.0785 | 2954.1432 | 6315.979 | 33.1688 | 1.2851 | 49.4501 | 528190.4122 | 0 | 1471867.2398 | 0 | 0 | 0 | 0 | 780022.4843 | 2029458.4995 | 1385147.1271 | 6194685.7629 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255913.139 | 24065221.8132 | 3162277.6602 | 0.077676 | 144907.8834 | 309814.0785 | 2954.1432 | 6315.979
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144908.2323 | 309814.8135 | 2954.1503 | 6315.994 | 33.1688 | 1.2851 | 50.1228 | 528190.3686 | 0 | 1471867.5242 | 0 | 0 | 0 | 0 | 780022.5782 | 2029458.7438 | 1385147.2938 | 6194686.5086 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255913.8846 | 24065222.5588 | 4216965.0343 | 0.077676 | 144908.2323 | 309814.8135 | 2954.1503 | 6315.994
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144908.4944 | 309815.3658 | 2954.1557 | 6316.0053 | 33.1688 | 1.2851 | 50.2516 | 528190.3358 | 0 | 1471867.7379 | 0 | 0 | 0 | 0 | 780022.6487 | 2029458.9274 | 1385147.4192 | 6194687.069 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255914.445 | 24065223.1192 | 5623413.2519 | 0.077676 | 144908.4944 | 309815.3658 | 2954.1557 | 6316.0053
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144908.6913 | 309815.7805 | 2954.1597 | 6316.0137 | 33.1688 | 1.2851 | 51.5058 | 528190.3112 | 0 | 1471867.8984 | 0 | 0 | 0 | 0 | 780022.7017 | 2029459.0653 | 1385147.5133 | 6194687.4899 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255914.866 | 24065223.5402 | 7498942.0933 | 0.077676 | 144908.6913 | 309815.7805 | 2954.1597 | 6316.0137
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 4.6761 | 0.019419 | 4 | 144908.8391 | 309816.0918 | 2954.1627 | 6316.0201 | 33.1688 | 1.2851 | 51.6687 | 528190.2927 | 0 | 1471868.0189 | 0 | 0 | 0 | 0 | 780022.7415 | 2029459.1688 | 1385147.584 | 6194687.806 | 961560.8286 | 4099666.5474 | 4099666.5474 | 5959114.5985 | 2750527.5283 | 0 | 11255915.182 | 24065223.8562 | 10000000 | 0.077676 | 144908.8391 | 309816.0918 | 2954.1627 | 6316.0201
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.53564 | 0.053875 | 0.00056366 | 4 | 2492598.6735 | 8445315.5893 | 50814.9954 | 172169.1814 | 32.5757 | 1.4868 | 30.9479 | 27879.3416 | 0 | 43372.7907 | 0 | 0 | 0 | 0 | 27788.3316 | 72299.5387 | 49345.9208 | 220685.9234 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 5619931.7119 | 19041210.8469 | 100 | 0.0022546 | 2492598.6735 | 8445315.5893 | 50814.9954 | 172169.1814
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.72086 | 0.077232 | 0.000833 | 4 | 1706685.0557 | 5734656.8473 | 34793.0833 | 116908.7365 | 33.1692 | 1.5328 | 26.7295 | 35576.9304 | 0 | 56868.127 | 0 | 0 | 0 | 366.6825 | 36196.5786 | 94176.0726 | 64277.1046 | 287461.4958 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 5686707.2843 | 19107986.4193 | 133.3521 | 0.003332 | 1706685.0557 | 5734656.8473 | 34793.0833 | 116908.7365
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.10712 | 0.0011927 | 4 | 1208124.8366 | 4021441.6761 | 24629.2589 | 81982.528 | 33.6603 | 1.5663 | 32.1677 | 44526.1758 | 0 | 73082.7084 | 0 | 0 | 0 | 0 | 45867.4648 | 119337.7348 | 81450.4561 | 364264.5399 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 5763510.3284 | 19184789.4634 | 177.8279 | 0.0047706 | 1208124.8366 | 4021441.6761 | 24629.2589 | 81982.528
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2667 | 0.1463 | 0.0016657 | 4 | 879330.0044 | 2893724.292 | 17926.3315 | 58992.4837 | 34.0697 | 1.5916 | 31.8753 | 55233.4737 | 0 | 93109.2449 | 0 | 0 | 0 | 0 | 57853.6602 | 150523.3565 | 102735.2838 | 459455.0192 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 5858700.8077 | 19279979.9427 | 237.1374 | 0.0066627 | 879330.0044 | 2893724.292 | 17926.3315 | 58992.4837
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.20239 | 0.0023293 | 4 | 642821.2082 | 2083289.7042 | 13104.7798 | 42470.6785 | 34.4281 | 1.612 | 132.626 | 69204.3708 | 0 | 120100.4671 | 0 | 0 | 0 | 1223.0397 | 74305.8723 | 193328.6374 | 131950.7675 | 590113.1548 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 5989358.9433 | 19410638.0783 | 316.2278 | 0.0093173 | 642821.2082 | 2083289.7042 | 13104.7798 | 42470.6785
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 0.274 | 0.0032227 | 4 | 475996.0269 | 1517140.5625 | 9703.8228 | 30928.9625 | 34.7 | 1.6265 | 182.1327 | 85419.7051 | 0 | 152457.6144 | 0 | 0 | 0 | 0 | 92772.1546 | 241374.1161 | 164742.794 | 736766.3842 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 6136012.1727 | 19557291.3077 | 421.6965 | 0.012891 | 475996.0269 | 1517140.5625 | 9703.8228 | 30928.9625
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 0.3702 | 0.0043926 | 4 | 360098.4478 | 1123956.6995 | 7341.0939 | 22913.3776 | 34.9165 | 1.6376 | 253.2046 | 105353.7992 | 0 | 193459.8353 | 0 | 0 | 0 | 748.6897 | 116829.3064 | 303965.8903 | 207462.966 | 927820.4869 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 6327066.2755 | 19748345.4104 | 562.3413 | 0.01757 | 360098.4478 | 1123956.6995 | 7341.0939 | 22913.3776
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0265 | 0.49643 | 0.0059491 | 4 | 275499.5765 | 839505.8251 | 5616.4315 | 17114.4618 | 35.0817 | 1.6457 | 34.2941 | 129266.1872 | 0 | 244172.1409 | 0 | 0 | 0 | 0 | 145640.948 | 378927.8716 | 258626.0585 | 1156633.2062 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 6555878.9947 | 19977158.1297 | 749.8942 | 0.023796 | 275499.5765 | 839505.8251 | 5616.4315 | 17114.4618
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3734 | 0.66744 | 0.0080421 | 4 | 212892.3418 | 630109.7267 | 4340.0983 | 12845.6391 | 35.2093 | 1.6515 | 41.0049 | 158918.1142 | 0 | 308977.8878 | 0 | 0 | 0 | 0 | 182479.4408 | 474774.0732 | 324043.0606 | 1449192.5766 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 6848438.3652 | 20269717.5001 | 1000 | 0.032169 | 212892.3418 | 630109.7267 | 4340.0983 | 12845.6391
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1763 | 0.89632 | 0.010837 | 4 | 166424.4154 | 476037.991 | 3392.7868 | 9704.6783 | 35.3033 | 1.6554 | 49.6253 | 195236.0863 | 0 | 390767.0507 | 0 | 0 | 0 | 0 | 228541.2234 | 594617.3831 | 405838.5822 | 1815000.3258 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 7214246.1143 | 20635525.2493 | 1333.5214 | 0.043348 | 166424.4154 | 476037.991 | 3392.7868 | 9704.6783
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5681 | 1.2002 | 0.014514 | 4 | 132078.286 | 363252.1733 | 2692.5945 | 7405.3869 | 35.367 | 1.657 | 43.8257 | 239317.932 | 0 | 493212.6035 | 0 | 0 | 0 | 0 | 285686.9089 | 743298.7344 | 507316.6595 | 2268832.8382 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 7668078.6268 | 21089357.7617 | 1778.2794 | 0.058057 | 132078.286 | 363252.1733 | 2692.5945 | 7405.3869
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7502 | 1.6043 | 0.019355 | 4 | 106331.5128 | 279685.4402 | 2167.7117 | 5701.766 | 35.4015 | 1.6566 | 40.7022 | 292949.093 | 0 | 621756.0171 | 0 | 0 | 0 | 0 | 356734.993 | 928151.2753 | 633482.317 | 2833073.6953 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 8232319.4839 | 21653598.6188 | 2371.3737 | 0.077421 | 106331.5128 | 279685.4402 | 2167.7117 | 5701.766
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9742 | 2.1408 | 0.025641 | 4 | 87093.4002 | 217951.2878 | 1775.5168 | 4443.2318 | 35.4036 | 1.653 | 41.435 | 357928.6697 | 0 | 782882.7382 | 0 | 0 | 0 | 0 | 444916.4491 | 1157581.3356 | 790073.0475 | 3533382.24 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 8932628.0286 | 22353907.1635 | 3162.2777 | 0.10256 | 87093.4002 | 217951.2878 | 1775.5168 | 4443.2318
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6085 | 2.8561 | 0.0337 | 4 | 72737.4334 | 172301.1864 | 1482.851 | 3512.5927 | 35.3624 | 1.6448 | 51.1429 | 436695.1351 | 0 | 985798.1636 | 0 | 0 | 0 | 0 | 554772.3865 | 1443403.9501 | 985152.855 | 4405822.4902 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 9805068.2787 | 23226347.4137 | 4216.965 | 0.1348 | 72737.4334 | 172301.1864 | 1482.851 | 3512.5927
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.0675 | 3.8035 | 0.043584 | 4 | 62422.7755 | 139407.7582 | 1272.5727 | 2842.0157 | 35.2559 | 1.6285 | 52.2595 | 530673.8741 | 0 | 1239704.7677 | 0 | 0 | 0 | 0 | 690447.6703 | 1796403.2079 | 1226082.1018 | 5483311.6218 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 10882557.4103 | 24303836.5453 | 5623.4133 | 0.17434 | 62422.7755 | 139407.7582 | 1272.5727 | 2842.0157
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.9238 | 5.0555 | 0.054794 | 4 | 55693.9486 | 116929.0445 | 1135.3965 | 2383.7567 | 35.0414 | 1.5983 | 47.609 | 640804.9147 | 0 | 1557124.6989 | 0 | 0 | 0 | 0 | 857192.5493 | 2230239.179 | 1522184.0665 | 6807545.4084 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 12206791.197 | 25628070.3319 | 7498.9421 | 0.21918 | 55693.9486 | 116929.0445 | 1135.3965 | 2383.7567
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.8131 | 6.6906 | 0.065136 | 4 | 52987.6748 | 104500.1533 | 1080.2254 | 2130.377 | 34.6376 | 1.5446 | 53.5317 | 764311.9483 | 0 | 1949830.4172 | 0 | 0 | 0 | 0 | 1058515.5226 | 2754040.2583 | 1879689.0662 | 8406387.2125 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13805633.0011 | 27226912.136 | 10000 | 0.26054 | 52987.6748 | 104500.1533 | 1080.2254 | 2130.377
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.9586 | 6.7096 | 0.065167 | 4 | 53029.6848 | 104517.7776 | 1081.0819 | 2130.7363 | 34.6304 | 1.5435 | 56.349 | 765498.3576 | 0 | 1954290.7039 | 0 | 0 | 0 | 0 | 1060717.734 | 2759769.9607 | 1883599.7058 | 8423876.4621 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13823122.2506 | 27244401.3856 | 13335.2143 | 0.26067 | 53029.6848 | 104517.7776 | 1081.0819 | 2130.7363
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.9003 | 6.7018 | 0.065119 | 4 | 53039.9537 | 104565.5553 | 1081.2912 | 2131.7103 | 34.6309 | 1.5437 | 51.6602 | 764934.392 | 0 | 1952469.3677 | 0 | 0 | 0 | 0 | 1059787.4663 | 2757349.5949 | 1881947.7564 | 8416488.5772 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13815734.3657 | 27237013.5007 | 17782.7941 | 0.26048 | 53039.9537 | 104565.5553 | 1081.2912 | 2131.7103
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.864 | 6.6969 | 0.065086 | 4 | 53049.5067 | 104601.8432 | 1081.4859 | 2132.4501 | 34.6308 | 1.5438 | 57.9041 | 764570.4619 | 0 | 1951322.9962 | 0 | 0 | 0 | 0 | 1059198.4487 | 2755817.0919 | 1880901.7916 | 8411810.7903 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13811056.5788 | 27232335.7138 | 23713.7371 | 0.26034 | 53049.5067 | 104601.8432 | 1081.4859 | 2132.4501
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.8271 | 6.692 | 0.065053 | 4 | 53058.5309 | 104637.0213 | 1081.6699 | 2133.1672 | 34.631 | 1.5439 | 54.0206 | 764209.3864 | 0 | 1950181.1415 | 0 | 0 | 0 | 0 | 1058612.3059 | 2754292.0687 | 1879860.9319 | 8407155.8344 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13806401.623 | 27227680.7579 | 31622.7766 | 0.26021 | 53058.5309 | 104637.0213 | 1081.6699 | 2133.1672
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7882 | 6.687 | 0.06502 | 4 | 53066.7309 | 104671.2136 | 1081.8371 | 2133.8643 | 34.6316 | 1.544 | 51.2384 | 763837.9623 | 0 | 1948995.8862 | 0 | 0 | 0 | 0 | 1058005.2009 | 2752712.5061 | 1878782.848 | 8402334.4036 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13801580.1922 | 27222859.3271 | 42169.6503 | 0.26008 | 53066.7309 | 104671.2136 | 1081.8371 | 2133.8643
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7734 | 6.685 | 0.065002 | 4 | 53073.8609 | 104692.4019 | 1081.9824 | 2134.2962 | 34.6314 | 1.544 | 58.9883 | 763682.5085 | 0 | 1948536.3004 | 0 | 0 | 0 | 0 | 1057765.3355 | 2752088.4254 | 1878356.9001 | 8400429.4698 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13799675.2584 | 27220954.3933 | 56234.1325 | 0.26001 | 53073.8609 | 104692.4019 | 1081.9824 | 2134.2962
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7493 | 6.6819 | 0.064981 | 4 | 53079.8408 | 104715.2897 | 1082.1043 | 2134.7628 | 34.6317 | 1.5441 | 58.0746 | 763452.0447 | 0 | 1947809.6638 | 0 | 0 | 0 | 0 | 1057392.0663 | 2751117.2556 | 1877694.0568 | 8397465.0872 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13796710.8758 | 27217990.0107 | 74989.4209 | 0.25992 | 53079.8408 | 104715.2897 | 1082.1043 | 2134.7628
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7345 | 6.68 | 0.064966 | 4 | 53084.7161 | 104731.777 | 1082.2037 | 2135.0989 | 34.6318 | 1.5441 | 57.1161 | 763306.7573 | 0 | 1947362.4818 | 0 | 0 | 0 | 0 | 1057161.0032 | 2750516.0768 | 1877283.7399 | 8395630.059 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13794875.8475 | 27216154.9824 | 100000 | 0.25987 | 53084.7161 | 104731.777 | 1082.2037 | 2135.0989
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7151 | 6.6775 | 0.06495 | 4 | 53088.6082 | 104748.3107 | 1082.2831 | 2135.436 | 34.6322 | 1.5442 | 56.8462 | 763124.8886 | 0 | 1946780.9139 | 0 | 0 | 0 | 0 | 1056863.263 | 2749741.4178 | 1876755.0192 | 8393265.5024 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13792511.2909 | 27213790.4259 | 133352.1432 | 0.2598 | 53088.6082 | 104748.3107 | 1082.2831 | 2135.436
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7151 | 6.6775 | 0.064947 | 4 | 53091.6652 | 104754.4906 | 1082.3454 | 2135.562 | 34.6319 | 1.5441 | 54.0076 | 763115.1587 | 0 | 1946777.8731 | 0 | 0 | 0 | 0 | 1056858.2824 | 2749728.4593 | 1876746.1747 | 8393225.9481 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13792471.7367 | 27213750.8716 | 177827.941 | 0.25979 | 53091.6652 | 104754.4906 | 1082.3454 | 2135.562
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6956 | 6.675 | 0.064933 | 4 | 53094.0399 | 104767.9399 | 1082.3938 | 2135.8362 | 34.6325 | 1.5442 | 52.2371 | 762938.5389 | 0 | 1946199.2462 | 0 | 0 | 0 | 0 | 1056563.7362 | 2748962.1106 | 1876223.126 | 8390886.7579 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13790132.5464 | 27211411.6814 | 237137.3706 | 0.25973 | 53094.0399 | 104767.9399 | 1082.3938 | 2135.8362
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7003 | 6.6756 | 0.064933 | 4 | 53095.866 | 104769.5619 | 1082.431 | 2135.8692 | 34.6322 | 1.5442 | 61.3344 | 762973.1836 | 0 | 1946335.3253 | 0 | 0 | 0 | 0 | 1056630.3185 | 2749135.344 | 1876341.3614 | 8391415.5329 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13790661.3214 | 27211940.4564 | 316227.766 | 0.25973 | 53095.866 | 104769.5619 | 1082.431 | 2135.8692
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7003 | 6.6756 | 0.064931 | 4 | 53097.2636 | 104772.3786 | 1082.4595 | 2135.9267 | 34.632 | 1.5442 | 61.7944 | 762968.9075 | 0 | 1946334.5182 | 0 | 0 | 0 | 0 | 1056628.336 | 2749130.1861 | 1876337.841 | 8391399.7888 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13790645.5774 | 27211924.7123 | 421696.5034 | 0.25972 | 53097.2636 | 104772.3786 | 1082.4595 | 2135.9267
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064919 | 4 | 53098.3272 | 104783.1794 | 1082.4812 | 2136.1468 | 34.6327 | 1.5442 | 60.6669 | 762796.4828 | 0 | 1945757.2788 | 0 | 0 | 0 | 0 | 1056335.967 | 2748369.5018 | 1875818.6584 | 8389077.8888 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788323.6773 | 27209602.8123 | 562341.3252 | 0.25968 | 53098.3272 | 104783.1794 | 1082.4812 | 2136.1468
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064918 | 4 | 53099.1324 | 104784.8008 | 1082.4976 | 2136.1799 | 34.6326 | 1.5442 | 60.1017 | 762794.0505 | 0 | 1945756.9193 | 0 | 0 | 0 | 0 | 1056334.8782 | 2748366.6691 | 1875816.7249 | 8389069.2421 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788315.0306 | 27209594.1656 | 749894.2093 | 0.25967 | 53099.1324 | 104784.8008 | 1082.4976 | 2136.1799
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064917 | 4 | 53099.7413 | 104786.0265 | 1082.51 | 2136.2049 | 34.6326 | 1.5442 | 60.1134 | 762792.2184 | 0 | 1945756.6717 | 0 | 0 | 0 | 0 | 1056334.0671 | 2748364.5587 | 1875815.2846 | 8389062.8005 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788308.589 | 27209587.724 | 1000000 | 0.25967 | 53099.7413 | 104786.0265 | 1082.51 | 2136.2049
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064916 | 4 | 53100.2008 | 104786.9512 | 1082.5194 | 2136.2237 | 34.6325 | 1.5442 | 60.0685 | 762790.8398 | 0 | 1945756.4984 | 0 | 0 | 0 | 0 | 1056333.4619 | 2748362.9841 | 1875814.2099 | 8389057.9942 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788303.7827 | 27209582.9176 | 1333521.4322 | 0.25967 | 53100.2008 | 104786.9512 | 1082.5194 | 2136.2237
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064916 | 4 | 53100.547 | 104787.6478 | 1082.5265 | 2136.2379 | 34.6325 | 1.5442 | 60.9223 | 762789.8034 | 0 | 1945756.3755 | 0 | 0 | 0 | 0 | 1056333.0098 | 2748361.8078 | 1875813.407 | 8389054.4036 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788300.1921 | 27209579.3271 | 1778279.41 | 0.25966 | 53100.547 | 104787.6478 | 1082.5265 | 2136.2379
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064916 | 4 | 53100.8075 | 104788.172 | 1082.5318 | 2136.2486 | 34.6325 | 1.5442 | 61.3516 | 762789.0248 | 0 | 1945756.2873 | 0 | 0 | 0 | 0 | 1056332.6717 | 2748360.9282 | 1875812.8067 | 8389051.7188 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788297.5073 | 27209576.6423 | 2371373.7057 | 0.25966 | 53100.8075 | 104788.172 | 1082.5318 | 2136.2486
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064915 | 4 | 53101.0034 | 104788.5661 | 1082.5358 | 2136.2567 | 34.6325 | 1.5442 | 61.2515 | 762788.4401 | 0 | 1945756.2235 | 0 | 0 | 0 | 0 | 1056332.4188 | 2748360.2701 | 1875812.3575 | 8389049.7099 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788295.4984 | 27209574.6333 | 3162277.6602 | 0.25966 | 53101.0034 | 104788.5661 | 1082.5358 | 2136.2567
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064915 | 4 | 53101.1505 | 104788.8621 | 1082.5388 | 2136.2627 | 34.6325 | 1.5442 | 61.1813 | 762788.0011 | 0 | 1945756.1768 | 0 | 0 | 0 | 0 | 1056332.2294 | 2748359.7773 | 1875812.0212 | 8389048.2058 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788293.9944 | 27209573.1293 | 4216965.0343 | 0.25966 | 53101.1505 | 104788.8621 | 1082.5388 | 2136.2627
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064915 | 4 | 53101.2611 | 104789.0845 | 1082.541 | 2136.2672 | 34.6325 | 1.5442 | 61.3596 | 762787.6717 | 0 | 1945756.1425 | 0 | 0 | 0 | 0 | 1056332.0875 | 2748359.4083 | 1875811.7693 | 8389047.0793 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788292.8679 | 27209572.0028 | 5623413.2519 | 0.25966 | 53101.2611 | 104789.0845 | 1082.541 | 2136.2672
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064915 | 4 | 53101.344 | 104789.2514 | 1082.5427 | 2136.2706 | 34.6324 | 1.5442 | 61.4358 | 762787.4245 | 0 | 1945756.1172 | 0 | 0 | 0 | 0 | 1056331.9813 | 2748359.1318 | 1875811.5806 | 8389046.2354 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788292.0239 | 27209571.1589 | 7498942.0933 | 0.25966 | 53101.344 | 104789.2514 | 1082.5427 | 2136.2706
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6808 | 6.6731 | 0.064915 | 4 | 53101.4063 | 104789.3767 | 1082.544 | 2136.2732 | 34.6324 | 1.5442 | 61.9335 | 762787.239 | 0 | 1945756.0985 | 0 | 0 | 0 | 0 | 1056331.9016 | 2748358.9246 | 1875811.4392 | 8389045.6029 | 961560.8286 | 4437684.9599 | 4437684.9599 | 6124832.4428 | 2858761.7322 | 0 | 13788291.3915 | 27209570.5264 | 10000000 | 0.25966 | 53101.4063 | 104789.3767 | 1082.544 | 2136.2732
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.51156 | 0.047094 | 0.00080046 | 4 | 1860672.0573 | 6247857.197 | 37932.3166 | 127371.0198 | 34.1248 | 1.7529 | 27.381 | 28677.2457 | 0 | 39206.2644 | 0 | 0 | 0 | 1349.194 | 27000.7546 | 70250.4249 | 47947.3585 | 214431.2421 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 5957555.534 | 20004576.3432 | 100 | 0.0032018 | 1860672.0573 | 6247857.197 | 37932.3166 | 127371.0198
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.68196 | 0.068204 | 0.0011859 | 4 | 1269059.8618 | 4230375.9411 | 25871.5018 | 86241.9356 | 34.8231 | 1.8163 | 22.107 | 36648.5979 | 0 | 51491.6591 | 0 | 0 | 0 | 1186.9039 | 34837.5928 | 90640.2702 | 61863.8469 | 276668.8708 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6019793.1627 | 20066813.9719 | 133.3521 | 0.0047435 | 1269059.8618 | 4230375.9411 | 25871.5018 | 86241.9356
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.095709 | 0.0017128 | 4 | 889210.4377 | 2939545.752 | 18127.7575 | 59926.6162 | 35.4209 | 1.8641 | 37.1089 | 46110.4732 | 0 | 66547.9455 | 0 | 0 | 0 | 0 | 43936.7833 | 114314.4974 | 78021.9934 | 348931.6928 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6092055.9847 | 20139076.7939 | 177.8279 | 0.0068511 | 889210.4377 | 2939545.752 | 18127.7575 | 59926.6162
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2041 | 0.13294 | 0.0024131 | 4 | 641086.5655 | 2096380.537 | 13069.4168 | 42737.5528 | 35.9398 | 1.9014 | 87.0226 | 57830.8544 | 0 | 85804.0761 | 0 | 0 | 0 | 0 | 56017.6229 | 145746.364 | 99474.8882 | 444873.8056 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6187998.0975 | 20235018.9068 | 237.1374 | 0.0096524 | 641086.5655 | 2096380.537 | 13069.4168 | 42737.5528
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.18356 | 0.003374 | 4 | 467489.608 | 1508322.5191 | 9530.408 | 30749.1947 | 36.3752 | 1.9301 | 122.1291 | 72342.5089 | 0 | 110428.5879 | 0 | 0 | 0 | 0 | 71280.7278 | 185457.8319 | 126578.7811 | 566088.4376 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6309212.7295 | 20356233.5388 | 316.2278 | 0.013496 | 467489.608 | 1508322.5191 | 9530.408 | 30749.1947
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.25105 | 0.004642 | 4 | 348099.875 | 1104618.519 | 7096.4868 | 22519.1426 | 36.7247 | 1.9516 | 170.2397 | 89979.7953 | 0 | 141330.4237 | 0 | 0 | 0 | 1278.4828 | 90709.5937 | 236007.7557 | 161080.1428 | 720386.194 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6463510.4859 | 20510531.2952 | 421.6965 | 0.018568 | 348099.875 | 1104618.519 | 7096.4868 | 22519.1426
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8766 | 0.34035 | 0.0063449 | 4 | 261994.903 | 815472.9072 | 5341.1205 | 16624.5182 | 36.9986 | 1.9676 | 231.8131 | 111257.0918 | 0 | 179792.7228 | 0 | 0 | 0 | 1527.9589 | 114105.3317 | 296878.6667 | 202625.7903 | 906187.5621 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6649311.854 | 20696332.6633 | 562.3413 | 0.02538 | 261994.903 | 815472.9072 | 5341.1205 | 16624.5182
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 0.45828 | 0.0086325 | 4 | 199023.5795 | 605827.8832 | 4057.3649 | 12350.6208 | 37.2106 | 1.9796 | 43.3354 | 136942.3175 | 0 | 227636.571 | 0 | 0 | 0 | 0 | 142185.7665 | 369938.1982 | 252490.4217 | 1129193.275 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 6872317.5669 | 20919338.3762 | 749.8942 | 0.03453 | 199023.5795 | 605827.8832 | 4057.3649 | 12350.6208
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0982 | 0.61624 | 0.011656 | 4 | 153501.1853 | 454775.2124 | 3129.3293 | 9271.2078 | 37.3738 | 1.988 | 33.4765 | 168416.1016 | 0 | 288094.548 | 0 | 0 | 0 | 0 | 178039.1534 | 463221.3562 | 316158.0939 | 1413929.2531 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 7157053.545 | 21204074.3542 | 1000 | 0.046625 | 153501.1853 | 454775.2124 | 3129.3293 | 9271.2078
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8102 | 0.82894 | 0.01571 | 4 | 119623.2691 | 343153.7135 | 2438.6821 | 6995.6526 | 37.4969 | 1.9938 | 43.4858 | 207192.3005 | 0 | 364859.3666 | 0 | 0 | 0 | 777.9855 | 223403.5645 | 581250.2485 | 396715.2381 | 1774198.7036 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 7517322.9955 | 21564343.8048 | 1333.5214 | 0.062842 | 119623.2691 | 343153.7135 | 2438.6821 | 6995.6526
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0734 | 1.1099 | 0.021083 | 4 | 94348.8411 | 260920.824 | 1923.4287 | 5319.2239 | 37.5839 | 1.9977 | 46.9074 | 254113.0057 | 0 | 460493.1831 | 0 | 0 | 0 | 0 | 278696.4136 | 725110.8998 | 494903.0886 | 2213316.5908 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 7956440.8827 | 22003461.692 | 1778.2794 | 0.08433 | 94348.8411 | 260920.824 | 1923.4287 | 5319.2239
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0943 | 1.4852 | 0.028188 | 4 | 75450.3409 | 200032.3788 | 1538.1573 | 4077.9306 | 37.6385 | 1.9986 | 50.2322 | 311431.3883 | 0 | 581017.8076 | 0 | 0 | 0 | 0 | 348055.1864 | 905568.1991 | 618068.9034 | 2764141.4848 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 8507265.7767 | 22554286.586 | 2371.3737 | 0.11275 | 75450.3409 | 200032.3788 | 1538.1573 | 4077.9306
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1117 | 1.9841 | 0.037532 | 4 | 61225.0213 | 154792.9614 | 1248.1549 | 3155.6639 | 37.6595 | 1.9966 | 37.6798 | 381102.8986 | 0 | 732260.753 | 0 | 0 | 0 | 0 | 434211.8241 | 1129730.0973 | 771064.005 | 3448369.5781 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 9191493.87 | 23238514.6793 | 3162.2777 | 0.15013 | 61225.0213 | 154792.9614 | 1248.1549 | 3155.6639
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.4512 | 2.6473 | 0.049684 | 4 | 50523.5352 | 121205.1593 | 1029.9906 | 2470.9311 | 37.6389 | 1.9899 | 39.9741 | 465500.4206 | 0 | 922099.18 | 0 | 0 | 0 | 0 | 541163.8442 | 1407997.3147 | 960987.0987 | 4297747.8582 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 10040872.1501 | 24087892.9594 | 4216.965 | 0.19874 | 50523.5352 | 121205.1593 | 1029.9906 | 2470.9311
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.5354 | 3.5276 | 0.065172 | 4 | 42551.0613 | 96435.7715 | 867.4609 | 1965.9736 | 37.5587 | 1.9755 | 45.749 | 566967.5507 | 0 | 1160164.6218 | 0 | 0 | 0 | 0 | 673581.5473 | 1752521.0154 | 1196131.6037 | 5349366.3388 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 11092490.6307 | 25139511.4399 | 5623.4133 | 0.26069 | 42551.0613 | 96435.7715 | 867.4609 | 1965.9736
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8775 | 4.6882 | 0.084139 | 4 | 36794.0479 | 78531.7111 | 750.0964 | 1600.9752 | 37.3843 | 1.9489 | 43.5021 | 686900.9025 | 0 | 1456965.4891 | 0 | 0 | 0 | 0 | 836107.8927 | 2175381.2275 | 1484742.3874 | 6640097.8992 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 12383222.1911 | 26430243.0003 | 7498.9421 | 0.33656 | 36794.0479 | 78531.7111 | 750.0964 | 1600.9752
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.0823 | 6.2029 | 0.1055 | 4 | 33044.813 | 66331.8712 | 673.6632 | 1352.2649 | 37.0493 | 1.9012 | 45.5167 | 824236.7244 | 0 | 1823809.2236 | 0 | 0 | 0 | 0 | 1032737.9197 | 2686972.2234 | 1833913.7543 | 8201669.8454 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 13944794.1373 | 27991814.9466 | 10000 | 0.422 | 33044.813 | 66331.8712 | 673.6632 | 1352.2649
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.883 | 8.1581 | 0.12503 | 4 | 31586.0981 | 59672.5505 | 643.9253 | 1216.5057 | 36.4263 | 1.8158 | 45.3102 | 972601.0172 | 0 | 2273562.6663 | 0 | 0 | 0 | 0 | 1266003.8366 | 3293882.2896 | 2248142.3452 | 10054192.1549 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15797316.4468 | 29844337.256 | 13335.2143 | 0.50014 | 31586.0981 | 59672.5505 | 643.9253 | 1216.5057
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.824 | 8.1505 | 0.12488 | 4 | 31608.8791 | 59728.8171 | 644.3898 | 1217.6527 | 36.4241 | 1.8156 | 58.6505 | 971894.2704 | 0 | 2271869.9914 | 0 | 0 | 0 | 0 | 1265068.0621 | 3291447.5964 | 2246480.617 | 10046760.5373 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15789884.8292 | 29836905.6385 | 17782.7941 | 0.49954 | 31608.8791 | 59728.8171 | 644.3898 | 1217.6527
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.7313 | 8.1382 | 0.12475 | 4 | 31621.1468 | 59772.4308 | 644.6398 | 1218.5419 | 36.4244 | 1.8159 | 60.4648 | 970955.8484 | 0 | 2269108.2102 | 0 | 0 | 0 | 0 | 1263624.9829 | 3287693.0003 | 2243918.028 | 10035300.0698 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15778424.3617 | 29825445.171 | 23713.7371 | 0.49898 | 31621.1468 | 59772.4308 | 644.6398 | 1218.5419
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.6628 | 8.129 | 0.12464 | 4 | 31631.4515 | 59807.1901 | 644.8499 | 1219.2505 | 36.4244 | 1.8161 | 64.7557 | 970247.6263 | 0 | 2267053.607 | 0 | 0 | 0 | 0 | 1262547.481 | 3284889.5614 | 2242004.6234 | 10026742.8992 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15769867.1911 | 29816888.0003 | 31622.7766 | 0.49855 | 31631.4515 | 59807.1901 | 644.8499 | 1219.2505
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5922 | 8.1198 | 0.12454 | 4 | 31640.0477 | 59838.7998 | 645.0252 | 1219.8949 | 36.4251 | 1.8163 | 55.9544 | 969548.4102 | 0 | 2264980.0719 | 0 | 0 | 0 | 0 | 1261466.108 | 3282076.0508 | 2240084.3446 | 10018154.9856 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15761279.2775 | 29808300.0867 | 42169.6503 | 0.49814 | 31640.0477 | 59838.7998 | 645.0252 | 1219.8949
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5339 | 8.1122 | 0.12445 | 4 | 31647.0988 | 59864.7762 | 645.1689 | 1220.4244 | 36.4257 | 1.8165 | 51.0173 | 968973.6511 | 0 | 2263275.1357 | 0 | 0 | 0 | 0 | 1260577.0269 | 3279762.844 | 2238505.5334 | 10011094.1911 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15754218.483 | 29801239.2922 | 56234.1325 | 0.49781 | 31647.0988 | 59864.7762 | 645.1689 | 1220.4244
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4996 | 8.1076 | 0.1244 | 4 | 31652.7776 | 59883.1215 | 645.2847 | 1220.7984 | 36.4257 | 1.8166 | 57.5245 | 968618.7771 | 0 | 2262260.1176 | 0 | 0 | 0 | 0 | 1260042.7689 | 3278372.8144 | 2237556.8097 | 10006851.2877 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15749975.5796 | 29796996.3888 | 74989.4209 | 0.49759 | 31652.7776 | 59883.1215 | 645.2847 | 1220.7984
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4756 | 8.1044 | 0.12436 | 4 | 31657.2802 | 59897.0275 | 645.3765 | 1221.0819 | 36.4256 | 1.8166 | 57.7542 | 968364.2963 | 0 | 2261544.4441 | 0 | 0 | 0 | 0 | 1259664.4087 | 3277388.3989 | 2236884.9258 | 10003846.4738 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15746970.7657 | 29793991.5749 | 100000 | 0.49742 | 31657.2802 | 59897.0275 | 645.3765 | 1221.0819
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4413 | 8.1 | 0.12431 | 4 | 31660.8043 | 59910.9862 | 645.4483 | 1221.3665 | 36.4262 | 1.8167 | 52.8051 | 968037.0138 | 0 | 2260559.5802 | 0 | 0 | 0 | 0 | 1259152.6717 | 3276056.9639 | 2235976.1941 | 9999782.4238 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15742906.7157 | 29789927.5249 | 133352.1432 | 0.49724 | 31660.8043 | 59910.9862 | 645.4483 | 1221.3665
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4218 | 8.0975 | 0.12428 | 4 | 31663.5343 | 59920.3722 | 645.504 | 1221.5578 | 36.4264 | 1.8168 | 51.3741 | 967843.1188 | 0 | 2259994.3469 | 0 | 0 | 0 | 0 | 1258856.6116 | 3275286.6764 | 2235450.4571 | 9997431.2109 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15740555.5028 | 29787576.312 | 177827.941 | 0.49712 | 31663.5343 | 59920.3722 | 645.504 | 1221.5578
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.407 | 8.0956 | 0.12426 | 4 | 31665.6325 | 59927.5562 | 645.5467 | 1221.7043 | 36.4265 | 1.8168 | 58.7506 | 967695.3996 | 0 | 2259564.2386 | 0 | 0 | 0 | 0 | 1258631.2589 | 3274700.3549 | 2235050.2806 | 9995641.5327 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15738765.8246 | 29785786.6339 | 237137.3706 | 0.49703 | 31665.6325 | 59927.5562 | 645.5467 | 1221.7043
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.405 | 8.0953 | 0.12425 | 4 | 31667.235 | 59931.1793 | 645.5794 | 1221.7782 | 36.4262 | 1.8168 | 58.9218 | 967660.2579 | 0 | 2259493.2508 | 0 | 0 | 0 | 0 | 1258589.8684 | 3274592.6653 | 2234976.7802 | 9995312.8225 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15738437.1144 | 29785457.9237 | 316227.766 | 0.49699 | 31667.235 | 59931.1793 | 645.5794 | 1221.7782
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.405 | 8.0952 | 0.12424 | 4 | 31668.4544 | 59933.6253 | 645.6043 | 1221.828 | 36.4258 | 1.8168 | 57.219 | 967646.476 | 0 | 2259482.1896 | 0 | 0 | 0 | 0 | 1258580.1796 | 3274567.457 | 2234959.575 | 9995235.8773 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15738360.1692 | 29785380.9784 | 421696.5034 | 0.49697 | 31668.4544 | 59933.6253 | 645.6043 | 1221.828
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3876 | 8.0931 | 0.12422 | 4 | 31669.3779 | 59938.9681 | 645.6231 | 1221.9369 | 36.4264 | 1.8168 | 57.6463 | 967490.6399 | 0 | 2258991.8006 | 0 | 0 | 0 | 0 | 1258328.1518 | 3273911.7324 | 2234512.0295 | 9993234.3542 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15736358.6461 | 29783379.4554 | 562341.3252 | 0.4969 | 31669.3779 | 59938.9681 | 645.6231 | 1221.9369
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3876 | 8.093 | 0.12422 | 4 | 31670.0761 | 59940.3675 | 645.6373 | 1221.9655 | 36.4262 | 1.8168 | 57.3212 | 967482.8021 | 0 | 2258985.642 | 0 | 0 | 0 | 0 | 1258322.6932 | 3273897.5302 | 2234502.3362 | 9993191.0037 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15736315.2956 | 29783336.1049 | 749894.2093 | 0.49688 | 31670.0761 | 59940.3675 | 645.6373 | 1221.9655
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.383 | 8.0924 | 0.12421 | 4 | 31670.6029 | 59942.3512 | 645.6481 | 1222.0059 | 36.4263 | 1.8168 | 57.6108 | 967438.2415 | 0 | 2258852.8755 | 0 | 0 | 0 | 0 | 1258253.5356 | 3273717.5964 | 2234379.5277 | 9992641.7768 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15735766.0687 | 29782786.8779 | 1000000 | 0.49686 | 31670.6029 | 59942.3512 | 645.6481 | 1222.0059
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.383 | 8.0924 | 0.12421 | 4 | 31670.9997 | 59943.1462 | 645.6562 | 1222.0221 | 36.4262 | 1.8168 | 57.2358 | 967433.8038 | 0 | 2258849.4306 | 0 | 0 | 0 | 0 | 1258250.4614 | 3273709.598 | 2234374.0686 | 9992617.3624 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15735741.6543 | 29782762.4635 | 1333521.4322 | 0.49685 | 31670.9997 | 59943.1462 | 645.6562 | 1222.0221
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.383 | 8.0924 | 0.12421 | 4 | 31671.2984 | 59943.7443 | 645.6623 | 1222.0343 | 36.4261 | 1.8168 | 56.0346 | 967430.4683 | 0 | 2258846.8513 | 0 | 0 | 0 | 0 | 1258248.1547 | 3273703.5962 | 2234369.9723 | 9992599.0428 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15735723.3347 | 29782744.144 | 1778279.41 | 0.49684 | 31671.2984 | 59943.7443 | 645.6623 | 1222.0343
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.383 | 8.0924 | 0.12421 | 4 | 31671.5229 | 59944.194 | 645.6668 | 1222.0435 | 36.4261 | 1.8168 | 56.2132 | 967427.9626 | 0 | 2258844.9195 | 0 | 0 | 0 | 0 | 1258246.424 | 3273699.0935 | 2234366.8991 | 9992585.2987 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15735709.5906 | 29782730.3999 | 2371373.7057 | 0.49684 | 31671.5229 | 59944.194 | 645.6668 | 1222.0435
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3681 | 8.0906 | 0.1242 | 4 | 31671.6915 | 59947.5026 | 645.6703 | 1222.1109 | 36.4267 | 1.8169 | 56.3546 | 967302.3694 | 0 | 2258433.3603 | 0 | 0 | 0 | 0 | 1258036.9346 | 3273154.0449 | 2233994.8922 | 9990921.6013 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15734045.8932 | 29781066.7025 | 3162277.6602 | 0.49679 | 31671.6915 | 59947.5026 | 645.6703 | 1222.1109
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3681 | 8.0906 | 0.1242 | 4 | 31671.8181 | 59947.7561 | 645.6729 | 1222.1161 | 36.4267 | 1.8169 | 55.6568 | 967300.9589 | 0 | 2258432.2775 | 0 | 0 | 0 | 0 | 1258035.9622 | 3273151.515 | 2233993.1655 | 9990913.879 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15734038.1709 | 29781058.9802 | 4216965.0343 | 0.49678 | 31671.8181 | 59947.7561 | 645.6729 | 1222.1161
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3681 | 8.0906 | 0.1242 | 4 | 31671.9131 | 59947.9464 | 645.6748 | 1222.12 | 36.4267 | 1.8169 | 55.6288 | 967299.9005 | 0 | 2258431.4659 | 0 | 0 | 0 | 0 | 1258035.2329 | 3273149.6174 | 2233991.8704 | 9990908.087 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15734032.3789 | 29781053.1881 | 5623413.2519 | 0.49678 | 31671.9131 | 59947.9464 | 645.6748 | 1222.12
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3681 | 8.0906 | 0.1242 | 4 | 31671.9844 | 59948.0892 | 645.6762 | 1222.1229 | 36.4266 | 1.8169 | 55.6668 | 967299.1063 | 0 | 2258430.8575 | 0 | 0 | 0 | 0 | 1258034.6859 | 3273148.1942 | 2233990.899 | 9990903.7429 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15734028.0348 | 29781048.8441 | 7498942.0933 | 0.49678 | 31671.9844 | 59948.0892 | 645.6762 | 1222.1229
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.3681 | 8.0906 | 0.12419 | 4 | 31672.0379 | 59948.1963 | 645.6773 | 1222.1251 | 36.4266 | 1.8169 | 55.5606 | 967298.5105 | 0 | 2258430.4014 | 0 | 0 | 0 | 0 | 1258034.2756 | 3273147.1269 | 2233990.1706 | 9990900.485 | 961560.8286 | 4781563.4633 | 4781563.4633 | 6296117.3735 | 2969339.9724 | 0 | 15734024.7769 | 29781045.5862 | 10000000 | 0.49678 | 31672.0379 | 59948.1963 | 645.6773 | 1222.1251
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.47729 | 0.039772 | 0.00096247 | 4 | 1634962.7943 | 5449762.6063 | 33330.928 | 111100.7821 | 35.5462 | 2.0155 | 25.2224 | 28591.8128 | 0 | 34774.1786 | 0 | 0 | 0 | 1708.7264 | 25379.1399 | 66031.3162 | 45067.7301 | 201552.904 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6294415.7901 | 20980949.4872 | 100 | 0.0038499 | 1634962.7943 | 5449762.6063 | 33330.928 | 111100.7821
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.62825 | 0.058483 | 0.0014436 | 4 | 1099259.1026 | 3642628.0806 | 22409.8837 | 74259.9004 | 36.3827 | 2.1 | 27.2388 | 36540.6067 | 0 | 45707.6695 | 0 | 0 | 0 | 0 | 32076.8277 | 83457.3258 | 56961.3398 | 254743.7695 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6347606.6556 | 21034140.3527 | 133.3521 | 0.0057744 | 1099259.1026 | 3642628.0806 | 22409.8837 | 74259.9004
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | 0.085075 | 0.0021089 | 4 | 761762.308 | 2502808.7748 | 15529.555 | 51023.1422 | 37.1805 | 2.1705 | 31.55 | 46977.7136 | 0 | 60522.4151 | 0 | 0 | 0 | 0 | 41925.0502 | 109080.3806 | 74449.6011 | 332955.1606 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6425818.0467 | 21112351.7438 | 177.8279 | 0.0084355 | 761762.308 | 2502808.7748 | 15529.555 | 51023.1422
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1458 | 0.12179 | 0.0030034 | 4 | 543815.7917 | 1766305.4661 | 11086.4205 | 36008.526 | 37.8782 | 2.2252 | 81.6927 | 60122.1282 | 0 | 79812.4297 | 0 | 0 | 0 | 2235.4699 | 55446.3108 | 144259.9271 | 98460.3645 | 440336.6301 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6533199.5163 | 21219733.2133 | 237.1374 | 0.012014 | 543815.7917 | 1766305.4661 | 11086.4205 | 36008.526
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.16739 | 0.0042209 | 4 | 393334.9952 | 1263196.798 | 8018.6659 | 25751.9753 | 38.4117 | 2.2633 | 115.1318 | 74842.9335 | 0 | 102123.159 | 0 | 0 | 0 | 0 | 69016.7761 | 179567.4941 | 122558.5044 | 548108.8671 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6640971.7532 | 21327505.4503 | 316.2278 | 0.016884 | 393334.9952 | 1263196.798 | 8018.6659 | 25751.9753
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.22958 | 0.0058354 | 4 | 290771.4727 | 919971.0796 | 5927.7698 | 18754.8548 | 38.8612 | 2.2931 | 159.9853 | 93244.1083 | 0 | 130893.9114 | 0 | 0 | 0 | 0 | 87413.8277 | 227432.8486 | 155227.5924 | 694212.2883 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6787075.1745 | 21473608.8715 | 421.6965 | 0.023342 | 290771.4727 | 919971.0796 | 5927.7698 | 18754.8548
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7009 | 0.31327 | 0.0080163 | 4 | 217365.7086 | 675387.5987 | 4431.294 | 13768.6897 | 39.2228 | 2.3158 | 39.3128 | 115828.2451 | 0 | 167325.1534 | 0 | 0 | 0 | 0 | 110429.8254 | 287315.7534 | 196098.9055 | 876997.8827 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 6969860.7689 | 21656394.4659 | 562.3413 | 0.032065 | 217365.7086 | 675387.5987 | 4431.294 | 13768.6897
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6024 | 0.42427 | 0.010914 | 4 | 164815.1836 | 501216.1318 | 3359.9804 | 10217.9688 | 39.5047 | 2.3326 | 43.8677 | 143177.2148 | 0 | 212818.673 | 0 | 0 | 0 | 0 | 138838.3963 | 361229.0274 | 246546.2337 | 1102609.5451 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 7195472.4313 | 21882006.1283 | 749.8942 | 0.043658 | 164815.1836 | 501216.1318 | 3359.9804 | 10217.9688
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8157 | 0.57367 | 0.01482 | 4 | 126149.996 | 373892.2882 | 2571.7383 | 7622.3 | 39.7245 | 2.3452 | 37.6984 | 176829.8092 | 0 | 270501.2057 | 0 | 0 | 0 | 0 | 174459.0958 | 453906.7808 | 309800.7048 | 1385497.5963 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 7478360.4824 | 22164894.1795 | 1000 | 0.059281 | 126149.996 | 373892.2882 | 2571.7383 | 7622.3
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4204 | 0.77136 | 0.01998 | 4 | 97939.415 | 281706.3502 | 1996.6274 | 5742.965 | 39.888 | 2.3538 | 49.2109 | 217537.4985 | 0 | 342439.6813 | 0 | 0 | 0 | 0 | 218391.1001 | 568208.8443 | 387814.2118 | 1734391.3361 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 7827254.2222 | 22513787.9193 | 1333.5214 | 0.079919 | 97939.415 | 281706.3502 | 1996.6274 | 5742.965
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5741 | 1.0368 | 0.026882 | 4 | 76882.5936 | 213468.1785 | 1567.3557 | 4351.8376 | 40.0095 | 2.3594 | 40.6201 | 267558.413 | 0 | 433514.8757 | 0 | 0 | 0 | 849.5161 | 273749.8939 | 712241.07 | 486119.1654 | 2174032.9341 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 8266895.8202 | 22953429.5173 | 1778.2794 | 0.10753 | 76882.5936 | 213468.1785 | 1567.3557 | 4351.8376
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4272 | 1.3884 | 0.036017 | 4 | 61113.526 | 163055.182 | 1245.8819 | 3324.1004 | 40.0912 | 2.3622 | 35.6884 | 328207.2249 | 0 | 547291.7927 | 0 | 0 | 0 | 0 | 341444.6168 | 888368.8531 | 606329.9964 | 2711642.4839 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 8804505.37 | 23491039.067 | 2371.3737 | 0.14407 | 61113.526 | 163055.182 | 1245.8819 | 3324.1004
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2297 | 1.8569 | 0.048074 | 4 | 49298.9276 | 125673.6702 | 1005.0253 | 2562.0278 | 40.1358 | 2.3617 | 35.2564 | 402155.7498 | 0 | 690378.2116 | 0 | 0 | 0 | 1050.4783 | 426497.9315 | 1109660.131 | 757365.8407 | 3387108.343 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 9479971.2291 | 24166504.9262 | 3162.2777 | 0.1923 | 49298.9276 | 125673.6702 | 1005.0253 | 2562.0278
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2721 | 2.4782 | 0.063888 | 4 | 40339.6813 | 97809.7161 | 822.379 | 1993.9834 | 40.1383 | 2.3568 | 48.2132 | 491700.6845 | 0 | 869501.7762 | 0 | 0 | 0 | 0 | 530868.9597 | 1381212.1369 | 942705.6645 | 4215989.2218 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 10308852.1079 | 24995385.805 | 4216.965 | 0.25555 | 40339.6813 | 97809.7161 | 822.379 | 1993.9834
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.954 | 3.3014 | 0.084319 | 4 | 33615.1703 | 77159.5738 | 685.2907 | 1573.0023 | 40.0849 | 2.3449 | 48.3147 | 599632.447 | 0 | 1093728.0963 | 0 | 0 | 0 | 0 | 660410.6119 | 1718252.9433 | 1172742.9404 | 5244767.039 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 11337629.9251 | 26024163.6221 | 5623.4133 | 0.33728 | 33615.1703 | 77159.5738 | 685.2907 | 1573.0023
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.7976 | 4.3919 | 0.11014 | 4 | 28614.201 | 61949.5312 | 583.3392 | 1262.925 | 39.9457 | 2.3209 | 29.5593 | 728524.5645 | 0 | 1374527.2308 | 0 | 0 | 0 | 0 | 820190.2002 | 2133966.6567 | 1456476.0919 | 6513684.7442 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 12606547.6303 | 27293081.3274 | 7498.9421 | 0.44057 | 28614.201 | 61949.5312 | 583.3392 | 1262.925
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3439 | 5.8142 | 0.14111 | 4 | 25058.12 | 51078.2857 | 510.8437 | 1041.2999 | 39.6676 | 2.2781 | 45.1987 | 878044.8815 | 0 | 1721246.4222 | 0 | 0 | 0 | 0 | 1013723.6085 | 2637500.8859 | 1800148.5498 | 8050664.3479 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 14143527.234 | 28830060.9311 | 10000 | 0.56443 | 25058.12 | 51078.2857 | 510.8437 | 1041.2999
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2406 | 7.6443 | 0.17457 | 4 | 22868.2166 | 43900.2452 | 466.1995 | 894.9659 | 39.1454 | 2.2019 | 48.9167 | 1043877.8683 | 0 | 2144711.3212 | 0 | 0 | 0 | 0 | 1243549.7839 | 3235461.4506 | 2208268.9221 | 9875869.3462 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 15968732.2323 | 30655265.9294 | 13335.2143 | 0.69829 | 22868.2166 | 43900.2452 | 466.1995 | 894.9659
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6936 | 9.4102 | 0.19748 | 4 | 22272.2888 | 40865.18 | 454.0507 | 833.092 | 38.4506 | 2.1041 | 52.0166 | 1176760.8648 | 0 | 2536215.2761 | 0 | 0 | 0 | 0 | 1448060.695 | 3767556.8902 | 2571434.9931 | 11500028.7193 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17592891.6054 | 32279425.3025 | 17782.7941 | 0.7899 | 22272.2888 | 40865.18 | 454.0507 | 833.092
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.564 | 9.3928 | 0.19719 | 4 | 22284.1806 | 40903.9805 | 454.2932 | 833.883 | 38.4506 | 2.1045 | 65.4808 | 1175366.5323 | 0 | 2532429.2286 | 0 | 0 | 0 | 0 | 1446040.3468 | 3762300.3587 | 2567847.3023 | 11483983.7688 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17576846.6549 | 32263380.352 | 23713.7371 | 0.78876 | 22284.1806 | 40903.9805 | 454.2932 | 833.883
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.454 | 9.378 | 0.19695 | 4 | 22293.8849 | 40936.1823 | 454.491 | 834.5394 | 38.4509 | 2.1048 | 66.2997 | 1174192.5732 | 0 | 2529223.0262 | 0 | 0 | 0 | 0 | 1444332.0838 | 3757855.8087 | 2564813.8057 | 11470417.2977 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17563280.1838 | 32249813.8809 | 31622.7766 | 0.78781 | 22293.8849 | 40936.1823 | 454.491 | 834.5394
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.3614 | 9.3657 | 0.19675 | 4 | 22301.7872 | 40962.7418 | 454.6521 | 835.0809 | 38.4514 | 2.1051 | 69.6168 | 1173214.2262 | 0 | 2526539.9087 | 0 | 0 | 0 | 0 | 1442904.1126 | 3754140.5206 | 2562278.0452 | 11459076.8132 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17551939.6994 | 32238473.3964 | 42169.6503 | 0.78702 | 22301.7872 | 40962.7418 | 454.6521 | 835.0809
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.3102 | 9.3586 | 0.19663 | 4 | 22308.1498 | 40981.4235 | 454.7818 | 835.4617 | 38.4506 | 2.1052 | 62.8003 | 1172622.4446 | 0 | 2525008.7905 | 0 | 0 | 0 | 0 | 1442076.1817 | 3751986.4142 | 2560807.8233 | 11452501.6543 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17545364.5404 | 32231898.2375 | 56234.1325 | 0.7865 | 22308.1498 | 40981.4235 | 454.7818 | 835.4617
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.2519 | 9.3509 | 0.1965 | 4 | 22313.2056 | 40998.2814 | 454.8849 | 835.8054 | 38.4509 | 2.1054 | 57.4043 | 1172007.8744 | 0 | 2523328.3126 | 0 | 0 | 0 | 0 | 1441181.113 | 3749657.629 | 2559218.3796 | 11445393.3086 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17538256.1947 | 32224789.8918 | 74989.4209 | 0.786 | 22313.2056 | 40998.2814 | 454.8849 | 835.8054
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1982 | 9.3439 | 0.19639 | 4 | 22317.1747 | 41012.4125 | 454.9658 | 836.0935 | 38.4516 | 2.1056 | 62.0374 | 1171461.4511 | 0 | 2521803.5183 | 0 | 0 | 0 | 0 | 1440373.3381 | 3747555.9644 | 2557783.9503 | 11438978.2222 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17531841.1083 | 32218374.8054 | 100000 | 0.78558 | 22317.1747 | 41012.4125 | 454.9658 | 836.0935
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1787 | 9.3411 | 0.19634 | 4 | 22320.2587 | 41020.8295 | 455.0287 | 836.2651 | 38.451 | 2.1056 | 60.2258 | 1171221.371 | 0 | 2521211.3292 | 0 | 0 | 0 | 0 | 1440048.7531 | 3746711.4609 | 2557207.5593 | 11436400.4734 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17529263.3596 | 32215797.0566 | 133352.1432 | 0.78535 | 22320.2587 | 41020.8295 | 455.0287 | 836.2651
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1445 | 9.3367 | 0.19627 | 4 | 22322.6351 | 41029.5229 | 455.0771 | 836.4423 | 38.4516 | 2.1057 | 66.9997 | 1170877.9277 | 0 | 2520246.0029 | 0 | 0 | 0 | 0 | 1439538.3329 | 3745383.4524 | 2556301.1662 | 11432346.8821 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17525209.7682 | 32211743.4653 | 177827.941 | 0.78509 | 22322.6351 | 41029.5229 | 455.0771 | 836.4423
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.125 | 9.3341 | 0.19623 | 4 | 22324.4546 | 41035.3978 | 455.1142 | 836.5621 | 38.4516 | 2.1058 | 65.1524 | 1170671.1874 | 0 | 2519687.4645 | 0 | 0 | 0 | 0 | 1439239.8742 | 3744606.924 | 2555771.1696 | 11429976.6197 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17522839.5058 | 32209373.2029 | 237137.3706 | 0.78492 | 22324.4546 | 41035.3978 | 455.1142 | 836.5621
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.1056 | 9.3316 | 0.19619 | 4 | 22325.8408 | 41040.4041 | 455.1425 | 836.6641 | 38.452 | 2.1059 | 64.2374 | 1170475.6731 | 0 | 2519139.84 | 0 | 0 | 0 | 0 | 1438950.0501 | 3743852.8611 | 2555256.5062 | 11427674.9305 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17520537.8166 | 32207071.5137 | 316227.766 | 0.78476 | 22325.8408 | 41040.4041 | 455.1425 | 836.6641
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.101 | 9.3309 | 0.19617 | 4 | 22326.8925 | 41043.0388 | 455.1639 | 836.7179 | 38.4516 | 2.1059 | 63.9534 | 1170410.8634 | 0 | 2518992.6503 | 0 | 0 | 0 | 0 | 1438867.3703 | 3743637.7453 | 2555109.6853 | 11427018.3146 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17519881.2008 | 32206414.8978 | 421696.5034 | 0.7847 | 22326.8925 | 41043.0388 | 455.1639 | 836.7179
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0861 | 9.329 | 0.19615 | 4 | 22327.6886 | 41046.3318 | 455.1801 | 836.785 | 38.452 | 2.1059 | 62.4774 | 1170268.6384 | 0 | 2518581.9619 | 0 | 0 | 0 | 0 | 1438651.7341 | 3743076.7041 | 2554726.7631 | 11425305.8017 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17518168.6878 | 32204702.3849 | 562341.3252 | 0.78459 | 22327.6886 | 41046.3318 | 455.1801 | 836.785
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0861 | 9.329 | 0.19614 | 4 | 22328.2893 | 41047.5323 | 455.1924 | 836.8095 | 38.4517 | 2.1059 | 61.9394 | 1170253.4816 | 0 | 2518568.1061 | 0 | 0 | 0 | 0 | 1438640.4192 | 3743047.265 | 2554706.6703 | 11425215.9423 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17518078.8284 | 32204612.5255 | 749894.2093 | 0.78457 | 22328.2893 | 41047.5323 | 455.1924 | 836.8095
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0861 | 9.3289 | 0.19614 | 4 | 22328.7423 | 41048.4371 | 455.2016 | 836.8279 | 38.4515 | 2.1059 | 61.3703 | 1170242.0697 | 0 | 2518557.7089 | 0 | 0 | 0 | 0 | 1438631.9137 | 3743025.1354 | 2554691.5664 | 11425148.3941 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17518011.2802 | 32204544.9773 | 1000000 | 0.78455 | 22328.7423 | 41048.4371 | 455.2016 | 836.8279
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0861 | 9.3289 | 0.19613 | 4 | 22329.0833 | 41049.1183 | 455.2086 | 836.8418 | 38.4513 | 2.1059 | 61.7073 | 1170233.486 | 0 | 2518549.9085 | 0 | 0 | 0 | 0 | 1438625.5238 | 3743008.5104 | 2554680.2195 | 11425097.6482 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17517960.5343 | 32204494.2314 | 1333521.4322 | 0.78454 | 22329.0833 | 41049.1183 | 455.2086 | 836.8418
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3265 | 0.19611 | 4 | 22329.3398 | 41051.8649 | 455.2138 | 836.8978 | 38.4522 | 2.106 | 59.8021 | 1170066.7853 | 0 | 2518029.3142 | 0 | 0 | 0 | 0 | 1438357.4788 | 3742311.1121 | 2554204.2308 | 11422968.9212 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515831.8074 | 32202365.5044 | 1778279.41 | 0.78443 | 22329.3398 | 41051.8649 | 455.2138 | 836.8978
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3265 | 0.19611 | 4 | 22329.5323 | 41052.2495 | 455.2177 | 836.9056 | 38.4521 | 2.106 | 60.9571 | 1170061.9453 | 0 | 2518024.9315 | 0 | 0 | 0 | 0 | 1438353.882 | 3742301.7539 | 2554197.8437 | 11422940.3563 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515803.2425 | 32202336.9395 | 2371373.7057 | 0.78442 | 22329.5323 | 41052.2495 | 455.2177 | 836.9056
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3265 | 0.1961 | 4 | 22329.677 | 41052.5384 | 455.2207 | 836.9115 | 38.452 | 2.106 | 60.458 | 1170058.3112 | 0 | 2518021.6443 | 0 | 0 | 0 | 0 | 1438351.1827 | 3742294.7309 | 2554193.0503 | 11422918.9194 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515781.8055 | 32202315.5026 | 3162277.6602 | 0.78442 | 22329.677 | 41052.5384 | 455.2207 | 836.9115
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3265 | 0.1961 | 4 | 22329.7856 | 41052.7553 | 455.2229 | 836.9159 | 38.452 | 2.106 | 60.726 | 1170055.5834 | 0 | 2518019.1789 | 0 | 0 | 0 | 0 | 1438349.1573 | 3742289.4613 | 2554189.4537 | 11422902.8347 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515765.7208 | 32202299.4179 | 4216965.0343 | 0.78441 | 22329.7856 | 41052.7553 | 455.2229 | 836.9159
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3264 | 0.1961 | 4 | 22329.8672 | 41052.9181 | 455.2245 | 836.9193 | 38.4519 | 2.106 | 60.7147 | 1170053.5364 | 0 | 2518017.3299 | 0 | 0 | 0 | 0 | 1438347.6379 | 3742285.508 | 2554186.7555 | 11422890.7677 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515753.6539 | 32202287.3509 | 5623413.2519 | 0.78441 | 22329.8672 | 41052.9181 | 455.2245 | 836.9193
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3264 | 0.1961 | 4 | 22329.9284 | 41053.0402 | 455.2258 | 836.9218 | 38.4519 | 2.106 | 59.8131 | 1170052.0005 | 0 | 2518015.9433 | 0 | 0 | 0 | 0 | 1438346.4981 | 3742282.5425 | 2554184.7315 | 11422881.7159 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515744.602 | 32202278.2991 | 7498942.0933 | 0.78441 | 22329.9284 | 41053.0402 | 455.2258 | 836.9218
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0667 | 9.3264 | 0.1961 | 4 | 22329.9743 | 41053.1319 | 455.2267 | 836.9236 | 38.4519 | 2.106 | 61.0912 | 1170050.8483 | 0 | 2518014.9034 | 0 | 0 | 0 | 0 | 1438345.6431 | 3742280.3182 | 2554183.2133 | 11422874.9263 | 961560.8286 | 5131302.0575 | 5131302.0575 | 6472969.3905 | 3082262.2491 | 0 | 17515737.8125 | 32202271.5095 | 10000000 | 0.7844 | 22329.9743 | 41053.1319 | 455.2267 | 836.9236
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.441 | 0.032612 | 0.0010492 | 4 | 1581292.4359 | 5236476.7982 | 32236.7852 | 106752.6624 | 36.7758 | 2.2718 | 23.6405 | 27950.0344 | 0 | 30498.847 | 0 | 0 | 0 | 2183.5681 | 23646.6553 | 61523.7466 | 41991.2212 | 187794.0727 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 6636255.6439 | 21976073.4423 | 100 | 0.0041967 | 1581292.4359 | 5236476.7982 | 32236.7852 | 106752.6624
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6062 | 0.052568 | 0.0016156 | 4 | 1037943.2596 | 3411650.4762 | 21159.8773 | 69551.1096 | 37.9817 | 2.4006 | 39.5812 | 37592.3807 | 0 | 42540.1645 | 0 | 0 | 0 | 3532.1665 | 32629.2375 | 84894.5829 | 57942.2973 | 259130.8294 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 6707592.4006 | 22047410.199 | 133.3521 | 0.0064624 | 1037943.2596 | 3411650.4762 | 21159.8773 | 69551.1096
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.78679 | 0.075203 | 0.002391 | 4 | 707550.5109 | 2311470.7372 | 14424.3742 | 47122.4575 | 38.8588 | 2.4824 | 27.1341 | 47255.7413 | 0 | 54977.9989 | 0 | 0 | 0 | 605.2138 | 40107.1921 | 104350.6866 | 71221.4878 | 318518.3205 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 6766979.8917 | 22106797.6901 | 177.8279 | 0.009564 | 707550.5109 | 2311470.7372 | 14424.3742 | 47122.4575
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.068 | 0.10956 | 0.0034594 | 4 | 496549.0619 | 1605109.4981 | 10122.8243 | 32722.3282 | 39.7525 | 2.5565 | 75.0076 | 61017.3237 | 0 | 73244.1281 | 0 | 0 | 0 | 2177.6763 | 53211.26 | 138444.7834 | 94491.4094 | 422586.581 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 6871048.1522 | 22210865.9506 | 237.1374 | 0.013838 | 496549.0619 | 1605109.4981 | 10122.8243 | 32722.3282
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.15279 | 0.0048989 | 4 | 356217.4402 | 1139034.0381 | 7261.9743 | 23220.7495 | 40.4504 | 2.6088 | 106.6859 | 76625.4373 | 0 | 94635.6185 | 0 | 0 | 0 | 458.425 | 66970.5975 | 174243.7571 | 118924.9446 | 531858.78 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 6980320.3512 | 22320138.1496 | 316.2278 | 0.019596 | 356217.4402 | 1139034.0381 | 7261.9743 | 23220.7495
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9042 | 0.21261 | 0.00684 | 4 | 260652.6123 | 821315.931 | 5313.7561 | 16743.6362 | 41.048 | 2.6501 | 149.0824 | 96394.7499 | 0 | 122598.0083 | 0 | 0 | 0 | 1533.6342 | 86005.293 | 223768.1303 | 152726.3469 | 683026.1624 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 7131487.7337 | 22471305.5321 | 421.6965 | 0.02736 | 260652.6123 | 821315.931 | 5313.7561 | 16743.6362
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5377 | 0.2908 | 0.0094406 | 4 | 193464.4594 | 599682.3564 | 3944.0347 | 12225.336 | 41.5162 | 2.6803 | 31.5298 | 119886.6271 | 0 | 156889.8574 | 0 | 0 | 0 | 0 | 107942.829 | 280845.0988 | 191682.5507 | 857246.963 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 7305708.5342 | 22645526.3327 | 562.3413 | 0.037763 | 193464.4594 | 599682.3564 | 3944.0347 | 12225.336
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.3971 | 0.012919 | 4 | 145880.0399 | 442730.7642 | 2973.9619 | 9025.6655 | 41.894 | 2.7036 | 35.1227 | 149086.5402 | 0 | 200833.9998 | 0 | 0 | 0 | 1977.4498 | 137240.2161 | 357070.8903 | 243708.2197 | 1089917.316 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 7538378.8872 | 22878196.6857 | 749.8942 | 0.051675 | 145880.0399 | 442730.7642 | 2973.9619 | 9025.6655
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5257 | 0.53604 | 0.017555 | 4 | 111182.1353 | 329631.5314 | 2266.5982 | 6719.9846 | 42.1816 | 2.7206 | 30.0963 | 183906.5866 | 0 | 254837.3607 | 0 | 0 | 0 | 0 | 171110.1395 | 445193.4834 | 303853.7002 | 1358901.2704 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 7807362.8416 | 23147180.64 | 1000 | 0.070221 | 111182.1353 | 329631.5314 | 2266.5982 | 6719.9846
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0525 | 0.72449 | 0.023753 | 4 | 85894.9778 | 247343.5129 | 1751.0853 | 5042.4321 | 42.4044 | 2.7328 | 44.4416 | 227114.6163 | 0 | 323915.5735 | 0 | 0 | 0 | 1955.0379 | 215664.2388 | 561114.1105 | 382971.9102 | 1712735.4872 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 8161197.0584 | 23501014.8568 | 1333.5214 | 0.095014 | 85894.9778 | 247343.5129 | 1751.0853 | 5042.4321
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0555 | 0.97186 | 0.031969 | 4 | 67100.136 | 187059.2154 | 1367.927 | 3813.4551 | 42.569 | 2.7413 | 41.7731 | 279007.2384 | 0 | 409343.4287 | 0 | 0 | 0 | 0 | 268456.7602 | 698469.4219 | 476719.7326 | 2131996.5818 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 8580458.153 | 23920275.9514 | 1778.2794 | 0.12788 | 67100.136 | 187059.2154 | 1367.927 | 3813.4551
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7472 | 1.3042 | 0.042934 | 4 | 53067.7876 | 142390.2808 | 1081.8586 | 2902.8185 | 42.6876 | 2.7465 | 35.2124 | 342874.196 | 0 | 517612.8058 | 0 | 0 | 0 | 0 | 335589.9307 | 873136.1607 | 595933.3709 | 2665146.4641 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 9113608.0353 | 24453425.8338 | 2371.3737 | 0.17174 | 53067.7876 | 142390.2808 | 1081.8586 | 2902.8185
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3406 | 1.7481 | 0.057466 | 4 | 42554.3381 | 109288.8704 | 867.5277 | 2228.0014 | 42.761 | 2.7474 | 42.0234 | 420878.9342 | 0 | 654073.3014 | 0 | 0 | 0 | 1232.7181 | 419712.1319 | 1092004.8725 | 745315.7639 | 3333217.7221 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 9781679.2933 | 25121497.0917 | 3162.2777 | 0.22986 | 42554.3381 | 109288.8704 | 867.5277 | 2228.0014
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0929 | 2.3351 | 0.076567 | 4 | 34601.5022 | 84687.9965 | 705.3984 | 1726.4794 | 42.79 | 2.7441 | 49.0539 | 515190.2133 | 0 | 824325.9144 | 0 | 0 | 0 | 0 | 522411.2898 | 1359207.0147 | 927686.7164 | 4148821.1485 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 10597282.7197 | 25937100.5182 | 4216.965 | 0.30627 | 34601.5022 | 84687.9965 | 705.3984 | 1726.4794
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3876 | 3.1123 | 0.10144 | 4 | 28611.6437 | 66416.4256 | 583.2871 | 1353.9887 | 42.7648 | 2.7346 | 49.7658 | 629106.656 | 0 | 1037244.5012 | 0 | 0 | 0 | 0 | 649876.9513 | 1690846.5192 | 1154037.4928 | 5161112.1205 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 11609573.6917 | 26949391.4901 | 5623.4133 | 0.40576 | 28611.6437 | 66416.4256 | 583.2871 | 1353.9887
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.7144 | 4.1413 | 0.13334 | 4 | 24107.5629 | 52868.4133 | 491.4653 | 1077.7941 | 42.6598 | 2.7134 | 44.9455 | 765699.9483 | 0 | 1303710.8597 | 0 | 0 | 0 | 0 | 807070.2151 | 2099831.1468 | 1433177.9049 | 6409490.0748 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 12857951.646 | 28197769.4445 | 7498.9421 | 0.53336 | 24107.5629 | 52868.4133 | 491.4653 | 1077.7941
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.5964 | 5.4853 | 0.17278 | 4 | 20798.2424 | 42993.9996 | 424.0003 | 876.4908 | 42.4321 | 2.675 | 48.4501 | 925764.4602 | 0 | 1633119.6205 | 0 | 0 | 0 | 0 | 997964.7915 | 2596499.6767 | 1772164.3821 | 7925512.931 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 14373974.5022 | 29713792.3006 | 10000 | 0.69111 | 20798.2424 | 42993.9996 | 424.0003 | 876.4908
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.6085 | 7.212 | 0.21835 | 4 | 18521.5686 | 36084.6759 | 377.5872 | 735.6349 | 41.9962 | 2.6071 | 46.8094 | 1106417.6829 | 0 | 2034586.7271 | 0 | 0 | 0 | 0 | 1224991.7199 | 3187177.1748 | 2175313.9117 | 9728487.2164 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 16176948.7876 | 31516766.5861 | 13335.2143 | 0.87341 | 18521.5686 | 36084.6759 | 377.5872 | 735.6349
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.3286 | 9.3848 | 0.26407 | 4 | 17284.9644 | 31807.2059 | 352.3774 | 648.4329 | 41.2008 | 2.4888 | 46.7223 | 1297174.9245 | 0 | 2515756.4377 | 0 | 0 | 0 | 0 | 1487043.2313 | 3868981.4533 | 2640659.3415 | 11809615.3882 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 18258076.9594 | 33597894.7578 | 17782.7941 | 1.0563 | 17284.9644 | 31807.2059 | 352.3774 | 648.4329
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.0649 | 10.5692 | 0.28181 | 4 | 17133.4258 | 30741.6113 | 349.2881 | 626.7093 | 40.6397 | 2.4078 | 65.4283 | 1383901.8893 | 0 | 2769836.3831 | 0 | 0 | 0 | 0 | 1619957.9262 | 4214798.225 | 2876686.394 | 12865180.8176 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19313642.3888 | 34653460.1872 | 23713.7371 | 1.1272 | 17133.4258 | 30741.6113 | 349.2881 | 626.7093
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9398 | 10.5519 | 0.28144 | 4 | 17141.9944 | 30768.1301 | 349.4627 | 627.2499 | 40.6391 | 2.4081 | 70.1642 | 1382453.6802 | 0 | 2766184.5087 | 0 | 0 | 0 | 0 | 1617968.8936 | 4209623.1702 | 2873154.3128 | 12849384.5655 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19297846.1367 | 34637663.9351 | 31622.7766 | 1.1258 | 17141.9944 | 30768.1301 | 349.4627 | 627.2499
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.8233 | 10.5361 | 0.28112 | 4 | 17148.89 | 30790.6664 | 349.6033 | 627.7094 | 40.6397 | 2.4086 | 69.411 | 1381158.1039 | 0 | 2762840.0231 | 0 | 0 | 0 | 0 | 1616159.2695 | 4204914.8995 | 2869940.8213 | 12835013.1173 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19283474.6885 | 34623292.4869 | 42169.6503 | 1.1245 | 17148.89 | 30790.6664 | 349.6033 | 627.7094
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.7501 | 10.5259 | 0.28089 | 4 | 17154.3923 | 30807.1683 | 349.7155 | 628.0458 | 40.639 | 2.4088 | 71.2491 | 1380290.4054 | 0 | 2760687.6204 | 0 | 0 | 0 | 0 | 1614981.4301 | 4201850.4029 | 2867849.2393 | 12825659.0982 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19274120.6694 | 34613938.4678 | 56234.1325 | 1.1236 | 17154.3923 | 30807.1683 | 349.7155 | 628.0458
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6964 | 10.5184 | 0.28072 | 4 | 17158.7348 | 30819.8835 | 349.804 | 628.305 | 40.6382 | 2.4089 | 77.2809 | 1379640.6801 | 0 | 2759097.7413 | 0 | 0 | 0 | 0 | 1614107.9844 | 4199577.8762 | 2866298.1932 | 12818722.4752 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19267184.0464 | 34607001.8449 | 74989.4209 | 1.1229 | 17158.7348 | 30819.8835 | 349.804 | 628.305
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6381 | 10.5106 | 0.28056 | 4 | 17162.1267 | 30831.0337 | 349.8732 | 628.5323 | 40.6386 | 2.4091 | 71.4023 | 1378998.8486 | 0 | 2757437.7536 | 0 | 0 | 0 | 0 | 1613210.2749 | 4197242.2203 | 2864704.0601 | 12811593.1575 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19260054.7287 | 34599872.5271 | 100000 | 1.1222 | 17162.1267 | 30831.0337 | 349.8732 | 628.5323
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6038 | 10.5058 | 0.28045 | 4 | 17164.7525 | 30838.8468 | 349.9267 | 628.6916 | 40.6383 | 2.4092 | 79.2848 | 1378592.9812 | 0 | 2756435.7034 | 0 | 0 | 0 | 0 | 1612661.187 | 4195813.6062 | 2863729.0016 | 12807232.4793 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19255694.0505 | 34595511.8489 | 133352.1432 | 1.1218 | 17164.7525 | 30838.8468 | 349.9267 | 628.6916
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5649 | 10.5007 | 0.28035 | 4 | 17166.7706 | 30845.7887 | 349.9678 | 628.8331 | 40.6389 | 2.4094 | 76.2944 | 1378177.6663 | 0 | 2755343.8648 | 0 | 0 | 0 | 0 | 1612073.3971 | 4194284.2975 | 2862685.217 | 12802564.4426 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19251026.0139 | 34590843.8123 | 177827.941 | 1.1214 | 17166.7706 | 30845.7887 | 349.9678 | 628.8331
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5527 | 10.4988 | 0.2803 | 4 | 17168.3125 | 30849.7814 | 349.9993 | 628.9145 | 40.6382 | 2.4094 | 72.0063 | 1378005.3974 | 0 | 2754960.8787 | 0 | 0 | 0 | 0 | 1611856.8477 | 4193720.8804 | 2862300.6732 | 12800844.6775 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19249306.2487 | 34589124.0471 | 237137.3706 | 1.1212 | 17168.3125 | 30849.7814 | 349.9993 | 628.9145
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5332 | 10.4962 | 0.28025 | 4 | 17169.4854 | 30853.5776 | 350.0232 | 628.9919 | 40.6383 | 2.4095 | 71.5988 | 1377790.5462 | 0 | 2754408.7852 | 0 | 0 | 0 | 0 | 1611557.7393 | 4192942.6616 | 2861769.5229 | 12798469.2553 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19246930.8265 | 34586748.6249 | 316227.766 | 1.121 | 17169.4854 | 30853.5776 | 350.0232 | 628.9919
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5138 | 10.4937 | 0.2802 | 4 | 17170.3745 | 30856.8072 | 350.0413 | 629.0578 | 40.6387 | 2.4096 | 69.4073 | 1377588.8749 | 0 | 2753869.5421 | 0 | 0 | 0 | 0 | 1611268.7826 | 4192190.8557 | 2861256.3999 | 12796174.4552 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19244636.0264 | 34584453.8249 | 421696.5034 | 1.1208 | 17170.3745 | 30856.8072 | 350.0413 | 629.0578
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.5092 | 10.493 | 0.28018 | 4 | 17171.0467 | 30858.4943 | 350.055 | 629.0921 | 40.6384 | 2.4095 | 68.6534 | 1377519.753 | 0 | 2753721.1448 | 0 | 0 | 0 | 0 | 1611183.9501 | 4191970.139 | 2861105.7562 | 12795500.7432 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19243962.3144 | 34583780.1128 | 562341.3252 | 1.1207 | 17171.0467 | 30858.4943 | 350.055 | 629.0921
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 10.4911 | 0.28015 | 4 | 17171.5539 | 30860.6153 | 350.0654 | 629.1354 | 40.6388 | 2.4096 | 67.5837 | 1377374.0035 | 0 | 2753318.0019 | 0 | 0 | 0 | 0 | 1610969.8821 | 4191413.1779 | 2860725.6188 | 12793800.6842 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19242262.2554 | 34582080.0538 | 749894.2093 | 1.1206 | 17171.5539 | 30860.6153 | 350.0654 | 629.1354
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 10.491 | 0.28014 | 4 | 17171.9359 | 30861.3768 | 350.0731 | 629.1509 | 40.6385 | 2.4096 | 67.4159 | 1377356.5197 | 0 | 2753301.4802 | 0 | 0 | 0 | 0 | 1610956.6199 | 4191378.6725 | 2860702.0682 | 12793695.3605 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19242156.9317 | 34581974.7301 | 1000000 | 1.1206 | 17171.9359 | 30861.3768 | 350.0731 | 629.1509
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 10.4909 | 0.28013 | 4 | 17172.2235 | 30861.9498 | 350.079 | 629.1626 | 40.6382 | 2.4096 | 69.1574 | 1377343.3696 | 0 | 2753289.0741 | 0 | 0 | 0 | 0 | 1610946.653 | 4191352.7406 | 2860684.3692 | 12793616.2065 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19242077.7777 | 34581895.5762 | 1333521.4322 | 1.1205 | 17172.2235 | 30861.9498 | 350.079 | 629.1626
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 10.4909 | 0.28013 | 4 | 17172.4397 | 30862.3808 | 350.0834 | 629.1714 | 40.638 | 2.4096 | 68.3388 | 1377333.4864 | 0 | 2753279.7616 | 0 | 0 | 0 | 0 | 1610939.1667 | 4191333.2627 | 2860671.0751 | 12793556.7524 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19242018.3236 | 34581836.1221 | 1778279.41 | 1.1205 | 17172.4397 | 30862.3808 | 350.0834 | 629.1714
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 10.4909 | 0.28013 | 4 | 17172.6022 | 30862.7046 | 350.0867 | 629.178 | 40.6379 | 2.4095 | 67.7278 | 1377326.0626 | 0 | 2753272.773 | 0 | 0 | 0 | 0 | 1610933.5459 | 4191318.6384 | 2860661.0937 | 12793512.1135 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19241973.6847 | 34581791.4831 | 2371373.7057 | 1.1205 | 17172.6022 | 30862.7046 | 350.0867 | 629.178
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4749 | 10.4885 | 0.28009 | 4 | 17172.7242 | 30864.4044 | 350.0892 | 629.2126 | 40.639 | 2.4097 | 66.354 | 1377159.7082 | 0 | 2752767.3312 | 0 | 0 | 0 | 0 | 1610671.5454 | 4190636.9669 | 2860195.8389 | 12791431.3906 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19239892.9618 | 34579710.7603 | 3162277.6602 | 1.1204 | 17172.7242 | 30864.4044 | 350.0892 | 629.2126
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4749 | 10.4885 | 0.28009 | 4 | 17172.8158 | 30864.5868 | 350.0911 | 629.2163 | 40.6389 | 2.4097 | 64.9276 | 1377155.5288 | 0 | 2752763.402 | 0 | 0 | 0 | 0 | 1610668.383 | 4190628.739 | 2860190.2232 | 12791406.276 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19239867.8472 | 34579685.6456 | 4216965.0343 | 1.1204 | 17172.8158 | 30864.5868 | 350.0911 | 629.2163
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4749 | 10.4884 | 0.28009 | 4 | 17172.8845 | 30864.7237 | 350.0925 | 629.2191 | 40.6388 | 2.4097 | 65.5698 | 1377152.3924 | 0 | 2752760.4545 | 0 | 0 | 0 | 0 | 1610666.0103 | 4190622.5658 | 2860186.0098 | 12791387.4329 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19239849.0041 | 34579666.8025 | 5623413.2519 | 1.1204 | 17172.8845 | 30864.7237 | 350.0925 | 629.2191
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4749 | 10.4884 | 0.28009 | 4 | 17172.936 | 30864.8264 | 350.0935 | 629.2212 | 40.6388 | 2.4097 | 65.6699 | 1377150.0392 | 0 | 2752758.2438 | 0 | 0 | 0 | 0 | 1610664.2304 | 4190617.9347 | 2860182.849 | 12791373.2971 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19239834.8683 | 34579652.6667 | 7498942.0933 | 1.1204 | 17172.936 | 30864.8264 | 350.0935 | 629.2212
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4749 | 10.4884 | 0.28009 | 4 | 17172.9747 | 30864.9035 | 350.0943 | 629.2228 | 40.6388 | 2.4097 | 66.2929 | 1377148.2738 | 0 | 2752756.5856 | 0 | 0 | 0 | 0 | 1610662.8952 | 4190614.4609 | 2860180.4781 | 12791362.6936 | 961560.8286 | 5486900.7426 | 5486900.7426 | 6655388.4938 | 3197528.562 | 0 | 19239824.2648 | 34579642.0633 | 10000000 | 1.1204 | 17172.9747 | 30864.9035 | 350.0943 | 629.2228
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.47729 | 0.032687 | 0.0011179 | 4 | 1572932.5574 | 5152513.2392 | 32066.3577 | 105040.9517 | 38.5319 | 2.6077 | 26.6978 | 31642.5168 | 0 | 31852.71 | 0 | 0 | 0 | 8758.9446 | 28179.1268 | 73316.3077 | 50039.8865 | 223789.4924 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7033709.8395 | 23040582.9528 | 100 | 0.0044717 | 1572932.5574 | 5152513.2392 | 32066.3577 | 105040.9517
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.64046 | 0.05252 | 0.0017633 | 4 | 1007488.7445 | 3276876.4576 | 20539.0208 | 66803.5589 | 39.8485 | 2.7436 | 34.9324 | 41749.7985 | 0 | 43601.0372 | 0 | 0 | 0 | 10311.0565 | 37308.138 | 97068.122 | 66250.9878 | 296289.14 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7106209.4871 | 23113082.6004 | 133.3521 | 0.0070534 | 1007488.7445 | 3276876.4576 | 20539.0208 | 66803.5589
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85995 | 0.079327 | 0.0026627 | 4 | 675785.721 | 2178690.0643 | 13776.806 | 44415.5439 | 41.0112 | 2.8496 | 33.5588 | 54215.8184 | 0 | 58524.9897 | 0 | 0 | 0 | 12409.1283 | 48808.4752 | 126989.6404 | 86673.0389 | 387621.0907 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7197541.4379 | 23204414.5512 | 177.8279 | 0.010651 | 675785.721 | 2178690.0643 | 13776.806 | 44415.5439
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1458 | 0.11452 | 0.0038943 | 4 | 469081.3406 | 1496674.9618 | 9562.8576 | 30511.7435 | 41.9895 | 2.9291 | 81.5288 | 69058.2199 | 0 | 76845.1483 | 0 | 0 | 0 | 14555.3282 | 62578.8916 | 162817.4392 | 111126.2478 | 496981.2751 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7306901.6222 | 23313774.7355 | 237.1374 | 0.015577 | 469081.3406 | 1496674.9618 | 9562.8576 | 30511.7435
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.15819 | 0.0055549 | 4 | 334220.0151 | 1054619.4569 | 6813.5271 | 21499.8441 | 42.7621 | 2.9863 | 111.9056 | 85725.3111 | 0 | 98033.828 | 0 | 0 | 0 | 15211.2195 | 77598.4399 | 201895.2229 | 137797.6382 | 616261.6596 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7426182.0067 | 23433055.12 | 316.2278 | 0.022219 | 334220.0151 | 1054619.4569 | 6813.5271 | 21499.8441
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.21854 | 0.0077998 | 4 | 243100.9914 | 756157.7577 | 4955.9425 | 15415.2987 | 43.4412 | 3.0329 | 155.4735 | 106946.0958 | 0 | 125820.0107 | 0 | 0 | 0 | 17324.6904 | 97535.4108 | 253767.1316 | 173201.2817 | 774594.6209 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7584514.968 | 23591388.0813 | 421.6965 | 0.031199 | 243100.9914 | 756157.7577 | 4955.9425 | 15415.2987
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5766 | 0.29295 | 0.010782 | 4 | 179846.6133 | 551010.8737 | 3666.4165 | 11233.102 | 43.9592 | 3.0664 | 35.9682 | 130766.3664 | 0 | 157926.2377 | 0 | 0 | 0 | 16792.7585 | 119139.2914 | 309975.9975 | 211564.9876 | 946165.6392 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7756085.9863 | 23762959.0996 | 562.3413 | 0.043126 | 179846.6133 | 551010.8737 | 3666.4165 | 11233.102
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.364 | 0.39139 | 0.014759 | 4 | 134963.6502 | 406100.6414 | 2751.4166 | 8278.9109 | 44.3856 | 3.0925 | 40.8227 | 159791.1961 | 0 | 198157.4285 | 0 | 0 | 0 | 15869.1651 | 145788.938 | 379312.9111 | 258888.856 | 1157808.4947 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 7967728.8418 | 23974601.9551 | 749.8942 | 0.059036 | 134963.6502 | 406100.6414 | 2751.4166 | 8278.9109
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2479 | 0.50311 | 0.019883 | 4 | 102487.3202 | 303746.0005 | 2089.3426 | 6192.2731 | 44.6874 | 3.1103 | 35.8888 | 189940.2649 | 0 | 241046.8398 | 0 | 0 | 0 | 2070.255 | 168892.3703 | 439423.3029 | 299915.4335 | 1341288.4665 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 8151208.8137 | 24158081.927 | 1000 | 0.079534 | 102487.3202 | 303746.0005 | 2089.3426 | 6192.2731
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6582 | 0.67887 | 0.026957 | 4 | 78671.8131 | 227120.9998 | 1603.8313 | 4630.1688 | 44.9816 | 3.1271 | 47.3675 | 234302.9907 | 0 | 305868.4242 | 0 | 0 | 0 | 0 | 210666.8518 | 548111.9347 | 374097.658 | 1673047.8595 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 8482968.2067 | 24489841.32 | 1333.5214 | 0.10783 | 78671.8131 | 227120.9998 | 1603.8313 | 4630.1688
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5607 | 0.91605 | 0.036431 | 4 | 61140.9541 | 170985.3616 | 1246.441 | 3485.7679 | 45.2058 | 3.1386 | 44.5741 | 289066.0829 | 0 | 388335.2092 | 0 | 0 | 0 | 532.2524 | 264394.0824 | 687899.1676 | 469505.3168 | 2099732.1112 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 8909652.4584 | 24916525.5717 | 1778.2794 | 0.14572 | 61140.9541 | 170985.3616 | 1246.441 | 3485.7679
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0868 | 1.2309 | 0.049008 | 4 | 48123.7811 | 129778.46 | 981.0684 | 2645.7094 | 45.3698 | 3.1462 | 42.5265 | 355622.1429 | 0 | 491530.7008 | 0 | 0 | 0 | 0 | 330389.609 | 859605.9904 | 586698.7516 | 2623847.1947 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 9433767.5419 | 25440640.6552 | 2371.3737 | 0.19603 | 48123.7811 | 129778.46 | 981.0684 | 2645.7094
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4508 | 1.6503 | 0.065693 | 4 | 38385.6255 | 99301.3896 | 782.5429 | 2024.3931 | 45.4813 | 3.1497 | 58.4764 | 436768.432 | 0 | 621166.985 | 0 | 0 | 0 | 0 | 412594.8126 | 1073487.0677 | 732676.9816 | 3276694.279 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 10086614.6261 | 26093487.7394 | 3162.2777 | 0.26277 | 38385.6255 | 99301.3896 | 782.5429 | 2024.3931
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.9091 | 2.206 | 0.087675 | 4 | 31061.8868 | 76704.3972 | 633.2386 | 1563.7229 | 45.5433 | 3.1489 | 48.7968 | 535183.8663 | 0 | 783246.6909 | 0 | 0 | 0 | 0 | 514187.9173 | 1337811.4864 | 913083.8288 | 4083513.7897 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 10893434.1369 | 26900307.2502 | 4216.965 | 0.3507 | 31061.8868 | 76704.3972 | 633.2386 | 1563.7229
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.8406 | 2.9458 | 0.11656 | 4 | 25511.9853 | 59843.7105 | 520.0963 | 1219.995 | 45.5471 | 3.1408 | 55.2594 | 654728.4209 | 0 | 986992.0045 | 0 | 0 | 0 | 0 | 640270.9659 | 1665853.7156 | 1136979.3908 | 5084824.4976 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 11894744.8447 | 27901617.958 | 5623.4133 | 0.46624 | 25511.9853 | 59843.7105 | 520.0963 | 1219.995
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.6533 | 3.9201 | 0.15382 | 4 | 21329.849 | 47345.7855 | 434.8378 | 965.2079 | 45.4775 | 3.1229 | 50.0884 | 797947.5732 | 0 | 1240547.1372 | 0 | 0 | 0 | 0 | 795012.9371 | 2068460.5826 | 1411766.8503 | 6313735.0804 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 13123655.4275 | 29130528.5408 | 7498.9421 | 0.61527 | 21329.849 | 47345.7855 | 434.8378 | 965.2079
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8728 | 5.1944 | 0.20071 | 4 | 18209.5928 | 38147.6982 | 371.2272 | 777.6924 | 45.2971 | 3.0889 | 41.1778 | 967007.7202 | 0 | 1554340.2619 | 0 | 0 | 0 | 0 | 983325.713 | 2558411.7975 | 1746168.6219 | 7809254.1146 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 14619174.4617 | 30626047.575 | 10000 | 0.80283 | 18209.5928 | 38147.6982 | 371.2272 | 777.6924
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.0763 | 6.8395 | 0.25697 | 4 | 15964.5495 | 31537.52 | 325.4589 | 642.935 | 44.9325 | 3.0271 | 56.2163 | 1160877.386 | 0 | 1938462.6889 | 0 | 0 | 0 | 0 | 1208742.6292 | 3144900.374 | 2146459.1265 | 9599442.2045 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 16409362.5516 | 32416235.6649 | 13335.2143 | 1.0279 | 15964.5495 | 31537.52 | 325.4589 | 642.935
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.683 | 8.8986 | 0.31817 | 4 | 14516.3624 | 27093.4916 | 295.9357 | 552.3375 | 44.2649 | 2.9218 | 48.656 | 1370274.3173 | 0 | 2395968.3562 | 0 | 0 | 0 | 0 | 1468834.6427 | 3821606.4408 | 2608324.922 | 11665008.6789 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 18474929.0261 | 34481802.1394 | 17782.7941 | 1.2727 | 14516.3624 | 27093.4916 | 295.9357 | 552.3375
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.946 | 11.3887 | 0.37286 | 4 | 13913.2173 | 24645.6885 | 283.6398 | 502.4357 | 43.119 | 2.7487 | 47.2699 | 1575427.9158 | 0 | 2925609.8551 | 0 | 0 | 0 | 0 | 1755404.7306 | 4567203.0261 | 3117209.912 | 13940855.4396 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20750775.7868 | 36757648.9001 | 23713.7371 | 1.4914 | 13913.2173 | 24645.6885 | 283.6398 | 502.4357
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.4077 | 11.6874 | 0.3774 | 4 | 13915.5771 | 24518.8305 | 283.6879 | 499.8495 | 42.9443 | 2.7231 | 67.7034 | 1595970.8353 | 0 | 2987864.223 | 0 | 0 | 0 | 0 | 1787695.6728 | 4651217.4337 | 3174551.4715 | 14197299.6362 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 21007219.9834 | 37014093.0967 | 31622.7766 | 1.5096 | 13915.5771 | 24518.8305 | 283.6879 | 499.8495
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3003 | 11.6721 | 0.37699 | 4 | 13921.5069 | 24536.3584 | 283.8087 | 500.2069 | 42.9431 | 2.7235 | 77.5136 | 1594619.1517 | 0 | 2984692.1495 | 0 | 0 | 0 | 0 | 1785931.4075 | 4646627.1773 | 3171418.5272 | 14183288.4131 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20993208.7603 | 37000081.8736 | 42169.6503 | 1.508 | 13921.5069 | 24536.3584 | 283.8087 | 500.2069
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2102 | 11.6593 | 0.37666 | 4 | 13926.2104 | 24550.5185 | 283.9046 | 500.4955 | 42.9425 | 2.7238 | 67.2011 | 1593508.1149 | 0 | 2982058.0655 | 0 | 0 | 0 | 0 | 1784470.8104 | 4642827.0033 | 3168824.8303 | 14171688.8245 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20981609.1717 | 36988482.285 | 56234.1325 | 1.5066 | 13926.2104 | 24550.5185 | 283.9046 | 500.4955
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.1371 | 11.649 | 0.37639 | 4 | 13929.9061 | 24561.7721 | 283.98 | 500.7249 | 42.9422 | 2.7241 | 70.6703 | 1592616.2258 | 0 | 2979930.9082 | 0 | 0 | 0 | 0 | 1783293.3823 | 4639763.5769 | 3166733.9788 | 14162338.072 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20972258.4192 | 36979131.5325 | 74989.4209 | 1.5056 | 13929.9061 | 24561.7721 | 283.98 | 500.7249
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.0787 | 11.6408 | 0.37618 | 4 | 13932.7834 | 24570.604 | 284.0386 | 500.905 | 42.9421 | 2.7243 | 65.2502 | 1591911.4551 | 0 | 2978243.1863 | 0 | 0 | 0 | 0 | 1782360.3101 | 4637335.9146 | 3165077.0494 | 14154927.9155 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20964848.2626 | 36971721.3759 | 100000 | 1.5047 | 13932.7834 | 24570.604 | 284.0386 | 500.905
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.0445 | 11.6359 | 0.37604 | 4 | 13935.0054 | 24576.851 | 284.0839 | 501.0324 | 42.9413 | 2.7244 | 72.2559 | 1591458.5014 | 0 | 2977215.0757 | 0 | 0 | 0 | 0 | 1781782.6951 | 4635833.0787 | 3164051.3331 | 14150340.684 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20960261.0312 | 36967134.1445 | 133352.1432 | 1.5041 | 13935.0054 | 24576.851 | 284.0839 | 501.0324
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.0056 | 11.6305 | 0.3759 | 4 | 13936.7099 | 24582.3095 | 284.1187 | 501.1436 | 42.9415 | 2.7245 | 69.425 | 1591005.793 | 0 | 2976108.8828 | 0 | 0 | 0 | 0 | 1781174.7236 | 4634251.2616 | 3162971.7104 | 14145512.3713 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20955432.7185 | 36962305.8318 | 177827.941 | 1.5036 | 13936.7099 | 24582.3095 | 284.1187 | 501.1436
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9861 | 11.6277 | 0.37582 | 4 | 13938.0106 | 24585.9318 | 284.1452 | 501.2175 | 42.941 | 2.7246 | 68.5526 | 1590746.4463 | 0 | 2975524.4231 | 0 | 0 | 0 | 0 | 1780845.6391 | 4633395.0512 | 3162387.3292 | 14142898.889 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20952819.2362 | 36959692.3495 | 237137.3706 | 1.5033 | 13938.0106 | 24585.9318 | 284.1452 | 501.2175
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9667 | 11.625 | 0.37575 | 4 | 13938.999 | 24588.9311 | 284.1653 | 501.2786 | 42.941 | 2.7246 | 66.2002 | 1590510.4029 | 0 | 2974962.7351 | 0 | 0 | 0 | 0 | 1780534.5238 | 4632585.5932 | 3161834.8575 | 14140428.1125 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20950348.4597 | 36957221.573 | 316227.766 | 1.503 | 13938.999 | 24588.9311 | 284.1653 | 501.2786
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9519 | 11.6229 | 0.3757 | 4 | 13939.7477 | 24591.2073 | 284.1806 | 501.325 | 42.9409 | 2.7247 | 74.8467 | 1590330.9917 | 0 | 2974535.4003 | 0 | 0 | 0 | 0 | 1780297.8929 | 4631969.928 | 3161414.6533 | 14138548.8661 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20948469.2133 | 36955342.3266 | 421696.5034 | 1.5028 | 13939.7477 | 24591.2073 | 284.1806 | 501.325
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9324 | 11.6203 | 0.37564 | 4 | 13940.3135 | 24593.3646 | 284.1921 | 501.369 | 42.9415 | 2.7248 | 71.8527 | 1590126.3235 | 0 | 2974004.0772 | 0 | 0 | 0 | 0 | 1780010.8563 | 4631223.1175 | 3160904.9398 | 14136269.3143 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20946189.6614 | 36953062.7748 | 562341.3252 | 1.5026 | 13940.3135 | 24593.3646 | 284.1921 | 501.369
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9324 | 11.6202 | 0.37563 | 4 | 13940.7402 | 24594.2138 | 284.2008 | 501.3863 | 42.9409 | 2.7248 | 72.8509 | 1590094.9409 | 0 | 2973974.2517 | 0 | 0 | 0 | 0 | 1779986.9851 | 4631161.0097 | 3160862.5499 | 14136079.7372 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20946000.0844 | 36952873.1977 | 749894.2093 | 1.5025 | 13940.7402 | 24594.2138 | 284.2008 | 501.3863
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9324 | 11.6201 | 0.37561 | 4 | 13941.0616 | 24594.8534 | 284.2074 | 501.3994 | 42.9404 | 2.7247 | 73.2492 | 1590071.3159 | 0 | 2973951.8333 | 0 | 0 | 0 | 0 | 1779969.0282 | 4631114.2895 | 3160830.6625 | 14135937.1293 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20945857.4765 | 36952730.5898 | 1000000 | 1.5025 | 13941.0616 | 24594.8534 | 284.2074 | 501.3994
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.913 | 11.6176 | 0.37557 | 4 | 13941.3033 | 24596.3657 | 284.2123 | 501.4302 | 42.9414 | 2.7249 | 72.5074 | 1589890.5656 | 0 | 2973443.4017 | 0 | 0 | 0 | 0 | 1779700.2472 | 4630414.9765 | 3160353.367 | 14133802.558 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20943722.9051 | 36950596.0184 | 1333521.4322 | 1.5023 | 13941.3033 | 24596.3657 | 284.2123 | 501.4302
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.913 | 11.6176 | 0.37556 | 4 | 13941.4851 | 24596.7272 | 284.216 | 501.4376 | 42.9412 | 2.7249 | 71.3795 | 1589877.2246 | 0 | 2973430.7687 | 0 | 0 | 0 | 0 | 1779690.1174 | 4630388.6208 | 3160335.3787 | 14133722.1101 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20943642.4572 | 36950515.5705 | 1778279.41 | 1.5023 | 13941.4851 | 24596.7272 | 284.216 | 501.4376
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.913 | 11.6175 | 0.37556 | 4 | 13941.6216 | 24596.9989 | 284.2188 | 501.4431 | 42.941 | 2.7249 | 71.5032 | 1589867.2038 | 0 | 2973421.286 | 0 | 0 | 0 | 0 | 1779682.511 | 4630368.8307 | 3160321.8715 | 14133661.703 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20943582.0502 | 36950455.1635 | 2371373.7057 | 1.5022 | 13941.6216 | 24596.9989 | 284.2188 | 501.4431
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.913 | 11.6175 | 0.37555 | 4 | 13941.7241 | 24597.2028 | 284.2209 | 501.4472 | 42.9408 | 2.7248 | 71.2454 | 1589859.6801 | 0 | 2973414.1698 | 0 | 0 | 0 | 0 | 1779676.8014 | 4630353.9755 | 3160311.7325 | 14133616.3593 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20943536.7065 | 36950409.8198 | 3162277.6602 | 1.5022 | 13941.7241 | 24597.2028 | 284.2209 | 501.4472
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9083 | 11.6169 | 0.37554 | 4 | 13941.8011 | 24597.6015 | 284.2225 | 501.4554 | 42.941 | 2.7249 | 71.3668 | 1589815.2275 | 0 | 2973291.7898 | 0 | 0 | 0 | 0 | 1779611.7368 | 4630184.6905 | 3160196.1921 | 14133099.6367 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20943019.9839 | 36949893.0972 | 4216965.0343 | 1.5022 | 13941.8011 | 24597.6015 | 284.2225 | 501.4554
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9083 | 11.6169 | 0.37554 | 4 | 13941.8589 | 24597.7164 | 284.2237 | 501.4577 | 42.941 | 2.7249 | 70.8536 | 1589810.9907 | 0 | 2973287.7852 | 0 | 0 | 0 | 0 | 1779608.5226 | 4630176.3279 | 3160190.4844 | 14133074.1107 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20942994.4578 | 36949867.5712 | 5623413.2519 | 1.5022 | 13941.8589 | 24597.7164 | 284.2237 | 501.4577
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9083 | 11.6168 | 0.37554 | 4 | 13941.9022 | 24597.8026 | 284.2245 | 501.4595 | 42.9409 | 2.7249 | 72.0745 | 1589807.8118 | 0 | 2973284.7812 | 0 | 0 | 0 | 0 | 1779606.1113 | 4630170.0541 | 3160186.2024 | 14133054.9609 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20942975.308 | 36949848.4213 | 7498942.0933 | 1.5022 | 13941.9022 | 24597.8026 | 284.2245 | 501.4595
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9083 | 11.6168 | 0.37554 | 4 | 13941.9347 | 24597.8673 | 284.2252 | 501.4608 | 42.9408 | 2.7249 | 71.8289 | 1589805.4271 | 0 | 2973282.528 | 0 | 0 | 0 | 0 | 1779604.3025 | 4630165.348 | 3160182.9904 | 14133040.5961 | 961560.8286 | 5848359.5185 | 5848359.5185 | 6843374.6835 | 3315138.9113 | 0 | 20942960.9432 | 36949834.0565 | 10000000 | 1.5022 | 13941.9347 | 24597.8673 | 284.2252 | 501.4608
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.51156 | 0.032679 | 0.0011891 | 4 | 1562681.1446 | 5071009.5274 | 31857.3688 | 103379.3883 | 40.2418 | 2.9559 | 32.6394 | 35420.097 | 0 | 33168.2355 | 0 | 0 | 0 | 14001.9897 | 32210.2257 | 83804.4 | 57198.225 | 255803.173 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7433042.3869 | 24120742.0286 | 100 | 0.0047566 | 1562681.1446 | 5071009.5274 | 31857.3688 | 103379.3883
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.69881 | 0.055005 | 0.0019262 | 4 | 976487.8101 | 3142390.3745 | 19907.0248 | 64061.8782 | 41.8646 | 3.1163 | 44.2573 | 47617.117 | 0 | 46497.1425 | 0 | 0 | 0 | 17706.7565 | 43610.1963 | 113464.785 | 77442.0472 | 346338.0446 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7523577.2586 | 24211276.9003 | 133.3521 | 0.0077047 | 976487.8101 | 3142390.3745 | 19907.0248 | 64061.8782
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.082181 | 0.0029557 | 4 | 644325.5221 | 2055814.5143 | 13135.4473 | 41910.5596 | 43.1127 | 3.2259 | 31.8292 | 60768.2008 | 0 | 61281.0572 | 0 | 0 | 0 | 20163.3919 | 55462.9335 | 144303.1759 | 98489.8827 | 440468.6419 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7617707.8559 | 24305407.4976 | 177.8279 | 0.011823 | 644325.5221 | 2055814.5143 | 13135.4473 | 41910.5596
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2236 | 0.11992 | 0.0043755 | 4 | 442350.9716 | 1395820.1053 | 9017.9229 | 28455.6808 | 44.2496 | 3.3159 | 92.0556 | 77565.7535 | 0 | 80714.3369 | 0 | 0 | 0 | 24083.386 | 71121.7558 | 185044.2195 | 126296.4821 | 564825.9338 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7742065.1477 | 24429764.7894 | 237.1374 | 0.017502 | 442350.9716 | 1395820.1053 | 9017.9229 | 28455.6808
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.16853 | 0.0063009 | 4 | 312924.0812 | 975042.0595 | 6379.3807 | 19877.5512 | 45.1757 | 3.3827 | 124.1409 | 97174.4024 | 0 | 104079.094 | 0 | 0 | 0 | 27835.6565 | 89344.7696 | 232456.7635 | 158656.5176 | 709547.2036 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 7886786.4176 | 24574486.0593 | 316.2278 | 0.025204 | 312924.0812 | 975042.0595 | 6379.3807 | 19877.5512
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.23203 | 0.0088945 | 4 | 226551.8256 | 695597.459 | 4618.5654 | 14180.6951 | 45.9363 | 3.4334 | 169.8803 | 120554.7585 | 0 | 132770.5629 | 0 | 0 | 0 | 31772.026 | 111187.9655 | 289288.2784 | 197445.1943 | 883018.7855 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 8060257.9994 | 24747957.6411 | 421.6965 | 0.035578 | 226551.8256 | 695597.459 | 4618.5654 | 14180.6951
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7935 | 0.31685 | 0.012376 | 4 | 167194.0534 | 504296.5192 | 3408.4769 | 10280.7667 | 46.5677 | 3.4732 | 41.6791 | 149194.0828 | 0 | 168936.7369 | 0 | 0 | 0 | 36837.1043 | 138437.4904 | 360185.9525 | 245834.3137 | 1099425.6806 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 8276664.8945 | 24964364.5363 | 562.3413 | 0.049503 | 167194.0534 | 504296.5192 | 3408.4769 | 10280.7667
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.42559 | 0.017008 | 4 | 125377.3574 | 370667.873 | 2555.987 | 7556.566 | 47.0615 | 3.5028 | 41.5519 | 182775.6485 | 0 | 212571.5251 | 0 | 0 | 0 | 41324.1635 | 170301.8214 | 443090.4057 | 302418.3065 | 1352481.8707 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 8529721.0846 | 25217420.7263 | 749.8942 | 0.068032 | 125377.3574 | 370667.873 | 2555.987 | 7556.566
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7567 | 0.56471 | 0.023144 | 4 | 95337.8946 | 275598.7573 | 1943.5919 | 5618.4534 | 47.4466 | 3.5249 | 54.9928 | 222223.7192 | 0 | 265259.1284 | 0 | 0 | 0 | 44825.1828 | 207600.1319 | 540132.9584 | 368651.8428 | 1648692.9635 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 8825932.1774 | 25513631.8191 | 1000 | 0.092575 | 95337.8946 | 275598.7573 | 1943.5919 | 5618.4534
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1575 | 0.7421 | 0.031233 | 4 | 73415.5968 | 206991.1615 | 1496.6762 | 4219.7948 | 47.745 | 3.5413 | 53.8668 | 268545.6326 | 0 | 328800.8828 | 0 | 0 | 0 | 46652.6199 | 251159.6627 | 653465.9225 | 446003.9195 | 1994628.64 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 9171867.854 | 25859567.4957 | 1333.5214 | 0.12493 | 73415.5968 | 206991.1615 | 1496.6762 | 4219.7948
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9286 | 0.96679 | 0.041837 | 4 | 57198.9474 | 156917.5667 | 1166.0779 | 3198.9768 | 47.974 | 3.5531 | 50.0553 | 322701.2923 | 0 | 405038.918 | 0 | 0 | 0 | 45487.8581 | 301558.9467 | 784594.521 | 535501.8824 | 2394883.4185 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 9572122.6325 | 26259822.2742 | 1778.2794 | 0.16735 | 57198.9474 | 156917.5667 | 1166.0779 | 3198.9768
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1017 | 1.2433 | 0.055552 | 4 | 45058.7933 | 120158.8078 | 918.5844 | 2449.5998 | 48.1426 | 3.561 | 44.3516 | 384311.6053 | 0 | 493980.0142 | 0 | 0 | 0 | 37071.1098 | 356991.4644 | 928818.5614 | 633937.7535 | 2835110.5086 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 10012349.7225 | 26700049.3642 | 2371.3737 | 0.22221 | 45058.7933 | 120158.8078 | 918.5844 | 2449.5998
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5688 | 1.559 | 0.072672 | 4 | 35769.7311 | 93177.0484 | 729.2144 | 1899.5402 | 48.2578 | 3.5655 | 56.237 | 449514.0141 | 0 | 590324.3386 | 0 | 0 | 0 | 0 | 405536.9575 | 1055123.9764 | 720143.7945 | 3220643.0812 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 10397882.2951 | 27085581.9368 | 3162.2777 | 0.29069 | 35769.7311 | 93177.0484 | 729.2144 | 1899.5402
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7641 | 2.0898 | 0.097299 | 4 | 28770.4448 | 71647.6249 | 586.5244 | 1460.6337 | 48.3567 | 3.5661 | 50.0942 | 551982.5094 | 0 | 745990.4945 | 0 | 0 | 0 | 0 | 506209.4715 | 1317053.2071 | 898915.8766 | 4020151.5591 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 11197390.773 | 27885090.4147 | 4216.965 | 0.3892 | 28770.4448 | 71647.6249 | 586.5244 | 1460.6337
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.313 | 2.7918 | 0.1296 | 4 | 23500.4129 | 55690.3367 | 479.0877 | 1135.3228 | 48.3962 | 3.5606 | 49.7179 | 675882.4898 | 0 | 940290.7352 | 0 | 0 | 0 | 0 | 630307.5578 | 1639930.9715 | 1119286.5852 | 5005698.3396 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 12182937.5535 | 28870637.1952 | 5623.4133 | 0.51841 | 23500.4129 | 55690.3367 | 479.0877 | 1135.3228
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.6265 | 3.7169 | 0.17154 | 4 | 19519.8217 | 43840.7925 | 397.938 | 893.7539 | 48.3635 | 3.5459 | 47.9415 | 824775.5586 | 0 | 1182221.3755 | 0 | 0 | 0 | 0 | 782728.8043 | 2036499.789 | 1389952.9519 | 6216178.4793 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 13393417.6933 | 30081117.335 | 7498.9421 | 0.68614 | 19519.8217 | 43840.7925 | 397.938 | 893.7539
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2049 | 4.9289 | 0.22493 | 4 | 16526.7032 | 35074.359 | 336.9192 | 715.0383 | 48.2281 | 3.5159 | 49.3856 | 1001537.5842 | 0 | 1482007.3937 | 0 | 0 | 0 | 0 | 968582.5414 | 2520053.089 | 1719988.0152 | 7692168.6235 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 14869407.8374 | 31557107.4792 | 10000 | 0.89972 | 16526.7032 | 35074.359 | 336.9192 | 715.0383
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.5755 | 6.4934 | 0.29038 | 4 | 14324.8401 | 28691.729 | 292.0312 | 584.9197 | 47.9317 | 3.4609 | 44.6009 | 1206055.1152 | 0 | 1848786.4706 | 0 | 0 | 0 | 0 | 1191388.2184 | 3099747.7571 | 2115641.5377 | 9461619.0989 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 16638858.3129 | 33326557.9546 | 13335.2143 | 1.1615 | 14324.8401 | 28691.729 | 292.0312 | 584.9197
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.1781 | 8.4605 | 0.36509 | 4 | 12802.3786 | 24229.5442 | 260.9938 | 493.952 | 47.3707 | 3.366 | 51.8038 | 1431692.2611 | 0 | 2287330.7194 | 0 | 0 | 0 | 0 | 1450418.9624 | 3773692.6183 | 2575622.7536 | 11518757.3148 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 18695996.5288 | 35383696.1705 | 17782.7941 | 1.4604 | 12802.3786 | 24229.5442 | 260.9938 | 493.952
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.1849 | 10.8387 | 0.43978 | 4 | 11924.6344 | 21410.9939 | 243.0998 | 436.4921 | 46.3988 | 3.2108 | 43.3814 | 1661306.1371 | 0 | 2794154.9292 | 0 | 0 | 0 | 0 | 1737629.8158 | 4520956.344 | 3085645.6011 | 13799692.8272 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 20976932.0412 | 37664631.6829 | 23713.7371 | 1.7591 | 11924.6344 | 21410.9939 | 243.0998 | 436.4921
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0501 | 12.8028 | 0.48416 | 4 | 11724.7287 | 20341.604 | 239.0245 | 414.6911 | 45.3362 | 3.0468 | 68.3983 | 1814594.0998 | 0 | 3199274.5937 | 0 | 0 | 0 | 0 | 1955408.7905 | 5087572.5634 | 3472372.8137 | 15529222.861 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22706462.075 | 39394161.7167 | 31622.7766 | 1.9366 | 11724.7287 | 20341.604 | 239.0245 | 414.6911
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.925 | 12.7845 | 0.4836 | 4 | 11729.8295 | 20356.7237 | 239.1284 | 414.9993 | 45.335 | 3.0474 | 72.839 | 1812955.9598 | 0 | 3195584.2537 | 0 | 0 | 0 | 0 | 1953330.6833 | 5082165.7546 | 3468682.5556 | 15512719.207 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22689958.4209 | 39377658.0626 | 42169.6503 | 1.9344 | 11729.8295 | 20356.7237 | 239.1284 | 414.9993
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.8324 | 12.7709 | 0.48317 | 4 | 11733.8577 | 20368.4269 | 239.2106 | 415.2379 | 45.3337 | 3.0477 | 75.0645 | 1811715.9561 | 0 | 3192826.1982 | 0 | 0 | 0 | 0 | 1951771.4402 | 5078108.9239 | 3465913.6853 | 15500336.2036 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22677575.4176 | 39365275.0593 | 56234.1325 | 1.9327 | 11733.8577 | 20368.4269 | 239.2106 | 415.2379
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.7741 | 12.762 | 0.48286 | 4 | 11737.0124 | 20377.0298 | 239.2749 | 415.4133 | 45.3317 | 3.0478 | 69.5973 | 1810867.5101 | 0 | 3191024.8823 | 0 | 0 | 0 | 0 | 1950738.0331 | 5075420.2106 | 3464078.5832 | 15492129.2194 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22669368.4333 | 39357068.075 | 74989.4209 | 1.9314 | 11737.0124 | 20377.0298 | 239.2749 | 415.4133
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.7009 | 12.7516 | 0.48256 | 4 | 11739.4622 | 20384.8156 | 239.3248 | 415.572 | 45.3321 | 3.0482 | 72.948 | 1809971.2285 | 0 | 3188930.388 | 0 | 0 | 0 | 0 | 1949571.6304 | 5072385.4703 | 3462007.3106 | 15482866.0278 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22660105.2418 | 39347804.8835 | 100000 | 1.9303 | 11739.4622 | 20384.8156 | 239.3248 | 415.572
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6692 | 12.7467 | 0.48239 | 4 | 11741.3505 | 20389.8334 | 239.3633 | 415.6743 | 45.3307 | 3.0482 | 68.2077 | 1809492.7936 | 0 | 3187937.859 | 0 | 0 | 0 | 0 | 1948997.9545 | 5070892.8832 | 3460988.5892 | 15478310.0796 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22655549.2936 | 39343248.9353 | 133352.1432 | 1.9296 | 11741.3505 | 20389.8334 | 239.3633 | 415.6743
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6233 | 12.7403 | 0.48221 | 4 | 11742.7971 | 20394.5389 | 239.3928 | 415.7703 | 45.3312 | 3.0485 | 73.8348 | 1808941.103 | 0 | 3186635.0724 | 0 | 0 | 0 | 0 | 1948274.7084 | 5069011.1452 | 3459704.2644 | 15472566.2934 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22649805.5074 | 39337505.1491 | 177827.941 | 1.9288 | 11742.7971 | 20394.5389 | 239.3928 | 415.7703
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6085 | 12.7379 | 0.48211 | 4 | 11743.8998 | 20397.3216 | 239.4153 | 415.827 | 45.3301 | 3.0484 | 82.6947 | 1808693.789 | 0 | 3186149.2418 | 0 | 0 | 0 | 0 | 1947988.782 | 5068267.2233 | 3459196.5224 | 15470295.5585 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22647534.7724 | 39335234.4141 | 237137.3706 | 1.9285 | 11743.8998 | 20397.3216 | 239.4153 | 415.827
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.587 | 12.7348 | 0.48202 | 4 | 11744.7371 | 20399.8408 | 239.4324 | 415.8783 | 45.33 | 3.0485 | 80.8373 | 1808418.7025 | 0 | 3185524.6402 | 0 | 0 | 0 | 0 | 1947637.9037 | 5067354.3099 | 3458573.4402 | 15467508.9966 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22644748.2105 | 39332447.8522 | 316227.766 | 1.9281 | 11744.7371 | 20399.8408 | 239.4324 | 415.8783
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5696 | 12.7323 | 0.48195 | 4 | 11745.3709 | 20401.7939 | 239.4453 | 415.9182 | 45.3301 | 3.0486 | 79.6389 | 1808200.6325 | 0 | 3185023.0145 | 0 | 0 | 0 | 0 | 1947357.2223 | 5066624.0346 | 3458075.0123 | 15465279.9163 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22642519.1302 | 39330218.772 | 421696.5034 | 1.9278 | 11745.3709 | 20401.7939 | 239.4453 | 415.9182
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5501 | 12.7297 | 0.48188 | 4 | 11745.8498 | 20403.5194 | 239.455 | 415.9533 | 45.3306 | 3.0487 | 77.2798 | 1807982.1831 | 0 | 3184486.7452 | 0 | 0 | 0 | 0 | 1947062.882 | 5065858.2216 | 3457552.3292 | 15462942.3611 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22640181.575 | 39327881.2168 | 562341.3252 | 1.9275 | 11745.8498 | 20403.5194 | 239.455 | 415.9533
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5501 | 12.7295 | 0.48186 | 4 | 11746.2107 | 20404.2367 | 239.4624 | 415.968 | 45.3298 | 3.0487 | 78.09 | 1807942.9203 | 0 | 3184449.7656 | 0 | 0 | 0 | 0 | 1947033.1475 | 5065780.8584 | 3457499.5273 | 15462706.2191 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22639945.4331 | 39327645.0748 | 749894.2093 | 1.9274 | 11746.2107 | 20404.2367 | 239.4624 | 415.968
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5501 | 12.7293 | 0.48184 | 4 | 11746.4826 | 20404.7769 | 239.4679 | 415.979 | 45.3293 | 3.0486 | 78.3287 | 1807913.366 | 0 | 3184421.9614 | 0 | 0 | 0 | 0 | 1947010.7777 | 5065722.6568 | 3457459.8034 | 15462528.5653 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22639767.7793 | 39327467.421 | 1000000 | 1.9274 | 11746.4826 | 20404.7769 | 239.4679 | 415.979
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7268 | 0.48179 | 4 | 11746.687 | 20405.9571 | 239.4721 | 416.003 | 45.3303 | 3.0488 | 76.3455 | 1807724.8475 | 0 | 3183914.0353 | 0 | 0 | 0 | 0 | 1946739.1643 | 5065015.9744 | 3456977.4782 | 15460371.4997 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637610.7137 | 39325310.3554 | 1333521.4322 | 1.9271 | 11746.687 | 20405.9571 | 239.4721 | 416.003
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7267 | 0.48178 | 4 | 11746.8407 | 20406.2623 | 239.4752 | 416.0093 | 45.33 | 3.0488 | 76.4628 | 1807708.1585 | 0 | 3183898.3593 | 0 | 0 | 0 | 0 | 1946726.5419 | 5064983.1336 | 3456955.0637 | 15460271.257 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637510.471 | 39325210.1127 | 1778279.41 | 1.9271 | 11746.8407 | 20406.2623 | 239.4752 | 416.0093
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7267 | 0.48177 | 4 | 11746.9561 | 20406.4916 | 239.4776 | 416.0139 | 45.3298 | 3.0488 | 76.0879 | 1807695.6235 | 0 | 3183886.5909 | 0 | 0 | 0 | 0 | 1946717.0636 | 5064958.4729 | 3456938.2323 | 15460195.9832 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637435.1971 | 39325134.8389 | 2371373.7057 | 1.9271 | 11746.9561 | 20406.4916 | 239.4776 | 416.0139
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7266 | 0.48177 | 4 | 11747.0428 | 20406.6638 | 239.4794 | 416.0174 | 45.3296 | 3.0488 | 76.5086 | 1807686.2123 | 0 | 3183877.7585 | 0 | 0 | 0 | 0 | 1946709.9486 | 5064939.9611 | 3456925.5976 | 15460139.478 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637378.692 | 39325078.3337 | 3162277.6602 | 1.9271 | 11747.0428 | 20406.6638 | 239.4794 | 416.0174
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7266 | 0.48176 | 4 | 11747.1078 | 20406.7931 | 239.4807 | 416.0201 | 45.3295 | 3.0487 | 75.7512 | 1807679.1485 | 0 | 3183871.131 | 0 | 0 | 0 | 0 | 1946704.609 | 5064926.0686 | 3456916.1156 | 15460097.0727 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637336.2866 | 39325035.9284 | 4216965.0343 | 1.9271 | 11747.1078 | 20406.7931 | 239.4807 | 416.0201
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7266 | 0.48176 | 4 | 11747.1567 | 20406.8901 | 239.4817 | 416.0221 | 45.3294 | 3.0487 | 75.1311 | 1807673.8478 | 0 | 3183866.1588 | 0 | 0 | 0 | 0 | 1946700.6026 | 5064915.6447 | 3456909.0011 | 15460065.2548 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637304.4688 | 39325004.1105 | 5623413.2519 | 1.927 | 11747.1567 | 20406.8901 | 239.4817 | 416.0221
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7266 | 0.48176 | 4 | 11747.1933 | 20406.9629 | 239.4824 | 416.0235 | 45.3293 | 3.0487 | 75.3009 | 1807669.8708 | 0 | 3183862.4288 | 0 | 0 | 0 | 0 | 1946697.5969 | 5064907.8244 | 3456903.6636 | 15460041.3846 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637280.5985 | 39324980.2402 | 7498942.0933 | 1.927 | 11747.1933 | 20406.9629 | 239.4824 | 416.0235
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.5307 | 12.7265 | 0.48176 | 4 | 11747.2208 | 20407.0175 | 239.483 | 416.0247 | 45.3293 | 3.0487 | 74.7556 | 1807666.8873 | 0 | 3183859.6311 | 0 | 0 | 0 | 0 | 1946695.3422 | 5064901.9582 | 3456899.6598 | 15460023.4786 | 961560.8286 | 6215678.3853 | 6215678.3853 | 7036927.9594 | 3435093.2969 | 0 | 22637262.6925 | 39324962.3343 | 10000000 | 1.927 | 11747.2208 | 20407.0175 | 239.483 | 416.0247
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.55509 | 0.033618 | 0.0012649 | 4 | 1550470.6142 | 4985990.0519 | 31608.4406 | 101646.1513 | 42.0309 | 3.3266 | 36.0662 | 40051.2864 | 0 | 35254.2954 | 0 | 0 | 0 | 19719.6788 | 37059.8516 | 96422.1319 | 65810.0863 | 294317.3303 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7844735.502 | 25227032.8856 | 100 | 0.0050596 | 1550470.6142 | 4985990.0519 | 31608.4406 | 101646.1513
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.055314 | 0.0020996 | 4 | 944408.0549 | 3014108.3484 | 19253.0356 | 61446.6756 | 43.6948 | 3.4844 | 37.0932 | 52236.8751 | 0 | 47854.1733 | 0 | 0 | 0 | 22971.5679 | 47994.4203 | 124871.6367 | 85227.4579 | 381156.1312 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 7931574.3029 | 25313871.6865 | 133.3521 | 0.0083985 | 944408.0549 | 3014108.3484 | 19253.0356 | 61446.6756
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.99609 | 0.087294 | 0.0032837 | 4 | 613314.89 | 1936704.8355 | 12503.2536 | 39482.3477 | 45.3057 | 3.621 | 38.7409 | 68824.303 | 0 | 65482.392 | 0 | 0 | 0 | 28829.3931 | 63623.0744 | 165534.1886 | 112980.4851 | 505273.8363 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8055692.0079 | 25437989.3915 | 177.8279 | 0.013135 | 613314.89 | 1936704.8355 | 12503.2536 | 39482.3477
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3208 | 0.12782 | 0.004916 | 4 | 416718.4014 | 1300688.919 | 8495.3683 | 26516.3029 | 46.5792 | 3.7182 | 100.3579 | 87586.1847 | 0 | 86012.7784 | 0 | 0 | 0 | 34290.3302 | 81076.8244 | 210945.2659 | 143974.4785 | 643885.8621 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8194304.0337 | 25576601.4174 | 237.1374 | 0.019664 | 416718.4014 | 1300688.919 | 8495.3683 | 26516.3029
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.18166 | 0.007141 | 4 | 292801.7259 | 901342.0569 | 5969.1592 | 18375.077 | 47.6504 | 3.793 | 139.4435 | 110251.6203 | 0 | 111543.7859 | 0 | 0 | 0 | 40742.6467 | 102389.8406 | 266397.3623 | 181821.6737 | 813146.9296 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8363565.1013 | 25745862.4849 | 316.2278 | 0.028564 | 292801.7259 | 901342.0569 | 5969.1592 | 18375.077
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.25082 | 0.010137 | 4 | 211120.4698 | 639793.7836 | 4303.9763 | 13043.0617 | 48.5102 | 3.8488 | 189.6529 | 136715.4566 | 0 | 142223.2434 | 0 | 0 | 0 | 47259.0566 | 127217.1251 | 330992.8636 | 225909.4307 | 1010317.176 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8560735.3477 | 25943032.7313 | 421.6965 | 0.040549 | 211120.4698 | 639793.7836 | 4303.9763 | 13043.0617
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9982 | 0.34072 | 0.014149 | 4 | 155429.33 | 462568.756 | 3168.6371 | 9430.0898 | 49.2068 | 3.8914 | 42.8871 | 168198.5187 | 0 | 179763.6956 | 0 | 0 | 0 | 54321.2719 | 156890.5596 | 408197.0534 | 278602.8766 | 1245973.9758 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 8796392.1474 | 26178689.5311 | 562.3413 | 0.056594 | 155429.33 | 462568.756 | 3168.6371 | 9430.0898
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9339 | 0.46011 | 0.019514 | 4 | 116433.7053 | 339128.8642 | 2373.6586 | 6913.6006 | 49.7761 | 3.9245 | 38.5561 | 206602.2605 | 0 | 226857.6662 | 0 | 0 | 0 | 63019.9585 | 193627.1552 | 503778.1395 | 343838.9318 | 1537724.1117 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 9088142.2834 | 26470439.667 | 749.8942 | 0.078054 | 116433.7053 | 339128.8642 | 2373.6586 | 6913.6006
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1124 | 0.61111 | 0.026608 | 4 | 88544.8781 | 251860.6138 | 1805.1071 | 5134.5193 | 50.2138 | 3.9489 | 50.0887 | 251125.3515 | 0 | 282971.8766 | 0 | 0 | 0 | 70871.1436 | 235937.665 | 613861.4068 | 418973.0238 | 1873740.4673 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 9424158.639 | 26806456.0226 | 1000 | 0.10643 | 88544.8781 | 251860.6138 | 1805.1071 | 5134.5193
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5472 | 0.79597 | 0.035875 | 4 | 68253.3114 | 189385.8578 | 1391.4361 | 3860.8869 | 50.5413 | 3.9659 | 44.8485 | 301241.5969 | 0 | 347818.4291 | 0 | 0 | 0 | 75390.2941 | 282535.6248 | 735099.7398 | 501720.6772 | 2243806.3619 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 9794224.5335 | 27176521.9171 | 1333.5214 | 0.1435 | 68253.3114 | 189385.8578 | 1391.4361 | 3860.8869
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5741 | 1.0557 | 0.048328 | 4 | 53275.8291 | 143193.5999 | 1086.0998 | 2919.1952 | 50.8209 | 3.9799 | 44.3445 | 366628.1548 | 0 | 434636.6487 | 0 | 0 | 0 | 86136.2228 | 346086.4002 | 900445.8213 | 614572.7754 | 2748506.0232 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 10298924.1948 | 27681221.5784 | 1778.2794 | 0.19331 | 53275.8291 | 143193.5999 | 1086.0998 | 2919.1952
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0102 | 1.3694 | 0.064404 | 4 | 42095.6069 | 109568.9465 | 858.1759 | 2233.7112 | 51.0178 | 3.9887 | 39.6717 | 439235.1136 | 0 | 533602.3977 | 0 | 0 | 0 | 90729.5951 | 414791.1715 | 1079201.5428 | 736577.2284 | 3294137.0491 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 10844555.2207 | 28226852.6044 | 2371.3737 | 0.25762 | 42095.6069 | 109568.9465 | 858.1759 | 2233.7112
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0381 | 1.7601 | 0.085173 | 4 | 33654.195 | 84674.518 | 686.0863 | 1726.2046 | 51.1585 | 3.9933 | 56.2576 | 522927.7724 | 0 | 650598.0614 | 0 | 0 | 0 | 90610.4239 | 493013.1405 | 1282719.0607 | 875482.1162 | 3915350.5752 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 11465768.7468 | 28848066.1305 | 3162.2777 | 0.34069 | 33654.195 | 84674.518 | 686.0863 | 1726.2046
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6728 | 2.2307 | 0.11148 | 4 | 27216.8324 | 66196.0545 | 554.8519 | 1349.4961 | 51.2484 | 3.9938 | 45.875 | 616348.8993 | 0 | 784496.9557 | 0 | 0 | 0 | 80010.7278 | 577534.0673 | 1502625.1746 | 1025572.5575 | 4586588.3821 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 12137006.5538 | 29519303.9374 | 4216.965 | 0.44594 | 27216.8324 | 66196.0545 | 554.8519 | 1349.4961
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8056 | 2.644 | 0.14047 | 4 | 22189.4905 | 53126.0431 | 452.3628 | 1083.0462 | 51.286 | 3.9913 | 39.3689 | 692120.6984 | 0 | 895470.9921 | 0 | 0 | 0 | 0 | 619160.7593 | 1610929.2883 | 1099492.3406 | 4917174.0787 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 12467592.2504 | 29849889.634 | 5623.4133 | 0.56187 | 22189.4905 | 53126.0431 | 452.3628 | 1083.0462
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6508 | 3.5258 | 0.18648 | 4 | 18315.6375 | 41618.6768 | 373.389 | 848.453 | 51.2914 | 3.979 | 53.6986 | 846031.523 | 0 | 1127218.6722 | 0 | 0 | 0 | 0 | 769567.5761 | 2002256.9731 | 1366581.5264 | 6111656.2709 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 13662074.4425 | 31044371.8262 | 7498.9421 | 0.74592 | 18315.6375 | 41618.6768 | 373.389 | 848.453
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6009 | 4.6788 | 0.24542 | 4 | 15398.4724 | 33105.2085 | 313.9187 | 674.8945 | 51.2014 | 3.9531 | 43.4044 | 1029059.1421 | 0 | 1413720.9924 | 0 | 0 | 0 | 0 | 952684.2525 | 2478689.0025 | 1691756.1762 | 7565909.5657 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 15116327.7373 | 32498625.121 | 10000 | 0.98168 | 15398.4724 | 33105.2085 | 313.9187 | 674.8945
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.1527 | 6.1663 | 0.31867 | 4 | 13227.716 | 26864.4362 | 269.6649 | 547.6679 | 50.969 | 3.905 | 51.106 | 1242133.9378 | 0 | 1763927.4367 | 0 | 0 | 0 | 0 | 1172363.9361 | 3050250.4767 | 2081858.6267 | 9310534.4141 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 16860952.5857 | 34243249.9693 | 13335.2143 | 1.2747 | 13227.716 | 26864.4362 | 269.6649 | 547.6679
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.7548 | 8.0432 | 0.40487 | 4 | 11671.1999 | 22404.588 | 237.9332 | 456.7478 | 50.5062 | 3.8203 | 48.3821 | 1480902.9186 | 0 | 2183836.7414 | 0 | 0 | 0 | 0 | 1429248.4674 | 3718611.333 | 2538028.6446 | 11350628.1049 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 18901046.2765 | 36283343.6601 | 17782.7941 | 1.6195 | 11671.1999 | 22404.588 | 237.9332 | 456.7478
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5427 | 10.3159 | 0.49659 | 4 | 10661.6622 | 19412.4636 | 217.3524 | 395.7493 | 49.6892 | 3.6818 | 52.0447 | 1730502.9636 | 0 | 2669378.5208 | 0 | 0 | 0 | 0 | 1715953.7789 | 4464559.7422 | 3047153.7616 | 13627548.767 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 21177966.9387 | 38560264.3223 | 23713.7371 | 1.9864 | 10661.6622 | 19412.4636 | 217.3524 | 395.7493
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2764 | 12.9379 | 0.57869 | 4 | 10184.6116 | 17693.8972 | 207.6271 | 360.714 | 48.3782 | 3.4695 | 50.996 | 1965672.217 | 0 | 3208154.5647 | 0 | 0 | 0 | 0 | 2017792.4449 | 5249882.0354 | 3583152.3635 | 16024653.6255 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 23575071.7971 | 40957369.1808 | 31622.7766 | 2.3148 | 10184.6116 | 17693.8972 | 207.6271 | 360.714
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8855 | 13.8892 | 0.6004 | 4 | 10154.0476 | 17391.8015 | 207.004 | 354.5554 | 47.7917 | 3.3773 | 60.748 | 2036135.4463 | 0 | 3399549.0766 | 0 | 0 | 0 | 0 | 2119916.9639 | 5515589.0854 | 3764502.8848 | 16835693.4569 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24386111.6286 | 41768409.0122 | 42169.6503 | 2.4016 | 10154.0476 | 17391.8015 | 207.004 | 354.5554
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.7728 | 13.8725 | 0.59983 | 4 | 10157.5226 | 17402.2142 | 207.0748 | 354.7677 | 47.7912 | 3.3779 | 77.0255 | 2034612.0778 | 0 | 3396224.69 | 0 | 0 | 0 | 0 | 2118026.3395 | 5510670.0683 | 3761145.5546 | 16820678.7302 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24371096.9018 | 41753394.2854 | 56234.1325 | 2.3993 | 10157.5226 | 17402.2142 | 207.0748 | 354.7677
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6996 | 13.8613 | 0.59942 | 4 | 10160.2366 | 17409.8868 | 207.1302 | 354.9241 | 47.7896 | 3.3781 | 80.8492 | 2033553.7145 | 0 | 3394001.9852 | 0 | 0 | 0 | 0 | 2116746.7229 | 5507340.7685 | 3758873.2391 | 16810516.4302 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24360934.6018 | 41743231.9855 | 74989.4209 | 2.3977 | 10160.2366 | 17409.8868 | 207.1302 | 354.9241
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6413 | 13.8524 | 0.5991 | 4 | 10162.3398 | 17415.8842 | 207.173 | 355.0464 | 47.7885 | 3.3784 | 76.3279 | 2032719.9597 | 0 | 3392240.416 | 0 | 0 | 0 | 0 | 2115734.5465 | 5504707.2932 | 3757075.8381 | 16802478.0536 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24352896.2252 | 41735193.6088 | 100000 | 2.3964 | 10162.3398 | 17415.8842 | 207.173 | 355.0464
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.605 | 13.8466 | 0.59887 | 4 | 10163.9585 | 17420.2313 | 207.206 | 355.135 | 47.787 | 3.3784 | 80.7999 | 2032154.43 | 0 | 3391101.3586 | 0 | 0 | 0 | 0 | 2115069.7576 | 5502977.6487 | 3755895.3201 | 16797198.515 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24347616.6866 | 41729914.0702 | 133352.1432 | 2.3955 | 10163.9585 | 17420.2313 | 207.206 | 355.135
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5681 | 13.8411 | 0.59868 | 4 | 10165.197 | 17423.8404 | 207.2313 | 355.2086 | 47.7866 | 3.3786 | 77.2539 | 2031642.3999 | 0 | 3390003.7051 | 0 | 0 | 0 | 0 | 2114441.9809 | 5501344.3027 | 3754780.5279 | 16792212.9166 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24342631.0882 | 41724928.4719 | 177827.941 | 2.3947 | 10165.197 | 17423.8404 | 207.2313 | 355.2086
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5487 | 13.838 | 0.59855 | 4 | 10166.1404 | 17426.32 | 207.2505 | 355.2591 | 47.7856 | 3.3786 | 76.5912 | 2031328.3485 | 0 | 3389383.9416 | 0 | 0 | 0 | 0 | 2114077.7931 | 5500396.7608 | 3754133.8111 | 16789320.6551 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24339738.8267 | 41722036.2103 | 237137.3706 | 2.3942 | 10166.1404 | 17426.32 | 207.2505 | 355.2591
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5144 | 13.8332 | 0.5984 | 4 | 10166.8561 | 17428.8091 | 207.2651 | 355.3098 | 47.7864 | 3.3789 | 82.4886 | 2030919.2721 | 0 | 3388427.0672 | 0 | 0 | 0 | 0 | 2113545.0723 | 5499010.7304 | 3753187.8169 | 16785089.9589 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24335508.1305 | 41717805.5142 | 316227.766 | 2.3936 | 10166.8561 | 17428.8091 | 207.2651 | 355.3098
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5 | 13.831 | 0.59832 | 4 | 10167.3978 | 17430.3339 | 207.2762 | 355.3409 | 47.7861 | 3.3789 | 81.0279 | 2030710.6938 | 0 | 3387990.6379 | 0 | 0 | 0 | 0 | 2113293.5194 | 5498356.2413 | 3752741.1146 | 16783092.2071 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24333510.3787 | 41715807.7624 | 421696.5034 | 2.3933 | 10167.3978 | 17430.3339 | 207.2762 | 355.3409
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4903 | 13.8295 | 0.59826 | 4 | 10167.8067 | 17431.4467 | 207.2845 | 355.3636 | 47.7858 | 3.379 | 81.1728 | 2030564.0163 | 0 | 3387691.8875 | 0 | 0 | 0 | 0 | 2113119.8025 | 5497904.2656 | 3752432.6319 | 16781712.6037 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24332130.7753 | 41714428.159 | 562341.3252 | 2.3931 | 10167.8067 | 17431.4467 | 207.2845 | 355.3636
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4903 | 13.8292 | 0.59824 | 4 | 10168.115 | 17432.0586 | 207.2908 | 355.3761 | 47.7849 | 3.3789 | 80.1586 | 2030517.2737 | 0 | 3387648.5168 | 0 | 0 | 0 | 0 | 2113084.6583 | 5497812.8276 | 3752370.2236 | 16781433.5 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24331851.6716 | 41714149.0552 | 749894.2093 | 2.393 | 10168.115 | 17432.0586 | 207.2908 | 355.3761
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4755 | 13.8272 | 0.59818 | 4 | 10168.347 | 17432.981 | 207.2955 | 355.3949 | 47.7855 | 3.379 | 80.1794 | 2030352.3018 | 0 | 3387246.0954 | 0 | 0 | 0 | 0 | 2112863.3749 | 5497237.0937 | 3751977.2734 | 16779676.1392 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24330094.3108 | 41712391.6945 | 1000000 | 2.3927 | 10168.347 | 17432.981 | 207.2955 | 355.3949
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4755 | 13.8271 | 0.59817 | 4 | 10168.5215 | 17433.3273 | 207.2991 | 355.402 | 47.785 | 3.379 | 80.225 | 2030325.8615 | 0 | 3387221.6002 | 0 | 0 | 0 | 0 | 2112843.5101 | 5497185.4094 | 3751941.9978 | 16779518.3791 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24329936.5507 | 41712233.9344 | 1333521.4322 | 2.3927 | 10168.5215 | 17433.3273 | 207.2991 | 355.402
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4755 | 13.827 | 0.59816 | 4 | 10168.6527 | 17433.5877 | 207.3017 | 355.4073 | 47.7847 | 3.3789 | 80.3137 | 2030305.9929 | 0 | 3387203.2024 | 0 | 0 | 0 | 0 | 2112828.5862 | 5497146.5805 | 3751915.4962 | 16779399.8582 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24329818.0298 | 41712115.4135 | 1778279.41 | 2.3926 | 10168.6527 | 17433.5877 | 207.3017 | 355.4073
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8245 | 0.5981 | 4 | 10168.7512 | 17434.3897 | 207.3037 | 355.4236 | 47.786 | 3.3792 | 78.051 | 2030120.7149 | 0 | 3386704.0467 | 0 | 0 | 0 | 0 | 2112561.657 | 5496452.0856 | 3751441.4892 | 16777279.9935 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327698.1651 | 41709995.5488 | 2371373.7057 | 2.3924 | 10168.7512 | 17434.3897 | 207.3037 | 355.4236
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8244 | 0.59809 | 4 | 10168.8252 | 17434.5364 | 207.3053 | 355.4266 | 47.7858 | 3.3791 | 77.7185 | 2030109.5196 | 0 | 3386693.6874 | 0 | 0 | 0 | 0 | 2112553.2507 | 5496430.2142 | 3751426.5615 | 16777213.2335 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327631.4052 | 41709928.7888 | 3162277.6602 | 2.3924 | 10168.8252 | 17434.5364 | 207.3053 | 355.4266
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8244 | 0.59809 | 4 | 10168.8807 | 17434.6465 | 207.3064 | 355.4289 | 47.7856 | 3.3791 | 77.3129 | 2030101.117 | 0 | 3386685.9139 | 0 | 0 | 0 | 0 | 2112546.942 | 5496413.8002 | 3751415.3587 | 16777163.1318 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327581.3034 | 41709878.687 | 4216965.0343 | 2.3924 | 10168.8807 | 17434.6465 | 207.3064 | 355.4289
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8244 | 0.59809 | 4 | 10168.9224 | 17434.7292 | 207.3072 | 355.4305 | 47.7855 | 3.3791 | 78.0882 | 2030094.8117 | 0 | 3386680.0817 | 0 | 0 | 0 | 0 | 2112542.2084 | 5496401.4843 | 3751406.9528 | 16777125.5389 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327543.7105 | 41709841.0942 | 5623413.2519 | 2.3923 | 10168.9224 | 17434.7292 | 207.3072 | 355.4305
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8243 | 0.59808 | 4 | 10168.9536 | 17434.7912 | 207.3079 | 355.4318 | 47.7854 | 3.3791 | 78.1387 | 2030090.0811 | 0 | 3386675.7065 | 0 | 0 | 0 | 0 | 2112538.6572 | 5496392.2447 | 3751400.6465 | 16777097.3359 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327515.5076 | 41709812.8912 | 7498942.0933 | 2.3923 | 10168.9536 | 17434.7912 | 207.3079 | 355.4318
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.4561 | 13.8243 | 0.59808 | 4 | 10168.9771 | 17434.8377 | 207.3084 | 355.4327 | 47.7854 | 3.3791 | 77.7575 | 2030086.5323 | 0 | 3386672.4246 | 0 | 0 | 0 | 0 | 2112535.9932 | 5496385.3136 | 3751395.916 | 16777076.1798 | 961560.8286 | 6588857.343 | 6588857.343 | 7236048.3217 | 3557391.7189 | 0 | 24327494.3514 | 41709791.7351 | 10000000 | 2.3923 | 10168.9771 | 17434.8377 | 207.3084 | 355.4327
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.5699 | 0.032064 | 0.0013433 | 4 | 1534066.798 | 4900865.6775 | 31274.0267 | 99910.7757 | 43.4518 | 3.6729 | 26.0128 | 42781.2849 | 0 | 35338.0952 | 0 | 0 | 0 | 23090.8338 | 39471.9834 | 102698.0041 | 70093.498 | 313473.6994 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8242930.9196 | 26333597.2587 | 100 | 0.0053733 | 1534066.798 | 4900865.6775 | 31274.0267 | 99910.7757
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79142 | 0.058111 | 0.002293 | 4 | 911665.8597 | 2884022.1623 | 18585.5417 | 58794.6927 | 45.6901 | 3.878 | 41.1294 | 58685.161 | 0 | 50984.4086 | 0 | 0 | 0 | 29951.2591 | 54452.1232 | 141673.2549 | 96694.9076 | 432441.1144 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8361898.3346 | 26452564.6737 | 133.3521 | 0.0091721 | 911665.8597 | 2884022.1623 | 18585.5417 | 58794.6927
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.068 | 0.092056 | 0.0036426 | 4 | 583191.9854 | 1824792.657 | 11889.1574 | 37200.8665 | 47.4695 | 4.0231 | 81.6232 | 76925.1382 | 0 | 69440.1913 | 0 | 0 | 0 | 36992.5296 | 71509.565 | 186053.2196 | 126985.1454 | 567905.7891 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8497363.0093 | 26588029.3484 | 177.8279 | 0.01457 | 583191.9854 | 1824792.657 | 11889.1574 | 37200.8665
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.13613 | 0.0055138 | 4 | 392388.893 | 1212638.5432 | 7999.3783 | 24721.2769 | 48.9162 | 4.1297 | 114.3044 | 98121.0061 | 0 | 91501.3443 | 0 | 0 | 0 | 44361.9322 | 91253.8702 | 237423.8515 | 162046.6572 | 724708.6615 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8654165.8816 | 26744832.2207 | 237.1374 | 0.022055 | 392388.893 | 1212638.5432 | 7999.3783 | 24721.2769
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.19329 | 0.008065 | 4 | 273962.2137 | 834736.7338 | 5585.0903 | 17017.2374 | 50.1007 | 4.2098 | 154.1858 | 122993.892 | 0 | 118128.807 | 0 | 0 | 0 | 52234.95 | 114409.4831 | 297670.0064 | 203165.8959 | 908603.0344 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 8838060.2545 | 26928726.5936 | 316.2278 | 0.03226 | 273962.2137 | 834736.7338 | 5585.0903 | 17017.2374
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.26838 | 0.011511 | 4 | 196774.2658 | 589686.5249 | 4011.5096 | 12021.5574 | 51.0795 | 4.2714 | 211.3436 | 152794.4364 | 0 | 150941.1236 | 0 | 0 | 0 | 61272.8909 | 142353.2959 | 370374.0752 | 252787.9167 | 1130523.7387 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 9059980.9589 | 27150647.298 | 421.6965 | 0.046043 | 196774.2658 | 589686.5249 | 4011.5096 | 12021.5574
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.36739 | 0.016137 | 4 | 144551.1617 | 424821.7843 | 2946.871 | 8660.5667 | 51.8806 | 4.319 | 44.316 | 188741.5698 | 0 | 191650.8164 | 0 | 0 | 0 | 71913.6329 | 176399.3475 | 458954.9176 | 313246.1618 | 1400906.446 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 9330363.6662 | 27421030.0053 | 562.3413 | 0.064547 | 144551.1617 | 424821.7843 | 2946.871 | 8660.5667
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2091 | 0.49628 | 0.02231 | 4 | 108187.5694 | 310909.3572 | 2205.5499 | 6338.3078 | 52.5195 | 4.3551 | 47.5015 | 231597.5965 | 0 | 241556.2621 | 0 | 0 | 0 | 83817.2775 | 217218.7431 | 565158.6118 | 385732.3654 | 1725080.8564 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 9654538.0765 | 27745204.4156 | 749.8942 | 0.089239 | 108187.5694 | 310909.3572 | 2205.5499 | 6338.3078
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4756 | 0.66108 | 0.030488 | 4 | 82283.3142 | 230626.8848 | 1677.4567 | 4701.641 | 53.0172 | 4.3819 | 56.9005 | 281872.7416 | 0 | 301712.7501 | 0 | 0 | 0 | 96076.6729 | 265068.2442 | 689653.1984 | 470702.4788 | 2105086.086 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 10034543.3061 | 28125209.6452 | 1000 | 0.12195 | 82283.3142 | 230626.8848 | 1677.4567 | 4701.641
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1003 | 0.87294 | 0.041289 | 4 | 63487.3264 | 173023.3065 | 1294.275 | 3527.3141 | 53.4058 | 4.4019 | 48.6141 | 341382.9525 | 0 | 374827.7926 | 0 | 0 | 0 | 109016.4725 | 321838.6149 | 837358.0577 | 571514.0804 | 2555937.9706 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 10485395.1908 | 28576061.5299 | 1333.5214 | 0.16516 | 63487.3264 | 173023.3065 | 1294.275 | 3527.3141
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1855 | 1.1452 | 0.055507 | 4 | 49640.6859 | 131120.5668 | 1011.9925 | 2673.0701 | 53.7059 | 4.4163 | 56.9578 | 411940.7712 | 0 | 463803.8008 | 0 | 0 | 0 | 122583.2488 | 389347.8501 | 1013003.2399 | 691395.5263 | 3092074.4372 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 11021531.6574 | 29112197.9965 | 1778.2794 | 0.22203 | 49640.6859 | 131120.5668 | 1011.9925 | 2673.0701
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7996 | 1.4874 | 0.074031 | 4 | 39308.5431 | 100400.0813 | 801.3578 | 2046.7915 | 53.9289 | 4.4256 | 51.1607 | 493801.7195 | 0 | 569713.329 | 0 | 0 | 0 | 134560.2427 | 467249.3636 | 1215686.9979 | 829731.356 | 3710743.0086 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 11640200.2288 | 29730866.5679 | 2371.3737 | 0.29612 | 39308.5431 | 100400.0813 | 801.3578 | 2046.7915
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0586 | 1.9149 | 0.097979 | 4 | 31513.4431 | 77672.8198 | 642.4442 | 1583.4655 | 54.0883 | 4.4303 | 57.2134 | 588432.2009 | 0 | 695283.9879 | 0 | 0 | 0 | 143745.8109 | 556710.1799 | 1448445.6912 | 988593.9468 | 4421211.8176 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 12350669.0378 | 30441335.3769 | 3162.2777 | 0.39192 | 31513.4431 | 77672.8198 | 642.4442 | 1583.4655
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1077 | 2.4473 | 0.1287 | 4 | 25572.3955 | 60714.0542 | 521.3279 | 1237.7381 | 54.1914 | 4.4297 | 43.0256 | 697582.5476 | 0 | 843916.0374 | 0 | 0 | 0 | 148715.9701 | 659183.6765 | 1715060.7091 | 1170564.1749 | 5235023.1155 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 13164480.3357 | 31255146.6748 | 4216.965 | 0.51479 | 25572.3955 | 60714.0542 | 521.3279 | 1237.7381
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9675 | 3.088 | 0.16722 | 4 | 21011.5183 | 48057.0128 | 428.3482 | 979.7072 | 54.2412 | 4.4241 | 48.175 | 819421.0065 | 0 | 1014146.4091 | 0 | 0 | 0 | 144022.3195 | 771259.9967 | 2006660.3043 | 1369586.8904 | 6125096.9265 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 14054554.1467 | 32145220.4858 | 5623.4133 | 0.6689 | 21011.5183 | 48057.0128 | 428.3482 | 979.7072
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5144 | 3.8226 | 0.21395 | 4 | 17477.9876 | 38617.2576 | 356.3124 | 787.265 | 54.2382 | 4.4123 | 51.3332 | 949095.8503 | 0 | 1200225.3043 | 0 | 0 | 0 | 119766.2533 | 884944.0891 | 2302442.9927 | 1571464.653 | 7027939.1427 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 14957396.3629 | 33048062.702 | 7498.9421 | 0.85578 | 17477.9876 | 38617.2576 | 356.3124 | 787.265
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0451 | 4.4344 | 0.26202 | 4 | 14646.7344 | 31907.5991 | 298.5935 | 650.4796 | 54.2022 | 4.3989 | 42.2104 | 1048998.95 | 0 | 1347126.0645 | 0 | 0 | 0 | 0 | 934488.7556 | 2431348.0521 | 1659445.0048 | 7421406.827 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 15350864.0472 | 33441530.3863 | 10000 | 1.0481 | 14646.7344 | 31907.5991 | 298.5935 | 650.4796
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8197 | 5.8506 | 0.34184 | 4 | 12484.1049 | 25714.5749 | 254.5054 | 524.2264 | 54.0293 | 4.3568 | 56.7313 | 1269113.694 | 0 | 1682103.3975 | 0 | 0 | 0 | 0 | 1150974.6657 | 2994599.9827 | 2043876.0211 | 9140667.7609 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 17070124.9811 | 35160791.3202 | 13335.2143 | 1.3673 | 12484.1049 | 25714.5749 | 254.5054 | 524.2264
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.4498 | 7.6402 | 0.43766 | 4 | 10902.9387 | 21236.6466 | 222.2712 | 432.9378 | 53.656 | 4.2819 | 38.9161 | 1518386.7862 | 0 | 2084072.8384 | 0 | 0 | 0 | 0 | 1404959.2536 | 3655415.7811 | 2494896.3819 | 11157731.0412 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 19087188.2614 | 37177854.6005 | 17782.7941 | 1.7506 | 10902.9387 | 21236.6466 | 222.2712 | 432.9378
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0975 | 9.8166 | 0.54388 | 4 | 9816.6382 | 18132.2638 | 200.1254 | 369.6507 | 52.9744 | 4.1582 | 55.3596 | 1784604.2467 | 0 | 2550418.9567 | 0 | 0 | 0 | 0 | 1690659.0493 | 4398748.0445 | 3002235.9256 | 13426666.2227 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 21356123.4429 | 39446789.782 | 23713.7371 | 2.1755 | 9816.6382 | 18132.2638 | 200.1254 | 369.6507
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.4669 | 12.3268 | 0.64728 | 4 | 9177.3195 | 16164.5537 | 187.0921 | 329.5363 | 51.8687 | 3.9691 | 59.785 | 2044568.0648 | 0 | 3066916.7205 | 0 | 0 | 0 | 0 | 1993479.0663 | 5186623.6117 | 3539977.1894 | 15831564.6527 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 23761021.8729 | 41851688.212 | 31622.7766 | 2.5891 | 9177.3195 | 16164.5537 | 187.0921 | 329.5363
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.2226 | 14.9837 | 0.72671 | 4 | 8971.5075 | 15195.0077 | 182.8963 | 309.7708 | 50.3046 | 3.7121 | 61.7132 | 2263109.925 | 0 | 3596663.1212 | 0 | 0 | 0 | 0 | 2285311.488 | 5945911.71 | 4058206.9183 | 18149203.1625 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26078660.3827 | 44169326.7218 | 42169.6503 | 2.9068 | 8971.5075 | 15195.0077 | 182.8963 | 309.7708
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.1387 | 14.9699 | 0.72611 | 4 | 8974.5323 | 15203.1209 | 182.958 | 309.9362 | 50.301 | 3.7124 | 79.5287 | 2261736.6943 | 0 | 3593994.3118 | 0 | 0 | 0 | 0 | 2283735.0924 | 5941810.2519 | 4055407.5889 | 18136683.9393 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26066141.1595 | 44156807.4986 | 56234.1325 | 2.9045 | 8974.5323 | 15203.1209 | 182.958 | 309.9362
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.0534 | 14.9567 | 0.72559 | 4 | 8976.8894 | 15209.9501 | 183.006 | 310.0754 | 50.2998 | 3.7128 | 68.821 | 2260486.8427 | 0 | 3591414.738 | 0 | 0 | 0 | 0 | 2282241.6165 | 5937924.5339 | 4052755.5065 | 18124823.2375 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26054280.4577 | 44144946.7968 | 74989.4209 | 2.9024 | 8976.8894 | 15209.9501 | 183.006 | 310.0754
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9996 | 14.948 | 0.72523 | 4 | 8978.7128 | 15214.923 | 183.0432 | 310.1768 | 50.298 | 3.713 | 75.0817 | 2259631.79 | 0 | 3589729.2258 | 0 | 0 | 0 | 0 | 2281250.7962 | 5935346.6227 | 4050996.0292 | 18116954.4639 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26046411.684 | 44137078.0231 | 100000 | 2.9009 | 8978.7128 | 15214.923 | 183.0432 | 310.1768
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9607 | 14.9417 | 0.72495 | 4 | 8980.1143 | 15218.6848 | 183.0718 | 310.2535 | 50.2963 | 3.7131 | 71.6794 | 2258996.6516 | 0 | 3588494.6991 | 0 | 0 | 0 | 0 | 2280521.6267 | 5933449.4735 | 4049701.1858 | 18111163.6367 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26040620.8569 | 44131287.196 | 133352.1432 | 2.8998 | 8980.1143 | 15218.6848 | 183.0718 | 310.2535
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9265 | 14.9363 | 0.72473 | 4 | 8981.1855 | 15221.6745 | 183.0936 | 310.3144 | 50.2954 | 3.7133 | 77.9396 | 2258470.7293 | 0 | 3587438.6113 | 0 | 0 | 0 | 0 | 2279904.6428 | 5931844.2079 | 4048605.5591 | 18106263.7503 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26035720.9705 | 44126387.3096 | 177827.941 | 2.8989 | 8981.1855 | 15221.6745 | 183.0936 | 310.3144
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8876 | 14.9305 | 0.72452 | 4 | 8982.0007 | 15224.273 | 183.1102 | 310.3674 | 50.2959 | 3.7135 | 74.5125 | 2257955.3854 | 0 | 3586315.1843 | 0 | 0 | 0 | 0 | 2279265.5222 | 5930181.347 | 4047470.6224 | 18101188.0612 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26030645.2814 | 44121311.6205 | 237137.3706 | 2.8981 | 8982.0007 | 15224.273 | 183.1102 | 310.3674
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8681 | 14.9274 | 0.72439 | 4 | 8982.6189 | 15225.99 | 183.1228 | 310.4024 | 50.2954 | 3.7136 | 72.5978 | 2257655.172 | 0 | 3585714.7656 | 0 | 0 | 0 | 0 | 2278914.2756 | 5929267.4756 | 4046846.8864 | 18098398.5751 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26027855.7953 | 44118522.1344 | 316227.766 | 2.8976 | 8982.6189 | 15225.99 | 183.1228 | 310.4024
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8487 | 14.9245 | 0.72428 | 4 | 8983.0866 | 15227.4083 | 183.1324 | 310.4313 | 50.2954 | 3.7137 | 71.9542 | 2257385.5629 | 0 | 3585142.4855 | 0 | 0 | 0 | 0 | 2278585.9389 | 5928413.2107 | 4046263.833 | 18095791.0308 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26025248.251 | 44115914.5901 | 421696.5034 | 2.8971 | 8983.0866 | 15227.4083 | 183.1324 | 310.4313
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8487 | 14.9241 | 0.72424 | 4 | 8983.4395 | 15228.1079 | 183.1396 | 310.4456 | 50.2941 | 3.7136 | 71.538 | 2257314.1963 | 0 | 3585077.4002 | 0 | 0 | 0 | 0 | 2278532.7226 | 5928274.753 | 4046169.3328 | 18095368.4048 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26024825.625 | 44115491.9641 | 562341.3252 | 2.897 | 8983.4395 | 15228.1079 | 183.1396 | 310.4456
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8339 | 14.922 | 0.72417 | 4 | 8983.7055 | 15229.0094 | 183.145 | 310.464 | 50.2945 | 3.7138 | 80.5531 | 2257127.136 | 0 | 3584658.259 | 0 | 0 | 0 | 0 | 2278296.304 | 5927659.6403 | 4045749.5057 | 18093490.8451 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26022948.0652 | 44113614.4043 | 749894.2093 | 2.8967 | 8983.7055 | 15229.0094 | 183.145 | 310.464
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8339 | 14.9218 | 0.72415 | 4 | 8983.9057 | 15229.4062 | 183.1491 | 310.472 | 50.2938 | 3.7137 | 78.3334 | 2257086.6896 | 0 | 3584621.4279 | 0 | 0 | 0 | 0 | 2278266.1658 | 5927581.2268 | 4045695.9869 | 18093251.4971 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26022708.7172 | 44113375.0563 | 1000000 | 2.8966 | 8983.9057 | 15229.4062 | 183.1491 | 310.472
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9192 | 0.72407 | 4 | 8984.0563 | 15230.1958 | 183.1521 | 310.4881 | 50.2949 | 3.7139 | 77.0207 | 2256881.3325 | 0 | 3584107.9658 | 0 | 0 | 0 | 0 | 2277985.8263 | 5926851.841 | 4045198.1661 | 18091025.1316 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020482.3518 | 44111148.6909 | 1333521.4322 | 2.8963 | 8984.0563 | 15230.1958 | 183.1521 | 310.4881
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9191 | 0.72406 | 4 | 8984.1694 | 15230.42 | 183.1544 | 310.4927 | 50.2945 | 3.7139 | 78.5289 | 2256858.496 | 0 | 3584087.1894 | 0 | 0 | 0 | 0 | 2277968.8173 | 5926807.587 | 4045167.9618 | 18090890.0515 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020347.2717 | 44111013.6108 | 1778279.41 | 2.8962 | 8984.1694 | 15230.42 | 183.1544 | 310.4927
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.919 | 0.72405 | 4 | 8984.2543 | 15230.5883 | 183.1562 | 310.4961 | 50.2942 | 3.7139 | 76.7308 | 2256841.345 | 0 | 3584071.5903 | 0 | 0 | 0 | 0 | 2277956.0448 | 5926774.3554 | 4045145.2806 | 18090788.6161 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020245.8363 | 44110912.1754 | 2371373.7057 | 2.8962 | 8984.2543 | 15230.5883 | 183.1562 | 310.4961
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9189 | 0.72404 | 4 | 8984.3181 | 15230.7148 | 183.1575 | 310.4987 | 50.294 | 3.7138 | 77.811 | 2256828.469 | 0 | 3584059.8818 | 0 | 0 | 0 | 0 | 2277946.4568 | 5926749.4096 | 4045128.2545 | 18090712.4717 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020169.6919 | 44110836.031 | 3162277.6602 | 2.8962 | 8984.3181 | 15230.7148 | 183.1575 | 310.4987
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9189 | 0.72404 | 4 | 8984.366 | 15230.8097 | 183.1585 | 310.5007 | 50.2938 | 3.7138 | 78.3485 | 2256818.8052 | 0 | 3584051.0956 | 0 | 0 | 0 | 0 | 2277939.2613 | 5926730.6883 | 4045115.4769 | 18090655.3272 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020112.5473 | 44110778.8864 | 4216965.0343 | 2.8962 | 8984.366 | 15230.8097 | 183.1585 | 310.5007
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9188 | 0.72403 | 4 | 8984.4019 | 15230.8809 | 183.1592 | 310.5021 | 50.2937 | 3.7138 | 78.0774 | 2256811.5536 | 0 | 3584044.5035 | 0 | 0 | 0 | 0 | 2277933.8623 | 5926716.6411 | 4045105.8894 | 18090612.4499 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020069.6701 | 44110736.0092 | 5623413.2519 | 2.8961 | 8984.4019 | 15230.8809 | 183.1592 | 310.5021
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9188 | 0.72403 | 4 | 8984.4289 | 15230.9343 | 183.1597 | 310.5032 | 50.2936 | 3.7138 | 78.5219 | 2256806.1131 | 0 | 3584039.5581 | 0 | 0 | 0 | 0 | 2277929.8118 | 5926706.1027 | 4045098.6967 | 18090580.2824 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020037.5026 | 44110703.8417 | 7498942.0933 | 2.8961 | 8984.4289 | 15230.9343 | 183.1597 | 310.5032
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8144 | 14.9188 | 0.72403 | 4 | 8984.4491 | 15230.9744 | 183.1601 | 310.504 | 50.2935 | 3.7138 | 77.6854 | 2256802.0319 | 0 | 3584035.8486 | 0 | 0 | 0 | 0 | 2277926.7734 | 5926698.1973 | 4045093.3012 | 18090556.1524 | 961560.8286 | 6967896.3915 | 6967896.3915 | 7440735.7703 | 3682034.1773 | 0 | 26020013.3726 | 44110679.7117 | 10000000 | 2.8961 | 8984.4491 | 15230.9744 | 183.1601 | 310.504
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6088 | 0.032778 | 0.0014308 | 4 | 1513969.9025 | 4801193.9277 | 30864.3243 | 97878.8323 | 45.1361 | 4.0555 | 29.8184 | 47429.6096 | 0 | 37243.2283 | 0 | 0 | 0 | 28364.1362 | 44084.4199 | 114698.6177 | 78284.1634 | 350104.1752 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8664460.5348 | 27477267.0428 | 100 | 0.005723 | 1513969.9025 | 4801193.9277 | 30864.3243 | 97878.8323
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | 0.060604 | 0.0025025 | 4 | 878748.9101 | 2758139.7975 | 17914.4851 | 56228.4104 | 47.6381 | 4.276 | 35.8164 | 65100.8932 | 0 | 53889.5191 | 0 | 0 | 0 | 36621.2333 | 60688.5418 | 157899.1368 | 107769.4053 | 481968.7295 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8796325.089 | 27609131.5971 | 133.3521 | 0.01001 | 878748.9101 | 2758139.7975 | 17914.4851 | 56228.4104
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.095678 | 0.0040334 | 4 | 553994.4854 | 1720063.5841 | 11293.9269 | 35065.8227 | 49.554 | 4.4271 | 91.6785 | 84494.6794 | 0 | 72649.0738 | 0 | 0 | 0 | 44172.7477 | 78513.4353 | 204275.8534 | 139422.4674 | 623528.2571 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 8937884.6167 | 27750691.1247 | 177.8279 | 0.016134 | 553994.4854 | 1720063.5841 | 11293.9269 | 35065.8227
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.14484 | 0.0061735 | 4 | 369405.7558 | 1131246.421 | 7530.836 | 23061.9884 | 51.2553 | 4.5486 | 127.1442 | 109145.9215 | 0 | 97162.6602 | 0 | 0 | 0 | 54473.1796 | 101704.8869 | 264615.2532 | 180605.3476 | 807707.2491 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9122063.6086 | 27934870.1167 | 237.1374 | 0.024694 | 369405.7558 | 1131246.421 | 7530.836 | 23061.9884
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.2077 | 0.0090971 | 4 | 256444.7912 | 773444.8818 | 5227.9739 | 15767.7201 | 52.6001 | 4.6367 | 174.065 | 137397.3374 | 0 | 126067.4486 | 0 | 0 | 0 | 64974.411 | 128091.2868 | 333267.2531 | 227461.7482 | 1017259.485 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9331615.8446 | 28144422.3527 | 316.2278 | 0.036388 | 256444.7912 | 773444.8818 | 5227.9739 | 15767.7201
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6238 | 0.28909 | 0.013046 | 4 | 183542.817 | 544045.8795 | 3741.7686 | 11091.1111 | 53.6885 | 4.7031 | 226.4729 | 170618.5166 | 0 | 161017.2616 | 0 | 0 | 0 | 76403.8545 | 159135.4568 | 414037.8153 | 282589.3166 | 1263802.2213 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9578158.5809 | 28390965.089 | 421.6965 | 0.052185 | 183542.817 | 544045.8795 | 3741.7686 | 11091.1111
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4392 | 0.39625 | 0.01835 | 4 | 134574.0217 | 390879.9617 | 2743.4735 | 7968.6167 | 54.5796 | 4.7544 | 43.7442 | 210625.7102 | 0 | 204288.2641 | 0 | 0 | 0 | 89839.9313 | 196854.0232 | 512173.788 | 349569.1344 | 1563350.8511 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 9877707.2107 | 28690513.7188 | 562.3413 | 0.0734 | 134574.0217 | 390879.9617 | 2743.4735 | 7968.6167
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4844 | 0.53431 | 0.025414 | 4 | 100646.9069 | 285706.701 | 2051.8233 | 5824.5175 | 55.2858 | 4.7931 | 54.3597 | 257809.0227 | 0 | 256735.6021 | 0 | 0 | 0 | 104457.2538 | 241410.7327 | 628101.2062 | 428691.9794 | 1917205.7969 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 10231562.1564 | 29044368.6645 | 749.8942 | 0.10166 | 100646.9069 | 285706.701 | 2051.8233 | 5824.5175
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.848 | 0.71477 | 0.034809 | 4 | 76561.8788 | 211674.9036 | 1560.8175 | 4315.2792 | 55.8501 | 4.8226 | 62.2118 | 314513.6607 | 0 | 321486.6088 | 0 | 0 | 0 | 121423.0331 | 295395.088 | 768557.4252 | 524556.235 | 2345932.0508 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 10660288.4104 | 29473094.9185 | 1000 | 0.13924 | 76561.8788 | 211674.9036 | 1560.8175 | 4315.2792
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5802 | 0.94473 | 0.047197 | 4 | 59126.1514 | 158777.4739 | 1205.3666 | 3236.8936 | 56.2857 | 4.8443 | 53.934 | 380958.0171 | 0 | 399389.4061 | 0 | 0 | 0 | 139129.1754 | 358595.8734 | 932992.9045 | 636786.8284 | 2847852.205 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 11162208.5645 | 29975015.0726 | 1333.5214 | 0.18879 | 59126.1514 | 158777.4739 | 1205.3666 | 3236.8936
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7922 | 1.239 | 0.063475 | 4 | 46299.7977 | 120394.6634 | 943.884 | 2454.4081 | 56.6211 | 4.8597 | 51.7072 | 459376.0785 | 0 | 493738.5474 | 0 | 0 | 0 | 157946.2606 | 433313.7457 | 1127393.4814 | 769469.2167 | 3441237.3302 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 11755593.6897 | 30568400.1978 | 1778.2794 | 0.2539 | 46299.7977 | 120394.6634 | 943.884 | 2454.4081
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.587 | 1.6115 | 0.084716 | 4 | 36736.2186 | 92253.2922 | 748.9175 | 1880.7081 | 56.8725 | 4.8697 | 57.052 | 551075.7987 | 0 | 606920.7554 | 0 | 0 | 0 | 176821.8789 | 520579.1889 | 1354440.264 | 924433.3112 | 4134271.1972 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 12448627.5567 | 31261434.0648 | 2371.3737 | 0.33887 | 36736.2186 | 92253.2922 | 748.9175 | 1880.7081
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0797 | 2.078 | 0.11219 | 4 | 29523.1101 | 71445.9181 | 601.8685 | 1456.5217 | 57.0523 | 4.8743 | 67.3194 | 657314.5491 | 0 | 741421.5432 | 0 | 0 | 0 | 194320.9305 | 621292.2389 | 1616474.961 | 1103277.3762 | 4934101.5989 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 13248457.9585 | 32061264.4666 | 3162.2777 | 0.44875 | 29523.1101 | 71445.9181 | 601.8685 | 1456.5217
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.3964 | 2.656 | 0.14733 | 4 | 24028.9881 | 55952.3904 | 489.8634 | 1140.6652 | 57.1685 | 4.8734 | 63.9546 | 779207.1448 | 0 | 899749.0275 | 0 | 0 | 0 | 208582.6424 | 736140.1377 | 1915285.6353 | 1307221.8013 | 5846186.389 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 14160542.7486 | 32973349.2566 | 4216.965 | 0.58931 | 24028.9881 | 55952.3904 | 489.8634 | 1140.6652
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.6239 | 3.3579 | 0.19152 | 4 | 19809.0574 | 44365.8813 | 403.8344 | 904.4585 | 57.2239 | 4.8661 | 64.6703 | 916420.2278 | 0 | 1082739.1194 | 0 | 0 | 0 | 216100.1053 | 863951.1865 | 2247823.7664 | 1534185.9087 | 6861220.3141 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 15175576.6736 | 33988383.1817 | 5623.4133 | 0.76609 | 19809.0574 | 44365.8813 | 403.8344 | 904.4585
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.8145 | 4.192 | 0.24593 | 4 | 16543.4744 | 35667.318 | 337.2611 | 727.1265 | 57.2167 | 4.8505 | 38.9246 | 1067623.6268 | 0 | 1290124.0775 | 0 | 0 | 0 | 212286.9226 | 1002313.5045 | 2607814.1359 | 1779886.733 | 7960049.0002 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 16274405.3597 | 35087211.8678 | 7498.9421 | 0.98374 | 16543.4744 | 35667.318 | 337.2611 | 727.1265
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.7593 | 5.1317 | 0.31022 | 4 | 14005.3235 | 29166.1039 | 285.5175 | 594.5905 | 57.1476 | 4.8268 | 42.7083 | 1225777.0992 | 0 | 1513441.8836 | 0 | 0 | 0 | 187457.5404 | 1141403.844 | 2969698.668 | 2026880.3621 | 9064659.3973 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 17379015.7569 | 36191822.2649 | 10000 | 1.2409 | 14005.3235 | 29166.1039 | 285.5175 | 594.5905
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.3339 | 6.0307 | 0.3789 | 4 | 12014.4868 | 24427.2259 | 244.9316 | 497.982 | 57.0345 | 4.7982 | 58.8106 | 1366190.7837 | 0 | 1717694.0661 | 0 | 0 | 0 | 110834.8751 | 1245940.6927 | 3241682.1049 | 2212514.6465 | 9894857.1691 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 18209213.5287 | 37022020.0368 | 13335.2143 | 1.5156 | 12014.4868 | 24427.2259 | 244.9316 | 497.982
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.2304 | 7.2389 | 0.46333 | 4 | 10383.6323 | 20534.4899 | 211.6844 | 418.6234 | 56.8144 | 4.7498 | 40.8499 | 1543695.3225 | 0 | 1985191.2331 | 0 | 0 | 0 | 0 | 1376265.7567 | 3580761.188 | 2443943.0881 | 10929856.5884 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 19244212.948 | 38057019.4561 | 17782.7941 | 1.8533 | 10383.6323 | 20534.4899 | 211.6844 | 418.6234
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.7682 | 9.3194 | 0.58158 | 4 | 9240.2949 | 17327.2607 | 188.3759 | 353.2396 | 56.2562 | 4.6402 | 43.9093 | 1823201.3654 | 0 | 2432650.7983 | 0 | 0 | 0 | 0 | 1659782.3439 | 4318413.1906 | 2947405.7371 | 13181453.4352 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 21495809.7948 | 40308616.3029 | 23713.7371 | 2.3263 | 9240.2949 | 17327.2607 | 188.3759 | 353.2396
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9138 | 11.7327 | 0.70314 | 4 | 8500.3397 | 15189.2118 | 173.2909 | 309.6526 | 55.3258 | 4.4711 | 62.188 | 2104205.5952 | 0 | 2930350.9763 | 0 | 0 | 0 | 0 | 1963477.0629 | 5108564.5531 | 3486700.278 | 15593298.4654 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 23907654.8249 | 42720461.333 | 31622.7766 | 2.8126 | 8500.3397 | 15189.2118 | 173.2909 | 309.6526
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7849 | 14.3463 | 0.80976 | 4 | 8121.2923 | 13929.4653 | 165.5635 | 283.971 | 53.9664 | 4.2363 | 54.2368 | 2357223.5549 | 0 | 3451373.0184 | 0 | 0 | 0 | 0 | 2265352.6636 | 5893982.9429 | 4022764.4678 | 17990696.6476 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 26305053.0072 | 45117859.5153 | 42169.6503 | 3.239 | 8121.2923 | 13929.4653 | 165.5635 | 283.971
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9855 | 16.0631 | 0.86147 | 4 | 8056.5546 | 13516.0682 | 164.2438 | 275.5433 | 52.8565 | 4.0501 | 59.7405 | 2492409.5199 | 0 | 3786550.3733 | 0 | 0 | 0 | 0 | 2448794.3584 | 6371260.6036 | 4348516.2783 | 19447531.1335 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27761887.4931 | 46574694.0011 | 56234.1325 | 3.4459 | 8056.5546 | 13516.0682 | 164.2438 | 275.5433
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9117 | 16.0509 | 0.86091 | 4 | 8058.6214 | 13521.7093 | 164.2859 | 275.6583 | 52.8539 | 4.0505 | 78.8349 | 2491184.5558 | 0 | 3784208.9926 | 0 | 0 | 0 | 0 | 2447403.4839 | 6367641.8336 | 4346046.3934 | 19436485.2592 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27750841.6188 | 46563648.1269 | 74989.4209 | 3.4436 | 8058.6214 | 13521.7093 | 164.2859 | 275.6583
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8534 | 16.0412 | 0.86047 | 4 | 8060.2179 | 13526.0955 | 164.3184 | 275.7478 | 52.852 | 4.0507 | 73.5936 | 2490226.5641 | 0 | 3782367.9442 | 0 | 0 | 0 | 0 | 2446311.8582 | 6364801.6476 | 4344107.9081 | 19427815.9222 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27742172.2817 | 46554978.7898 | 100000 | 3.4419 | 8060.2179 | 13526.0955 | 164.3184 | 275.7478
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7996 | 16.0327 | 0.8601 | 4 | 8061.4434 | 13529.6502 | 164.3434 | 275.8202 | 52.8514 | 4.0511 | 79.3437 | 2489408.9839 | 0 | 3780731.5605 | 0 | 0 | 0 | 0 | 2445354.8123 | 6362311.6105 | 4342408.4066 | 19420215.3739 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27734571.7334 | 46547378.2415 | 133352.1432 | 3.4404 | 8061.4434 | 13529.6502 | 164.3434 | 275.8202
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7607 | 16.0265 | 0.85983 | 4 | 8062.3793 | 13532.3205 | 164.3625 | 275.8747 | 52.8507 | 4.0513 | 74.9908 | 2488804.641 | 0 | 3779536.0282 | 0 | 0 | 0 | 0 | 2444652.861 | 6360485.277 | 4341161.8964 | 19414640.7035 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27728997.0631 | 46541803.5712 | 177827.941 | 3.4393 | 8062.3793 | 13532.3205 | 164.3625 | 275.8747
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7413 | 16.023 | 0.85965 | 4 | 8063.0911 | 13534.1385 | 164.377 | 275.9117 | 52.8493 | 4.0513 | 73.6933 | 2488439.0541 | 0 | 3778881.6157 | 0 | 0 | 0 | 0 | 2444255.0612 | 6359450.2837 | 4340455.4922 | 19411481.507 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27725837.8665 | 46538644.3746 | 237137.3706 | 3.4386 | 8063.0911 | 13534.1385 | 164.377 | 275.9117
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7265 | 16.0204 | 0.85952 | 4 | 8063.6306 | 13535.5181 | 164.388 | 275.9398 | 52.8482 | 4.0514 | 81.2626 | 2488161.3594 | 0 | 3778383.9535 | 0 | 0 | 0 | 0 | 2443952.672 | 6358663.529 | 4339918.516 | 19409080.03 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27723436.3896 | 46536242.8977 | 316227.766 | 3.4381 | 8063.6306 | 13535.5181 | 164.388 | 275.9398
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.705 | 16.0171 | 0.85939 | 4 | 8064.0385 | 13536.7767 | 164.3963 | 275.9655 | 52.8484 | 4.0515 | 80.9462 | 2487856.4341 | 0 | 3777750.1497 | 0 | 0 | 0 | 0 | 2443586.5677 | 6357711.0007 | 4339268.3958 | 19406172.5481 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27720528.9077 | 46533335.4157 | 421696.5034 | 3.4375 | 8064.0385 | 13536.7767 | 164.3963 | 275.9655
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6876 | 16.0145 | 0.85928 | 4 | 8064.3463 | 13537.752 | 164.4026 | 275.9854 | 52.8486 | 4.0517 | 79.5702 | 2487615.1728 | 0 | 3777241.5952 | 0 | 0 | 0 | 0 | 2443294.1395 | 6356950.1625 | 4338749.1082 | 19403850.1783 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27718206.5379 | 46531013.046 | 562341.3252 | 3.4371 | 8064.3463 | 13537.752 | 164.4026 | 275.9854
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.683 | 16.0136 | 0.85923 | 4 | 8064.5782 | 13538.3083 | 164.4073 | 275.9967 | 52.8479 | 4.0517 | 79.3195 | 2487512.0185 | 0 | 3777071.5686 | 0 | 0 | 0 | 0 | 2443187.599 | 6356672.9658 | 4338559.9157 | 19403004.0676 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27717360.4271 | 46530166.9352 | 749894.2093 | 3.4369 | 8064.5782 | 13538.3083 | 164.4073 | 275.9967
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.683 | 16.0134 | 0.8592 | 4 | 8064.7527 | 13538.6538 | 164.4109 | 276.0038 | 52.8472 | 4.0516 | 79.2491 | 2487466.6366 | 0 | 3777031.0475 | 0 | 0 | 0 | 0 | 2443154.0968 | 6356585.8001 | 4338500.4233 | 19402738.0043 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27717094.3639 | 46529900.8719 | 1000000 | 3.4368 | 8064.7527 | 13538.6538 | 164.4109 | 276.0038
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0113 | 0.85914 | 4 | 8064.884 | 13539.2248 | 164.4136 | 276.0154 | 52.8479 | 4.0518 | 78.6975 | 2487295.4533 | 0 | 3776628.9643 | 0 | 0 | 0 | 0 | 2442930.5229 | 6356004.1066 | 4338103.4055 | 19400962.4526 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27715318.8121 | 46528125.3202 | 1333521.4322 | 3.4365 | 8064.884 | 13539.2248 | 164.4136 | 276.0154
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0111 | 0.85912 | 4 | 8064.9825 | 13539.4199 | 164.4156 | 276.0194 | 52.8475 | 4.0517 | 77.6677 | 2487269.8288 | 0 | 3776606.0999 | 0 | 0 | 0 | 0 | 2442911.6122 | 6355954.9048 | 4338069.8243 | 19400812.2699 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27715168.6295 | 46527975.1376 | 1778279.41 | 3.4365 | 8064.9825 | 13539.4199 | 164.4156 | 276.0194
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0111 | 0.85911 | 4 | 8065.0566 | 13539.5665 | 164.4171 | 276.0224 | 52.8472 | 4.0517 | 77.6696 | 2487250.5848 | 0 | 3776588.9325 | 0 | 0 | 0 | 0 | 2442897.4118 | 6355917.9582 | 4338044.6075 | 19400699.4948 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27715055.8544 | 46527862.3625 | 2371373.7057 | 3.4364 | 8065.0566 | 13539.5665 | 164.4171 | 276.0224
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.011 | 0.8591 | 4 | 8065.1122 | 13539.6766 | 164.4182 | 276.0246 | 52.8469 | 4.0517 | 78.0505 | 2487236.138 | 0 | 3776576.0467 | 0 | 0 | 0 | 0 | 2442886.752 | 6355890.2238 | 4338025.6782 | 19400614.8387 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27714971.1983 | 46527777.7063 | 3162277.6602 | 3.4364 | 8065.1122 | 13539.6766 | 164.4182 | 276.0246
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0109 | 0.85909 | 4 | 8065.1539 | 13539.7592 | 164.4191 | 276.0263 | 52.8467 | 4.0517 | 77.7182 | 2487225.2954 | 0 | 3776566.3769 | 0 | 0 | 0 | 0 | 2442878.7522 | 6355869.4099 | 4338011.4723 | 19400551.3067 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27714907.6663 | 46527714.1743 | 4216965.0343 | 3.4364 | 8065.1539 | 13539.7592 | 164.4191 | 276.0263
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0109 | 0.85909 | 4 | 8065.1852 | 13539.8212 | 164.4197 | 276.0276 | 52.8466 | 4.0516 | 77.7945 | 2487217.1596 | 0 | 3776559.1217 | 0 | 0 | 0 | 0 | 2442872.7497 | 6355853.7927 | 4338000.8132 | 19400503.6369 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27714859.9965 | 46527666.5046 | 5623413.2519 | 3.4364 | 8065.1852 | 13539.8212 | 164.4197 | 276.0276
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0109 | 0.85909 | 4 | 8065.2087 | 13539.8677 | 164.4202 | 276.0285 | 52.8465 | 4.0516 | 76.1883 | 2487211.0558 | 0 | 3776553.679 | 0 | 0 | 0 | 0 | 2442868.2465 | 6355842.0763 | 4337992.8166 | 19400467.8742 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27714824.2337 | 46527630.7418 | 7498942.0933 | 3.4363 | 8065.2087 | 13539.8677 | 164.4202 | 276.0285
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6681 | 16.0108 | 0.85908 | 4 | 8065.2263 | 13539.9025 | 164.4205 | 276.0292 | 52.8464 | 4.0516 | 77.0817 | 2487206.4769 | 0 | 3776549.5963 | 0 | 0 | 0 | 0 | 2442864.8685 | 6355833.2875 | 4337986.818 | 19400441.0472 | 961560.8286 | 7352795.5309 | 7352795.5309 | 7650990.3052 | 3809020.6719 | 0 | 27714797.4068 | 46527603.9148 | 10000000 | 3.4363 | 8065.2263 | 13539.9025 | 164.4205 | 276.0292
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.6477 | 0.03357 | 0.0015246 | 4 | 1491058.1708 | 4696696.5976 | 30397.2376 | 95748.5129 | 46.8027 | 4.4445 | 33.1001 | 52264.3996 | 0 | 39209.6093 | 0 | 0 | 0 | 33701.0498 | 48818.2729 | 127015.1321 | 86690.4376 | 387698.9013 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9092814.4911 | 28641532.3817 | 100 | 0.0060982 | 1491058.1708 | 4696696.5976 | 30397.2376 | 95748.5129
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.061813 | 0.0027275 | 4 | 845799.9751 | 2637639.9175 | 17242.7765 | 53771.8574 | 49.4421 | 4.6696 | 38.995 | 70666.6092 | 0 | 55864.289 | 0 | 0 | 0 | 42148.0101 | 65784.7742 | 171158.4883 | 116819.1852 | 522441.356 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9227556.9458 | 28776274.8364 | 133.3521 | 0.01091 | 845799.9751 | 2637639.9175 | 17242.7765 | 53771.8574
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2041 | 0.10153 | 0.0044672 | 4 | 525962.1371 | 1619975.3274 | 10722.4496 | 33025.3882 | 51.7361 | 4.8451 | 104.1362 | 93680.142 | 0 | 77239.4084 | 0 | 0 | 0 | 52892.8798 | 87286.8478 | 227102.4729 | 155002.1043 | 693203.8552 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9398319.4451 | 28947037.3357 | 177.8279 | 0.017869 | 525962.1371 | 1619975.3274 | 10722.4496 | 33025.3882
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.15259 | 0.0068939 | 4 | 347786.7759 | 1056697.3365 | 7090.1038 | 21542.2045 | 53.5483 | 4.9707 | 140.1031 | 119847.0263 | 0 | 102215.1903 | 0 | 0 | 0 | 63789.274 | 111482.0813 | 290053.5075 | 197967.4789 | 885354.5583 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9590470.1481 | 29139188.0387 | 237.1374 | 0.027576 | 347786.7759 | 1056697.3365 | 7090.1038 | 21542.2045
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.22055 | 0.010224 | 4 | 240192.6623 | 718192.9455 | 4896.6523 | 14641.3346 | 55.0615 | 5.067 | 186.6074 | 151315.0986 | 0 | 133089.0413 | 0 | 0 | 0 | 76565.2441 | 140778.0598 | 366275.634 | 249990.6464 | 1118013.7244 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 9823129.3142 | 29371847.2048 | 316.2278 | 0.040897 | 240192.6623 | 718192.9455 | 4896.6523 | 14641.3346
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7935 | 0.31012 | 0.014738 | 4 | 171381.4576 | 502987.5408 | 3493.8428 | 10254.0814 | 56.3011 | 5.1405 | 44.7829 | 188963.6501 | 0 | 171072.7687 | 0 | 0 | 0 | 91363.5071 | 176045.9711 | 458035.5049 | 312618.6438 | 1398100.0458 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 10103215.6356 | 29651933.5262 | 421.6965 | 0.058952 | 171381.4576 | 502987.5408 | 3493.8428 | 10254.0814
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6755 | 0.42791 | 0.020808 | 4 | 125452.483 | 360326.6921 | 2557.5186 | 7345.747 | 57.305 | 5.1966 | 47.7171 | 234104.3431 | 0 | 217904.7427 | 0 | 0 | 0 | 108606.2913 | 218639.9971 | 568856.4231 | 388256.1976 | 1736367.9949 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 10441483.5847 | 29990201.4753 | 562.3413 | 0.083231 | 125452.483 | 360326.6921 | 2557.5186 | 7345.747
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7808 | 0.57674 | 0.028871 | 4 | 93772.4518 | 263047.553 | 1911.6783 | 5362.5802 | 58.0823 | 5.2379 | 62.7269 | 286155.0614 | 0 | 273393.8509 | 0 | 0 | 0 | 126280.1368 | 267473.3291 | 695910.7361 | 474973.3769 | 2124186.4911 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 10829302.081 | 30378019.9716 | 749.8942 | 0.11548 | 93772.4518 | 263047.553 | 1911.6783 | 5362.5802
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2307 | 0.77228 | 0.039602 | 4 | 71352.1168 | 194758.8155 | 1454.6094 | 3970.4219 | 58.7086 | 5.2697 | 57.7034 | 349084.0198 | 0 | 342289.1804 | 0 | 0 | 0 | 147335.6076 | 327096.435 | 851037.8272 | 580850.8042 | 2597693.8741 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 11302809.464 | 30851527.3546 | 1000 | 0.15841 | 71352.1168 | 194758.8155 | 1454.6094 | 3970.4219
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0749 | 1.0218 | 0.053752 | 4 | 55153.6519 | 146074.2571 | 1124.3818 | 2977.9213 | 59.1933 | 5.2929 | 50.4077 | 422940.7379 | 0 | 425297.9501 | 0 | 0 | 0 | 169888.2899 | 397069.5214 | 1033093.4445 | 705107.5038 | 3153397.4476 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 11858513.0374 | 31407230.928 | 1333.5214 | 0.21501 | 55153.6519 | 146074.2571 | 1124.3818 | 2977.9213
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4307 | 1.3413 | 0.072344 | 4 | 43251.6621 | 110806.4758 | 881.7436 | 2258.9399 | 59.5667 | 5.3094 | 55.0034 | 510138.3191 | 0 | 525857.2917 | 0 | 0 | 0 | 194404.7968 | 479856.159 | 1248487.2936 | 852118.2317 | 3810862.0919 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 12515977.6817 | 32064695.5723 | 1778.2794 | 0.28938 | 43251.6621 | 110806.4758 | 881.7436 | 2258.9399
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3855 | 1.743 | 0.096541 | 4 | 34382.2737 | 85005.2375 | 700.9292 | 1732.9467 | 59.8449 | 5.3198 | 52.2182 | 611398.3777 | 0 | 645637.2163 | 0 | 0 | 0 | 219126.3706 | 575703.1662 | 1497861.5455 | 1022321.2828 | 4572047.9591 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 13277163.549 | 32825881.4395 | 2371.3737 | 0.38616 | 34382.2737 | 85005.2375 | 700.9292 | 1732.9467
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.1003 | 2.249 | 0.12786 | 4 | 27693.6294 | 65915.8907 | 564.5721 | 1343.7846 | 60.0454 | 5.3244 | 50.7862 | 729440.8165 | 0 | 788851.213 | 0 | 0 | 0 | 244156.2813 | 687354.8412 | 1788356.301 | 1220589.9225 | 5458749.3755 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 14163864.9653 | 33712582.8559 | 3162.2777 | 0.51145 | 27693.6294 | 65915.8907 | 564.5721 | 1343.7846
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6681 | 2.873 | 0.16782 | 4 | 22598.4001 | 51720.1065 | 460.699 | 1054.3843 | 60.1743 | 5.3227 | 51.9068 | 864201.6963 | 0 | 956600.4017 | 0 | 0 | 0 | 266421.2167 | 814017.0927 | 2117905.4974 | 1445514.0206 | 6464659.9255 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 15169775.5153 | 34718493.4059 | 4216.965 | 0.67128 | 22598.4001 | 51720.1065 | 460.699 | 1054.3843
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.2318 | 3.6349 | 0.21811 | 4 | 18684.4163 | 41091.3893 | 380.9071 | 837.7036 | 60.2358 | 5.3135 | 53.2448 | 1016768.5781 | 0 | 1151622.3061 | 0 | 0 | 0 | 284071.6829 | 956460.4012 | 2488513.7669 | 1698461.7797 | 7595898.5149 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 16301014.1048 | 35849731.9954 | 5623.4133 | 0.87244 | 18684.4163 | 41091.3893 | 380.9071 | 837.7036
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8166 | 4.5397 | 0.27989 | 4 | 15658.0817 | 33119.0972 | 319.2112 | 675.1776 | 60.2279 | 5.2953 | 63.661 | 1184746.9021 | 0 | 1372472.1288 | 0 | 0 | 0 | 292112.7395 | 1111239.3905 | 2891216.9475 | 1973314.9752 | 8825103.0836 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 17530218.6734 | 37078936.564 | 7498.9421 | 1.1196 | 15658.0817 | 33119.0972 | 319.2112 | 675.1776
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.764 | 5.5018 | 0.35083 | 4 | 13306.8693 | 27237.3212 | 271.2785 | 555.2696 | 60.154 | 5.2684 | 62.3983 | 1350169.5699 | 0 | 1596519.1195 | 0 | 0 | 0 | 271815.5528 | 1255216.6545 | 3265816.2546 | 2228986.6996 | 9968523.8508 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 18673639.4406 | 38222357.3312 | 10000 | 1.4033 | 13306.8693 | 27237.3212 | 271.2785 | 555.2696
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3387 | 6.6872 | 0.43605 | 4 | 11475.246 | 22683.1248 | 233.9384 | 462.4262 | 59.9928 | 5.2265 | 66.2503 | 1540579.9435 | 0 | 1862928.8008 | 0 | 0 | 0 | 248094.9615 | 1424125.4452 | 3705282.2802 | 2528931.2922 | 11309942.7234 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 20015058.3133 | 39563776.2039 | 13335.2143 | 1.7442 | 11475.246 | 22683.1248 | 233.9384 | 462.4262
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.7512 | 7.7249 | 0.52071 | 4 | 10041.6558 | 19427.1887 | 204.7127 | 396.0495 | 59.7956 | 5.182 | 61.458 | 1694432.7104 | 0 | 2085938.9231 | 0 | 0 | 0 | 161899.1042 | 1537485.5877 | 4000222.1176 | 2730233.7916 | 12210212.2346 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 20915327.8244 | 40464045.715 | 17782.7941 | 2.0829 | 10041.6558 | 19427.1887 | 204.7127 | 396.0495
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5586 | 8.8186 | 0.60977 | 4 | 8853.2367 | 16867.9862 | 180.4852 | 343.8767 | 59.53 | 5.1264 | 59.564 | 1846579.4498 | 0 | 2314768.6226 | 0 | 0 | 0 | 0 | 1622925.7483 | 4222519.8892 | 2881956.5885 | 12888750.2984 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 21593865.8882 | 41142583.7788 | 23713.7371 | 2.4391 | 8853.2367 | 16867.9862 | 180.4852 | 343.8767
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.4849 | 11.1291 | 0.74622 | 4 | 8039.2778 | 14588.5497 | 163.8916 | 297.4073 | 58.7617 | 4.977 | 53.2264 | 2144132.1088 | 0 | 2792846.4969 | 0 | 0 | 0 | 0 | 1925421.6562 | 5009552.1912 | 3419122.3065 | 15291074.7595 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 23996190.3493 | 43544908.2399 | 31622.7766 | 2.9849 | 8039.2778 | 14588.5497 | 163.8916 | 297.4073
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1406 | 13.6532 | 0.87476 | 4 | 7550.6302 | 13137.5363 | 153.9298 | 267.8264 | 57.6102 | 4.7665 | 53.5405 | 2422724.1364 | 0 | 3296768.7478 | 0 | 0 | 0 | 0 | 2230602.2248 | 5803569.4296 | 3961055.3871 | 17714719.9257 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 26419835.5155 | 45968553.4061 | 42169.6503 | 3.499 | 7550.6302 | 13137.5363 | 153.9298 | 267.8264
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.269 | 16.2101 | 0.97667 | 4 | 7340.4068 | 12344.3248 | 149.6441 | 251.6558 | 56.0998 | 4.5018 | 63.6003 | 2654468.0836 | 0 | 3793670.8408 | 0 | 0 | 0 | 0 | 2514774.1805 | 6542926.5666 | 4465681.8254 | 19971521.4969 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 28676637.0867 | 48225354.9773 | 56234.1325 | 3.9067 | 7340.4068 | 12344.3248 | 149.6441 | 251.6558
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3297 | 17.1444 | 1.0049 | 4 | 7326.6642 | 12189.954 | 149.364 | 248.5087 | 55.4471 | 4.3902 | 70.8222 | 2725175.0767 | 0 | 3972856.4498 | 0 | 0 | 0 | 0 | 2612232.2953 | 6796492.5899 | 4638745.8466 | 20745502.2583 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29450617.8481 | 48999335.7387 | 74989.4209 | 4.0196 | 7326.6642 | 12189.954 | 149.364 | 248.5087
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.2707 | 17.1343 | 1.0044 | 4 | 7328.075 | 12193.7956 | 149.3927 | 248.587 | 55.4449 | 4.3905 | 81.9541 | 2724151.577 | 0 | 3970959.8085 | 0 | 0 | 0 | 0 | 2611093.4403 | 6793529.5229 | 4636723.4924 | 20736457.8412 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29441573.431 | 48990291.3216 | 100000 | 4.0176 | 7328.075 | 12193.7956 | 149.3927 | 248.587
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.2124 | 17.1248 | 1.004 | 4 | 7329.1569 | 12196.9755 | 149.4148 | 248.6518 | 55.4445 | 4.3909 | 77.4073 | 2723242.2572 | 0 | 3969175.0262 | 0 | 0 | 0 | 0 | 2610042.7405 | 6790795.8174 | 4634857.6823 | 20728113.5235 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29433229.1134 | 48981947.0039 | 133352.1432 | 4.0159 | 7329.1569 | 12196.9755 | 149.4148 | 248.6518
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1735 | 17.1184 | 1.0037 | 4 | 7329.9825 | 12199.302 | 149.4316 | 248.6993 | 55.4437 | 4.3912 | 73.417 | 2722602.2847 | 0 | 3967955.8937 | 0 | 0 | 0 | 0 | 2609317.6896 | 6788909.3836 | 4633570.1525 | 20722355.4041 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29427470.9939 | 48976188.8845 | 177827.941 | 4.0147 | 7329.9825 | 12199.302 | 149.4316 | 248.6993
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1586 | 17.1154 | 1.0035 | 4 | 7330.6099 | 12200.8073 | 149.4444 | 248.73 | 55.4416 | 4.3912 | 81.7784 | 2722256.5204 | 0 | 3967402.1383 | 0 | 0 | 0 | 0 | 2608966.8769 | 6787996.641 | 4632947.1869 | 20719569.3635 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29424684.9533 | 48973402.8439 | 237137.3706 | 4.0139 | 7330.6099 | 12200.8073 | 149.4444 | 248.73
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1346 | 17.1115 | 1.0033 | 4 | 7331.0853 | 12202.177 | 149.4541 | 248.7579 | 55.4413 | 4.3913 | 79.9646 | 2721872.2728 | 0 | 3966658.2576 | 0 | 0 | 0 | 0 | 2608526.9069 | 6786851.9292 | 4632165.8975 | 20716075.264 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29421190.8538 | 48969908.7444 | 316227.766 | 4.0132 | 7331.0853 | 12202.177 | 149.4541 | 248.7579
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1197 | 17.1089 | 1.0032 | 4 | 7331.4446 | 12203.1519 | 149.4614 | 248.7778 | 55.4408 | 4.3914 | 78.2035 | 2721614.1356 | 0 | 3966181.5888 | 0 | 0 | 0 | 0 | 2608240.3325 | 6786106.3215 | 4631657.005 | 20713799.3833 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29418914.9731 | 48967632.8637 | 421696.5034 | 4.0127 | 7331.4446 | 12203.1519 | 149.4614 | 248.7778
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1003 | 17.1059 | 1.003 | 4 | 7331.7156 | 12204.0348 | 149.4669 | 248.7958 | 55.4411 | 4.3916 | 77.8637 | 2721340.7129 | 0 | 3965613.3127 | 0 | 0 | 0 | 0 | 2607912.07 | 6785252.2498 | 4631074.0835 | 20711192.429 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29416308.0188 | 48965025.9094 | 562341.3252 | 4.0122 | 7331.7156 | 12204.0348 | 149.4669 | 248.7958
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1003 | 17.1056 | 1.003 | 4 | 7331.9198 | 12204.4385 | 149.4711 | 248.804 | 55.44 | 4.3915 | 78.1795 | 2721274.2574 | 0 | 3965555.1642 | 0 | 0 | 0 | 0 | 2607863.4744 | 6785125.814 | 4630987.7885 | 20710806.4985 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29415922.0883 | 48964639.9789 | 749894.2093 | 4.012 | 7331.9198 | 12204.4385 | 149.4711 | 248.804
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1003 | 17.1054 | 1.003 | 4 | 7332.0734 | 12204.7423 | 149.4742 | 248.8102 | 55.4392 | 4.3914 | 77.0207 | 2721224.2553 | 0 | 3965511.4275 | 0 | 0 | 0 | 0 | 2607826.9163 | 6785030.6974 | 4630922.8694 | 20710516.166 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29415631.7558 | 48964349.6464 | 1000000 | 4.0119 | 7332.0734 | 12204.7423 | 149.4742 | 248.8102
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0808 | 17.1026 | 1.0029 | 4 | 7332.1889 | 12205.3176 | 149.4766 | 248.8219 | 55.4404 | 4.3917 | 75.8438 | 2721001.5459 | 0 | 3964987.6268 | 0 | 0 | 0 | 0 | 2607535.7773 | 6784273.2135 | 4630405.8711 | 20708204.0346 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413319.6244 | 48962037.515 | 1333521.4322 | 4.0115 | 7332.1889 | 12205.3176 | 149.4766 | 248.8219
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1031 | 1.0029 | 4 | 7332.2757 | 12205.4066 | 149.4784 | 248.8237 | 55.4395 | 4.3916 | 85.247 | 2721017.3969 | 0 | 3965079.8355 | 0 | 0 | 0 | 0 | 2607577.9206 | 6784382.8617 | 4630480.7082 | 20708538.7229 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413654.3127 | 48962372.2033 | 1778279.41 | 4.0115 | 7332.2757 | 12205.4066 | 149.4784 | 248.8237
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.103 | 1.0029 | 4 | 7332.3408 | 12205.5354 | 149.4797 | 248.8263 | 55.4391 | 4.3915 | 85.2851 | 2720996.197 | 0 | 3965061.3043 | 0 | 0 | 0 | 0 | 2607562.4255 | 6784342.5465 | 4630453.1923 | 20708415.6655 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413531.2554 | 48962249.146 | 2371373.7057 | 4.0115 | 7332.3408 | 12205.5354 | 149.4797 | 248.8263
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1029 | 1.0029 | 4 | 7332.3897 | 12205.6322 | 149.4807 | 248.8283 | 55.4388 | 4.3915 | 85.3132 | 2720980.2823 | 0 | 3965047.3947 | 0 | 0 | 0 | 0 | 2607550.794 | 6784312.2838 | 4630432.5374 | 20708323.2921 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413438.8819 | 48962156.7725 | 3162277.6602 | 4.0114 | 7332.3897 | 12205.6322 | 149.4807 | 248.8283
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1029 | 1.0029 | 4 | 7332.4265 | 12205.7048 | 149.4814 | 248.8298 | 55.4386 | 4.3915 | 85.1008 | 2720968.3383 | 0 | 3965036.9565 | 0 | 0 | 0 | 0 | 2607542.065 | 6784289.5727 | 4630417.0366 | 20708253.9691 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413369.5589 | 48962087.4495 | 4216965.0343 | 4.0114 | 7332.4265 | 12205.7048 | 149.4814 | 248.8298
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1028 | 1.0028 | 4 | 7332.454 | 12205.7593 | 149.482 | 248.8309 | 55.4385 | 4.3915 | 85.2604 | 2720959.3762 | 0 | 3965029.1248 | 0 | 0 | 0 | 0 | 2607535.5154 | 6784272.532 | 4630405.406 | 20708201.9545 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413317.5443 | 48962035.4349 | 5623413.2519 | 4.0114 | 7332.454 | 12205.7593 | 149.482 | 248.8309
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1028 | 1.0028 | 4 | 7332.4747 | 12205.8002 | 149.4824 | 248.8317 | 55.4384 | 4.3915 | 84.9258 | 2720952.6526 | 0 | 3965023.2495 | 0 | 0 | 0 | 0 | 2607530.6018 | 6784259.7479 | 4630396.6805 | 20708162.9324 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413278.5223 | 48961996.4128 | 7498942.0933 | 4.0114 | 7332.4747 | 12205.8002 | 149.4824 | 248.8317
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0855 | 17.1028 | 1.0028 | 4 | 7332.4902 | 12205.8308 | 149.4827 | 248.8324 | 55.4383 | 4.3915 | 84.7239 | 2720947.6089 | 0 | 3965018.8424 | 0 | 0 | 0 | 0 | 2607526.916 | 6784250.1581 | 4630390.1353 | 20708133.6606 | 961560.8286 | 7743554.7612 | 7743554.7612 | 7866811.9264 | 3938351.203 | 0 | 29413249.2504 | 48961967.141 | 10000000 | 4.0114 | 7332.4902 | 12205.8308 | 149.4827 | 248.8324
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.67936 | 0.033812 | 0.0016241 | 4 | 1465778.446 | 4590262.405 | 29881.8762 | 93578.7079 | 48.3481 | 4.8295 | 40.2348 | 56670.6448 | 0 | 40709.618 | 0 | 0 | 0 | 38476.9066 | 52984.296 | 137854.2697 | 94088.3717 | 420784.1068 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9522519.0178 | 29820919.5044 | 100 | 0.0064966 | 1465778.446 | 4590262.405 | 29881.8762 | 93578.7079
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95256 | 0.066013 | 0.0029794 | 4 | 812813.9525 | 2516048.3953 | 16570.3118 | 51293.0497 | 51.4975 | 5.0896 | 33.9299 | 78701.4988 | 0 | 59954.5796 | 0 | 0 | 0 | 50229.0051 | 73665.1826 | 191661.6942 | 130813.0446 | 585025.0049 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9686759.9159 | 29985160.4025 | 133.3521 | 0.011918 | 812813.9525 | 2516048.3953 | 16570.3118 | 51293.0497
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.10763 | 0.0049416 | 4 | 499156.4156 | 1526065.5667 | 10175.9787 | 31110.9107 | 53.913 | 5.2683 | 110.5531 | 103232.9627 | 0 | 81939.7595 | 0 | 0 | 0 | 61768.8723 | 96307.2219 | 250571.636 | 171020.2903 | 764840.7427 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 9866575.6536 | 30164976.1402 | 177.8279 | 0.019767 | 499156.4156 | 1526065.5667 | 10175.9787 | 31110.9107
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.16346 | 0.0076954 | 4 | 327547.0119 | 986982.4285 | 6677.4889 | 20120.9718 | 55.9309 | 5.4038 | 157.856 | 132587.9062 | 0 | 108951.3961 | 0 | 0 | 0 | 75079.2913 | 123481.2515 | 321272.8869 | 219275.3468 | 980648.0787 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10082382.9897 | 30380783.4763 | 237.1374 | 0.030781 | 327547.0119 | 986982.4285 | 6677.4889 | 20120.9718
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.2362 | 0.011474 | 4 | 225167.5137 | 667429.3883 | 4590.3443 | 13606.4508 | 57.5712 | 5.5052 | 205.9624 | 166944.023 | 0 | 141431.7434 | 0 | 0 | 0 | 89632.0782 | 155223.0594 | 403858.56 | 275641.7656 | 1232731.2296 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10334466.1406 | 30632866.6272 | 316.2278 | 0.045897 | 225167.5137 | 667429.3883 | 4590.3443 | 13606.4508
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9787 | 0.33389 | 0.016611 | 4 | 160224.7306 | 465712.2866 | 3266.3979 | 9494.1749 | 58.9459 | 5.5843 | 41.0939 | 208929.0423 | 0 | 182231.6857 | 0 | 0 | 0 | 107521.0988 | 194485.9124 | 506012.4496 | 345363.8944 | 1544544.0832 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 10646278.9941 | 30944679.4808 | 421.6965 | 0.066446 | 160224.7306 | 465712.2866 | 3266.3979 | 9494.1749
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 0.45945 | 0.023501 | 4 | 117124.9754 | 333059.9157 | 2387.751 | 6789.8769 | 60.0333 | 5.6433 | 48.8559 | 257970.5633 | 0 | 231216.9962 | 0 | 0 | 0 | 126936.582 | 240288.4152 | 625181.1664 | 426698.9923 | 1908292.7155 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 11010027.6264 | 31308428.113 | 562.3413 | 0.094002 | 117124.9754 | 333059.9157 | 2387.751 | 6789.8769
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0929 | 0.62299 | 0.032697 | 4 | 87514.7941 | 242713.3243 | 1784.1074 | 4948.0394 | 60.9047 | 5.6883 | 48.7775 | 316456.1955 | 0 | 291232.9087 | 0 | 0 | 0 | 149212.556 | 295191.6475 | 768028.1147 | 524194.9697 | 2344316.3921 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 11446051.3031 | 31744451.7897 | 749.8942 | 0.13079 | 87514.7941 | 242713.3243 | 1784.1074 | 4948.0394
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.623 | 0.83357 | 0.044894 | 4 | 66615.1188 | 179650.4128 | 1358.0393 | 3662.4167 | 61.5904 | 5.722 | 57.144 | 385570.688 | 0 | 364062.7976 | 0 | 0 | 0 | 173999.8405 | 360216.9972 | 937210.736 | 639665.5851 | 2860726.6444 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 11962461.5554 | 32260862.042 | 1000 | 0.17958 | 66615.1188 | 179650.4128 | 1358.0393 | 3662.4167
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5741 | 1.103 | 0.060975 | 4 | 51541.5345 | 134765.6154 | 1050.7439 | 2747.3794 | 62.1239 | 5.7467 | 49.478 | 466933.7064 | 0 | 452055.687 | 0 | 0 | 0 | 201123.7825 | 436844.1386 | 1136578.8396 | 775738.4124 | 3469274.5664 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 12571009.4774 | 32869409.964 | 1333.5214 | 0.2439 | 51541.5345 | 134765.6154 | 1050.7439 | 2747.3794
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0614 | 1.4472 | 0.082082 | 4 | 40476.5933 | 102300.2516 | 825.1701 | 2085.529 | 62.5351 | 5.7641 | 54.9046 | 562842.7073 | 0 | 558464.4169 | 0 | 0 | 0 | 230806.696 | 527324.3899 | 1371989.8933 | 936411.2938 | 4187839.3971 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 13289574.308 | 33587974.7946 | 1778.2794 | 0.32833 | 40476.5933 | 102300.2516 | 825.1701 | 2085.529
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.2091 | 1.8838 | 0.1096 | 4 | 32234.444 | 78534.5805 | 657.1427 | 1601.0337 | 62.8442 | 5.775 | 51.0249 | 675224.6854 | 0 | 686350.9465 | 0 | 0 | 0 | 262488.4064 | 633384.9749 | 1647937.7796 | 1124751.3963 | 5030138.1891 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 14131873.1001 | 34430273.5867 | 2371.3737 | 0.43841 | 32234.444 | 78534.5805 | 657.1427 | 1601.0337
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1138 | 2.427 | 0.14505 | 4 | 26018.9079 | 61003.366 | 530.4306 | 1243.6361 | 63.0641 | 5.7793 | 56.4441 | 804509.8245 | 0 | 837240.2459 | 0 | 0 | 0 | 293753.7681 | 754846.497 | 1963955.7448 | 1340440.1511 | 5994746.2314 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 15096481.1423 | 35394881.6289 | 3162.2777 | 0.58021 | 26018.9079 | 61003.366 | 530.4306 | 1243.6361
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9593 | 3.1025 | 0.19036 | 4 | 21283.0825 | 47941.107 | 433.8844 | 977.3443 | 63.2069 | 5.7766 | 41.668 | 953490.9152 | 0 | 1015641.1308 | 0 | 0 | 0 | 324508.7054 | 894519.8931 | 2327357.2705 | 1588469.1595 | 7103987.0745 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 16205721.9855 | 36504122.4721 | 4216.965 | 0.76144 | 21283.0825 | 47941.107 | 433.8844 | 977.3443
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8176 | 3.9218 | 0.24715 | 4 | 17644.2984 | 38177.1226 | 359.7029 | 778.2923 | 63.2743 | 5.7655 | 53.7308 | 1120912.9569 | 0 | 1221549.7828 | 0 | 0 | 0 | 350606.4183 | 1050296.9716 | 2732657.2746 | 1865094.7404 | 8341118.1445 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 17442853.0554 | 37741253.5421 | 5623.4133 | 0.98858 | 17644.2984 | 38177.1226 | 359.7029 | 778.2923
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.7554 | 4.8953 | 0.31678 | 4 | 14830.745 | 30850.2866 | 302.3448 | 628.9248 | 63.2651 | 5.744 | 70.5878 | 1305365.2816 | 0 | 1454937.9266 | 0 | 0 | 0 | 368384.2232 | 1220188.0982 | 3174679.1366 | 2166783.7439 | 9690338.4101 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 18792073.321 | 39090473.8076 | 7498.9421 | 1.2671 | 14830.745 | 30850.2866 | 302.3448 | 628.9248
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.6554 | 6.0083 | 0.39924 | 4 | 12646.8195 | 25357.5555 | 257.8225 | 516.9481 | 63.1745 | 5.7104 | 73.8319 | 1500885.2322 | 0 | 1710105.2106 | 0 | 0 | 0 | 371084.3296 | 1397009.1612 | 3634731.2715 | 2480778.7791 | 11094593.9843 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 20196328.8952 | 40494729.3818 | 10000 | 1.5969 | 12646.8195 | 25357.5555 | 257.8225 | 516.9481
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.1692 | 7.2137 | 0.49227 | 4 | 10949.2836 | 21257.8432 | 223.216 | 433.3699 | 63.0007 | 5.664 | 60.993 | 1697183.1346 | 0 | 1975178.3577 | 0 | 0 | 0 | 350009.7085 | 1568724.7683 | 4081500.0575 | 2785707.6557 | 12458303.6823 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 21560038.5932 | 41858439.0799 | 13335.2143 | 1.9691 | 10949.2836 | 21257.8432 | 223.216 | 433.3699
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.6882 | 8.427 | 0.59077 | 4 | 9628.6688 | 18218.5471 | 196.2934 | 371.4097 | 62.754 | 5.6067 | 56.8046 | 1880430.1233 | 0 | 2232071.5331 | 0 | 0 | 0 | 295077.462 | 1718955.8562 | 4472370.5314 | 3052484.7857 | 13651390.2917 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 22753125.2027 | 43051525.6893 | 17782.7941 | 2.3631 | 9628.6688 | 18218.5471 | 196.2934 | 371.4097
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.9233 | 9.468 | 0.68412 | 4 | 8597.2917 | 16014.9509 | 175.2674 | 326.4864 | 62.4902 | 5.5501 | 65.054 | 2026563.3264 | 0 | 2444575.2435 | 0 | 0 | 0 | 186125.0526 | 1816332.8127 | 4725725.3977 | 3225404.6879 | 14424726.5207 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 23526461.4316 | 43824861.9182 | 23713.7371 | 2.7365 | 8597.2917 | 16014.9509 | 175.2674 | 326.4864
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2017 | 10.5143 | 0.77676 | 4 | 7733.1958 | 14266.2258 | 157.6517 | 290.8363 | 62.1724 | 5.485 | 71.5813 | 2165093.4251 | 0 | 2653895.6697 | 0 | 0 | 0 | 0 | 1879405.747 | 4889828.2345 | 3337408.246 | 14925631.3222 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 24027366.2331 | 44325766.7198 | 31622.7766 | 3.107 | 7733.1958 | 14266.2258 | 157.6517 | 290.8363
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.6297 | 12.9389 | 0.92328 | 4 | 7163.7372 | 12660.0203 | 146.0425 | 258.0916 | 61.2147 | 5.299 | 53.6831 | 2463986.5037 | 0 | 3139288.4553 | 0 | 0 | 0 | 0 | 2185277.234 | 5685643.1009 | 3880568.2447 | 17354763.5387 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 26456498.4497 | 46754898.9363 | 42169.6503 | 3.6931 | 7163.7372 | 12660.0203 | 146.0425 | 258.0916
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.6742 | 15.4249 | 1.0501 | 4 | 6847.3023 | 11679.6843 | 139.5915 | 238.1062 | 59.9259 | 5.0605 | 54.4272 | 2725001.5537 | 0 | 3622664.0514 | 0 | 0 | 0 | 0 | 2475589.586 | 6440976.2895 | 4396098.6664 | 19660330.1469 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 28762065.0579 | 49060465.5445 | 56234.1325 | 4.2005 | 6847.3023 | 11679.6843 | 139.5915 | 238.1062
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.924 | 17.7728 | 1.1427 | 4 | 6732.8695 | 11173.7473 | 137.2587 | 227.792 | 58.4122 | 4.7905 | 63.3095 | 2927537.9682 | 0 | 4069926.021 | 0 | 0 | 0 | 0 | 2729010.9558 | 7100326.7099 | 4846118.8766 | 21672920.5315 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 30774655.4425 | 51073055.9291 | 74989.4209 | 4.5708 | 6732.8695 | 11173.7473 | 137.2587 | 227.792
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2996 | 18.2277 | 1.1567 | 4 | 6731.4751 | 11118.6855 | 137.2302 | 226.6694 | 58.0739 | 4.7315 | 70.3318 | 2961038.269 | 0 | 4155888.1866 | 0 | 0 | 0 | 0 | 2775601.3177 | 7221545.2745 | 4928853.0378 | 22042926.0855 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31144660.9965 | 51443061.4831 | 100000 | 4.6267 | 6731.4751 | 11118.6855 | 137.2302 | 226.6694
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2601 | 18.2205 | 1.1563 | 4 | 6732.4386 | 11121.198 | 137.2499 | 226.7207 | 58.0714 | 4.7317 | 84.305 | 2960265.7804 | 0 | 4154550.1979 | 0 | 0 | 0 | 0 | 2774778.2315 | 7219403.7732 | 4927391.4191 | 22036389.4021 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31138124.313 | 51436524.7997 | 133352.1432 | 4.6251 | 6732.4386 | 11121.198 | 137.2499 | 226.7207
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2212 | 18.2138 | 1.1559 | 4 | 6733.1733 | 11123.2486 | 137.2648 | 226.7625 | 58.0704 | 4.732 | 80.9234 | 2959591.2957 | 0 | 4153307.7694 | 0 | 0 | 0 | 0 | 2774030.6354 | 7217458.6814 | 4926063.854 | 22030452.2358 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31132187.1468 | 51430587.6334 | 177827.941 | 4.6237 | 6733.1733 | 11123.2486 | 137.2648 | 226.7625
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2017 | 18.2101 | 1.1557 | 4 | 6733.7313 | 11124.6509 | 137.2762 | 226.7911 | 58.0687 | 4.732 | 79.8201 | 2959178.0957 | 0 | 4152621.4975 | 0 | 0 | 0 | 0 | 2773601.8413 | 7216343.0472 | 4925302.4107 | 22027046.8925 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31128781.8034 | 51427182.29 | 237137.3706 | 4.6228 | 6733.7313 | 11124.6509 | 137.2762 | 226.7911
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1823 | 18.2066 | 1.1555 | 4 | 6734.154 | 11125.7855 | 137.2848 | 226.8142 | 58.0678 | 4.7321 | 77.4813 | 2958819.0122 | 0 | 4151981.7774 | 0 | 0 | 0 | 0 | 2773212.3079 | 7215329.5612 | 4924610.6857 | 22023953.3445 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31125688.2554 | 51424088.742 | 316227.766 | 4.6221 | 6734.154 | 11125.7855 | 137.2848 | 226.8142
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1675 | 18.204 | 1.1554 | 4 | 6734.4733 | 11126.6447 | 137.2913 | 226.8317 | 58.0672 | 4.7322 | 86.5773 | 2958546.564 | 0 | 4151495.4285 | 0 | 0 | 0 | 0 | 2772916.3771 | 7214559.6097 | 4924085.178 | 22021603.1572 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31123338.0682 | 51421738.5548 | 421696.5034 | 4.6215 | 6734.4733 | 11126.6447 | 137.2913 | 226.8317
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.148 | 18.2009 | 1.1552 | 4 | 6734.7141 | 11127.4202 | 137.2963 | 226.8475 | 58.0675 | 4.7324 | 84.7301 | 2958260.0749 | 0 | 4150918.1212 | 0 | 0 | 0 | 0 | 2772579.4965 | 7213683.1156 | 4923486.9527 | 22018927.7609 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31120662.6718 | 51419063.1585 | 562341.3252 | 4.6209 | 6734.7141 | 11127.4202 | 137.2963 | 226.8475
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.146 | 18.2003 | 1.1552 | 4 | 6734.8955 | 11127.8097 | 137.3 | 226.8555 | 58.0665 | 4.7324 | 84.2463 | 2958167.9683 | 0 | 4150804.6018 | 0 | 0 | 0 | 0 | 2772499.3023 | 7213474.4669 | 4923344.5457 | 22018290.885 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31120025.7959 | 51418426.2825 | 749894.2093 | 4.6207 | 6734.8955 | 11127.8097 | 137.3 | 226.8555
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1286 | 18.1977 | 1.1551 | 4 | 6735.0319 | 11128.3478 | 137.3027 | 226.8664 | 58.0673 | 4.7326 | 82.8062 | 2957942.9753 | 0 | 4150314.673 | 0 | 0 | 0 | 0 | 2772220.4829 | 7212749.0358 | 4922849.4241 | 22016076.5911 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31117811.502 | 51416211.9887 | 1000000 | 4.6203 | 6735.0319 | 11128.3478 | 137.3027 | 226.8664
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1286 | 18.1975 | 1.155 | 4 | 6735.1345 | 11128.5504 | 137.3048 | 226.8706 | 58.0667 | 4.7325 | 83.0679 | 2957902.1453 | 0 | 4150279.7103 | 0 | 0 | 0 | 0 | 2772190.9237 | 7212672.1289 | 4922796.9336 | 22015841.8418 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31117576.7528 | 51415977.2394 | 1333521.4322 | 4.6202 | 6735.1345 | 11128.5504 | 137.3048 | 226.8706
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.124 | 18.1967 | 1.155 | 4 | 6735.2115 | 11128.774 | 137.3064 | 226.8751 | 58.0666 | 4.7326 | 81.5923 | 2957826.1084 | 0 | 4150135.592 | 0 | 0 | 0 | 0 | 2772105.0631 | 7212448.7374 | 4922644.4642 | 22015159.9651 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31116894.876 | 51415295.3627 | 1778279.41 | 4.62 | 6735.2115 | 11128.774 | 137.3064 | 226.8751
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.124 | 18.1966 | 1.155 | 4 | 6735.2694 | 11128.8883 | 137.3076 | 226.8774 | 58.0662 | 4.7325 | 82.5074 | 2957803.0769 | 0 | 4150115.8754 | 0 | 0 | 0 | 0 | 2772088.3914 | 7212405.3609 | 4922614.8589 | 22015027.5636 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31116762.4745 | 51415162.9612 | 2371373.7057 | 4.62 | 6735.2694 | 11128.8883 | 137.3076 | 226.8774
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.124 | 18.1965 | 1.155 | 4 | 6735.3128 | 11128.9741 | 137.3085 | 226.8792 | 58.066 | 4.7325 | 82.2904 | 2957785.7878 | 0 | 4150101.076 | 0 | 0 | 0 | 0 | 2772075.8769 | 7212372.8007 | 4922592.6359 | 22014928.1774 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31116663.0883 | 51415063.5749 | 3162277.6602 | 4.6199 | 6735.3128 | 11128.9741 | 137.3085 | 226.8792
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.124 | 18.1964 | 1.155 | 4 | 6735.3454 | 11129.0385 | 137.3091 | 226.8805 | 58.0657 | 4.7325 | 82.622 | 2957772.8127 | 0 | 4150089.9701 | 0 | 0 | 0 | 0 | 2772066.4853 | 7212348.3657 | 4922575.9586 | 22014853.5924 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31116588.5034 | 51414988.99 | 4216965.0343 | 4.6199 | 6735.3454 | 11129.0385 | 137.3091 | 226.8805
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.124 | 18.1964 | 1.155 | 4 | 6735.3699 | 11129.0868 | 137.3096 | 226.8815 | 58.0656 | 4.7325 | 83.5712 | 2957763.0771 | 0 | 4150081.6374 | 0 | 0 | 0 | 0 | 2772059.4387 | 7212330.0318 | 4922563.4453 | 22014797.6302 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31116532.5412 | 51414933.0278 | 5623413.2519 | 4.6199 | 6735.3699 | 11129.0868 | 137.3096 | 226.8815
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1091 | 18.1944 | 1.1549 | 4 | 6735.3883 | 11129.3515 | 137.31 | 226.8869 | 58.0669 | 4.7327 | 82.8806 | 2957610.6185 | 0 | 4149698.27 | 0 | 0 | 0 | 0 | 2771850.4665 | 7211786.3292 | 4922192.357 | 22013138.0412 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31114872.9521 | 51413273.4388 | 7498942.0933 | 4.6196 | 6735.3883 | 11129.3515 | 137.31 | 226.8869
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1091 | 18.1943 | 1.1549 | 4 | 6735.402 | 11129.3787 | 137.3103 | 226.8874 | 58.0668 | 4.7327 | 83.22 | 2957605.1418 | 0 | 4149693.5829 | 0 | 0 | 0 | 0 | 2771846.5027 | 7211776.016 | 4922185.3181 | 22013106.5616 | 961560.8286 | 8140174.0823 | 8140174.0823 | 8088200.634 | 4070025.7703 | 0 | 31114841.4725 | 51413241.9592 | 10000000 | 4.6196 | 6735.402 | 11129.3787 | 137.3103 | 226.8874
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.036045 | 0.0017353 | 4 | 1437247.5181 | 4471656.6501 | 29300.2347 | 91160.7692 | 50.2002 | 5.2465 | 34.8424 | 63113.8596 | 0 | 43855.4611 | 0 | 0 | 0 | 45336.7143 | 59399.3536 | 154544.9337 | 105480.0928 | 471730.4151 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 9975944.7381 | 31037799.0343 | 100 | 0.006941 | 1437247.5181 | 4471656.6501 | 29300.2347 | 91160.7692
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0109 | 0.069376 | 0.0032505 | 4 | 780344.217 | 2400213.9014 | 15908.3724 | 48931.6069 | 53.4527 | 5.5064 | 30.3329 | 86237.4187 | 0 | 63420.722 | 0 | 0 | 0 | 57612.5451 | 80835.5675 | 210317.5649 | 143546.0596 | 641969.8779 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10146184.2008 | 31208038.497 | 133.3521 | 0.013002 | 780344.217 | 2400213.9014 | 15908.3724 | 48931.6069
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3597 | 0.11399 | 0.0054594 | 4 | 473612.5575 | 1438081.8866 | 9655.2326 | 29317.2444 | 56.0847 | 5.6957 | 122.088 | 113140.6535 | 0 | 86744.5574 | 0 | 0 | 0 | 70814.3787 | 105572.84 | 274678.8736 | 187473.9753 | 838425.2786 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10342639.6015 | 31404493.8977 | 177.8279 | 0.021838 | 473612.5575 | 1438081.8866 | 9655.2326 | 29317.2444
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.17336 | 0.0085654 | 4 | 308647.6445 | 923381.0244 | 6292.1997 | 18824.3711 | 58.2658 | 5.8383 | 170.9656 | 144973.2656 | 0 | 115058.9196 | 0 | 0 | 0 | 85629.0793 | 134807.8931 | 350742.485 | 239388.9531 | 1070600.5956 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10574814.9186 | 31636669.2148 | 237.1374 | 0.034262 | 308647.6445 | 923381.0244 | 6292.1997 | 18824.3711
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4099 | 0.25475 | 0.012857 | 4 | 211296.1036 | 620839.0256 | 4307.5569 | 12656.6433 | 60.1334 | 5.9504 | 235.1018 | 184400.8429 | 0 | 151090.8506 | 0 | 0 | 0 | 104336.7553 | 171533.095 | 446293.927 | 304604.7756 | 1362260.2464 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 10866474.5693 | 31928328.8655 | 316.2278 | 0.051428 | 211296.1036 | 620839.0256 | 4307.5569 | 12656.6433
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1614 | 0.35832 | 0.018663 | 4 | 150001.198 | 432133.9052 | 3057.9773 | 8809.6342 | 61.5963 | 6.0322 | 51.6593 | 229545.5402 | 0 | 193491.2259 | 0 | 0 | 0 | 123808.8225 | 213269.7796 | 554884.2187 | 378719.881 | 1693719.4679 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 11197933.7909 | 32259788.087 | 421.6965 | 0.074652 | 150001.198 | 432133.9052 | 3057.9773 | 8809.6342
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.136 | 0.49381 | 0.026466 | 4 | 109529.5773 | 308478.4021 | 2232.9086 | 6288.7495 | 62.7854 | 6.0949 | 53.9589 | 283422.4774 | 0 | 245471.7084 | 0 | 0 | 0 | 146287.7784 | 263320.966 | 685107.139 | 467599.6999 | 2091209.7692 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 11595424.0921 | 32657278.3883 | 562.3413 | 0.10587 | 109529.5773 | 308478.4021 | 2232.9086 | 6288.7495
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.407 | 0.67142 | 0.036897 | 4 | 81821.498 | 224528.2392 | 1668.0419 | 4577.3119 | 63.7447 | 6.143 | 62.7187 | 348099.2224 | 0 | 309568.0151 | 0 | 0 | 0 | 172644.6897 | 323821.6516 | 842517.5126 | 575035.5143 | 2571686.6057 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 12075900.9286 | 33137755.2248 | 749.8942 | 0.14759 | 81821.498 | 224528.2392 | 1668.0419 | 4577.3119
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0271 | 0.89897 | 0.050716 | 4 | 62310.1711 | 166132.2522 | 1270.2771 | 3386.8307 | 64.4948 | 6.1787 | 53.5203 | 424080.115 | 0 | 386882.0878 | 0 | 0 | 0 | 201654.6566 | 394920.5752 | 1027502.3272 | 701291.4514 | 3136331.2132 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 12640545.5362 | 33702399.8324 | 1000 | 0.20286 | 62310.1711 | 166132.2522 | 1270.2771 | 3386.8307
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0929 | 1.1901 | 0.068932 | 4 | 48258.4169 | 124645.202 | 983.8131 | 2541.061 | 65.079 | 6.2049 | 59.5598 | 513544.6858 | 0 | 480297.2387 | 0 | 0 | 0 | 233666.8242 | 478728.412 | 1245553.1272 | 850115.6029 | 3801905.8907 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 13306120.2137 | 34367974.5098 | 1333.5214 | 0.27573 | 48258.4169 | 124645.202 | 983.8131 | 2541.061
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7265 | 1.5622 | 0.092831 | 4 | 37951.7308 | 94672.9655 | 773.6974 | 1930.0365 | 65.5297 | 6.2233 | 57.83 | 619029.019 | 0 | 593278.189 | 0 | 0 | 0 | 269039.4612 | 577725.201 | 1503122.4653 | 1025911.9686 | 4588106.3042 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 14092320.6271 | 35154174.9233 | 1778.2794 | 0.37132 | 37951.7308 | 94672.9655 | 773.6974 | 1930.0365
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0346 | 2.0309 | 0.1239 | 4 | 30276.5862 | 72773.0041 | 617.2292 | 1483.5761 | 65.8666 | 6.2343 | 58.2077 | 741755.7534 | 0 | 728083.1287 | 0 | 0 | 0 | 306350.9401 | 692714.0306 | 1802299.8125 | 1230106.6556 | 5501310.3209 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 15005524.6438 | 36067378.94 | 2371.3737 | 0.49561 | 30276.5862 | 72773.0041 | 617.2292 | 1483.5761
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.166 | 2.6178 | 0.16397 | 4 | 24488.2647 | 56600.0785 | 499.2264 | 1153.8692 | 66.1081 | 6.2383 | 57.6769 | 883937.6759 | 0 | 888248.9652 | 0 | 0 | 0 | 344986.3335 | 825697.4601 | 2148295.4174 | 1466255.7654 | 6557421.6175 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 16061635.9405 | 37123490.2367 | 3162.2777 | 0.65589 | 24488.2647 | 56600.0785 | 499.2264 | 1153.8692
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.2692 | 3.3446 | 0.21504 | 4 | 20076.7762 | 44562.1907 | 409.2922 | 908.4605 | 66.264 | 6.2344 | 55.18 | 1047032.756 | 0 | 1076767.0744 | 0 | 0 | 0 | 383395.2944 | 977806.0987 | 2544050.8932 | 1736367.0096 | 7765419.1263 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 17269633.4492 | 38331487.7454 | 4216.965 | 0.86018 | 20076.7762 | 44562.1907 | 409.2922 | 908.4605
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.4307 | 4.2249 | 0.27892 | 4 | 16686.2077 | 35564.3167 | 340.1709 | 725.0267 | 66.3371 | 6.221 | 58.6929 | 1230085.033 | 0 | 1294108.5403 | 0 | 0 | 0 | 417828.4085 | 1147388.5729 | 2985269.705 | 2037507.9148 | 9112188.1745 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 18616402.4974 | 39678256.7936 | 5623.4133 | 1.1157 | 16686.2077 | 35564.3167 | 340.1709 | 725.0267
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.6922 | 5.2662 | 0.35691 | 4 | 14064.3684 | 28817.2508 | 286.7212 | 587.4786 | 66.3261 | 6.1961 | 60.9253 | 1430807.796 | 0 | 1539355.5605 | 0 | 0 | 0 | 444050.9843 | 1331543.5929 | 3464403.2916 | 2364526.4329 | 10574687.6581 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 20078901.981 | 41140756.2772 | 7498.9421 | 1.4276 | 14064.3684 | 28817.2508 | 286.7212 | 587.4786
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9406 | 6.4539 | 0.4489 | 4 | 12030.1991 | 23759.9905 | 245.2519 | 484.3795 | 66.2259 | 6.1574 | 67.9871 | 1643053.4601 | 0 | 1806940.8651 | 0 | 0 | 0 | 455739.4004 | 1523236.153 | 3963148.0113 | 2704929.9523 | 12097047.8421 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 21601262.165 | 42663116.4612 | 10000 | 1.7956 | 12030.1991 | 23759.9905 | 245.2519 | 484.3795
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8151 | 7.7379 | 0.5522 | 4 | 10451.3626 | 19986.7469 | 213.0652 | 407.4569 | 66.0339 | 6.1043 | 62.7172 | 1855720.1453 | 0 | 2084547.0724 | 0 | 0 | 0 | 444540.7098 | 1710075.0917 | 4449264.604 | 3036714.5155 | 13580862.1386 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 23085076.4615 | 44146930.7577 | 13335.2143 | 2.2088 | 10451.3626 | 19986.7469 | 213.0652 | 407.4569
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.7233 | 9.0338 | 0.66124 | 4 | 9227.6672 | 17190.7317 | 188.1185 | 350.4563 | 65.7608 | 6.0391 | 78.7029 | 2054744.9386 | 0 | 2354454.7798 | 0 | 0 | 0 | 402302.5048 | 1876485.867 | 4882231.3059 | 3332223.1861 | 14902442.5822 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 24406656.9051 | 45468511.2013 | 17782.7941 | 2.6449 | 9227.6672 | 17190.7317 | 188.1185 | 350.4563
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.0371 | 10.2504 | 0.76887 | 4 | 8278.8658 | 15127.1728 | 168.7759 | 308.3879 | 65.4346 | 5.9672 | 72.7523 | 2228371.9649 | 0 | 2599689.4275 | 0 | 0 | 0 | 324018.9804 | 2009311.3454 | 5227815.9542 | 3568091.8096 | 15957299.482 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 25461513.8049 | 46523368.1011 | 23713.7371 | 3.0755 | 8278.8658 | 15127.1728 | 168.7759 | 308.3879
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.3176 | 11.1819 | 0.86211 | 4 | 7538.0929 | 13645.7676 | 153.6742 | 278.1874 | 65.1438 | 5.9063 | 62.0149 | 2352144.1496 | 0 | 2781083.3609 | 0 | 0 | 0 | 190950.3194 | 2076429.3536 | 5402443.244 | 3687278.5231 | 16490328.9506 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 25994543.2735 | 47056397.5697 | 31622.7766 | 3.4484 | 7538.0929 | 13645.7676 | 153.6742 | 278.1874
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.3138 | 12.2093 | 0.95598 | 4 | 6909.8712 | 12417.7924 | 140.8671 | 253.1535 | 64.7735 | 5.8307 | 71.1859 | 2482619.6402 | 0 | 2979828.0638 | 0 | 0 | 0 | 0 | 2130354.6046 | 5542745.6852 | 3783037.8222 | 16918585.816 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 26422800.1389 | 47484654.4351 | 42169.6503 | 3.8239 | 6909.8712 | 12417.7924 | 140.8671 | 253.1535
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2011 | 14.6047 | 1.1032 | 4 | 6514.884 | 11287.8994 | 132.8147 | 230.1191 | 63.697 | 5.6201 | 62.5016 | 2766683.775 | 0 | 3446553.6869 | 0 | 0 | 0 | 0 | 2423162.6101 | 6304572.0526 | 4302999.9719 | 19243972.0966 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 28748186.4195 | 49810040.7157 | 56234.1325 | 4.4127 | 6514.884 | 11287.8994 | 132.8147 | 230.1191
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5159 | 16.8955 | 1.2216 | 4 | 6307.4084 | 10617.8424 | 128.5851 | 216.4591 | 62.4051 | 5.3774 | 55.0711 | 2999227.9596 | 0 | 3882789.8472 | 0 | 0 | 0 | 0 | 2683986.9446 | 6983183.4685 | 4766166.2073 | 21315354.4273 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 30819568.7502 | 51881423.0464 | 74989.4209 | 4.8862 | 6307.4084 | 10617.8424 | 128.5851 | 216.4591
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3543 | 18.9579 | 1.3049 | 4 | 6237.4271 | 10272.4734 | 127.1584 | 209.4183 | 61.0076 | 5.1223 | 65.4468 | 3173585.6283 | 0 | 4269613.1676 | 0 | 0 | 0 | 0 | 2902847.5304 | 7552613.8183 | 5154814.1217 | 23053474.2663 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32557688.5892 | 53619542.8854 | 100000 | 5.2197 | 6237.4271 | 10272.4734 | 127.1584 | 209.4183
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9593 | 19.3167 | 1.3166 | 4 | 6237.1627 | 10236.5421 | 127.153 | 208.6858 | 60.7327 | 5.0732 | 79.6176 | 3199953.2027 | 0 | 4336541.3906 | 0 | 0 | 0 | 0 | 2939232.8914 | 7647281.0639 | 5219426.462 | 23342435.0107 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32846649.3336 | 53908503.6298 | 133352.1432 | 5.2663 | 6237.1627 | 10236.5421 | 127.153 | 208.6858
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9204 | 19.3098 | 1.3162 | 4 | 6237.8217 | 10238.368 | 127.1664 | 208.723 | 60.7315 | 5.0735 | 75.5015 | 3199245.3329 | 0 | 4335276.2548 | 0 | 0 | 0 | 0 | 2938463.4192 | 7645279.055 | 5218060.0498 | 23336324.1117 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32840538.4346 | 53902392.7308 | 177827.941 | 5.2647 | 6237.8217 | 10238.368 | 127.1664 | 208.723
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9003 | 19.3059 | 1.3159 | 4 | 6238.3221 | 10239.627 | 127.1766 | 208.7486 | 60.7297 | 5.0736 | 89.2966 | 3198803.1447 | 0 | 4334558.3824 | 0 | 0 | 0 | 0 | 2938010.9956 | 7644101.9416 | 5217256.6457 | 23332731.11 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32836945.4329 | 53898799.7291 | 237137.3706 | 5.2637 | 6238.3221 | 10239.627 | 127.1766 | 208.7486
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8808 | 19.3023 | 1.3157 | 4 | 6238.7009 | 10240.6373 | 127.1844 | 208.7692 | 60.7287 | 5.0737 | 87.6114 | 3198425.8167 | 0 | 4333906.3449 | 0 | 0 | 0 | 0 | 2937609.543 | 7643057.4444 | 5216543.7549 | 23329542.904 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32833757.2269 | 53895611.5231 | 316227.766 | 5.2629 | 6238.7009 | 10240.6373 | 127.1844 | 208.7692
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8614 | 19.2989 | 1.3156 | 4 | 6238.987 | 10241.4647 | 127.1902 | 208.7861 | 60.7285 | 5.0739 | 86.747 | 3198092.8801 | 0 | 4333291.6383 | 0 | 0 | 0 | 0 | 2937239.9622 | 7642095.8708 | 5215887.4612 | 23326607.8125 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32830822.1355 | 53892676.4316 | 421696.5034 | 5.2622 | 6238.987 | 10241.4647 | 127.1902 | 208.7861
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8567 | 19.2978 | 1.3155 | 4 | 6239.2027 | 10241.953 | 127.1946 | 208.7961 | 60.7273 | 5.0738 | 86.5468 | 3197943.0653 | 0 | 4333086.119 | 0 | 0 | 0 | 0 | 2937101.3819 | 7641735.3133 | 5215641.3733 | 23325507.2527 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32829721.5757 | 53891575.8719 | 562341.3252 | 5.2618 | 6239.2027 | 10241.953 | 127.1946 | 208.7961
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8419 | 19.2954 | 1.3153 | 4 | 6239.3651 | 10242.4738 | 127.1979 | 208.8067 | 60.7276 | 5.074 | 85.5873 | 3197716.0142 | 0 | 4332640.1706 | 0 | 0 | 0 | 0 | 2936838.9121 | 7641052.4208 | 5215175.2851 | 23323422.8029 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32827637.1259 | 53889491.4221 | 749894.2093 | 5.2614 | 6239.3651 | 10242.4738 | 127.1979 | 208.8067
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8445 | 19.2955 | 1.3153 | 4 | 6239.4873 | 10242.6798 | 127.2004 | 208.8109 | 60.7263 | 5.0739 | 74.8649 | 3197683.858 | 0 | 4332658.0788 | 0 | 0 | 0 | 0 | 2936833.3554 | 7641037.9633 | 5215165.4176 | 23323378.673 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32827592.9959 | 53889447.2921 | 1000000 | 5.2613 | 6239.4873 | 10242.6798 | 127.2004 | 208.8109
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8445 | 19.2952 | 1.3153 | 4 | 6239.5792 | 10242.861 | 127.2023 | 208.8146 | 60.7256 | 5.0738 | 73.6113 | 3197639.9649 | 0 | 4332621.2784 | 0 | 0 | 0 | 0 | 2936801.8849 | 7640956.0835 | 5215109.533 | 23323128.7447 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32827343.0676 | 53889197.3638 | 1333521.4322 | 5.2611 | 6239.5792 | 10242.861 | 127.2023 | 208.8146
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8251 | 19.2924 | 1.3152 | 4 | 6239.6482 | 10243.26 | 127.2037 | 208.8227 | 60.7271 | 5.0741 | 72.049 | 3197410.9209 | 0 | 4332093.8522 | 0 | 0 | 0 | 0 | 2936506.8615 | 7640188.4933 | 5214585.6368 | 23320785.7647 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825000.0876 | 53886854.3838 | 1778279.41 | 5.2607 | 6239.6482 | 10243.26 | 127.2037 | 208.8227
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2929 | 1.3152 | 4 | 6239.7 | 10243.2997 | 127.2047 | 208.8235 | 60.7262 | 5.074 | 81.5774 | 3197432.8597 | 0 | 4332192.1024 | 0 | 0 | 0 | 0 | 2936553.7352 | 7640310.449 | 5214668.8741 | 23321158.0203 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825372.3432 | 53887226.6394 | 2371373.7057 | 5.2607 | 6239.7 | 10243.2997 | 127.2047 | 208.8235
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2928 | 1.3152 | 4 | 6239.7388 | 10243.3764 | 127.2055 | 208.8251 | 60.7259 | 5.074 | 81.8198 | 3197414.2807 | 0 | 4332176.5296 | 0 | 0 | 0 | 0 | 2936540.416 | 7640275.7953 | 5214645.2222 | 23321052.2439 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825266.5668 | 53887120.863 | 3162277.6602 | 5.2607 | 6239.7388 | 10243.3764 | 127.2055 | 208.8251
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2928 | 1.3152 | 4 | 6239.768 | 10243.434 | 127.2061 | 208.8263 | 60.7257 | 5.074 | 81.1834 | 3197400.338 | 0 | 4332164.8434 | 0 | 0 | 0 | 0 | 2936530.4207 | 7640249.7895 | 5214627.4728 | 23320972.8643 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825187.1873 | 53887041.4835 | 4216965.0343 | 5.2606 | 6239.768 | 10243.434 | 127.2061 | 208.8263
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2927 | 1.3152 | 4 | 6239.7899 | 10243.4772 | 127.2066 | 208.8271 | 60.7255 | 5.074 | 81.6946 | 3197389.8764 | 0 | 4332156.0753 | 0 | 0 | 0 | 0 | 2936522.9212 | 7640230.2772 | 5214614.1552 | 23320913.3053 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825127.6282 | 53886981.9244 | 5623413.2519 | 5.2606 | 6239.7899 | 10243.4772 | 127.2066 | 208.8271
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2927 | 1.3151 | 4 | 6239.8064 | 10243.5096 | 127.2069 | 208.8278 | 60.7254 | 5.074 | 82.2161 | 3197382.0281 | 0 | 4332149.4975 | 0 | 0 | 0 | 0 | 2936517.295 | 7640215.639 | 5214604.1643 | 23320868.6238 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825082.9467 | 53886937.2429 | 7498942.0933 | 5.2606 | 6239.8064 | 10243.5096 | 127.2069 | 208.8278
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8297 | 19.2926 | 1.3151 | 4 | 6239.8187 | 10243.534 | 127.2071 | 208.8283 | 60.7253 | 5.0739 | 82.2728 | 3197376.1407 | 0 | 4332144.5633 | 0 | 0 | 0 | 0 | 2936513.0746 | 7640204.6584 | 5214596.6699 | 23320835.107 | 961560.8286 | 8542653.4943 | 8542653.4943 | 8315156.4279 | 4204044.374 | 0 | 32825049.4299 | 53886903.7261 | 10000000 | 5.2606 | 6239.8187 | 10243.534 | 127.2071 | 208.8283
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.76734 | 0.03667 | 0.0018527 | 4 | 1406232.8059 | 4353178.8988 | 28667.9578 | 88745.44 | 51.7551 | 5.6428 | 39.2261 | 68066.9472 | 0 | 45645.9007 | 0 | 0 | 0 | 50524.6733 | 64052.6333 | 166651.8128 | 113743.2866 | 508685.2538 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10421239.0796 | 32260318.3989 | 100 | 0.0074107 | 1406232.8059 | 4353178.8988 | 28667.9578 | 88745.44
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.068 | 0.072758 | 0.0035449 | 4 | 748386.8472 | 2288541.1675 | 15256.8781 | 46655.0072 | 55.3867 | 5.926 | 87.7781 | 93923.2082 | 0 | 66871.0976 | 0 | 0 | 0 | 65025.6099 | 88069.7671 | 229139.4685 | 156392.3956 | 699421.5469 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10611975.3727 | 32451054.6919 | 133.3521 | 0.01418 | 748386.8472 | 2288541.1675 | 15256.8781 | 46655.0072
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.12059 | 0.0060233 | 4 | 449355.8932 | 1355792.5834 | 9160.7277 | 27639.6657 | 58.2516 | 6.1267 | 127.7355 | 123392.4147 | 0 | 91649.0935 | 0 | 0 | 0 | 80034.9111 | 115079.8035 | 299414.0427 | 204356.2365 | 913926.502 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 10826480.3278 | 32665559.6471 | 177.8279 | 0.024093 | 449355.8932 | 1355792.5834 | 9160.7277 | 27639.6657
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.18584 | 0.0095255 | 4 | 291014.238 | 864188.7643 | 5932.7189 | 17617.6569 | 60.6773 | 6.281 | 180.3267 | 159160.4517 | 0 | 122500.1063 | 0 | 0 | 0 | 97921.632 | 148037.0541 | 385162.0482 | 262881.0122 | 1175662.3046 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11088216.1304 | 32927295.4496 | 237.1374 | 0.038102 | 291014.238 | 864188.7643 | 5932.7189 | 17617.6569
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.27169 | 0.014353 | 4 | 198499.8727 | 578896.4756 | 4046.6884 | 11801.5877 | 62.6537 | 6.3965 | 247.0737 | 201270.7438 | 0 | 159800.4157 | 0 | 0 | 0 | 117930.6813 | 186810.7179 | 486043.1679 | 331734.4493 | 1483590.1759 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11396144.0017 | 33235223.3209 | 316.2278 | 0.057411 | 198499.8727 | 578896.4756 | 4046.6884 | 11801.5877
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3466 | 0.38401 | 0.020907 | 4 | 140636.4953 | 401785.7604 | 2867.0652 | 8190.9462 | 64.26 | 6.484 | 47.117 | 251088.2187 | 0 | 205126.8855 | 0 | 0 | 0 | 140580.4871 | 232750.2806 | 605568.4865 | 413312.9352 | 1848427.2937 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 11760981.1194 | 33600060.4387 | 421.6965 | 0.083627 | 140636.4953 | 401785.7604 | 2867.0652 | 8190.9462
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3944 | 0.53231 | 0.029735 | 4 | 102600.1544 | 286214.5482 | 2091.6429 | 5834.8707 | 65.5716 | 6.5513 | 44.594 | 311049.0305 | 0 | 261172.4774 | 0 | 0 | 0 | 167368.9559 | 288440.2809 | 750462.4436 | 512206.0382 | 2290699.2263 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 12203253.0521 | 34042332.3714 | 562.3413 | 0.11894 | 102600.1544 | 286214.5482 | 2091.6429 | 5834.8707
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7313 | 0.72308 | 0.041502 | 4 | 76639.9931 | 208194.4532 | 1562.4099 | 4244.3255 | 66.6061 | 6.6016 | 63.2726 | 381479.5867 | 0 | 328785.4017 | 0 | 0 | 0 | 197084.115 | 353866.1503 | 920687.1353 | 628387.888 | 2810290.2771 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 12722844.1028 | 34561923.4221 | 749.8942 | 0.16601 | 76639.9931 | 208194.4532 | 1562.4099 | 4244.3255
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4292 | 0.96672 | 0.057072 | 4 | 58396.0715 | 154060.4066 | 1190.4829 | 3140.7298 | 67.4159 | 6.6391 | 51.9118 | 463990.4782 | 0 | 410084.6726 | 0 | 0 | 0 | 229678.4838 | 430463.9175 | 1119978.8131 | 764408.5532 | 3418604.9184 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 13331158.7442 | 35170238.0634 | 1000 | 0.22829 | 58396.0715 | 154060.4066 | 1190.4829 | 3140.7298
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6265 | 1.2828 | 0.077653 | 4 | 45273.1141 | 115582.881 | 922.9537 | 2356.3134 | 68.0566 | 6.6669 | 58.8991 | 562616.4761 | 0 | 509790.0354 | 0 | 0 | 0 | 267436.2606 | 522538.6811 | 1359538.4609 | 927912.9353 | 4149832.8495 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 14062386.6753 | 35901465.9946 | 1333.5214 | 0.31061 | 45273.1141 | 115582.881 | 922.9537 | 2356.3134
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3844 | 1.681 | 0.10454 | 4 | 35653.7487 | 87880.1345 | 726.8499 | 1791.5554 | 68.5437 | 6.6859 | 60.8932 | 677130.7152 | 0 | 628526.9282 | 0 | 0 | 0 | 307539.8587 | 629147.0258 | 1636911.5054 | 1117225.7376 | 4996481.7708 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 14909035.5966 | 36748114.9159 | 1778.2794 | 0.41816 | 35653.7487 | 87880.1345 | 726.8499 | 1791.5554
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8823 | 2.1871 | 0.13956 | 4 | 28491.7045 | 67612.0648 | 580.8419 | 1378.3634 | 68.9119 | 6.6972 | 57.0127 | 811703.506 | 0 | 771609.0488 | 0 | 0 | 0 | 351640.6883 | 754631.7648 | 1963397.0557 | 1340058.8343 | 5993040.8979 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 15905594.7237 | 37744674.043 | 2371.3737 | 0.55825 | 28491.7045 | 67612.0648 | 580.8419 | 1378.3634
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2332 | 2.8186 | 0.18463 | 4 | 23089.6305 | 52660.449 | 470.7133 | 1073.5545 | 69.1745 | 6.7006 | 56.3516 | 966985.5185 | 0 | 940934.1574 | 0 | 0 | 0 | 397329.8682 | 899047.3222 | 2339136.7124 | 1596508.8707 | 7139942.4494 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 17052496.2752 | 38891575.5944 | 3162.2777 | 0.73853 | 23089.6305 | 52660.449 | 470.7133 | 1073.5545
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.5728 | 3.5958 | 0.24187 | 4 | 18971.2753 | 41544.2081 | 386.7551 | 846.9349 | 69.343 | 6.6953 | 59.0736 | 1144007.2433 | 0 | 1139002.2598 | 0 | 0 | 0 | 442617.8268 | 1062994.6586 | 2765694.0516 | 1887643.0196 | 8441959.0597 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 18354512.8854 | 40193592.2047 | 4216.965 | 0.96749 | 18971.2753 | 41544.2081 | 386.7551 | 846.9349
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.036 | 4.5395 | 0.3134 | 4 | 15805.0459 | 33226.4141 | 322.2072 | 677.3654 | 69.422 | 6.6795 | 60.4145 | 1343239.7263 | 0 | 1368010.3807 | 0 | 0 | 0 | 485238.5688 | 1246630.5835 | 3243477.0593 | 2213739.7397 | 9900336.0582 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 19812889.884 | 41651969.2033 | 5623.4133 | 1.2536 | 15805.0459 | 33226.4141 | 322.2072 | 677.3654
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.6265 | 5.6521 | 0.4004 | 4 | 13356.4606 | 26992.1168 | 272.2895 | 550.2708 | 69.4088 | 6.6506 | 64.0802 | 1560943.0067 | 0 | 1625596.9414 | 0 | 0 | 0 | 519763.3874 | 1445458.3009 | 3760785.9946 | 2566813.7177 | 11479361.3487 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 21391915.1745 | 43230994.4938 | 7498.9421 | 1.6016 | 13356.4606 | 26992.1168 | 272.2895 | 550.2708
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.201 | 6.9144 | 0.50246 | 4 | 11457.4811 | 22323.5125 | 233.5763 | 455.095 | 69.2985 | 6.6066 | 67.5645 | 1789868.6676 | 0 | 1905208.8487 | 0 | 0 | 0 | 539399.797 | 1651446.1522 | 4296724.1299 | 2932602.5075 | 13115250.1031 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 23027803.9288 | 44866883.2481 | 10000 | 2.0098 | 11457.4811 | 22323.5125 | 233.5763 | 455.095
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.3554 | 8.269 | 0.61622 | 4 | 9985.2965 | 18845.3781 | 203.5638 | 384.1885 | 69.0893 | 6.5469 | 83.9347 | 2017480.7176 | 0 | 2193207.1762 | 0 | 0 | 0 | 535468.5704 | 1851001.0211 | 4815924.9643 | 3286967.7455 | 14700050.1951 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 24612604.0209 | 46451683.3402 | 13335.2143 | 2.4649 | 9985.2965 | 18845.3781 | 203.5638 | 384.1885
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.564 | 9.6384 | 0.73585 | 4 | 8846.7798 | 16266.4388 | 180.3536 | 331.6134 | 68.7915 | 6.4736 | 78.1383 | 2230877.7197 | 0 | 2473923.0359 | 0 | 0 | 0 | 502110.1575 | 2030695.2561 | 5283452.5035 | 3606064.8977 | 16127123.5703 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 26039677.3961 | 47878756.7153 | 17782.7941 | 2.9434 | 8846.7798 | 16266.4388 | 180.3536 | 331.6134
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.1823 | 10.9268 | 0.85354 | 4 | 7968.1445 | 14364.7949 | 162.4414 | 292.8458 | 68.4355 | 6.393 | 93.022 | 2417453.9463 | 0 | 2729711.6853 | 0 | 0 | 0 | 435790.6739 | 2177352.9591 | 5665025.7631 | 3866496.488 | 17291831.5156 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 27204385.3414 | 49043464.6607 | 23713.7371 | 3.4141 | 7968.1445 | 14364.7949 | 162.4414 | 292.8458
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.6218 | 12.0462 | 0.9615 | 4 | 7288.6873 | 12967.0624 | 148.5898 | 264.3511 | 68.0682 | 6.3138 | 80.1217 | 2568672.3734 | 0 | 2945825.3567 | 0 | 0 | 0 | 335782.1932 | 2281609.1701 | 5936279.0383 | 4051632.422 | 18119800.5537 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 28032354.3795 | 49871433.6988 | 31622.7766 | 3.846 | 7288.6873 | 12967.0624 | 148.5898 | 264.3511
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.5741 | 12.8057 | 1.0472 | 4 | 6757.3075 | 11970.9212 | 137.7569 | 244.0434 | 67.7934 | 6.2567 | 72.9118 | 2664395.8759 | 0 | 3087394.6562 | 0 | 0 | 0 | 186644.0162 | 2315989.4738 | 6025729.5362 | 4112684.2248 | 18392837.7831 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 28305391.6089 | 50144470.9282 | 42169.6503 | 4.1889 | 6757.3075 | 11970.9212 | 137.7569 | 244.0434
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.913 | 13.7566 | 1.1365 | 4 | 6300.7322 | 11104.6939 | 128.4489 | 226.3842 | 67.4065 | 6.1774 | 62.505 | 2781205.6508 | 0 | 3266387.0406 | 0 | 0 | 0 | 0 | 2358561.1496 | 6136492.304 | 4188282.0898 | 18730928.2348 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 28643482.0605 | 50482561.3798 | 56234.1325 | 4.5461 | 6300.7322 | 11104.6939 | 128.4489 | 226.3842
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3506 | 15.9917 | 1.2769 | 4 | 6023.0031 | 10298.7091 | 122.7871 | 209.9531 | 66.3117 | 5.9598 | 64.6408 | 3039505.6278 | 0 | 3692657.8255 | 0 | 0 | 0 | 0 | 2625543.7468 | 6831126.256 | 4662384.0353 | 20851217.4914 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 30763771.3172 | 52602850.6365 | 74989.4209 | 5.1077 | 6023.0031 | 10298.7091 | 122.7871 | 209.9531
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3607 | 18.0008 | 1.3845 | 4 | 5878.5285 | 9822.1069 | 119.8418 | 200.2369 | 65.1255 | 5.7324 | 59.2794 | 3241274.6483 | 0 | 4069090.4078 | 0 | 0 | 0 | 0 | 2851042.3719 | 7417827.4225 | 5062819.637 | 22642054.4875 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 32554608.3133 | 54393687.6326 | 100000 | 5.5379 | 5878.5285 | 9822.1069 | 119.8418 | 200.2369
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5534 | 19.7349 | 1.46 | 4 | 5823.9748 | 9563.609 | 118.7296 | 194.9671 | 63.9351 | 5.5093 | 59.3313 | 3390393.3687 | 0 | 4390325.7621 | 0 | 0 | 0 | 0 | 3034480.461 | 7895095.7021 | 5388565.0447 | 24098860.3386 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34011414.1644 | 55850493.4836 | 133352.1432 | 5.8399 | 5823.9748 | 9563.609 | 118.7296 | 194.9671
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3445 | 20.4119 | 1.4843 | 4 | 5820.2236 | 9498.4636 | 118.6531 | 193.639 | 63.4218 | 5.4146 | 72.3056 | 3441718.5334 | 0 | 4515097.9301 | 0 | 0 | 0 | 0 | 3103158.4208 | 8073781.6655 | 5510521.8864 | 24644278.4362 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34556832.262 | 56395911.5813 | 177827.941 | 5.9374 | 5820.2236 | 9498.4636 | 118.6531 | 193.639
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.323 | 20.4077 | 1.4841 | 4 | 5820.6754 | 9499.6119 | 118.6623 | 193.6624 | 63.4199 | 5.4147 | 69.8136 | 3441240.3295 | 0 | 4514330.069 | 0 | 0 | 0 | 0 | 3102672.4554 | 8072517.2834 | 5509658.9195 | 24640419.0569 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34552972.8826 | 56392052.2019 | 237137.3706 | 5.9362 | 5820.6754 | 9499.6119 | 118.6623 | 193.6624
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3003 | 20.4035 | 1.4838 | 4 | 5821.0174 | 9500.5583 | 118.6693 | 193.6817 | 63.4192 | 5.4149 | 75.4593 | 3440811.5519 | 0 | 4513581.4082 | 0 | 0 | 0 | 0 | 3102213.2545 | 8071322.5367 | 5508843.4804 | 24636772.2316 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34549326.0574 | 56388405.3767 | 316227.766 | 5.9353 | 5821.0174 | 9500.5583 | 118.6693 | 193.6817
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2855 | 20.4007 | 1.4836 | 4 | 5821.2756 | 9501.2451 | 118.6746 | 193.6957 | 63.4185 | 5.415 | 82.7263 | 3440511.9783 | 0 | 4513076.6579 | 0 | 0 | 0 | 0 | 3101899.5681 | 8070506.3892 | 5508286.4429 | 24634281.0365 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34546834.8623 | 56385914.1816 | 421696.5034 | 5.9346 | 5821.2756 | 9501.2451 | 118.6746 | 193.6957
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.266 | 20.3975 | 1.4835 | 4 | 5821.4703 | 9501.8622 | 118.6785 | 193.7083 | 63.4188 | 5.4153 | 82.7824 | 3440200.2946 | 0 | 4512481.1631 | 0 | 0 | 0 | 0 | 3101545.7685 | 8069585.8752 | 5507658.1732 | 24631471.2746 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34544025.1004 | 56383104.4196 | 562341.3252 | 5.9339 | 5821.4703 | 9501.8622 | 118.6785 | 193.7083
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.264 | 20.3968 | 1.4834 | 4 | 5821.6168 | 9502.1755 | 118.6815 | 193.7147 | 63.4177 | 5.4152 | 81.7671 | 3440096.5144 | 0 | 4512360.5361 | 0 | 0 | 0 | 0 | 3101458.2497 | 8069358.1692 | 5507502.7592 | 24630776.2287 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34543330.0544 | 56382409.3737 | 749894.2093 | 5.9336 | 5821.6168 | 9502.1755 | 118.6815 | 193.7147
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.264 | 20.3965 | 1.4834 | 4 | 5821.7271 | 9502.3928 | 118.6838 | 193.7191 | 63.4167 | 5.4151 | 82.4339 | 3440034.2832 | 0 | 4512309.4453 | 0 | 0 | 0 | 0 | 3101414.0541 | 8069243.1813 | 5507424.2776 | 24630425.2414 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34542979.0672 | 56382058.3865 | 1000000 | 5.9335 | 5821.7271 | 9502.3928 | 118.6838 | 193.7191
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2466 | 20.3938 | 1.4832 | 4 | 5821.8099 | 9502.7651 | 118.6855 | 193.7267 | 63.4178 | 5.4154 | 81.8682 | 3439806.8256 | 0 | 4511818.5884 | 0 | 0 | 0 | 0 | 3101133.9115 | 8068514.3076 | 5506926.8063 | 24628200.4395 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34540754.2653 | 56379833.5845 | 1333521.4322 | 5.933 | 5821.8099 | 9502.7651 | 118.6855 | 193.7267
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2466 | 20.3936 | 1.4832 | 4 | 5821.8721 | 9502.8878 | 118.6867 | 193.7292 | 63.4172 | 5.4154 | 81.2019 | 3439771.7041 | 0 | 4511789.7588 | 0 | 0 | 0 | 0 | 3101108.9705 | 8068449.4164 | 5506882.5167 | 24628002.3664 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34540556.1922 | 56379635.5115 | 1778279.41 | 5.9329 | 5821.8721 | 9502.8878 | 118.6867 | 193.7292
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2466 | 20.3935 | 1.4832 | 4 | 5821.9189 | 9502.9799 | 118.6877 | 193.7311 | 63.4168 | 5.4153 | 81.5467 | 3439745.3323 | 0 | 4511768.1124 | 0 | 0 | 0 | 0 | 3101090.2434 | 8068400.6923 | 5506849.2616 | 24627853.642 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34540407.4678 | 56379486.7871 | 2371373.7057 | 5.9328 | 5821.9189 | 9502.9799 | 118.6877 | 193.7311
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2466 | 20.3934 | 1.4832 | 4 | 5821.9539 | 9503.0491 | 118.6884 | 193.7325 | 63.4165 | 5.4153 | 80.9411 | 3439725.5369 | 0 | 4511751.8646 | 0 | 0 | 0 | 0 | 3101076.1866 | 8068364.1193 | 5506824.2997 | 24627742.007 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34540295.8328 | 56379375.1521 | 3162277.6602 | 5.9328 | 5821.9539 | 9503.0491 | 118.6884 | 193.7325
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.242 | 20.3927 | 1.4832 | 4 | 5821.9803 | 9503.1565 | 118.6889 | 193.7347 | 63.4167 | 5.4154 | 81.4236 | 3439662.6541 | 0 | 4511619.4064 | 0 | 0 | 0 | 0 | 3101000.0036 | 8068165.9068 | 5506689.0156 | 24627136.9865 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34539690.8123 | 56378770.1316 | 4216965.0343 | 5.9326 | 5821.9803 | 9503.1565 | 118.6889 | 193.7347
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.242 | 20.3926 | 1.4832 | 4 | 5822 | 9503.1954 | 118.6893 | 193.7355 | 63.4165 | 5.4154 | 81.1109 | 3439651.5093 | 0 | 4511610.2594 | 0 | 0 | 0 | 0 | 3100992.0898 | 8068145.3167 | 5506674.9625 | 24627074.1378 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34539627.9636 | 56378707.2828 | 5623413.2519 | 5.9326 | 5822 | 9503.1954 | 118.6893 | 193.7355
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.242 | 20.3926 | 1.4831 | 4 | 5822.0148 | 9503.2246 | 118.6896 | 193.7361 | 63.4164 | 5.4154 | 80.6158 | 3439643.1484 | 0 | 4511603.3974 | 0 | 0 | 0 | 0 | 3100986.1529 | 8068129.8701 | 5506664.4198 | 24627026.9887 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34539580.8145 | 56378660.1338 | 7498942.0933 | 5.9326 | 5822.0148 | 9503.2246 | 118.6896 | 193.7361
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.242 | 20.3925 | 1.4831 | 4 | 5822.0259 | 9503.2466 | 118.6899 | 193.7365 | 63.4163 | 5.4154 | 81.3532 | 3439636.8767 | 0 | 4511598.2502 | 0 | 0 | 0 | 0 | 3100981.6995 | 8068118.2832 | 5506656.5116 | 24626991.6212 | 961560.8286 | 8950992.9972 | 8950992.9972 | 8547679.308 | 4340407.0141 | 0 | 34539545.447 | 56378624.7662 | 10000000 | 5.9326 | 5822.0259 | 9503.2466 | 118.6899 | 193.7365
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81087 | 0.038169 | 0.0019805 | 4 | 1373500.8128 | 4230154.8719 | 28000.6719 | 86237.4288 | 53.4374 | 6.0536 | 44.2138 | 74002.4983 | 0 | 48153.2289 | 0 | 0 | 0 | 56698.7116 | 69753.2311 | 181483.599 | 123866.2855 | 553957.5544 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 10880710.9739 | 33510786.5298 | 100 | 0.0079219 | 1373500.8128 | 4230154.8719 | 28000.6719 | 86237.4288
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.07641 | 0.0038646 | 4 | 717153.8997 | 2181092.9828 | 14620.1523 | 44464.5306 | 57.3249 | 6.3495 | 94.1344 | 101960.0345 | 0 | 70478.7651 | 0 | 0 | 0 | 72700.6535 | 95604.3867 | 248743.0031 | 169772.2108 | 759259.0538 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11086012.4733 | 33716088.0292 | 133.3521 | 0.015458 | 717153.8997 | 2181092.9828 | 14620.1523 | 44464.5306
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.12744 | 0.0066359 | 4 | 426395.1917 | 1278957.8423 | 8692.6427 | 26073.2855 | 60.4145 | 6.5609 | 137.6092 | 133978.8934 | 0 | 96649.4031 | 0 | 0 | 0 | 89431.6377 | 124823.3743 | 324764.8152 | 221658.6596 | 991306.7834 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11318060.2029 | 33948135.7588 | 177.8279 | 0.026544 | 426395.1917 | 1278957.8423 | 8692.6427 | 26073.2855
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.19876 | 0.01057 | 4 | 274602.8517 | 809840.4135 | 5598.1506 | 16509.6922 | 63.0918 | 6.7269 | 193.8053 | 173853.4048 | 0 | 130075.8178 | 0 | 0 | 0 | 110494.0248 | 161625.0665 | 420515.2691 | 287010.3119 | 1283573.895 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11610327.3144 | 34240402.8703 | 237.1374 | 0.04228 | 274602.8517 | 809840.4135 | 5598.1506 | 16509.6922
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7035 | 0.29183 | 0.015998 | 4 | 186707.7657 | 540336.5603 | 3806.2903 | 11015.4916 | 65.2341 | 6.8488 | 33.2813 | 220150.1033 | 0 | 169930.5553 | 0 | 0 | 0 | 133415.157 | 204163.3681 | 531191.204 | 362548.9116 | 1621399.2993 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 11948152.7187 | 34578228.2746 | 316.2278 | 0.063994 | 186707.7657 | 540336.5603 | 3806.2903 | 11015.4916
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.41308 | 0.023371 | 4 | 132055.888 | 374127.434 | 2692.1379 | 7627.0938 | 66.9643 | 6.9405 | 44.8165 | 274596.1082 | 0 | 218062.9392 | 0 | 0 | 0 | 159047.542 | 254165.5698 | 661286.6762 | 451341.7446 | 2018500.58 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 12345253.9995 | 34975329.5554 | 421.6965 | 0.093485 | 132055.888 | 374127.434 | 2692.1379 | 7627.0938
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6501 | 0.57192 | 0.033292 | 4 | 96275.7165 | 266210.0296 | 1962.7107 | 5427.0515 | 68.3682 | 7.0106 | 52.0375 | 339551.4379 | 0 | 277032.3729 | 0 | 0 | 0 | 188723.2424 | 314069.7507 | 817145.0669 | 557718.2988 | 2494240.1695 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 12820993.589 | 35451069.1449 | 562.3413 | 0.13317 | 96275.7165 | 266210.0296 | 1962.7107 | 5427.0515
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0527 | 0.77632 | 0.046512 | 4 | 71920.3543 | 193556.3954 | 1466.1937 | 3945.9089 | 69.4804 | 7.0633 | 61.819 | 415936.7556 | 0 | 348227.1287 | 0 | 0 | 0 | 221821.0155 | 384534.1109 | 1000478.8778 | 682847.3919 | 3053845.2805 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 13380598.7 | 36010674.2559 | 749.8942 | 0.18605 | 71920.3543 | 193556.3954 | 1466.1937 | 3945.9089
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8554 | 1.0403 | 0.06404 | 4 | 54833.7962 | 143177.564 | 1117.8611 | 2918.8683 | 70.3623 | 7.1029 | 63.8003 | 506524.8912 | 0 | 434874.0823 | 0 | 0 | 0 | 259481.731 | 468343.4748 | 1218533.6509 | 831674.2551 | 3719432.0854 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 14046185.5049 | 36676261.0608 | 1000 | 0.25616 | 54833.7962 | 143177.564 | 1117.8611 | 2918.8683
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1601 | 1.379 | 0.087143 | 4 | 42555.9211 | 107478.0811 | 867.56 | 2191.0861 | 71.052 | 7.1318 | 59.2099 | 613517.4295 | 0 | 539860.8804 | 0 | 0 | 0 | 301803.7064 | 567520.9863 | 1476573.1918 | 1007791.544 | 4507067.7383 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 14833821.1578 | 37463896.7137 | 1333.5214 | 0.34857 | 42555.9211 | 107478.0811 | 867.56 | 2191.0861
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0714 | 1.8083 | 0.11735 | 4 | 33560.2966 | 81769.075 | 684.172 | 1666.9732 | 71.5803 | 7.1516 | 41.3252 | 738579.3947 | 0 | 665710.0568 | 0 | 0 | 0 | 347927.0521 | 683364.4364 | 1777974.0862 | 1213503.8475 | 5427058.8737 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 15753812.2932 | 38383887.8491 | 1778.2794 | 0.46942 | 33560.2966 | 81769.075 | 684.172 | 1666.9732
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7371 | 2.3504 | 0.1566 | 4 | 26863.2076 | 62990.6912 | 547.6428 | 1284.1504 | 71.9772 | 7.1629 | 57.5956 | 884520.1888 | 0 | 816290.7993 | 0 | 0 | 0 | 397895.3683 | 818495.479 | 2129557.3398 | 1453466.6424 | 6500225.8176 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 16826979.2371 | 39457054.793 | 2371.3737 | 0.6264 | 26863.2076 | 62990.6912 | 547.6428 | 1284.1504
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3003 | 3.0272 | 0.20706 | 4 | 21810.8802 | 49134.5923 | 444.6443 | 1001.6751 | 72.2609 | 7.1657 | 47.0867 | 1053107.9668 | 0 | 994677.6215 | 0 | 0 | 0 | 450388.3942 | 974287.8532 | 2534897.14 | 1730119.385 | 7737478.3607 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 18064231.7802 | 40694307.3361 | 3162.2777 | 0.82822 | 21810.8802 | 49134.5923 | 444.6443 | 1001.6751
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.9151 | 3.8623 | 0.27111 | 4 | 17957.9218 | 38825.6345 | 366.0965 | 791.5131 | 72.443 | 7.1588 | 57.0931 | 1245817.3353 | 0 | 1203928.8679 | 0 | 0 | 0 | 503769.635 | 1151871.1769 | 2996932.521 | 2045468.0264 | 9147787.5623 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 19474540.9818 | 42104616.5377 | 4216.965 | 1.0845 | 17957.9218 | 38825.6345 | 366.0965 | 791.5131
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.6554 | 4.8686 | 0.35077 | 4 | 14994.8464 | 31123.7996 | 305.6902 | 634.5008 | 72.527 | 7.1401 | 72.0018 | 1460945.4304 | 0 | 1443942.556 | 0 | 0 | 0 | 553688.755 | 1348844.9292 | 3509417.8195 | 2395249.7732 | 10712089.2633 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 21038842.6828 | 43668918.2387 | 5623.4133 | 1.4031 | 14994.8464 | 31123.7996 | 305.6902 | 634.5008
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.5554 | 6.0525 | 0.44735 | 4 | 12703.2105 | 25350.0775 | 258.9721 | 516.7956 | 72.5113 | 7.1071 | 75.8404 | 1695590.1932 | 0 | 1713480.1428 | 0 | 0 | 0 | 595813.9104 | 1561904.8561 | 4063756.0448 | 2773597.0024 | 12404142.1496 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 22730895.569 | 45360971.1249 | 7498.9421 | 1.7894 | 12703.2105 | 25350.0775 | 258.9721 | 516.7956
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.4176 | 7.3869 | 0.55991 | 4 | 10926.6782 | 21030.9635 | 222.7551 | 428.7446 | 72.3907 | 7.0575 | 67.5827 | 1940650.854 | 0 | 2004180.4393 | 0 | 0 | 0 | 622181.1168 | 1781134.8399 | 4634147.4924 | 3162900.8858 | 14145195.6281 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 24471949.0476 | 47102024.6035 | 10000 | 2.2397 | 10926.6782 | 21030.9635 | 222.7551 | 428.7446
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8575 | 8.8153 | 0.68474 | 4 | 9550.8716 | 17813.1522 | 194.7074 | 363.1452 | 72.1635 | 6.9905 | 80.0922 | 2183737.4374 | 0 | 2303056.3303 | 0 | 0 | 0 | 625065.3945 | 1993625.0733 | 5187003.492 | 3540236.4655 | 15832724.193 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 26159477.6125 | 48789553.1684 | 13335.2143 | 2.739 | 9550.8716 | 17813.1522 | 194.7074 | 363.1452
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.2534 | 10.2447 | 0.81477 | 4 | 8488.7625 | 15432.4889 | 173.0549 | 314.6122 | 71.8439 | 6.9096 | 70.7172 | 2409245.1042 | 0 | 2591462.3461 | 0 | 0 | 0 | 597381.0953 | 2183254.5328 | 5680380.4472 | 3876976.3754 | 17338699.9009 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 27665453.3204 | 50295528.8763 | 17782.7941 | 3.2591 | 8488.7625 | 15432.4889 | 173.0549 | 314.6122
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.0741 | 11.5931 | 0.94226 | 4 | 7671.3551 | 13675.5624 | 156.391 | 278.7948 | 71.4619 | 6.8207 | 71.4415 | 2607015.2521 | 0 | 2855203.4373 | 0 | 0 | 0 | 538860.2435 | 2340420.7838 | 6089294.7931 | 4156068.8188 | 18586863.3284 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 28913616.7479 | 51543692.3038 | 23713.7371 | 3.769 | 7671.3551 | 13675.5624 | 156.391 | 278.7948
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.346 | 12.7148 | 1.0563 | 4 | 7042.2489 | 12398.2126 | 143.5658 | 252.7543 | 71.0866 | 6.7374 | 71.52 | 2760218.21 | 0 | 3068215.135 | 0 | 0 | 0 | 444295.8181 | 2446364.3736 | 6364938.2817 | 4344201.1637 | 19428232.9821 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 29754986.4015 | 52385061.9574 | 31622.7766 | 4.2252 | 7042.2489 | 12398.2126 | 143.5658 | 252.7543
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.0176 | 13.7428 | 1.1603 | 4 | 6557.3463 | 11433.2953 | 133.6804 | 233.0832 | 70.6979 | 6.6543 | 72.8002 | 2893248.5291 | 0 | 3260314.6586 | 0 | 0 | 0 | 338304.8404 | 2531828.5309 | 6587298.4881 | 4495966.5736 | 20106961.6206 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 30433715.0401 | 53063790.596 | 42169.6503 | 4.6412 | 6557.3463 | 11433.2953 | 133.6804 | 233.0832
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.7176 | 14.3306 | 1.2348 | 4 | 6177.1069 | 10758.6745 | 125.9287 | 219.3301 | 70.4619 | 6.6051 | 77.3265 | 2963842.5276 | 0 | 3365568.8257 | 0 | 0 | 0 | 187422.5505 | 2541565.2225 | 6612631.3622 | 4513256.7807 | 20184287.2692 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 30511040.6887 | 53141116.2446 | 56234.1325 | 4.9394 | 6177.1069 | 10758.6745 | 125.9287 | 219.3301
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.2466 | 15.0318 | 1.3083 | 4 | 5844.5015 | 10168.9234 | 119.1481 | 207.3073 | 70.1544 | 6.5413 | 66.9734 | 3047210.525 | 0 | 3493432.5114 | 0 | 0 | 0 | 0 | 2550850.7842 | 6636790.489 | 4529745.8811 | 20258030.1907 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 30584783.6102 | 53214859.1661 | 74989.4209 | 5.2331 | 5844.5015 | 10168.9234 | 119.1481 | 207.3073
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.599 | 17.0075 | 1.4373 | 4 | 5641.9204 | 9578.2014 | 115.0182 | 195.2646 | 69.1434 | 6.3362 | 65.0648 | 3274259.1082 | 0 | 3864069.9273 | 0 | 0 | 0 | 0 | 2783948.3239 | 7243262.4724 | 4943675.4715 | 22109215.3033 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 32435968.7228 | 55066044.2787 | 100000 | 5.7491 | 5641.9204 | 9578.2014 | 115.0182 | 195.2646
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.2439 | 18.7174 | 1.5347 | 4 | 5531.4674 | 9217.9584 | 112.7664 | 187.9205 | 68.1219 | 6.1346 | 54.0894 | 3448554.2555 | 0 | 4180457.7864 | 0 | 0 | 0 | 0 | 2975314.6964 | 7741158.519 | 5283499.7541 | 23628985.0113 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 33955738.4308 | 56585813.9867 | 133352.1432 | 6.1386 | 5531.4674 | 9217.9584 | 112.7664 | 187.9205
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.8884 | 20.1229 | 1.6035 | 4 | 5479.9534 | 9008.2039 | 111.7163 | 183.6444 | 67.1774 | 5.9525 | 63.73 | 3575853.1407 | 0 | 4438174.3411 | 0 | 0 | 0 | 0 | 3125470.7179 | 8131833.6857 | 5550143.583 | 24821475.4684 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 35148228.8879 | 57778304.4438 | 177827.941 | 6.414 | 5479.9534 | 9008.2039 | 111.7163 | 183.6444
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7495 | 21.2623 | 1.6506 | 4 | 5464.056 | 8891.6288 | 111.3922 | 181.2679 | 66.3351 | 5.7924 | 65.6249 | 3667474.6495 | 0 | 4645994.4186 | 0 | 0 | 0 | 0 | 3242252.9366 | 8435677.0634 | 5757522.9316 | 25748921.9998 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36075675.4193 | 58705750.9752 | 237137.3706 | 6.6024 | 5464.056 | 8891.6288 | 111.3922 | 181.2679
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4472 | 21.5073 | 1.6594 | 4 | 5464.162 | 8873.4521 | 111.3943 | 180.8973 | 66.1407 | 5.7559 | 61.7988 | 3685551.614 | 0 | 4690606.2576 | 0 | 0 | 0 | 0 | 3266701.5699 | 8499287.3922 | 5800938.2881 | 25943085.1218 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36269838.5413 | 58899914.0972 | 316227.766 | 6.6378 | 5464.162 | 8873.4521 | 111.3943 | 180.8973
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4324 | 21.5044 | 1.6593 | 4 | 5464.3967 | 8874.0736 | 111.3991 | 180.91 | 66.1399 | 5.756 | 67.9353 | 3685239.148 | 0 | 4690092.7562 | 0 | 0 | 0 | 0 | 3266379.4426 | 8498449.2831 | 5800366.2614 | 25940526.8913 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36267280.3108 | 58897355.8667 | 421696.5034 | 6.637 | 5464.3967 | 8874.0736 | 111.3991 | 180.91
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4271 | 21.5031 | 1.6591 | 4 | 5464.5735 | 8874.4787 | 111.4027 | 180.9183 | 66.1386 | 5.756 | 76.9567 | 3685066.4228 | 0 | 4689860.3237 | 0 | 0 | 0 | 0 | 3266221.4311 | 8498038.1697 | 5800085.668 | 25939272.0154 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36266025.4349 | 58896100.9908 | 562341.3252 | 6.6366 | 5464.5735 | 8874.4787 | 111.4027 | 180.9183
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4271 | 21.5026 | 1.6591 | 4 | 5464.7066 | 8874.7409 | 111.4054 | 180.9236 | 66.1372 | 5.7559 | 75.9682 | 3684978.8534 | 0 | 4689789.9184 | 0 | 0 | 0 | 0 | 3266159.821 | 8497877.8727 | 5799976.2621 | 25938782.7276 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36265536.147 | 58895611.7029 | 749894.2093 | 6.6363 | 5464.7066 | 8874.7409 | 111.4054 | 180.9236
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4271 | 21.5023 | 1.659 | 4 | 5464.8067 | 8874.9381 | 111.4075 | 180.9276 | 66.1361 | 5.7558 | 75.343 | 3684912.9893 | 0 | 4689736.9654 | 0 | 0 | 0 | 0 | 3266113.4823 | 8497757.309 | 5799893.9748 | 25938414.7208 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36265168.1403 | 58895243.6962 | 1000000 | 6.6361 | 5464.8067 | 8874.9381 | 111.4075 | 180.9276
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.4993 | 1.6589 | 4 | 5464.8819 | 8875.2955 | 111.409 | 180.9349 | 66.1375 | 5.7561 | 74.684 | 3684656.052 | 0 | 4689186.2167 | 0 | 0 | 0 | 0 | 3265798.4848 | 8496937.75 | 5799334.609 | 25935913.1124 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262666.5319 | 58892742.0878 | 1333521.4322 | 6.6356 | 5464.8819 | 8875.2955 | 111.409 | 180.9349
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.4991 | 1.6589 | 4 | 5464.9384 | 8875.4068 | 111.4102 | 180.9372 | 66.1369 | 5.7561 | 73.538 | 3684618.8854 | 0 | 4689156.3383 | 0 | 0 | 0 | 0 | 3265772.3372 | 8496869.7194 | 5799288.1767 | 25935705.457 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262458.8765 | 58892534.4324 | 1778279.41 | 6.6355 | 5464.9384 | 8875.4068 | 111.4102 | 180.9372
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.499 | 1.6588 | 4 | 5464.9809 | 8875.4904 | 111.411 | 180.9389 | 66.1365 | 5.756 | 74.4058 | 3684590.979 | 0 | 4689133.9047 | 0 | 0 | 0 | 0 | 3265752.7047 | 8496818.6395 | 5799253.3136 | 25935549.5415 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262302.961 | 58892378.5169 | 2371373.7057 | 6.6354 | 5464.9809 | 8875.4904 | 111.411 | 180.9389
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.4989 | 1.6588 | 4 | 5465.0127 | 8875.5532 | 111.4117 | 180.9402 | 66.1361 | 5.756 | 73.6263 | 3684570.0323 | 0 | 4689117.0662 | 0 | 0 | 0 | 0 | 3265737.9684 | 8496780.2988 | 5799227.1453 | 25935432.511 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262185.9305 | 58892261.4864 | 3162277.6602 | 6.6353 | 5465.0127 | 8875.5532 | 111.4117 | 180.9402
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.4988 | 1.6588 | 4 | 5465.0366 | 8875.6002 | 111.4122 | 180.9411 | 66.1359 | 5.756 | 75.355 | 3684554.3132 | 0 | 4689104.4302 | 0 | 0 | 0 | 0 | 3265726.9099 | 8496751.527 | 5799207.5079 | 25935344.6883 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262098.1078 | 58892173.6637 | 4216965.0343 | 6.6353 | 5465.0366 | 8875.6002 | 111.4122 | 180.9411
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4077 | 21.4987 | 1.6588 | 4 | 5465.0546 | 8875.6355 | 111.4125 | 180.9418 | 66.1357 | 5.756 | 74.4675 | 3684542.5193 | 0 | 4689094.9496 | 0 | 0 | 0 | 0 | 3265718.6129 | 8496729.9397 | 5799192.7742 | 25935278.7956 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36262032.2151 | 58892107.771 | 5623413.2519 | 6.6353 | 5465.0546 | 8875.6355 | 111.4125 | 180.9418
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.405 | 21.4983 | 1.6588 | 4 | 5465.068 | 8875.6909 | 111.4128 | 180.943 | 66.1359 | 5.756 | 89.4945 | 3684505.0431 | 0 | 4689017.3199 | 0 | 0 | 0 | 0 | 3265673.7215 | 8496613.1417 | 5799113.0571 | 25934922.2832 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36261675.7027 | 58891751.2586 | 7498942.0933 | 6.6352 | 5465.068 | 8875.6909 | 111.4128 | 180.943
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.405 | 21.4983 | 1.6588 | 4 | 5465.0781 | 8875.7108 | 111.413 | 180.9434 | 66.1357 | 5.756 | 90.1924 | 3684498.4066 | 0 | 4689011.9852 | 0 | 0 | 0 | 0 | 3265669.0528 | 8496600.9946 | 5799104.7665 | 25934885.2057 | 961560.8286 | 9365192.5909 | 9365192.5909 | 8785769.2746 | 4479113.6905 | 0 | 36261638.6252 | 58891714.1811 | 10000000 | 6.6352 | 5465.0781 | 8875.7108 | 111.413 | 180.9434
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | 0.038951 | 0.0021173 | 4 | 1338893.3276 | 4105946.6713 | 27295.1515 | 83705.2766 | 54.9648 | 6.4555 | 36.8992 | 79239.6579 | 0 | 50033.5326 | 0 | 0 | 0 | 62056.905 | 74618.7372 | 194142.6479 | 132506.3464 | 592597.827 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11339410.9311 | 34774253.9371 | 100 | 0.0084692 | 1338893.3276 | 4105946.6713 | 27295.1515 | 83705.2766
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1847 | 0.080208 | 0.0042108 | 4 | 686765.6473 | 2078120.4129 | 14000.6466 | 42365.2955 | 59.2561 | 6.7756 | 99.4649 | 110238.4341 | 0 | 74153.3213 | 0 | 0 | 0 | 80522.4278 | 103316.5315 | 268808.4218 | 183467.2713 | 820506.4079 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11567319.5119 | 35002162.518 | 133.3521 | 0.016843 | 686765.6473 | 2078120.4129 | 14000.6466 | 42365.2955
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.13529 | 0.0073034 | 4 | 404689.7555 | 1206877.0574 | 8250.148 | 24603.8212 | 62.6197 | 7.0005 | 146.6969 | 145458.4245 | 0 | 102198.394 | 0 | 0 | 0 | 99639.2003 | 135445.4473 | 352401.2703 | 240521.1081 | 1075663.8444 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 11822476.9485 | 35257319.9545 | 177.8279 | 0.029214 | 404689.7555 | 1206877.0574 | 8250.148 | 24603.8212
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.21214 | 0.011704 | 4 | 259332.8694 | 759899.5419 | 5286.8513 | 15491.58 | 65.5099 | 7.1754 | 204.2872 | 189040.9901 | 0 | 137783.0741 | 0 | 0 | 0 | 123341.5307 | 175564.5821 | 456783.0293 | 311763.8034 | 1394277.0098 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 12141090.1138 | 35575933.1199 | 237.1374 | 0.046817 | 259332.8694 | 759899.5419 | 5286.8513 | 15491.58
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8519 | 0.31156 | 0.017778 | 4 | 175833.2911 | 505383.1736 | 3584.5995 | 10302.9196 | 67.7979 | 7.3024 | 51.2493 | 239052.484 | 0 | 179699.6953 | 0 | 0 | 0 | 148520.1106 | 221236.193 | 575611.1925 | 392866.4665 | 1756986.142 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 12503799.246 | 35938642.2521 | 316.2278 | 0.071112 | 175833.2911 | 505383.1736 | 3584.5995 | 10302.9196
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7487 | 0.44228 | 0.02604 | 4 | 124190.2955 | 349180.418 | 2531.7872 | 7118.5151 | 69.667 | 7.399 | 45.1576 | 298468.9993 | 0 | 230824.4084 | 0 | 0 | 0 | 177389.8713 | 275606.4788 | 717071.5233 | 489416.049 | 2188777.3302 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 12935590.4343 | 36370433.4403 | 421.6965 | 0.10416 | 124190.2955 | 349180.418 | 2531.7872 | 7118.5151
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9077 | 0.6132 | 0.037158 | 4 | 90497.656 | 248167.6944 | 1844.9171 | 5059.2341 | 71.1786 | 7.4726 | 52.9903 | 369152.4511 | 0 | 293271.1594 | 0 | 0 | 0 | 210624.5746 | 340488.7921 | 885881.9933 | 604632.6635 | 2704051.6339 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 13450864.7379 | 36885707.744 | 562.3413 | 0.14863 | 90497.656 | 248167.6944 | 1844.9171 | 5059.2341
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3887 | 0.83348 | 0.051977 | 4 | 67616.5021 | 180334.5433 | 1378.4539 | 3676.3636 | 72.3778 | 7.5279 | 50.6547 | 452384.508 | 0 | 368753.576 | 0 | 0 | 0 | 247910.6138 | 416928.9922 | 1084763.7137 | 740373.5243 | 3311114.9279 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 14057928.032 | 37492771.038 | 749.8942 | 0.20791 | 67616.5021 | 180334.5433 | 1378.4539 | 3676.3636
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2964 | 1.1186 | 0.071635 | 4 | 51587.7298 | 133373.59 | 1051.6856 | 2719.001 | 73.3299 | 7.5695 | 65.8347 | 551308.245 | 0 | 460813.317 | 0 | 0 | 0 | 290673.3321 | 508090.0087 | 1321945.9791 | 902255.294 | 4035086.176 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 14781899.2801 | 38216742.2861 | 1000 | 0.28654 | 51587.7298 | 133373.59 | 1051.6856 | 2719.001
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7083 | 1.4808 | 0.097473 | 4 | 40079.4475 | 100185.3089 | 817.0737 | 2042.413 | 74.0673 | 7.5995 | 50.6146 | 666891.1263 | 0 | 571143.7811 | 0 | 0 | 0 | 337514.2194 | 614464.1595 | 1598709.699 | 1091152.2198 | 4879875.205 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 15626688.3091 | 39061531.3151 | 1333.5214 | 0.38989 | 40079.4475 | 100185.3089 | 817.0737 | 2042.413
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7681 | 1.9418 | 0.13127 | 4 | 31650.6541 | 76280.6971 | 645.2414 | 1555.0852 | 74.6357 | 7.6198 | 48.5874 | 802631.1195 | 0 | 704000.3715 | 0 | 0 | 0 | 389457.0236 | 739474.5207 | 1923961.0157 | 1313142.9267 | 5872666.9775 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 16619480.0816 | 40054323.0876 | 1778.2794 | 0.52509 | 31650.6541 | 76280.6971 | 645.2414 | 1555.0852
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6191 | 2.5237 | 0.17514 | 4 | 25375.5561 | 58826.8289 | 517.315 | 1199.2645 | 75.0627 | 7.6311 | 61.4125 | 960986.9766 | 0 | 862912.5306 | 0 | 0 | 0 | 445999.4976 | 885260.6119 | 2303266.5203 | 1572026.7275 | 7030452.8645 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 17777265.9686 | 41212108.9746 | 2371.3737 | 0.70057 | 25375.5561 | 58826.8289 | 517.315 | 1199.2645
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4038 | 3.2489 | 0.23146 | 4 | 20640.4827 | 45952.9056 | 420.7842 | 936.8121 | 75.3672 | 7.633 | 63.9272 | 1143600.5939 | 0 | 1050845.8286 | 0 | 0 | 0 | 505570.3045 | 1053006.5235 | 2739706.9728 | 1869906.3043 | 8362636.5276 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 19109449.6316 | 42544292.6377 | 3162.2777 | 0.92582 | 20640.4827 | 45952.9056 | 420.7842 | 936.8121
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2575 | 4.139 | 0.3027 | 4 | 17028.2566 | 36382.9086 | 347.144 | 741.7148 | 75.5614 | 7.6243 | 64.313 | 1351211.0646 | 0 | 1270106.5922 | 0 | 0 | 0 | 565764.8501 | 1242962.1777 | 3233932.6198 | 2207225.4637 | 9871202.7681 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 20618015.8722 | 44052858.8782 | 4216.965 | 1.2108 | 17028.2566 | 36382.9086 | 347.144 | 741.7148
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.295 | 5.213 | 0.39118 | 4 | 14249.5255 | 29226.679 | 290.4959 | 595.8254 | 75.6503 | 7.6025 | 65.9047 | 1583362.8712 | 0 | 1522059.1045 | 0 | 0 | 0 | 623528.7406 | 1454290.7794 | 3783766.2918 | 2582498.2428 | 11549506.0303 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 22296319.1343 | 45731162.1404 | 5623.4133 | 1.5647 | 14249.5255 | 29226.679 | 290.4959 | 595.8254
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.4922 | 6.4692 | 0.49791 | 4 | 12100.3905 | 23867.0125 | 246.6828 | 486.5613 | 75.6314 | 7.565 | 66.0809 | 1835039.0555 | 0 | 1803367.8405 | 0 | 0 | 0 | 672759.4727 | 1681354.8838 | 4374540.5143 | 2985713.7889 | 13352775.5557 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 24099588.6598 | 47534431.6658 | 7498.9421 | 1.9916 | 12100.3905 | 23867.0125 | 246.6828 | 486.5613
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6419 | 7.8782 | 0.62162 | 4 | 10435.0577 | 19859.8929 | 212.7328 | 404.8708 | 75.4997 | 7.5092 | 69.3491 | 2096595.8933 | 0 | 2105392.6043 | 0 | 0 | 0 | 705568.0634 | 1913947.0588 | 4979697.6425 | 3398745.9635 | 15199947.2258 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 25946760.3299 | 49381603.3359 | 10000 | 2.4865 | 10435.0577 | 19859.8929 | 212.7328 | 404.8708
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2935 | 9.3723 | 0.75764 | 4 | 9146.6604 | 16879.5214 | 186.467 | 344.1119 | 75.2553 | 7.4351 | 66.1611 | 2353567.5412 | 0 | 2413078.4799 | 0 | 0 | 0 | 713248.593 | 2137158.8995 | 5560449.065 | 3795120.7426 | 16972623.3213 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 27719436.4253 | 51154279.4314 | 13335.2143 | 3.0306 | 9146.6604 | 16879.5214 | 186.467 | 344.1119
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8797 | 10.8639 | 0.89852 | 4 | 8153.5429 | 14673.9534 | 166.221 | 299.1484 | 74.9136 | 7.3461 | 85.181 | 2591486.925 | 0 | 2709529.3233 | 0 | 0 | 0 | 690624.2605 | 2336739.7984 | 6079717.6243 | 4149532.2043 | 18557630.1357 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 29304443.2398 | 52739286.2458 | 17782.7941 | 3.5941 | 8153.5429 | 14673.9534 | 166.221 | 299.1484
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.7996 | 12.2589 | 1.0354 | 4 | 7390.8423 | 13048.9866 | 150.6723 | 266.0212 | 74.5101 | 7.2496 | 86.722 | 2798348.7303 | 0 | 2978386.5458 | 0 | 0 | 0 | 636849.968 | 2501298.2452 | 6507864.9472 | 4441751.5497 | 19864499.9863 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 30611313.0903 | 54046156.0964 | 23713.7371 | 4.1418 | 7390.8423 | 13048.9866 | 150.6723 | 266.0212
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.6756 | 13.4963 | 1.1613 | 4 | 6806.2374 | 11851.2294 | 138.7544 | 241.6033 | 74.0864 | 7.1534 | 86.7382 | 2969774.9331 | 0 | 3210858.5778 | 0 | 0 | 0 | 557372.4476 | 2627822.3238 | 6837054.6461 | 4666430.2834 | 20869313.2119 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 31616126.3159 | 55050969.322 | 31622.7766 | 4.6452 | 6806.2374 | 11851.2294 | 138.7544 | 241.6033
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1971 | 14.5268 | 1.2705 | 4 | 6357.231 | 10968.397 | 129.6008 | 223.6056 | 73.6869 | 7.0654 | 75.5925 | 3103823.2956 | 0 | 3400277.0803 | 0 | 0 | 0 | 457509.803 | 2715027.9697 | 7063945.8485 | 4821288.1912 | 21561872.1882 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 32308685.2923 | 55743528.2983 | 42169.6503 | 5.0822 | 6357.231 | 10968.397 | 129.6008 | 223.6056
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.154 | 15.3159 | 1.3596 | 4 | 6011.6062 | 10320.6928 | 122.5547 | 210.4013 | 73.3557 | 6.9945 | 79.0875 | 3201052.7208 | 0 | 3542384.2456 | 0 | 0 | 0 | 342561.3607 | 2763539.3476 | 7190162.5025 | 4907433.651 | 21947133.8281 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 32693946.9322 | 56128789.9382 | 56234.1325 | 5.4385 | 6011.6062 | 10320.6928 | 122.5547 | 210.4013
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0265 | 15.7862 | 1.4237 | 4 | 5740.9938 | 9856.2583 | 117.0379 | 200.9332 | 73.1512 | 6.9514 | 65.5935 | 3255472.4932 | 0 | 3624037.3593 | 0 | 0 | 0 | 206099.9859 | 2763387.837 | 7189768.303 | 4907164.6018 | 21945930.5802 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 32692743.6843 | 56127586.6903 | 74989.4209 | 5.6946 | 5740.9938 | 9856.2583 | 117.0379 | 200.9332
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.854 | 15.9434 | 1.4625 | 4 | 5500.0422 | 9506.1261 | 112.1258 | 193.7952 | 73.0875 | 6.9381 | 74.2554 | 3270724.5497 | 0 | 3647471.6229 | 0 | 0 | 0 | 0 | 2698096.5073 | 7019893.6564 | 4791221.6649 | 21427408.0011 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 32174221.1052 | 55609064.1112 | 100000 | 5.8498 | 5500.0422 | 9506.1261 | 112.1258 | 193.7952
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9265 | 17.6206 | 1.5786 | 4 | 5343.9823 | 9055.3532 | 108.9443 | 184.6056 | 72.2251 | 6.7583 | 66.6188 | 3466719.8046 | 0 | 3958208.789 | 0 | 0 | 0 | 0 | 2895722.1515 | 7534075.044 | 5142161.0273 | 22996886.8165 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 33743699.9205 | 57178542.9266 | 133352.1432 | 6.3143 | 5343.9823 | 9055.3532 | 108.9443 | 184.6056
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.2226 | 19.0199 | 1.6659 | 4 | 5252.233 | 8769.0492 | 107.0739 | 178.7689 | 71.4094 | 6.5922 | 72.7966 | 3615574.0642 | 0 | 4214668.0594 | 0 | 0 | 0 | 0 | 3053794.4282 | 7945346.6828 | 5422862.3716 | 24252245.6061 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 34999058.7102 | 58433901.7162 | 177827.941 | 6.6637 | 5252.233 | 8769.0492 | 107.0739 | 178.7689
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.8138 | 20.1567 | 1.7296 | 4 | 5200.947 | 8588.2552 | 106.0283 | 175.0832 | 70.6793 | 6.446 | 62.2908 | 3726217.2993 | 0 | 4421503.1891 | 0 | 0 | 0 | 0 | 3177610.9905 | 8267491.9796 | 5642733.156 | 25235556.6144 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 35982369.7185 | 59417212.7245 | 237137.3706 | 6.9184 | 5200.947 | 8588.2552 | 106.0283 | 175.0832
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7265 | 21.0371 | 1.7743 | 4 | 5174.0577 | 8475.9648 | 105.4802 | 172.794 | 70.0735 | 6.3268 | 53.102 | 3805674.4259 | 0 | 4580906.6886 | 0 | 0 | 0 | 0 | 3270766.6346 | 8509863.8568 | 5808156.9425 | 25975368.5484 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 36722181.6525 | 60157024.6585 | 316227.766 | 7.0974 | 5174.0577 | 8475.9648 | 105.4802 | 172.794
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3791 | 21.7281 | 1.8061 | 4 | 5161.5037 | 8405.3992 | 105.2242 | 171.3554 | 69.5691 | 6.2282 | 71.511 | 3863667.5458 | 0 | 4705662.7249 | 0 | 0 | 0 | 0 | 3342038.8055 | 8695299.4256 | 5934720.5285 | 26541389.0302 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37288202.1343 | 60723045.1403 | 421696.5034 | 7.2243 | 5161.5037 | 8405.3992 | 105.2242 | 171.3554
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1018 | 22.2795 | 1.8292 | 4 | 5156.6525 | 8359.4822 | 105.1253 | 170.4194 | 69.1487 | 6.1467 | 57.9346 | 3907206.5042 | 0 | 4805025.0492 | 0 | 0 | 0 | 0 | 3397770.3058 | 8840301.3572 | 6033687.3263 | 26983990.5425 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37730803.6466 | 61165646.6526 | 562341.3252 | 7.3169 | 5156.6525 | 8359.4822 | 105.1253 | 170.4194
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3501 | 22.6121 | 1.8421 | 4 | 5156.228 | 8336.6494 | 105.1167 | 169.9539 | 68.8859 | 6.0958 | 70.4465 | 3932136.5771 | 0 | 4864916.3627 | 0 | 0 | 0 | 0 | 3430850.6465 | 8926369.618 | 6092430.6828 | 27246703.8871 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37993516.9912 | 61428359.9972 | 749894.2093 | 7.3685 | 5156.228 | 8336.6494 | 105.1167 | 169.9539
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3501 | 22.6118 | 1.8421 | 4 | 5156.3195 | 8336.8294 | 105.1185 | 169.9575 | 68.8848 | 6.0957 | 70.7215 | 3932067.2814 | 0 | 4864861.7906 | 0 | 0 | 0 | 0 | 3430802.3381 | 8926243.9294 | 6092344.8978 | 27246320.2372 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37993133.3413 | 61427976.3473 | 1000000 | 7.3683 | 5156.3195 | 8336.8294 | 105.1185 | 169.9575
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3501 | 22.6115 | 1.842 | 4 | 5156.3882 | 8336.9647 | 105.1199 | 169.9603 | 68.884 | 6.0956 | 69.8437 | 3932015.2033 | 0 | 4864820.7775 | 0 | 0 | 0 | 0 | 3430766.0325 | 8926149.4697 | 6092280.4271 | 27246031.91 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37992845.014 | 61427688.0201 | 1333521.4322 | 7.3681 | 5156.3882 | 8336.9647 | 105.1199 | 169.9603
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3325 | 22.6087 | 1.8419 | 4 | 5156.4399 | 8337.2384 | 105.121 | 169.9659 | 68.8854 | 6.096 | 64.0747 | 3931782.3004 | 0 | 4864319.9794 | 0 | 0 | 0 | 0 | 3430479.8891 | 8925404.9833 | 6091772.2998 | 27243759.452 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990572.5561 | 61425415.5621 | 1778279.41 | 7.3676 | 5156.4399 | 8337.2384 | 105.121 | 169.9659
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.6093 | 1.8419 | 4 | 5156.4786 | 8337.2696 | 105.1218 | 169.9665 | 68.8844 | 6.0959 | 74.2592 | 3931803.7094 | 0 | 4864419.9781 | 0 | 0 | 0 | 0 | 3430527.2381 | 8925528.1758 | 6091856.3812 | 27244135.4827 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990948.5867 | 61425791.5928 | 2371373.7057 | 7.3676 | 5156.4786 | 8337.2696 | 105.1218 | 169.9665
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.6092 | 1.8419 | 4 | 5156.5077 | 8337.3269 | 105.1224 | 169.9677 | 68.884 | 6.0958 | 74.3003 | 3931781.6712 | 0 | 4864402.6228 | 0 | 0 | 0 | 0 | 3430511.8747 | 8925488.2032 | 6091829.0991 | 27244013.4711 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990826.5751 | 61425669.5812 | 3162277.6602 | 7.3675 | 5156.5077 | 8337.3269 | 105.1224 | 169.9677
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.6091 | 1.8419 | 4 | 5156.5295 | 8337.3698 | 105.1228 | 169.9686 | 68.8838 | 6.0958 | 74.3953 | 3931765.1335 | 0 | 4864389.5991 | 0 | 0 | 0 | 0 | 3430500.3457 | 8925458.2072 | 6091808.6262 | 27243921.9117 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990735.0158 | 61425578.0218 | 4216965.0343 | 7.3675 | 5156.5295 | 8337.3698 | 105.1228 | 169.9686
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.609 | 1.8419 | 4 | 5156.5459 | 8337.4021 | 105.1232 | 169.9692 | 68.8836 | 6.0958 | 74.8207 | 3931752.7254 | 0 | 4864379.8277 | 0 | 0 | 0 | 0 | 3430491.6957 | 8925435.7016 | 6091793.2657 | 27243853.2161 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990666.3202 | 61425509.3262 | 5623413.2519 | 7.3675 | 5156.5459 | 8337.4021 | 105.1232 | 169.9692
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.609 | 1.8419 | 4 | 5156.5582 | 8337.4262 | 105.1234 | 169.9697 | 68.8834 | 6.0958 | 74.6469 | 3931743.417 | 0 | 4864372.4973 | 0 | 0 | 0 | 0 | 3430485.2066 | 8925418.8182 | 6091781.7425 | 27243801.6816 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990614.7856 | 61425457.7917 | 7498942.0933 | 7.3674 | 5156.5582 | 8337.4262 | 105.1234 | 169.9697
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3371 | 22.609 | 1.8419 | 4 | 5156.5674 | 8337.4444 | 105.1236 | 169.9701 | 68.8833 | 6.0958 | 74.2068 | 3931736.4347 | 0 | 4864366.9986 | 0 | 0 | 0 | 0 | 3430480.339 | 8925406.1538 | 6091773.0987 | 27243763.0248 | 961560.8286 | 9785252.2754 | 9785252.2754 | 9029426.3274 | 4620164.4032 | 0 | 37990576.1289 | 61425419.1349 | 10000000 | 7.3674 | 5156.5674 | 8337.4444 | 105.1236 | 169.9701
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.040208 | 0.0022655 | 4 | 1303091.0843 | 3979467.7947 | 26565.2743 | 81126.8336 | 56.5538 | 6.8653 | 41.9598 | 85049.9821 | 0 | 52292.207 | 0 | 0 | 0 | 67970.5926 | 80071.9849 | 208330.8796 | 142190.1061 | 635905.7523 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 11808638.6318 | 36062020.3015 | 100 | 0.009062 | 1303091.0843 | 3979467.7947 | 26565.2743 | 81126.8336
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.243 | 0.084154 | 0.0045851 | 4 | 657342.4187 | 1979750.865 | 13400.8143 | 40359.8992 | 61.1813 | 7.204 | 106.3773 | 118752.4522 | 0 | 77892.6069 | 0 | 0 | 0 | 88488.6028 | 111202.1281 | 289325.1267 | 197470.344 | 883131.2606 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12055864.1401 | 36309245.8098 | 133.3521 | 0.01834 | 657342.4187 | 1979750.865 | 13400.8143 | 40359.8992
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.14402 | 0.0080288 | 4 | 384210.4249 | 1139408.9112 | 7832.6492 | 23228.3918 | 64.8615 | 7.4447 | 155.5774 | 157759.7129 | 0 | 108209.6037 | 0 | 0 | 0 | 110582.8821 | 146855.3575 | 382087.516 | 260782.5808 | 1166277.6529 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12339010.5323 | 36592392.202 | 177.8279 | 0.032115 | 384210.4249 | 1139408.9112 | 7832.6492 | 23228.3918
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 0.22598 | 0.012932 | 4 | 245129.7783 | 713979.7079 | 4997.3021 | 14555.4421 | 67.9318 | 7.6261 | 220.2314 | 204713.3137 | 0 | 145619.0816 | 0 | 0 | 0 | 136457.8431 | 189848.193 | 493946.0549 | 337128.332 | 1507712.8182 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 12680445.6977 | 36933827.3674 | 237.1374 | 0.05173 | 245129.7783 | 713979.7079 | 4997.3021 | 14555.4421
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9982 | 0.33173 | 0.019703 | 4 | 165806.7402 | 473550.4315 | 3380.1947 | 9653.9661 | 70.3628 | 7.7579 | 44.1031 | 258415.0725 | 0 | 189516.3338 | 0 | 0 | 0 | 163755.9689 | 238558.0763 | 620679.1796 | 423626.2938 | 1894550.9249 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 13067283.8044 | 37320665.4741 | 316.2278 | 0.07881 | 165806.7402 | 473550.4315 | 3380.1947 | 9653.9661
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9534 | 0.47344 | 0.028939 | 4 | 116974.1953 | 326496.613 | 2384.6772 | 6656.0751 | 72.3911 | 7.8604 | 42.8373 | 323598.9259 | 0 | 244207.0731 | 0 | 0 | 0 | 196638.6249 | 298133.4033 | 775681.9599 | 529418.8763 | 2367678.8636 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 13540411.7431 | 37793793.4128 | 421.6965 | 0.11576 | 116974.1953 | 326496.613 | 2384.6772 | 6656.0751
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1707 | 0.65666 | 0.041352 | 4 | 85212.7378 | 231839.923 | 1737.1769 | 4726.3704 | 74.0061 | 7.9371 | 58.7643 | 400067.116 | 0 | 310076.9152 | 0 | 0 | 0 | 233329.7687 | 367954.782 | 957342.8648 | 653406.1767 | 2922177.6234 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 14094910.5029 | 38348292.1726 | 562.3413 | 0.16541 | 85212.7378 | 231839.923 | 1737.1769 | 4726.3704
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7371 | 0.89436 | 0.057917 | 4 | 63686.3203 | 168376.8607 | 1298.3318 | 3432.5901 | 75.2962 | 7.9952 | 56.4311 | 490750.0477 | 0 | 390251.8603 | 0 | 0 | 0 | 275283.5011 | 450951.3095 | 1173282.8046 | 800789.6227 | 3581309.1458 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 14754042.0253 | 39007423.695 | 749.8942 | 0.23167 | 63686.3203 | 168376.8607 | 1298.3318 | 3432.5901
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.725 | 1.198 | 0.079823 | 4 | 48625.1195 | 124585.4459 | 991.2888 | 2539.8428 | 76.307 | 8.0382 | 52.5446 | 596984.5503 | 0 | 486614.2165 | 0 | 0 | 0 | 321771.2457 | 548094.3049 | 1426028.9517 | 973294.0615 | 4352787.3305 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 15525520.21 | 39778901.8797 | 1000 | 0.31929 | 48625.1195 | 124585.4459 | 991.2888 | 2539.8428
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.266 | 1.5877 | 0.10867 | 4 | 37818.7669 | 93615.1258 | 770.9867 | 1908.471 | 77.0999 | 8.0694 | 53.5473 | 722524.0163 | 0 | 603397.7797 | 0 | 0 | 0 | 374360.9989 | 663110.29 | 1725276.952 | 1177536.9706 | 5266207.0076 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 16438939.8871 | 40692321.5568 | 1333.5214 | 0.43468 | 37818.7669 | 93615.1258 | 770.9867 | 1908.471
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4667 | 2.0804 | 0.14632 | 4 | 29905.9242 | 71346.0776 | 609.6727 | 1454.4863 | 77.7071 | 8.0902 | 53.7688 | 868936.9974 | 0 | 743041.6721 | 0 | 0 | 0 | 431797.5049 | 797072.708 | 2073819.6841 | 1415424.5471 | 6330093.1135 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 17502825.993 | 41756207.6627 | 1778.2794 | 0.58526 | 29905.9242 | 71346.0776 | 609.6727 | 1454.4863
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5009 | 2.7032 | 0.19516 | 4 | 24014.4996 | 55083.4384 | 489.5681 | 1122.9504 | 78.1644 | 8.1013 | 55.2712 | 1040045.4954 | 0 | 910354.983 | 0 | 0 | 0 | 494905.8221 | 953669.4572 | 2481252.303 | 1693505.6814 | 7573733.742 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 18746466.6215 | 42999848.2912 | 2371.3737 | 0.78063 | 24014.4996 | 55083.4384 | 489.5681 | 1122.9504
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5124 | 3.4793 | 0.25779 | 4 | 19567.7561 | 43088.064 | 398.9152 | 878.4085 | 78.4902 | 8.1022 | 44.8637 | 1237349.2005 | 0 | 1108213.647 | 0 | 0 | 0 | 561821.0258 | 1133879.7106 | 2950122.4162 | 2013519.168 | 9004905.168 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 20177638.0475 | 44431019.7172 | 3162.2777 | 1.0312 | 19567.7561 | 43088.064 | 398.9152 | 878.4085
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.6265 | 4.4296 | 0.33685 | 4 | 16174.3326 | 34174.338 | 329.7356 | 696.6901 | 78.6969 | 8.0914 | 62.9324 | 1461062.1174 | 0 | 1338463.014 | 0 | 0 | 0 | 629551.3921 | 1337339.8442 | 3479483.9484 | 2374819.291 | 10620719.6071 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 21793452.4866 | 46046834.1563 | 4216.965 | 1.3474 | 16174.3326 | 34174.338 | 329.7356 | 696.6901
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.9493 | 5.572 | 0.4347 | 4 | 13563.2295 | 27511.4416 | 276.5048 | 560.8579 | 78.7901 | 8.0662 | 61.0277 | 1710313.9468 | 0 | 1602132.6093 | 0 | 0 | 0 | 694727.6801 | 1562797.9521 | 4066079.6975 | 2775182.9431 | 12411234.829 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 23583967.7085 | 47837349.3782 | 5623.4133 | 1.7388 | 13563.2295 | 27511.4416 | 276.5048 | 560.8579
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.4413 | 6.9028 | 0.55223 | 4 | 11543.7648 | 22523.4763 | 235.3353 | 459.1715 | 78.7673 | 8.0237 | 60.2257 | 1979367.776 | 0 | 1895344.7095 | 0 | 0 | 0 | 750869.8084 | 1803977.0946 | 4693578.3536 | 3203463.6697 | 14326601.4117 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 25499334.2912 | 49752715.9609 | 7498.9421 | 2.2089 | 11543.7648 | 22523.4763 | 235.3353 | 459.1715
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.854 | 8.3853 | 0.68758 | 4 | 9979.6589 | 18798.0465 | 203.4488 | 383.2236 | 78.6239 | 7.9614 | 68.7387 | 2257072.761 | 0 | 2208120.5311 | 0 | 0 | 0 | 789305.5722 | 2049254.5571 | 5331739.9977 | 3639022.1047 | 16274515.5239 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 27447248.4033 | 51700630.0731 | 10000 | 2.7503 | 9979.6589 | 18798.0465 | 203.4488 | 383.2236
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.7218 | 9.9478 | 0.83534 | 4 | 8770.7595 | 16029.2551 | 178.8038 | 326.778 | 78.3614 | 7.8797 | 88.5621 | 2528257.7981 | 0 | 2524972.6401 | 0 | 0 | 0 | 801535.6609 | 2283358.7786 | 5940831.1608 | 4054739.3391 | 18133695.3776 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 29306428.2571 | 53559809.9268 | 13335.2143 | 3.3414 | 8770.7595 | 16029.2551 | 178.8038 | 326.778
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.4271 | 11.4929 | 0.987 | 4 | 7840.1972 | 13983.3847 | 159.833 | 285.0702 | 77.9995 | 7.7829 | 78.4715 | 2776956.9653 | 0 | 2827466.9399 | 0 | 0 | 0 | 782029.1729 | 2490716.7005 | 6480333.9384 | 4422961.0705 | 19780464.7875 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 30953197.6669 | 55206579.3367 | 17782.7941 | 3.948 | 7840.1972 | 13983.3847 | 159.833 | 285.0702
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.4527 | 12.9368 | 1.1337 | 4 | 7126.7771 | 12475.0546 | 145.289 | 254.3209 | 77.5742 | 7.6784 | 89.1764 | 2993152.5556 | 0 | 3101818.4009 | 0 | 0 | 0 | 732301.1836 | 2662636.1347 | 6927633.0406 | 4728251.8988 | 21145793.2143 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 32318526.0937 | 56571907.7634 | 23713.7371 | 4.5348 | 7126.7771 | 12475.0546 | 145.289 | 254.3209
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.3527 | 14.2067 | 1.2674 | 4 | 6581.2249 | 11365.2068 | 134.1672 | 231.6951 | 77.133 | 7.5755 | 93.1629 | 3170848.5436 | 0 | 3337116.9011 | 0 | 0 | 0 | 657138.2222 | 2794390.4301 | 7270430.6908 | 4962218.3389 | 22192143.1267 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 33364876.0062 | 57618257.6759 | 31622.7766 | 5.0697 | 6581.2249 | 11365.2068 | 134.1672 | 231.6951
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.9614 | 15.2739 | 1.3836 | 4 | 6164.2029 | 10546.4934 | 125.6656 | 215.0045 | 76.7149 | 7.4812 | 97.3518 | 3311349.8811 | 0 | 3530825.5368 | 0 | 0 | 0 | 565186.3429 | 2888871.0867 | 7516249.9787 | 5129995.054 | 22942477.8803 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 34115210.7598 | 58368592.4295 | 42169.6503 | 5.5344 | 6164.2029 | 10546.4934 | 125.6656 | 215.0045
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.246 | 16.1317 | 1.4803 | 4 | 5844.3867 | 9940.3326 | 119.1457 | 202.6471 | 76.3473 | 7.4 | 82.5022 | 3418320.4567 | 0 | 3683899.6122 | 0 | 0 | 0 | 463746.181 | 2950726.8375 | 7677185.9538 | 5239837.1639 | 23433716.205 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 34606449.0845 | 58859830.7542 | 56234.1325 | 5.9213 | 5844.3867 | 9940.3326 | 119.1457 | 202.6471
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0944 | 16.7617 | 1.5561 | 4 | 5598.6811 | 9495.067 | 114.1367 | 193.5698 | 76.0626 | 7.3384 | 82.3056 | 3493294.4994 | 0 | 3794280.4549 | 0 | 0 | 0 | 356851.8598 | 2981326.4575 | 7756799.8883 | 5294175.3101 | 23676728.4701 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 34849461.3495 | 59102843.0192 | 74989.4209 | 6.2246 | 5598.6811 | 9495.067 | 114.1367 | 193.5698
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.465 | 17.1585 | 1.6111 | 4 | 5407.4739 | 9170.8902 | 110.2387 | 186.961 | 75.8787 | 7.2991 | 81.8209 | 3538180.0174 | 0 | 3861846.3671 | 0 | 0 | 0 | 244099.9987 | 2981209.2894 | 7756495.041 | 5293967.2455 | 23675797.959 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 34848530.8385 | 59101912.5082 | 100000 | 6.4445 | 5407.4739 | 9170.8902 | 110.2387 | 186.961
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.6608 | 16.4515 | 1.592 | 4 | 5241.7289 | 9050.2667 | 106.8597 | 184.5019 | 76.2354 | 7.3768 | 69.1177 | 3445736.0245 | 0 | 3724306.5826 | 0 | 0 | 0 | 0 | 2796316.6168 | 7275442.2335 | 4965638.8197 | 22207440.2772 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 33380173.1567 | 57633554.8264 | 133352.1432 | 6.3682 | 5241.7289 | 9050.2667 | 106.8597 | 184.5019
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.525 | 17.8277 | 1.695 | 4 | 5115.133 | 8692.3592 | 104.2789 | 177.2055 | 75.5501 | 7.229 | 73.6782 | 3612790.1966 | 0 | 3977019.3074 | 0 | 0 | 0 | 0 | 2960025.7066 | 7701379.7037 | 5256349.8953 | 23507564.8096 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 34680297.6891 | 58933679.3588 | 177827.941 | 6.7799 | 5115.133 | 8692.3592 | 104.2789 | 177.2055
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7996 | 18.952 | 1.7731 | 4 | 5034.7601 | 8454.443 | 102.6404 | 172.3553 | 74.9296 | 7.0978 | 70.1185 | 3739967.2441 | 0 | 4181645.5801 | 0 | 0 | 0 | 0 | 3089429.0015 | 8038060.5328 | 5486141.4792 | 24535243.8377 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 35707976.7172 | 59961358.3869 | 237137.3706 | 7.0923 | 5034.7601 | 8454.443 | 102.6404 | 172.3553
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.5855 | 19.8425 | 1.8308 | 4 | 4984.2262 | 8296.0981 | 101.6102 | 169.1272 | 74.3991 | 6.9874 | 66.7685 | 3834697.9493 | 0 | 4342732.1824 | 0 | 0 | 0 | 0 | 3189197.7514 | 8297638.3546 | 5663308.6764 | 25327574.9141 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 36500307.7936 | 60753689.4633 | 316227.766 | 7.3232 | 4984.2262 | 8296.0981 | 101.6102 | 169.1272
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1365 | 20.5407 | 1.8733 | 4 | 4952.3343 | 8189.1244 | 100.96 | 166.9464 | 73.958 | 6.8965 | 55.332 | 3905117.429 | 0 | 4468521.1683 | 0 | 0 | 0 | 0 | 3265719.0529 | 8496731.0847 | 5799193.5557 | 25935282.2905 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 37108015.17 | 61361396.8397 | 421696.5034 | 7.493 | 4952.3343 | 8189.1244 | 100.96 | 166.9464
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.6689 | 21.0813 | 1.9044 | 4 | 4932.1415 | 8116.0698 | 100.5484 | 165.4571 | 73.601 | 6.8235 | 69.4174 | 3957255.7696 | 0 | 4565636.2627 | 0 | 0 | 0 | 0 | 3323927.8926 | 8648178.5452 | 5902559.5594 | 26397558.0296 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 37570290.9091 | 61823672.5788 | 562341.3252 | 7.6174 | 4932.1415 | 8116.0698 | 100.5484 | 165.4571
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3775 | 21.495 | 1.9271 | 4 | 4919.2553 | 8065.6486 | 100.2857 | 164.4292 | 73.3186 | 6.7661 | 63.0478 | 3995734.1605 | 0 | 4639794.6254 | 0 | 0 | 0 | 0 | 3367856.2265 | 8762471.0591 | 5980566.5486 | 26746422.6202 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 37919155.4997 | 62172537.1694 | 749894.2093 | 7.7083 | 4919.2553 | 8065.6486 | 100.2857 | 164.4292
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3265 | 21.7913 | 1.943 | 4 | 4910.8654 | 8031.4791 | 100.1146 | 163.7326 | 73.1136 | 6.7251 | 60.2616 | 4022805.7345 | 0 | 4692809.1736 | 0 | 0 | 0 | 0 | 3399089.8142 | 8843734.4473 | 6036030.4808 | 26994469.6504 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38167202.5299 | 62420584.1996 | 1000000 | 7.772 | 4910.8654 | 8031.4791 | 100.1146 | 163.7326
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8929 | 22.0298 | 1.9553 | 4 | 4905.333 | 8006.3836 | 100.0018 | 163.221 | 72.9437 | 6.6909 | 58.5939 | 4043910.9969 | 0 | 4735473.4055 | 0 | 0 | 0 | 0 | 3423959.9169 | 8908441.3531 | 6080194.2737 | 27191979.9461 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38364712.8256 | 62618094.4953 | 1333521.4322 | 7.821 | 4905.333 | 8006.3836 | 100.0018 | 163.221
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0844 | 22.2112 | 1.9643 | 4 | 4901.6413 | 7988.3584 | 99.9266 | 162.8535 | 72.8126 | 6.6645 | 61.6825 | 4059654.7042 | 0 | 4767883.0897 | 0 | 0 | 0 | 0 | 3442739.7396 | 8957302.5995 | 6113543.0783 | 27341123.2114 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38513856.0909 | 62767237.7606 | 1778279.41 | 7.8573 | 4901.6413 | 7988.3584 | 99.9266 | 162.8535
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.9735 | 22.3463 | 1.971 | 4 | 4899.1165 | 7975.4037 | 99.8751 | 162.5894 | 72.7141 | 6.6448 | 56.9681 | 4071251.0154 | 0 | 4792018.919 | 0 | 0 | 0 | 0 | 3456675.2744 | 8993560.0024 | 6138289.5008 | 27451794.7119 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38624527.5914 | 62877909.2611 | 2371373.7057 | 7.884 | 4899.1165 | 7975.4037 | 99.8751 | 162.5894
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.6508 | 22.4492 | 1.976 | 4 | 4897.382 | 7965.91 | 99.8398 | 162.3958 | 72.6383 | 6.6296 | 60.4573 | 4079975.0939 | 0 | 4810402.5089 | 0 | 0 | 0 | 0 | 3467247.2651 | 9021066.1536 | 6157063.0142 | 27535754.0358 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38708486.9152 | 62961868.585 | 3162277.6602 | 7.9039 | 4897.382 | 7965.91 | 99.8398 | 162.3958
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.165 | 22.5273 | 1.9797 | 4 | 4896.1751 | 7958.9204 | 99.8152 | 162.2534 | 72.5803 | 6.618 | 67.5743 | 4086533.1462 | 0 | 4824355.297 | 0 | 0 | 0 | 0 | 3475246.4929 | 9041878.5033 | 6171267.8705 | 27599281.3099 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38772014.1894 | 63025395.8591 | 4216965.0343 | 7.9188 | 4896.1751 | 7958.9204 | 99.8152 | 162.2534
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5522 | 22.5862 | 1.9825 | 4 | 4895.3206 | 7953.766 | 99.7977 | 162.1483 | 72.5365 | 6.6092 | 65.0829 | 4091439.3489 | 0 | 4834860.7636 | 0 | 0 | 0 | 0 | 3481257.0439 | 9057516.7242 | 6181941.2776 | 27647015.1582 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38819748.0377 | 63073129.7074 | 5623413.2519 | 7.93 | 4895.3206 | 7953.766 | 99.7977 | 162.1483
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8838 | 22.6368 | 1.9848 | 4 | 4894.8006 | 7949.7125 | 99.7871 | 162.0656 | 72.4978 | 6.6013 | 60.1429 | 4095544.7106 | 0 | 4843919.4039 | 0 | 0 | 0 | 0 | 3486391.0047 | 9070874.237 | 6191058.0546 | 27687787.4107 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38860520.2902 | 63113901.9599 | 7498942.0933 | 7.9391 | 4894.8006 | 7949.7125 | 99.7871 | 162.0656
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.047 | 22.6612 | 1.986 | 4 | 4894.2289 | 7947.208 | 99.7755 | 162.0146 | 72.4806 | 6.5981 | 67.6887 | 4097692.6016 | 0 | 4848248.3308 | 0 | 0 | 0 | 0 | 3488916.9636 | 9077446.2641 | 6195543.5981 | 27707847.7582 | 961560.8286 | 10211172.0509 | 10211172.0509 | 9278650.4665 | 4763559.1523 | 0 | 38880580.6377 | 63133962.3074 | 10000000 | 7.9442 | 4894.2289 | 7947.208 | 99.7755 | 162.0146
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | 0.042815 | 0.0024287 | 4 | 1265862.8045 | 3848109.3193 | 25806.3255 | 78448.9134 | 58.3764 | 7.2955 | 35.5653 | 92480.4268 | 0 | 55676.9832 | 0 | 0 | 0 | 75568.4999 | 87253.1049 | 227014.6808 | 154942.1843 | 692935.88 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12297448.6258 | 37383140.1727 | 100 | 0.0097147 | 1265862.8045 | 3848109.3193 | 25806.3255 | 78448.9134
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3013 | 0.08825 | 0.0049889 | 4 | 628977.6994 | 1886054.2025 | 12822.5612 | 38449.766 | 63.1018 | 7.6344 | 111.198 | 127496.8079 | 0 | 81694.7313 | 0 | 0 | 0 | 96596.2929 | 119257.2545 | 310282.9133 | 211774.464 | 947102.4639 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12551615.2097 | 37637306.7566 | 133.3521 | 0.019956 | 628977.6994 | 1886054.2025 | 12822.5612 | 38449.766
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.15381 | 0.008816 | 4 | 364932.7809 | 1076304.2903 | 7439.6483 | 21941.9188 | 67.1507 | 7.8936 | 164.4562 | 171029.6618 | 0 | 114774.5062 | 0 | 0 | 0 | 122434.5009 | 159213.0809 | 414239.7774 | 282727.1599 | 1264418.6872 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 12868931.433 | 37954622.9799 | 177.8279 | 0.035264 | 364932.7809 | 1076304.2903 | 7439.6483 | 21941.9188
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.24028 | 0.014259 | 4 | 231923.0004 | 671732.5497 | 4728.0641 | 13694.1766 | 70.3579 | 8.0788 | 228.2088 | 220861.5276 | 0 | 153581.2216 | 0 | 0 | 0 | 149835.9425 | 204468.6898 | 531985.5884 | 363091.0953 | 1623824.0652 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 13228336.811 | 38314028.3579 | 237.1374 | 0.057038 | 231923.0004 | 671732.5497 | 4728.0641 | 13694.1766
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1614 | 0.3547 | 0.021799 | 4 | 156555.3013 | 444246.2269 | 3191.5916 | 9056.5602 | 72.9798 | 8.2178 | 51.4415 | 279598.2116 | 0 | 200493.0734 | 0 | 0 | 0 | 180684.0103 | 257702.3652 | 670488.6921 | 457622.3095 | 2046588.6621 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 13651101.4079 | 38736792.9548 | 316.2278 | 0.087197 | 156555.3013 | 444246.2269 | 3191.5916 | 9056.5602
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1554 | 0.50531 | 0.032067 | 4 | 110346.9107 | 305921.6694 | 2249.571 | 6236.627 | 75.12 | 8.3234 | 54.4941 | 349350.761 | 0 | 257661.0265 | 0 | 0 | 0 | 216072.3358 | 321002.8081 | 835183.4599 | 570029.8727 | 2549300.2638 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 14153813.0096 | 39239504.5565 | 421.6965 | 0.12827 | 110346.9107 | 305921.6694 | 2249.571 | 6236.627
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4413 | 0.70264 | 0.045894 | 4 | 80372.329 | 217022.3068 | 1638.4986 | 4424.2933 | 76.8524 | 8.4039 | 52.8871 | 432440.5251 | 0 | 327559.4328 | 0 | 0 | 0 | 257010.2859 | 396633.9951 | 1031960.2943 | 704334.1056 | 3149938.6387 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 14754451.3845 | 39840142.9314 | 562.3413 | 0.18358 | 80372.329 | 217022.3068 | 1638.4986 | 4424.2933
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0855 | 0.95734 | 0.064329 | 4 | 60091.7374 | 157581.0499 | 1225.0513 | 3212.5028 | 78.2268 | 8.4643 | 59.2329 | 530364.3504 | 0 | 412101.4013 | 0 | 0 | 0 | 303197.1366 | 485808.5264 | 1263974.1327 | 862688.3177 | 3858133.8651 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 15462646.6109 | 40548338.1578 | 749.8942 | 0.25732 | 60091.7374 | 157581.0499 | 1225.0513 | 3212.5028
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.166 | 1.2819 | 0.088686 | 4 | 45916.7513 | 116631.5223 | 936.0751 | 2377.6913 | 79.302 | 8.5089 | 54.5815 | 644786.4761 | 0 | 513433.7069 | 0 | 0 | 0 | 354155.8951 | 589826.6704 | 1534608.0063 | 1047401.4974 | 4684212.2521 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 16288724.9979 | 41374416.5448 | 1000 | 0.35474 | 45916.7513 | 116631.5223 | 936.0751 | 2377.6913
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8339 | 1.6997 | 0.12077 | 4 | 35751.4677 | 87679.4762 | 728.842 | 1787.4647 | 80.1489 | 8.5412 | 44.5011 | 780466.0547 | 0 | 636648.562 | 0 | 0 | 0 | 412415.6258 | 713516.7946 | 1856424.3371 | 1267047.7557 | 5666519.1299 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 17271031.8756 | 42356723.4225 | 1333.5214 | 0.48309 | 35751.4677 | 87679.4762 | 728.842 | 1787.4647
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1977 | 2.2285 | 0.16264 | 4 | 28309.0544 | 66869.3314 | 577.1184 | 1363.2218 | 80.7978 | 8.5625 | 64.8506 | 938867.04 | 0 | 784130.9875 | 0 | 0 | 0 | 476423.1737 | 857774.2685 | 2231752.6929 | 1523217.0708 | 6812165.2335 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 18416677.9793 | 43502369.5262 | 1778.2794 | 0.65056 | 28309.0544 | 66869.3314 | 577.1184 | 1363.2218
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4024 | 2.8919 | 0.21678 | 4 | 22767.1507 | 51696.6518 | 464.1392 | 1053.9062 | 81.2826 | 8.5732 | 60.2001 | 1122491.2365 | 0 | 959400.479 | 0 | 0 | 0 | 545470.9621 | 1024671.4443 | 2665984.9089 | 1819589.4809 | 8137608.5116 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 19742121.2574 | 44827812.8043 | 2371.3737 | 0.86713 | 22767.1507 | 51696.6518 | 464.1392 | 1053.9062
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6176 | 3.7174 | 0.28609 | 4 | 18582.9743 | 40504.0332 | 378.8391 | 825.7295 | 81.6281 | 8.573 | 58.9933 | 1334002.1152 | 0 | 1166433.5733 | 0 | 0 | 0 | 618841.2657 | 1216518.0121 | 3165130.3254 | 2160266.484 | 9661191.7757 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 21265704.5215 | 46351396.0684 | 3162.2777 | 1.1444 | 18582.9743 | 40504.0332 | 378.8391 | 825.7295
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9908 | 4.7297 | 0.3735 | 4 | 15388.8355 | 32179.9358 | 313.7222 | 656.0315 | 81.8473 | 8.5598 | 48.9017 | 1574271.2434 | 0 | 1407824.3451 | 0 | 0 | 0 | 694133.251 | 1433729.2474 | 3730269.4035 | 2545985.5172 | 11386213.0077 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 22990725.7534 | 48076417.3003 | 4216.965 | 1.494 | 15388.8355 | 32179.9358 | 313.7222 | 656.0315
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6083 | 5.9444 | 0.4814 | 4 | 12930.4899 | 25958.0883 | 263.6055 | 529.1907 | 81.9446 | 8.5309 | 56.3524 | 1841437.5827 | 0 | 1683764.9925 | 0 | 0 | 0 | 767047.9849 | 1673977.7184 | 4355346.6433 | 2972613.5775 | 13294188.4992 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 24898701.245 | 49984392.7919 | 5623.4133 | 1.9256 | 12930.4899 | 25958.0883 | 263.6055 | 529.1907
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3755 | 7.3492 | 0.61025 | 4 | 11029.2832 | 21306.1415 | 224.8469 | 434.3545 | 81.9176 | 8.4831 | 63.9412 | 2127688.2329 | 0 | 1988439.2922 | 0 | 0 | 0 | 829492.4582 | 1928791.7935 | 5018320.597 | 3425106.9236 | 15317839.2974 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 26922352.0432 | 52008043.5901 | 7498.9421 | 2.441 | 11029.2832 | 21306.1415 | 224.8469 | 434.3545
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.0413 | 8.9061 | 0.75777 | 4 | 9557.5349 | 17833.6533 | 194.8433 | 363.5631 | 81.762 | 8.414 | 70.9615 | 2421602.0558 | 0 | 2311871.9959 | 0 | 0 | 0 | 873193.9368 | 2186600.5155 | 5689086.0079 | 3882918.0994 | 17365272.6114 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 28969785.3572 | 54055476.9041 | 10000 | 3.0311 | 9557.5349 | 17833.6533 | 194.8433 | 363.5631
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.3749 | 10.5772 | 0.91984 | 4 | 8416.3269 | 15234.2554 | 171.5782 | 310.5709 | 81.4723 | 8.3216 | 87.0129 | 2714053.8444 | 0 | 2641986.8878 | 0 | 0 | 0 | 895394.5462 | 2438059.7586 | 6343331.377 | 4329454.0072 | 19362280.4212 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 30966793.167 | 56052484.7139 | 13335.2143 | 3.6794 | 8416.3269 | 15234.2554 | 171.5782 | 310.5709
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.2434 | 12.1841 | 1.0833 | 4 | 7538.9582 | 13328.2713 | 153.6919 | 271.7148 | 81.0853 | 8.2157 | 85.5208 | 2974253.5201 | 0 | 2947279.0052 | 0 | 0 | 0 | 878870.0393 | 2652157.0002 | 6900368.4824 | 4709643.2776 | 21062571.325 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 32667084.0708 | 57752775.6177 | 17782.7941 | 4.3331 | 7538.9582 | 13328.2713 | 153.6919 | 271.7148
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.3445 | 13.6735 | 1.2401 | 4 | 6867.8085 | 11925.1977 | 140.0096 | 243.1113 | 80.6367 | 8.1028 | 67.6137 | 3198615.5655 | 0 | 3221959.8441 | 0 | 0 | 0 | 831408.0856 | 2828273.5631 | 7358587.6525 | 5022387.2767 | 22461231.9875 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 34065744.7333 | 59151436.2802 | 23713.7371 | 4.9602 | 6867.8085 | 11925.1977 | 140.0096 | 243.1113
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2956 | 14.9808 | 1.3823 | 4 | 6355.8564 | 10892.926 | 129.5727 | 222.067 | 80.174 | 7.9921 | 78.6012 | 3382741.6472 | 0 | 3457208.4185 | 0 | 0 | 0 | 759474.2405 | 2963775.4794 | 7711135.8435 | 5263008.6612 | 23537344.2903 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 35141857.0361 | 60227548.583 | 31622.7766 | 5.5291 | 6355.8564 | 10892.926 | 129.5727 | 222.067
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9628 | 16.0817 | 1.5055 | 4 | 5965.7295 | 10131.3527 | 121.6195 | 206.5413 | 79.7358 | 7.8908 | 98.2088 | 3528706.7846 | 0 | 3651417.2372 | 0 | 0 | 0 | 672494.9795 | 3062521.4105 | 7968052.5006 | 5438359.5588 | 24321552.4711 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 35926065.2169 | 61011756.7638 | 42169.6503 | 6.0221 | 5965.7295 | 10131.3527 | 121.6195 | 206.5413
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.3024 | 16.9675 | 1.6079 | 4 | 5668.2281 | 9568.6825 | 115.5545 | 195.0705 | 79.3517 | 7.8041 | 100.5366 | 3640074.8794 | 0 | 3805105.035 | 0 | 0 | 0 | 578244.211 | 3129135.4089 | 8141368.4601 | 5556651.2624 | 24850579.2568 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36455092.0026 | 61540783.5495 | 56234.1325 | 6.4315 | 5668.2281 | 9568.6825 | 115.5545 | 195.0705
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.4707 | 17.6623 | 1.6905 | 4 | 5440.4902 | 9150.2871 | 110.9118 | 186.541 | 79.0302 | 7.7324 | 81.4541 | 3723519.5516 | 0 | 3924009.0207 | 0 | 0 | 0 | 483593.6362 | 3171137.6613 | 8250649.705 | 5631237.9576 | 25184147.5324 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36788660.2782 | 61874351.8251 | 74989.4209 | 6.762 | 5440.4902 | 9150.2871 | 110.9118 | 186.541
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.4844 | 18.1683 | 1.7541 | 4 | 5266.3093 | 8841.6389 | 107.3608 | 180.2488 | 78.7874 | 7.6792 | 86.3511 | 3782027.5845 | 0 | 4009416.1415 | 0 | 0 | 0 | 391821.9464 | 3191473.6122 | 8303559.6777 | 5667350.1012 | 25345649.0635 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36950161.8093 | 62035853.3562 | 100000 | 7.0163 | 5266.3093 | 8841.6389 | 107.3608 | 180.2488
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.4935 | 18.5105 | 1.8011 | 4 | 5131.9954 | 8614.0497 | 104.6227 | 175.6091 | 78.6198 | 7.6427 | 81.4161 | 3820124.9913 | 0 | 4066103.4547 | 0 | 0 | 0 | 304193.9785 | 3194264.7456 | 8310821.6341 | 5672306.5356 | 25367815.3398 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36972328.0856 | 62058019.6325 | 133352.1432 | 7.2043 | 5131.9954 | 8614.0497 | 104.6227 | 175.6091
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4487 | 18.6823 | 1.8321 | 4 | 5027.4959 | 8450.5477 | 102.4923 | 172.2758 | 78.5375 | 7.6251 | 79.0714 | 3837935.1248 | 0 | 4092983.4778 | 0 | 0 | 0 | 218004.4465 | 3178079.9891 | 8268712.2179 | 5643565.9938 | 25239281.2499 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36843793.9957 | 61929485.5426 | 177827.941 | 7.3285 | 5027.4959 | 8450.5477 | 102.4923 | 172.2758
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.766 | 17.6552 | 1.7819 | 4 | 4936.2961 | 8455.8093 | 100.6331 | 172.3831 | 79.0741 | 7.7437 | 76.8126 | 3709045.0775 | 0 | 3903971.9076 | 0 | 0 | 0 | 0 | 2969076.6242 | 7724928.3347 | 5272422.3199 | 23579444.2639 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 35183957.0096 | 60269648.5565 | 237137.3706 | 7.1276 | 4936.2961 | 8455.8093 | 100.6331 | 172.3831
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.3498 | 18.5418 | 1.851 | 4 | 4863.3905 | 8251.5642 | 99.1468 | 168.2193 | 78.6245 | 7.6445 | 65.4488 | 3817032.8256 | 0 | 4062055.0138 | 0 | 0 | 0 | 0 | 3072844.2574 | 7994910.4306 | 5456690.6479 | 24403533.1753 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36008045.9211 | 61093737.468 | 316227.766 | 7.4039 | 4863.3905 | 8251.5642 | 99.1468 | 168.2193
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7324 | 19.2357 | 1.9027 | 4 | 4814.1164 | 8110.1196 | 98.1423 | 165.3358 | 78.2501 | 7.5629 | 69.4699 | 3898052.535 | 0 | 4185060.3688 | 0 | 0 | 0 | 0 | 3152414.0325 | 8201934.6635 | 5597988.9408 | 25035450.5406 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 36639963.2864 | 61725654.8333 | 421696.5034 | 7.6109 | 4814.1164 | 8110.1196 | 98.1423 | 165.3358
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.1432 | 19.7745 | 1.9414 | 4 | 4780.3026 | 8010.5981 | 97.4529 | 163.3069 | 77.9454 | 7.497 | 68.3224 | 3958796.6564 | 0 | 4280166.6511 | 0 | 0 | 0 | 0 | 3213195.6899 | 8360076.0682 | 5705923.6989 | 25518158.7646 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 37122671.5104 | 62208363.0573 | 562341.3252 | 7.7658 | 4780.3026 | 8010.5981 | 97.4529 | 163.3069
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7548 | 20.1862 | 1.9701 | 4 | 4756.9224 | 7940.18 | 96.9763 | 161.8713 | 77.7044 | 7.4454 | 77.667 | 4003952.5003 | 0 | 4352631.2613 | 0 | 0 | 0 | 0 | 3259067.667 | 8479425.5428 | 5787382.1677 | 25882459.139 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 37486971.8848 | 62572663.4317 | 749894.2093 | 7.8805 | 4756.9224 | 7940.18 | 96.9763 | 161.8713
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7453 | 20.4995 | 1.9914 | 4 | 4740.5188 | 7889.7325 | 96.6419 | 160.8429 | 77.5162 | 7.4052 | 65.1423 | 4037573.8822 | 0 | 4407662.0201 | 0 | 0 | 0 | 0 | 3293642.0019 | 8569380.87 | 5848778.527 | 26157037.3012 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 37761550.047 | 62847241.5939 | 1000000 | 7.9657 | 4740.5188 | 7889.7325 | 96.6419 | 160.8429
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2728 | 20.7398 | 2.0074 | 4 | 4728.7866 | 7852.9305 | 96.4027 | 160.0926 | 77.3687 | 7.3739 | 61.7034 | 4062880.1944 | 0 | 4449774.9672 | 0 | 0 | 0 | 0 | 3319935.513 | 8637791.1924 | 5895469.9777 | 26365851.8446 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 37970364.5904 | 63056056.1373 | 1333521.4322 | 8.0296 | 4728.7866 | 7852.9305 | 96.4027 | 160.0926
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4371 | 20.9228 | 2.0194 | 4 | 4720.3324 | 7825.9627 | 96.2304 | 159.5428 | 77.2546 | 7.3496 | 58.7334 | 4081880.9733 | 0 | 4481807.4581 | 0 | 0 | 0 | 0 | 3339838.4882 | 8689574.6513 | 5930813.2524 | 26523914.8234 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38128427.5691 | 63214119.1161 | 1778279.41 | 8.0775 | 4720.3324 | 7825.9627 | 96.2304 | 159.5428
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2996 | 21.0583 | 2.0281 | 4 | 4714.2828 | 7806.4785 | 96.107 | 159.1456 | 77.1695 | 7.3316 | 60.7474 | 4095826.4862 | 0 | 4505501.5899 | 0 | 0 | 0 | 0 | 3354517.9497 | 8727767.5988 | 5956880.7239 | 26640494.3483 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38245007.0941 | 63330698.641 | 2371373.7057 | 8.1126 | 4714.2828 | 7806.4785 | 96.107 | 159.1456
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.9648 | 21.1627 | 2.0348 | 4 | 4709.8063 | 7791.8547 | 96.0158 | 158.8475 | 77.1031 | 7.3176 | 63.2769 | 4106467.703 | 0 | 4523750.945 | 0 | 0 | 0 | 0 | 3365785.2727 | 8757082.8621 | 5976888.9934 | 26729975.7763 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38334488.522 | 63420180.0689 | 3162277.6602 | 8.1393 | 4709.8063 | 7791.8547 | 96.0158 | 158.8475
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.4586 | 21.2402 | 2.0398 | 4 | 4706.5473 | 7781.1471 | 95.9493 | 158.6292 | 77.0536 | 7.3071 | 68.0048 | 4114328.2308 | 0 | 4537290.1503 | 0 | 0 | 0 | 0 | 3374131.1686 | 8778797.1713 | 5991709.4556 | 26796256.1766 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38400768.9224 | 63486460.4693 | 4216965.0343 | 8.159 | 4706.5473 | 7781.1471 | 95.9493 | 158.6292
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8265 | 21.2979 | 2.0434 | 4 | 4704.1562 | 7773.2558 | 95.9006 | 158.4683 | 77.0166 | 7.2994 | 72.5582 | 4120159.721 | 0 | 4547367.4106 | 0 | 0 | 0 | 0 | 3380335.5813 | 8794939.7804 | 6002727.1181 | 26845529.6114 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38450042.3572 | 63535733.9041 | 5623413.2519 | 8.1736 | 4704.1562 | 7773.2558 | 95.9006 | 158.4683
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1043 | 21.3414 | 2.0462 | 4 | 4702.3797 | 7767.359 | 95.8644 | 158.3481 | 76.9886 | 7.2935 | 68.9951 | 4124546.2058 | 0 | 4554975.117 | 0 | 0 | 0 | 0 | 3385013.3159 | 8807110.2863 | 6011033.7384 | 26882678.6634 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38487191.4092 | 63572882.9561 | 7498942.0933 | 8.1846 | 4702.3797 | 7767.359 | 95.8644 | 158.3481
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3212 | 21.3755 | 2.0483 | 4 | 4701.0304 | 7762.8292 | 95.8369 | 158.2558 | 76.9665 | 7.2888 | 69.6654 | 4127948.56 | 0 | 4560911.751 | 0 | 0 | 0 | 0 | 3388655.5213 | 8816586.5576 | 6017501.4883 | 26911603.8783 | 961560.8286 | 10642951.9172 | 10642951.9172 | 9533441.692 | 4909297.9377 | 0 | 38516116.6241 | 63601808.171 | 10000000 | 8.1931 | 4701.0304 | 7762.8292 | 95.8369 | 158.2558
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.044217 | 0.0026009 | 4 | 1228468.8129 | 3721065.7243 | 25043.9984 | 75858.9579 | 59.9533 | 7.7096 | 43.5585 | 98614.9357 | 0 | 58018.2726 | 0 | 0 | 0 | 81720.7435 | 92958.0412 | 241857.7549 | 165072.8874 | 738242.6354 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 12780395.3384 | 38712167.976 | 100 | 0.010404 | 1228468.8129 | 3721065.7243 | 25043.9984 | 75858.9579
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3791 | 0.094451 | 0.0054317 | 4 | 601605.2059 | 1795148.4447 | 12264.5359 | 36596.5292 | 65.2231 | 8.08 | 120.1073 | 138324.5633 | 0 | 86923.8502 | 0 | 0 | 0 | 106901.1937 | 129538.3468 | 337032.2063 | 230031.4061 | 1028751.5664 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13070904.2693 | 39002676.9069 | 133.3521 | 0.021727 | 601605.2059 | 1795148.4447 | 12264.5359 | 36596.5292
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.16174 | 0.009654 | 4 | 346790.6355 | 1018319.146 | 7069.7962 | 20759.8132 | 69.3116 | 8.3363 | 172.2171 | 182974.8534 | 0 | 120141.6371 | 0 | 0 | 0 | 132601.3887 | 169929.9729 | 442122.932 | 301757.9858 | 1349528.7698 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13391681.4728 | 39323454.1104 | 177.8279 | 0.038616 | 346790.6355 | 1018319.146 | 7069.7962 | 20759.8132
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.25504 | 0.01569 | 4 | 219645.0121 | 632840.8683 | 4477.7607 | 12901.3171 | 72.7883 | 8.5332 | 242.3527 | 237477.667 | 0 | 161667.0361 | 0 | 0 | 0 | 163468.5757 | 219419.1787 | 570883.694 | 389639.8517 | 1742556.0033 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 13784708.7062 | 39716481.3438 | 237.1374 | 0.062759 | 219645.0121 | 632840.8683 | 4477.7607 | 12901.3171
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.37875 | 0.024062 | 4 | 148013.7889 | 417438.19 | 3017.4613 | 8510.0421 | 75.6111 | 8.6797 | 45.3436 | 301621.0787 | 0 | 211792.4472 | 0 | 0 | 0 | 198183.1627 | 277522.7085 | 722057.1598 | 492818.8484 | 2203995.4053 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 14246148.1082 | 40177920.7458 | 316.2278 | 0.096249 | 148013.7889 | 417438.19 | 3017.4613 | 8510.0421
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3749 | 0.54055 | 0.035462 | 4 | 104253.3341 | 287065.0217 | 2125.3452 | 5852.2088 | 77.8873 | 8.7896 | 42.6907 | 377084.6798 | 0 | 272305.6178 | 0 | 0 | 0 | 237248.6 | 345789.17 | 899672.4893 | 614044.9604 | 2746145.5173 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 14788298.2203 | 40720070.8579 | 421.6965 | 0.14185 | 104253.3341 | 287065.0217 | 2125.3452 | 5852.2088
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7165 | 0.75079 | 0.050795 | 4 | 75932.4336 | 203562.1966 | 1547.9854 | 4149.8907 | 79.7138 | 8.8726 | 61.254 | 466108.6725 | 0 | 345561.5531 | 0 | 0 | 0 | 281483.3318 | 426329.8874 | 1109222.9147 | 757067.4315 | 3385773.7911 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 15427926.494 | 41359699.1316 | 562.3413 | 0.20318 | 75932.4336 | 203562.1966 | 1547.9854 | 4149.8907
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4339 | 1.0224 | 0.071233 | 4 | 56798.5332 | 147809.4571 | 1157.9149 | 3013.2957 | 81.1686 | 8.9351 | 63.7199 | 571209.8127 | 0 | 434294.9871 | 0 | 0 | 0 | 331638.5786 | 521485.9176 | 1356799.386 | 926043.4604 | 4141472.1424 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 16183624.8453 | 42115397.4829 | 749.8942 | 0.28493 | 56798.5332 | 147809.4571 | 1157.9149 | 3013.2957
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6265 | 1.3715 | 0.098278 | 4 | 43436.3018 | 109401.7824 | 885.5078 | 2230.3033 | 82.3171 | 8.9816 | 58.7053 | 695133.164 | 0 | 541607.1437 | 0 | 0 | 0 | 388294.9369 | 633763.7454 | 1648923.2626 | 1125424.0087 | 5033146.2612 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 17075298.9641 | 43007071.6017 | 1000 | 0.39311 | 43436.3018 | 109401.7824 | 885.5078 | 2230.3033
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4038 | 1.8158 | 0.13379 | 4 | 33857.5253 | 82313.344 | 690.2314 | 1678.0689 | 83.2112 | 9.0146 | 63.4981 | 840323.8557 | 0 | 670521.1304 | 0 | 0 | 0 | 451264.2866 | 765222.6163 | 1990952.279 | 1358865.8404 | 6077150.0084 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 18119302.7113 | 44051075.3489 | 1333.5214 | 0.53516 | 33857.5253 | 82313.344 | 690.2314 | 1678.0689
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9212 | 2.3806 | 0.18015 | 4 | 26844.8298 | 62831.0603 | 547.2682 | 1280.8962 | 83.9005 | 9.0362 | 61.6752 | 1010646.9806 | 0 | 825550.1506 | 0 | 0 | 0 | 521473.0516 | 919491.3713 | 2392327.9345 | 1632812.9727 | 7302302.4612 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 19344455.1642 | 45276227.8018 | 1778.2794 | 0.7206 | 26844.8298 | 62831.0603 | 547.2682 | 1280.8962
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.3233 | 3.0899 | 0.24009 | 4 | 21621.9432 | 48624.626 | 440.7926 | 991.2788 | 84.416 | 9.0466 | 70.04 | 1208353.2714 | 0 | 1010034.027 | 0 | 0 | 0 | 597745.4469 | 1098291.7707 | 2857529.8968 | 1950322.8709 | 8722277.2838 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 20764429.9868 | 46696202.6244 | 2371.3737 | 0.96034 | 21621.9432 | 48624.626 | 440.7926 | 991.2788
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.8823 | 3.9876 | 0.31735 | 4 | 17665.4992 | 38093.8865 | 360.1351 | 776.5954 | 84.7874 | 9.0447 | 60.0748 | 1440050.4141 | 0 | 1228950.9217 | 0 | 0 | 0 | 683133.8668 | 1307332.729 | 3401411.5901 | 2321533.3022 | 10382412.8239 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 22424565.5268 | 48356338.1644 | 3162.2777 | 1.2694 | 17665.4992 | 38093.8865 | 360.1351 | 776.5954
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.5519 | 5.0699 | 0.41419 | 4 | 14636.865 | 30288.9539 | 298.3923 | 617.4813 | 85.0158 | 9.0286 | 55.3196 | 1698311.0589 | 0 | 1476363.9866 | 0 | 0 | 0 | 766764.119 | 1537161.2742 | 3999378.3202 | 2729657.8826 | 12207636.6415 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 24249789.3444 | 50181561.982 | 4216.965 | 1.6568 | 14636.865 | 30288.9539 | 298.3923 | 617.4813
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.4714 | 6.3606 | 0.53321 | 4 | 12308.4809 | 24466.7595 | 250.925 | 498.788 | 85.1135 | 8.9952 | 61.4085 | 1983631.9893 | 0 | 1757318.5622 | 0 | 0 | 0 | 846978.2186 | 1789292.2203 | 4655371.323 | 3177386.5862 | 14209978.8996 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 26252131.6025 | 52183904.2402 | 5623.4133 | 2.1328 | 12308.4809 | 24466.7595 | 250.925 | 498.788
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.5823 | 7.8526 | 0.67497 | 4 | 10509.8409 | 20114.6195 | 214.2573 | 410.0637 | 85.0779 | 8.9409 | 71.3923 | 2289207.4926 | 0 | 2067252.9377 | 0 | 0 | 0 | 916979.8206 | 2056641.6979 | 5350959.8227 | 3652140.0302 | 16333181.8019 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 28375334.5048 | 54307107.1424 | 7498.9421 | 2.6999 | 10509.8409 | 20114.6195 | 214.2573 | 410.0637
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.5675 | 9.4967 | 0.83632 | 4 | 9119.4998 | 16871.2171 | 185.9133 | 343.9426 | 84.9043 | 8.8633 | 82.4616 | 2601017.9787 | 0 | 2394085.6615 | 0 | 0 | 0 | 966711.7706 | 2325108.0102 | 6049454.0973 | 4128876.7252 | 18465254.2435 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 30507406.9464 | 56439179.584 | 10000 | 3.3453 | 9119.4998 | 16871.2171 | 185.9133 | 343.9426
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.8381 | 11.1978 | 1.0095 | 4 | 8047.8803 | 14469.6803 | 164.0669 | 294.984 | 84.6001 | 8.7644 | 80.8618 | 2899755.0203 | 0 | 2718980.7152 | 0 | 0 | 0 | 985783.2292 | 2575762.3962 | 6701605.3934 | 4573983.3852 | 20455870.1395 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 32498022.8424 | 58429795.4801 | 13335.2143 | 4.0381 | 8047.8803 | 14469.6803 | 164.0669 | 294.984
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.8381 | 12.8629 | 1.1849 | 4 | 7225.7038 | 12697.128 | 147.3057 | 258.8481 | 84.1905 | 8.6496 | 82.4898 | 3171026.7244 | 0 | 3026219.081 | 0 | 0 | 0 | 971690.933 | 2795885.328 | 7274320.1084 | 4964872.9463 | 22204015.121 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 34246167.824 | 60177940.4616 | 17782.7941 | 4.7395 | 7225.7038 | 12697.128 | 147.3057 | 258.8481
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9897 | 14.3948 | 1.3518 | 4 | 6597.6394 | 11393.5663 | 134.5018 | 232.2733 | 83.7214 | 8.5285 | 91.2875 | 3403221.1373 | 0 | 3300684.8179 | 0 | 0 | 0 | 925935.3742 | 2975638.1184 | 7741999.9969 | 5284074.0801 | 23631553.5247 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 35673706.2277 | 61605478.8653 | 23713.7371 | 5.407 | 6597.6394 | 11393.5663 | 134.5018 | 232.2733
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.948 | 15.7333 | 1.5022 | 4 | 6119.2857 | 10434.816 | 124.7499 | 212.7278 | 83.2418 | 8.4109 | 101.4558 | 3593008.7909 | 0 | 3534789.1117 | 0 | 0 | 0 | 856140.5865 | 3113736.0107 | 8101302.3848 | 5529305.3428 | 24728282.2274 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 36770434.9303 | 62702207.568 | 31622.7766 | 6.0089 | 6119.2857 | 10434.816 | 124.7499 | 212.7278
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.6159 | 16.8594 | 1.6322 | 4 | 5755.4555 | 9727.4191 | 117.3327 | 198.3066 | 82.7891 | 8.3036 | 99.7755 | 3743436.0737 | 0 | 3727977.9413 | 0 | 0 | 0 | 772505.7376 | 3215128.7035 | 8365105.373 | 5709356.3028 | 25533510.132 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37575662.835 | 63507435.4726 | 42169.6503 | 6.5287 | 5755.4555 | 9727.4191 | 117.3327 | 198.3066
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9897 | 17.7707 | 1.7401 | 4 | 5478.7367 | 9204.3667 | 111.6915 | 187.6435 | 82.3905 | 8.2112 | 94.0637 | 3858983.5436 | 0 | 3881866.8823 | 0 | 0 | 0 | 683353.3097 | 3285439.4569 | 8548039.5305 | 5834212.6242 | 26091895.3472 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38134048.0502 | 64065820.6878 | 56234.1325 | 6.9604 | 5478.7367 | 9204.3667 | 111.6915 | 187.6435
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.1749 | 18.4835 | 1.8269 | 4 | 5268.0851 | 8816.7181 | 107.397 | 179.7407 | 82.059 | 8.1356 | 99.8715 | 3945442.0096 | 0 | 4000666.1906 | 0 | 0 | 0 | 595195.3291 | 3331108.3764 | 8666860.6912 | 5915310.5079 | 26454583.1049 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38496735.8078 | 64428508.4454 | 74989.4209 | 7.3075 | 5268.0851 | 8816.7181 | 107.397 | 179.7407
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4 | 19.0351 | 1.8955 | 4 | 5107.1376 | 8527.2731 | 104.1159 | 173.84 | 81.7898 | 8.0747 | 90.8349 | 4009871.998 | 0 | 4091614.4808 | 0 | 0 | 0 | 512796.9718 | 3359570.5457 | 8740913.4174 | 5965853.0152 | 26680620.4289 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38722773.1318 | 64654545.7695 | 100000 | 7.5821 | 5107.1376 | 8527.2731 | 104.1159 | 173.84
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.7534 | 19.4397 | 1.9479 | 4 | 4984.6677 | 8312.8041 | 101.6192 | 169.4678 | 81.5875 | 8.0296 | 81.017 | 4055784.6698 | 0 | 4157660.5201 | 0 | 0 | 0 | 438342.6876 | 3374197.2723 | 8778969.1594 | 5991826.841 | 26796781.1503 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38838933.8532 | 64770706.4908 | 133352.1432 | 7.7917 | 4984.6677 | 8312.8041 | 101.6192 | 169.4678
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3929 | 19.7243 | 1.987 | 4 | 4890.9887 | 8153.7243 | 99.7094 | 166.2247 | 81.4427 | 7.9976 | 74.8833 | 4087168.3742 | 0 | 4203519.203 | 0 | 0 | 0 | 372068.2571 | 3378474.7754 | 8790098.345 | 5999422.7389 | 26830751.6936 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38872904.3965 | 64804677.0341 | 177827.941 | 7.9479 | 4890.9887 | 8153.7243 | 99.7094 | 166.2247
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.477 | 19.9152 | 2.0154 | 4 | 4819.2195 | 8035.9404 | 98.2463 | 163.8235 | 81.3451 | 7.9761 | 86.1274 | 4107635.7713 | 0 | 4233772.1792 | 0 | 0 | 0 | 314082.9995 | 3375641.4705 | 8782726.6669 | 5994391.4172 | 26808250.5046 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38850403.2075 | 64782175.8451 | 237137.3706 | 8.0616 | 4819.2195 | 8035.9404 | 98.2463 | 163.8235
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1024 | 20.0289 | 2.0352 | 4 | 4764.1434 | 7949.5696 | 97.1235 | 162.0627 | 81.2877 | 7.9636 | 92.1419 | 4119323.8268 | 0 | 4251200.3284 | 0 | 0 | 0 | 263437.8727 | 3367245.1909 | 8760881.2697 | 5979481.4847 | 26741569.9732 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38783722.6762 | 64715495.3138 | 316227.766 | 8.1408 | 4764.1434 | 7949.5696 | 97.1235 | 162.0627
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.3607 | 20.0807 | 2.0481 | 4 | 4721.7934 | 7887.0885 | 96.2601 | 160.789 | 81.2633 | 7.9584 | 86.6124 | 4124100.5671 | 0 | 4258395.6092 | 0 | 0 | 0 | 219084.9527 | 3354616.6403 | 8728024.3716 | 5957055.9766 | 26641278.1176 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38683430.8206 | 64615203.4582 | 421696.5034 | 8.1925 | 4721.7934 | 7887.0885 | 96.2601 | 160.789
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.2339 | 20.0687 | 2.0547 | 4 | 4689.1358 | 7844.2576 | 95.5944 | 159.9158 | 81.2737 | 7.9609 | 93.6889 | 4121672.711 | 0 | 4254862.8228 | 0 | 0 | 0 | 178656.005 | 3336524.7001 | 8680952.8544 | 5924928.6989 | 26497597.7921 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38539750.495 | 64471523.1327 | 562341.3252 | 8.2189 | 4689.1358 | 7844.2576 | 95.5944 | 159.9158
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.6297 | 19.9785 | 2.0546 | 4 | 4663.8047 | 7819.1822 | 95.078 | 159.4046 | 81.3269 | 7.9728 | 83.927 | 4110277.7449 | 0 | 4238029.952 | 0 | 0 | 0 | 138661.2689 | 3309917.8967 | 8611727.4096 | 5877680.9104 | 26286295.1825 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 38328447.8854 | 64260220.523 | 749894.2093 | 8.2183 | 4663.8047 | 7819.1822 | 95.078 | 159.4046
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.983 | 19.0812 | 1.999 | 4 | 4636.0266 | 7879.0447 | 94.5117 | 160.625 | 81.8115 | 8.0816 | 82.9351 | 4000945.843 | 0 | 4079882.384 | 0 | 0 | 0 | 0 | 3151523.0085 | 8199616.4019 | 5596406.6796 | 25028374.3169 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37070527.0198 | 63002299.6575 | 1000000 | 7.9962 | 4636.0266 | 7879.0447 | 94.5117 | 160.625
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.4491 | 19.3191 | 2.0182 | 4 | 4618.9544 | 7831.2175 | 94.1636 | 159.65 | 81.6881 | 8.0538 | 80.2717 | 4029832.0477 | 0 | 4121091.05 | 0 | 0 | 0 | 0 | 3178860.0081 | 8270741.6672 | 5644951.1346 | 25245475.9075 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37287628.6105 | 63219401.2481 | 1333521.4322 | 8.0727 | 4618.9544 | 7831.2175 | 94.1636 | 159.65
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5675 | 19.5004 | 2.0326 | 4 | 4606.4262 | 7795.8998 | 93.9082 | 158.93 | 81.5923 | 8.0323 | 86.4728 | 4051603.838 | 0 | 4152453.5658 | 0 | 0 | 0 | 0 | 3199582.3875 | 8324657.0476 | 5681749.4896 | 25410046.3285 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37452199.0315 | 63383971.6691 | 1778279.41 | 8.1304 | 4606.4262 | 7795.8998 | 93.9082 | 158.93
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4176 | 19.6382 | 2.0435 | 4 | 4597.1846 | 7769.712 | 93.7198 | 158.3961 | 81.5186 | 8.0157 | 76.6687 | 4068002.4063 | 0 | 4176255.9363 | 0 | 0 | 0 | 0 | 3215260.7536 | 8365448.9402 | 5709590.7945 | 25534558.8309 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37576711.5338 | 63508484.1715 | 2371373.7057 | 8.1739 | 4597.1846 | 7769.712 | 93.7198 | 158.3961
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.0633 | 19.7428 | 2.0516 | 4 | 4590.3299 | 7750.2043 | 93.5801 | 157.9984 | 81.462 | 8.003 | 76.3361 | 4080366.4908 | 0 | 4194310.3576 | 0 | 0 | 0 | 0 | 3227123.9708 | 8396314.598 | 5730657.2401 | 25628772.6573 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37670925.3603 | 63602697.9979 | 3162277.6602 | 8.2066 | 4590.3299 | 7750.2043 | 93.5801 | 157.9984
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.536 | 19.8193 | 2.0576 | 4 | 4585.3677 | 7736.0688 | 93.4789 | 157.7102 | 81.4206 | 7.9938 | 85.4596 | 4089387.3786 | 0 | 4207514.8543 | 0 | 0 | 0 | 0 | 3235791.8708 | 8418866.6957 | 5746049.5102 | 25697610.3097 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37739763.0127 | 63671535.6503 | 4216965.0343 | 8.2305 | 4585.3677 | 7736.0688 | 93.4789 | 157.7102
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9064 | 19.8793 | 2.0623 | 4 | 4581.5593 | 7725.1634 | 93.4013 | 157.4879 | 81.3877 | 7.9865 | 78.4084 | 4096411.6727 | 0 | 4217856.354 | 0 | 0 | 0 | 0 | 3242564.5304 | 8436487.7668 | 5758076.2533 | 25751396.5773 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37793549.2802 | 63725321.9178 | 5623413.2519 | 8.2491 | 4581.5593 | 7725.1634 | 93.4013 | 157.4879
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.1692 | 19.9218 | 2.0656 | 4 | 4578.8513 | 7717.4281 | 93.3461 | 157.3302 | 81.3645 | 7.9813 | 72.3028 | 4101399.4267 | 0 | 4225190.1095 | 0 | 0 | 0 | 0 | 3247369.9191 | 8448990.4024 | 5766609.559 | 25789559.4167 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37831712.1196 | 63763484.7572 | 7498942.0933 | 8.2623 | 4578.8513 | 7717.4281 | 93.3461 | 157.3302
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.3713 | 19.9545 | 2.0681 | 4 | 4576.7941 | 7711.5338 | 93.3041 | 157.21 | 81.3466 | 7.9773 | 82.2078 | 4105219.9202 | 0 | 4230826.0334 | 0 | 0 | 0 | 0 | 3251057.9219 | 8458585.829 | 5773158.6349 | 25818848.3393 | 961560.8286 | 11080591.8743 | 11080591.8743 | 9793800.0038 | 5057380.7595 | 0 | 37861001.0422 | 63792773.6799 | 10000000 | 8.2724 | 4576.7941 | 7711.5338 | 93.3041 | 157.21
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.046989 | 0.0027903 | 4 | 1190157.2907 | 3590620.9973 | 24262.9662 | 73199.6657 | 61.7685 | 8.1426 | 38.8337 | 106432.34 | 0 | 61493.5502 | 0 | 0 | 0 | 89630.4556 | 100446.9749 | 261342.4241 | 178371.5745 | 797717.3192 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13283370.0702 | 40074995.0121 | 100 | 0.011161 | 1190157.2907 | 3590620.9973 | 24262.9662 | 73199.6657
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.098855 | 0.0059001 | 4 | 575468.2879 | 1710683.6457 | 11731.6994 | 34874.6 | 67.1406 | 8.514 | 131.6362 | 147565.8383 | 0 | 90851.0762 | 0 | 0 | 0 | 115339.6678 | 137965.0671 | 358956.8041 | 244995.3946 | 1095673.8481 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13581326.599 | 40372951.5409 | 133.3521 | 0.0236 | 575468.2879 | 1710683.6457 | 11731.6994 | 34874.6
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9626 | 0.17213 | 0.010568 | 4 | 329723.9976 | 963536.0491 | 6721.8697 | 19642.9856 | 71.6057 | 8.7883 | 184.2325 | 196986.8183 | 0 | 126893.5884 | 0 | 0 | 0 | 144916.6158 | 182830.8388 | 475688.3388 | 324667.0656 | 1451983.2657 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 13937636.0167 | 40729260.9585 | 177.8279 | 0.042271 | 329723.9976 | 963536.0491 | 6721.8697 | 19642.9856
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6238 | 0.27028 | 0.017228 | 4 | 208231.1183 | 597014.4436 | 4245.073 | 12170.947 | 75.2228 | 8.989 | 256.1925 | 254554.5154 | 0 | 169874.2127 | 0 | 0 | 0 | 177348.5227 | 234693.1278 | 610623.3764 | 416763.0014 | 1863856.7564 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 14349509.5074 | 41141134.4493 | 237.1374 | 0.068911 | 208231.1183 | 597014.4436 | 4245.073 | 12170.947
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4929 | 0.40357 | 0.026496 | 4 | 140120.0406 | 392906.5948 | 2856.5366 | 8009.9324 | 78.2493 | 9.143 | 39.4908 | 324288.7456 | 0 | 223258.5606 | 0 | 0 | 0 | 216030.151 | 297795.2083 | 774802.0458 | 528818.3169 | 2364993.0282 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 14850645.7792 | 41642270.7211 | 316.2278 | 0.10599 | 140120.0406 | 392906.5948 | 2856.5366 | 8009.9324
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.577 | 0.57457 | 0.039085 | 4 | 98643.4189 | 270010.8612 | 2010.9795 | 5504.5366 | 80.6329 | 9.2558 | 55.0518 | 404409.1659 | 0 | 286182.8469 | 0 | 0 | 0 | 257435.5583 | 369730.7527 | 961963.5764 | 656559.9072 | 2936281.8074 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 15421934.5584 | 42213559.5002 | 421.6965 | 0.15634 | 98643.4189 | 270010.8612 | 2010.9795 | 5504.5366
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9944 | 0.80086 | 0.056066 | 4 | 71853.5391 | 191318.0212 | 1464.8316 | 3900.2766 | 82.5874 | 9.3429 | 57.1829 | 500948.5392 | 0 | 363973.3965 | 0 | 0 | 0 | 306611.0672 | 456897.8711 | 1188754.538 | 811349.3986 | 3628534.8105 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 16114187.5615 | 42905812.5034 | 562.3413 | 0.22426 | 71853.5391 | 191318.0212 | 1464.8316 | 3900.2766
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7971 | 1.0918 | 0.078683 | 4 | 53776.3213 | 138901.8646 | 1096.303 | 2831.7024 | 84.1308 | 9.4078 | 57.5138 | 614165.7243 | 0 | 457575.2462 | 0 | 0 | 0 | 361596.113 | 559001.4626 | 1454407.1387 | 992662.7573 | 4439408.4422 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 16925061.1931 | 43716686.135 | 749.8942 | 0.31473 | 53776.3213 | 138901.8646 | 1096.303 | 2831.7024
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0823 | 1.4633 | 0.10856 | 4 | 41160.4424 | 102858.6865 | 839.1113 | 2096.9135 | 85.3414 | 9.4555 | 50.7925 | 746745.0862 | 0 | 569985.3317 | 0 | 0 | 0 | 422781.8384 | 678409.7799 | 1765083.0864 | 1204705.4753 | 5387710.5978 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 17873363.3488 | 44664988.2907 | 1000 | 0.43424 | 41160.4424 | 102858.6865 | 839.1113 | 2096.9135
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9936 | 1.9387 | 0.14783 | 4 | 32119.1021 | 77428.6364 | 654.7913 | 1578.4875 | 86.2902 | 9.4896 | 44.89 | 903004.185 | 0 | 705816.2116 | 0 | 0 | 0 | 491892.7194 | 819278.1152 | 2131593.5988 | 1454856.431 | 6506441.261 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 18992094.0119 | 45783718.9538 | 1333.5214 | 0.5913 | 32119.1021 | 77428.6364 | 654.7913 | 1578.4875
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7519 | 2.5538 | 0.19951 | 4 | 25465.6949 | 59038.2712 | 519.1526 | 1203.575 | 87.0319 | 9.5117 | 47.3451 | 1089721.7524 | 0 | 867728.1155 | 0 | 0 | 0 | 572698.0222 | 986757.6771 | 2567341.064 | 1752263.0298 | 7836509.6609 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 20322162.4118 | 47113787.3537 | 1778.2794 | 0.79802 | 25465.6949 | 59038.2712 | 519.1526 | 1203.575
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3781 | 3.3148 | 0.26608 | 4 | 20503.5367 | 45676.4072 | 417.9923 | 931.1753 | 87.574 | 9.5211 | 55.5622 | 1302757.4666 | 0 | 1054647.6516 | 0 | 0 | 0 | 656999.1371 | 1175617.6596 | 3058715.9979 | 2087636.5189 | 9336374.4318 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 21822027.1827 | 48613652.1246 | 2371.3737 | 1.0643 | 20503.5367 | 45676.4072 | 417.9923 | 931.1753
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.066 | 4.2544 | 0.35089 | 4 | 16762.6528 | 35850.8448 | 341.7294 | 730.868 | 87.9554 | 9.5175 | 61.4176 | 1546051.8428 | 0 | 1273714.0864 | 0 | 0 | 0 | 745300.174 | 1390375.7803 | 3617472.5749 | 2468999.364 | 11041913.8224 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 23527566.5734 | 50319191.5152 | 3162.2777 | 1.4036 | 16762.6528 | 35850.8448 | 341.7294 | 730.868
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0038 | 5.4045 | 0.4575 | 4 | 13909.9782 | 28550.1885 | 283.5737 | 582.0342 | 88.1944 | 9.4985 | 78.1864 | 1821983.0223 | 0 | 1528813.0214 | 0 | 0 | 0 | 836670.4431 | 1633111.9299 | 4249022.2442 | 2900044.9903 | 12969645.6511 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 25455298.4021 | 52246923.3439 | 4216.965 | 1.83 | 13909.9782 | 28550.1885 | 283.5737 | 582.0342
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.2204 | 6.7728 | 0.58814 | 4 | 11716.6555 | 23104.9292 | 238.8599 | 471.0252 | 88.294 | 9.4604 | 69.719 | 2126055.9738 | 0 | 1817815.7942 | 0 | 0 | 0 | 924477.0689 | 1898656.0464 | 4939913.5648 | 3371592.513 | 15078510.9611 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 27564163.712 | 54355788.6539 | 5623.4133 | 2.3526 | 11716.6555 | 23104.9292 | 238.8599 | 471.0252
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.624 | 8.3467 | 0.74298 | 4 | 10022.7945 | 19037.6796 | 204.3282 | 388.1088 | 88.2513 | 9.3996 | 75.5938 | 2450021.1543 | 0 | 2135075.8483 | 0 | 0 | 0 | 1000951.9827 | 2178559.1042 | 5668163.9053 | 3868638.3345 | 17301410.3292 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 29787063.0802 | 56578688.022 | 7498.9421 | 2.9719 | 10022.7945 | 19037.6796 | 204.3282 | 388.1088
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.8332 | 10.0653 | 0.91787 | 4 | 8714.3965 | 16011.6205 | 177.6548 | 326.4185 | 88.0628 | 9.3142 | 73.2492 | 2777519.7003 | 0 | 2466663.8778 | 0 | 0 | 0 | 1054653.3167 | 2456546.3889 | 6391429.7971 | 4362282.1673 | 19509095.248 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 31994747.999 | 58786372.9409 | 10000 | 3.6715 | 8714.3965 | 16011.6205 | 177.6548 | 326.4185
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.3077 | 11.8388 | 1.1046 | 4 | 7707.0129 | 13770.6605 | 157.1179 | 280.7335 | 87.7373 | 9.206 | 79.5063 | 3090503.0792 | 0 | 2795631.2425 | 0 | 0 | 0 | 1077137.4614 | 2715675.9954 | 7065631.8783 | 4822438.9411 | 21567018.5979 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 34052671.3489 | 60844296.2907 | 13335.2143 | 4.4184 | 7707.0129 | 13770.6605 | 157.1179 | 280.7335
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.3855 | 13.5551 | 1.2918 | 4 | 6935.0503 | 12119.9982 | 141.3804 | 247.0826 | 87.3068 | 9.0824 | 90.0543 | 3371404.397 | 0 | 3103222.0314 | 0 | 0 | 0 | 1064016.4008 | 2940070.7034 | 7649460.8788 | 5220914.2305 | 23349088.6418 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 35834741.3928 | 62626366.3347 | 17782.7941 | 5.1672 | 6935.0503 | 12119.9982 | 141.3804 | 247.0826
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.565 | 15.1265 | 1.4688 | 4 | 6346.0713 | 10906.1143 | 129.3732 | 222.3359 | 86.8187 | 8.9533 | 95.0554 | 3610841.4534 | 0 | 3376880.8154 | 0 | 0 | 0 | 1019186.2623 | 3122694.3272 | 8124610.0866 | 5545213.3281 | 24799426.2731 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 37285079.024 | 64076703.9659 | 23713.7371 | 5.8753 | 6346.0713 | 10906.1143 | 129.3732 | 222.3359
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5233 | 16.4955 | 1.6276 | 4 | 5898.0694 | 10013.2023 | 120.2401 | 204.1327 | 86.3229 | 8.8287 | 93.0758 | 3806078.746 | 0 | 3609708.3759 | 0 | 0 | 0 | 950916.5745 | 3263014.4416 | 8489694.2407 | 5794390.765 | 25913803.1437 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 38399455.8946 | 65191080.8365 | 31622.7766 | 6.5105 | 5898.0694 | 10013.2023 | 120.2401 | 204.1327
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.1586 | 17.6417 | 1.764 | 4 | 5557.8384 | 9354.7823 | 113.3041 | 190.7099 | 85.8585 | 8.7158 | 95.8699 | 3960183.6068 | 0 | 3800988.8449 | 0 | 0 | 0 | 869384.4396 | 3365917.1876 | 8757426.0776 | 5977123.2451 | 26731023.4017 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 39216676.1526 | 66008301.0945 | 42169.6503 | 7.0561 | 5557.8384 | 9354.7823 | 113.3041 | 190.7099
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.5307 | 18.5731 | 1.8772 | 4 | 5299.5648 | 8867.504 | 108.0388 | 180.7761 | 85.4487 | 8.6184 | 93.2195 | 4079175.4556 | 0 | 3954101.5266 | 0 | 0 | 0 | 783803.5785 | 3438661.4187 | 8946691.6449 | 6106300.8838 | 27308734.5081 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 39794387.259 | 66586012.2009 | 56234.1325 | 7.509 | 5299.5648 | 8867.504 | 108.0388 | 180.7761
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7371 | 19.3052 | 1.9683 | 4 | 5103.459 | 8506.2846 | 104.0409 | 173.4121 | 85.1063 | 8.5384 | 97.2309 | 4168724.8931 | 0 | 4072962.0139 | 0 | 0 | 0 | 700315.1323 | 3487380.7953 | 9073449.4693 | 6192815.7036 | 27695648.0076 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40181300.7586 | 66972925.7004 | 74989.4209 | 7.8733 | 5103.459 | 8506.2846 | 104.0409 | 173.4121
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.9554 | 19.8676 | 2.04 | 4 | 4954.4853 | 8237.8191 | 101.0039 | 167.9391 | 84.8316 | 8.4749 | 102.73 | 4235074.7316 | 0 | 4163319.1717 | 0 | 0 | 0 | 623268.5763 | 3518448.367 | 9154280.918 | 6247984.8282 | 27942376.5927 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40428029.3437 | 67219654.2856 | 100000 | 8.1599 | 4954.4853 | 8237.8191 | 101.0039 | 167.9391
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.146 | 20.2556 | 2.0932 | 4 | 4840.906 | 8040.7438 | 98.6884 | 163.9214 | 84.6365 | 8.43 | 86.6373 | 4279045.6679 | 0 | 4224541.5513 | 0 | 0 | 0 | 551635.331 | 3531536.7946 | 9188334.3216 | 6271226.9759 | 28046320.6422 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40531973.3932 | 67323598.3351 | 133352.1432 | 8.3728 | 4840.906 | 8040.7438 | 98.6884 | 163.9214
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.2427 | 20.6205 | 2.1384 | 4 | 4754.9455 | 7887.1698 | 96.936 | 160.7906 | 84.4472 | 8.387 | 94.6841 | 4320456.4459 | 0 | 4282934.2336 | 0 | 0 | 0 | 496926.9362 | 3549123.8702 | 9234092.2848 | 6302457.726 | 28185991.4967 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40671644.2477 | 67463269.1896 | 177827.941 | 8.5535 | 4754.9455 | 7887.1698 | 96.936 | 160.7906
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5534 | 20.8524 | 2.1703 | 4 | 4689.629 | 7775.843 | 95.6044 | 158.5211 | 84.3261 | 8.3596 | 86.6266 | 4345910.4299 | 0 | 4319332.7248 | 0 | 0 | 0 | 447773.1673 | 3554076.3656 | 9246977.6619 | 6311252.2606 | 28225322.6101 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40710975.3611 | 67502600.3029 | 237137.3706 | 8.6811 | 4689.629 | 7775.843 | 95.6044 | 158.5211
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.5083 | 21.0221 | 2.1942 | 4 | 4640.0199 | 7692.5643 | 94.5931 | 156.8233 | 84.2366 | 8.3395 | 87.7455 | 4364252.6957 | 0 | 4345806.56 | 0 | 0 | 0 | 407358.8339 | 3555793.0549 | 9251444.1354 | 6314300.7206 | 28238956.0005 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40724608.7514 | 67516233.6933 | 316227.766 | 8.7768 | 4640.0199 | 7692.5643 | 94.5931 | 156.8233
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1781 | 21.1421 | 2.2119 | 4 | 4602.3763 | 7630.5411 | 93.8257 | 155.5589 | 84.1731 | 8.3252 | 88.6423 | 4377009.4085 | 0 | 4364349.0074 | 0 | 0 | 0 | 374386.7553 | 3555140.6168 | 9249746.6252 | 6313142.135 | 28233774.5481 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40719427.2991 | 67511052.2409 | 421696.5034 | 8.8475 | 4602.3763 | 7630.5411 | 93.8257 | 155.5589
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.6339 | 21.2246 | 2.2248 | 4 | 4573.8455 | 7584.4761 | 93.244 | 154.6198 | 84.1294 | 8.3155 | 80.3488 | 4385637.7104 | 0 | 4376957.4057 | 0 | 0 | 0 | 347745.325 | 3553032.772 | 9244262.4456 | 6309399.0697 | 28217034.7284 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40702687.4794 | 67494312.4212 | 562341.3252 | 8.899 | 4573.8455 | 7584.4761 | 93.244 | 154.6198
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.9675 | 21.2852 | 2.2344 | 4 | 4552.2498 | 7549.9052 | 92.8038 | 153.915 | 84.0974 | 8.3083 | 91.3322 | 4391925.7612 | 0 | 4386178.6203 | 0 | 0 | 0 | 326801.2917 | 3550913.2125 | 9238747.7866 | 6305635.2016 | 28200201.8739 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40685854.6249 | 67477479.5668 | 749894.2093 | 8.9375 | 4552.2498 | 7549.9052 | 92.8038 | 153.915
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.2038 | 21.3285 | 2.2415 | 4 | 4535.9255 | 7524.0694 | 92.471 | 153.3883 | 84.0745 | 8.3032 | 94.2146 | 4396366.0543 | 0 | 4392708.8036 | 0 | 0 | 0 | 310387.8122 | 3548790.4413 | 9233224.7713 | 6301865.6302 | 28183343.5129 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40668996.2639 | 67460621.2058 | 1000000 | 8.966 | 4535.9255 | 7524.0694 | 92.471 | 153.3883
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.3501 | 21.3559 | 2.2465 | 4 | 4523.6019 | 7505.042 | 92.2197 | 153.0004 | 84.0602 | 8.3001 | 87.4546 | 4399105.6149 | 0 | 4396750.7199 | 0 | 0 | 0 | 297376.1504 | 3546360.6693 | 9226903.0028 | 6297550.8933 | 28164047.0506 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40649699.8016 | 67441324.7435 | 1333521.4322 | 8.9861 | 4523.6019 | 7505.042 | 92.2197 | 153.0004
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4692 | 21.378 | 2.2504 | 4 | 4514.3099 | 7490.608 | 92.0303 | 152.7062 | 84.0486 | 8.2975 | 77.4018 | 4401334.0498 | 0 | 4400040.3923 | 0 | 0 | 0 | 287527.3764 | 3544671.7092 | 9222508.6752 | 6294551.6745 | 28150633.8774 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40636286.6284 | 67427911.5703 | 1778279.41 | 9.0017 | 4514.3099 | 7490.608 | 92.0303 | 152.7062
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5398 | 21.3915 | 2.2531 | 4 | 4507.3107 | 7480.0063 | 91.8876 | 152.49 | 84.0417 | 8.296 | 84.3322 | 4402650.1401 | 0 | 4401988.7817 | 0 | 0 | 0 | 279795.5151 | 3542929.4304 | 9217975.6232 | 6291457.7733 | 28136797.2639 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40622450.0148 | 67414074.9567 | 2371373.7057 | 9.0126 | 4507.3107 | 7480.0063 | 91.8876 | 152.49
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5935 | 21.4018 | 2.2552 | 4 | 4502.0437 | 7472.0302 | 91.7803 | 152.3274 | 84.0364 | 8.2948 | 79.9305 | 4403651.3723 | 0 | 4403471.8487 | 0 | 0 | 0 | 273934.8193 | 3541612.6357 | 9214549.5934 | 6289119.4376 | 28126339.707 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40611992.4579 | 67403617.3998 | 3162277.6602 | 9.0208 | 4502.0437 | 7472.0302 | 91.7803 | 152.3274
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.613 | 21.4062 | 2.2565 | 4 | 4498.0832 | 7466.3154 | 91.6995 | 152.2109 | 84.0344 | 8.2944 | 81.2093 | 4404009.713 | 0 | 4404008.7904 | 0 | 0 | 0 | 269247.1429 | 3540133.602 | 9210701.4512 | 6286493.0015 | 28114593.701 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40600246.452 | 67391871.3938 | 4216965.0343 | 9.0261 | 4498.0832 | 7466.3154 | 91.6995 | 152.2109
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.6519 | 21.4133 | 2.2578 | 4 | 4495.1069 | 7461.7026 | 91.6388 | 152.1169 | 84.0306 | 8.2935 | 85.3011 | 4404735.8986 | 0 | 4405082.6247 | 0 | 0 | 0 | 265999.7172 | 3539569.1138 | 9209232.7686 | 6285490.5954 | 28110110.7183 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40595763.4693 | 67387388.4112 | 5623413.2519 | 9.0311 | 4495.1069 | 7461.7026 | 91.6388 | 152.1169
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.6667 | 21.4164 | 2.2586 | 4 | 4492.8713 | 7458.4302 | 91.5933 | 152.0502 | 84.0291 | 8.2932 | 78.0671 | 4405010.2963 | 0 | 4405491.6872 | 0 | 0 | 0 | 263377.5965 | 3538813.0362 | 9207265.6099 | 6284147.9691 | 28104106.1952 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40589758.9462 | 67381383.888 | 7498942.0933 | 9.0343 | 4492.8713 | 7458.4302 | 91.5933 | 152.0502
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.6861 | 21.4201 | 2.2592 | 4 | 4491.1927 | 7455.8641 | 91.559 | 151.9979 | 84.0272 | 8.2928 | 76.7234 | 4405372.8516 | 0 | 4406028.5674 | 0 | 0 | 0 | 261503.6852 | 3538432.9906 | 9206276.8092 | 6283473.0924 | 28101087.9965 | 961560.8286 | 11524091.9223 | 11524091.9223 | 10059725.4019 | 5207807.6177 | 0 | 40586740.7474 | 67378365.6893 | 10000000 | 9.037 | 4491.1927 | 7455.8641 | 91.559 | 151.9979
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.068 | 0.048454 | 0.002991 | 4 | 1151694.5659 | 3464095.0911 | 23478.8515 | 70620.264 | 63.3138 | 8.5575 | 105.9027 | 112736.7854 | 0 | 63823.9647 | 0 | 0 | 0 | 95843.7412 | 106237.7516 | 276408.8374 | 188654.7111 | 843705.7915 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 13778718.6813 | 41443967.141 | 100 | 0.011964 | 1151694.5659 | 3464095.0911 | 23478.8515 | 70620.264
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.10542 | 0.0064124 | 4 | 550331.8823 | 1628912.0523 | 11219.2598 | 33207.5755 | 69.2629 | 8.9622 | 144.8115 | 158969.1691 | 0 | 96216.8496 | 0 | 0 | 0 | 126064.6583 | 148687.764 | 386855.0619 | 264036.5288 | 1180830.0318 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 14115842.9216 | 41781091.3813 | 133.3521 | 0.02565 | 550331.8823 | 1628912.0523 | 11219.2598 | 33207.5755
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.18285 | 0.011549 | 4 | 313692.34 | 912544.0904 | 6395.0427 | 18603.4456 | 73.9028 | 9.2415 | 196.8635 | 211381.8313 | 0 | 133739.8378 | 0 | 0 | 0 | 157478.9122 | 196014.2267 | 509988.8097 | 348077.8419 | 1556681.4594 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 14491694.3493 | 42156942.8089 | 177.8279 | 0.046197 | 313692.34 | 912544.0904 | 6395.0427 | 18603.4456
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7593 | 0.28833 | 0.018898 | 4 | 197604.7504 | 563593.1028 | 4028.4401 | 11489.6077 | 77.7442 | 9.4505 | 54.7924 | 273694.072 | 0 | 179392.7978 | 0 | 0 | 0 | 193302.6226 | 252091.902 | 655891.418 | 447659.37 | 2002032.1824 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 14937045.0723 | 42602293.5319 | 237.1374 | 0.075591 | 197604.7504 | 563593.1028 | 4028.4401 | 11489.6077
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.42882 | 0.029105 | 4 | 132817.6186 | 370449.98 | 2707.6668 | 7552.1239 | 80.8868 | 9.6072 | 48.2052 | 347387.0129 | 0 | 234732.7799 | 0 | 0 | 0 | 233978.6974 | 318278.4112 | 828095.1381 | 565191.9474 | 2527663.9871 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 15462676.8769 | 43127925.3366 | 316.2278 | 0.11642 | 132817.6186 | 370449.98 | 2707.6668 | 7552.1239
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8009 | 0.61267 | 0.043008 | 4 | 93470.9352 | 254286.6873 | 1905.5314 | 5183.9781 | 83.4243 | 9.7251 | 44.508 | 434081.9244 | 0 | 301505.7613 | 0 | 0 | 0 | 279782.4244 | 395994.3429 | 1030296.0507 | 703198.2251 | 3144858.7288 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 16079871.6187 | 43745120.0783 | 421.6965 | 0.17203 | 93470.9352 | 254286.6873 | 1905.5314 | 5183.9781
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2696 | 0.85213 | 0.061711 | 4 | 68100.3962 | 180177.0107 | 1388.3187 | 3673.1521 | 85.4671 | 9.8143 | 65.3881 | 536611.0895 | 0 | 382512.9155 | 0 | 0 | 0 | 331998.9426 | 487937.9496 | 1269514.4549 | 866469.7014 | 3875045.0534 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 16810057.9433 | 44475306.4029 | 562.3413 | 0.24684 | 68100.3962 | 180177.0107 | 1388.3187 | 3673.1521
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1481 | 1.1615 | 0.086631 | 4 | 50997.844 | 130833.8606 | 1039.66 | 2667.2252 | 87.0944 | 9.8813 | 47.9376 | 657610.4404 | 0 | 480573.0037 | 0 | 0 | 0 | 391255.898 | 596481.3434 | 1551922.1004 | 1059218.7223 | 4737061.5082 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 17672074.398 | 45337322.8577 | 749.8942 | 0.34653 | 50997.844 | 130833.8606 | 1039.66 | 2667.2252
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6378 | 1.5728 | 0.1199 | 4 | 39068.0319 | 96753.5817 | 796.4547 | 1972.4526 | 88.4178 | 9.9322 | 30.2118 | 805552.4829 | 0 | 603410.8656 | 0 | 0 | 0 | 464151.9794 | 730514.9779 | 1900650.1232 | 1297232.7636 | 5801513.1926 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 18736526.0825 | 46401774.5421 | 1000 | 0.47959 | 39068.0319 | 96753.5817 | 796.4547 | 1972.4526
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6755 | 2.0794 | 0.16344 | 4 | 30439.5117 | 72757.9331 | 620.5506 | 1483.2689 | 89.4038 | 9.9665 | 50.5756 | 972398.6246 | 0 | 737713.0445 | 0 | 0 | 0 | 538498.5714 | 876957.9938 | 2281664.8111 | 1557283.1171 | 6964516.1626 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 19899529.0524 | 47564777.5121 | 1333.5214 | 0.65374 | 30439.5117 | 72757.9331 | 620.5506 | 1483.2689
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5413 | 2.7262 | 0.22029 | 4 | 24142.3748 | 55538.358 | 492.175 | 1132.2245 | 90.1684 | 9.988 | 53.0751 | 1169161.91 | 0 | 900288.3509 | 0 | 0 | 0 | 622793.5426 | 1049975.0834 | 2731819.7874 | 1864523.1382 | 8338561.8125 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 21273574.7024 | 48938823.162 | 1778.2794 | 0.88117 | 24142.3748 | 55538.358 | 492.175 | 1132.2245
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.3527 | 3.5346 | 0.29358 | 4 | 19462.4962 | 43020.7991 | 396.7693 | 877.0372 | 90.7364 | 9.9966 | 57.5643 | 1396368.7097 | 0 | 1092939.8544 | 0 | 0 | 0 | 713658.8488 | 1249157.291 | 3250051.0339 | 2218226.6125 | 9920402.3503 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 22855415.2402 | 50520663.6998 | 2371.3737 | 1.1743 | 19462.4962 | 43020.7991 | 396.7693 | 877.0372
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.277 | 4.5339 | 0.3869 | 4 | 15933.3041 | 33809.6819 | 324.822 | 689.2561 | 91.1365 | 9.9911 | 67.247 | 1656286.5158 | 0 | 1319102.75 | 0 | 0 | 0 | 809628.5212 | 1476156.9369 | 3840657.5484 | 2621327.6944 | 11723159.9666 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 24658172.8564 | 52323421.3161 | 3162.2777 | 1.5476 | 15933.3041 | 33809.6819 | 324.822 | 689.2561
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.4802 | 5.7537 | 0.50388 | 4 | 13241.3445 | 26967.4112 | 269.9427 | 549.7672 | 91.3852 | 9.9687 | 63.6354 | 1950178.8119 | 0 | 1581688.9374 | 0 | 0 | 0 | 908603.3863 | 1731783.7429 | 4505746.0613 | 3075264.2707 | 13753265.2106 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 26688278.1004 | 54353526.5601 | 4216.965 | 2.0155 | 13241.3445 | 26967.4112 | 269.9427 | 549.7672
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.9844 | 7.2005 | 0.64677 | 4 | 11171.4476 | 21865.0495 | 227.7451 | 445.7486 | 91.4857 | 9.9257 | 77.5385 | 2273065.154 | 0 | 1878325.9059 | 0 | 0 | 0 | 1003647.7772 | 2010465.1465 | 5230817.908 | 3570140.7048 | 15966462.5964 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 28901475.4863 | 56566723.9459 | 5623.4133 | 2.5871 | 11171.4476 | 21865.0495 | 227.7451 | 445.7486
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.6554 | 8.8547 | 0.81521 | 4 | 9573.4027 | 18057.5078 | 195.1668 | 368.1267 | 91.4352 | 9.858 | 77.38 | 2614922.0154 | 0 | 2202029.8035 | 0 | 0 | 0 | 1085778.6971 | 2302064.9012 | 5989500.6545 | 4087957.2687 | 18282253.3404 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 31217266.2302 | 58882514.6899 | 7498.9421 | 3.2608 | 9573.4027 | 18057.5078 | 195.1668 | 368.1267
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.0982 | 10.6514 | 1.0043 | 4 | 8339.9745 | 15226.5969 | 170.0217 | 310.4148 | 91.231 | 9.7641 | 76.8148 | 2958643.4462 | 0 | 2538685.7094 | 0 | 0 | 0 | 1143621.1036 | 2589970.6011 | 6738572.2281 | 4599214.0095 | 20568707.0979 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 33503719.9878 | 61168968.4474 | 10000 | 4.0172 | 8339.9745 | 15226.5969 | 170.0217 | 310.4148
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.7218 | 12.4903 | 1.2046 | 4 | 7391.3254 | 13132.8721 | 150.6822 | 267.7314 | 90.8852 | 9.6468 | 91.2268 | 3284388.2535 | 0 | 2870055.0232 | 0 | 0 | 0 | 1168037.9587 | 2855767.6818 | 7430121.7096 | 5071210.7405 | 22679581.3673 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 35614594.2571 | 63279842.7168 | 13335.2143 | 4.8184 | 7391.3254 | 13132.8721 | 150.6822 | 267.7314
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.883 | 14.2595 | 1.404 | 4 | 6665.2024 | 11591.346 | 135.8792 | 236.3053 | 90.4337 | 9.5141 | 83.8425 | 3575099.4118 | 0 | 3178254.6739 | 0 | 0 | 0 | 1155846.2179 | 3084588.1184 | 8025465.5481 | 5477545.1434 | 24496799.1135 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 37431812.0033 | 65097060.463 | 17782.7941 | 5.616 | 6665.2024 | 11591.346 | 135.8792 | 236.3053
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.0787 | 15.8692 | 1.5912 | 4 | 6111.8197 | 10458.3158 | 124.5977 | 213.2069 | 89.9273 | 9.377 | 78.6048 | 3821417.4807 | 0 | 3450845.5773 | 0 | 0 | 0 | 1111435.0989 | 3269642.2812 | 8506938.5198 | 5806160.3399 | 25966439.2977 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 38901452.1876 | 66566700.6472 | 23713.7371 | 6.365 | 6111.8197 | 10458.3158 | 124.5977 | 213.2069
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0176 | 17.2656 | 1.7583 | 4 | 5691.37 | 9624.9464 | 116.0263 | 196.2176 | 89.4171 | 9.2455 | 86.8486 | 4021550.4605 | 0 | 3681904.6386 | 0 | 0 | 0 | 1043965.3634 | 3411493.9804 | 8876007.5433 | 6058057.532 | 27092979.5182 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 40027992.4081 | 67693240.8677 | 31622.7766 | 7.0331 | 5691.37 | 9624.9464 | 116.0263 | 196.2176
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6265 | 18.433 | 1.9012 | 4 | 5372.4596 | 9010.2998 | 109.5249 | 183.6871 | 88.9413 | 9.127 | 100.6156 | 4179385.4399 | 0 | 3871514.3867 | 0 | 0 | 0 | 964107.6618 | 3515852.9205 | 9147528.0985 | 6243375.8901 | 27921764.3975 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 40856777.2874 | 68522025.747 | 42169.6503 | 7.6049 | 5372.4596 | 9010.2998 | 109.5249 | 183.6871
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9466 | 19.3764 | 2.0193 | 4 | 5130.729 | 8555.878 | 104.5969 | 174.4231 | 88.5244 | 9.0254 | 99.5455 | 4300653.6717 | 0 | 4022475.0598 | 0 | 0 | 0 | 880626.6505 | 3589464.599 | 9339050.5861 | 6374093.9233 | 28506364.4902 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 41441377.3801 | 69106625.8397 | 56234.1325 | 8.0771 | 5130.729 | 8555.878 | 104.5969 | 174.4231
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.142 | 20.1228 | 2.1144 | 4 | 4947.5216 | 8218.6223 | 100.8619 | 167.5477 | 88.1744 | 8.9415 | 93.0879 | 4392626.3335 | 0 | 4140527.0917 | 0 | 0 | 0 | 800445.3585 | 3640103.5256 | 9470802.6858 | 6464017.4386 | 28908522.4338 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 41843535.3236 | 69508783.7833 | 74989.4209 | 8.4575 | 4947.5216 | 8218.6223 | 100.8619 | 167.5477
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.3649 | 20.6983 | 2.1892 | 4 | 4808.6649 | 7967.993 | 98.0311 | 162.4383 | 87.8926 | 8.8748 | 100.2032 | 4461073.6047 | 0 | 4230647.4898 | 0 | 0 | 0 | 727256.743 | 3673401.3566 | 9557436.8116 | 6523147.0096 | 29172963.0153 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42107975.9052 | 69773224.3648 | 100000 | 8.7567 | 4808.6649 | 7967.993 | 98.0311 | 162.4383
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8345 | 21.1404 | 2.2474 | 4 | 4703.4325 | 7780.8982 | 95.8858 | 158.6241 | 87.6689 | 8.8223 | 99.3557 | 4512215.4051 | 0 | 4299378.789 | 0 | 0 | 0 | 663593.6349 | 3695323.2533 | 9614473.0901 | 6562075.4417 | 29347059.6141 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42282072.5039 | 69947320.9636 | 133352.1432 | 8.9896 | 4703.4325 | 7780.8982 | 95.8858 | 158.6241
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.6936 | 21.4741 | 2.2921 | 4 | 4623.7105 | 7641.1906 | 94.2606 | 155.776 | 87.4962 | 8.782 | 90.6162 | 4549958.8865 | 0 | 4350936.4921 | 0 | 0 | 0 | 609686.3795 | 3709126.8856 | 9650387.3098 | 6586587.6346 | 29456683.5881 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42391696.4779 | 70056944.9376 | 177827.941 | 9.1683 | 4623.7105 | 7641.1906 | 94.2606 | 155.776
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1138 | 21.7298 | 2.3265 | 4 | 4563.0172 | 7535.9074 | 93.0233 | 153.6297 | 87.3603 | 8.7502 | 89.2795 | 4578264.0571 | 0 | 4390222.0393 | 0 | 0 | 0 | 565026.9638 | 3718070.0935 | 9673655.7021 | 6602468.7905 | 29527707.6462 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42462720.536 | 70127968.9957 | 237137.3706 | 9.3058 | 4563.0172 | 7535.9074 | 93.0233 | 153.6297
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.142 | 21.9154 | 2.3521 | 4 | 4517.4196 | 7457.8909 | 92.0937 | 152.0392 | 87.2616 | 8.7274 | 84.3691 | 4598595.4975 | 0 | 4418607.0951 | 0 | 0 | 0 | 528951.1229 | 3722999.9491 | 9686482.1752 | 6611223.1219 | 29566858.9617 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42501871.8516 | 70167120.3112 | 316227.766 | 9.4084 | 4517.4196 | 7457.8909 | 92.0937 | 152.0392
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8971 | 22.0521 | 2.3714 | 4 | 4482.9608 | 7399.565 | 91.3912 | 150.8501 | 87.1884 | 8.7106 | 86.0508 | 4613397.7596 | 0 | 4439425.4828 | 0 | 0 | 0 | 500092.7505 | 3725637.2372 | 9693343.858 | 6615906.3614 | 29587803.4495 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42522816.3394 | 70188064.799 | 421696.5034 | 9.4854 | 4482.9608 | 7399.565 | 91.3912 | 150.8501
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4501 | 22.1526 | 2.3858 | 4 | 4456.9489 | 7355.9518 | 90.8609 | 149.961 | 87.1343 | 8.6982 | 89.0012 | 4624168.2978 | 0 | 4454657.534 | 0 | 0 | 0 | 477301.5193 | 3726889.6669 | 9696602.4232 | 6618130.3991 | 29597749.8402 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42532762.7301 | 70198011.1897 | 562341.3252 | 9.543 | 4456.9489 | 7355.9518 | 90.8609 | 149.961
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8593 | 22.227 | 2.3966 | 4 | 4437.3348 | 7323.2788 | 90.4611 | 149.2949 | 87.094 | 8.689 | 76.4013 | 4632098.0081 | 0 | 4465918.0912 | 0 | 0 | 0 | 459542.5622 | 3727447.878 | 9698054.7737 | 6619121.6582 | 29602182.9713 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42537195.8612 | 70202444.3208 | 749894.2093 | 9.5862 | 4437.3348 | 7323.2788 | 90.4611 | 149.2949
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.154 | 22.2809 | 2.4046 | 4 | 4422.5597 | 7298.8998 | 90.1599 | 148.7979 | 87.0649 | 8.6823 | 83.0354 | 4637787.6374 | 0 | 4474023.4881 | 0 | 0 | 0 | 445721.852 | 3727437.8612 | 9698028.7123 | 6619103.8707 | 29602103.4219 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42537116.3117 | 70202364.7714 | 1000000 | 9.6182 | 4422.5597 | 7298.8998 | 90.1599 | 148.7979
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.3929 | 22.3243 | 2.4108 | 4 | 4411.4397 | 7280.3791 | 89.9332 | 148.4204 | 87.0412 | 8.6769 | 75.9741 | 4642390.5879 | 0 | 4480592.934 | 0 | 0 | 0 | 435356.2092 | 3727752.4951 | 9698847.3252 | 6619662.5908 | 29604602.1422 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42539615.0321 | 70204863.4917 | 1333521.4322 | 9.643 | 4411.4397 | 7280.3791 | 89.9332 | 148.4204
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5561 | 22.3542 | 2.4153 | 4 | 4403.0774 | 7266.6755 | 89.7627 | 148.141 | 87.0249 | 8.6732 | 82.0408 | 4645525.7598 | 0 | 4485077.883 | 0 | 0 | 0 | 427270.234 | 3727570.812 | 9698374.6228 | 6619339.9617 | 29603159.2734 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42538172.1632 | 70203420.6229 | 1778279.41 | 9.661 | 4403.0774 | 7266.6755 | 89.7627 | 148.141
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.683 | 22.3774 | 2.4187 | 4 | 4396.7918 | 7256.3356 | 89.6345 | 147.9302 | 87.0123 | 8.6703 | 81.5756 | 4647960.8783 | 0 | 4488564.4592 | 0 | 0 | 0 | 421187.3205 | 3727507.9366 | 9698211.034 | 6619228.309 | 29602659.9377 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42537672.8275 | 70202921.2872 | 2371373.7057 | 9.6747 | 4396.7918 | 7256.3356 | 89.6345 | 147.9302
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7756 | 22.3943 | 2.4212 | 4 | 4392.0704 | 7248.6087 | 89.5383 | 147.7727 | 87.0031 | 8.6682 | 82.0615 | 4649735.9465 | 0 | 4491108.9778 | 0 | 0 | 0 | 416554.4482 | 3727385.7553 | 9697893.1433 | 6619011.3421 | 29601689.6131 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42536702.5029 | 70201950.9626 | 3162277.6602 | 9.6849 | 4392.0704 | 7248.6087 | 89.5383 | 147.7727
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8339 | 22.4052 | 2.423 | 4 | 4388.5251 | 7242.9465 | 89.466 | 147.6573 | 86.9972 | 8.6668 | 76.8068 | 4650852.1161 | 0 | 4492711.8395 | 0 | 0 | 0 | 412926.5874 | 3727031.3118 | 9696970.9541 | 6618381.929 | 29598874.738 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42533887.6278 | 70199136.0875 | 4216965.0343 | 9.6921 | 4388.5251 | 7242.9465 | 89.466 | 147.6573
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8922 | 22.4158 | 2.4245 | 4 | 4385.8638 | 7238.5216 | 89.4118 | 147.5671 | 86.9914 | 8.6655 | 81.9756 | 4651969.5873 | 0 | 4494314.5583 | 0 | 0 | 0 | 410363.1357 | 3727092.4397 | 9697129.9963 | 6618490.4786 | 29599360.1958 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42534373.0856 | 70199621.5453 | 5623413.2519 | 9.6981 | 4385.8638 | 7238.5216 | 89.4118 | 147.5671
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9239 | 22.4217 | 2.4255 | 4 | 4383.8666 | 7235.3492 | 89.371 | 147.5024 | 86.9882 | 8.6648 | 86.5172 | 4652574.5408 | 0 | 4495184.3035 | 0 | 0 | 0 | 408291.7906 | 3726859.7476 | 9696524.5793 | 6618077.269 | 29597512.2309 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42532525.1208 | 70197773.5804 | 7498942.0933 | 9.7021 | 4383.8666 | 7235.3492 | 89.371 | 147.5024
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9628 | 22.4287 | 2.4264 | 4 | 4382.368 | 7232.7861 | 89.3405 | 147.4501 | 86.9844 | 8.6639 | 89.0364 | 4653319.5346 | 0 | 4496252.6516 | 0 | 0 | 0 | 406911.1482 | 3727028.5004 | 9696963.6394 | 6618376.9366 | 29598852.4108 | 961560.8286 | 11973452.0612 | 11973452.0612 | 10331217.8863 | 5360578.5121 | 0 | 42533865.3007 | 70199113.7603 | 10000000 | 9.7057 | 4382.368 | 7232.7861 | 89.3405 | 147.4501
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.051808 | 0.0032118 | 4 | 1113073.1361 | 3335524.3616 | 22691.5014 | 67999.1757 | 65.2013 | 8.9982 | 112.981 | 121428.4592 | 0 | 67732.2055 | 0 | 0 | 0 | 104591.2848 | 114563.2603 | 298070.1032 | 203438.9702 | 909824.2832 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14300057.4028 | 42852700.5937 | 100 | 0.012847 | 1113073.1361 | 3335524.3616 | 22691.5014 | 67999.1757
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5736 | 0.11017 | 0.0069544 | 4 | 526316.2276 | 1552747.0934 | 10729.6682 | 31654.8497 | 71.1785 | 9.3982 | 161.4549 | 168685.9602 | 0 | 100270.3143 | 0 | 0 | 0 | 134794.5152 | 157462.808 | 409685.9263 | 279619.0629 | 1250518.587 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 14640751.7066 | 43193394.8975 | 133.3521 | 0.027817 | 526316.2276 | 1552747.0934 | 10729.6682 | 31654.8497
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.19387 | 0.012601 | 4 | 298674.5044 | 865170.3209 | 6088.8838 | 17637.6672 | 76.2039 | 9.6963 | 208.2951 | 226157.8299 | 0 | 140676.0471 | 0 | 0 | 0 | 170294.5869 | 209480.101 | 545024.2524 | 371990.2514 | 1663623.0688 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 15053856.1884 | 43606499.3793 | 177.8279 | 0.050402 | 298674.5044 | 865170.3209 | 6088.8838 | 17637.6672
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.30584 | 0.020678 | 4 | 187716.8275 | 532914.951 | 3826.8614 | 10864.1921 | 80.233 | 9.911 | 43.7118 | 292606.3529 | 0 | 188493.6666 | 0 | 0 | 0 | 208716.3046 | 269028.3664 | 699956.6241 | 477734.7786 | 2136536.0934 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 15526769.2129 | 44079412.4039 | 237.1374 | 0.082714 | 187716.8275 | 532914.951 | 3826.8614 | 10864.1921
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 0.45582 | 0.031909 | 4 | 126055.654 | 349759.9356 | 2569.815 | 7130.3294 | 83.5506 | 10.0736 | 53.5033 | 371688.383 | 0 | 246803.8616 | 0 | 0 | 0 | 252913.064 | 339848.0703 | 884214.9666 | 603494.8835 | 2698963.2289 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 16089196.3485 | 44641839.5394 | 316.2278 | 0.12764 | 126055.654 | 349759.9356 | 2569.815 | 7130.3294
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0346 | 0.65331 | 0.047225 | 4 | 88695.9974 | 239848.1116 | 1808.1879 | 4889.6282 | 86.2403 | 10.1961 | 53.4047 | 465300.6304 | 0 | 317594.8897 | 0 | 0 | 0 | 303371.9905 | 423644.3291 | 1102235.6429 | 752298.475 | 3364445.9575 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 16754679.0771 | 45307322.268 | 421.6965 | 0.1889 | 88695.9974 | 239848.1116 | 1808.1879 | 4889.6282
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5667 | 0.90816 | 0.0678 | 4 | 64641.0173 | 169924.1563 | 1317.7946 | 3464.1338 | 88.3792 | 10.2878 | 51.1552 | 574754.7634 | 0 | 402494.7668 | 0 | 0 | 0 | 359522.5974 | 521341.1298 | 1356422.6779 | 925786.3493 | 4140322.2846 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 17530555.4042 | 46083198.5951 | 562.3413 | 0.2712 | 64641.0173 | 169924.1563 | 1317.7946 | 3464.1338
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5204 | 1.2366 | 0.095189 | 4 | 48438.8064 | 123427.9312 | 987.4906 | 2516.2453 | 90.0816 | 10.3565 | 56.9681 | 703601.7946 | 0 | 504985.8946 | 0 | 0 | 0 | 422918.1385 | 636287.2728 | 1655488.9634 | 1129905.2344 | 5053187.2983 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 18443420.4179 | 46996063.6088 | 749.8942 | 0.38076 | 48438.8064 | 123427.9312 | 987.4906 | 2516.2453
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1151 | 1.674 | 0.13199 | 4 | 37022.9803 | 91102.7068 | 754.7635 | 1857.2519 | 91.4717 | 10.4088 | 48.8688 | 861531.7213 | 0 | 624974.3864 | 0 | 0 | 0 | 501353.7678 | 775265.3515 | 2017081.4157 | 1376699.5131 | 6156906.1558 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 19547139.2754 | 48099782.4663 | 1000 | 0.52797 | 37022.9803 | 91102.7068 | 754.7635 | 1857.2519
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3017 | 2.216 | 0.17998 | 4 | 28874.7604 | 68536.3546 | 588.651 | 1397.2063 | 92.5137 | 10.4438 | 48.9457 | 1040813.9805 | 0 | 764616.1799 | 0 | 0 | 0 | 582781.5338 | 931402.5608 | 2423318.4062 | 1653964.6064 | 7396897.2676 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 20787130.3872 | 49339773.5781 | 1333.5214 | 0.71991 | 28874.7604 | 68536.3546 | 588.651 | 1397.2063
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3112 | 2.9011 | 0.24241 | 4 | 22927.0004 | 52373.5268 | 467.3979 | 1067.7052 | 93.3127 | 10.4652 | 56.6243 | 1249891.9868 | 0 | 931765.132 | 0 | 0 | 0 | 672739.9917 | 1113214.8731 | 2896356.748 | 1976822.9947 | 8840791.7262 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 22231024.8458 | 50783668.0368 | 1778.2794 | 0.96964 | 22927.0004 | 52373.5268 | 467.3979 | 1067.7052
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.3271 | 3.7613 | 0.32294 | 4 | 18505.4586 | 40609.0405 | 377.2588 | 827.8702 | 93.9098 | 10.4728 | 48.851 | 1492621.6291 | 0 | 1130892.7144 | 0 | 0 | 0 | 771260.5843 | 1323962.2218 | 3444678.1192 | 2351063.5974 | 10514478.8662 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 23904711.9858 | 52457355.1767 | 2371.3737 | 1.2918 | 18505.4586 | 40609.0405 | 377.2588 | 827.8702
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.5 | 4.8242 | 0.42536 | 4 | 15170.058 | 31951.5314 | 309.2622 | 651.3752 | 94.3292 | 10.4652 | 60.6917 | 1770146.3619 | 0 | 1364551.5136 | 0 | 0 | 0 | 875527.7729 | 1563988.0029 | 4069175.9654 | 2777296.2096 | 12420685.8263 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 25810918.9459 | 54363562.1369 | 3162.2777 | 1.7014 | 15170.058 | 31951.5314 | 309.2622 | 651.3752
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.954 | 6.1133 | 0.55323 | 4 | 12625.4321 | 25528.0209 | 257.3865 | 520.4232 | 94.5867 | 10.4393 | 62.9741 | 2081816.1211 | 0 | 1634034.4519 | 0 | 0 | 0 | 981562.3383 | 1831991.0354 | 4766464.8811 | 3253210.2224 | 14549079.0504 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 27939312.1699 | 56491955.3609 | 4216.965 | 2.2129 | 12625.4321 | 25528.0209 | 257.3865 | 520.4232
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.7554 | 7.6426 | 0.70911 | 4 | 10668.8044 | 20735.1805 | 217.498 | 422.7147 | 94.688 | 10.3908 | 74.055 | 2424301.1983 | 0 | 1938591.7002 | 0 | 0 | 0 | 1084242.6323 | 2124382.857 | 5527208.4232 | 3772433.3216 | 16871160.1326 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 30261393.2522 | 58814036.4432 | 5623.4133 | 2.8364 | 10668.8044 | 20735.1805 | 217.498 | 422.7147
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6964 | 9.3798 | 0.89181 | 4 | 9158.7433 | 17162.8633 | 186.7134 | 349.8882 | 94.6288 | 10.3158 | 89.5479 | 2784417.4386 | 0 | 2268789.1611 | 0 | 0 | 0 | 1172061.088 | 2427854.3982 | 6316779.1227 | 4311331.5481 | 19281232.7568 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 32671465.8764 | 61224109.0673 | 7498.9421 | 3.5672 | 9158.7433 | 17162.8633 | 186.7134 | 349.8882
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.3445 | 11.252 | 1.0955 | 4 | 7994.0799 | 14510.2116 | 162.9701 | 295.8103 | 94.4084 | 10.2131 | 66.1721 | 3143603.6604 | 0 | 2609614.3866 | 0 | 0 | 0 | 1233146.044 | 2724681.9955 | 7089063.6432 | 4838431.6022 | 21638541.332 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 35028774.4516 | 63581417.6426 | 10000 | 4.3818 | 7994.0799 | 14510.2116 | 162.9701 | 295.8103
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0996 | 13.1548 | 1.3096 | 4 | 7099.1952 | 12549.9267 | 144.7267 | 255.8472 | 94.0425 | 10.0864 | 82.7086 | 3481628.3423 | 0 | 2942891.1339 | 0 | 0 | 0 | 1258926.3619 | 2996543.8769 | 7796392.4919 | 5321198.0756 | 23797580.2825 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 37187813.4021 | 65740456.5931 | 13335.2143 | 5.2383 | 7099.1952 | 12549.9267 | 144.7267 | 255.8472
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.3313 | 14.9757 | 1.5213 | 4 | 6414.9332 | 11107.0184 | 130.7771 | 226.4316 | 93.5704 | 9.9446 | 86.4685 | 3781769.2858 | 0 | 3251385.1802 | 0 | 0 | 0 | 1247220.0302 | 3229346.0535 | 8402096.0013 | 5734603.1667 | 25646419.7177 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 39036652.8373 | 67589296.0283 | 17782.7941 | 6.0853 | 6414.9332 | 11107.0184 | 130.7771 | 226.4316
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.5271 | 16.6213 | 1.7187 | 4 | 5893.9738 | 10047.0907 | 120.1566 | 204.8235 | 93.0471 | 9.7994 | 81.4819 | 4034450.4353 | 0 | 3522506.8498 | 0 | 0 | 0 | 1202669.8705 | 3416254.5907 | 8888393.6748 | 6066511.3213 | 27130786.7423 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 40521019.8619 | 69073663.0529 | 23713.7371 | 6.875 | 5893.9738 | 10047.0907 | 120.1566 | 204.8235
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4466 | 18.0454 | 1.8941 | 4 | 5498.5466 | 9267.2164 | 112.0953 | 188.9247 | 92.523 | 9.6611 | 86.4475 | 4239386.0145 | 0 | 3751869.3232 | 0 | 0 | 0 | 1135703.8882 | 3559514.0981 | 9261125.5266 | 6320908.469 | 28268507.3196 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 41658740.4392 | 70211383.6301 | 31622.7766 | 7.5763 | 5498.5466 | 9267.2164 | 112.0953 | 188.9247
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0165 | 19.2318 | 2.0435 | 4 | 5198.9264 | 8692.1097 | 105.9871 | 177.2004 | 92.0371 | 9.537 | 96.7784 | 4400564.9499 | 0 | 3939511.9105 | 0 | 0 | 0 | 1056907.3052 | 3664823.8246 | 9535119.8328 | 6507915.213 | 29104843.0359 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 42495076.1555 | 71047719.3465 | 42169.6503 | 8.1738 | 5198.9264 | 8692.1097 | 105.9871 | 177.2004
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.2829 | 20.1868 | 2.1663 | 4 | 4972.0853 | 8267.1584 | 101.3627 | 168.5372 | 91.6141 | 9.4314 | 102.2131 | 4523972.0458 | 0 | 4088321.5218 | 0 | 0 | 0 | 974956.9246 | 3739027.692 | 9728183.0745 | 6639684.8425 | 29694146.1011 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 43084379.2207 | 71637022.4117 | 56234.1325 | 8.6653 | 4972.0853 | 8267.1584 | 101.3627 | 168.5372
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.4512 | 20.9449 | 2.2653 | 4 | 4800.4017 | 7951.5523 | 97.8627 | 162.1031 | 91.2581 | 9.344 | 90.9036 | 4617977.2675 | 0 | 4205148.7974 | 0 | 0 | 0 | 897198.5269 | 3790926.5908 | 9863213.3633 | 6731845.7892 | 30106310.3351 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 43496543.4547 | 72049186.6456 | 74989.4209 | 9.061 | 4800.4017 | 7951.5523 | 97.8627 | 162.1031
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.6519 | 21.5291 | 2.343 | 4 | 4670.4916 | 7717.1359 | 95.2143 | 157.3243 | 90.9718 | 9.2745 | 90.7905 | 4687938.7129 | 0 | 4294305.824 | 0 | 0 | 0 | 826715.1018 | 3825494.2591 | 9953151.3455 | 6793230.3101 | 30380835.5534 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 43771068.673 | 72323711.864 | 100000 | 9.3718 | 4670.4916 | 7717.1359 | 95.2143 | 157.3243
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.1197 | 21.9804 | 2.4035 | 4 | 4572.2227 | 7542.0703 | 93.2109 | 153.7553 | 90.7434 | 9.2196 | 93.6361 | 4740557.9885 | 0 | 4362734.4851 | 0 | 0 | 0 | 766073.8749 | 3849052.8759 | 10014446.0339 | 6835065.1944 | 30567930.4529 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 43958163.5725 | 72510806.7634 | 133352.1432 | 9.6142 | 4572.2227 | 7542.0703 | 93.2109 | 153.7553
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9808 | 22.3216 | 2.45 | 4 | 4497.928 | 7411.4365 | 91.6963 | 151.0922 | 90.5666 | 9.1773 | 99.799 | 4779469.9502 | 0 | 4414161.3372 | 0 | 0 | 0 | 715102.6471 | 3864406.2344 | 10054392.3233 | 6862329.3577 | 30689861.8499 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44080094.9695 | 72632738.1604 | 177827.941 | 9.8001 | 4497.928 | 7411.4365 | 91.6963 | 151.0922
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.377 | 22.5783 | 2.4854 | 4 | 4441.7995 | 7313.814 | 90.5521 | 149.102 | 90.4315 | 9.1452 | 103.4317 | 4808224.0444 | 0 | 4452643.2935 | 0 | 0 | 0 | 673323.2096 | 3874334.3135 | 10080223.1486 | 6879959.4268 | 30768707.4364 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44158940.556 | 72711583.747 | 237137.3706 | 9.9417 | 4441.7995 | 7313.814 | 90.5521 | 149.102
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4272 | 22.7716 | 2.5123 | 4 | 4399.4325 | 7240.7115 | 89.6884 | 147.6117 | 90.3284 | 9.1208 | 89.4865 | 4829605.0504 | 0 | 4481534.8664 | 0 | 0 | 0 | 639817.7777 | 3880873.5009 | 10097236.7726 | 6891571.5748 | 30820639.5428 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44210872.6624 | 72763515.8533 | 316227.766 | 10.0492 | 4399.4325 | 7240.7115 | 89.6884 | 147.6117
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2166 | 22.9171 | 2.5327 | 4 | 4367.4827 | 7185.9248 | 89.037 | 146.4948 | 90.25 | 9.1023 | 94.5152 | 4845535.5672 | 0 | 4503220.7949 | 0 | 0 | 0 | 613358.0709 | 3885224.6289 | 10108557.5152 | 6899298.2142 | 30855194.7912 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44245427.9108 | 72798071.1017 | 421696.5034 | 10.1306 | 4367.4827 | 7185.9248 | 89.037 | 146.4948
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.7903 | 23.0233 | 2.5478 | 4 | 4343.411 | 7145.071 | 88.5463 | 145.6619 | 90.1926 | 9.0887 | 212.5057 | 4857036.16 | 0 | 4518966.3088 | 0 | 0 | 0 | 592475.6393 | 3887706.4621 | 10115014.7361 | 6903705.4002 | 30874904.7064 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44265137.826 | 72817781.0169 | 562341.3252 | 10.1913 | 4343.411 | 7145.071 | 88.5463 | 145.6619
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2681 | 23.1115 | 2.5598 | 4 | 4324.9881 | 7113.5051 | 88.1707 | 145.0184 | 90.1433 | 9.0768 | 96.0051 | 4866473.9657 | 0 | 4532068.8598 | 0 | 0 | 0 | 576391.2416 | 3890224.2862 | 10121565.5979 | 6908176.498 | 30894900.4492 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44285133.5688 | 72837776.7597 | 749894.2093 | 10.2394 | 4324.9881 | 7113.5051 | 88.1707 | 145.0184
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5971 | 23.1723 | 2.5685 | 4 | 4311.3758 | 7090.4823 | 87.8932 | 144.5491 | 90.1101 | 9.069 | 96.5454 | 4873014.209 | 0 | 4541083.3786 | 0 | 0 | 0 | 564098.1374 | 3891496.3327 | 10124875.2021 | 6910435.3708 | 30905002.6307 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44295235.7503 | 72847878.9412 | 1000000 | 10.274 | 4311.3758 | 7090.4823 | 87.8932 | 144.5491
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8406 | 23.2174 | 2.575 | 4 | 4301.1428 | 7073.2503 | 87.6846 | 144.1978 | 90.0854 | 9.0632 | 98.4325 | 4877842.9571 | 0 | 4547755.2771 | 0 | 0 | 0 | 554675.4575 | 3892306.7398 | 10126983.715 | 6911874.4742 | 30911438.6206 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44301671.7402 | 72854314.9311 | 1333521.4322 | 10.3 | 4301.1428 | 7073.2503 | 87.6846 | 144.1978
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.0233 | 23.2512 | 2.5799 | 4 | 4293.4544 | 7060.326 | 87.5279 | 143.9343 | 90.0669 | 9.0589 | 105.0265 | 4881455.7384 | 0 | 4552756.0861 | 0 | 0 | 0 | 547512.6879 | 3892872.5598 | 10128455.8627 | 6912879.2452 | 30915932.18 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44306165.2996 | 72858808.4906 | 1778279.41 | 10.3195 | 4293.4544 | 7060.326 | 87.5279 | 143.9343
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.165 | 23.2774 | 2.5836 | 4 | 4287.6802 | 7050.5781 | 87.4102 | 143.7356 | 90.0525 | 9.0555 | 96.0063 | 4884254.8388 | 0 | 4556635.2655 | 0 | 0 | 0 | 542142.4295 | 3893382.6882 | 10129783.112 | 6913785.1202 | 30919983.454 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44310216.5736 | 72862859.7645 | 2371373.7057 | 10.3343 | 4287.6802 | 7050.5781 | 87.4102 | 143.7356
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.2692 | 23.2967 | 2.5863 | 4 | 4283.3453 | 7043.2897 | 87.3218 | 143.587 | 90.0419 | 9.053 | 88.8693 | 4886312.5048 | 0 | 4559490.1517 | 0 | 0 | 0 | 538060.2369 | 3893706.5284 | 10130625.6779 | 6914360.1887 | 30922555.2884 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44312788.408 | 72865431.5989 | 3162277.6602 | 10.3454 | 4283.3453 | 7043.2897 | 87.3218 | 143.587
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3398 | 23.3099 | 2.5883 | 4 | 4280.0917 | 7037.9105 | 87.2555 | 143.4773 | 90.0347 | 9.0514 | 95.8623 | 4887702.5786 | 0 | 4561421.2834 | 0 | 0 | 0 | 534890.1965 | 3893765.4828 | 10130779.0652 | 6914464.8787 | 30923023.4853 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44313256.6048 | 72865899.7958 | 4216965.0343 | 10.3533 | 4280.0917 | 7037.9105 | 87.2555 | 143.4773
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3935 | 23.3199 | 2.5898 | 4 | 4277.6503 | 7033.8671 | 87.2057 | 143.3949 | 90.0292 | 9.0501 | 92.8354 | 4888760.1982 | 0 | 4562891.2204 | 0 | 0 | 0 | 532512.3684 | 3893823.8769 | 10130930.9947 | 6914568.5737 | 30923487.2323 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44313720.3519 | 72866363.5428 | 5623413.2519 | 10.3594 | 4277.6503 | 7033.8671 | 87.2057 | 143.3949
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4324 | 23.3272 | 2.591 | 4 | 4275.8185 | 7030.8504 | 87.1683 | 143.3334 | 90.0252 | 9.0492 | 93.2739 | 4889525.5524 | 0 | 4563955.5837 | 0 | 0 | 0 | 530707.1233 | 3893833.4212 | 10130955.8268 | 6914585.5221 | 30923563.0295 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44313796.1491 | 72866439.34 | 7498942.0933 | 10.3638 | 4275.8185 | 7030.8504 | 87.1683 | 143.3334
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4667 | 23.3335 | 2.5918 | 4 | 4274.4444 | 7028.5301 | 87.1403 | 143.2861 | 90.0217 | 9.0483 | 88.6863 | 4890200.1208 | 0 | 4564893.1856 | 0 | 0 | 0 | 529410.4589 | 3893956.4685 | 10131275.9707 | 6914804.0269 | 30924540.2313 | 961560.8286 | 12428672.291 | 12428672.291 | 10608277.457 | 5515693.4429 | 0 | 44314773.3509 | 72867416.5419 | 10000000 | 10.3674 | 4274.4444 | 7028.5301 | 87.1403 | 143.2861
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1652 | 0.053555 | 0.0034447 | 4 | 1074846.253 | 3212455.6829 | 21912.1947 | 65490.2543 | 66.7617 | 9.4168 | 117.9702 | 128174.1841 | 0 | 70237.1857 | 0 | 0 | 0 | 111165.024 | 120734.7936 | 314127.1668 | 214398.246 | 958836.6003 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 14810150.0405 | 44263959.1763 | 100 | 0.013779 | 1074846.253 | 3212455.6829 | 21912.1947 | 65490.2543
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.11711 | 0.0075445 | 4 | 503359.9482 | 1479365.6856 | 10261.6734 | 30158.8705 | 73.3033 | 9.8483 | 181.3657 | 180647.2729 | 0 | 105770.8564 | 0 | 0 | 0 | 145911.8632 | 168608.6971 | 438685.2434 | 299411.6927 | 1339035.6256 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 15190349.0658 | 44644158.2016 | 133.3521 | 0.030178 | 503359.9482 | 1479365.6856 | 10261.6734 | 30158.8705
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.20524 | 0.013728 | 4 | 284532.8056 | 820923.9987 | 5800.5861 | 16735.6461 | 78.5074 | 10.1516 | 225.0039 | 241303.8451 | 0 | 147707.6869 | 0 | 0 | 0 | 183329.2664 | 223212.9114 | 580754.2082 | 396376.6804 | 1772684.5985 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 15623998.0387 | 45077807.1745 | 177.8279 | 0.054911 | 284532.8056 | 820923.9987 | 5800.5861 | 16735.6461
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0176 | 0.32448 | 0.022588 | 4 | 178506.3597 | 504489.1653 | 3639.0936 | 10284.694 | 82.7468 | 10.3736 | 46.8538 | 312417.5428 | 0 | 198014.1462 | 0 | 0 | 0 | 224873.8012 | 286769.1412 | 746114.481 | 509238.4644 | 2277427.5768 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 16128741.017 | 45582550.1527 | 237.1374 | 0.090354 | 178506.3597 | 504489.1653 | 3639.0936 | 10284.694
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 0.48299 | 0.034899 | 4 | 119787.7006 | 330783.4586 | 2442.0343 | 6743.4682 | 86.2072 | 10.5402 | 47.2495 | 396244.6914 | 0 | 258756.591 | 0 | 0 | 0 | 271745.2545 | 361431.1494 | 940369.711 | 641821.6504 | 2870369.0478 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 16721682.488 | 46175491.6238 | 316.2278 | 0.13959 | 119787.7006 | 330783.4586 | 2442.0343 | 6743.4682
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2561 | 0.69344 | 0.051707 | 4 | 84281.22 | 226688.4855 | 1718.1867 | 4621.3514 | 89.0421 | 10.6672 | 57.6811 | 496441.2909 | 0 | 333203.8184 | 0 | 0 | 0 | 326347.4997 | 450837.1175 | 1172985.7003 | 800586.8429 | 3580402.2697 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 17431715.7099 | 46885524.8457 | 421.6965 | 0.20683 | 84281.22 | 226688.4855 | 1718.1867 | 4621.3514
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8567 | 0.96484 | 0.074283 | 4 | 61447.4855 | 160574.3613 | 1252.6901 | 3273.5255 | 91.2915 | 10.7619 | 60.4875 | 613438.5097 | 0 | 422363.3313 | 0 | 0 | 0 | 386983.4974 | 554886.282 | 1443700.2829 | 985355.1081 | 4406727.0114 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 18258040.4516 | 47711849.5873 | 562.3413 | 0.29713 | 61447.4855 | 160574.3613 | 1252.6901 | 3273.5255
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9808 | 1.3273 | 0.10478 | 4 | 45942.5797 | 116215.3525 | 936.6016 | 2369.2072 | 93.1381 | 10.8349 | 60.1602 | 756556.4505 | 0 | 526968.5239 | 0 | 0 | 0 | 461520.8994 | 680567.8908 | 1770698.0481 | 1208537.802 | 5404849.6147 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 19256163.0549 | 48709972.1907 | 749.8942 | 0.41914 | 45942.5797 | 116215.3525 | 936.6016 | 2369.2072
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6144 | 1.7816 | 0.14499 | 4 | 35143.1123 | 85929.7108 | 716.4399 | 1751.7934 | 94.5443 | 10.8866 | 56.6252 | 920350.2733 | 0 | 647336.8086 | 0 | 0 | 0 | 540638.3516 | 822246.9191 | 2139317.8173 | 1460128.3689 | 6530018.5388 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 20381331.979 | 49835141.1148 | 1000 | 0.57995 | 35143.1123 | 85929.7108 | 716.4399 | 1751.7934
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9271 | 2.3567 | 0.19762 | 4 | 27435.8045 | 64696.1266 | 559.316 | 1318.918 | 95.6332 | 10.922 | 56.8011 | 1111064.5188 | 0 | 791249.4673 | 0 | 0 | 0 | 627779.0932 | 986736.3009 | 2567285.4475 | 1752225.0704 | 7836339.8981 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 21687653.3383 | 51141462.4741 | 1333.5214 | 0.79049 | 27435.8045 | 64696.1266 | 559.316 | 1318.918
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1077 | 3.0854 | 0.26612 | 4 | 21808.7139 | 49478.5331 | 444.6001 | 1008.6868 | 96.4713 | 10.9432 | 50.5858 | 1334179.8536 | 0 | 964048.2453 | 0 | 0 | 0 | 724934.1456 | 1179033.2753 | 3067602.7294 | 2093701.8958 | 9363500.145 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 23214813.5852 | 52668622.721 | 1778.2794 | 1.0645 | 21808.7139 | 49478.5331 | 444.6001 | 1008.6868
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.3204 | 3.9978 | 0.3543 | 4 | 17624.797 | 38408.0724 | 359.3053 | 783.0005 | 97.0952 | 10.9497 | 61.9099 | 1592362.6253 | 0 | 1169252.5595 | 0 | 0 | 0 | 830708.6787 | 1401006.3068 | 3645131.0244 | 2487876.8241 | 11126338.0188 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 24977651.459 | 54431460.5948 | 2371.3737 | 1.4172 | 17624.797 | 38408.0724 | 359.3053 | 783.0005
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.713 | 5.1216 | 0.46616 | 4 | 14467.6626 | 30263.5906 | 294.9429 | 616.9642 | 97.5316 | 10.9397 | 53.5719 | 1886576.9283 | 0 | 1409255.6374 | 0 | 0 | 0 | 942035.2869 | 1652768.4625 | 4300164.5101 | 2934950.6377 | 13125751.4629 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 26977064.9031 | 56430874.0389 | 3162.2777 | 1.8646 | 14467.6626 | 30263.5906 | 294.9429 | 616.9642
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4498 | 6.4875 | 0.60574 | 4 | 12058.2308 | 24214.2784 | 245.8233 | 493.6408 | 97.7989 | 10.9099 | 50.3185 | 2217766.7354 | 0 | 1686737.8688 | 0 | 0 | 0 | 1056499.5344 | 1934791.614 | 5033930.8994 | 3435761.2758 | 15365487.9278 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 29216801.368 | 58670610.5038 | 4216.965 | 2.423 | 12058.2308 | 24214.2784 | 245.8233 | 493.6408
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.507 | 8.0948 | 0.77495 | 4 | 10205.4153 | 19707.2621 | 208.0512 | 401.7592 | 97.8999 | 10.8557 | 66.3979 | 2578611.1389 | 0 | 1997738.3966 | 0 | 0 | 0 | 1165323.0811 | 2239252.3204 | 5826075.204 | 3976416.0406 | 17783416.1815 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 31634729.6217 | 61088538.7575 | 5623.4133 | 3.0998 | 10205.4153 | 19707.2621 | 208.0512 | 401.7592
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.7038 | 9.9148 | 0.97243 | 4 | 8775.9533 | 16348.1666 | 178.9097 | 333.2795 | 97.8317 | 10.7731 | 89.0036 | 2956840.4706 | 0 | 2333973.4188 | 0 | 0 | 0 | 1258443.1713 | 2554210.2537 | 6645531.1395 | 4535711.5547 | 20284710.0087 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 34136023.4489 | 63589832.5847 | 7498.9421 | 3.8897 | 8775.9533 | 16348.1666 | 178.9097 | 333.2795
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.554 | 11.8638 | 1.1911 | 4 | 7674.2665 | 13856.1808 | 156.4503 | 282.477 | 97.5949 | 10.6613 | 79.3123 | 3331612.3333 | 0 | 2678911.7884 | 0 | 0 | 0 | 1322690.9694 | 2859953.8855 | 7441013.3529 | 5078644.5109 | 22712826.8403 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 36564140.2805 | 66017949.4163 | 10000 | 4.7645 | 7674.2665 | 13856.1808 | 156.4503 | 282.477
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.436 | 13.831 | 1.4194 | 4 | 6828.5764 | 12016.2405 | 139.2098 | 244.9673 | 97.2089 | 10.5249 | 84.0779 | 3681856.9411 | 0 | 3014019.7056 | 0 | 0 | 0 | 1349652.289 | 3137756.2849 | 8163798.211 | 5571960.0283 | 24919043.46 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 38770356.9002 | 68224166.036 | 13335.2143 | 5.6777 | 6828.5764 | 12016.2405 | 139.2098 | 244.9673
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7324 | 15.7034 | 1.6437 | 4 | 6182.5624 | 10662.3596 | 126.0399 | 217.3666 | 96.7165 | 10.3736 | 91.7616 | 3991249.0379 | 0 | 3322705.2804 | 0 | 0 | 0 | 1338179.1201 | 3374332.041 | 8779319.8 | 5992066.1605 | 26797851.4399 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 40649164.8801 | 70102974.0159 | 17782.7941 | 6.5748 | 6182.5624 | 10662.3596 | 126.0399 | 217.3666
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9313 | 17.3858 | 1.8515 | 4 | 5691.1761 | 9668.245 | 116.0223 | 197.1003 | 96.1764 | 10.2203 | 99.43 | 4250284.979 | 0 | 3592521.9965 | 0 | 0 | 0 | 1293357.0058 | 3563103.9527 | 9270465.5919 | 6327283.2555 | 28297016.7813 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 42148330.2215 | 71602139.3573 | 23713.7371 | 7.4059 | 5691.1761 | 9668.245 | 116.0223 | 197.1003
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.8165 | 18.8351 | 2.035 | 4 | 5318.5237 | 8936.9205 | 108.4253 | 182.1912 | 95.6398 | 10.0753 | 100.738 | 4459528.2491 | 0 | 3819821.514 | 0 | 0 | 0 | 1226347.5421 | 3707221.949 | 9645431.0556 | 6583204.8892 | 29441555.1989 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 43292868.6391 | 72746677.7749 | 31622.7766 | 8.14 | 5318.5237 | 8936.9205 | 108.4253 | 182.1912
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3212 | 20.036 | 2.1905 | 4 | 5036.413 | 8397.8927 | 102.6741 | 171.2024 | 95.1465 | 9.9462 | 94.4077 | 4623298.3433 | 0 | 4004803.6254 | 0 | 0 | 0 | 1147824.0198 | 3812611.1355 | 9919632.1006 | 6770352.7367 | 30278521.9613 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 44129835.4015 | 73583644.5373 | 42169.6503 | 8.7622 | 5036.413 | 8397.8927 | 102.6741 | 171.2024
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5487 | 21.0048 | 2.3183 | 4 | 4823.0366 | 7999.2208 | 98.3241 | 163.0749 | 94.7167 | 9.8363 | 96.4488 | 4749110.6616 | 0 | 4151927.0417 | 0 | 0 | 0 | 1067246.4496 | 3887630.8196 | 10114817.9299 | 6903571.0759 | 30874303.9782 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 44725617.4183 | 74179426.5541 | 56234.1325 | 9.2733 | 4823.0366 | 7999.2208 | 98.3241 | 163.0749
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.6554 | 21.7686 | 2.4207 | 4 | 4661.7213 | 7703.5466 | 95.0355 | 157.0472 | 94.3581 | 9.7461 | 113.3909 | 4844301.1892 | 0 | 4266597.8866 | 0 | 0 | 0 | 990905.6845 | 3939703.8565 | 10250301.2902 | 6996041.2532 | 31287851.1601 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45139164.6003 | 74592973.736 | 74989.4209 | 9.6829 | 4661.7213 | 7703.5466 | 95.0355 | 157.0472
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8419 | 22.3627 | 2.5014 | 4 | 4539.8073 | 7483.5227 | 92.5501 | 152.5617 | 94.0671 | 9.6737 | 101.9647 | 4915934.1879 | 0 | 4355044.233 | 0 | 0 | 0 | 922712.2364 | 3975539.3563 | 10343537.91 | 7059677.162 | 31572445.0856 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45423758.5258 | 74877567.6616 | 100000 | 10.0057 | 4539.8073 | 7483.5227 | 92.5501 | 152.5617
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2929 | 22.8207 | 2.5642 | 4 | 4447.7109 | 7319.3579 | 90.6726 | 149.215 | 93.8355 | 9.6166 | 89.7485 | 4969699.6504 | 0 | 4422770.7852 | 0 | 0 | 0 | 864298.0265 | 4000139.7002 | 10407542.9584 | 7103361.9227 | 31767813.0432 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45619126.4834 | 75072935.6192 | 133352.1432 | 10.2568 | 4447.7109 | 7319.3579 | 90.6726 | 149.215
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.1345 | 23.1659 | 2.6122 | 4 | 4378.1803 | 7197.0103 | 89.2551 | 146.7208 | 93.6571 | 9.5729 | 95.1029 | 5009327.0322 | 0 | 4473488.6597 | 0 | 0 | 0 | 815361.1745 | 4016288.9779 | 10449560.0664 | 7132039.4623 | 31896065.373 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45747378.8132 | 75201187.949 | 177827.941 | 10.4489 | 4378.1803 | 7197.0103 | 89.2551 | 146.7208
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5371 | 23.4291 | 2.649 | 4 | 4325.7244 | 7105.3937 | 88.1857 | 144.8531 | 93.5187 | 9.5392 | 105.0405 | 5039062.9602 | 0 | 4512018.7713 | 0 | 0 | 0 | 775723.9978 | 4027454.2345 | 10478609.7736 | 7151866.4844 | 31984736.2218 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45836049.662 | 75289858.7978 | 237137.3706 | 10.5962 | 4325.7244 | 7105.3937 | 88.1857 | 144.8531
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5971 | 23.6282 | 2.677 | 4 | 4286.1822 | 7036.7838 | 87.3796 | 143.4544 | 93.4125 | 9.5134 | 107.1873 | 5061279.6291 | 0 | 4541083.3786 | 0 | 0 | 0 | 744124.8247 | 4035130.2546 | 10498581.2035 | 7165497.3957 | 32045696.6863 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45897010.1265 | 75350819.2623 | 316227.766 | 10.7081 | 4286.1822 | 7036.7838 | 87.3796 | 143.4544
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3741 | 23.7746 | 2.698 | 4 | 4256.3989 | 6985.6225 | 86.7724 | 142.4114 | 93.3339 | 9.4944 | 98.9884 | 5077421.9235 | 0 | 4562359.0155 | 0 | 0 | 0 | 719004.7729 | 4039926.4277 | 10511059.862 | 7174014.3365 | 32083786.3381 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45935099.7783 | 75388908.9141 | 421696.5034 | 10.792 | 4256.3989 | 6985.6225 | 86.7724 | 142.4114
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.966 | 23.8861 | 2.7139 | 4 | 4233.9835 | 6947.1912 | 86.3155 | 141.6279 | 93.2735 | 9.4798 | 105.914 | 5089640.5578 | 0 | 4578551.1369 | 0 | 0 | 0 | 699575.3293 | 4043429.1394 | 10520173.1993 | 7180234.3764 | 32111603.7391 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45962917.1793 | 75416726.3151 | 562341.3252 | 10.8557 | 4233.9835 | 6947.1912 | 86.3155 | 141.6279
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4265 | 23.9727 | 2.7261 | 4 | 4217.125 | 6918.2081 | 85.9718 | 141.037 | 93.2263 | 9.4684 | 109.5043 | 5099098.5528 | 0 | 4591136.1876 | 0 | 0 | 0 | 684792.3872 | 4046260.5798 | 10527540.0264 | 7185262.3873 | 32134090.1211 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45985403.5613 | 75439212.6971 | 749894.2093 | 10.9044 | 4217.125 | 6918.2081 | 85.9718 | 141.037
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.7554 | 24.0348 | 2.7351 | 4 | 4204.4536 | 6896.6625 | 85.7135 | 140.5978 | 93.1924 | 9.4603 | 111.9474 | 5105827.5928 | 0 | 4600121.6072 | 0 | 0 | 0 | 673258.2466 | 4047890.9042 | 10531781.7961 | 7188157.4823 | 32147037.6291 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 45998351.0693 | 75452160.2051 | 1000000 | 10.9404 | 4204.4536 | 6896.6625 | 85.7135 | 140.5978
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.9944 | 24.0801 | 2.7418 | 4 | 4194.934 | 6880.5931 | 85.5194 | 140.2702 | 93.1677 | 9.4543 | 100.4694 | 5110700.8912 | 0 | 4606645.6033 | 0 | 0 | 0 | 664372.7284 | 4048870.4969 | 10534330.4954 | 7189897.022 | 32154817.2372 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46006130.6774 | 75459939.8132 | 1333521.4322 | 10.9671 | 4194.934 | 6880.5931 | 85.5194 | 140.2702
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.177 | 24.1147 | 2.7468 | 4 | 4187.7852 | 6868.5065 | 85.3737 | 140.0238 | 93.1488 | 9.4498 | 111.1695 | 5114418.3161 | 0 | 4611630.3637 | 0 | 0 | 0 | 657671.3816 | 4049650.824 | 10536360.7463 | 7191282.7099 | 32161014.3416 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46012327.7818 | 75466136.9176 | 1778279.41 | 10.9873 | 4187.7852 | 6868.5065 | 85.3737 | 140.0238
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.3233 | 24.1422 | 2.7507 | 4 | 4182.4186 | 6859.3421 | 85.2643 | 139.837 | 93.1336 | 9.4461 | 102.6999 | 5117393.2894 | 0 | 4615623.4597 | 0 | 0 | 0 | 652714.7235 | 4050435.2743 | 10538401.7252 | 7192675.7199 | 32167244.1919 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46018557.6321 | 75472366.7679 | 2371373.7057 | 11.0029 | 4182.4186 | 6859.3421 | 85.2643 | 139.837
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.4398 | 24.164 | 2.7537 | 4 | 4178.3908 | 6852.3971 | 85.1821 | 139.6954 | 93.1215 | 9.4432 | 106.9286 | 5119759.9377 | 0 | 4618802.4532 | 0 | 0 | 0 | 649054.0095 | 4051170.3962 | 10540314.3615 | 7193981.1335 | 32173082.2916 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46024395.7317 | 75478204.8675 | 3162277.6602 | 11.0149 | 4178.3908 | 6852.3971 | 85.1821 | 139.6954
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5083 | 24.1771 | 2.7558 | 4 | 4175.3685 | 6847.3925 | 85.1205 | 139.5934 | 93.1143 | 9.4415 | 102.3691 | 5121148.5952 | 0 | 4620672.0187 | 0 | 0 | 0 | 646063.5884 | 4051274.8389 | 10540586.1 | 7194166.6006 | 32173911.7418 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46025225.1819 | 75479034.3177 | 4216965.0343 | 11.023 | 4175.3685 | 6847.3925 | 85.1205 | 139.5934
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5667 | 24.1882 | 2.7574 | 4 | 4173.101 | 6843.5646 | 85.0743 | 139.5153 | 93.1083 | 9.44 | 95.8476 | 5122331.0737 | 0 | 4622263.5267 | 0 | 0 | 0 | 643897.5712 | 4051511.947 | 10541203.0066 | 7194587.6521 | 32175794.7773 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46027108.2175 | 75480917.3532 | 5623413.2519 | 11.0295 | 4173.101 | 6843.5646 | 85.0743 | 139.5153
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6056 | 24.1956 | 2.7585 | 4 | 4171.4 | 6840.7463 | 85.0396 | 139.4579 | 93.1042 | 9.439 | 96.6172 | 5123118.4058 | 0 | 4623324.456 | 0 | 0 | 0 | 642209.3505 | 4051574.3628 | 10541365.3998 | 7194698.4888 | 32176290.4637 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46027603.9039 | 75481413.0397 | 7498942.0933 | 11.0341 | 4171.4 | 6840.7463 | 85.0396 | 139.4579
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.6445 | 24.2029 | 2.7595 | 4 | 4170.124 | 6838.5284 | 85.0136 | 139.4127 | 93.1002 | 9.4381 | 101.7007 | 5123906.8064 | 0 | 4624385.3244 | 0 | 0 | 0 | 641059.1284 | 4051846.9911 | 10542074.7227 | 7195182.6162 | 32178455.5891 | 961560.8286 | 12889752.6116 | 12889752.6116 | 10890904.1141 | 5673152.4101 | 0 | 46029769.0293 | 75483578.1651 | 10000000 | 11.038 | 4170.124 | 6838.5284 | 85.0136 | 139.4127
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2236 | 0.057103 | 0.0037002 | 4 | 1036803.8292 | 3088615.1785 | 21136.6484 | 62965.5981 | 68.6471 | 9.8591 | 125.2272 | 137257.687 | 0 | 74237.3148 | 0 | 0 | 0 | 120225.4226 | 129370.9655 | 336596.7147 | 229734.1741 | 1027422.2788 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 15345676.1305 | 45714422.4246 | 100 | 0.014801 | 1036803.8292 | 3088615.1785 | 21136.6484 | 62965.5981
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.12426 | 0.0081762 | 4 | 481506.035 | 1410075.4016 | 9816.1518 | 28746.2943 | 75.4295 | 10.2991 | 189.2196 | 192902.3915 | 0 | 111340.8053 | 0 | 0 | 0 | 157243.5452 | 179979.8294 | 468270.5971 | 319604.3045 | 1429341.473 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 15747595.3246 | 46116341.6188 | 133.3521 | 0.032705 | 481506.035 | 1410075.4016 | 9816.1518 | 28746.2943
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.21695 | 0.014933 | 4 | 271252.2654 | 779679.0662 | 5529.8443 | 15894.8124 | 80.8139 | 10.6077 | 243.0712 | 256818.0718 | 0 | 154830.7662 | 0 | 0 | 0 | 196588.2668 | 237212.4708 | 617178.1901 | 421236.7965 | 1883864.5622 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 16202118.4139 | 46570864.708 | 177.8279 | 0.059731 | 271252.2654 | 779679.0662 | 5529.8443 | 15894.8124
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1567 | 0.34462 | 0.024635 | 4 | 169938.3529 | 478128.5158 | 3464.4232 | 9747.2965 | 85.2998 | 10.8392 | 59.0707 | 333424.1 | 0 | 208143.4305 | 0 | 0 | 0 | 242126.5184 | 305640.6791 | 795214.3514 | 542750.1349 | 2427299.2143 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 16745553.0659 | 47114299.3601 | 237.1374 | 0.098539 | 169938.3529 | 478128.5158 | 3464.4232 | 9747.2965
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1702 | 0.51264 | 0.038108 | 4 | 113969.1878 | 313197.5431 | 2323.416 | 6384.9555 | 88.9041 | 11.0093 | 44.9865 | 422447.4061 | 0 | 271611.6118 | 0 | 0 | 0 | 292066.2417 | 384588.8512 | 1000621.3009 | 682944.5986 | 3054280.0102 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 17372533.8619 | 47741280.156 | 316.2278 | 0.15243 | 113969.1878 | 313197.5431 | 2323.416 | 6384.9555
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4802 | 0.73512 | 0.05649 | 4 | 80193.8924 | 214591.9349 | 1634.861 | 4374.7468 | 91.8552 | 11.1394 | 59.6111 | 528580.9731 | 0 | 349168.2265 | 0 | 0 | 0 | 349937.2641 | 478797.7209 | 1245733.4548 | 850238.6801 | 3802456.3195 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 18120710.1712 | 48489456.4653 | 421.6965 | 0.22596 | 80193.8924 | 214591.9349 | 1634.861 | 4374.7468
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2124 | 1.033 | 0.081463 | 4 | 58391.188 | 151589.3826 | 1190.3833 | 3090.3546 | 94.2842 | 11.2398 | 50.3763 | 657833.4496 | 0 | 442174.6834 | 0 | 0 | 0 | 420237.5915 | 592895.8325 | 1542593.3366 | 1052851.6494 | 4708586.543 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 19026840.3946 | 49395586.6887 | 562.3413 | 0.32585 | 58391.188 | 151589.3826 | 1190.3833 | 3090.3546
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3707 | 1.4098 | 0.1148 | 4 | 43641.3673 | 109777.2907 | 889.6883 | 2237.9586 | 96.1548 | 11.3123 | 53.2431 | 806320.7583 | 0 | 545192.4435 | 0 | 0 | 0 | 495700.1243 | 720413.1972 | 1874367.3621 | 1279294.239 | 5721288.1244 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 20039541.9761 | 50408288.2702 | 749.8942 | 0.45919 | 43641.3673 | 109777.2907 | 889.6883 | 2237.9586
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1091 | 1.8917 | 0.15882 | 4 | 33411.6862 | 81216.6305 | 681.1424 | 1655.7109 | 97.6238 | 11.3651 | 52.0373 | 980448.1175 | 0 | 669302.9588 | 0 | 0 | 0 | 580281.9603 | 869712.8843 | 2262814.5222 | 1544417.4076 | 6906977.8507 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 21225231.7024 | 51593977.9965 | 1000 | 0.63526 | 33411.6862 | 81216.6305 | 681.1424 | 1655.7109
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5682 | 2.504 | 0.21647 | 4 | 26110.7257 | 61182.8598 | 532.3025 | 1247.2954 | 98.7661 | 11.4011 | 56.5453 | 1184050.3511 | 0 | 818318.5103 | 0 | 0 | 0 | 674474.819 | 1043969.0353 | 2716193.2824 | 1853857.7274 | 8290863.7254 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 22609117.577 | 52977863.8711 | 1333.5214 | 0.86589 | 26110.7257 | 61182.8598 | 532.3025 | 1247.2954
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9165 | 3.2773 | 0.29137 | 4 | 20779.858 | 46836.5095 | 423.6255 | 954.8256 | 99.6414 | 11.4219 | 58.623 | 1421298.4543 | 0 | 996559.2623 | 0 | 0 | 0 | 778666.6197 | 1246644.4912 | 3243513.2441 | 2213764.4366 | 9900446.5082 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 24218700.3599 | 54587446.654 | 1778.2794 | 1.1655 | 20779.858 | 46836.5095 | 423.6255 | 954.8256
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3144 | 4.2415 | 0.38757 | 4 | 16814.304 | 36403.6907 | 342.7823 | 742.1385 | 100.2904 | 11.4271 | 66.3342 | 1694684.9234 | 0 | 1207331.9359 | 0 | 0 | 0 | 891143.0138 | 1479332.3505 | 3848919.3232 | 2626966.5255 | 11748378.0723 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 26066631.9239 | 56435378.2181 | 2371.3737 | 1.5503 | 16814.304 | 36403.6907 | 342.7823 | 742.1385
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.9434 | 5.4307 | 0.50951 | 4 | 13820.5341 | 28721.3841 | 281.7503 | 585.5243 | 100.7448 | 11.4146 | 62.6529 | 2006720.8189 | 0 | 1454242.4071 | 0 | 0 | 0 | 1010336.7216 | 1743806.9796 | 4537028.0569 | 3096614.8754 | 13848749.8594 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 28167003.7111 | 58535750.0052 | 3162.2777 | 2.0381 | 13820.5341 | 28721.3841 | 281.7503 | 585.5243
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.936 | 6.871 | 0.66123 | 4 | 11535.0308 | 23016.9187 | 235.1572 | 469.231 | 101.0205 | 11.3805 | 64.561 | 2356686.5566 | 0 | 1738696.2483 | 0 | 0 | 0 | 1132168.303 | 2038744.9321 | 5304396.1092 | 3620359.339 | 16191051.4882 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 30509305.3399 | 60878051.634 | 4216.965 | 2.6449 | 11535.0308 | 23016.9187 | 235.1572 | 469.231
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.2728 | 8.5625 | 0.84461 | 4 | 9777.4447 | 18766.4591 | 199.3264 | 382.5797 | 101.121 | 11.3202 | 70.3079 | 2737197.8393 | 0 | 2056923.4063 | 0 | 0 | 0 | 1248053.8753 | 2356448.2971 | 6130995.0952 | 4184530.1318 | 18714148.645 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 33032402.4967 | 63401148.7908 | 5623.4133 | 3.3784 | 9777.4447 | 18766.4591 | 199.3264 | 382.5797
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.7092 | 10.4648 | 1.0574 | 4 | 8421.9611 | 15602.2651 | 171.6931 | 318.0733 | 101.0432 | 11.2295 | 75.3539 | 3133188.4596 | 0 | 2398640.4327 | 0 | 0 | 0 | 1345883.7504 | 2682307.9306 | 6978815.0185 | 4763184.6504 | 21302020.2423 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 35620274.0939 | 65989020.3881 | 7498.9421 | 4.2295 | 8421.9611 | 15602.2651 | 171.6931 | 318.0733
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.7466 | 12.4898 | 1.2915 | 4 | 7378.0698 | 13256.6504 | 150.4119 | 270.2547 | 100.7895 | 11.1082 | 73.9192 | 3523183.7226 | 0 | 2747240.5322 | 0 | 0 | 0 | 1412786.7975 | 2996452.3104 | 7796154.2548 | 5321035.4739 | 23796853.0914 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 38115106.9431 | 68483853.2372 | 10000 | 5.166 | 7378.0698 | 13256.6504 | 150.4119 | 270.2547
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.7593 | 14.5233 | 1.5344 | 4 | 6577.4863 | 11525.5342 | 134.091 | 234.9636 | 100.3827 | 10.9616 | 92.1307 | 3885801.7008 | 0 | 3084337.3308 | 0 | 0 | 0 | 1440926.9468 | 3280315.7316 | 8534708.6483 | 5825114.0232 | 26051204.3816 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 40369458.2333 | 70738204.5274 | 13335.2143 | 6.1375 | 6577.4863 | 11525.5342 | 134.091 | 234.9636
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.0862 | 16.4421 | 1.7711 | 4 | 5966.495 | 10253.2216 | 121.6351 | 209.0258 | 99.8717 | 10.8011 | 79.4377 | 4203352.5735 | 0 | 3392249.9992 | 0 | 0 | 0 | 1428711.6206 | 3519482.5354 | 9156971.6119 | 6249821.2821 | 27950589.6226 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 42268843.4742 | 72637589.7684 | 17782.7941 | 7.0844 | 5966.495 | 10253.2216 | 121.6351 | 209.0258
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2749 | 18.1593 | 1.9892 | 4 | 5502.1462 | 9318.8866 | 112.1687 | 189.9781 | 99.316 | 10.6397 | 87.9651 | 4468286.7917 | 0 | 3660444.2426 | 0 | 0 | 0 | 1383179.6582 | 3709645.1701 | 9651735.7797 | 6587507.993 | 29460799.6354 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 43779053.4871 | 74147799.7812 | 23713.7371 | 7.9567 | 5502.1462 | 9318.8866 | 112.1687 | 189.9781
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1212 | 19.6329 | 2.1809 | 4 | 5150.2786 | 8631.5236 | 104.9954 | 175.9653 | 98.7679 | 10.4881 | 95.2111 | 4681613.9755 | 0 | 3885613.4974 | 0 | 0 | 0 | 1315837.4689 | 3854395.3273 | 10028345.9964 | 6844552.2044 | 30610358.4699 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 44928612.3215 | 75297358.6156 | 31622.7766 | 8.7235 | 5150.2786 | 8631.5236 | 104.9954 | 175.9653
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5667 | 20.8491 | 2.3426 | 4 | 4884.1122 | 8125.0063 | 99.5692 | 165.6392 | 98.2671 | 10.3539 | 92.5655 | 4848005.9002 | 0 | 4068163.934 | 0 | 0 | 0 | 1237419.5165 | 3959899.8468 | 10302847.1141 | 7031904.8577 | 31448241.1693 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 45766495.0209 | 76135241.3151 | 42169.6503 | 9.3705 | 4884.1122 | 8125.0063 | 99.5692 | 165.6392
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7413 | 21.8292 | 2.4752 | 4 | 4682.9618 | 7750.2931 | 95.4685 | 158.0002 | 97.8322 | 10.24 | 89.5169 | 4975798.3392 | 0 | 4213247.6219 | 0 | 0 | 0 | 1157661.428 | 4035215.8817 | 10498803.9877 | 7165649.4505 | 32046376.709 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 46364630.5607 | 76733376.8548 | 56234.1325 | 9.9007 | 4682.9618 | 7750.2931 | 95.4685 | 158.0002
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8091 | 22.6022 | 2.5813 | 4 | 4531.026 | 7472.3063 | 92.3711 | 152.3331 | 97.4695 | 10.1466 | 102.9368 | 5072613.7775 | 0 | 4326427.3374 | 0 | 0 | 0 | 1082706.2302 | 4087881.4646 | 10635829.031 | 7259171.8581 | 32464629.6988 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 46782883.5504 | 77151629.8446 | 74989.4209 | 10.325 | 4531.026 | 7472.3063 | 92.3711 | 152.3331
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9567 | 23.202 | 2.6646 | 4 | 4416.3118 | 7265.5675 | 90.0325 | 148.1184 | 97.1763 | 10.0719 | 99.277 | 5145308.9229 | 0 | 4413496.9324 | 0 | 0 | 0 | 1016025.3309 | 4124184.1626 | 10730281.2046 | 7323637.4074 | 32752933.9608 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47071187.8125 | 77439934.1066 | 100000 | 10.6585 | 4416.3118 | 7265.5675 | 90.0325 | 148.1184
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.3586 | 23.6609 | 2.7292 | 4 | 4329.7425 | 7111.5706 | 88.2677 | 144.979 | 96.945 | 10.0135 | 94.3796 | 5199469.3343 | 0 | 4479650.9522 | 0 | 0 | 0 | 958953.329 | 4148848.71 | 10794453.2976 | 7367436.1795 | 32948811.8027 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47267065.6543 | 77635811.9485 | 133352.1432 | 10.9168 | 4329.7425 | 7111.5706 | 88.2677 | 144.979
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2 | 24.0132 | 2.779 | 4 | 4264.4517 | 6996.4109 | 86.9366 | 142.6313 | 96.7633 | 9.9679 | 107.8257 | 5240217.3262 | 0 | 4530201.1589 | 0 | 0 | 0 | 911897.6906 | 4166103.3085 | 10839346.2235 | 7398076.5238 | 33085842.2316 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47404096.0833 | 77772842.3774 | 177827.941 | 11.1161 | 4264.4517 | 6996.4109 | 86.9366 | 142.6313
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5936 | 24.2803 | 2.8171 | 4 | 4215.2433 | 6910.3147 | 85.9334 | 140.8761 | 96.6232 | 9.9329 | 96.9057 | 5270606.5551 | 0 | 4568364.4278 | 0 | 0 | 0 | 873801.4907 | 4177981.2647 | 10870250.229 | 7419169.1426 | 33180173.1099 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47498426.9615 | 77867173.2557 | 237137.3706 | 11.2683 | 4215.2433 | 6910.3147 | 85.9334 | 140.8761
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.6387 | 24.481 | 2.8459 | 4 | 4178.1829 | 6845.9532 | 85.1779 | 139.564 | 96.5166 | 9.9064 | 109.1019 | 5293142.5409 | 0 | 4596934.6289 | 0 | 0 | 0 | 843425.016 | 4186065.8524 | 10891284.6679 | 7433525.5793 | 33244378.2854 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47562632.1371 | 77931378.4312 | 316227.766 | 11.3836 | 4178.1829 | 6845.9532 | 85.1779 | 139.564
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.4204 | 24.6313 | 2.8677 | 4 | 4150.2918 | 6797.8126 | 84.6093 | 138.5826 | 96.4361 | 9.8865 | 101.3716 | 5309851.7488 | 0 | 4618271.8664 | 0 | 0 | 0 | 819536.76 | 4191587.5463 | 10905650.9827 | 7443330.8844 | 33288229.7886 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47606483.6402 | 77975229.9344 | 421696.5034 | 11.4706 | 4150.2918 | 6797.8126 | 84.6093 | 138.5826
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.0271 | 24.7477 | 2.8843 | 4 | 4129.3148 | 6761.5444 | 84.1817 | 137.8432 | 96.3731 | 9.8709 | 96.6106 | 5322740.5541 | 0 | 4634818.7682 | 0 | 0 | 0 | 801252.9924 | 4195936.8027 | 10916966.8557 | 7451054.2002 | 33322770.1732 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47641024.0249 | 78009770.319 | 562341.3252 | 11.5373 | 4129.3148 | 6761.5444 | 84.1817 | 137.8432
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4681 | 24.8326 | 2.8967 | 4 | 4113.5475 | 6734.5218 | 83.8602 | 137.2923 | 96.3271 | 9.8595 | 98.6616 | 5332059.5551 | 0 | 4646835.743 | 0 | 0 | 0 | 786985.4379 | 4198693.4871 | 10924139.1829 | 7455949.4609 | 33344662.8669 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47662916.7185 | 78031663.0127 | 749894.2093 | 11.5868 | 4113.5475 | 6734.5218 | 83.8602 | 137.2923
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.7971 | 24.8961 | 2.906 | 4 | 4101.7018 | 6714.2889 | 83.6187 | 136.8799 | 96.2926 | 9.851 | 101.0018 | 5338984.6739 | 0 | 4655794.1474 | 0 | 0 | 0 | 776047.5956 | 4200622.3026 | 10929157.5652 | 7459374.61 | 33359980.8946 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47678234.7463 | 78046981.0404 | 1000000 | 11.624 | 4101.7018 | 6714.2889 | 83.6187 | 136.8799
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.0406 | 24.9431 | 2.913 | 4 | 4092.806 | 6699.1551 | 83.4374 | 136.5713 | 96.2669 | 9.8447 | 103.1886 | 5344097.7969 | 0 | 4662424.602 | 0 | 0 | 0 | 767681.5742 | 4201939.5495 | 10932584.7714 | 7461713.7487 | 33370442.0426 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47688695.8943 | 78057442.1884 | 1333521.4322 | 11.6518 | 4092.806 | 6699.1551 | 83.4374 | 136.5713
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.2381 | 24.981 | 2.9184 | 4 | 4086.1277 | 6687.6572 | 83.3012 | 136.3369 | 96.2461 | 9.8395 | 103.1477 | 5348235.5864 | 0 | 4667797.5864 | 0 | 0 | 0 | 761524.5287 | 4203247.5036 | 10935987.7997 | 7464036.3854 | 33380829.3901 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47699083.2417 | 78067829.5359 | 1778279.41 | 11.6734 | 4086.1277 | 6687.6572 | 83.3012 | 136.3369
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3696 | 25.0065 | 2.9222 | 4 | 4081.1153 | 6679.2074 | 83.1991 | 136.1647 | 96.2322 | 9.8361 | 105.072 | 5350985.2758 | 0 | 4671375.5178 | 0 | 0 | 0 | 756656.8151 | 4203816.8674 | 10937469.1675 | 7465047.4493 | 33385351.0929 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47703604.9445 | 78072351.2387 | 2371373.7057 | 11.6889 | 4081.1153 | 6679.2074 | 83.1991 | 136.1647
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.4887 | 25.0292 | 2.9254 | 4 | 4077.3542 | 6672.6615 | 83.1224 | 136.0312 | 96.2196 | 9.833 | 92.7088 | 5353475.6228 | 0 | 4674615.7593 | 0 | 0 | 0 | 753242.5496 | 4204720.2333 | 10939819.5404 | 7466651.6272 | 33392525.3325 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47710779.1842 | 78079525.4783 | 3162277.6602 | 11.7014 | 4077.3542 | 6672.6615 | 83.1224 | 136.0312
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5593 | 25.0429 | 2.9275 | 4 | 4074.5323 | 6667.9457 | 83.0649 | 135.9351 | 96.2122 | 9.8312 | 105.9547 | 5354947.35 | 0 | 4676534.8928 | 0 | 0 | 0 | 750432.156 | 4204946.6156 | 10940408.5405 | 7467053.6318 | 33394323.1868 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47712577.0385 | 78081323.3326 | 4216965.0343 | 11.71 | 4074.5323 | 6667.9457 | 83.0649 | 135.9351
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.613 | 25.0534 | 2.9291 | 4 | 4072.4154 | 6664.4013 | 83.0217 | 135.8628 | 96.2064 | 9.8298 | 99.8369 | 5356067.1328 | 0 | 4677995.7013 | 0 | 0 | 0 | 748327.5357 | 4205132.2442 | 10940891.5082 | 7467383.2672 | 33395797.3895 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47714051.2411 | 78082797.5353 | 5623413.2519 | 11.7164 | 4072.4154 | 6664.4013 | 83.0217 | 135.8628
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6667 | 25.0636 | 2.9305 | 4 | 4070.8275 | 6661.6062 | 82.9893 | 135.8059 | 96.2008 | 9.8284 | 92.9688 | 5357188.2105 | 0 | 4679456.3957 | 0 | 0 | 0 | 746914.1868 | 4205587.9293 | 10942077.1073 | 7468192.4629 | 33399416.2925 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47717670.1442 | 78086416.4383 | 7498942.0933 | 11.7219 | 4070.8275 | 6661.6062 | 82.9893 | 135.8059
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.701 | 25.0702 | 2.9314 | 4 | 4069.6365 | 6659.5718 | 82.965 | 135.7644 | 96.1971 | 9.8275 | 99.1539 | 5357902.4419 | 0 | 4680388.1584 | 0 | 0 | 0 | 745776.2322 | 4205786.0647 | 10942592.615 | 7468544.3075 | 33400989.8199 | 961560.8286 | 13356693.023 | 13356693.023 | 11179097.8575 | 5832955.4136 | 0 | 47719243.6715 | 78087989.9657 | 10000000 | 11.7257 | 4069.6365 | 6659.5718 | 82.965 | 135.7644
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.060759 | 0.0039741 | 4 | 999507.7854 | 2968365.691 | 20376.3181 | 60514.1496 | 70.5313 | 10.3018 | 135.7189 | 146553.7052 | 0 | 78285.9091 | 0 | 0 | 0 | 129464.5509 | 138178.6244 | 359512.4364 | 245374.6251 | 1097369.851 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 15888424.205 | 47185878.8711 | 100 | 0.015896 | 999507.7854 | 2968365.691 | 20376.3181 | 60514.1496
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.13162 | 0.0088518 | 4 | 460708.7811 | 1344635.2593 | 9392.1717 | 27412.2085 | 77.5574 | 10.7505 | 206.9829 | 205447.7444 | 0 | 116979.8447 | 0 | 0 | 0 | 168782.465 | 191571.9211 | 498430.842 | 340189.2914 | 1521402.1086 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 16312456.4626 | 47609911.1286 | 133.3521 | 0.035407 | 460708.7811 | 1344635.2593 | 9392.1717 | 27412.2085
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.229 | 0.016218 | 4 | 258781.364 | 741215.897 | 5275.6081 | 15110.6886 | 83.1234 | 11.0645 | 279.9688 | 272696.2622 | 0 | 162044.3037 | 0 | 0 | 0 | 210064.9232 | 251474.1408 | 654284.1298 | 446562.3628 | 1997126.1225 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 16788180.4765 | 48085635.1425 | 177.8279 | 0.064874 | 258781.364 | 741215.897 | 5275.6081 | 15110.6886
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2929 | 0.36497 | 0.026815 | 4 | 161930.3975 | 453720.1892 | 3301.1702 | 9249.6998 | 87.8435 | 11.3044 | 62.346 | 354670.3008 | 0 | 218212.4329 | 0 | 0 | 0 | 259353.0806 | 324571.9676 | 844469.6808 | 576367.9093 | 2577645.3721 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 17368699.7261 | 48666154.3921 | 237.1374 | 0.10726 | 161930.3975 | 453720.1892 | 3301.1702 | 9249.6998
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 0.54482 | 0.041547 | 4 | 108562.3383 | 296886.5155 | 2213.1901 | 6052.4332 | 91.6403 | 11.4807 | 55.5014 | 450324.6587 | 0 | 285356.3139 | 0 | 0 | 0 | 313906.879 | 409339.2621 | 1065016.7931 | 726895.8452 | 3250839.752 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 18041894.106 | 49339348.772 | 316.2278 | 0.16619 | 108562.3383 | 296886.5155 | 2213.1901 | 6052.4332
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7165 | 0.7798 | 0.061608 | 4 | 76403.9224 | 203405.5838 | 1557.5973 | 4146.698 | 94.6967 | 11.6132 | 63.7439 | 562489.6102 | 0 | 366044.5484 | 0 | 0 | 0 | 375016.2173 | 508384.6466 | 1322712.5665 | 902778.5056 | 4037426.0947 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 18828480.4487 | 50125935.1147 | 421.6965 | 0.24643 | 76403.9224 | 203405.5838 | 1557.5973 | 4146.698
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5218 | 1.0962 | 0.089041 | 4 | 55509.4253 | 143383.4593 | 1131.6347 | 2923.0658 | 97.2334 | 11.7163 | 51.6905 | 700041.2639 | 0 | 457290.1871 | 0 | 0 | 0 | 450329.4059 | 626987.7342 | 1631293.4714 | 1113391.314 | 4979333.3764 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 19770387.7304 | 51067842.3964 | 562.3413 | 0.35616 | 55509.4253 | 143383.4593 | 1131.6347 | 2923.0658
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7728 | 1.4967 | 0.12549 | 4 | 41518.0675 | 103866.274 | 846.402 | 2117.4545 | 99.1881 | 11.7907 | 53.0499 | 858181.5907 | 0 | 563829.1814 | 0 | 0 | 0 | 531371.3899 | 761819.0432 | 1982096.8797 | 1352821.8484 | 6050119.9333 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 20841174.2872 | 52138628.9533 | 749.8942 | 0.50198 | 41518.0675 | 103866.274 | 846.402 | 2117.4545
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6233 | 2.0081 | 0.17359 | 4 | 31815.3529 | 76888.3936 | 648.599 | 1567.4739 | 100.7202 | 11.8445 | 51.8221 | 1043283.1508 | 0 | 691943.2685 | 0 | 0 | 0 | 621905.0408 | 919281.2695 | 2391781.2926 | 1632439.8784 | 7300633.9006 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 22091688.2546 | 53389142.9206 | 1000 | 0.69437 | 31815.3529 | 76888.3936 | 648.599 | 1567.4739
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2159 | 2.6567 | 0.2365 | 4 | 24890.7554 | 57974.1348 | 507.4317 | 1181.8812 | 101.9097 | 11.8808 | 73.781 | 1259241.4421 | 0 | 845443.2386 | 0 | 0 | 0 | 722347.2947 | 1102542.4704 | 2868589.3455 | 1957871.1719 | 8756034.9632 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 23547089.3172 | 54844543.9832 | 1333.5214 | 0.94602 | 24890.7554 | 57974.1348 | 507.4317 | 1181.8812
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.713 | 3.4726 | 0.31806 | 4 | 19832.0529 | 44432.234 | 404.3032 | 905.8112 | 102.8188 | 11.9011 | 54.2184 | 1509909.7257 | 0 | 1028315.1448 | 0 | 0 | 0 | 832559.3586 | 1314605.8494 | 3420334.7573 | 2334448.7527 | 10440173.5885 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 25231227.9425 | 56528682.6085 | 1778.2794 | 1.2722 | 19832.0529 | 44432.234 | 404.3032 | 905.8112
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.3233 | 4.4948 | 0.42288 | 4 | 16066.9442 | 34569.5249 | 327.5464 | 704.7465 | 103.4964 | 11.9048 | 61.7812 | 1800250.0475 | 0 | 1245674.3279 | 0 | 0 | 0 | 953256.2119 | 1559680.429 | 4057968.5419 | 2769646.9128 | 12386476.471 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 27177530.825 | 58474985.4911 | 2371.3737 | 1.6915 | 16066.9442 | 34569.5249 | 327.5464 | 704.7465
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.1903 | 5.7515 | 0.55547 | 4 | 13223.1674 | 27309.0844 | 269.5722 | 556.7326 | 103.9681 | 11.8895 | 70.3472 | 2130546.4459 | 0 | 1499483.4742 | 0 | 0 | 0 | 1080420.546 | 1837075.6818 | 4779694.0879 | 3262239.4279 | 14589459.6637 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 29380514.0177 | 60677968.6837 | 3162.2777 | 2.2219 | 13223.1674 | 27309.0844 | 269.5722 | 556.7326
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.4387 | 7.2684 | 0.71995 | 4 | 11051.5087 | 21919.414 | 225.3 | 446.8569 | 104.2516 | 11.8509 | 78.1596 | 2499628.0393 | 0 | 1790842.8288 | 0 | 0 | 0 | 1209609.0429 | 2145031.1653 | 5580931.0857 | 3809100.1427 | 17035142.3047 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 31826196.6587 | 63123651.3247 | 4216.965 | 2.8798 | 11051.5087 | 21919.414 | 225.3 | 446.8569
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.0413 | 9.044 | 0.91805 | 4 | 9381.4677 | 17904.3102 | 191.2539 | 365.0036 | 104.3508 | 11.784 | 82.3011 | 2899573.2794 | 0 | 2115774.6516 | 0 | 0 | 0 | 1332027.3618 | 2475476.3642 | 6440681.7096 | 4395897.6096 | 19659430.9762 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 34450485.3302 | 65747939.9962 | 5623.4133 | 3.6722 | 9381.4677 | 17904.3102 | 191.2539 | 365.0036
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.7017 | 11.0279 | 1.1465 | 4 | 8094.0274 | 14918.3379 | 165.0077 | 304.1305 | 104.2628 | 11.685 | 73.7788 | 3312980.9949 | 0 | 2462466.1279 | 0 | 0 | 0 | 1434017.0483 | 2811691.0268 | 7315443.2945 | 4992940.3658 | 22329538.8582 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 37120593.2122 | 68418047.8782 | 7498.9421 | 4.5862 | 8094.0274 | 14918.3379 | 165.0077 | 304.1305
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.9339 | 13.1319 | 1.3967 | 4 | 7103.2839 | 12705.3021 | 144.81 | 259.0148 | 103.9914 | 11.5536 | 80.1271 | 3718602.8983 | 0 | 2814983.7555 | 0 | 0 | 0 | 1503758.9227 | 3134564.7748 | 8155494.5564 | 5566292.6134 | 24893697.5211 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 39684751.8751 | 70982206.5411 | 10000 | 5.5868 | 7103.2839 | 12705.3021 | 144.81 | 259.0148
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.025 | 15.2237 | 1.654 | 4 | 6344.1423 | 11074.7447 | 129.3339 | 225.7737 | 103.5656 | 11.3972 | 86.9888 | 4091905.755 | 0 | 3152530.2164 | 0 | 0 | 0 | 1531567.5111 | 3422641.3581 | 8905010.7336 | 6077852.8053 | 27181508.3795 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 41972562.7335 | 73270017.3995 | 13335.2143 | 6.616 | 6344.1423 | 11074.7447 | 129.3339 | 225.7737
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3929 | 17.1912 | 1.9034 | 4 | 5765.2883 | 9875.9587 | 117.5332 | 201.3348 | 103.0358 | 11.2272 | 94.2184 | 4417908.4272 | 0 | 3460060.2667 | 0 | 0 | 0 | 1518802.0864 | 3664740.6043 | 9534903.3108 | 6507767.4323 | 29104182.1277 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 43895236.4817 | 75192691.1477 | 17782.7941 | 7.6137 | 5765.2883 | 9875.9587 | 117.5332 | 201.3348
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.577 | 18.9443 | 2.132 | 4 | 5325.7149 | 8995.7077 | 108.5719 | 183.3897 | 102.4645 | 11.0574 | 99.63 | 4688803.7253 | 0 | 3726858.3474 | 0 | 0 | 0 | 1472545.8733 | 3856401.0989 | 10033564.6028 | 6848114.0105 | 30626287.6582 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 45417342.0122 | 76714796.6782 | 23713.7371 | 8.5279 | 5325.7149 | 8995.7077 | 108.5719 | 183.3897
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3649 | 20.4388 | 2.3317 | 4 | 4992.8639 | 8348.5776 | 101.7863 | 170.197 | 101.9066 | 10.8994 | 104.0042 | 4905557.5746 | 0 | 3949399.1335 | 0 | 0 | 0 | 1404284.4639 | 4001104.057 | 10410052.0171 | 7105074.4069 | 31775471.6529 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 46566526.0069 | 77863980.673 | 31622.7766 | 9.3266 | 4992.8639 | 8348.5776 | 101.7863 | 170.197
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7593 | 21.6714 | 2.4997 | 4 | 4741.2586 | 7871.4233 | 96.657 | 160.4696 | 101.3985 | 10.7601 | 90.7991 | 5074665.1034 | 0 | 4129794.8488 | 0 | 0 | 0 | 1325895.5248 | 4106838.636 | 10685151.7025 | 7292835.5949 | 32615181.4105 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 47406235.7645 | 78703690.4305 | 42169.6503 | 9.9987 | 4741.2586 | 7871.4233 | 96.657 | 160.4696
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8749 | 22.6614 | 2.6369 | 4 | 4551.2481 | 7518.5317 | 92.7833 | 153.2754 | 100.9594 | 10.6423 | 103.0689 | 5204180.6588 | 0 | 4272704.6842 | 0 | 0 | 0 | 1246577.3755 | 4182150.4602 | 10881097.6205 | 7426572.7102 | 33213283.5094 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 48004337.8634 | 79301792.5294 | 56234.1325 | 10.5475 | 4551.2481 | 7518.5317 | 92.7833 | 153.2754
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8897 | 23.441 | 2.7464 | 4 | 4407.8342 | 7256.754 | 89.8597 | 147.9387 | 100.5943 | 10.546 | 102.7113 | 5302206.9954 | 0 | 4384028.575 | 0 | 0 | 0 | 1172484.2532 | 4234900.7312 | 11018343.005 | 7520245.5052 | 33632209.065 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 48423263.419 | 79720718.085 | 74989.4209 | 10.9857 | 4407.8342 | 7256.754 | 89.8597 | 147.9387
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130 | 24.0465 | 2.8325 | 4 | 4299.6393 | 7062.0135 | 87.654 | 143.9687 | 100.2991 | 10.469 | 90.3455 | 5375944.9025 | 0 | 4469788.8165 | 0 | 0 | 0 | 1107027.1743 | 4271576.7484 | 11113766.4785 | 7585373.9866 | 33923478.1068 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 48714532.4608 | 80011987.1268 | 100000 | 11.3299 | 4299.6393 | 7062.0135 | 87.654 | 143.9687
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.3802 | 24.511 | 2.8992 | 4 | 4218.0552 | 6916.8944 | 85.9908 | 141.0102 | 100.0657 | 10.4087 | 107.0212 | 5431062.7724 | 0 | 4535140.2694 | 0 | 0 | 0 | 1051362.5162 | 4296850.5676 | 11179523.7716 | 7630254.6904 | 34124194.5875 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 48915248.9415 | 80212703.6076 | 133352.1432 | 11.5966 | 4218.0552 | 6916.8944 | 85.9908 | 141.0102
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1977 | 24.8663 | 2.9505 | 4 | 4156.5726 | 6808.4756 | 84.7374 | 138.8 | 99.8831 | 10.3618 | 109.5915 | 5472381.884 | 0 | 4584885.1209 | 0 | 0 | 0 | 1005545.9356 | 4314497.0468 | 11225436.2907 | 7661590.9281 | 34264337.2061 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49055391.5601 | 80352846.2261 | 177827.941 | 11.8019 | 4156.5726 | 6808.4756 | 84.7374 | 138.8
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5667 | 25.1344 | 2.9895 | 4 | 4110.2685 | 6727.5072 | 83.7934 | 137.1493 | 99.7431 | 10.326 | 96.3205 | 5503059.3069 | 0 | 4622263.5267 | 0 | 0 | 0 | 968487.1171 | 4326585.8808 | 11256888.957 | 7683058.0191 | 34360342.8077 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49151397.1617 | 80448851.8277 | 237137.3706 | 11.9582 | 4110.2685 | 6727.5072 | 83.7934 | 137.1493
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5996 | 25.337 | 3.0192 | 4 | 4075.4187 | 6666.9276 | 83.0829 | 135.9143 | 99.636 | 10.2988 | 104.1925 | 5525953.9791 | 0 | 4650417.7007 | 0 | 0 | 0 | 939109.8958 | 4335037.8145 | 11278879.1548 | 7698066.7809 | 34427465.3257 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49218519.6797 | 80515974.3458 | 316227.766 | 12.0769 | 4075.4187 | 6666.9276 | 83.0829 | 135.9143
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.387 | 25.4914 | 3.0418 | 4 | 4049.2063 | 6621.4758 | 82.5485 | 134.9877 | 99.5535 | 10.2778 | 110.3873 | 5543259.6124 | 0 | 4671849.4043 | 0 | 0 | 0 | 916257.7241 | 4341233.0289 | 11294997.832 | 7709068.1093 | 34476665.7111 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49267720.0651 | 80565174.7311 | 421696.5034 | 12.1673 | 4049.2063 | 6621.4758 | 82.5485 | 134.9877
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.9614 | 25.6044 | 3.0587 | 4 | 4029.5019 | 6587.6105 | 82.1468 | 134.2974 | 99.4929 | 10.2624 | 104.0847 | 5555801.1074 | 0 | 4687467.8011 | 0 | 0 | 0 | 898318.2099 | 4345218.9762 | 11305368.449 | 7716146.2685 | 34508320.8121 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49299375.1661 | 80596829.8321 | 562341.3252 | 12.2346 | 4029.5019 | 6587.6105 | 82.1468 | 134.2974
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4024 | 25.6911 | 3.0715 | 4 | 4014.6971 | 6562.1403 | 81.845 | 133.7781 | 99.446 | 10.2506 | 106.7996 | 5565385.6743 | 0 | 4699450.9439 | 0 | 0 | 0 | 884664.1005 | 4348305.2803 | 11313398.3793 | 7721626.861 | 34532831.2394 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49323885.5934 | 80621340.2594 | 749894.2093 | 12.2858 | 4014.6971 | 6562.1403 | 81.845 | 133.7781
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7339 | 25.7562 | 3.0811 | 4 | 4003.5781 | 6543.0477 | 81.6184 | 133.3889 | 99.4107 | 10.2417 | 92.9155 | 5572564.9778 | 0 | 4708454.842 | 0 | 0 | 0 | 874239.3338 | 4350551.0699 | 11319241.4632 | 7725614.8858 | 34550666.5726 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49341720.9266 | 80639175.5926 | 1000000 | 12.3244 | 4003.5781 | 6543.0477 | 81.6184 | 133.3889
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.9897 | 25.8064 | 3.0884 | 4 | 3995.2301 | 6528.6682 | 81.4482 | 133.0957 | 99.3834 | 10.2348 | 100.2389 | 5578089.0509 | 0 | 4715398.2447 | 0 | 0 | 0 | 866403.1084 | 4352357.2576 | 11323940.793 | 7728822.2749 | 34565010.7296 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49356065.0836 | 80653519.7496 | 1333521.4322 | 12.3537 | 3995.2301 | 6528.6682 | 81.4482 | 133.0957
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1749 | 25.8429 | 3.0939 | 4 | 3988.9644 | 6517.9548 | 81.3204 | 132.8773 | 99.3635 | 10.2298 | 96.4751 | 5582079.9572 | 0 | 4720424.6306 | 0 | 0 | 0 | 860375.2558 | 4353523.139 | 11326974.1774 | 7730892.6221 | 34574269.7823 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49365324.1363 | 80662778.8023 | 1778279.41 | 12.3755 | 3988.9644 | 6517.9548 | 81.3204 | 132.8773
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3233 | 25.8719 | 3.0981 | 4 | 3984.2624 | 6509.8306 | 81.2246 | 132.7117 | 99.3476 | 10.2257 | 113.9757 | 5585272.5898 | 0 | 4724449.5615 | 0 | 0 | 0 | 855942.1136 | 4354609.0633 | 11329799.5296 | 7732820.983 | 34582893.8407 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49373948.1947 | 80671402.8607 | 2371373.7057 | 12.3922 | 3984.2624 | 6509.8306 | 81.2246 | 132.7117
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.4112 | 25.8895 | 3.1009 | 4 | 3980.7346 | 6503.9676 | 81.1527 | 132.5922 | 99.3381 | 10.2233 | 96.9922 | 5587160.945 | 0 | 4726836.1176 | 0 | 0 | 0 | 852292.6356 | 4354852.9823 | 11330434.1568 | 7733254.1292 | 34584830.9666 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49375885.3206 | 80673339.9866 | 3162277.6602 | 12.4037 | 3980.7346 | 6503.9676 | 81.1527 | 132.5922
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.489 | 25.9049 | 3.1032 | 4 | 3978.088 | 6499.4558 | 81.0987 | 132.5002 | 99.3297 | 10.2212 | 104.7851 | 5588831.163 | 0 | 4728946.0848 | 0 | 0 | 0 | 849698.7824 | 4355315.6518 | 11331637.9278 | 7734075.7276 | 34588505.3374 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49379559.6914 | 80677014.3574 | 4216965.0343 | 12.4129 | 3978.088 | 6499.4558 | 81.0987 | 132.5002
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5498 | 25.9168 | 3.105 | 4 | 3976.1028 | 6496.0491 | 81.0582 | 132.4307 | 99.3232 | 10.2196 | 88.7754 | 5590135.3756 | 0 | 4730594.2403 | 0 | 0 | 0 | 847778.748 | 4355718.2619 | 11332685.4369 | 7734790.6741 | 34591702.7367 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49382757.0907 | 80680211.7567 | 5623413.2519 | 12.4199 | 3976.1028 | 6496.0491 | 81.0582 | 132.4307
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6035 | 25.9272 | 3.1064 | 4 | 3974.6137 | 6493.4153 | 81.0279 | 132.3771 | 99.3174 | 10.2181 | 81.8316 | 5591288.5157 | 0 | 4732050.8582 | 0 | 0 | 0 | 846441.084 | 4356214.3786 | 11333976.2306 | 7735671.6673 | 34595642.7342 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49386697.0882 | 80684151.7542 | 7498942.0933 | 12.4255 | 3974.6137 | 6493.4153 | 81.0279 | 132.3771
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6398 | 25.9343 | 3.1074 | 4 | 3973.4969 | 6491.4794 | 81.0051 | 132.3376 | 99.3135 | 10.2171 | 99.5623 | 5592066.9215 | 0 | 4733035.0283 | 0 | 0 | 0 | 845383.8873 | 4356489.4765 | 11334691.9789 | 7736160.1802 | 34597827.4728 | 961560.8286 | 13829493.5254 | 13829493.5254 | 11472858.6872 | 5995102.4534 | 0 | 49388881.8268 | 80686336.4928 | 10000000 | 12.4296 | 3973.4969 | 6491.4794 | 81.0051 | 132.3376
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3208 | 0.062779 | 0.0042629 | 4 | 962885.4625 | 2853594.0418 | 19629.7226 | 58174.3743 | 72.0884 | 10.7229 | 137.7786 | 153765.928 | 0 | 80911.048 | 0 | 0 | 0 | 136358.1131 | 144703.6848 | 376489.305 | 256961.6867 | 1149189.7656 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 16418904.7128 | 48658838.9642 | 100 | 0.017052 | 962885.4625 | 2853594.0418 | 19629.7226 | 58174.3743
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.13919 | 0.0095735 | 4 | 440927.894 | 1282833.1318 | 8988.9115 | 26152.2886 | 79.687 | 11.2025 | 210.6173 | 218280.0039 | 0 | 122687.5929 | 0 | 0 | 0 | 180522.0618 | 203380.9668 | 529155.5566 | 361159.5404 | 1615185.7224 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 16884900.6696 | 49124834.921 | 133.3521 | 0.038294 | 440927.894 | 1282833.1318 | 8988.9115 | 26152.2886
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.24377 | 0.017607 | 4 | 247058.3911 | 704836.7448 | 5036.6195 | 14369.0504 | 85.5718 | 11.5292 | 296.8022 | 290939.7274 | 0 | 170685.3448 | 0 | 0 | 0 | 226034.0091 | 268187.0417 | 697767.6698 | 476240.7723 | 2129854.5652 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 17399569.5124 | 49639503.7638 | 177.8279 | 0.070427 | 247058.3911 | 704836.7448 | 5036.6195 | 14369.0504
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4346 | 0.38664 | 0.029143 | 4 | 154454.7044 | 431020.1922 | 3148.7681 | 8786.9296 | 90.4163 | 11.7715 | 51.3198 | 376949.3178 | 0 | 228767.3885 | 0 | 0 | 0 | 277471.638 | 344443.4543 | 896171.213 | 611655.2673 | 2735458.2788 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 18005173.226 | 50245107.4775 | 237.1374 | 0.11657 | 154454.7044 | 431020.1922 | 3148.7681 | 8786.9296
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5381 | 0.57619 | 0.04518 | 4 | 103541.0064 | 281939.087 | 2110.8235 | 5747.7096 | 94.3491 | 11.9518 | 57.7605 | 477851.1592 | 0 | 298534.3838 | 0 | 0 | 0 | 334959.9664 | 433424.7487 | 1127682.2884 | 769666.3334 | 3442118.88 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 18711833.8272 | 50951768.0786 | 316.2278 | 0.18072 | 103541.0064 | 281939.087 | 2110.8235 | 5747.7096
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0138 | 0.83488 | 0.067294 | 4 | 72729.3834 | 192502.2466 | 1482.6869 | 3924.4187 | 97.653 | 12.0921 | 58.4921 | 602167.0025 | 0 | 382341.585 | 0 | 0 | 0 | 406162.6962 | 542361.8006 | 1411114.1515 | 963114.4039 | 4307261.6398 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 19576976.587 | 51816910.8384 | 421.6965 | 0.26918 | 72729.3834 | 192502.2466 | 1482.6869 | 3924.4187
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.836 | 1.1619 | 0.09711 | 4 | 52844.9008 | 135843.0521 | 1077.3148 | 2769.3444 | 100.195 | 12.1937 | 61.1789 | 743638.0458 | 0 | 472505.1611 | 0 | 0 | 0 | 481309.8509 | 662006.6925 | 1722405.6177 | 1175577.226 | 5257442.5939 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 20527157.5411 | 52767091.7925 | 562.3413 | 0.38844 | 52844.9008 | 135843.0521 | 1077.3148 | 2769.3444
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1749 | 1.586 | 0.13685 | 4 | 39556.478 | 98450.8426 | 806.4123 | 2007.0536 | 102.2291 | 12.2698 | 49.3141 | 911327.9724 | 0 | 582313.1388 | 0 | 0 | 0 | 567630.0559 | 803895.7552 | 2091571.8533 | 1427540.7674 | 6384279.5429 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 21653994.4901 | 53893928.7415 | 749.8942 | 0.54742 | 39556.478 | 98450.8426 | 806.4123 | 2007.0536
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1297 | 2.1265 | 0.18921 | 4 | 30343.7459 | 72940.709 | 618.5983 | 1486.995 | 103.8216 | 12.3244 | 45.4616 | 1107141.3422 | 0 | 714062.2562 | 0 | 0 | 0 | 663659.1972 | 969096.4903 | 2521390.2787 | 1720900.6746 | 7696250.2391 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 22965965.1863 | 55205899.4377 | 1000 | 0.75686 | 30343.7459 | 72940.709 | 618.5983 | 1486.995
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.8567 | 2.8125 | 0.25767 | 4 | 23765.5767 | 55045.817 | 484.4934 | 1122.1834 | 105.0602 | 12.3611 | 60.6345 | 1335833.97 | 0 | 872069.2783 | 0 | 0 | 0 | 770542.5391 | 1161593.8571 | 3022228.9405 | 2062733.3525 | 9225001.9375 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 24494716.8847 | 56734651.1362 | 1333.5214 | 1.0307 | 23765.5767 | 55045.817 | 484.4934 | 1122.1834
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.5218 | 3.6756 | 0.34635 | 4 | 18957.213 | 42228.0881 | 386.4684 | 860.8767 | 106.007 | 12.3808 | 59.2189 | 1601300.27 | 0 | 1060316.0479 | 0 | 0 | 0 | 887975.4635 | 1384340.7948 | 3601770.7806 | 2458282.5668 | 10993985.9237 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 26263700.8709 | 58503635.1223 | 1778.2794 | 1.3854 | 18957.213 | 42228.0881 | 386.4684 | 860.8767
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3218 | 4.7534 | 0.46011 | 4 | 15376.4675 | 32893.9643 | 313.4701 | 670.588 | 106.7104 | 12.3829 | 64.8681 | 1907783.9188 | 0 | 1283334.526 | 0 | 0 | 0 | 1015763.2579 | 1640683.8641 | 4268722.8638 | 2913491.068 | 13029779.4985 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 28299494.4457 | 60539428.6971 | 2371.3737 | 1.8404 | 15376.4675 | 32893.9643 | 313.4701 | 670.588
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.4324 | 6.0806 | 0.60393 | 4 | 12670.6891 | 26016.4958 | 258.3091 | 530.3815 | 107.2001 | 12.3645 | 63.6104 | 2257039.4833 | 0 | 1544209.9494 | 0 | 0 | 0 | 1151303.9704 | 1931495.8272 | 5025355.9381 | 3429908.6885 | 15339313.8569 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 30609028.8041 | 62848963.0555 | 3162.2777 | 2.4157 | 12670.6891 | 26016.4958 | 258.3091 | 530.3815
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.9346 | 7.6757 | 0.78176 | 4 | 10603.8293 | 20913.8304 | 216.1734 | 426.3567 | 107.4913 | 12.3211 | 63.1331 | 2645546.8831 | 0 | 1842374.5931 | 0 | 0 | 0 | 1287852.2385 | 2252551.7488 | 5860677.5884 | 4000032.8789 | 17889035.9308 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 33158750.878 | 65398685.1294 | 4216.965 | 3.1271 | 10603.8293 | 20913.8304 | 216.1734 | 426.3567
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7929 | 9.5359 | 0.99513 | 4 | 9014.437 | 17113.8835 | 183.7715 | 348.8897 | 107.5889 | 12.2473 | 73.2059 | 3064880.3554 | 0 | 2173664.5315 | 0 | 0 | 0 | 1416495.8088 | 2595465.8713 | 6752869.794 | 4608972.392 | 20612348.753 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 35882063.7002 | 68121997.9516 | 5623.4133 | 3.9805 | 9014.437 | 17113.8835 | 183.7715 | 348.8897
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.6897 | 11.6055 | 1.2401 | 4 | 7789.7086 | 14289.3048 | 158.8037 | 291.3068 | 107.4899 | 12.1393 | 69.5461 | 3496428.8417 | 0 | 2525733.9368 | 0 | 0 | 0 | 1523089.9256 | 2942648.5546 | 7656167.9188 | 5225491.9231 | 23369561.1006 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 38639276.0478 | 70879210.2992 | 7498.9421 | 4.9603 | 7789.7086 | 14289.3048 | 158.8037 | 291.3068
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0728 | 13.7824 | 1.5063 | 4 | 6847.9349 | 12198.8164 | 139.6044 | 248.6894 | 107.2016 | 11.998 | 80.2536 | 3916245.5158 | 0 | 2880835.2094 | 0 | 0 | 0 | 1594292.211 | 3272635.4451 | 8514726.1183 | 5811475.5359 | 25990210.0355 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 41259924.9827 | 73499859.2341 | 10000 | 6.0252 | 6847.9349 | 12198.8164 | 139.6044 | 248.6894
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.2714 | 15.9385 | 1.7786 | 4 | 6126.9435 | 10658.5794 | 124.906 | 217.2896 | 106.7556 | 11.831 | 73.753 | 4301232.597 | 0 | 3219775.6202 | 0 | 0 | 0 | 1622543.1621 | 3565985.0379 | 9277961.5846 | 6332399.4245 | 28319897.4264 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 43589612.3736 | 75829546.625 | 13335.2143 | 7.1144 | 6126.9435 | 10658.5794 | 124.906 | 217.2896
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.6682 | 17.9532 | 2.0408 | 4 | 5577.6395 | 9527.0159 | 113.7077 | 194.2211 | 106.2076 | 11.6513 | 91.6551 | 4635229.9954 | 0 | 3526623.6891 | 0 | 0 | 0 | 1608807.1891 | 3810557.7407 | 9914289.5885 | 6766706.3624 | 30262214.5652 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 45531929.5124 | 77771863.7638 | 17782.7941 | 8.1633 | 5577.6395 | 9527.0159 | 113.7077 | 194.2211
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.8297 | 19.7391 | 2.2797 | 4 | 5160.8183 | 8696.335 | 105.2103 | 177.2866 | 105.6222 | 11.4734 | 95.6763 | 4911448.728 | 0 | 3791563.7626 | 0 | 0 | 0 | 1561287.5125 | 4003077.0012 | 10415185.2131 | 7108577.9186 | 31791140.1359 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 47060855.0831 | 79300789.3345 | 23713.7371 | 9.1189 | 5160.8183 | 8696.335 | 105.2103 | 177.2866
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5593 | 21.2542 | 2.4873 | 4 | 4845.4074 | 8085.7977 | 98.7802 | 164.8399 | 105.0551 | 11.3091 | 92.8009 | 5131492.27 | 0 | 4011533.9378 | 0 | 0 | 0 | 1491935.7651 | 4147635.1694 | 10791295.9139 | 7365281.2002 | 32939174.2563 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 48208889.2035 | 80448823.4549 | 31622.7766 | 9.9494 | 4845.4074 | 8085.7977 | 98.7802 | 164.8399
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8982 | 22.5022 | 2.6616 | 4 | 4607.1354 | 7635.4321 | 93.9227 | 155.6586 | 104.5404 | 11.1647 | 91.2611 | 5303085.6263 | 0 | 4189695.1665 | 0 | 0 | 0 | 1413299.2552 | 4253371.2187 | 11066399.4247 | 7553044.9991 | 33778895.6905 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 49048610.6377 | 81288544.8891 | 42169.6503 | 10.6462 | 4607.1354 | 7635.4321 | 93.9227 | 155.6586
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.9601 | 23.5027 | 2.8034 | 4 | 4427.3066 | 7302.3313 | 90.2566 | 148.8679 | 104.0971 | 11.043 | 108.8776 | 5434352.0964 | 0 | 4330613.0174 | 0 | 0 | 0 | 1334284.296 | 4328707.2698 | 11262408.376 | 7686825.136 | 34377190.1915 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 49646905.1387 | 81886839.3901 | 56234.1325 | 11.2138 | 4427.3066 | 7302.3313 | 90.2566 | 148.8679
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.9165 | 24.2876 | 2.9164 | 4 | 4291.6642 | 7055.3662 | 87.4914 | 143.8332 | 103.7306 | 10.9441 | 102.6314 | 5533363.8666 | 0 | 4439961.3342 | 0 | 0 | 0 | 1260706.9038 | 4381272.5208 | 11399172.3765 | 7780169.3765 | 34794646.3783 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50064361.3255 | 82304295.5769 | 74989.4209 | 11.6655 | 4291.6642 | 7055.3662 | 87.4914 | 143.8332
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.9781 | 24.8965 | 3.0049 | 4 | 4189.399 | 6871.6598 | 85.4066 | 140.0881 | 103.4347 | 10.8651 | 106.926 | 5607803.706 | 0 | 4524116.5552 | 0 | 0 | 0 | 1196035.0489 | 4417902.5709 | 11494476.2531 | 7845216.2306 | 35085550.3647 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50355265.3119 | 82595199.5634 | 100000 | 12.0197 | 4189.399 | 6871.6598 | 85.4066 | 140.0881
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.3339 | 25.366 | 3.0736 | 4 | 4112.3362 | 6734.624 | 83.8355 | 137.2944 | 103.1998 | 10.8029 | 111.726 | 5663780.5983 | 0 | 4588605.6479 | 0 | 0 | 0 | 1141495.8113 | 4443614.0024 | 11561372.1237 | 7890874.0368 | 35289742.2203 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50559457.1675 | 82799391.4189 | 133352.1432 | 12.2946 | 4112.3362 | 6734.624 | 83.8355 | 137.2944
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1197 | 25.7227 | 3.1263 | 4 | 4054.2969 | 6632.3922 | 82.6523 | 135.2103 | 103.0174 | 10.755 | 96.2578 | 5705454.3434 | 0 | 4637342.9784 | 0 | 0 | 0 | 1096565.9827 | 4461351.6888 | 11607521.9451 | 7922372.2383 | 35430609.1767 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50700324.1238 | 82940258.3753 | 177827.941 | 12.5053 | 4054.2969 | 6632.3922 | 82.6523 | 135.2103
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.4692 | 25.9927 | 3.1665 | 4 | 4010.6111 | 6556.0084 | 81.7617 | 133.6531 | 102.8771 | 10.7183 | 92.2926 | 5736507.2814 | 0 | 4674086.7635 | 0 | 0 | 0 | 1060400.5364 | 4473687.8867 | 11639618.2016 | 7944278.5928 | 35528579.2623 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50798294.2095 | 83038228.461 | 237137.3706 | 12.666 | 4010.6111 | 6556.0084 | 81.7617 | 133.6531
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4903 | 26.1971 | 3.197 | 4 | 3977.7487 | 6498.8402 | 81.0918 | 132.4876 | 102.7695 | 10.6902 | 102.4991 | 5759751.8464 | 0 | 4701840.6666 | 0 | 0 | 0 | 1031840.7123 | 4482438.9579 | 11662386.6937 | 7959818.5565 | 35598077.4333 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50867792.3805 | 83107726.6319 | 316227.766 | 12.7881 | 3977.7487 | 6498.8402 | 81.0918 | 132.4876
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.2675 | 26.3528 | 3.2202 | 4 | 3953.042 | 6455.9661 | 80.5881 | 131.6136 | 102.6868 | 10.6687 | 93.8627 | 5777298.9932 | 0 | 4722937.3218 | 0 | 0 | 0 | 1009656.1111 | 4488858.0462 | 11679087.8448 | 7971217.4353 | 35649055.7525 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50918770.6997 | 83158704.9511 | 421696.5034 | 12.8809 | 3953.042 | 6455.9661 | 80.5881 | 131.6136
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8445 | 26.4685 | 3.2377 | 4 | 3934.4762 | 6423.9296 | 80.2096 | 130.9605 | 102.6249 | 10.6527 | 97.7948 | 5790243.0042 | 0 | 4738583.9296 | 0 | 0 | 0 | 992393.8378 | 4493276.1009 | 11690582.717 | 7979062.9218 | 35684142.5113 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50953857.4585 | 83193791.7099 | 562341.3252 | 12.9506 | 3934.4762 | 6423.9296 | 80.2096 | 130.9605
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2756 | 26.5551 | 3.2508 | 4 | 3920.531 | 6399.9512 | 79.9253 | 130.4717 | 102.5784 | 10.6406 | 108.3137 | 5799868.3317 | 0 | 4750266.024 | 0 | 0 | 0 | 979112.5943 | 4496406.3105 | 11698726.8802 | 7984621.4806 | 35709001.6214 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50978716.5685 | 83218650.82 | 749894.2093 | 13.003 | 3920.531 | 6399.9512 | 79.9253 | 130.4717
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.6091 | 26.622 | 3.2607 | 4 | 3910.0603 | 6381.8888 | 79.7119 | 130.1034 | 102.5423 | 10.6313 | 111.314 | 5807290.736 | 0 | 4759300.7052 | 0 | 0 | 0 | 969113.2155 | 4498924.8161 | 11705279.5151 | 7989093.7885 | 35729002.7763 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 50998717.7235 | 83238651.9749 | 1000000 | 13.0429 | 3910.0603 | 6381.8888 | 79.7119 | 130.1034
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8527 | 26.6709 | 3.2682 | 4 | 3902.2003 | 6368.415 | 79.5516 | 129.8288 | 102.5159 | 10.6244 | 112.2585 | 5812694.9815 | 0 | 4765894.8435 | 0 | 0 | 0 | 961420.5553 | 4500604.0483 | 11709648.5329 | 7992075.7329 | 35742338.6944 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51012053.6416 | 83251987.8931 | 1333521.4322 | 13.0726 | 3902.2003 | 6368.415 | 79.5516 | 129.8288
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.0307 | 26.7068 | 3.2737 | 4 | 3896.3017 | 6358.36 | 79.4314 | 129.6238 | 102.4965 | 10.6194 | 110.1734 | 5816635.5103 | 0 | 4770712.1488 | 0 | 0 | 0 | 955529.4764 | 4501722.0828 | 11712557.4294 | 7994061.1145 | 35751217.7622 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51020932.7094 | 83260866.9608 | 1778279.41 | 13.0947 | 3896.3017 | 6358.36 | 79.4314 | 129.6238
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.1692 | 26.7346 | 3.2779 | 4 | 3891.8758 | 6350.7745 | 79.3412 | 129.4691 | 102.4814 | 10.6155 | 99.6039 | 5819699.3045 | 0 | 4774461.605 | 0 | 0 | 0 | 951147.4522 | 4502670.2611 | 11715024.3946 | 7995744.869 | 35758747.8863 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51028462.8335 | 83268397.085 | 2371373.7057 | 13.1115 | 3891.8758 | 6350.7745 | 79.3412 | 129.4691
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2741 | 26.7557 | 3.2811 | 4 | 3888.5554 | 6345.0791 | 79.2735 | 129.353 | 102.4699 | 10.6126 | 102.5348 | 5822014.5319 | 0 | 4777297.6284 | 0 | 0 | 0 | 947854.6869 | 4503395.0704 | 11716910.1998 | 7997031.9698 | 35764504.0873 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51034219.0344 | 83274153.2859 | 3162277.6602 | 13.1242 | 3888.5554 | 6345.0791 | 79.2735 | 129.353
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.3519 | 26.7713 | 3.2834 | 4 | 3886.0646 | 6340.8167 | 79.2227 | 129.2661 | 102.4614 | 10.6104 | 108.494 | 5823731.0784 | 0 | 4779402.0031 | 0 | 0 | 0 | 945363.6124 | 4503913.7106 | 11718259.5953 | 7997952.96 | 35768622.9598 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51038337.907 | 83278272.1585 | 4216965.0343 | 13.1337 | 3886.0646 | 6340.8167 | 79.2227 | 129.2661
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4056 | 26.7822 | 3.2851 | 4 | 3884.1963 | 6337.6639 | 79.1846 | 129.2019 | 102.4555 | 10.6089 | 102.8422 | 5824914.9371 | 0 | 4780854.8886 | 0 | 0 | 0 | 943427.1575 | 4504186.8234 | 11718970.1788 | 7998437.9478 | 35770791.9332 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51040506.8804 | 83280441.1318 | 5623413.2519 | 13.1406 | 3884.1963 | 6337.6639 | 79.1846 | 129.2019
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4593 | 26.7928 | 3.2866 | 4 | 3882.795 | 6335.1746 | 79.156 | 129.1511 | 102.4497 | 10.6074 | 97.875 | 5826100.1701 | 0 | 4782307.6637 | 0 | 0 | 0 | 942152.6221 | 4504718.5778 | 11720353.6947 | 7999382.2258 | 35775014.9542 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51044729.9014 | 83284664.1529 | 7498942.0933 | 13.1464 | 3882.795 | 6335.1746 | 79.156 | 129.1511
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4936 | 26.7997 | 3.2876 | 4 | 3881.744 | 6333.3641 | 79.1346 | 129.1142 | 102.4459 | 10.6064 | 100.709 | 5826855.2826 | 0 | 4783234.3764 | 0 | 0 | 0 | 941113.8136 | 4504969.3543 | 11721006.1637 | 7999827.5493 | 35777006.54 | 961560.8286 | 14308154.1186 | 14308154.1186 | 11772186.6032 | 6159593.5296 | 0 | 51046721.4871 | 83286655.7386 | 10000000 | 13.1505 | 3881.744 | 6333.3641 | 79.1346 | 129.1142
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3791 | 0.066644 | 0.0045782 | 4 | 926978.5093 | 2739695.9874 | 18897.7107 | 55852.4084 | 73.9726 | 11.1667 | 145.1692 | 163438.1569 | 0 | 85050.0243 | 0 | 0 | 0 | 145882.3326 | 153804.5004 | 400167.7603 | 273122.719 | 1221465.4934 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 16975701.1246 | 50171886.175 | 100 | 0.018313 | 926978.5093 | 2739695.9874 | 18897.7107 | 55852.4084
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.14485 | 0.010332 | 4 | 422125.5275 | 1225341.682 | 8605.5998 | 24980.2476 | 81.6079 | 11.6427 | 216.9932 | 229199.6624 | 0 | 127047.9821 | 0 | 0 | 0 | 189986.0399 | 213031.1369 | 554263.3196 | 378296.1046 | 1691824.2454 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 17446059.8767 | 50642244.927 | 133.3521 | 0.041329 | 422125.5275 | 1225341.682 | 8605.5998 | 24980.2476
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6692 | 0.25736 | 0.019072 | 4 | 236045.0916 | 671182.5134 | 4812.0985 | 13682.9634 | 87.9333 | 11.9897 | 46.0061 | 308260.2193 | 0 | 178535.6613 | 0 | 0 | 0 | 240752.2015 | 283743.752 | 738243.0389 | 503866.0434 | 2253400.9163 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 18007636.5476 | 51203821.5979 | 177.8279 | 0.076289 | 236045.0916 | 671182.5134 | 4812.0985 | 13682.9634
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5707 | 0.40816 | 0.03161 | 4 | 147468.7776 | 410017.0033 | 3006.3505 | 8358.7512 | 92.9686 | 12.2379 | 53.7517 | 399207.5893 | 0 | 239085.611 | 0 | 0 | 0 | 295270.9286 | 364090.0102 | 947287.5215 | 646543.1983 | 2891484.8589 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 18645720.4901 | 51841905.5405 | 237.1374 | 0.12644 | 147468.7776 | 410017.0033 | 3006.3505 | 8358.7512
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7304 | 0.61051 | 0.049067 | 4 | 98856.375 | 267993.6716 | 2015.3209 | 5463.4135 | 97.1032 | 12.4248 | 40.5564 | 507292.841 | 0 | 312760.4507 | 0 | 0 | 0 | 357788.8744 | 459358.4447 | 1195156.4459 | 815718.8323 | 3648075.8889 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 19402311.5202 | 52598496.5705 | 316.2278 | 0.19627 | 98856.375 | 267993.6716 | 2015.3209 | 5463.4135
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.265 | 0.88445 | 0.07324 | 4 | 69292.7581 | 182605.0527 | 1412.6266 | 3722.651 | 100.5343 | 12.5688 | 68.7116 | 639056.468 | 0 | 395063.048 | 0 | 0 | 0 | 433600.9194 | 572410.9698 | 1489295.9258 | 1016475.0713 | 4545902.4024 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 20300138.0336 | 53496323.084 | 421.6965 | 0.29296 | 69292.7581 | 182605.0527 | 1412.6266 | 3722.651
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1675 | 1.2321 | 0.10573 | 4 | 50377.1822 | 128869.8572 | 1027.007 | 2627.1863 | 103.1827 | 12.6723 | 50.9659 | 789609.0768 | 0 | 488432.1532 | 0 | 0 | 0 | 514295.903 | 699011.4819 | 1818684.4889 | 1241289.5339 | 5551322.6376 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 21305558.2689 | 54501743.3192 | 562.3413 | 0.42292 | 50377.1822 | 128869.8572 | 1027.007 | 2627.1863
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5692 | 1.6765 | 0.14885 | 4 | 37745.0772 | 93500.1501 | 769.4845 | 1906.127 | 105.2724 | 12.7492 | 45.9617 | 965168.5923 | 0 | 600298.9907 | 0 | 0 | 0 | 603848.6218 | 846033.3199 | 2201205.153 | 1502367.7472 | 6718922.4248 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 22473158.056 | 55669343.1064 | 749.8942 | 0.59539 | 37745.0772 | 93500.1501 | 769.4845 | 1906.127
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6413 | 2.2491 | 0.20575 | 4 | 28984.719 | 69319.3353 | 590.8927 | 1413.1684 | 106.9332 | 12.805 | 59.2642 | 1172811.4615 | 0 | 736233.9292 | 0 | 0 | 0 | 706420.1314 | 1020031.5536 | 2653912.8652 | 1811350.063 | 8100760.0039 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 23854995.6352 | 57051180.6855 | 1000 | 0.82302 | 28984.719 | 69319.3353 | 590.8927 | 1413.1684
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.505 | 2.9739 | 0.28007 | 4 | 22725.8633 | 52358.1827 | 463.2975 | 1067.3924 | 108.221 | 12.8418 | 61.6647 | 1414637.2591 | 0 | 898797.8291 | 0 | 0 | 0 | 819939.9429 | 1222016.2622 | 3179435.6441 | 2170030.158 | 9704857.0955 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 25459092.7267 | 58655277.7771 | 1333.5214 | 1.1203 | 22725.8633 | 52358.1827 | 463.2975 | 1067.3924
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.3527 | 3.8879 | 0.37636 | 4 | 18148.1846 | 40199.1526 | 369.9753 | 819.5141 | 109.2072 | 12.8609 | 57.38 | 1696022.3812 | 0 | 1092939.8544 | 0 | 0 | 0 | 945502.0462 | 1456441.0699 | 3789360.9068 | 2586316.6825 | 11566582.941 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 27320818.5722 | 60517003.6226 | 1778.2794 | 1.5054 | 18148.1846 | 40199.1526 | 369.9753 | 819.5141
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.3501 | 5.0242 | 0.49958 | 4 | 14737.3383 | 31349.3875 | 300.4406 | 639.0997 | 109.9357 | 12.8611 | 63.0409 | 2019307.7278 | 0 | 1321832.4093 | 0 | 0 | 0 | 1080737.9785 | 1724532.4651 | 4486879.7239 | 3062387.6077 | 13695677.9122 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 29449913.5434 | 62646098.5938 | 2371.3737 | 1.9983 | 14737.3383 | 31349.3875 | 300.4406 | 639.0997
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.6823 | 6.42 | 0.65503 | 4 | 12158.777 | 24828.4851 | 247.8731 | 506.1623 | 110.4411 | 12.8394 | 75.6846 | 2386754.678 | 0 | 1588891.2497 | 0 | 0 | 0 | 1223556.1734 | 2027688.8194 | 5275630.372 | 3600726.1323 | 16103247.4248 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 31857483.0561 | 65053668.1064 | 3162.2777 | 2.6201 | 12158.777 | 24828.4851 | 247.8731 | 506.1623
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.4324 | 8.0944 | 0.84678 | 4 | 10188.5858 | 19989.2612 | 207.7081 | 407.5081 | 110.7395 | 12.7909 | 66.5582 | 2794776.1421 | 0 | 1893617.6193 | 0 | 0 | 0 | 1367246.4232 | 2361699.672 | 6144658.0953 | 4193855.4101 | 18755853.3619 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 34510088.9932 | 67706274.0435 | 4216.965 | 3.3871 | 10188.5858 | 19989.2612 | 207.7081 | 407.5081
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.5445 | 10.0409 | 1.076 | 4 | 8673.6403 | 16386.2391 | 176.8239 | 334.0556 | 110.8348 | 12.7098 | 69.5613 | 3233722.0038 | 0 | 2231171.4615 | 0 | 0 | 0 | 1502058.2395 | 2717111.1649 | 7069365.8948 | 4824987.4842 | 21578416.2486 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 37332651.8798 | 70528836.9302 | 5623.4133 | 4.3042 | 8673.6403 | 16386.2391 | 176.8239 | 334.0556
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.6575 | 12.1946 | 1.3378 | 4 | 7506.8233 | 13710.2434 | 153.0367 | 279.5019 | 110.7245 | 12.5926 | 86.9963 | 3682849.4111 | 0 | 2587974.0371 | 0 | 0 | 0 | 1612552.4311 | 3074516.593 | 7999261.5048 | 5459660.3454 | 24416814.3226 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 40171049.9539 | 73367235.0043 | 7498.9421 | 5.3513 | 7506.8233 | 13710.2434 | 153.0367 | 279.5019
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.1922 | 14.4459 | 1.6205 | 4 | 6610.2561 | 11731.4183 | 134.759 | 239.1608 | 110.4188 | 12.4408 | 80.4867 | 4116983.7601 | 0 | 2945718.7313 | 0 | 0 | 0 | 1685206.5111 | 3411684.511 | 8876503.2649 | 6058395.8722 | 27094492.6506 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 42848728.2818 | 76044913.3322 | 10000 | 6.4822 | 6610.2561 | 11731.4183 | 134.759 | 239.1608
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4808 | 16.6643 | 1.908 | 4 | 5924.452 | 10274.0642 | 120.778 | 209.4507 | 109.9532 | 12.2631 | 88.4511 | 4513075.4455 | 0 | 3285576.5411 | 0 | 0 | 0 | 1713357.6518 | 3709683.759 | 9651836.1801 | 6587576.5183 | 29461106.0957 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 45215341.7269 | 78411526.7773 | 13335.2143 | 7.632 | 5924.452 | 10274.0642 | 120.778 | 209.4507
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.8971 | 18.7247 | 2.183 | 4 | 5402.3732 | 9203.9617 | 110.1347 | 187.6352 | 109.3877 | 12.0738 | 97.4326 | 4854703.0064 | 0 | 3591526.5219 | 0 | 0 | 0 | 1698339.5184 | 3956381.9282 | 10293694.2117 | 7025657.8137 | 31420303.0003 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 47174538.6316 | 80370723.6819 | 17782.7941 | 8.7322 | 5402.3732 | 9203.9617 | 110.1347 | 187.6352
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0151 | 20.5397 | 2.4321 | 4 | 5006.4903 | 8418.8267 | 102.0641 | 171.6292 | 108.7901 | 11.8882 | 95.3875 | 5135515.0952 | 0 | 3854071.9468 | 0 | 0 | 0 | 1648978.8144 | 4149040.684 | 10794952.7744 | 7367777.0826 | 32950336.3973 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 48704572.0286 | 81900757.0789 | 23713.7371 | 9.7283 | 5006.4903 | 8418.8267 | 102.0641 | 171.6292
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7176 | 22.0808 | 2.648 | 4 | 4707.11 | 7841.1414 | 95.9608 | 159.8523 | 108.2121 | 11.7169 | 98.3926 | 5359633.7349 | 0 | 4072414.4785 | 0 | 0 | 0 | 1579081.5219 | 4294340.5967 | 11172993.3423 | 7625797.5382 | 34104261.2124 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 49858496.8437 | 83054681.894 | 31622.7766 | 10.5922 | 4707.11 | 7841.1414 | 95.9608 | 159.8523
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9787 | 23.3399 | 2.8281 | 4 | 4481.0774 | 7415.5448 | 91.3528 | 151.1759 | 107.6932 | 11.5679 | 87.8348 | 5532976.6277 | 0 | 4247756.8009 | 0 | 0 | 0 | 1499579.0047 | 4399321.849 | 11446133.0261 | 7812220.9848 | 34937988.2932 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 50692223.9245 | 83888408.9748 | 42169.6503 | 11.3125 | 4481.0774 | 7415.5448 | 91.3528 | 151.1759
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.9823 | 24.3499 | 2.9746 | 4 | 4310.5805 | 7100.5548 | 87.877 | 144.7544 | 107.2467 | 11.4425 | 99.0626 | 5665781.4184 | 0 | 4386588.1228 | 0 | 0 | 0 | 1420603.0504 | 4474459.3107 | 11641625.2887 | 7945648.471 | 35534705.6621 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 51288941.2933 | 84485126.3437 | 56234.1325 | 11.8984 | 4310.5805 | 7100.5548 | 87.877 | 144.7544
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8728 | 25.1382 | 3.0907 | 4 | 4182.0481 | 6867.1817 | 85.2567 | 139.9968 | 106.8798 | 11.3411 | 95.0216 | 5765500.222 | 0 | 4493780.3346 | 0 | 0 | 0 | 1347207.3104 | 4526530.2681 | 11777103.2387 | 8038114.9557 | 35948236.3294 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 51702471.9607 | 84898657.011 | 74989.4209 | 12.363 | 4182.0481 | 6867.1817 | 85.2567 | 139.9968
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.9077 | 25.7544 | 3.182 | 4 | 4085.1968 | 6693.2927 | 83.2823 | 136.4518 | 106.5816 | 11.2596 | 100.4222 | 5841122.2689 | 0 | 4576955.843 | 0 | 0 | 0 | 1283476.247 | 4563606.2 | 11873567.208 | 8103953.5968 | 36242681.3637 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 51996916.9949 | 85193102.0453 | 100000 | 12.7281 | 4085.1968 | 6693.2927 | 83.2823 | 136.4518
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.2124 | 26.2237 | 3.2524 | 4 | 4012.2527 | 6563.8965 | 81.7952 | 133.8139 | 106.348 | 11.1964 | 94.8077 | 5897267.0148 | 0 | 4639866.8452 | 0 | 0 | 0 | 1229442.3965 | 4588964.74 | 11939544.9274 | 8148984.7461 | 36444070.67 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52198306.3012 | 85394491.3516 | 133352.1432 | 13.0097 | 4012.2527 | 6563.8965 | 81.7952 | 133.8139
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.9808 | 26.5843 | 3.3066 | 4 | 3957.3433 | 6467.1498 | 80.6758 | 131.8416 | 106.1645 | 11.147 | 107.8726 | 5939596.2518 | 0 | 4687996.419 | 0 | 0 | 0 | 1185430.5493 | 4607079.0558 | 11986674.6614 | 8181151.758 | 36587928.6953 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52342164.3266 | 85538349.3769 | 177827.941 | 13.2266 | 3957.3433 | 6467.1498 | 80.6758 | 131.8416
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3038 | 26.8547 | 3.3478 | 4 | 3916.0324 | 6395.0013 | 79.8336 | 130.3708 | 106.0248 | 11.1096 | 110.1413 | 5970830.2758 | 0 | 4723921.9663 | 0 | 0 | 0 | 1149885.5621 | 4619408.7436 | 12018753.9799 | 8203046.552 | 36685847.0796 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52440082.7109 | 85636267.7612 | 237137.3706 | 13.3911 | 3916.0324 | 6395.0013 | 79.8336 | 130.3708
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3191 | 27.0621 | 3.3792 | 4 | 3884.9689 | 6340.8722 | 79.2003 | 129.2673 | 105.9163 | 11.0807 | 113.4179 | 5994550.2461 | 0 | 4751445.1717 | 0 | 0 | 0 | 1122091.846 | 4628554.0329 | 12042548.1465 | 8219286.5596 | 36758476.0028 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52512711.634 | 85708896.6844 | 316227.766 | 13.5169 | 3884.9689 | 6340.8722 | 79.2003 | 129.2673
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.0696 | 27.2159 | 3.4028 | 4 | 3861.6225 | 6300.4897 | 78.7244 | 128.444 | 105.8352 | 11.0591 | 115.6339 | 6011941.3829 | 0 | 4771764.728 | 0 | 0 | 0 | 1100215.5454 | 4634729.4459 | 12058615.3046 | 8230252.7251 | 36807519.1319 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52561754.7632 | 85757939.8135 | 421696.5034 | 13.6113 | 3861.6225 | 6300.4897 | 78.7244 | 128.444
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6567 | 27.3358 | 3.4209 | 4 | 3844.084 | 6270.0382 | 78.3669 | 127.8232 | 105.7713 | 11.0421 | 110.0692 | 6025466.673 | 0 | 4787646.6783 | 0 | 0 | 0 | 1083652.7658 | 4639738.7857 | 12071648.5791 | 8239148.2028 | 36847301.6848 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52601537.316 | 85797722.3664 | 562341.3252 | 13.6838 | 3844.084 | 6270.0382 | 78.3669 | 127.8232
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0855 | 27.4237 | 3.4344 | 4 | 3830.9133 | 6247.3411 | 78.0984 | 127.3605 | 105.7244 | 11.0297 | 98.4269 | 6035295.7907 | 0 | 4799236.6513 | 0 | 0 | 0 | 1070770.7622 | 4643068.2496 | 12080311.1613 | 8245060.5931 | 36873743.2082 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52627978.8394 | 85824163.8898 | 749894.2093 | 13.7377 | 3830.9133 | 6247.3411 | 78.0984 | 127.3605
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3996 | 27.4882 | 3.4445 | 4 | 3821.0259 | 6230.4049 | 77.8968 | 127.0152 | 105.6899 | 11.0206 | 110.384 | 6042470.4588 | 0 | 4807722.9427 | 0 | 0 | 0 | 1060836.4021 | 4645301.6234 | 12086121.9417 | 8249026.5702 | 36891479.9389 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52645715.5702 | 85841900.6205 | 1000000 | 13.7779 | 3821.0259 | 6230.4049 | 77.8968 | 127.0152
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.636 | 27.5368 | 3.452 | 4 | 3813.605 | 6217.7062 | 77.7455 | 126.7564 | 105.6638 | 11.0137 | 114.4002 | 6047854.4486 | 0 | 4814105.1491 | 0 | 0 | 0 | 1053301.6825 | 4646951.8993 | 12090415.6211 | 8251957.0946 | 36904585.8952 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52658821.5264 | 85855006.5768 | 1333521.4322 | 13.8081 | 3813.605 | 6217.7062 | 77.7455 | 126.7564
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8212 | 27.5747 | 3.4578 | 4 | 3808.0365 | 6208.1163 | 77.632 | 126.5608 | 105.6434 | 11.0083 | 109.8278 | 6052066.7741 | 0 | 4819105.5867 | 0 | 0 | 0 | 1047709.0759 | 4648363.7603 | 12094088.9938 | 8254464.247 | 36915798.4379 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52670034.0691 | 85866219.1195 | 1778279.41 | 13.8313 | 3808.0365 | 6208.1163 | 77.632 | 126.5608
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.9675 | 27.6045 | 3.4623 | 4 | 3803.8586 | 6200.861 | 77.5468 | 126.4129 | 105.6272 | 11.004 | 101.6126 | 6055390.3164 | 0 | 4823055.0153 | 0 | 0 | 0 | 1043587.7587 | 4649592.9052 | 12097286.9768 | 8256646.936 | 36925559.9084 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52679795.5396 | 85875980.59 | 2371373.7057 | 13.849 | 3803.8586 | 6200.861 | 77.5468 | 126.4129
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.0723 | 27.626 | 3.4655 | 4 | 3800.7245 | 6195.4662 | 77.4829 | 126.303 | 105.6156 | 11.0009 | 113.8722 | 6057767.8169 | 0 | 4825883.8709 | 0 | 0 | 0 | 1040410.4923 | 4650384.2502 | 12099345.8941 | 8258052.1894 | 36931844.5137 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52686080.145 | 85882265.1953 | 3162277.6602 | 13.8621 | 3800.7245 | 6195.4662 | 77.4829 | 126.303
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.1501 | 27.6419 | 3.468 | 4 | 3798.3735 | 6191.4289 | 77.435 | 126.2207 | 105.607 | 10.9986 | 112.3722 | 6059530.5471 | 0 | 4827982.9303 | 0 | 0 | 0 | 1038006.3792 | 4650952.7441 | 12100824.9985 | 8259061.7086 | 36936359.3078 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52690594.9391 | 85886779.9894 | 4216965.0343 | 13.8719 | 3798.3735 | 6191.4289 | 77.435 | 126.2207
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2085 | 27.6539 | 3.4698 | 4 | 3796.6102 | 6188.4018 | 77.399 | 126.1589 | 105.6005 | 10.9969 | 117.1432 | 6060851.7404 | 0 | 4829557.0752 | 0 | 0 | 0 | 1036197.9771 | 4651376.6492 | 12101927.9125 | 8259814.4701 | 36939725.8245 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52693961.4557 | 85890146.5061 | 5623413.2519 | 13.8792 | 3796.6102 | 6188.4018 | 77.399 | 126.1589
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2427 | 27.6611 | 3.4711 | 4 | 3795.2876 | 6186.2169 | 77.3721 | 126.1144 | 105.5967 | 10.9959 | 107.9118 | 6061626.0153 | 0 | 4830481.5132 | 0 | 0 | 0 | 1034706.4596 | 4651457.4554 | 12102138.1537 | 8259957.964 | 36940367.5611 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52694603.1924 | 85890788.2427 | 7498942.0933 | 13.8842 | 3795.2876 | 6186.2169 | 77.3721 | 126.1144
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2692 | 27.6667 | 3.472 | 4 | 3794.2958 | 6184.5714 | 77.3519 | 126.0809 | 105.5937 | 10.9951 | 98.0649 | 6062224.9238 | 0 | 4831196.5809 | 0 | 0 | 0 | 1033597.6037 | 4651537.4523 | 12102346.2893 | 8260100.0208 | 36941002.8708 | 961560.8286 | 14792674.8026 | 14792674.8026 | 12077081.6056 | 6326428.6422 | 0 | 52695238.502 | 85891423.5524 | 10000000 | 13.888 | 3794.2958 | 6184.5714 | 77.3519 | 126.0809
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.070625 | 0.0049156 | 4 | 892043.5452 | 2629692.0669 | 18185.5142 | 53609.8297 | 75.8565 | 11.6108 | 150.9251 | 173315.6 | 0 | 89237.0103 | 0 | 0 | 0 | 155570.1422 | 163067.8735 | 424269.1569 | 289572.4174 | 1295032.2002 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 17539648.6064 | 51705855.6692 | 100 | 0.019662 | 892043.5452 | 2629692.0669 | 18185.5142 | 53609.8297
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.15498 | 0.011164 | 4 | 404265.8108 | 1169383.6547 | 8241.5054 | 23839.4675 | 83.9514 | 12.1078 | 230.3436 | 244793.0063 | 0 | 134307.4578 | 0 | 0 | 0 | 204579.3983 | 227635.1463 | 592259.9564 | 404229.59 | 1807804.5551 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 18052420.9612 | 52218628.0241 | 133.3521 | 0.044655 | 404265.8108 | 1169383.6547 | 8241.5054 | 23839.4675
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7741 | 0.27144 | 0.020631 | 4 | 225692.6305 | 639716.0411 | 4601.0495 | 13041.4768 | 90.3051 | 12.451 | 48.2274 | 326071.8068 | 0 | 186551.3589 | 0 | 0 | 0 | 255826.0115 | 299695.1791 | 779745.3801 | 532192.2441 | 2380081.9806 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 18624698.3867 | 52790905.4495 | 177.8279 | 0.082522 | 225692.6305 | 639716.0411 | 4601.0495 | 13041.4768
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7144 | 0.4313 | 0.034238 | 4 | 140935.9253 | 390412.3873 | 2873.1695 | 7959.0846 | 95.5591 | 12.7064 | 62.4845 | 422710.4578 | 0 | 250024.2727 | 0 | 0 | 0 | 314200.1746 | 384904.613 | 1001442.8482 | 683505.3215 | 3056787.6877 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 19301404.0938 | 53467611.1566 | 237.1374 | 0.13695 | 140935.9253 | 390412.3873 | 2873.1695 | 7959.0846
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9667 | 0.65228 | 0.053314 | 4 | 94403.3345 | 254615.2364 | 1924.5397 | 5190.676 | 99.9864 | 12.9035 | 45.7924 | 541434.1813 | 0 | 328084.3898 | 0 | 0 | 0 | 385624.0787 | 489505.6334 | 1273593.2467 | 869253.5606 | 3887495.0904 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 20132111.4966 | 54298318.5594 | 316.2278 | 0.21326 | 94403.3345 | 254615.2364 | 1924.5397 | 5190.676
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5083 | 0.9342 | 0.07953 | 4 | 66098.205 | 173498.1763 | 1347.5013 | 3536.995 | 103.4074 | 13.0449 | 63.8059 | 676148.63 | 0 | 407294.4656 | 0 | 0 | 0 | 460706.6871 | 602218.4153 | 1566848.7846 | 1069406.491 | 4782623.4736 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 21027239.8798 | 55193446.9426 | 421.6965 | 0.31812 | 66098.205 | 173498.1763 | 1347.5013 | 3536.995
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4887 | 1.3026 | 0.11482 | 4 | 48091.8735 | 122482.9225 | 980.4179 | 2496.98 | 106.1659 | 13.1511 | 51.4214 | 835845.5832 | 0 | 503738.49 | 0 | 0 | 0 | 546908.4071 | 735732.0673 | 1914223.9198 | 1306497.1586 | 5842945.626 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 22087562.0321 | 56253769.0949 | 562.3413 | 0.45928 | 48091.8735 | 122482.9225 | 980.4179 | 2496.98
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9862 | 1.7732 | 0.16161 | 4 | 36069.777 | 88922.7059 | 735.3312 | 1812.8096 | 108.3386 | 13.2296 | 45.7145 | 1021827.6817 | 0 | 619169.2429 | 0 | 0 | 0 | 642414.0079 | 890530.2637 | 2316977.0732 | 1581384.4616 | 7072302.7311 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 23316919.1372 | 57483126.2 | 749.8942 | 0.64644 | 36069.777 | 88922.7059 | 735.3312 | 1812.8096
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1554 | 2.3754 | 0.22322 | 4 | 27727.3664 | 65992.3119 | 565.2599 | 1345.3425 | 110.0536 | 13.286 | 57.0185 | 1240123.3912 | 0 | 758351.4057 | 0 | 0 | 0 | 750005.7482 | 1071907.4126 | 2788883.209 | 1903470.096 | 8512741.2626 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 24757357.6688 | 58923564.7316 | 1000 | 0.89289 | 27727.3664 | 65992.3119 | 565.2599 | 1345.3425
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1481 | 3.1388 | 0.30365 | 4 | 21763.3462 | 49893.0252 | 443.6752 | 1017.1368 | 111.3884 | 13.3229 | 49.1969 | 1494877.5182 | 0 | 925116.8827 | 0 | 0 | 0 | 869715.4423 | 1282986.8388 | 3338068.5778 | 2278300.3948 | 10189065.6545 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 26433682.0607 | 60599889.1235 | 1333.5214 | 1.2146 | 21763.3462 | 49893.0252 | 443.6752 | 1017.1368
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.1614 | 4.1021 | 0.40781 | 4 | 17398.624 | 38343.4235 | 354.6945 | 781.6826 | 112.4121 | 13.3412 | 53.8647 | 1791591.8096 | 0 | 1124458.8729 | 0 | 0 | 0 | 1002547.2002 | 1528253.1743 | 3976201.2716 | 2713839.0706 | 12136891.3993 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 28381507.8054 | 62547714.8682 | 1778.2794 | 1.6313 | 17398.624 | 38343.4235 | 354.6945 | 781.6826
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.3707 | 5.3011 | 0.54106 | 4 | 14144.65 | 29931.3689 | 288.3578 | 610.1914 | 113.1686 | 13.3394 | 56.913 | 2132885.3518 | 0 | 1359764.5716 | 0 | 0 | 0 | 1146222.3085 | 1809160.1705 | 4707063.6538 | 3212667.6642 | 14367763.7203 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 30612380.1265 | 64778587.1893 | 2371.3737 | 2.1642 | 14144.65 | 29931.3689 | 288.3578 | 610.1914
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.9345 | 6.7689 | 0.70876 | 4 | 11683.5932 | 23734.9284 | 238.1859 | 483.8686 | 113.6904 | 13.3141 | 61.6192 | 2519409.2883 | 0 | 1633346.4492 | 0 | 0 | 0 | 1296918.0202 | 2125372.7655 | 5529783.962 | 3774191.1798 | 16879021.6651 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 33123638.0713 | 67289845.1341 | 3162.2777 | 2.8351 | 11683.5932 | 23734.9284 | 238.1859 | 483.8686
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9406 | 8.5262 | 0.91513 | 4 | 9802.7477 | 19136.4237 | 199.8423 | 390.1219 | 113.9958 | 13.2601 | 69.2962 | 2947654.0611 | 0 | 1944867.1684 | 0 | 0 | 0 | 1448142.1313 | 2472858.7107 | 6433871.1121 | 4391249.2368 | 19638642.4203 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 35883258.8265 | 70049465.8893 | 4216.965 | 3.6605 | 9802.7477 | 19136.4237 | 199.8423 | 390.1219
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.2862 | 10.5574 | 1.1607 | 4 | 8356.6592 | 15715.576 | 170.3618 | 320.3833 | 114.0882 | 13.1715 | 71.0455 | 3405616.2871 | 0 | 2287987.6776 | 0 | 0 | 0 | 1588311.7338 | 2839947.1224 | 7388959.8593 | 5043116.9319 | 22553939.6121 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 38798556.0182 | 72964763.0811 | 5623.4133 | 4.6428 | 8356.6592 | 15715.576 | 170.3618 | 320.3833
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.6138 | 12.7967 | 1.4399 | 4 | 7243.4226 | 13175.5948 | 147.667 | 268.6023 | 113.9662 | 13.0445 | 79.019 | 3872469.8383 | 0 | 2649479.7284 | 0 | 0 | 0 | 1702661.4764 | 3207598.3068 | 8345512.8254 | 5695983.9864 | 25473706.1616 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 41718322.5678 | 75884529.6306 | 7498.9421 | 5.7595 | 7243.4226 | 13175.5948 | 147.667 | 268.6023
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.2922 | 15.1223 | 1.7394 | 4 | 6388.6651 | 11299.184 | 130.2416 | 230.3491 | 113.6428 | 12.882 | 80.0923 | 4320704.8535 | 0 | 3009656.3517 | 0 | 0 | 0 | 1776473.5125 | 3551665.5399 | 9240705.188 | 6306971.1683 | 28206176.6139 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 44450793.0201 | 78617000.0829 | 10000 | 6.9578 | 6388.6651 | 11299.184 | 130.2416 | 230.3491
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6487 | 17.3997 | 2.0421 | 4 | 5735.3764 | 9918.191 | 116.9234 | 202.1957 | 113.1584 | 12.6937 | 89.5201 | 4727122.9249 | 0 | 3349820.4284 | 0 | 0 | 0 | 1803835.6923 | 3853503.8278 | 10026026.4975 | 6842969.0988 | 30603278.4697 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 46847894.8758 | 81014101.9386 | 13335.2143 | 8.1682 | 5735.3764 | 9918.191 | 116.9234 | 202.1957
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0749 | 19.5045 | 2.33 | 4 | 5238.4298 | 8904.4002 | 106.7925 | 181.5282 | 112.5764 | 12.4947 | 103.8714 | 5076011.709 | 0 | 3654659.0288 | 0 | 0 | 0 | 1787240.479 | 4101985.3745 | 10672524.5116 | 7284217.2776 | 32576638.3806 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 48821254.7867 | 82987461.8496 | 17782.7941 | 9.3198 | 5238.4298 | 8904.4002 | 106.7925 | 181.5282
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1734 | 21.3529 | 2.5894 | 4 | 4861.8551 | 8160.4535 | 99.1155 | 166.3619 | 111.9655 | 12.3007 | 100.0257 | 5362037.536 | 0 | 3915559.097 | 0 | 0 | 0 | 1736511.0747 | 4295502.006 | 11176015.091 | 7627859.9438 | 34113484.7485 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 50358101.1547 | 84524308.2175 | 23713.7371 | 10.3578 | 4861.8551 | 8160.4535 | 99.1155 | 166.3619
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7982 | 22.9106 | 2.8131 | 4 | 4577.2414 | 7613.5925 | 93.3133 | 155.2134 | 111.381 | 12.1236 | 95.2519 | 5588637.9882 | 0 | 4130886.0783 | 0 | 0 | 0 | 1664849.0256 | 4439905.5059 | 11551723.3765 | 7884288.5686 | 35260290.5431 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 51504906.9492 | 85671114.012 | 31622.7766 | 11.2524 | 4577.2414 | 7613.5925 | 93.3133 | 155.2134
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0197 | 24.1874 | 2.9995 | 4 | 4362.4703 | 7210.1222 | 88.9349 | 146.9881 | 110.8552 | 11.9692 | 100.871 | 5764690.1742 | 0 | 4304522.5043 | 0 | 0 | 0 | 1585120.2763 | 4545189.8523 | 11825651.6492 | 8071250.2434 | 36096424.6996 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 52341041.1058 | 86507248.1686 | 42169.6503 | 11.998 | 4362.4703 | 7210.1222 | 88.9349 | 146.9881
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.936 | 25.2009 | 3.1501 | 4 | 4200.5484 | 6912.0537 | 85.6339 | 140.9116 | 110.4085 | 11.8409 | 105.3665 | 5898146.4567 | 0 | 4440497.1693 | 0 | 0 | 0 | 1505467.443 | 4619203.3169 | 12018219.5018 | 8202681.7597 | 36684215.6474 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 52928832.0535 | 87095039.1164 | 56234.1325 | 12.6005 | 4200.5484 | 6912.0537 | 85.6339 | 140.9116
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8017 | 26.0002 | 3.27 | 4 | 4078.5396 | 6690.661 | 83.1465 | 136.3982 | 110.0378 | 11.7361 | 107.2001 | 5999553.2214 | 0 | 4546689.9671 | 0 | 0 | 0 | 1432805.0447 | 4671828.811 | 12155140.2423 | 8296132.9785 | 37102150.2651 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 53346766.6712 | 87512973.7341 | 74989.4209 | 13.0799 | 4078.5396 | 6690.661 | 83.1465 | 136.3982
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.7714 | 26.6162 | 3.3635 | 4 | 3986.6475 | 6526.1596 | 81.2732 | 133.0446 | 109.7413 | 11.6532 | 94.6403 | 6075317.7568 | 0 | 4627845.3533 | 0 | 0 | 0 | 1369186.9154 | 4708216.51 | 12249813.5709 | 8360749.4707 | 37391129.5771 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 53635745.9832 | 87801953.0461 | 100000 | 13.4538 | 3986.6475 | 6526.1596 | 81.2732 | 133.0446
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.054 | 27.0905 | 3.4359 | 4 | 3917.4699 | 6403.4589 | 79.8629 | 130.5432 | 109.5063 | 11.5881 | 103.1702 | 6132286.279 | 0 | 4689984.8958 | 0 | 0 | 0 | 1315953.2193 | 4733907.5137 | 12316656.2927 | 8406371.0017 | 37595159.2023 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 53839775.6084 | 88005982.6712 | 133352.1432 | 13.7435 | 3917.4699 | 6403.4589 | 79.8629 | 130.5432
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7861 | 27.4512 | 3.4914 | 4 | 3865.4176 | 6311.9059 | 78.8018 | 128.6767 | 109.3239 | 11.5379 | 95.2115 | 6174774.6019 | 0 | 4737002.2817 | 0 | 0 | 0 | 1272409.5716 | 4751832.7175 | 12363293.996 | 8438202.1926 | 37737515.3612 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 53982131.7674 | 88148338.8302 | 177827.941 | 13.9654 | 3865.4176 | 6311.9059 | 78.8018 | 128.6767
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.1085 | 27.7268 | 3.5338 | 4 | 3826.2708 | 6243.3848 | 78.0037 | 127.2798 | 109.1823 | 11.4991 | 120.1711 | 6206778.555 | 0 | 4772817.2491 | 0 | 0 | 0 | 1237743.3286 | 4764762.2618 | 12396934.018 | 8461162.1988 | 37840197.6113 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54084814.0175 | 88251021.0803 | 237137.3706 | 14.1351 | 3826.2708 | 6243.3848 | 78.0037 | 127.2798
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0977 | 27.9333 | 3.5659 | 4 | 3796.8443 | 6192.2143 | 77.4038 | 126.2367 | 109.075 | 11.4698 | 112.0516 | 6230473.2156 | 0 | 4799566.7372 | 0 | 0 | 0 | 1210296.9896 | 4773731.4075 | 12420269.8954 | 8477089.4147 | 37911427.66 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54156044.0662 | 88322251.129 | 316227.766 | 14.2634 | 3796.8443 | 6192.2143 | 77.4038 | 126.2367
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8406 | 28.0886 | 3.5901 | 4 | 3774.7343 | 6153.9341 | 76.9531 | 125.4563 | 108.9936 | 11.4477 | 113.0977 | 6248127.8219 | 0 | 4819630.5573 | 0 | 0 | 0 | 1188904.2232 | 4780098.4149 | 12436835.5427 | 8488395.8093 | 37961992.3694 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54206608.7755 | 88372815.8383 | 421696.5034 | 14.3604 | 3774.7343 | 6153.9341 | 76.9531 | 125.4563
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.4083 | 28.2072 | 3.6085 | 4 | 3758.1282 | 6125.1891 | 76.6145 | 124.8703 | 108.931 | 11.4307 | 104.4081 | 6261539.2504 | 0 | 4834948.4687 | 0 | 0 | 0 | 1172538.7755 | 4784920.3329 | 12449381.1841 | 8496958.4674 | 38000286.4791 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54244902.8852 | 88411109.948 | 562341.3252 | 14.434 | 3758.1282 | 6125.1891 | 76.6145 | 124.8703
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.8345 | 28.2963 | 3.6224 | 4 | 3745.6601 | 6103.6604 | 76.3603 | 124.4314 | 108.8837 | 11.4178 | 106.7723 | 6271561.2861 | 0 | 4846439.897 | 0 | 0 | 0 | 1159994.5055 | 4788418.3186 | 12458482.2252 | 8503170.1149 | 38028066.3473 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54272682.7535 | 88438889.8163 | 749894.2093 | 14.4895 | 3745.6601 | 6103.6604 | 76.3603 | 124.4314
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1512 | 28.3626 | 3.6328 | 4 | 3736.3014 | 6087.5581 | 76.1696 | 124.1031 | 108.8484 | 11.4083 | 103.386 | 6278983.269 | 0 | 4854975.5768 | 0 | 0 | 0 | 1150385.9127 | 4790894.4558 | 12464924.6264 | 8507567.1861 | 38047731.0267 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54292347.4329 | 88458554.4957 | 1000000 | 14.531 | 3736.3014 | 6087.5581 | 76.1696 | 124.1031
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.383 | 28.4112 | 3.6405 | 4 | 3729.2781 | 6075.5428 | 76.0264 | 123.8582 | 108.8225 | 11.4013 | 108.2371 | 6284398.05 | 0 | 4861217.487 | 0 | 0 | 0 | 1143005.03 | 4792562.0211 | 12469263.2893 | 8510528.4127 | 38060974.2902 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54305590.6964 | 88471797.7592 | 1333521.4322 | 14.562 | 3729.2781 | 6075.5428 | 76.0264 | 123.8582
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5682 | 28.4499 | 3.6464 | 4 | 3724.0085 | 6066.438 | 75.9189 | 123.6725 | 108.8018 | 11.3957 | 104.38 | 6288719.8226 | 0 | 4866205.7727 | 0 | 0 | 0 | 1137585.4132 | 4794079.2933 | 12473210.9203 | 8513222.752 | 38073023.974 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54317640.3802 | 88483847.443 | 1778279.41 | 14.5858 | 3724.0085 | 6066.438 | 75.9189 | 123.6725
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.6971 | 28.477 | 3.6508 | 4 | 3720.0551 | 6059.6998 | 75.8384 | 123.5352 | 108.7873 | 11.3918 | 108.0564 | 6291721.7319 | 0 | 4869676.6277 | 0 | 0 | 0 | 1133346.8845 | 4794950.6452 | 12475477.9991 | 8514770.0798 | 38079943.9682 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54324560.3743 | 88490767.4372 | 2371373.7057 | 14.6032 | 3720.0551 | 6059.6998 | 75.8384 | 123.5352
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.7897 | 28.4966 | 3.654 | 4 | 3717.0895 | 6054.6833 | 75.7779 | 123.4329 | 108.7769 | 11.3889 | 106.2902 | 6293875.5783 | 0 | 4872169.8468 | 0 | 0 | 0 | 1130093.4831 | 4795494.1742 | 12476892.1502 | 8515735.267 | 38084260.4995 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54328876.9057 | 88495083.9685 | 3162277.6602 | 14.616 | 3717.0895 | 6054.6833 | 75.7779 | 123.4329
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8823 | 28.5156 | 3.6567 | 4 | 3714.865 | 6050.7225 | 75.7325 | 123.3522 | 108.7665 | 11.3861 | 102.7895 | 6296031.2047 | 0 | 4874662.747 | 0 | 0 | 0 | 1127978.9351 | 4796482.4259 | 12479463.3783 | 8517490.183 | 38092108.874 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54336725.2801 | 88502932.343 | 4216965.0343 | 14.6268 | 3714.865 | 6050.7225 | 75.7325 | 123.3522
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9406 | 28.5278 | 3.6586 | 4 | 3713.1966 | 6047.8487 | 75.6985 | 123.2936 | 108.76 | 11.3844 | 110.5558 | 6297386.962 | 0 | 4876233.1105 | 0 | 0 | 0 | 1126227.4316 | 4796940.5266 | 12480655.2625 | 8518303.6685 | 38095746.9619 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54340363.368 | 88506570.4309 | 5623413.2519 | 14.6344 | 3713.1966 | 6047.8487 | 75.6985 | 123.2936
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9749 | 28.5352 | 3.6599 | 4 | 3711.9453 | 6045.7755 | 75.673 | 123.2513 | 108.7561 | 11.3833 | 101.5236 | 6298181.5008 | 0 | 4877155.3286 | 0 | 0 | 0 | 1124774.3073 | 4797043.3433 | 12480922.7703 | 8518486.2481 | 38096563.4983 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54341179.9045 | 88507386.9673 | 7498942.0933 | 14.6395 | 3711.9453 | 6045.7755 | 75.673 | 123.2513
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.0092 | 28.5423 | 3.661 | 4 | 3711.0068 | 6044.1473 | 75.6539 | 123.2181 | 108.7522 | 11.3823 | 105.0814 | 6298977.3401 | 0 | 4878077.503 | 0 | 0 | 0 | 1123806.4424 | 4797335.9014 | 12481683.9464 | 8519005.7664 | 38098886.8997 | 961560.8286 | 15283055.5775 | 15283055.5775 | 12387543.6942 | 6495607.7911 | 0 | 54343503.3059 | 88509710.3687 | 10000000 | 14.6439 | 3711.0068 | 6044.1473 | 75.6539 | 123.2181
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.074723 | 0.0052763 | 4 | 858119.3 | 2523590.6769 | 17493.9226 | 51446.8094 | 77.7404 | 12.0551 | 158.475 | 183396.0817 | 0 | 93471.8611 | 0 | 0 | 0 | 165416.6198 | 172490.9794 | 448786.1457 | 306305.7661 | 1369867.4538 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 18110724.7258 | 53260725.0146 | 100 | 0.021105 | 858119.3 | 2523590.6769 | 17493.9226 | 51446.8094
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.16321 | 0.012036 | 4 | 387311.6204 | 1117385.105 | 7895.8713 | 22779.4067 | 86.0863 | 12.5612 | 239.1102 | 258468.1081 | 0 | 140218.6171 | 0 | 0 | 0 | 216886.2324 | 240073.4535 | 624621.8801 | 426317.2679 | 1906585.559 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 18647442.831 | 53797443.1198 | 133.3521 | 0.048146 | 387311.6204 | 1117385.105 | 7895.8713 | 22779.4067
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.28684 | 0.022292 | 4 | 215958.7298 | 610159.262 | 4402.6108 | 12438.9219 | 92.7304 | 12.9153 | 48.2598 | 345050.1078 | 0 | 195164.0384 | 0 | 0 | 0 | 272025.0836 | 316773.2996 | 824179.1465 | 562519.2027 | 2515710.8785 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 19256568.1505 | 54406568.4393 | 177.8279 | 0.089168 | 215958.7298 | 610159.262 | 4402.6108 | 12438.9219
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8607 | 0.45543 | 0.037027 | 4 | 134820.921 | 372146.9689 | 2748.5068 | 7586.7193 | 98.1654 | 13.1759 | 53.0879 | 446992.6189 | 0 | 261260.417 | 0 | 0 | 0 | 333723.1373 | 406370.7075 | 1057293.2229 | 721624.3498 | 3227264.4533 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 19968121.7252 | 55118122.014 | 237.1374 | 0.14811 | 134820.921 | 372146.9689 | 2748.5068 | 7586.7193
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1519 | 0.68752 | 0.057773 | 4 | 90107.8548 | 242212.7973 | 1836.9705 | 4937.8355 | 102.7311 | 13.3764 | 42.8347 | 571652.9328 | 0 | 337836.487 | 0 | 0 | 0 | 408519.4976 | 514023.4778 | 1337383.6485 | 912791.8206 | 4082207.8643 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 20823065.1362 | 55973065.425 | 316.2278 | 0.23109 | 90107.8548 | 242212.7973 | 1836.9705 | 4937.8355
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7714 | 0.98835 | 0.086244 | 4 | 63128.796 | 165019.8277 | 1286.9659 | 3364.1524 | 106.3211 | 13.5228 | 55.8484 | 715750.8604 | 0 | 420409.6302 | 0 | 0 | 0 | 490147.0418 | 634259.9376 | 1650214.2531 | 1126305.1363 | 5037086.8595 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 21777944.1314 | 56927944.4202 | 421.6965 | 0.34498 | 63128.796 | 165019.8277 | 1286.9659 | 3364.1524
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7982 | 1.3729 | 0.12437 | 4 | 45977.5915 | 116636.399 | 937.3154 | 2377.7908 | 109.1437 | 13.6304 | 57.4723 | 882180.6639 | 0 | 518378.537 | 0 | 0 | 0 | 579001.3063 | 772028.5978 | 2008660.0466 | 1370951.7556 | 6131200.9072 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 22872058.1791 | 58022058.4679 | 562.3413 | 0.49746 | 45977.5915 | 116636.399 | 937.3154 | 2377.7908
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3929 | 1.8708 | 0.17502 | 4 | 34517.709 | 84725.6102 | 703.6902 | 1727.2462 | 111.405 | 13.7102 | 44.0191 | 1078986.7085 | 0 | 637440.8363 | 0 | 0 | 0 | 680732.2507 | 934892.3202 | 2432398.0445 | 1660161.6462 | 7424611.8064 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 24165469.0783 | 59315469.3671 | 749.8942 | 0.70009 | 34517.709 | 84725.6102 | 703.6902 | 1727.2462
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.6714 | 2.5053 | 0.24163 | 4 | 26562.0114 | 62929.84 | 541.5025 | 1282.9099 | 113.1823 | 13.7674 | 52.6468 | 1309011.1944 | 0 | 780384.153 | 0 | 0 | 0 | 794348.9777 | 1124660.2868 | 2926135.3668 | 1997147.5139 | 8931687.4927 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 25672544.7646 | 60822545.0534 | 1000 | 0.96651 | 26562.0114 | 62929.84 | 541.5025 | 1282.9099
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.8176 | 3.3126 | 0.32863 | 4 | 20870.6735 | 47610.3766 | 425.4769 | 970.6019 | 114.5705 | 13.8044 | 53.6499 | 1578500.0399 | 0 | 952323.325 | 0 | 0 | 0 | 921964.1763 | 1346587.141 | 3503543.518 | 2391240.4416 | 10694158.6417 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 27435015.9137 | 62585016.2025 | 1333.5214 | 1.3145 | 20870.6735 | 47610.3766 | 425.4769 | 970.6019
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9844 | 4.3245 | 0.44099 | 4 | 16702.9097 | 36629.7785 | 340.5114 | 746.7476 | 115.6272 | 13.8217 | 74.3178 | 1890033.7241 | 0 | 1156311.4798 | 0 | 0 | 0 | 1061242.3783 | 1601959.1571 | 4167969.1197 | 2844724.5674 | 12722240.4264 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 29463097.6983 | 64613097.9871 | 1778.2794 | 1.764 | 16702.9097 | 36629.7785 | 340.5114 | 746.7476
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3964 | 5.5861 | 0.58468 | 4 | 13594.0419 | 28623.7221 | 277.1329 | 583.5333 | 116.41 | 13.8177 | 66.7452 | 2249156.7109 | 0 | 1397623.6986 | 0 | 0 | 0 | 1212882.0686 | 1895268.3664 | 4931099.5165 | 3365576.744 | 15051607.105 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 31792464.3769 | 66942464.6658 | 2371.3737 | 2.3387 | 13594.0419 | 28623.7221 | 277.1329 | 583.5333
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.1844 | 7.1265 | 0.76513 | 4 | 11241.7244 | 22726.7575 | 229.1778 | 463.3157 | 116.9476 | 13.7887 | 70.8509 | 2654725.1253 | 0 | 1677415.8407 | 0 | 0 | 0 | 1371136.0898 | 2224278.0518 | 5787115.2286 | 3949825.0568 | 17664495.3931 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 34405352.665 | 69555352.9538 | 3162.2777 | 3.0605 | 11241.7244 | 22726.7575 | 229.1778 | 463.3157
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4292 | 8.9655 | 0.98656 | 4 | 9443.6156 | 18350.8616 | 192.5209 | 374.1071 | 117.2595 | 13.7289 | 58.1298 | 3102756.692 | 0 | 1995120.9425 | 0 | 0 | 0 | 1529212.4679 | 2584565.14 | 6724508.327 | 4589615.108 | 20525778.6775 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 37266635.9494 | 72416636.2382 | 4216.965 | 3.9462 | 9443.6156 | 18350.8616 | 192.5209 | 374.1071
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.0204 | 11.0856 | 1.2492 | 4 | 8061.3354 | 15095.9307 | 164.3412 | 307.751 | 117.3488 | 13.6322 | 76.89 | 3580587.2902 | 0 | 2344210.7924 | 0 | 0 | 0 | 1675319.132 | 2964045.7137 | 7711838.9377 | 5263488.5374 | 23539490.4034 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 40280347.6753 | 75430347.9641 | 5623.4133 | 4.9967 | 8061.3354 | 15095.9307 | 164.3412 | 307.751
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.548 | 13.4097 | 1.5461 | 4 | 6997.7632 | 12681.3759 | 142.6589 | 258.527 | 117.2146 | 13.4952 | 83.3133 | 4064774.7564 | 0 | 2709943.1609 | 0 | 0 | 0 | 1793013.6129 | 3341415.2968 | 8693677.1837 | 5933613.3151 | 26536437.3257 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 43277294.5976 | 78427294.8864 | 7498.9421 | 6.1844 | 6997.7632 | 12681.3759 | 142.6589 | 258.527
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.3797 | 15.8126 | 1.8631 | 4 | 6181.7439 | 10898.4398 | 126.0232 | 222.1794 | 116.8731 | 13.3214 | 96.4928 | 4527560.7676 | 0 | 3072878.0019 | 0 | 0 | 0 | 1868287.6929 | 3692803.3203 | 9607916.7413 | 6557600.5989 | 29327047.1228 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 46067904.3947 | 81217904.6835 | 10000 | 7.4523 | 6181.7439 | 10898.4398 | 126.0232 | 222.1794
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7876 | 18.1467 | 2.1809 | 4 | 5558.5565 | 9587.8766 | 113.3187 | 195.4618 | 116.3705 | 13.1224 | 90.7422 | 4943665.6147 | 0 | 3412905.0264 | 0 | 0 | 0 | 1894292.3206 | 3997836.5551 | 10401550.6472 | 7099272.0472 | 31749522.2113 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 48490379.4832 | 83640379.772 | 13335.2143 | 8.7236 | 5558.5565 | 9587.8766 | 113.3187 | 195.4618
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.2091 | 20.2934 | 2.4816 | 4 | 5084.8534 | 8625.9667 | 103.6616 | 175.852 | 115.7731 | 12.9139 | 91.5509 | 5299239.2634 | 0 | 3716266.2783 | 0 | 0 | 0 | 1875660.9246 | 4247554.9218 | 11051266.6133 | 7542716.5444 | 33732704.5458 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 50473561.8178 | 85623562.1066 | 17782.7941 | 9.9263 | 5084.8534 | 8625.9667 | 103.6616 | 175.852
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.2734 | 22.1724 | 2.7514 | 4 | 4726.1189 | 7919.9911 | 96.3483 | 161.4597 | 115.1504 | 12.7119 | 95.7979 | 5589923.2017 | 0 | 3975153.2847 | 0 | 0 | 0 | 1823144.5499 | 4441406.2042 | 11555627.8856 | 7886953.4763 | 35272208.6026 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 52013065.8745 | 87163066.1633 | 23713.7371 | 11.0055 | 4726.1189 | 7919.9911 | 96.3483 | 161.4597
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8593 | 23.7536 | 2.9832 | 4 | 4455.1359 | 7400.8247 | 90.824 | 150.8758 | 114.5568 | 12.528 | 87.7876 | 5820027.3329 | 0 | 4188607.7872 | 0 | 0 | 0 | 1750463.7825 | 4586048.572 | 11931957.6565 | 8143806.2778 | 36420911.409 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 53161768.6809 | 88311768.9697 | 31622.7766 | 11.9327 | 4455.1359 | 7400.8247 | 90.824 | 150.8758
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9929 | 25.0387 | 3.1752 | 4 | 4250.7493 | 7018.2825 | 86.6573 | 143.0772 | 114.0288 | 12.3694 | 107.7552 | 5997292.5073 | 0 | 4359223.0241 | 0 | 0 | 0 | 1669375.4782 | 4690097.4938 | 12202671.6075 | 8328574.1119 | 37247234.2228 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 53988091.4948 | 89138091.7836 | 42169.6503 | 12.7008 | 4250.7493 | 7018.2825 | 86.6573 | 143.0772
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8682 | 26.0642 | 3.3305 | 4 | 4096.7257 | 6735.2043 | 83.5173 | 137.3062 | 113.5782 | 12.2371 | 95.2111 | 6132553.9345 | 0 | 4493653.1361 | 0 | 0 | 0 | 1589782.2012 | 4764235.816 | 12395564.3141 | 8460227.3478 | 37836016.7497 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 54576874.0216 | 89726874.3104 | 56234.1325 | 13.3221 | 4096.7257 | 6735.2043 | 83.5173 | 137.3062
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.6628 | 26.8654 | 3.4534 | 4 | 3980.7183 | 6525.304 | 81.1523 | 133.0271 | 113.2084 | 12.1301 | 115.6976 | 6234345.129 | 0 | 4597592.3045 | 0 | 0 | 0 | 1516863.8647 | 4816032.5063 | 12530328.6773 | 8552206.7948 | 38247369.2767 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 54988226.5486 | 90138226.8375 | 74989.4209 | 13.8136 | 3980.7183 | 6525.304 | 81.1523 | 133.0271
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.5935 | 27.4858 | 3.5494 | 4 | 3893.3823 | 6369.1468 | 79.3719 | 129.8437 | 112.9113 | 12.0452 | 97.685 | 6310854.1722 | 0 | 4677466.8011 | 0 | 0 | 0 | 1453657.6131 | 4852371.6487 | 12624875.6716 | 8616737.0611 | 38535962.9677 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55276820.2397 | 90426820.5285 | 100000 | 14.1976 | 3893.3823 | 6369.1468 | 79.3719 | 129.8437
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8445 | 27.9632 | 3.6237 | 4 | 3827.6601 | 6252.6786 | 78.032 | 127.4693 | 112.6762 | 11.9786 | 100.9149 | 6368361.1037 | 0 | 4738583.9296 | 0 | 0 | 0 | 1400929.3304 | 4878071.0018 | 12691740.1168 | 8662373.4189 | 38740058.9012 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55480916.1732 | 90630916.462 | 133352.1432 | 14.4947 | 3827.6601 | 6252.6786 | 78.032 | 127.4693
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.5519 | 28.326 | 3.6805 | 4 | 3778.2253 | 6165.781 | 77.0242 | 125.6978 | 112.4939 | 11.9273 | 97.5564 | 6411247.8021 | 0 | 4784812.1893 | 0 | 0 | 0 | 1357905.588 | 4896046.576 | 12738508.8734 | 8694294.0563 | 38882815.085 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55623672.3569 | 90773672.6457 | 177827.941 | 14.7222 | 3778.2253 | 6165.781 | 77.0242 | 125.6978
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8406 | 28.6004 | 3.7238 | 4 | 3741.0587 | 6100.876 | 76.2665 | 124.3746 | 112.3539 | 11.888 | 112.2814 | 6443195.5795 | 0 | 4819630.5573 | 0 | 0 | 0 | 1323498.6188 | 4908666.6547 | 12771343.7296 | 8716704.5203 | 38983039.6602 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55723896.9321 | 90873897.2209 | 237137.3706 | 14.8952 | 3741.0587 | 6100.876 | 76.2665 | 124.3746
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.8151 | 28.808 | 3.7566 | 4 | 3713.1283 | 6052.3138 | 75.6971 | 123.3846 | 112.2468 | 11.8581 | 102.6911 | 6467110.0638 | 0 | 4845915.6539 | 0 | 0 | 0 | 1296477.1349 | 4917706.1125 | 12794862.5445 | 8732756.5947 | 39054828.1042 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55795685.3761 | 90945685.6649 | 316227.766 | 15.0266 | 3713.1283 | 6052.3138 | 75.6971 | 123.3846
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5534 | 28.9654 | 3.7815 | 4 | 3692.1471 | 6015.9302 | 75.2694 | 122.6429 | 112.1648 | 11.8353 | 101.991 | 6485090.0935 | 0 | 4865806.7569 | 0 | 0 | 0 | 1275542.588 | 4924311.381 | 12812048.0981 | 8744486.0882 | 39107285.0057 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55848142.2776 | 90998142.5664 | 421696.5034 | 15.1262 | 3692.1471 | 6015.9302 | 75.2694 | 122.6429
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.1038 | 29.0829 | 3.8003 | 4 | 3676.3917 | 5988.7276 | 74.9482 | 122.0883 | 112.1033 | 11.8182 | 117.5513 | 6498416.8107 | 0 | 4880624.2347 | 0 | 0 | 0 | 1259337.2514 | 4928967.5358 | 12824162.4578 | 8752754.3876 | 39144262.678 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55885119.95 | 91035120.2388 | 562341.3252 | 15.2011 | 3676.3917 | 5988.7276 | 74.9482 | 122.0883
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5324 | 29.1742 | 3.8146 | 4 | 3664.5641 | 5968.2239 | 74.7071 | 121.6703 | 112.0551 | 11.8048 | 105.9178 | 6508749.3216 | 0 | 4892154.0061 | 0 | 0 | 0 | 1247162.3082 | 4932745.598 | 12833992.2007 | 8759463.3891 | 39174266.8237 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55915124.0956 | 91065124.3844 | 749894.2093 | 15.2583 | 3664.5641 | 5968.2239 | 74.7071 | 121.6703
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8445 | 29.2409 | 3.8252 | 4 | 3655.6871 | 5952.944 | 74.5261 | 121.3588 | 112.0199 | 11.7951 | 91.1216 | 6516245.9743 | 0 | 4900545.2256 | 0 | 0 | 0 | 1237739.0221 | 4935266.7866 | 12840551.8162 | 8763940.4615 | 39194289.2863 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55935146.5582 | 91085146.847 | 1000000 | 15.3009 | 3655.6871 | 5952.944 | 74.5261 | 121.3588
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.066 | 29.2885 | 3.833 | 4 | 3649.026 | 5941.5995 | 74.3903 | 121.1275 | 111.9948 | 11.7881 | 105.0999 | 6521551.7753 | 0 | 4906498.8321 | 0 | 0 | 0 | 1230398.278 | 4936795.0653 | 12844528.084 | 8766654.346 | 39206426.3807 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55947283.6527 | 91097283.9415 | 1333521.4322 | 15.3321 | 3649.026 | 5941.5995 | 74.3903 | 121.1275
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2512 | 29.3279 | 3.8392 | 4 | 3644.0283 | 5932.9373 | 74.2884 | 120.951 | 111.9738 | 11.7823 | 101.6256 | 6525982.8696 | 0 | 4911475.5761 | 0 | 0 | 0 | 1225132.0012 | 4938410.2743 | 12848730.5265 | 8769522.5993 | 39219253.8471 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55960111.119 | 91110111.4078 | 1778279.41 | 15.3567 | 3644.0283 | 5932.9373 | 74.2884 | 120.951
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.3755 | 29.3546 | 3.8436 | 4 | 3640.2792 | 5926.5664 | 74.212 | 120.8211 | 111.9597 | 11.7784 | 105.2452 | 6528949.5379 | 0 | 4914814.0276 | 0 | 0 | 0 | 1220935.9797 | 4939232.8226 | 12850870.6285 | 8770983.2629 | 39225786.2592 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55966643.5311 | 91116643.8199 | 2371373.7057 | 15.3743 | 3640.2792 | 5926.5664 | 74.212 | 120.8211
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.483 | 29.3774 | 3.8471 | 4 | 3637.467 | 5921.6719 | 74.1547 | 120.7213 | 111.9475 | 11.775 | 107.326 | 6531513.5604 | 0 | 4917699.4715 | 0 | 0 | 0 | 1217986.5207 | 4940207.8255 | 12853407.386 | 8772714.652 | 39233529.4161 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55974386.688 | 91124386.9768 | 3162277.6602 | 15.3883 | 3637.467 | 5921.6719 | 74.1547 | 120.7213
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.5607 | 29.3939 | 3.8497 | 4 | 3635.3577 | 5918.0255 | 74.1117 | 120.647 | 111.9386 | 11.7726 | 102.5397 | 6533368.274 | 0 | 4919788.6666 | 0 | 0 | 0 | 1215724.3551 | 4940863.7053 | 12855113.8507 | 8773879.3493 | 39238738.2011 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55979595.473 | 91129595.7618 | 4216965.0343 | 15.3986 | 3635.3577 | 5918.0255 | 74.1117 | 120.647
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6191 | 29.4064 | 3.8516 | 4 | 3633.7756 | 5915.2916 | 74.0794 | 120.5912 | 111.932 | 11.7708 | 107.9113 | 6534758.4244 | 0 | 4921355.4174 | 0 | 0 | 0 | 1214023.0039 | 4941353.3698 | 12856387.8574 | 8774748.885 | 39242626.958 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55983484.23 | 91133484.5188 | 5623413.2519 | 15.4064 | 3633.7756 | 5915.2916 | 74.0794 | 120.5912
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6534 | 29.4138 | 3.8529 | 4 | 3632.5891 | 5913.3204 | 74.0552 | 120.551 | 111.9281 | 11.7697 | 99.1907 | 6535573.1277 | 0 | 4922275.5145 | 0 | 0 | 0 | 1212603.1678 | 4941476.2059 | 12856707.4516 | 8774967.0147 | 39243602.4822 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55984459.7542 | 91134460.043 | 7498942.0933 | 15.4117 | 3632.5891 | 5913.3204 | 74.0552 | 120.551
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6922 | 29.422 | 3.8541 | 4 | 3631.6993 | 5911.7329 | 74.0371 | 120.5187 | 111.9237 | 11.7684 | 103.7794 | 6536500.0602 | 0 | 4923319.897 | 0 | 0 | 0 | 1211733.2437 | 4941905.7483 | 12857825.0329 | 8775729.7869 | 39247013.769 | 961560.8286 | 15779296.4433 | 15779296.4433 | 12703572.8692 | 6667130.9763 | 0 | 55987871.041 | 91137871.3298 | 10000000 | 15.4164 | 3631.6993 | 5911.7329 | 74.0371 | 120.5187
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5542 | 0.078942 | 0.0056616 | 4 | 825244.546 | 2421409.4967 | 16823.7263 | 49363.7078 | 79.6244 | 12.4997 | 163.8597 | 193677.5592 | 0 | 97754.3939 | 0 | 0 | 0 | 175417.2024 | 182071.1706 | 473711.8381 | 323318.0633 | 1445950.2275 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 18688908.4561 | 54836473.1844 | 100 | 0.022647 | 825244.546 | 2421409.4967 | 16823.7263 | 49363.7078
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.17167 | 0.012964 | 4 | 371226.5216 | 1068316.2468 | 7567.9548 | 21779.0717 | 88.223 | 13.0149 | 250.482 | 272418.8001 | 0 | 146196.5892 | 0 | 0 | 0 | 229371.8515 | 252715.0239 | 657512.6533 | 448765.8964 | 2006980.8144 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 19249939.043 | 55397503.7713 | 133.3521 | 0.051855 | 371226.5216 | 1068316.2468 | 7567.9548 | 21779.0717
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9936 | 0.30204 | 0.024048 | 4 | 206798.6666 | 582587.2421 | 4215.8705 | 11876.8289 | 95.1264 | 13.3783 | 48.9479 | 363919.4043 | 0 | 203548.6268 | 0 | 0 | 0 | 287889.6163 | 333589.4825 | 867931.4048 | 592381.018 | 2649259.5526 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 19892217.7811 | 56039782.5095 | 177.8279 | 0.096191 | 206798.6666 | 582587.2421 | 4215.8705 | 11876.8289
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0117 | 0.48085 | 0.039986 | 4 | 129092.2554 | 355091.4078 | 2631.7202 | 7239.0186 | 100.7965 | 13.6468 | 58.8731 | 472271.5564 | 0 | 272930.0406 | 0 | 0 | 0 | 354087.462 | 428722.733 | 1115448.6082 | 761316.5953 | 3404776.9954 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 20647735.224 | 56795299.9523 | 237.1374 | 0.15995 | 129092.2554 | 355091.4078 | 2631.7202 | 7239.0186
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3487 | 0.72543 | 0.062516 | 4 | 86104.9937 | 230657.7769 | 1755.3668 | 4702.2708 | 105.5132 | 13.8512 | 61.7334 | 603610.5088 | 0 | 348120.7373 | 0 | 0 | 0 | 433002.2904 | 540046.0792 | 1405089.1195 | 959002.1958 | 4288870.9311 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 21531829.1597 | 57679393.888 | 316.2278 | 0.25006 | 86104.9937 | 230657.7769 | 1755.3668 | 4702.2708
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0077 | 1.0397 | 0.093256 | 4 | 60368.38 | 157272.8862 | 1230.6911 | 3206.2205 | 109.1938 | 13.9992 | 60.5806 | 753898.5896 | 0 | 432107.6404 | 0 | 0 | 0 | 517376.4017 | 664319.2264 | 1728422.3564 | 1179683.7738 | 5275807.9882 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 22518766.2168 | 58666330.9451 | 421.6965 | 0.37302 | 60368.38 | 157272.8862 | 1230.6911 | 3206.2205
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1271 | 1.4484 | 0.1345 | 4 | 44013.3211 | 111201.1508 | 897.2711 | 2266.9859 | 112.1487 | 14.1104 | 59.1137 | 931036.3218 | 0 | 533826.0994 | 0 | 0 | 0 | 613283.2393 | 810476.8076 | 2108694.4017 | 1439227.2585 | 6436544.1283 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 23679502.3569 | 59827067.0853 | 562.3413 | 0.53801 | 44013.3211 | 111201.1508 | 897.2711 | 2266.9859
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7996 | 1.9708 | 0.18913 | 4 | 33079.0849 | 80860.3396 | 674.3619 | 1648.4474 | 114.4791 | 14.1918 | 60.5807 | 1137359.5631 | 0 | 655582.4024 | 0 | 0 | 0 | 719636.714 | 979905.685 | 2549513.5861 | 1740095.4098 | 7782093.3605 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 25025051.5891 | 61172616.3174 | 749.8942 | 0.75652 | 33079.0849 | 80860.3396 | 674.3619 | 1648.4474
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2024 | 2.6412 | 0.26107 | 4 | 25480.0362 | 60094.984 | 519.445 | 1225.1175 | 116.3248 | 14.2493 | 68.1907 | 1380377.8397 | 0 | 802899.4201 | 0 | 0 | 0 | 840445.4733 | 1179251.8659 | 3068171.4573 | 2094090.0642 | 9365236.1207 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 26608194.3493 | 62755759.0776 | 1000 | 1.0443 | 25480.0362 | 60094.984 | 519.445 | 1225.1175
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4755 | 3.4889 | 0.35481 | 4 | 20041.3316 | 45511.3131 | 408.5697 | 927.8097 | 117.7572 | 14.2861 | 58.9484 | 1663135.943 | 0 | 978866.837 | 0 | 0 | 0 | 974151.0956 | 1410300.0115 | 3669311.3376 | 2504380.3847 | 11200145.6093 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 28443103.8379 | 64590668.5662 | 1333.5214 | 1.4192 | 20041.3316 | 45511.3131 | 408.5697 | 927.8097
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8151 | 4.554 | 0.47587 | 4 | 16056.035 | 35046.217 | 327.324 | 714.4645 | 118.8512 | 14.3023 | 61.4188 | 1990974.3638 | 0 | 1188241.6924 | 0 | 0 | 0 | 1121205.4014 | 1677164.3684 | 4363637.653 | 2978272.3619 | 13319495.8409 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 30562454.0695 | 66710018.7978 | 1778.2794 | 1.9035 | 16056.035 | 35046.217 | 327.324 | 714.4645
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4272 | 5.8794 | 0.63047 | 4 | 13081.6344 | 27415.3228 | 266.6868 | 558.8984 | 119.6595 | 14.296 | 48.9215 | 2368096.7374 | 0 | 1435411.9007 | 0 | 0 | 0 | 1280705.5995 | 1982843.5527 | 5158952.1869 | 3521090.8734 | 15747100.8505 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 32990059.0791 | 69137623.8074 | 2371.3737 | 2.5219 | 13081.6344 | 27415.3228 | 266.6868 | 558.8984
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.4413 | 7.4946 | 0.82424 | 4 | 10830.1307 | 21794.055 | 220.7869 | 444.3013 | 120.2128 | 14.2629 | 69.352 | 2793141.2134 | 0 | 1721444.0745 | 0 | 0 | 0 | 1446662.1144 | 2324886.4869 | 6048877.739 | 4128483.3489 | 18463494.9771 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 35706453.2056 | 71854017.934 | 3162.2777 | 3.297 | 10830.1307 | 21794.055 | 220.7869 | 444.3013
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.9413 | 9.4203 | 1.0615 | 4 | 9108.7812 | 17621.9364 | 185.6948 | 359.247 | 120.531 | 14.1969 | 84.0835 | 3262036.6477 | 0 | 2045843.5357 | 0 | 0 | 0 | 1612342.2192 | 2698886.737 | 7021949.6719 | 4792624.9377 | 21433683.7493 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 38676641.9779 | 74824206.7062 | 4216.965 | 4.2461 | 9108.7812 | 17621.9364 | 185.6948 | 359.247
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.7675 | 11.6295 | 1.3417 | 4 | 7785.7401 | 14521.034 | 158.7228 | 296.0309 | 120.6162 | 14.0916 | 69.5925 | 3759469.5539 | 0 | 2400515.2982 | 0 | 0 | 0 | 1763884.5095 | 3090309.051 | 8040350.2412 | 5487704.2523 | 24542232.9062 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 41785191.1348 | 77932755.8631 | 5623.4133 | 5.3669 | 7785.7401 | 14521.034 | 158.7228 | 296.0309
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.4628 | 14.0338 | 1.6566 | 4 | 6768.2847 | 12223.4818 | 137.9806 | 249.1922 | 120.4697 | 13.9446 | 85.7832 | 4259760.1967 | 0 | 2769468.2284 | 0 | 0 | 0 | 1883657.9016 | 3476025.6674 | 9043905.7557 | 6172651.5119 | 27605469.2618 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 44848427.4904 | 80995992.2187 | 7498.9421 | 6.6263 | 6768.2847 | 12223.4818 | 137.9806 | 249.1922
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.4138 | 16.509 | 1.9909 | 4 | 5988.2203 | 10527.3991 | 122.078 | 214.6153 | 120.1109 | 13.7596 | 88.8249 | 4735886.5687 | 0 | 3134170.7262 | 0 | 0 | 0 | 1959292.3878 | 3833446.3763 | 9973841.1231 | 6807351.5084 | 30443988.6905 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 47686946.9191 | 83834511.6474 | 10000 | 7.9635 | 5988.2203 | 10527.3991 | 122.078 | 214.6153
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.905 | 18.9064 | 2.3245 | 4 | 5392.9487 | 9280.5467 | 109.9426 | 189.1965 | 119.589 | 13.5491 | 89.9454 | 5162848.5549 | 0 | 3475070.3226 | 0 | 0 | 0 | 1984918.2102 | 4142906.4642 | 10778992.7928 | 7356884.0673 | 32901620.4119 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 50144578.6405 | 86292143.3688 | 13335.2143 | 9.2982 | 5392.9487 | 9280.5467 | 109.9426 | 189.1965
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.3233 | 21.0955 | 2.6381 | 4 | 4940.7821 | 8366.2925 | 100.7245 | 170.5582 | 118.9763 | 13.3309 | 101.6932 | 5525026.3595 | 0 | 3777042.4887 | 0 | 0 | 0 | 1964187.1187 | 4393839.8271 | 11431869.9296 | 7802486.1284 | 34894451.8519 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 52137410.0805 | 88284974.8088 | 17782.7941 | 10.5525 | 4940.7821 | 8366.2925 | 100.7245 | 170.5582
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.3487 | 23.0041 | 2.9182 | 4 | 4598.5626 | 7695.3234 | 93.7479 | 156.8796 | 118.3423 | 13.1208 | 102.6708 | 5820069.682 | 0 | 4033826.9232 | 0 | 0 | 0 | 1909650.6921 | 4587783.446 | 11936471.4426 | 8146887.0296 | 36434689.2155 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 53677647.4441 | 89825212.1724 | 23713.7371 | 11.6727 | 4598.5626 | 7695.3234 | 93.7479 | 156.8796
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.8472 | 24.5992 | 3.1574 | 4 | 4340.1866 | 7202.2804 | 88.4806 | 146.8282 | 117.744 | 12.9313 | 87.3058 | 6052083.5437 | 0 | 4244092.7749 | 0 | 0 | 0 | 1834753.7936 | 4731062.7438 | 12309254.7849 | 8401319.3206 | 37572566.9616 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 54815525.1902 | 90963089.9185 | 31622.7766 | 12.6298 | 4340.1866 | 7202.2804 | 88.4806 | 146.8282
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.9297 | 25.8993 | 3.3556 | 4 | 4145.3959 | 6838.5117 | 84.5095 | 139.4123 | 117.2111 | 12.7677 | 100.1138 | 6231519.4726 | 0 | 4412750.9683 | 0 | 0 | 0 | 1752975.8454 | 4834926.0517 | 12579485.8067 | 8585757.5457 | 38397415.6904 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 55640373.919 | 91787938.6473 | 42169.6503 | 13.4222 | 4145.3959 | 6838.5117 | 84.5095 | 139.4123
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.746 | 26.933 | 3.5153 | 4 | 3998.6639 | 6569.4241 | 81.5182 | 133.9266 | 116.7587 | 12.6319 | 116.0191 | 6367994.1016 | 0 | 4545163.1555 | 0 | 0 | 0 | 1672967.5516 | 4908588.6754 | 12771140.8433 | 8716566.0463 | 38982420.3736 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 56225378.6022 | 92372943.3305 | 56234.1325 | 14.061 | 3998.6639 | 6569.4241 | 81.5182 | 133.9266
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4876 | 27.7391 | 3.6414 | 4 | 3888.1909 | 6369.9109 | 79.266 | 129.8593 | 116.3885 | 12.5224 | 106.9787 | 6470561.2905 | 0 | 4647365.5126 | 0 | 0 | 0 | 1599985.2545 | 4959985.7025 | 12904865.3649 | 8807835.78 | 39390598.9049 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 56633557.1335 | 92781121.8618 | 74989.4209 | 14.5655 | 3888.1909 | 6369.9109 | 79.266 | 129.8593
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.377 | 28.3632 | 3.7398 | 4 | 3805.0516 | 6221.4569 | 77.5711 | 126.8328 | 116.0913 | 12.4355 | 109.63 | 6547683.2146 | 0 | 4725906.6526 | 0 | 0 | 0 | 1537014.2118 | 4996135.5908 | 12998919.959 | 8872029.9731 | 39677689.6019 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 56920647.8305 | 93068212.5588 | 100000 | 14.9592 | 3805.0516 | 6221.4569 | 77.5711 | 126.8328
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.5862 | 28.8415 | 3.8158 | 4 | 3742.5087 | 6110.8138 | 76.2961 | 124.5772 | 115.8574 | 12.3678 | 103.4455 | 6605413.9569 | 0 | 4785738.7807 | 0 | 0 | 0 | 1484495.2972 | 5021502.7335 | 13064920.0608 | 8917076.3988 | 39879147.2279 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57122105.4565 | 93269670.1848 | 133352.1432 | 15.2631 | 3742.5087 | 6110.8138 | 76.2961 | 124.5772
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2692 | 29.2064 | 3.874 | 4 | 3695.4796 | 6028.1915 | 75.3374 | 122.8928 | 115.6752 | 12.3153 | 103.2196 | 6648672.669 | 0 | 4831196.5809 | 0 | 0 | 0 | 1441892.8341 | 5039487.2128 | 13111711.9867 | 8949012.8496 | 40021974.1331 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57264932.3617 | 93412497.09 | 177827.941 | 15.4959 | 3695.4796 | 6028.1915 | 75.3374 | 122.8928
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5339 | 29.4812 | 3.9182 | 4 | 3660.1312 | 5966.5284 | 74.6167 | 121.6358 | 115.536 | 12.2754 | 103.768 | 6680761.2425 | 0 | 4865283.0362 | 0 | 0 | 0 | 1407796.3298 | 5051997.8373 | 13144262.0654 | 8971228.9472 | 40121329.4584 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57364287.687 | 93511852.4153 | 237137.3706 | 15.6727 | 3660.1312 | 5966.5284 | 74.6167 | 121.6358
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.4935 | 29.6899 | 3.9518 | 4 | 3633.5731 | 5920.3629 | 74.0753 | 120.6946 | 115.4292 | 12.2449 | 104.865 | 6704872.2832 | 0 | 4891107.964 | 0 | 0 | 0 | 1381120.5409 | 5061069.3073 | 13167864.1697 | 8987337.8683 | 40193372.1334 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57436330.362 | 93583895.0903 | 316227.766 | 15.8071 | 3633.5731 | 5920.3629 | 74.0753 | 120.6946
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2272 | 29.8493 | 3.9773 | 4 | 3613.6265 | 5885.7211 | 73.6687 | 119.9884 | 115.3467 | 12.2214 | 100.1938 | 6723167.9623 | 0 | 4910828.6707 | 0 | 0 | 0 | 1360585.797 | 5067887.1477 | 13185602.7917 | 8999444.8424 | 40247517.2116 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57490475.4402 | 93638040.1685 | 421696.5034 | 15.9094 | 3613.6265 | 5885.7211 | 73.6687 | 119.9884
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7628 | 29.9661 | 3.9964 | 4 | 3598.6504 | 5859.9157 | 73.3634 | 119.4623 | 115.286 | 12.2042 | 114.9121 | 6736446.8314 | 0 | 4925214.327 | 0 | 0 | 0 | 1344518.7893 | 5072410.1796 | 13197370.793 | 9007476.7451 | 40283437.6654 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57526395.894 | 93673960.6224 | 562341.3252 | 15.9855 | 3598.6504 | 5859.9157 | 73.3634 | 119.4623
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1797 | 30.0568 | 4.0109 | 4 | 3587.409 | 5840.4675 | 73.1342 | 119.0658 | 115.2386 | 12.1907 | 115.1823 | 6746740.0564 | 0 | 4936404.3259 | 0 | 0 | 0 | 1332459.4343 | 5076085.4885 | 13206933.1927 | 9014003.2793 | 40312625.777 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57555584.0056 | 93703148.7339 | 749894.2093 | 16.0438 | 3587.409 | 5840.4675 | 73.1342 | 119.0658
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.4887 | 30.1241 | 4.0218 | 4 | 3578.9729 | 5825.9296 | 72.9622 | 118.7695 | 115.2033 | 12.1807 | 98.5189 | 6754342.0794 | 0 | 4944692.7751 | 0 | 0 | 0 | 1323214.1178 | 5078677.0992 | 13213676.0321 | 9018605.4058 | 40333207.5093 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57576165.7379 | 93723730.4663 | 1000000 | 16.0873 | 3578.9729 | 5825.9296 | 72.9622 | 118.7695
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.723 | 30.1751 | 4.0301 | 4 | 3572.6431 | 5815.0155 | 72.8332 | 118.547 | 115.1765 | 12.1731 | 102.2714 | 6760093.0043 | 0 | 4950975.9625 | 0 | 0 | 0 | 1316239.5646 | 5080650.3272 | 13218809.9668 | 9022109.4217 | 40348878.247 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57591836.4756 | 93739401.2039 | 1333521.4322 | 16.1202 | 3572.6431 | 5815.0155 | 72.8332 | 118.547
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8862 | 30.2109 | 4.0361 | 4 | 3567.8943 | 5806.937 | 72.7364 | 118.3823 | 115.1577 | 12.1678 | 96.8897 | 6764088.6888 | 0 | 4955350.4285 | 0 | 0 | 0 | 1310768.9017 | 5081781.1274 | 13221752.0768 | 9024117.4723 | 40357858.6955 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57600816.9241 | 93748381.6524 | 1778279.41 | 16.1442 | 3567.8943 | 5806.937 | 72.7364 | 118.3823
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.0151 | 30.239 | 4.0406 | 4 | 3564.332 | 5800.8287 | 72.6637 | 118.2577 | 115.1429 | 12.1636 | 100.5759 | 6767242.0809 | 0 | 4958805.5742 | 0 | 0 | 0 | 1306741.6845 | 5082787.8424 | 13224371.3429 | 9025905.1752 | 40365853.7 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57608811.9286 | 93756376.6569 | 2371373.7057 | 16.1626 | 3564.332 | 5800.8287 | 72.6637 | 118.2577
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1077 | 30.2593 | 4.044 | 4 | 3561.66 | 5796.2822 | 72.6093 | 118.1651 | 115.1322 | 12.1606 | 99.1096 | 6769504.6287 | 0 | 4961287.5173 | 0 | 0 | 0 | 1303644.4401 | 5083430.2686 | 13226042.8039 | 9027045.9817 | 40370955.6403 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57613913.8689 | 93761478.5972 | 3162277.6602 | 16.1761 | 3561.66 | 5796.2822 | 72.6093 | 118.1651
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1808 | 30.2753 | 4.0466 | 4 | 3559.6558 | 5792.8438 | 72.5684 | 118.095 | 115.1238 | 12.1582 | 95.779 | 6771291.275 | 0 | 4963248.033 | 0 | 0 | 0 | 1301370.6944 | 5084004.9009 | 13227537.8795 | 9028066.4015 | 40375519.1843 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57618477.4129 | 93766042.1412 | 4216965.0343 | 16.1865 | 3559.6558 | 5792.8438 | 72.5684 | 118.095
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.2392 | 30.288 | 4.0486 | 4 | 3558.1528 | 5790.238 | 72.5378 | 118.0418 | 115.1171 | 12.1563 | 101.5638 | 6772715.7448 | 0 | 4964811.3435 | 0 | 0 | 0 | 1299714.3372 | 5084524.1559 | 13228888.8745 | 9028988.4833 | 40379642.9392 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57622601.1678 | 93770165.8961 | 5623413.2519 | 16.1945 | 3558.1528 | 5790.238 | 72.5378 | 118.0418
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.2929 | 30.2994 | 4.0503 | 4 | 3557.0255 | 5788.2045 | 72.5148 | 118.0004 | 115.1109 | 12.1546 | 95.7024 | 6774027.957 | 0 | 4966250.4729 | 0 | 0 | 0 | 1298622.3977 | 5085171.3228 | 13230572.6697 | 9030137.7082 | 40384782.5282 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57627740.7568 | 93775305.4851 | 7498942.0933 | 16.2011 | 3557.0255 | 5788.2045 | 72.5148 | 118.0004
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3124 | 30.3039 | 4.0512 | 4 | 3556.1801 | 5786.8464 | 72.4975 | 117.9727 | 115.1086 | 12.154 | 97.3395 | 6774500.3877 | 0 | 4966771.5113 | 0 | 0 | 0 | 1297482.3164 | 5085114.144 | 13230423.9023 | 9030036.1713 | 40384328.433 | 961560.8286 | 16281397.4 | 16281397.4 | 13025169.1305 | 6840998.1979 | 0 | 57627286.6616 | 93774851.3899 | 10000000 | 16.2048 | 3556.1801 | 5786.8464 | 72.4975 | 117.9727
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.083284 | 0.0060729 | 4 | 793453.7036 | 2323161.6888 | 16175.627 | 47360.7933 | 81.5088 | 12.9445 | 175.5103 | 204158.1107 | 0 | 102084.3956 | 0 | 0 | 0 | 185567.6485 | 191805.9604 | 499039.764 | 340604.8932 | 1523260.7724 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 19274180.0485 | 56433080.4298 | 100 | 0.024291 | 793453.7036 | 2323161.6888 | 16175.627 | 47360.7933
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 0.18036 | 0.013948 | 4 | 355973.5217 | 1022018.8573 | 7257.0017 | 20835.2368 | 90.3616 | 13.4689 | 259.0818 | 286642.6665 | 0 | 152240.8547 | 0 | 0 | 0 | 242031.6683 | 265556.9239 | 690924.6428 | 471570.2658 | 2108967.022 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 19859886.2981 | 57018786.6794 | 133.3521 | 0.05579 | 355973.5217 | 1022018.8573 | 7257.0017 | 20835.2368
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1102 | 0.31885 | 0.025917 | 4 | 198178.9422 | 556619.7916 | 4040.1458 | 11347.4473 | 97.59 | 13.8449 | 48.482 | 384214.5053 | 0 | 212678.2074 | 0 | 0 | 0 | 305172.71 | 351805.5148 | 915325.7844 | 624728.6559 | 2793925.3778 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 20544844.6539 | 57703745.0353 | 177.8279 | 0.10367 | 198178.9422 | 556619.7916 | 4040.1458 | 11347.4473
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1554 | 0.50588 | 0.043101 | 4 | 123718.3718 | 339250.6773 | 2522.1663 | 6916.0839 | 103.3995 | 14.1165 | 65.2983 | 497330.9004 | 0 | 284245.5506 | 0 | 0 | 0 | 373891.4685 | 450632.4886 | 1172453.298 | 800223.4674 | 3578777.1737 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 21329696.4498 | 58488596.8311 | 237.1374 | 0.17241 | 123718.3718 | 339250.6773 | 2522.1663 | 6916.0839
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5534 | 0.76553 | 0.067548 | 4 | 82370.0311 | 219897.5187 | 1679.2245 | 4482.9084 | 108.3224 | 14.3272 | 58.1175 | 637005.9527 | 0 | 358737.2788 | 0 | 0 | 0 | 458722.1509 | 567241.4991 | 1475846.0235 | 1007295.2366 | 4504848.1416 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 22255767.4177 | 59414667.7991 | 316.2278 | 0.27019 | 82370.0311 | 219897.5187 | 1679.2245 | 4482.9084
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2707 | 1.0966 | 0.10072 | 4 | 57802.8172 | 150032.525 | 1178.3886 | 3058.616 | 112.1192 | 14.4779 | 64.5551 | 795175.6817 | 0 | 445033.9524 | 0 | 0 | 0 | 547682.2198 | 697277.823 | 1814173.8641 | 1238210.9398 | 5537554.4807 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 23288473.7568 | 60447374.1381 | 421.6965 | 0.4029 | 57802.8172 | 150032.525 | 1178.3886 | 3058.616
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4561 | 1.5258 | 0.14517 | 4 | 42187.9066 | 106181.4088 | 860.0575 | 2164.6516 | 115.1601 | 14.5907 | 62.0561 | 980900.0707 | 0 | 549162.6898 | 0 | 0 | 0 | 648059.2598 | 849467.5879 | 2210140.4139 | 1508466.2464 | 6746196.2685 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 24497115.5445 | 61656015.9259 | 562.3413 | 0.58067 | 42187.9066 | 106181.4088 | 860.0575 | 2164.6516
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2212 | 2.076 | 0.20404 | 4 | 31740.2139 | 77269.9455 | 647.0672 | 1575.2524 | 117.5694 | 14.6735 | 61.2425 | 1198027.9456 | 0 | 674253.3824 | 0 | 0 | 0 | 760284.4531 | 1026700.6546 | 2671264.4981 | 1823192.9089 | 8153723.8427 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 25904643.1188 | 63063543.5001 | 749.8942 | 0.81615 | 31740.2139 | 77269.9455 | 647.0672 | 1575.2524
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7313 | 2.7802 | 0.28146 | 4 | 24474.8961 | 57480.4761 | 498.9539 | 1171.8173 | 119.4742 | 14.7321 | 74.5312 | 1453077.3153 | 0 | 825172.7862 | 0 | 0 | 0 | 887077.4852 | 1234477.7588 | 3211857.9023 | 2192159.0154 | 9803822.2633 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 27554741.5393 | 64713641.9207 | 1000 | 1.1258 | 24474.8961 | 57480.4761 | 498.9539 | 1171.8173
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1406 | 3.6709 | 0.38231 | 4 | 19269.5068 | 43568.318 | 392.835 | 888.1991 | 120.953 | 14.7681 | 59.3027 | 1749951.1169 | 0 | 1005520.4603 | 0 | 0 | 0 | 1027534.4492 | 1475372.3503 | 3838616.215 | 2619934.4424 | 11716929.0341 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 29467848.3102 | 66626748.6915 | 1333.5214 | 1.5292 | 19269.5068 | 43568.318 | 392.835 | 888.1991
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.6434 | 4.7888 | 0.51242 | 4 | 15453.5455 | 33582.8328 | 315.0414 | 684.6315 | 122.0822 | 14.7831 | 71.2836 | 2093799.5982 | 0 | 1219866.4104 | 0 | 0 | 0 | 1181805.8586 | 1753234.0282 | 4561555.3037 | 3113355.2253 | 13923616.4245 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 31674535.7006 | 68833436.0819 | 1778.2794 | 2.0497 | 15453.5455 | 33582.8328 | 315.0414 | 684.6315
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4593 | 6.1803 | 0.67843 | 4 | 12603.9695 | 26297.0311 | 256.949 | 536.1005 | 122.9167 | 14.7742 | 60.1016 | 2489482.7861 | 0 | 1473002.8311 | 0 | 0 | 0 | 1349481.3712 | 2071667.1255 | 5390052.9031 | 3678821.8609 | 16452508.8778 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 34203428.1539 | 71362328.5353 | 2371.3737 | 2.7137 | 12603.9695 | 26297.0311 | 256.949 | 536.1005
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.7077 | 7.8736 | 0.88617 | 4 | 10446.0998 | 20929.1411 | 212.9579 | 426.6689 | 123.4858 | 14.7367 | 68.7401 | 2934767.1618 | 0 | 1765523.2493 | 0 | 0 | 0 | 1523622.1142 | 2427325.8849 | 6315404.0395 | 4310393.0255 | 19277035.4753 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 37027954.7514 | 74186855.1327 | 3162.2777 | 3.5447 | 10446.0998 | 20929.1411 | 212.9579 | 426.6689
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.4371 | 9.8833 | 1.1396 | 4 | 8796.093 | 16947.4998 | 179.3203 | 345.4977 | 123.8092 | 14.6643 | 71.2411 | 3423586.8256 | 0 | 2095715.4609 | 0 | 0 | 0 | 1695747.5973 | 2813869.4547 | 7321111.1172 | 4996808.7713 | 22346839.227 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 40097758.5031 | 77256658.8844 | 4216.965 | 4.5586 | 8796.093 | 16947.4998 | 179.3203 | 345.4977
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.4823 | 12.1803 | 1.4378 | 4 | 7528.1468 | 13989.1324 | 153.4715 | 285.1874 | 123.8902 | 14.5503 | 84.5624 | 3940192.1693 | 0 | 2455456.0357 | 0 | 0 | 0 | 1852148.4411 | 3216640.692 | 8369039.2568 | 5712041.2593 | 25545517.8541 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 43296437.1302 | 80455337.5116 | 5623.4133 | 5.7513 | 7528.1468 | 13989.1324 | 153.4715 | 285.1874
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.3749 | 14.6722 | 1.7714 | 4 | 6553.5879 | 11797.7649 | 133.6038 | 240.5134 | 123.7307 | 14.3923 | 81.7462 | 4458027.8892 | 0 | 2828592.3402 | 0 | 0 | 0 | 1975176.0878 | 3612100.5637 | 9397944.723 | 6414290.3819 | 28686131.9858 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 46437051.2619 | 83595951.6432 | 7498.9421 | 7.0857 | 6553.5879 | 11797.7649 | 133.6038 | 240.5134
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4406 | 17.2199 | 2.1234 | 4 | 5806.952 | 10181.8872 | 118.3826 | 207.5715 | 123.3543 | 14.1958 | 89.3591 | 4947315.7615 | 0 | 3194948.862 | 0 | 0 | 0 | 2050940.8558 | 3975350.1369 | 10343045.5998 | 7059341.1502 | 31570942.3661 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 49321861.6422 | 86480762.0236 | 10000 | 8.4936 | 5806.952 | 10181.8872 | 118.3826 | 207.5715
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.9675 | 19.6721 | 2.4725 | 4 | 5237.6142 | 8994.8175 | 106.7759 | 183.3715 | 122.8154 | 13.9745 | 105.7708 | 5383341.2581 | 0 | 3535356.3728 | 0 | 0 | 0 | 2074689.8684 | 4287421.1247 | 11154990.2955 | 7613510.0888 | 34049309.0083 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 51800228.2843 | 88959128.6657 | 13335.2143 | 9.89 | 5237.6142 | 8994.8175 | 106.7759 | 183.3715
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.387 | 21.9046 | 2.7991 | 4 | 4805.4376 | 8124.2359 | 97.9653 | 165.6235 | 122.1876 | 13.7462 | 108.0965 | 5752230.5715 | 0 | 3836133.3072 | 0 | 0 | 0 | 2051989.7195 | 4539737.9033 | 11811466.7961 | 8061568.7897 | 36053127.0874 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 53804046.3634 | 90962946.7448 | 17782.7941 | 11.1965 | 4805.4376 | 8124.2359 | 97.9653 | 165.6235
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.3561 | 23.8391 | 3.0892 | 4 | 4478.5344 | 7485.7069 | 91.301 | 152.6063 | 121.5444 | 13.5285 | 101.378 | 6050973.3877 | 0 | 4090379.1969 | 0 | 0 | 0 | 1994961.7431 | 4733162.5878 | 12314718.1483 | 8405048.1784 | 37589243.2421 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 55340162.5182 | 92499062.8996 | 23713.7371 | 12.3568 | 4478.5344 | 7485.7069 | 91.301 | 152.6063
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.8151 | 25.4572 | 3.3365 | 4 | 4231.8411 | 7016.078 | 86.2718 | 143.0322 | 120.9382 | 13.3323 | 101.973 | 6286253.5515 | 0 | 4298838.6097 | 0 | 0 | 0 | 1918873.8735 | 4876546.7535 | 12687774.3354 | 8659666.6916 | 38727953.8151 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 56478873.0912 | 93637773.4725 | 31622.7766 | 13.3462 | 4231.8411 | 7016.078 | 86.2718 | 143.0322
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.825 | 26.7677 | 3.5404 | 4 | 4045.9355 | 6669.8819 | 82.4819 | 135.9746 | 120.4026 | 13.1643 | 99.1392 | 6467099.5029 | 0 | 4464975.3363 | 0 | 0 | 0 | 1835823.3496 | 4979480.2936 | 12955586.2922 | 8842453.8551 | 39545418.6297 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 57296337.9058 | 94455238.2872 | 42169.6503 | 14.1615 | 4045.9355 | 6669.8819 | 82.4819 | 135.9746
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5728 | 27.8073 | 3.7043 | 4 | 3905.9491 | 6413.7926 | 79.6281 | 130.7538 | 119.9497 | 13.0253 | 104.4859 | 6604415.4288 | 0 | 4595133.7298 | 0 | 0 | 0 | 1755093.2781 | 5052310.5503 | 13145075.6806 | 8971784.2563 | 40123812.9239 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 57874732.2 | 95033632.5813 | 56234.1325 | 14.8171 | 3905.9491 | 6413.7926 | 79.6281 | 130.7538
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2586 | 28.6175 | 3.8335 | 4 | 3800.5914 | 6223.8787 | 77.4802 | 126.8822 | 119.5797 | 12.9135 | 101.8457 | 6707607.1268 | 0 | 4695546.4776 | 0 | 0 | 0 | 1681884.6387 | 5103164.9148 | 13277388.3053 | 9062090.3414 | 40527681.8047 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 58278601.0808 | 95437501.4621 | 74989.4209 | 15.3341 | 3800.5914 | 6223.8787 | 77.4802 | 126.8822
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.1038 | 29.2445 | 3.9343 | 4 | 3721.3274 | 6082.549 | 75.8643 | 124.001 | 119.2831 | 12.8248 | 111.9263 | 6785207.2876 | 0 | 4772691.952 | 0 | 0 | 0 | 1618991.9005 | 5138987.5446 | 13370591.4399 | 9125703.3959 | 40812173.5205 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 58563092.7966 | 95721993.1779 | 100000 | 15.7372 | 3721.3274 | 6082.549 | 75.8643 | 124.001
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2887 | 29.7268 | 4.0121 | 4 | 3661.7174 | 5977.1211 | 74.6491 | 121.8517 | 119.0487 | 12.7554 | 105.3582 | 6843571.3217 | 0 | 4831721.2229 | 0 | 0 | 0 | 1566884.4444 | 5164449.0257 | 13436836.9907 | 9170917.3455 | 41014380.3509 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 58765299.627 | 95924200.0083 | 133352.1432 | 16.0486 | 3661.7174 | 5977.1211 | 74.6491 | 121.8517
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9406 | 30.0923 | 4.0716 | 4 | 3616.9056 | 5898.4978 | 73.7355 | 120.2489 | 118.8676 | 12.7021 | 113.631 | 6886985.8546 | 0 | 4876233.1105 | 0 | 0 | 0 | 1524493.9234 | 5182208.0265 | 13483042.268 | 9202453.3967 | 41155416.5797 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 58906335.8558 | 96065236.2371 | 177827.941 | 16.2864 | 3616.9056 | 5898.4978 | 73.7355 | 120.2489
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1929 | 30.3697 | 4.1169 | 4 | 3583.2315 | 5839.7253 | 73.049 | 119.0507 | 118.728 | 12.6612 | 99.5481 | 6919485.3785 | 0 | 4909908.0378 | 0 | 0 | 0 | 1490822.5801 | 5194884.2386 | 13516023.1716 | 9224963.5411 | 41256086.9478 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59007006.2239 | 96165906.6052 | 237137.3706 | 16.4675 | 3583.2315 | 5839.7253 | 73.049 | 119.0507
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1332 | 30.5784 | 4.1511 | 4 | 3557.9362 | 5795.8051 | 72.5333 | 118.1553 | 118.622 | 12.6303 | 109.301 | 6943654.6302 | 0 | 4935157.0985 | 0 | 0 | 0 | 1464350.9119 | 5203833.4298 | 13539307.1314 | 9240855.3221 | 41327158.524 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59078077.8001 | 96236978.1814 | 316227.766 | 16.6046 | 3557.9362 | 5795.8051 | 72.5333 | 118.1553
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8519 | 30.7378 | 4.1772 | 4 | 3538.9411 | 5762.8503 | 72.1461 | 117.4835 | 118.5402 | 12.6064 | 95.4748 | 6961991.4592 | 0 | 4954431.8708 | 0 | 0 | 0 | 1443998.3895 | 5210564.4706 | 13556819.9187 | 9252808.1593 | 41380614.2681 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59131533.5441 | 96290433.9255 | 421696.5034 | 16.7088 | 3538.9411 | 5762.8503 | 72.1461 | 117.4835
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3855 | 30.8563 | 4.1968 | 4 | 3524.6812 | 5738.23 | 71.8554 | 116.9816 | 118.4791 | 12.5887 | 94.9486 | 6975529.2123 | 0 | 4968731.4857 | 0 | 0 | 0 | 1428229.7243 | 5215271.2647 | 13569066.0315 | 9261166.3829 | 41417994.1015 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59168913.3776 | 96327813.7589 | 562341.3252 | 16.787 | 3524.6812 | 5738.23 | 71.8554 | 116.9816
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.7922 | 30.9466 | 4.2116 | 4 | 3513.9786 | 5719.7426 | 71.6372 | 116.6047 | 118.4323 | 12.5751 | 104.906 | 6985805.1386 | 0 | 4979624.1941 | 0 | 0 | 0 | 1416270.9827 | 5218863.123 | 13578411.31 | 9267544.7275 | 41446519.476 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59197438.7521 | 96356339.1334 | 749894.2093 | 16.8463 | 3513.9786 | 5719.7426 | 71.6372 | 116.6047
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.0887 | 31.0127 | 4.2226 | 4 | 3505.9474 | 5705.9614 | 71.4735 | 116.3237 | 118.398 | 12.5652 | 112.0685 | 6993269.3592 | 0 | 4987559.5873 | 0 | 0 | 0 | 1407027.9458 | 5221264.188 | 13584658.3886 | 9271808.487 | 41465587.9559 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59216507.232 | 96375407.6133 | 1000000 | 16.8903 | 3505.9474 | 5705.9614 | 71.4735 | 116.3237
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.323 | 31.0646 | 4.231 | 4 | 3499.9217 | 5695.5415 | 71.3506 | 116.1113 | 118.3708 | 12.5573 | 113.6292 | 6999156.4554 | 0 | 4993829.241 | 0 | 0 | 0 | 1400210.7351 | 5223346.6083 | 13590076.4192 | 9275506.4042 | 41482125.8634 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59233045.1395 | 96391945.5208 | 1333521.4322 | 16.9241 | 3499.9217 | 5695.5415 | 71.3506 | 116.1113
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.4862 | 31.1011 | 4.2372 | 4 | 3495.4014 | 5687.8301 | 71.2585 | 115.9541 | 118.3519 | 12.5518 | 109.7025 | 7003246.8072 | 0 | 4998194.2973 | 0 | 0 | 0 | 1394853.9711 | 5224555.0795 | 13593220.6132 | 9277652.3813 | 41491723.1496 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59242642.4257 | 96401542.807 | 1778279.41 | 16.9487 | 3495.4014 | 5687.8301 | 71.2585 | 115.9541
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.6151 | 31.1297 | 4.2419 | 4 | 3492.0105 | 5681.9989 | 71.1894 | 115.8352 | 118.3369 | 12.5475 | 112.5161 | 7006474.9348 | 0 | 5001642.0179 | 0 | 0 | 0 | 1390916.2594 | 5225622.9527 | 13595999.0003 | 9279548.6876 | 41500203.8528 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59251123.1289 | 96410023.5102 | 2371373.7057 | 16.9676 | 3492.0105 | 5681.9989 | 71.1894 | 115.8352
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.7077 | 31.1504 | 4.2454 | 4 | 3489.4672 | 5677.6591 | 71.1375 | 115.7468 | 118.3261 | 12.5444 | 111.3729 | 7008791.1232 | 0 | 5004118.6315 | 0 | 0 | 0 | 1387884.8143 | 5226309.8819 | 13597786.2492 | 9280768.5216 | 41505659.2218 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59256578.4979 | 96415478.8792 | 3162277.6602 | 16.9816 | 3489.4672 | 5677.6591 | 71.1375 | 115.7468
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.7855 | 31.1676 | 4.2481 | 4 | 3487.5597 | 5674.3409 | 71.0986 | 115.6791 | 118.317 | 12.5417 | 118.6482 | 7010736.5956 | 0 | 5006198.7501 | 0 | 0 | 0 | 1385735.8522 | 5227041.7672 | 13599690.4646 | 9282068.1878 | 41511471.6175 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59262390.8936 | 96421291.2749 | 4216965.0343 | 16.9925 | 3487.5597 | 5674.3409 | 71.0986 | 115.6791
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8346 | 31.1786 | 4.25 | 4 | 3486.129 | 5671.9246 | 71.0695 | 115.6299 | 118.3113 | 12.5401 | 113.2807 | 7011961.9791 | 0 | 5007511.0947 | 0 | 0 | 0 | 1383973.2223 | 5227344.0555 | 13600476.9566 | 9282604.9848 | 41513872.2929 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59264791.569 | 96423691.9504 | 5623413.2519 | 17.0002 | 3486.129 | 5671.9246 | 71.0695 | 115.6299
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8781 | 31.1883 | 4.2516 | 4 | 3485.0561 | 5670.061 | 71.0476 | 115.5919 | 118.3062 | 12.5386 | 117.5137 | 7013049.3795 | 0 | 5008674.8001 | 0 | 0 | 0 | 1382755.2648 | 5227746.9833 | 13601525.2923 | 9283320.4954 | 41517072.2154 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59267991.4915 | 96426891.8728 | 7498942.0933 | 17.0063 | 3485.0561 | 5670.061 | 71.0476 | 115.5919
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.9124 | 31.1958 | 4.2528 | 4 | 3484.2515 | 5668.6511 | 71.0312 | 115.5631 | 118.3022 | 12.5375 | 108.0437 | 7013905.3576 | 0 | 5009590.861 | 0 | 0 | 0 | 1381866.1389 | 5228091.3194 | 13602421.1842 | 9283931.96 | 41519806.8212 | 961560.8286 | 16789358.4475 | 16789358.4475 | 13352332.4781 | 7017209.4558 | 0 | 59270726.0973 | 96429626.4787 | 10000000 | 17.011 | 3484.2515 | 5668.6511 | 71.0312 | 115.5631
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.08775 | 0.0065113 | 4 | 762774.1416 | 2228847.3141 | 15550.1826 | 45438.0672 | 83.3936 | 13.3895 | 181.1221 | 214835.9254 | 0 | 106461.6303 | 0 | 0 | 0 | 195864.0048 | 201693.0086 | 524763.8354 | 358162.1004 | 1601780.5048 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 19866520.9192 | 58050528.1672 | 100 | 0.026045 | 762774.1416 | 2228847.3141 | 15550.1826 | 45438.0672
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.18927 | 0.01499 | 4 | 341515.4134 | 978340.1332 | 6962.2536 | 19944.7869 | 92.5021 | 13.9233 | 268.8289 | 301137.4295 | 0 | 158350.889 | 0 | 0 | 0 | 254861.3843 | 278596.3841 | 724850.6435 | 494725.4584 | 2212522.1888 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 20477262.6033 | 58661269.8512 | 133.3521 | 0.05996 | 341515.4134 | 978340.1332 | 6962.2536 | 19944.7869
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2151 | 0.33451 | 0.027879 | 4 | 190055.9538 | 532467.1672 | 3874.5477 | 10855.0634 | 99.9742 | 14.3077 | 53.3734 | 403566.4355 | 0 | 221066.3752 | 0 | 0 | 0 | 321160.2021 | 368859.275 | 959696.1701 | 655012.3559 | 2929360.8139 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 21194101.2283 | 59378108.4762 | 177.8279 | 0.11152 | 190055.9538 | 532467.1672 | 3874.5477 | 10855.0634
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3406 | 0.53762 | 0.04655 | 4 | 118399.233 | 323467.3087 | 2413.7285 | 6594.3186 | 106.1903 | 14.5946 | 60.2855 | 527289.8407 | 0 | 294560.9862 | 0 | 0 | 0 | 399033.4462 | 476144.8665 | 1238831.272 | 845527.7985 | 3781388.2102 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 22046128.6246 | 60230135.8725 | 237.1374 | 0.1862 | 118399.233 | 323467.3087 | 2413.7285 | 6594.3186
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7554 | 0.80624 | 0.072852 | 4 | 78881.0785 | 209913.9601 | 1608.0975 | 4279.38 | 111.1293 | 14.8032 | 72.9576 | 670847.7159 | 0 | 369142.3354 | 0 | 0 | 0 | 484529.3612 | 594562.5709 | 1546929.8479 | 1055811.4074 | 4721823.2387 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 22986563.6532 | 61170570.9011 | 316.2278 | 0.29141 | 78881.0785 | 209913.9601 | 1608.0975 | 4279.38
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5265 | 1.1537 | 0.10856 | 4 | 55414.9172 | 143351.8833 | 1129.708 | 2922.422 | 115.0376 | 14.9564 | 73.4534 | 836636.5527 | 0 | 457515.382 | 0 | 0 | 0 | 577679.3437 | 730014.1986 | 1899347.1982 | 1296343.4904 | 5797536.1656 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 24062276.58 | 62246283.828 | 421.6965 | 0.43422 | 55414.9172 | 143351.8833 | 1129.708 | 2922.422
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7728 | 1.603 | 0.15632 | 4 | 40488.8509 | 101557.1041 | 825.42 | 2070.3789 | 118.1642 | 15.0708 | 61.2935 | 1030743.9504 | 0 | 563829.1814 | 0 | 0 | 0 | 682163.5746 | 887927.3155 | 2310204.736 | 1576762.2022 | 7051630.9601 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 25316371.3745 | 63500378.6224 | 562.3413 | 0.62527 | 40488.8509 | 101557.1041 | 825.42 | 2070.3789
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6427 | 2.1837 | 0.21968 | 4 | 30493.6665 | 73948.1502 | 621.6546 | 1507.5331 | 120.6664 | 15.1555 | 62.1914 | 1259905.6703 | 0 | 692795.9721 | 0 | 0 | 0 | 801490.6805 | 1074135.0059 | 2794678.95 | 1907425.8083 | 8530432.0871 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 26795172.5016 | 64979179.7495 | 749.8942 | 0.87871 | 30493.6665 | 73948.1502 | 621.6546 | 1507.5331
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2501 | 2.9208 | 0.30278 | 4 | 23537.5262 | 55065.2876 | 479.8443 | 1122.5804 | 122.6254 | 15.2144 | 73.1451 | 1526473.9747 | 0 | 846872.1397 | 0 | 0 | 0 | 933488.8838 | 1289665.6493 | 3355445.4726 | 2290160.4826 | 10242106.6027 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 28506847.0171 | 66690854.2651 | 1000 | 1.2111 | 23537.5262 | 55065.2876 | 479.8443 | 1122.5804
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8056 | 3.8574 | 0.41112 | 4 | 18550.0173 | 41769.4347 | 378.1672 | 851.5264 | 124.1558 | 15.2502 | 55.3909 | 1838458.7055 | 0 | 1031991.6725 | 0 | 0 | 0 | 1081600.4895 | 1541299.8383 | 4010146.0153 | 2737007.0557 | 12240503.7769 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 30505244.1913 | 68689251.4393 | 1333.5214 | 1.6445 | 18550.0173 | 41769.4347 | 378.1672 | 851.5264
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4935 | 5.0335 | 0.55084 | 4 | 14891.4612 | 32221.2511 | 303.5826 | 656.8738 | 125.3239 | 15.2639 | 60.1274 | 2199965.5399 | 0 | 1252114.616 | 0 | 0 | 0 | 1244570.1495 | 1831693.6191 | 4765691.0649 | 3252682.077 | 14546717.0664 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 32811457.4809 | 70995464.7288 | 1778.2794 | 2.2034 | 14891.4612 | 32221.2511 | 303.5826 | 656.8738
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4922 | 6.4887 | 0.72858 | 4 | 12157.9604 | 25260.151 | 247.8565 | 514.9623 | 126.1811 | 15.2522 | 68.3398 | 2613256.0577 | 0 | 1510385.3608 | 0 | 0 | 0 | 1419164.543 | 2161694.325 | 5624285.2091 | 3838690.2227 | 17167475.7183 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 35432216.1328 | 73616223.3807 | 2371.3737 | 2.9143 | 12157.9604 | 25260.151 | 247.8565 | 514.9623
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.9575 | 8.2588 | 0.95067 | 4 | 10087.2067 | 20128.5067 | 205.6414 | 410.3468 | 126.7652 | 15.2102 | 77.5749 | 3078205.9729 | 0 | 1808756.8581 | 0 | 0 | 0 | 1600667.3151 | 2530175.757 | 6582998.3092 | 4493031.6131 | 20093835.8254 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 38358576.2398 | 76542583.4878 | 3162.2777 | 3.8027 | 10087.2067 | 20128.5067 | 205.6414 | 410.3468
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9381 | 10.3585 | 1.2212 | 4 | 8503.6259 | 16320.5952 | 173.3579 | 332.7174 | 127.0944 | 15.1308 | 75.2961 | 3588374.3519 | 0 | 2145462.8427 | 0 | 0 | 0 | 1780374.3032 | 2930542.4841 | 7624670.4068 | 5203994.2239 | 23273418.6126 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 41538159.0271 | 79722166.275 | 4216.965 | 4.8848 | 8503.6259 | 16320.5952 | 173.3579 | 332.7174
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.2 | 12.7448 | 1.5379 | 4 | 7287.0086 | 13494.1887 | 148.5555 | 275.0973 | 127.1704 | 15.0076 | 75.3154 | 4124252.7019 | 0 | 2510186.4755 | 0 | 0 | 0 | 1941521.5932 | 3344624.7006 | 8702027.394 | 5939312.5052 | 26561925.3703 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 44826665.7848 | 83010673.0327 | 5623.4133 | 6.1516 | 7287.0086 | 13494.1887 | 148.5555 | 275.0973
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2554 | 15.3191 | 1.8903 | 4 | 6352.4171 | 11402.2907 | 129.5026 | 232.4511 | 126.9981 | 14.8388 | 91.5965 | 4658279.0375 | 0 | 2886440.0601 | 0 | 0 | 0 | 2066470.6362 | 3748363.9962 | 9752474.223 | 6656264.0505 | 29768292.0035 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 48033032.418 | 86217039.6659 | 7498.9421 | 7.5614 | 6352.4171 | 11402.2907 | 129.5026 | 232.4511
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.446 | 17.9423 | 2.2605 | 4 | 5636.9121 | 9859.9634 | 114.9161 | 201.0087 | 126.6038 | 14.6302 | 90.7346 | 5161205.4717 | 0 | 3254799.8069 | 0 | 0 | 0 | 2142743.1337 | 4117911.8808 | 10713962.0139 | 7312499.2244 | 32703121.5314 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 50967861.9458 | 89151869.1938 | 10000 | 9.0418 | 5636.9121 | 9859.9634 | 114.9161 | 201.0087
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.0091 | 20.4499 | 2.6252 | 4 | 5091.7072 | 8728.0091 | 103.8013 | 177.9323 | 126.0477 | 14.3977 | 98.6549 | 5606245.3696 | 0 | 3594781.737 | 0 | 0 | 0 | 2164576.8449 | 4432585.5411 | 11532678.3296 | 7871289.9328 | 35202157.7549 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 53466898.1693 | 91650905.4173 | 13335.2143 | 10.5008 | 5091.7072 | 8728.0091 | 103.8013 | 177.9323
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.4159 | 22.7231 | 2.9647 | 4 | 4678.1172 | 7897.979 | 95.3697 | 161.011 | 125.4061 | 14.1597 | 111.1408 | 5981243.3033 | 0 | 3894005.5536 | 0 | 0 | 0 | 2139448.8598 | 4685732.1095 | 12191313.7732 | 8320822.1566 | 37212565.756 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 55477306.1705 | 93661313.4184 | 17782.7941 | 11.8589 | 4678.1172 | 7897.979 | 95.3697 | 161.011
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.3318 | 24.6841 | 3.2648 | 4 | 4365.4438 | 7289.3396 | 88.9955 | 148.603 | 124.7538 | 13.9342 | 96.5284 | 6283649.2533 | 0 | 4145849.1972 | 0 | 0 | 0 | 2079927.4798 | 4878676.1128 | 12693314.4915 | 8663447.962 | 38744864.4965 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 57009604.911 | 95193612.1589 | 23713.7371 | 13.0593 | 4365.4438 | 7289.3396 | 88.9955 | 148.603
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7371 | 26.322 | 3.52 | 4 | 4129.5964 | 6841.5134 | 84.1874 | 139.4735 | 124.1412 | 13.7317 | 105.1333 | 6521639.5249 | 0 | 4352141.8066 | 0 | 0 | 0 | 2002241.3336 | 5021648.8394 | 13065300.1983 | 8917335.8504 | 39880307.5532 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 58145047.9676 | 96329055.2155 | 31622.7766 | 14.0801 | 4129.5964 | 6841.5134 | 84.1874 | 139.4735
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.6808 | 27.6437 | 3.7296 | 4 | 3951.9335 | 6511.4758 | 80.5655 | 132.7452 | 123.6031 | 13.5592 | 117.6042 | 6703967.2075 | 0 | 4515962.3289 | 0 | 0 | 0 | 1917958.4348 | 5123776.3088 | 13331014.9244 | 9098691.6108 | 40691370.8151 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 58956111.2296 | 97140118.4775 | 42169.6503 | 14.9183 | 3951.9335 | 6511.4758 | 80.5655 | 132.7452
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3561 | 28.6881 | 3.8975 | 4 | 3818.2 | 6267.4385 | 77.8392 | 127.7702 | 123.1504 | 13.4172 | 106.8506 | 6841898.7713 | 0 | 4643782.9667 | 0 | 0 | 0 | 1836311.2212 | 5195577.2541 | 13517826.2556 | 9226194.183 | 41261590.6519 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 59526331.0663 | 97710338.3143 | 56234.1325 | 15.5902 | 3818.2 | 6267.4385 | 77.8392 | 127.7702
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0024 | 29.5052 | 4.0301 | 4 | 3717.5804 | 6086.2476 | 75.7879 | 124.0764 | 122.7794 | 13.3025 | 121.1393 | 6946089.5086 | 0 | 4742863.319 | 0 | 0 | 0 | 1763083.6605 | 5246294.2303 | 13649781.4244 | 9316256.2971 | 41664368.4399 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 59929108.8544 | 98113116.1023 | 74989.4209 | 16.1205 | 3717.5804 | 6086.2476 | 75.7879 | 124.0764
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8017 | 30.1344 | 4.1331 | 4 | 3641.903 | 5951.5237 | 74.2451 | 121.3299 | 122.4836 | 13.2122 | 110.6061 | 7024047.4564 | 0 | 4818580.6017 | 0 | 0 | 0 | 1700125.2709 | 5281673.7983 | 13741831.8029 | 9379082.5719 | 41945341.5021 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60210081.9166 | 98394089.1645 | 100000 | 16.5326 | 3641.903 | 5951.5237 | 74.2451 | 121.3299
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9406 | 30.6163 | 4.2125 | 4 | 3585.0052 | 5851.1007 | 73.0852 | 119.2826 | 122.2512 | 13.1419 | 113.1895 | 7082412.3498 | 0 | 4876233.1105 | 0 | 0 | 0 | 1647947.9692 | 5306571.4375 | 13806610.353 | 9423295.2634 | 42143070.4835 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60407810.898 | 98591818.1459 | 133352.1432 | 16.8501 | 3585.0052 | 5851.1007 | 73.0852 | 119.2826
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.5756 | 30.985 | 4.2734 | 4 | 3542.2422 | 5776.0556 | 72.2134 | 117.7527 | 122.0698 | 13.0873 | 108.3033 | 7126320.6699 | 0 | 4920186.5834 | 0 | 0 | 0 | 1605937.1337 | 5324453.3109 | 13853135.3194 | 9455049.509 | 42285082.5263 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60549822.9408 | 98733830.1887 | 177827.941 | 17.0936 | 3542.2422 | 5776.0556 | 72.2134 | 117.7527
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.7982 | 31.2615 | 4.3195 | 4 | 3510.1142 | 5720.0913 | 71.5584 | 116.6118 | 121.9319 | 13.046 | 101.3458 | 7158751.9762 | 0 | 4952991.8837 | 0 | 0 | 0 | 1572329.7771 | 5336788.7184 | 13885229.5195 | 9476954.46 | 42383046.335 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60647786.7494 | 98831793.9974 | 237137.3706 | 17.278 | 3510.1142 | 5720.0913 | 71.5584 | 116.6118
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.7339 | 31.473 | 4.3546 | 4 | 3485.9842 | 5678.1289 | 71.0665 | 115.7563 | 121.8252 | 13.0142 | 99.5126 | 7183341.0259 | 0 | 4978062.0477 | 0 | 0 | 0 | 1546254.6092 | 5345986.4963 | 13909160.2508 | 9493287.6758 | 42456092.1057 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60720832.5202 | 98904839.7681 | 316227.766 | 17.4186 | 3485.9842 | 5678.1289 | 71.0665 | 115.7563
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.4371 | 31.6321 | 4.3812 | 4 | 3467.8668 | 5646.7361 | 70.6972 | 115.1164 | 121.7443 | 12.9901 | 116.2284 | 7201685.4971 | 0 | 4996881.3414 | 0 | 0 | 0 | 1526026.8154 | 5352591.525 | 13926345.1806 | 9505016.7435 | 42508547.1031 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60773287.5175 | 98957294.7655 | 421696.5034 | 17.5247 | 3467.8668 | 5646.7361 | 70.6972 | 115.1164
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.9512 | 31.7489 | 4.401 | 4 | 3454.2672 | 5623.3432 | 70.4199 | 114.6395 | 121.6847 | 12.9724 | 114.3542 | 7215023.562 | 0 | 5010630.6632 | 0 | 0 | 0 | 1510235.3481 | 5356996.9336 | 13937807.15 | 9512839.7732 | 42543533.43 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60808273.8445 | 98992281.0924 | 562341.3252 | 17.6038 | 3454.2672 | 5623.3432 | 70.4199 | 114.6395
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.3534 | 31.8399 | 4.4161 | 4 | 3444.0611 | 5605.6998 | 70.2118 | 114.2798 | 121.6379 | 12.9585 | 111.3147 | 7225414.2967 | 0 | 5021376.8435 | 0 | 0 | 0 | 1498439.2049 | 5360639.8346 | 13947285.2311 | 9519308.7583 | 42572464.1689 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60837204.5834 | 99021211.8313 | 749894.2093 | 17.6644 | 3444.0611 | 5605.6998 | 70.2118 | 114.2798
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.648 | 31.9068 | 4.4274 | 4 | 3436.403 | 5592.536 | 70.0557 | 114.0114 | 121.6034 | 12.9483 | 121.0236 | 7233003.8092 | 0 | 5029248.3831 | 0 | 0 | 0 | 1489347.4468 | 5363123.8592 | 13953748.1538 | 9523719.8358 | 42592191.4879 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60856931.9024 | 99040939.1503 | 1000000 | 17.7095 | 3436.403 | 5592.536 | 70.0557 | 114.0114
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8797 | 31.9591 | 4.436 | 4 | 3430.6576 | 5582.5914 | 69.9386 | 113.8087 | 121.5763 | 12.9403 | 125.8074 | 7238958.8591 | 0 | 5035435.5456 | 0 | 0 | 0 | 1482631.1992 | 5365239.9855 | 13959253.8802 | 9527477.6072 | 42608997.0768 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60873737.4913 | 99057744.7392 | 1333521.4322 | 17.744 | 3430.6576 | 5582.5914 | 69.9386 | 113.8087
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0501 | 31.9977 | 4.4424 | 4 | 3426.3476 | 5575.1641 | 69.8507 | 113.6573 | 121.5563 | 12.9344 | 118.4539 | 7243329.8541 | 0 | 5039984.6175 | 0 | 0 | 0 | 1477496.5955 | 5366716.3162 | 13963094.9898 | 9530099.2435 | 42620721.6165 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60885462.031 | 99069469.2789 | 1778279.41 | 17.7698 | 3426.3476 | 5575.1641 | 69.8507 | 113.6573
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.1692 | 32.0249 | 4.4471 | 4 | 3423.1147 | 5569.6621 | 69.7848 | 113.5451 | 121.5423 | 12.9302 | 107.4291 | 7246379.8162 | 0 | 5043163.9407 | 0 | 0 | 0 | 1473480.1557 | 5367579.3259 | 13965340.3641 | 9531631.7575 | 42627575.3601 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60892315.7746 | 99076323.0225 | 2371373.7057 | 17.7886 | 3423.1147 | 5569.6621 | 69.7848 | 113.5451
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2546 | 32.0445 | 4.4506 | 4 | 3420.6899 | 5565.567 | 69.7354 | 113.4616 | 121.5322 | 12.9272 | 106.842 | 7248563.1417 | 0 | 5045442.4408 | 0 | 0 | 0 | 1470390.5019 | 5368114.4729 | 13966732.7068 | 9532582.06 | 42631825.324 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60896565.7385 | 99080572.9864 | 3162277.6602 | 17.8024 | 3420.6899 | 5565.567 | 69.7354 | 113.4616
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3324 | 32.062 | 4.4534 | 4 | 3418.8713 | 5562.3937 | 69.6983 | 113.3969 | 121.523 | 12.9245 | 115.9829 | 7250553.564 | 0 | 5047518.2881 | 0 | 0 | 0 | 1468290.7722 | 5368881.4235 | 13968728.1549 | 9533943.9944 | 42637916.197 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60902656.6115 | 99086663.8594 | 4216965.0343 | 17.8137 | 3418.8713 | 5562.3937 | 69.6983 | 113.3969
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3861 | 32.0742 | 4.4555 | 4 | 3417.5074 | 5560.0491 | 69.6705 | 113.3491 | 121.5167 | 12.9227 | 110.3148 | 7251926.3625 | 0 | 5048951.4867 | 0 | 0 | 0 | 1466636.3628 | 5369330.5427 | 13969896.671 | 9534741.5306 | 42641482.9564 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60906223.3709 | 99090230.6188 | 5623413.2519 | 17.8218 | 3417.5074 | 5560.0491 | 69.6705 | 113.3491
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.425 | 32.083 | 4.457 | 4 | 3416.4845 | 5558.3015 | 69.6497 | 113.3135 | 121.5121 | 12.9213 | 114.9544 | 7252919.8023 | 0 | 5049989.2567 | 0 | 0 | 0 | 1465370.7492 | 5369629.1252 | 13970673.5214 | 9535271.747 | 42643854.2018 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60908594.6163 | 99092601.8642 | 7498942.0933 | 17.8279 | 3416.4845 | 5558.3015 | 69.6497 | 113.3135
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.4593 | 32.0907 | 4.4582 | 4 | 3415.7174 | 5556.9531 | 69.634 | 113.286 | 121.5081 | 12.9201 | 105.1554 | 7253795.5637 | 0 | 5050903.4385 | 0 | 0 | 0 | 1464503.2774 | 5369988.889 | 13971609.5531 | 9535910.6079 | 42646711.3296 | 961560.8286 | 17303179.5858 | 17303179.5858 | 13685062.912 | 7195764.7501 | 0 | 60911451.7441 | 99095458.992 | 10000000 | 17.8327 | 3415.7174 | 5556.9531 | 69.634 | 113.286
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.092343 | 0.006978 | 4 | 733224.7543 | 2138448.6348 | 14947.7784 | 43595.1679 | 85.279 | 13.8347 | 192.2868 | 225709.2944 | 0 | 110885.8443 | 0 | 0 | 0 | 206302.5777 | 211730.1094 | 550878.3128 | 375985.7679 | 1681491.9065 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 20465913.5502 | 59688798.8782 | 100 | 0.027912 | 733224.7543 | 2138448.6348 | 14947.7784 | 43595.1679
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.20071 | 0.016109 | 4 | 327805.4311 | 936512.4999 | 6682.7571 | 19092.074 | 94.8533 | 14.3892 | 276.0714 | 318330.6123 | 0 | 165983.1724 | 0 | 0 | 0 | 270605.5247 | 294418.5307 | 766016.6233 | 522822.0854 | 2338176.5488 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 21122598.1925 | 60345483.5205 | 133.3521 | 0.064436 | 327805.4311 | 936512.4999 | 6682.7571 | 19092.074
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.35155 | 0.029959 | 4 | 182403.1044 | 509708.0346 | 3718.534 | 10391.0877 | 102.4119 | 14.7732 | 51.5011 | 424127.1705 | 0 | 230058.3275 | 0 | 0 | 0 | 338313.47 | 387074.5976 | 1007088.7029 | 687358.7333 | 3074021.0019 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 21858442.6456 | 61081327.9736 | 177.8279 | 0.11984 | 182403.1044 | 509708.0346 | 3718.534 | 10391.0877
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5038 | 0.56689 | 0.050151 | 4 | 113415.0944 | 308940.8531 | 2312.1201 | 6298.1772 | 108.8871 | 15.0686 | 68.5327 | 555519.1083 | 0 | 303386.5081 | 0 | 0 | 0 | 421870.6263 | 499502.7346 | 1299603.6534 | 887006.1977 | 3966888.8284 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 22751310.4721 | 61974195.8001 | 237.1374 | 0.2006 | 113415.0944 | 308940.8531 | 2312.1201 | 6298.1772
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9601 | 0.84837 | 0.078441 | 4 | 75624.718 | 200632.2317 | 1541.7122 | 4090.1594 | 113.9483 | 15.2797 | 69.0694 | 705618.2488 | 0 | 379607.1506 | 0 | 0 | 0 | 510998.1744 | 622527.1938 | 1619688.0603 | 1105470.3824 | 4943909.2104 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 23728330.8541 | 62951216.1821 | 316.2278 | 0.31376 | 75624.718 | 200632.2317 | 1541.7122 | 4090.1594
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7823 | 1.2123 | 0.11678 | 4 | 53189.181 | 137157.6798 | 1084.3334 | 2796.1448 | 117.9616 | 15.4352 | 78.6093 | 878901.8151 | 0 | 469912.2475 | 0 | 0 | 0 | 608082.4132 | 763189.6256 | 1985662.854 | 1355255.6991 | 6061004.6545 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 24845426.2982 | 64068311.6262 | 421.6965 | 0.46711 | 53189.181 | 137157.6798 | 1084.3334 | 2796.1448
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1017 | 1.6843 | 0.16806 | 4 | 38905.0747 | 97250.5039 | 793.1326 | 1982.5831 | 121.1879 | 15.5517 | 61.1614 | 1082571.0619 | 0 | 578961.0595 | 0 | 0 | 0 | 717875.4127 | 927968.9383 | 2414384.8248 | 1647867.2536 | 7369628.5508 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 26154050.1944 | 65376935.5225 | 562.3413 | 0.67225 | 38905.0747 | 97250.5039 | 793.1326 | 1982.5831
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0519 | 2.2919 | 0.236 | 4 | 29331.2386 | 70881.1115 | 597.957 | 1445.0073 | 123.7613 | 15.6374 | 44.6967 | 1322009.7255 | 0 | 710675.6368 | 0 | 0 | 0 | 842161.6188 | 1121190.3226 | 2917107.2318 | 1990985.6262 | 8904130.1618 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 27688551.8055 | 66911437.1335 | 749.8942 | 0.944 | 29331.2386 | 70881.1115 | 597.957 | 1445.0073
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7908 | 3.0688 | 0.32524 | 4 | 22662.9114 | 52812.0556 | 462.0141 | 1076.6452 | 125.7928 | 15.6972 | 59.134 | 1602848.6189 | 0 | 869339.562 | 0 | 0 | 0 | 982214.3854 | 1347217.0008 | 3505182.284 | 2392358.9331 | 10699160.7842 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 29483582.4279 | 68706467.7559 | 1000 | 1.301 | 22662.9114 | 52812.0556 | 462.0141 | 1076.6452
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.4855 | 4.0512 | 0.44135 | 4 | 17878.9892 | 40096.3581 | 364.4874 | 817.4185 | 127.3702 | 15.7332 | 48.355 | 1929675.6256 | 0 | 1058885.316 | 0 | 0 | 0 | 1137488.4274 | 1609159.2539 | 4186702.2948 | 2857510.3443 | 12779421.2622 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 31563842.9059 | 70786728.2339 | 1333.5214 | 1.7654 | 17878.9892 | 40096.3581 | 364.4874 | 817.4185
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3218 | 5.2801 | 0.59082 | 4 | 14366.2334 | 30963.1669 | 292.8751 | 631.226 | 128.5691 | 15.7446 | 68.8415 | 2306786.1363 | 0 | 1283334.526 | 0 | 0 | 0 | 1306713.4341 | 1909765.2976 | 4968817.5577 | 3391320.0821 | 15166737.0339 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 33951158.6776 | 73174044.0056 | 1778.2794 | 2.3633 | 14366.2334 | 30963.1669 | 292.8751 | 631.226
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.525 | 6.8046 | 0.78095 | 4 | 11740.8468 | 24297.0651 | 239.353 | 495.3285 | 129.4525 | 15.73 | 64.1745 | 2739329.7177 | 0 | 1547531.7226 | 0 | 0 | 0 | 1489682.2619 | 2252852.0439 | 5861458.8947 | 4000566.1366 | 17891420.7775 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 36675842.4211 | 75898727.7492 | 2371.3737 | 3.1238 | 11740.8468 | 24297.0651 | 239.353 | 495.3285
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.2144 | 8.6546 | 1.018 | 4 | 9751.2827 | 19383.3679 | 198.7931 | 395.1562 | 130.0518 | 15.6831 | 73.3815 | 3224650.8507 | 0 | 1851975.6076 | 0 | 0 | 0 | 1678987.2503 | 2634689.3463 | 6854921.2301 | 4678624.5941 | 20923848.879 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 39708270.5227 | 78931155.8507 | 3162.2777 | 4.0721 | 9751.2827 | 19383.3679 | 198.7931 | 395.1562
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.4145 | 10.8401 | 1.3058 | 4 | 8229.6541 | 15738.9071 | 167.7726 | 320.8589 | 130.3857 | 15.5967 | 59.7087 | 3754874.8959 | 0 | 2194114.9256 | 0 | 0 | 0 | 1864808.968 | 3047381.5279 | 7928661.6318 | 5411474.4814 | 24201316.4306 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 42985738.0743 | 82208623.4023 | 4216.965 | 5.2233 | 8229.6541 | 15738.9071 | 167.7726 | 320.8589
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.905 | 13.3199 | 1.6418 | 4 | 7060.9366 | 13033.5727 | 143.9467 | 265.707 | 130.4568 | 15.4638 | 84.748 | 4310872.5245 | 0 | 2564217.4193 | 0 | 0 | 0 | 2031329.4591 | 3473503.5671 | 9037343.7681 | 6168172.8206 | 27585439.5587 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 46369861.2024 | 85592746.5304 | 5623.4133 | 6.5671 | 7060.9366 | 13033.5727 | 143.9467 | 265.707
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.1339 | 15.9801 | 2.0137 | 4 | 6163.6436 | 11033.2233 | 125.6542 | 224.9272 | 130.2709 | 15.2835 | 73.8964 | 4861674.0047 | 0 | 2943937.4241 | 0 | 0 | 0 | 2158612.7936 | 3886047.4467 | 10110698.3184 | 6900759.3564 | 30861729.344 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 49646150.9876 | 88869036.3157 | 7498.9421 | 8.0547 | 6163.6436 | 11033.2233 | 125.6542 | 224.9272
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.4159 | 18.6732 | 2.4018 | 4 | 5477.1763 | 9559.8532 | 111.6596 | 194.8905 | 129.8596 | 15.063 | 104.013 | 5376885.5895 | 0 | 3313324.6774 | 0 | 0 | 0 | 2234186.2943 | 4260514.6589 | 11084985.1906 | 7565730.1663 | 33835626.577 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 52620048.2206 | 91842933.5487 | 10000 | 9.6071 | 5477.1763 | 9559.8532 | 111.6596 | 194.8905
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.0165 | 21.237 | 2.7823 | 4 | 4954.4647 | 8478.7251 | 101.0035 | 172.8503 | 129.2867 | 14.8191 | 94.8887 | 5830953.0355 | 0 | 3652971.2436 | 0 | 0 | 0 | 2254143.0798 | 4577846.27 | 11910616.9491 | 8129240.8064 | 36355771.3844 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 55140193.0281 | 94363078.3561 | 13335.2143 | 11.1294 | 4954.4647 | 8478.7251 | 101.0035 | 172.8503
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.4038 | 23.5497 | 3.1347 | 4 | 4558.1851 | 7686.259 | 92.9248 | 156.6948 | 128.632 | 14.5713 | 104.968 | 6211726.4387 | 0 | 3950502.6139 | 0 | 0 | 0 | 2226363.8738 | 4831551.2413 | 12570705.2424 | 8579764.6301 | 38370614.0401 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 57155035.6838 | 96377921.0118 | 17782.7941 | 12.539 | 4558.1851 | 7686.259 | 92.9248 | 156.6948
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.2855 | 25.5406 | 3.4452 | 4 | 4258.755 | 7104.9932 | 86.8205 | 144.8449 | 127.9697 | 14.3375 | 99.5728 | 6518309.1732 | 0 | 4200518.2667 | 0 | 0 | 0 | 2164780.2296 | 5024606.9911 | 13072996.7023 | 8922588.8725 | 39903800.2355 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 58688221.8792 | 97911107.2072 | 23713.7371 | 13.7806 | 4258.755 | 7104.9932 | 86.8205 | 144.8449
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.6083 | 27.1921 | 3.7077 | 4 | 4032.9945 | 6677.6944 | 82.218 | 136.1338 | 127.3536 | 14.1296 | 99.8229 | 6757951.0174 | 0 | 4403880.9486 | 0 | 0 | 0 | 2084715.0238 | 5166153.326 | 13441271.2305 | 9173943.8053 | 41027915.3516 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 59812336.9953 | 99035222.3233 | 31622.7766 | 14.8308 | 4032.9945 | 6677.6944 | 82.218 | 136.1338
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.4861 | 28.5247 | 3.9229 | 4 | 3862.9922 | 6362.5978 | 78.7523 | 129.7102 | 126.8133 | 13.9526 | 101.1316 | 6941670.1663 | 0 | 4565425.3166 | 0 | 0 | 0 | 1999135.3304 | 5267430.0172 | 13704772.4063 | 9353788.7722 | 41832222.0091 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 60616643.6528 | 99839528.9808 | 42169.6503 | 15.6916 | 3862.9922 | 6362.5978 | 78.7523 | 129.7102
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.1077 | 29.5772 | 4.0952 | 4 | 3735.0663 | 6129.5355 | 76.1444 | 124.9589 | 126.3596 | 13.8072 | 95.9927 | 7080674.9966 | 0 | 4691444.6559 | 0 | 0 | 0 | 1916870.5513 | 5338706.1795 | 13890218.3599 | 9480359.4461 | 42398274.1895 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 61182695.8332 | 100405581.1612 | 56234.1325 | 16.3806 | 3735.0663 | 6129.5355 | 76.1444 | 124.9589
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.7003 | 30.3981 | 4.2308 | 4 | 3638.8441 | 5956.5542 | 74.1828 | 121.4324 | 125.9891 | 13.6903 | 116.1288 | 7185383.9659 | 0 | 4788823.5179 | 0 | 0 | 0 | 1843250.3971 | 5388808.5736 | 14020574.5118 | 9569330.1983 | 42796171.1647 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 61580592.8084 | 100803478.1364 | 74989.4209 | 16.9231 | 3638.8441 | 5956.5542 | 74.1828 | 121.4324
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4607 | 31.0308 | 4.3361 | 4 | 3566.4931 | 5827.8886 | 72.7078 | 118.8094 | 125.6938 | 13.5981 | 106.3518 | 7263832.039 | 0 | 4863312.7228 | 0 | 0 | 0 | 1780270.0207 | 5423891.7651 | 14111853.7797 | 9631630.1743 | 43074790.5016 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 61859212.1453 | 101082097.4733 | 100000 | 17.3445 | 3566.4931 | 5827.8886 | 72.7078 | 118.8094
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.5607 | 31.5133 | 4.4171 | 4 | 3512.109 | 5732.0451 | 71.5991 | 116.8555 | 125.4629 | 13.5267 | 107.3736 | 7322329.9566 | 0 | 4919788.6666 | 0 | 0 | 0 | 1728060.2135 | 5448369.7463 | 14175540.4656 | 9675097.646 | 43269186.6947 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62053608.3384 | 101276493.6664 | 133352.1432 | 17.6685 | 3512.109 | 5732.0451 | 71.5991 | 116.8555
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.166 | 31.8825 | 4.4792 | 4 | 3471.2436 | 5660.4148 | 70.766 | 115.3952 | 125.2827 | 13.4713 | 108.4405 | 7366356.4024 | 0 | 4962850.9822 | 0 | 0 | 0 | 1686134.6255 | 5465983.3839 | 14221367.5376 | 9706375.5643 | 43409068.496 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62193490.1397 | 101416375.4677 | 177827.941 | 17.9168 | 3471.2436 | 5660.4148 | 70.766 | 115.3952
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3787 | 32.1619 | 4.5264 | 4 | 3440.5467 | 5606.8987 | 70.1402 | 114.3042 | 125.1445 | 13.429 | 111.5417 | 7399215.8246 | 0 | 4995320.5459 | 0 | 0 | 0 | 1652874.1953 | 5478490.1206 | 14253907.5011 | 9728584.758 | 43508392.9455 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62292814.5892 | 101515699.9172 | 237137.3706 | 18.1055 | 3440.5467 | 5606.8987 | 70.1402 | 114.3042
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.2996 | 32.3741 | 4.5622 | 4 | 3417.495 | 5566.8272 | 69.6703 | 113.4873 | 125.0383 | 13.3966 | 119.0424 | 7423938.0271 | 0 | 5019941.6809 | 0 | 0 | 0 | 1626974.0345 | 5487632.9596 | 14277695.2926 | 9744820.4145 | 43581002.4093 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62365424.053 | 101588309.381 | 316227.766 | 18.2489 | 3417.495 | 5566.8272 | 69.6703 | 113.4873
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.977 | 32.5308 | 4.589 | 4 | 3400.1892 | 5536.959 | 69.3175 | 112.8784 | 124.9594 | 13.3726 | 125.0038 | 7441991.0378 | 0 | 5038031.6092 | 0 | 0 | 0 | 1606647.2206 | 5493801.2483 | 14293743.9146 | 9755773.9288 | 43629988.9593 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62414410.603 | 101637295.931 | 421696.5034 | 18.3562 | 3400.1892 | 5536.959 | 69.3175 | 112.8784
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.4982 | 32.6511 | 4.6095 | 4 | 3387.2001 | 5514.5056 | 69.0527 | 112.4207 | 124.8984 | 13.3541 | 109.012 | 7455811.1562 | 0 | 5051941.1082 | 0 | 0 | 0 | 1591247.2183 | 5498609.7982 | 14306254.7751 | 9764312.8481 | 43668176.9041 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62452598.5478 | 101675483.8758 | 562341.3252 | 18.4378 | 3387.2001 | 5514.5056 | 69.0527 | 112.4207
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.8855 | 32.7406 | 4.6248 | 4 | 3377.4528 | 5497.7194 | 68.8539 | 112.0784 | 124.8528 | 13.3403 | 118.6999 | 7466037.5115 | 0 | 5062270.1948 | 0 | 0 | 0 | 1579414.9571 | 5502011.8387 | 14315106.1866 | 9770354.1184 | 43695194.8072 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62479616.4509 | 101702501.7789 | 749894.2093 | 18.499 | 3377.4528 | 5497.7194 | 68.8539 | 112.0784
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.1755 | 32.8077 | 4.6363 | 4 | 3370.1395 | 5485.148 | 68.7049 | 111.8222 | 124.8186 | 13.3299 | 115.9005 | 7473672.7018 | 0 | 5070002.3865 | 0 | 0 | 0 | 1570409.0391 | 5504492.8097 | 14321561.164 | 9774759.7731 | 43714897.8742 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62499319.5179 | 101722204.8459 | 1000000 | 18.545 | 3370.1395 | 5485.148 | 68.7049 | 111.8222
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3996 | 32.8595 | 4.645 | 4 | 3364.653 | 5475.68 | 68.593 | 111.6291 | 124.792 | 13.3219 | 114.501 | 7479559.7394 | 0 | 5075974.9761 | 0 | 0 | 0 | 1563695.4484 | 5506499.7639 | 14326782.8473 | 9778323.6792 | 43730836.4542 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62515258.0979 | 101738143.4259 | 1333521.4322 | 18.58 | 3364.653 | 5475.68 | 68.593 | 111.6291
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.5628 | 32.8973 | 4.6515 | 4 | 3360.5374 | 5468.6201 | 68.5091 | 111.4852 | 124.7727 | 13.316 | 124.2463 | 7483837.4713 | 0 | 5080322.2735 | 0 | 0 | 0 | 1558537.2209 | 5507851.8167 | 14330300.6112 | 9780724.6254 | 43741574.0189 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62525995.6626 | 101748880.9906 | 1778279.41 | 18.606 | 3360.5374 | 5468.6201 | 68.5091 | 111.4852
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.6897 | 32.9265 | 4.6564 | 4 | 3357.4504 | 5463.2954 | 68.4462 | 111.3767 | 124.7576 | 13.3115 | 115.3343 | 7487160.0853 | 0 | 5083701.9484 | 0 | 0 | 0 | 1554721.9999 | 5508977.7731 | 14333230.1189 | 9782724.0746 | 43750516.0002 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62534937.6439 | 101757822.9719 | 2371373.7057 | 18.6257 | 3357.4504 | 5463.2954 | 68.4462 | 111.3767
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.7823 | 32.948 | 4.6601 | 4 | 3355.135 | 5459.3223 | 68.399 | 111.2957 | 124.7466 | 13.3082 | 112.3024 | 7489582.4888 | 0 | 5086168.5097 | 0 | 0 | 0 | 1551805.221 | 5509746.9256 | 14335231.2959 | 9784089.919 | 43756624.36 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62541046.0037 | 101763931.3317 | 3162277.6602 | 18.6404 | 3355.135 | 5459.3223 | 68.399 | 111.2957
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.8601 | 32.9658 | 4.663 | 4 | 3353.3985 | 5456.2831 | 68.3636 | 111.2337 | 124.7373 | 13.3054 | 121.3346 | 7491617.181 | 0 | 5088240.1902 | 0 | 0 | 0 | 1549750.5441 | 5510547.087 | 14337313.1516 | 9785510.8283 | 43762978.9822 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62547400.6259 | 101770285.9539 | 4216965.0343 | 18.6519 | 3353.3985 | 5456.2831 | 68.3636 | 111.2337
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9092 | 32.9772 | 4.665 | 4 | 3352.0962 | 5454.0716 | 68.337 | 111.1886 | 124.7315 | 13.3036 | 112.8214 | 7492898.7834 | 0 | 5089547.2134 | 0 | 0 | 0 | 1548050.3122 | 5510893.5605 | 14338214.6048 | 9786126.0886 | 43765730.5629 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62550152.2066 | 101773037.5346 | 5623413.2519 | 18.66 | 3352.0962 | 5454.0716 | 68.337 | 111.1886
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9332 | 32.9831 | 4.6663 | 4 | 3351.1195 | 5452.5057 | 68.3171 | 111.1567 | 124.7285 | 13.3027 | 116.0088 | 7493524.9122 | 0 | 5090188.3639 | 0 | 0 | 0 | 1546559.8682 | 5510806.5263 | 14337988.1595 | 9785971.535 | 43765039.365 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62549461.0087 | 101772346.3367 | 7498942.0933 | 18.6652 | 3351.1195 | 5452.5057 | 68.3171 | 111.1567
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9649 | 32.9904 | 4.6675 | 4 | 3350.387 | 5451.2329 | 68.3022 | 111.1308 | 124.7248 | 13.3016 | 121.5772 | 7494351.9426 | 0 | 5091031.4578 | 0 | 0 | 0 | 1545668.862 | 5511110.3824 | 14338778.7307 | 9786511.1161 | 43767452.4916 | 961560.8286 | 17822860.8151 | 17822860.8151 | 14023360.4323 | 7376664.0807 | 0 | 62551874.1353 | 101774759.4633 | 10000000 | 18.67 | 3350.387 | 5451.2329 | 68.3022 | 111.1308
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.097065 | 0.0074744 | 4 | 704815.4731 | 2051928.2335 | 14368.6168 | 41831.3325 | 87.1651 | 14.2802 | 198.7475 | 236776.603 | 0 | 115356.7706 | 0 | 0 | 0 | 216879.9085 | 221915.18 | 577377.7774 | 394072.197 | 1762378.4366 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 21072341.4004 | 61347876.022 | 100 | 0.029898 | 704815.4731 | 2051928.2335 | 14368.6168 | 41831.3325
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5266 | 0.21012 | 0.017277 | 4 | 314795.7066 | 897583.1669 | 6417.5363 | 18298.4469 | 96.9981 | 14.8441 | 287.6534 | 333399.8281 | 0 | 172230.7523 | 0 | 0 | 0 | 283803.8172 | 307879.415 | 801039.0832 | 546725.634 | 2445078.5298 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 21755041.4935 | 62030576.1152 | 133.3521 | 0.069108 | 314795.7066 | 897583.1669 | 6417.5363 | 18298.4469
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4392 | 0.369 | 0.032153 | 4 | 175187.0037 | 488346.4799 | 3571.424 | 9955.6035 | 104.8527 | 15.239 | 51.2293 | 445079.5694 | 0 | 239143.884 | 0 | 0 | 0 | 355694.7456 | 405568.0976 | 1055204.9965 | 720199.0924 | 3220890.3854 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 22530853.3492 | 62806387.9708 | 177.8279 | 0.12861 | 175187.0037 | 488346.4799 | 3571.424 | 9955.6035
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.665 | 0.59657 | 0.053942 | 4 | 108742.7362 | 295404.7093 | 2216.8678 | 6022.2246 | 111.5788 | 15.5424 | 61.5926 | 584091.044 | 0 | 312039.7471 | 0 | 0 | 0 | 444784.4968 | 522956.9623 | 1360626.7426 | 928655.7099 | 4153154.7027 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 23463117.6665 | 63738652.2882 | 237.1374 | 0.21577 | 108742.7362 | 295404.7093 | 2216.8678 | 6022.2246
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1575 | 0.89035 | 0.084291 | 4 | 72584.2579 | 192037.5233 | 1479.7283 | 3914.9447 | 116.7523 | 15.7557 | 71.0877 | 740325.0413 | 0 | 389634.2477 | 0 | 0 | 0 | 536986.4147 | 650108.8244 | 1691449.8054 | 1154449.248 | 5162953.5815 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 24472916.5453 | 64748451.1669 | 316.2278 | 0.33717 | 72584.2579 | 192037.5233 | 1479.7283 | 3914.9447
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0406 | 1.2727 | 0.12541 | 4 | 51111.7298 | 131398.8744 | 1041.9817 | 2678.7438 | 120.8957 | 15.9143 | 68.4727 | 922204.0551 | 0 | 482352.7476 | 0 | 0 | 0 | 639160.4672 | 797049.7353 | 2073759.9138 | 1415383.7527 | 6329910.6716 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 25639873.6354 | 65915408.257 | 421.6965 | 0.50164 | 51111.7298 | 131398.8744 | 1041.9817 | 2678.7438
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4307 | 1.7674 | 0.18036 | 4 | 37426.5574 | 93251.6753 | 762.991 | 1901.0615 | 124.2176 | 16.0328 | 64.0342 | 1135370.7491 | 0 | 593994.6913 | 0 | 0 | 0 | 754048.9999 | 968531.6317 | 2519920.6326 | 1719897.6109 | 7691764.3155 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 27001727.2793 | 67277261.901 | 562.3413 | 0.72146 | 37426.5574 | 93251.6753 | 762.991 | 1901.0615
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4781 | 2.4058 | 0.25317 | 4 | 28245.5944 | 68016.9015 | 575.8246 | 1386.6165 | 126.8742 | 16.1199 | 59.5492 | 1386614.5937 | 0 | 729180.2871 | 0 | 0 | 0 | 884842.1625 | 1170248.4469 | 3044746.4078 | 2078101.9866 | 9293733.8845 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 28603696.8482 | 68879231.4699 | 749.8942 | 1.0127 | 28245.5944 | 68016.9015 | 575.8246 | 1386.6165
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3218 | 3.2186 | 0.34865 | 4 | 21845.5905 | 50724.8561 | 445.3519 | 1034.0948 | 128.9625 | 16.18 | 74.685 | 1679941.2782 | 0 | 891265.1211 | 0 | 0 | 0 | 1030786.0206 | 1404777.0438 | 3654941.7085 | 2494572.8176 | 11156283.9898 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 30466246.9536 | 70741781.5752 | 1000 | 1.3946 | 21845.5905 | 50724.8561 | 445.3519 | 1034.0948
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.148 | 4.2463 | 0.47281 | 4 | 17250.7665 | 38546.6798 | 351.6802 | 785.8262 | 130.586 | 16.2155 | 67.9084 | 2021379.4 | 0 | 1084926.6649 | 0 | 0 | 0 | 1192746.6222 | 1676630.548 | 4362248.7616 | 2977324.415 | 13315256.4116 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 32625219.3754 | 72900753.997 | 1333.5214 | 1.8912 | 17250.7665 | 38546.6798 | 351.6802 | 785.8262
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1649 | 5.5352 | 0.63265 | 4 | 13875.212 | 29790.7095 | 282.865 | 607.3239 | 131.8241 | 16.226 | 75.8897 | 2416518.814 | 0 | 1314919.1386 | 0 | 0 | 0 | 1370647.9621 | 1989813.5067 | 5177086.5776 | 3533467.9677 | 15802453.9667 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 35112416.9305 | 75387951.5521 | 1778.2794 | 2.5306 | 13875.212 | 29790.7095 | 282.865 | 607.3239
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5682 | 7.1299 | 0.83565 | 4 | 11350.1559 | 23399.2631 | 231.3883 | 477.0256 | 132.7316 | 16.2075 | 62.3728 | 2868293.6478 | 0 | 1584825.8254 | 0 | 0 | 0 | 1561643.5044 | 2345757.5613 | 6103179.9934 | 4165545.7533 | 18629246.2856 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 37939209.2494 | 78214743.871 | 2371.3737 | 3.3426 | 11350.1559 | 23399.2631 | 231.3883 | 477.0256
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.4861 | 9.0625 | 1.0884 | 4 | 9436.3819 | 18687.8764 | 192.3734 | 380.9776 | 133.3457 | 16.1554 | 61.8409 | 3374509.9457 | 0 | 1895448.7347 | 0 | 0 | 0 | 1758998.2792 | 2741293.2143 | 7132282.6269 | 4867929.4466 | 21770462.2475 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 41080425.2112 | 81355959.8329 | 3162.2777 | 4.3534 | 9436.3819 | 18687.8764 | 192.3734 | 380.9776
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.9077 | 11.3362 | 1.394 | 4 | 7972.6283 | 15195.3863 | 162.5328 | 309.7785 | 133.6836 | 16.0614 | 62.107 | 3925098.8806 | 0 | 2243049.3312 | 0 | 0 | 0 | 1950979.7055 | 3166459.8877 | 8238479.0977 | 5622931.268 | 25146998.1707 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 44456961.1344 | 84732495.7561 | 4216.965 | 5.5762 | 7972.6283 | 15195.3863 | 162.5328 | 309.7785
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.6003 | 13.906 | 1.7495 | 4 | 6848.6825 | 12603.9994 | 139.6197 | 256.9496 | 133.749 | 15.9186 | 72.0924 | 4500117.3287 | 0 | 2617660.0281 | 0 | 0 | 0 | 2121669.8731 | 3603384.4197 | 9375267.1043 | 6398812.4411 | 28616911.1951 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 47926874.1589 | 88202408.7805 | 5623.4133 | 6.998 | 6848.6825 | 12603.9994 | 139.6197 | 256.9496
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.9903 | 16.6512 | 2.1411 | 4 | 5986.2515 | 10688.8694 | 122.0378 | 217.9071 | 133.5495 | 15.7266 | 81.834 | 5067270.086 | 0 | 3000485.3404 | 0 | 0 | 0 | 2250818.6101 | 4024243.8742 | 10470257.0748 | 7146165.5958 | 31959240.5813 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 51269203.545 | 91544738.1667 | 7498.9421 | 8.5645 | 5986.2515 | 10688.8694 | 122.0378 | 217.9071
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.3527 | 19.4128 | 2.5474 | 4 | 5326.9111 | 9279.5494 | 108.5963 | 189.1762 | 133.1215 | 15.4942 | 94.0001 | 5594329.6703 | 0 | 3370617.1051 | 0 | 0 | 0 | 2325303.6075 | 4403197.6493 | 11456217.0636 | 7819103.5476 | 34968768.6435 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 54278731.6072 | 94554266.2289 | 10000 | 10.1895 | 5326.9111 | 9279.5494 | 108.5963 | 189.1762
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9922 | 22.0335 | 2.9439 | 4 | 4825.1979 | 8245.3991 | 98.3682 | 168.0936 | 132.5321 | 15.2386 | 88.6697 | 6057442.7049 | 0 | 3710017.471 | 0 | 0 | 0 | 2343430.9516 | 4723247.5397 | 12288921.2271 | 8387441.2496 | 37510501.1439 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 56820464.1077 | 97095998.7293 | 13335.2143 | 11.7758 | 4825.1979 | 8245.3991 | 98.3682 | 168.0936
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3593 | 24.3854 | 3.3092 | 4 | 4445.0663 | 7487.7223 | 90.6187 | 152.6473 | 131.8647 | 14.981 | 108.2109 | 6443855.2328 | 0 | 4005879.8056 | 0 | 0 | 0 | 2312936.657 | 4977441.9612 | 12950282.9694 | 8838834.2283 | 39529230.8543 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 58839193.8181 | 99114728.4397 | 17782.7941 | 13.237 | 4445.0663 | 7487.7223 | 90.6187 | 152.6473
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1755 | 26.3997 | 3.6294 | 4 | 4157.9815 | 6932.2153 | 84.7661 | 141.3226 | 131.1953 | 14.7398 | 107.714 | 6753439.3855 | 0 | 4253238.0106 | 0 | 0 | 0 | 2248429.1376 | 5169491.5481 | 13449956.5997 | 9179871.7483 | 41054426.4297 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 60364389.3935 | 100639924.0152 | 23713.7371 | 14.5177 | 4157.9815 | 6932.2153 | 84.7661 | 141.3226
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4307 | 28.0674 | 3.8995 | 4 | 3941.618 | 6523.74 | 80.3552 | 132.9953 | 130.5752 | 14.526 | 101.0123 | 6995110.3628 | 0 | 4454122.1252 | 0 | 0 | 0 | 2166305.9518 | 5310059.9915 | 13815686.8549 | 9429490.1625 | 42170775.4488 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 61480738.4126 | 101756273.0342 | 31622.7766 | 15.5978 | 3941.618 | 6523.74 | 80.3552 | 132.9953
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.2501 | 29.4121 | 4.1204 | 4 | 3778.748 | 6222.4156 | 77.0349 | 126.8524 | 130.0325 | 14.3445 | 108.2338 | 7180360.5374 | 0 | 4613627.0197 | 0 | 0 | 0 | 2079536.4505 | 5410674.363 | 14077464.8106 | 9608158.9962 | 42969822.1774 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 62279785.1412 | 102555319.7628 | 42169.6503 | 16.4816 | 3778.748 | 6222.4156 | 77.0349 | 126.8524
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8197 | 30.4726 | 4.2969 | 4 | 3656.2257 | 5999.519 | 74.5371 | 122.3083 | 129.5779 | 14.1956 | 106.8765 | 7320407.5332 | 0 | 4737913.4268 | 0 | 0 | 0 | 1996614.7617 | 5481424.9315 | 14261543.2768 | 9733796.3318 | 43531700.2618 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 62841663.2256 | 103117197.8472 | 56234.1325 | 17.1876 | 3656.2257 | 5999.519 | 74.5371 | 122.3083
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3593 | 31.2972 | 4.4355 | 4 | 3564.0926 | 5834.1514 | 72.6588 | 118.9371 | 129.2083 | 14.0765 | 111.6648 | 7425574.4447 | 0 | 4833624.5661 | 0 | 0 | 0 | 1922528.0735 | 5530873.5629 | 14390198.4725 | 9821606.1465 | 43924405.2662 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 63234368.23 | 103509902.8516 | 74989.4209 | 17.7421 | 3564.0926 | 5834.1514 | 72.6588 | 118.9371
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.0855 | 31.9339 | 4.5432 | 4 | 3494.8327 | 5711.0713 | 71.2469 | 116.4279 | 128.9132 | 13.9824 | 109.3234 | 7504588.1473 | 0 | 4907021.4495 | 0 | 0 | 0 | 1859538.3884 | 5565747.7142 | 14480933.8606 | 9883534.9133 | 44201364.4732 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 63511327.437 | 103786862.0586 | 100000 | 18.1729 | 3494.8327 | 5711.0713 | 71.2469 | 116.4279
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1466 | 32.4168 | 4.6258 | 4 | 3442.7832 | 5619.48 | 70.1858 | 114.5607 | 128.684 | 13.9099 | 103.7504 | 7563162.7197 | 0 | 4962329.8409 | 0 | 0 | 0 | 1807215.7229 | 5589756.2306 | 14543399.0953 | 9926168.7195 | 44392032.3288 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 63701995.2926 | 103977529.9143 | 133352.1432 | 18.5031 | 3442.7832 | 5619.48 | 70.1858 | 114.5607
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.7271 | 32.7874 | 4.6891 | 4 | 3403.6793 | 5550.9828 | 69.3886 | 113.1643 | 128.5046 | 13.8536 | 111.2431 | 7607401.6843 | 0 | 5004638.6814 | 0 | 0 | 0 | 1765397.9904 | 5607200.9589 | 14588786.7 | 9957146.6923 | 44530572.7073 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 63840535.6711 | 104116070.2927 | 177827.941 | 18.7563 | 3403.6793 | 5550.9828 | 69.3886 | 113.1643
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.9233 | 33.0682 | 4.7372 | 4 | 3374.3101 | 5499.7894 | 68.7899 | 112.1206 | 128.3668 | 13.8105 | 125.9496 | 7640485.3554 | 0 | 5036597.6344 | 0 | 0 | 0 | 1732316.2119 | 5619665.6887 | 14621217.37 | 9979281.291 | 44629563.5514 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 63939526.5151 | 104215061.1368 | 237137.3706 | 18.9489 | 3374.3101 | 5499.7894 | 68.7899 | 112.1206
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.8077 | 33.2765 | 4.7734 | 4 | 3352.2583 | 5461.632 | 68.3403 | 111.3428 | 128.2637 | 13.7784 | 106.999 | 7664724.5949 | 0 | 5060195.8618 | 0 | 0 | 0 | 1706158.7838 | 5628120.9038 | 14643216.1053 | 9994295.8799 | 44696712.1295 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64006675.0932 | 104282209.7149 | 316227.766 | 19.0936 | 3352.2583 | 5461.632 | 68.3403 | 111.3428
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4922 | 33.4374 | 4.801 | 4 | 3335.7049 | 5432.9373 | 68.0029 | 110.7578 | 128.1832 | 13.7534 | 110.0408 | 7683360.4185 | 0 | 5078442.4753 | 0 | 0 | 0 | 1686276.3976 | 5634750.9236 | 14660466.057 | 10006069.3263 | 44749365.5984 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64059328.5622 | 104334863.1838 | 421696.5034 | 19.2041 | 3335.7049 | 5432.9373 | 68.0029 | 110.7578
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.0038 | 33.5578 | 4.8218 | 4 | 3323.2816 | 5411.4755 | 67.7496 | 110.3202 | 128.1227 | 13.7346 | 121.4506 | 7697212.2994 | 0 | 5092067.077 | 0 | 0 | 0 | 1670958.4329 | 5639492.7456 | 14672803.305 | 10014489.7516 | 44787023.6115 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64096986.5753 | 104372521.1969 | 562341.3252 | 19.2873 | 3323.2816 | 5411.4755 | 67.7496 | 110.3202
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3935 | 33.6495 | 4.8375 | 4 | 3313.9595 | 5395.3617 | 67.5595 | 109.9917 | 128.0764 | 13.7203 | 107.6063 | 7707723.385 | 0 | 5102440.3815 | 0 | 0 | 0 | 1659363.2623 | 5643115.5412 | 14682229.0761 | 10020923.034 | 44815794.68 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64125757.6438 | 104401292.2654 | 749894.2093 | 19.3502 | 3313.9595 | 5395.3617 | 67.5595 | 109.9917
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6714 | 33.7152 | 4.8491 | 4 | 3306.9655 | 5383.3942 | 67.417 | 109.7478 | 128.0432 | 13.71 | 100.9201 | 7715191.8023 | 0 | 5109832.3726 | 0 | 0 | 0 | 1650293.5973 | 5645373.9311 | 14688104.9434 | 10024933.4342 | 44833730.0809 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64143693.0447 | 104419227.6664 | 1000000 | 19.3965 | 3306.9655 | 5383.3942 | 67.417 | 109.7478
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.8929 | 33.7673 | 4.8581 | 4 | 3301.7188 | 5374.3333 | 67.31 | 109.5631 | 128.0167 | 13.7018 | 114.1399 | 7721135.3633 | 0 | 5115724.1037 | 0 | 0 | 0 | 1643652.4843 | 5647399.661 | 14693375.4771 | 10028530.6818 | 44849817.7713 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64159780.7351 | 104435315.3567 | 1333521.4322 | 19.4322 | 3301.7188 | 5374.3333 | 67.31 | 109.5631
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0586 | 33.8063 | 4.8648 | 4 | 3297.7832 | 5367.5453 | 67.2298 | 109.4247 | 127.9968 | 13.6957 | 108.6003 | 7725575.4116 | 0 | 5120132.1157 | 0 | 0 | 0 | 1638626.5852 | 5648890.3039 | 14697253.824 | 10031177.7332 | 44861655.9737 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64171618.9374 | 104447153.5591 | 1778279.41 | 19.459 | 3297.7832 | 5367.5453 | 67.2298 | 109.4247
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1707 | 33.8329 | 4.8696 | 4 | 3294.8313 | 5362.5439 | 67.1696 | 109.3227 | 127.9834 | 13.6915 | 110.2067 | 7728570.8419 | 0 | 5123111.2959 | 0 | 0 | 0 | 1634623.4339 | 5649659.173 | 14699254.2636 | 10032543.0744 | 44867762.0826 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64177725.0464 | 104453259.6681 | 2371373.7057 | 19.4783 | 3294.8313 | 5362.5439 | 67.1696 | 109.3227
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.2561 | 33.8532 | 4.8732 | 4 | 3292.6173 | 5358.785 | 67.1245 | 109.2461 | 127.9731 | 13.6884 | 109.198 | 7730851.2778 | 0 | 5125380.8568 | 0 | 0 | 0 | 1631632.5617 | 5650267.2315 | 14700836.3072 | 10033622.8517 | 44872591.0867 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64182554.0504 | 104458088.6721 | 3162277.6602 | 19.4929 | 3292.6173 | 5358.785 | 67.1245 | 109.2461
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.3339 | 33.8713 | 4.8762 | 4 | 3290.9568 | 5355.8699 | 67.0906 | 109.1867 | 127.9638 | 13.6855 | 116.8859 | 7732930.2209 | 0 | 5127448.5644 | 0 | 0 | 0 | 1629620.0833 | 5651099.5588 | 14703001.852 | 10035100.8804 | 44879201.1597 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64189164.1235 | 104464698.7452 | 4216965.0343 | 19.5047 | 3290.9568 | 5355.8699 | 67.0906 | 109.1867
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.383 | 33.883 | 4.8782 | 4 | 3289.7115 | 5353.7495 | 67.0652 | 109.1434 | 127.9578 | 13.6837 | 111.6644 | 7734239.7074 | 0 | 5128753.0822 | 0 | 0 | 0 | 1627947.3727 | 5651466.6633 | 14703956.9826 | 10035752.7767 | 44882116.5848 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64192079.5486 | 104467614.1702 | 5623413.2519 | 19.513 | 3289.7115 | 5353.7495 | 67.0652 | 109.1434
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4265 | 33.8931 | 4.8799 | 4 | 3288.7776 | 5352.1124 | 67.0462 | 109.1101 | 127.9526 | 13.6821 | 115.0544 | 7735401.7303 | 0 | 5129909.8493 | 0 | 0 | 0 | 1626806.4271 | 5651926.0226 | 14705152.1414 | 10036568.4971 | 44885764.6678 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64195727.6316 | 104471262.2532 | 7498942.0933 | 19.5196 | 3288.7776 | 5352.1124 | 67.0462 | 109.1101
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4413 | 33.897 | 4.8809 | 4 | 3288.0773 | 5351.0102 | 67.0319 | 109.0876 | 127.9508 | 13.6815 | 104.8113 | 7735794.3521 | 0 | 5130303.6275 | 0 | 0 | 0 | 1625642.9628 | 5651778.9675 | 14704769.5343 | 10036307.3599 | 44884596.8042 | 961560.8286 | 18348402.1352 | 18348402.1352 | 14367225.0389 | 7559907.4476 | 0 | 64194559.768 | 104470094.3896 | 10000000 | 19.5234 | 3288.0773 | 5351.0102 | 67.0319 | 109.0876
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.077853 | 0.0075096 | 4 | 712710.9103 | 2089008.8038 | 14529.5759 | 42587.2701 | 84.6367 | 14.4478 | 24.4947 | 214137.0725 | 0 | 100321.7074 | 0 | 0 | 0 | 191608.3632 | 197366.1858 | 513506.3301 | 350478.6218 | 1567418.2808 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 21408782.6556 | 62750737.7844 | 100 | 0.030039 | 712710.9103 | 2089008.8038 | 14529.5759 | 42587.2701
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.21977 | 0.01851 | 4 | 302472.4461 | 860850.8846 | 6166.3099 | 17549.6097 | 99.1449 | 15.2992 | 294.7711 | 348733.6585 | 0 | 178542.5842 | 0 | 0 | 0 | 297159.7288 | 321530.0289 | 836555.1803 | 570966.1 | 2553487.2807 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 22394851.6555 | 63736806.7842 | 133.3521 | 0.074039 | 302472.4461 | 860850.8846 | 6166.3099 | 17549.6097
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.38688 | 0.034463 | 4 | 168378.8999 | 468280.7102 | 3432.6316 | 9546.5357 | 107.2967 | 15.705 | 51.8858 | 466420.9892 | 0 | 248322.308 | 0 | 0 | 0 | 373298.8325 | 424336.4306 | 1104036.349 | 753527.4939 | 3369942.4033 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 23211306.778 | 64553261.9068 | 177.8279 | 0.13785 | 168378.8999 | 468280.7102 | 3432.6316 | 9546.5357
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8204 | 0.6261 | 0.057921 | 4 | 104357.6725 | 282798.0425 | 2127.4723 | 5765.2206 | 114.2496 | 16.0153 | 53.7368 | 612582.0312 | 0 | 320328.7639 | 0 | 0 | 0 | 467278.6495 | 546073.8834 | 1420772.2295 | 969706.2406 | 4336741.7981 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 24178106.1728 | 65520061.3016 | 237.1374 | 0.23168 | 104357.6725 | 282798.0425 | 2127.4723 | 5765.2206
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3498 | 0.93249 | 0.090411 | 4 | 69742.2639 | 184059.1957 | 1421.7904 | 3752.2957 | 119.5469 | 16.2314 | 52.1675 | 775139.5966 | 0 | 399337.769 | 0 | 0 | 0 | 562693.8212 | 677496.7628 | 1762707.6032 | 1203084.1592 | 5380459.712 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 25221824.0867 | 66563779.2155 | 316.2278 | 0.36164 | 69742.2639 | 184059.1957 | 1421.7904 | 3752.2957
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2964 | 1.3341 | 0.13444 | 4 | 49170.0233 | 126048.3012 | 1002.3974 | 2569.6651 | 123.8307 | 16.3936 | 75.2172 | 966054.493 | 0 | 494589.4496 | 0 | 0 | 0 | 670353.1832 | 831088.8791 | 2162322.7836 | 1475829.7311 | 6600238.5195 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 26441602.8942 | 67783558.023 | 421.6965 | 0.53776 | 49170.0233 | 126048.3012 | 1002.3974 | 2569.6651
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7667 | 1.8538 | 0.19327 | 4 | 36044.2903 | 89522.603 | 734.8116 | 1825.0393 | 127.2609 | 16.5144 | 51.821 | 1189747.0399 | 0 | 609253.3219 | 0 | 0 | 0 | 791372.5826 | 1010245.4483 | 2628451.4267 | 1793972.108 | 8023041.9274 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 27864406.3022 | 69206361.431 | 562.3413 | 0.77306 | 36044.2903 | 89522.603 | 734.8116 | 1825.0393
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8996 | 2.5215 | 0.27108 | 4 | 27230.1614 | 65356.7539 | 555.1237 | 1332.3858 | 129.9901 | 16.6025 | 60.5766 | 1452024 | 0 | 747369.0854 | 0 | 0 | 0 | 927642.2798 | 1219543.7924 | 3173002.785 | 2165639.5994 | 9685221.5419 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 29526585.9166 | 70868541.0454 | 749.8942 | 1.0843 | 27230.1614 | 65356.7539 | 555.1237 | 1332.3858
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.8554 | 3.3724 | 0.37312 | 4 | 21080.6538 | 48781.1693 | 429.7576 | 994.4701 | 132.1396 | 16.663 | 75.7157 | 1758617.3073 | 0 | 913163.0956 | 0 | 0 | 0 | 1080157.0094 | 1463255.5908 | 3807090.8922 | 2598417.7618 | 11620701.6571 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 31462066.0319 | 72804021.1606 | 1000 | 1.4925 | 21080.6538 | 48781.1693 | 429.7576 | 994.4701
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.8324 | 4.4502 | 0.5058 | 4 | 16662.3855 | 37096.3018 | 339.6853 | 756.2583 | 133.814 | 16.698 | 61.7019 | 2116234.6844 | 0 | 1111664.8073 | 0 | 0 | 0 | 1250267.6621 | 1746485.19 | 4543996.2109 | 3101370.7837 | 13870019.3383 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 33711383.7131 | 75053338.8418 | 1333.5214 | 2.0232 | 16662.3855 | 37096.3018 | 339.6853 | 756.2583
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.0151 | 5.7977 | 0.67633 | 4 | 13414.4798 | 28696.0961 | 273.4723 | 585.0087 | 135.0862 | 16.7066 | 64.1413 | 2528637.2552 | 0 | 1346577.2482 | 0 | 0 | 0 | 1435733.7175 | 2071269.8062 | 5389019.1597 | 3678116.3098 | 16449353.4966 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 36290717.8713 | 77632673.0001 | 1778.2794 | 2.7053 | 13414.4798 | 28696.0961 | 273.4723 | 585.0087
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6056 | 7.4616 | 0.89254 | 4 | 10984.0548 | 22563.8698 | 223.9248 | 459.995 | 136.0175 | 16.6853 | 66.8574 | 2999214.269 | 0 | 1621698.6733 | 0 | 0 | 0 | 1634184.5586 | 2439488.0253 | 6347047.4341 | 4331990.2926 | 19373623.2529 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 39214987.6277 | 80556942.7565 | 2371.3737 | 3.5702 | 10984.0548 | 22563.8698 | 223.9248 | 459.995
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.736 | 9.4755 | 1.1612 | 4 | 9140.7572 | 18041.0796 | 186.3467 | 367.7918 | 136.645 | 16.6273 | 71.0023 | 3525744.0954 | 0 | 1937932.4817 | 0 | 0 | 0 | 1838731.2973 | 2847939.071 | 7409753.2701 | 5057308.8621 | 22617409.0776 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 42458773.4523 | 83800728.5811 | 3162.2777 | 4.645 | 9140.7572 | 18041.0796 | 186.3467 | 367.7918
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4003 | 11.8434 | 1.4857 | 4 | 7731.1556 | 14687.8057 | 157.6101 | 299.4308 | 136.9876 | 16.5252 | 87.1364 | 4098139.293 | 0 | 2291696.9525 | 0 | 0 | 0 | 2038055.9078 | 3286877.9398 | 8551782.1681 | 5836767.0512 | 26103319.3125 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 45944683.6873 | 87286638.816 | 4216.965 | 5.9428 | 7731.1556 | 14687.8057 | 157.6101 | 299.4308
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.2787 | 14.5016 | 1.8609 | 4 | 6649.1221 | 12203.0015 | 135.5513 | 248.7747 | 137.0468 | 16.3723 | 71.0163 | 4691573.1242 | 0 | 2670304.1669 | 0 | 0 | 0 | 2212203.2857 | 3733891.4249 | 9714819.5612 | 6630563.9701 | 29653355.5329 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 49494719.9077 | 90836675.0365 | 5623.4133 | 7.4438 | 6649.1221 | 12203.0015 | 135.5513 | 248.7747
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8191 | 17.3309 | 2.2726 | 4 | 5819.3247 | 10367.2097 | 118.6348 | 211.3496 | 136.8338 | 16.1683 | 93.3044 | 5274715.3718 | 0 | 3055930.5029 | 0 | 0 | 0 | 2342825.6641 | 4162653.9001 | 10830371.5704 | 7391951.1387 | 33058448.148 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 52899812.5227 | 94241767.6515 | 7498.9421 | 9.0904 | 5819.3247 | 10367.2097 | 118.6348 | 211.3496
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.2628 | 20.1621 | 2.6973 | 4 | 5185.3646 | 9017.1815 | 105.7107 | 183.8274 | 136.3893 | 15.9236 | 84.4147 | 5813683.9592 | 0 | 3426882.8244 | 0 | 0 | 0 | 2416272.6795 | 4546167.3906 | 11828195.0033 | 8072986.1349 | 36104187.992 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 55945552.3667 | 97287507.4955 | 10000 | 10.7891 | 5185.3646 | 9017.1815 | 105.7107 | 183.8274
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.9212 | 22.8358 | 3.1097 | 4 | 4703.2838 | 8026.9459 | 95.8828 | 163.6401 | 135.7845 | 15.6565 | 102.0824 | 6285009.1043 | 0 | 3765502.0684 | 0 | 0 | 0 | 2431921.3285 | 4868148.6754 | 12665924.2589 | 8644753.5654 | 38661259.0009 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 58502623.3756 | 99844578.5044 | 13335.2143 | 12.4387 | 4703.2838 | 8026.9459 | 95.8828 | 163.6401
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.265 | 25.2264 | 3.4878 | 4 | 4338.2394 | 7301.5301 | 88.4409 | 148.8516 | 135.1054 | 15.3892 | 108.6152 | 6676883.7272 | 0 | 4059664.4227 | 0 | 0 | 0 | 2398638.0724 | 5122722.6267 | 13328273.4597 | 9096820.5049 | 40683002.8136 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 60524367.1883 | 101866322.3171 | 17782.7941 | 13.9514 | 4338.2394 | 7301.5301 | 88.4409 | 148.8516
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0392 | 27.2686 | 3.8182 | 4 | 4062.6812 | 6769.6151 | 82.8233 | 138.0078 | 134.4277 | 15.1399 | 102.1247 | 6990173.9873 | 0 | 4305062.5052 | 0 | 0 | 0 | 2331803.2071 | 5314545.4828 | 13827357.1831 | 9437455.4013 | 42206397.7668 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 62047762.1415 | 103389717.2703 | 23713.7371 | 15.2726 | 4062.6812 | 6769.6151 | 82.8233 | 138.0078
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.2398 | 28.9549 | 4.0958 | 4 | 3855.0863 | 6378.5 | 78.5911 | 130.0343 | 133.8027 | 14.9199 | 110.3567 | 7234169.8276 | 0 | 4503859.0785 | 0 | 0 | 0 | 2247859.1655 | 5454496.3479 | 14191480.6262 | 9685977.1332 | 43317842.1789 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 63159206.5536 | 104501161.6824 | 31622.7766 | 16.3833 | 3855.0863 | 6378.5 | 78.5911 | 130.0343
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9823 | 30.3073 | 4.3221 | 4 | 3698.8679 | 6090.177 | 75.4064 | 124.1565 | 133.2597 | 14.7345 | 103.1899 | 7420225.7284 | 0 | 4660836.533 | 0 | 0 | 0 | 2159365.2365 | 5553766.7242 | 14449761.7821 | 9862259.3292 | 44106215.3333 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 63947579.7081 | 105289534.8369 | 42169.6503 | 17.2884 | 3698.8679 | 6090.177 | 75.4064 | 124.1565
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4936 | 31.3743 | 4.5027 | 4 | 3581.3823 | 5876.7919 | 73.0113 | 119.8064 | 132.8051 | 14.5824 | 105.768 | 7561027.8234 | 0 | 4783234.3764 | 0 | 0 | 0 | 2075568.2193 | 5623733.8634 | 14631801.9262 | 9986505.4681 | 44661871.6766 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 64503236.0514 | 105845191.1802 | 56234.1325 | 18.0107 | 3581.3823 | 5876.7919 | 73.0113 | 119.8064
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9749 | 32.201 | 4.6441 | 4 | 3493.0583 | 5718.5462 | 71.2107 | 116.5803 | 132.4373 | 14.4613 | 104.9122 | 7666421.668 | 0 | 4877155.3286 | 0 | 0 | 0 | 2000829.3368 | 5672318.47 | 14758209.1065 | 10072780.9661 | 45047714.876 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 64889079.2508 | 106231034.3795 | 74989.4209 | 18.5766 | 3493.0583 | 5718.5462 | 71.2107 | 116.5803
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.6667 | 32.8415 | 4.7542 | 4 | 3426.6765 | 5600.6597 | 69.8574 | 114.177 | 132.1426 | 14.3654 | 98.4896 | 7745947.7247 | 0 | 4949465.9563 | 0 | 0 | 0 | 1937764.6627 | 5706939.554 | 14848286.0654 | 10134260.3414 | 45322664.3045 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65164028.6792 | 106505983.808 | 100000 | 19.0167 | 3426.6765 | 5600.6597 | 69.8574 | 114.177
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.7077 | 33.3285 | 4.8385 | 4 | 3376.7994 | 5512.879 | 68.8406 | 112.3875 | 131.9132 | 14.2913 | 110.1373 | 7805091.4896 | 0 | 5004118.6315 | 0 | 0 | 0 | 1885627.3738 | 5730986.623 | 14910851.6061 | 10176962.6085 | 45513638.3325 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65355002.7072 | 106696957.836 | 133352.1432 | 19.3541 | 3376.7994 | 5512.879 | 68.8406 | 112.3875
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2593 | 33.6994 | 4.903 | 4 | 3339.3339 | 5447.3294 | 68.0768 | 111.0512 | 131.7352 | 14.2342 | 118.8843 | 7849382.3042 | 0 | 5045566.0091 | 0 | 0 | 0 | 1843775.7719 | 5748102.3932 | 14955383.3292 | 10207356.4246 | 45649566.2322 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65490930.607 | 106832885.7358 | 177827.941 | 19.612 | 3339.3339 | 5447.3294 | 68.0768 | 111.0512
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4191 | 33.9773 | 4.9517 | 4 | 3311.199 | 5398.4398 | 67.5033 | 110.0545 | 131.6002 | 14.1911 | 116.3511 | 7882107.4531 | 0 | 5076493.1758 | 0 | 0 | 0 | 1810457.9086 | 5759932.8296 | 14986163.698 | 10228364.6588 | 45743519.7239 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65584884.0987 | 106926839.2274 | 237137.3706 | 19.807 | 3311.199 | 5398.4398 | 67.5033 | 110.0545
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3009 | 34.1887 | 4.9888 | 4 | 3290.0765 | 5361.8208 | 67.0727 | 109.308 | 131.4964 | 14.1581 | 111.135 | 7906770.6921 | 0 | 5099975.7896 | 0 | 0 | 0 | 1784611.7165 | 5768629.6973 | 15008791.1637 | 10243808.3691 | 45812587.4283 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65653951.8031 | 106995906.9318 | 316227.766 | 19.9551 | 3290.0765 | 5361.8208 | 67.0727 | 109.308
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.966 | 34.3482 | 5.0168 | 4 | 3274.2222 | 5334.4058 | 66.7494 | 108.7491 | 131.4174 | 14.133 | 112.1746 | 7925247.4402 | 0 | 5117669.6562 | 0 | 0 | 0 | 1764669.7465 | 5774958.8687 | 15025258.3694 | 10255047.5753 | 45862851.6562 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65704216.031 | 107046171.1598 | 421696.5034 | 20.0671 | 3274.2222 | 5334.4058 | 66.7494 | 108.7491
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4756 | 34.4703 | 5.038 | 4 | 3262.3244 | 5313.8124 | 66.5069 | 108.3293 | 131.3566 | 14.1137 | 110.2005 | 7939330.4504 | 0 | 5131214.2106 | 0 | 0 | 0 | 1749547.2115 | 5779835.8303 | 15037947.2231 | 10263707.9787 | 45901582.9047 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65742947.2794 | 107084902.4082 | 562341.3252 | 20.1522 | 3262.3244 | 5313.8124 | 66.5069 | 108.3293
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.848 | 34.5598 | 5.0539 | 4 | 3253.3972 | 5298.4597 | 66.3249 | 108.0163 | 131.3118 | 14.0996 | 115.6819 | 7949582.978 | 0 | 5141109.6571 | 0 | 0 | 0 | 1737824.7401 | 5783121.7763 | 15046496.5805 | 10269543.0908 | 45927678.8227 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65769043.1974 | 107110998.3262 | 749894.2093 | 20.2155 | 3253.3972 | 5298.4597 | 66.3249 | 108.0163
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1381 | 34.6293 | 5.066 | 4 | 3246.6998 | 5286.8848 | 66.1884 | 107.7803 | 131.2769 | 14.0886 | 113.7051 | 7957545.0153 | 0 | 5148812.0614 | 0 | 0 | 0 | 1729108.2897 | 5785831.4929 | 15053546.7073 | 10274354.9472 | 45949198.5137 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65790562.8884 | 107132518.0172 | 1000000 | 20.2638 | 3246.6998 | 5286.8848 | 66.1884 | 107.7803
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3427 | 34.6787 | 5.0748 | 4 | 3241.6757 | 5278.3006 | 66.0859 | 107.6053 | 131.2522 | 14.0808 | 111.2634 | 7963148.5396 | 0 | 5154245.4594 | 0 | 0 | 0 | 1722275.2004 | 5787470.9878 | 15057812.3367 | 10277266.3269 | 45962218.8507 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65803583.2255 | 107145538.3542 | 1333521.4322 | 20.2992 | 3241.6757 | 5278.3006 | 66.0859 | 107.6053
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5083 | 34.7183 | 5.0817 | 4 | 3237.9072 | 5271.7837 | 66.0091 | 107.4724 | 131.2322 | 14.0744 | 106.4873 | 7967677.1077 | 0 | 5158640.5909 | 0 | 0 | 0 | 1717328.9937 | 5789022.21 | 15061848.2986 | 10280020.9538 | 45974538.1547 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65815902.5294 | 107157857.6582 | 1778279.41 | 20.3267 | 3237.9072 | 5271.7837 | 66.0091 | 107.4724
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.623 | 34.746 | 5.0867 | 4 | 3235.0807 | 5266.9644 | 65.9515 | 107.3742 | 131.2183 | 14.0701 | 107.2282 | 7970807.0175 | 0 | 5161683.2374 | 0 | 0 | 0 | 1713429.0921 | 5789908.5453 | 15064154.3614 | 10281594.8891 | 45981577.1428 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65822941.5175 | 107164896.6463 | 2371373.7057 | 20.3466 | 3235.0807 | 5266.9644 | 65.9515 | 107.3742
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.7176 | 34.7686 | 5.0905 | 4 | 3232.9608 | 5263.2923 | 65.9083 | 107.2993 | 131.2068 | 14.0664 | 106.124 | 7973389.6233 | 0 | 5164194.2532 | 0 | 0 | 0 | 1710645.9283 | 5790809.6239 | 15066498.783 | 10283195.005 | 45988733.2166 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65830097.5913 | 107172052.7201 | 3162277.6602 | 20.3622 | 3232.9608 | 5263.2923 | 65.9083 | 107.2993
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.7862 | 34.7851 | 5.0934 | 4 | 3231.3709 | 5260.556 | 65.8759 | 107.2435 | 131.1985 | 14.0638 | 100.1454 | 7975257.9722 | 0 | 5166012.3845 | 0 | 0 | 0 | 1708508.7005 | 5791413.8323 | 15068070.8093 | 10284267.9453 | 45993531.644 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65834896.0188 | 107176851.1476 | 4216965.0343 | 20.3737 | 3231.3709 | 5260.556 | 65.8759 | 107.2435
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.8297 | 34.7957 | 5.0954 | 4 | 3230.1785 | 5258.5582 | 65.8516 | 107.2028 | 131.1932 | 14.0621 | 106.2048 | 7976442.5786 | 0 | 5167167.0605 | 0 | 0 | 0 | 1706763.0987 | 5791645.3678 | 15068673.2171 | 10284679.1009 | 45995370.4236 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65836734.7984 | 107178689.9271 | 5623413.2519 | 20.3818 | 3230.1785 | 5258.5582 | 65.8516 | 107.2028
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.8614 | 34.8035 | 5.0969 | 4 | 3229.2843 | 5257.0669 | 65.8333 | 107.1724 | 131.1893 | 14.0609 | 112.0188 | 7977303.8198 | 0 | 5168006.9971 | 0 | 0 | 0 | 1705434.791 | 5791790.7871 | 15069051.5684 | 10284937.3335 | 45996525.2969 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65837889.6716 | 107179844.8004 | 7498942.0933 | 20.3878 | 3229.2843 | 5257.0669 | 65.8333 | 107.1724
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9003 | 34.8126 | 5.0983 | 4 | 3228.6137 | 5255.8453 | 65.8197 | 107.1475 | 131.1846 | 14.0594 | 115.9251 | 7978364.8278 | 0 | 5169038.7387 | 0 | 0 | 0 | 1704705.0685 | 5792322.3676 | 15070434.6319 | 10285881.3027 | 46000746.9372 | 961560.8286 | 18879803.5461 | 18879803.5461 | 14716656.7318 | 7745494.8509 | 0 | 65842111.312 | 107184066.4408 | 10000000 | 20.3933 | 3228.6137 | 5255.8453 | 65.8197 | 107.1475
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.076812 | 0.0078255 | 4 | 701549.2968 | 2056800.5328 | 14302.0313 | 41930.6609 | 85.389 | 14.8226 | 24.1674 | 216857.8021 | 0 | 100098.0527 | 0 | 0 | 0 | 193595.759 | 199115.1294 | 518056.7226 | 353584.3582 | 1581307.8241 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 21959933.7007 | 64382080.5501 | 100 | 0.031302 | 701549.2968 | 2056800.5328 | 14302.0313 | 41930.6609
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7035 | 0.23226 | 0.019831 | 4 | 290771.2828 | 825559.4631 | 5927.7659 | 16830.1463 | 101.5216 | 15.7664 | 36.1358 | 367121.3633 | 0 | 186541.1157 | 0 | 0 | 0 | 313830.7767 | 338322.3697 | 880245.4064 | 600785.5771 | 2686846.6088 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 23065472.4854 | 65487619.3348 | 133.3521 | 0.079325 | 290771.2828 | 825559.4631 | 5927.7659 | 16830.1463
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7339 | 0.41509 | 0.037027 | 4 | 161829.1192 | 448259.8028 | 3299.1055 | 9138.3824 | 110.2251 | 16.1935 | 64.3609 | 496726.7828 | 0 | 261131.5642 | 0 | 0 | 0 | 400994.9427 | 451952.783 | 1175888.433 | 802568.0176 | 3589262.5233 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 23967888.3998 | 66390035.2493 | 177.8279 | 0.14811 | 161829.1192 | 448259.8028 | 3299.1055 | 9138.3824
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9861 | 0.65792 | 0.062128 | 4 | 100239.4965 | 270943.4616 | 2043.5177 | 5523.5489 | 116.9694 | 16.4903 | 47.6833 | 642767.1361 | 0 | 329111.7349 | 0 | 0 | 0 | 491413.5176 | 570684.0316 | 1484802.7867 | 1013408.4116 | 4532187.6184 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 24910813.495 | 67332960.3444 | 237.1374 | 0.24851 | 100239.4965 | 270943.4616 | 2043.5177 | 5523.5489
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5472 | 0.97645 | 0.096834 | 4 | 67082.6671 | 176605.1196 | 1367.5709 | 3600.3342 | 122.3606 | 16.7078 | 52.7588 | 811101.7223 | 0 | 409240.6162 | 0 | 0 | 0 | 589326.3827 | 705770.8013 | 1836270.8514 | 1253292.5877 | 5605002.9615 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 25983628.838 | 68405775.6875 | 316.2278 | 0.38734 | 67082.6671 | 176605.1196 | 1367.5709 | 3600.3342
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5593 | 1.3982 | 0.14391 | 4 | 47352.7739 | 121048.584 | 965.3503 | 2467.7391 | 126.7834 | 16.8735 | 68.4811 | 1011358.28 | 0 | 507085.467 | 0 | 0 | 0 | 702702.9694 | 866247.2194 | 2253797.5731 | 1538263.1545 | 6879454.6634 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 27258080.5399 | 69680227.3894 | 421.6965 | 0.57564 | 47352.7739 | 121048.584 | 965.3503 | 2467.7391
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.0956 | 1.941 | 0.2067 | 4 | 34750.2228 | 86058.1818 | 708.4303 | 1754.4124 | 130.3021 | 16.9959 | 55.1019 | 1244467.7947 | 0 | 624099.4166 | 0 | 0 | 0 | 828451.2826 | 1051837.2127 | 2736664.6659 | 1867829.8673 | 8353350.2398 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 28731976.1164 | 71154122.9658 | 562.3413 | 0.82681 | 34750.2228 | 86058.1818 | 708.4303 | 1754.4124
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3212 | 2.6399 | 0.28978 | 4 | 26279.023 | 62878.0675 | 535.7334 | 1281.8545 | 133.1119 | 17.0853 | 59.5582 | 1518586.3012 | 0 | 765447.8722 | 0 | 0 | 0 | 970955.7143 | 1269446.0562 | 3302838.2391 | 2254254.9647 | 10081529.1477 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 30460155.0242 | 72882301.8737 | 749.8942 | 1.1591 | 26279.023 | 62878.0675 | 535.7334 | 1281.8545
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.4085 | 3.5334 | 0.39877 | 4 | 20363.6909 | 46959.5628 | 415.1414 | 957.3342 | 135.3313 | 17.1463 | 77.675 | 1840146.6473 | 0 | 935721.4916 | 0 | 0 | 0 | 1131718.3823 | 1523958.7432 | 3965028.043 | 2706213.1125 | 12102786.4199 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 32481412.2965 | 74903559.146 | 1000 | 1.5951 | 20363.6909 | 46959.5628 | 415.1414 | 957.3342
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5124 | 4.6579 | 0.54014 | 4 | 16110.5148 | 35745.3629 | 328.4346 | 728.7176 | 137.0472 | 17.1804 | 51.825 | 2212438.8852 | 0 | 1138070.5587 | 0 | 0 | 0 | 1308136.8633 | 1816872.0598 | 4727128.408 | 3226362.2712 | 14429009.0464 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 34807634.923 | 77229781.7724 | 1333.5214 | 2.1606 | 16110.5148 | 35745.3629 | 328.4346 | 728.7176
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8628 | 6.0657 | 0.72179 | 4 | 12982.0062 | 27675.2909 | 264.6558 | 564.1982 | 138.3542 | 17.1871 | 77.0942 | 2642540.7895 | 0 | 1377960.7375 | 0 | 0 | 0 | 1501407.6292 | 2153544.5709 | 5603081.2208 | 3824218.065 | 17102753.013 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 37481378.8895 | 79903525.739 | 1778.2794 | 2.8872 | 12982.0062 | 27675.2909 | 264.6558 | 564.1982
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.6534 | 7.8029 | 0.95185 | 4 | 10639.7788 | 21781.7507 | 216.9063 | 444.0505 | 139.3101 | 17.1622 | 65.4741 | 3132968.3606 | 0 | 1658728.2523 | 0 | 0 | 0 | 1708081.7721 | 2534913.5702 | 6595325.1273 | 4501444.9198 | 20131462.0022 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 40510087.8788 | 82932234.7283 | 2371.3737 | 3.8074 | 10639.7788 | 21781.7507 | 216.9063 | 444.0505
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.0077 | 9.9022 | 1.2373 | 4 | 8862.8362 | 17434.6205 | 180.6809 | 355.4283 | 139.9516 | 17.0983 | 61.6282 | 3680735.398 | 0 | 1980922.1523 | 0 | 0 | 0 | 1920527.5144 | 2957052.1753 | 7693643.1852 | 5251069.5625 | 23483949.9877 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 43862575.8643 | 86284722.7137 | 3162.2777 | 4.949 | 8862.8362 | 17434.6205 | 180.6809 | 355.4283
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.8696 | 12.3571 | 1.5805 | 4 | 7503.9811 | 14214.3375 | 152.9788 | 289.7785 | 140.297 | 16.9882 | 85.3182 | 4272765.171 | 0 | 2339335.9236 | 0 | 0 | 0 | 2124907.2807 | 3407433.2664 | 8865442.3984 | 6050846.6035 | 27060730.6436 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 47439356.5202 | 89861503.3696 | 4216.965 | 6.3219 | 7503.9811 | 14214.3375 | 152.9788 | 289.7785
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.9501 | 15.1086 | 1.9763 | 4 | 6461.2416 | 11827.6606 | 131.7211 | 241.1229 | 140.35 | 16.8246 | 81.9647 | 4885635.0273 | 0 | 2722470.3298 | 0 | 0 | 0 | 2303326.1857 | 3865458.3017 | 10057129.5865 | 6864197.5961 | 30698217.0271 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 51076842.9037 | 93498989.7531 | 5623.4133 | 7.9051 | 6461.2416 | 11827.6606 | 131.7211 | 241.1229
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.6413 | 18.0235 | 2.4084 | 4 | 5662.0365 | 10065.6529 | 115.4283 | 205.2019 | 140.1231 | 16.6081 | 97.6055 | 5484863.6559 | 0 | 3110927.2342 | 0 | 0 | 0 | 2435428.6472 | 4302175.6196 | 11193378.4645 | 7639710.803 | 34166484.4244 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 54545110.301 | 96967257.1504 | 7498.9421 | 9.6335 | 5662.0365 | 10065.6529 | 115.4283 | 205.2019
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.1628 | 20.9242 | 2.8517 | 4 | 5051.8567 | 8770.8725 | 102.9889 | 178.8061 | 139.6619 | 16.3508 | 96.6887 | 6035544.8073 | 0 | 3482620.2717 | 0 | 0 | 0 | 2507649.323 | 4690067.6168 | 12202593.8738 | 8328521.0571 | 37246996.9497 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 57625622.8262 | 100047769.6757 | 10000 | 11.4068 | 5051.8567 | 8770.8725 | 102.9889 | 178.8061
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.836 | 23.6505 | 3.28 | 4 | 4588.1586 | 7821.5718 | 93.5358 | 159.4533 | 139.0422 | 16.0722 | 103.8861 | 6514809.5709 | 0 | 3820377.8843 | 0 | 0 | 0 | 2520615.9542 | 5013763.3297 | 13044783.7195 | 8903332.9321 | 39817683.3906 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 60196309.2672 | 102618456.1166 | 13335.2143 | 13.1199 | 4588.1586 | 7821.5718 | 93.5358 | 159.4533
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.1527 | 26.0788 | 3.671 | 4 | 4237.2313 | 7126.2422 | 86.3817 | 145.2781 | 138.3517 | 15.795 | 104.2448 | 6911861.1727 | 0 | 4112767.4591 | 0 | 0 | 0 | 2484354.5113 | 5268503.4258 | 13707565.1953 | 9355694.9081 | 41840746.6724 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 62219372.5489 | 104641519.3984 | 17782.7941 | 14.684 | 4237.2313 | 7126.2422 | 86.3817 | 145.2781
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.8614 | 28.1438 | 4.011 | 4 | 3972.4521 | 6616.5733 | 80.9838 | 134.8878 | 137.6679 | 15.5384 | 105.2753 | 7227884.6402 | 0 | 4355582.6611 | 0 | 0 | 0 | 2414480.9858 | 5459199.8319 | 14203718.1269 | 9694329.4788 | 43355195.7246 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 63733821.6012 | 106155968.4506 | 23713.7371 | 16.0439 | 3972.4521 | 6616.5733 | 80.9838 | 134.8878
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.9844 | 29.8434 | 4.2959 | 4 | 3773.0523 | 6241.8384 | 76.9188 | 127.2483 | 137.0406 | 15.313 | 118.3954 | 7473329.6147 | 0 | 4551691.0688 | 0 | 0 | 0 | 2328100.1463 | 5597717.1236 | 14564111.7059 | 9940305.5019 | 44455255.1611 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 64833881.0376 | 107256027.8871 | 31622.7766 | 17.1834 | 3773.0523 | 6241.8384 | 76.9188 | 127.2483
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.6756 | 31.2085 | 4.5278 | 4 | 3623.0472 | 5965.3559 | 73.8607 | 121.6118 | 136.4954 | 15.1229 | 101.9487 | 7660940.9315 | 0 | 4706870.6695 | 0 | 0 | 0 | 2238450.7215 | 5696442.3058 | 14820974.3787 | 10115619.554 | 45239298.561 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 65617924.4375 | 108040071.287 | 42169.6503 | 18.1113 | 3623.0472 | 5965.3559 | 73.8607 | 121.6118
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.1307 | 32.282 | 4.7124 | 4 | 3510.264 | 5760.8094 | 71.5615 | 117.4419 | 136.0411 | 14.9677 | 110.5891 | 7802480.2219 | 0 | 4827458.1868 | 0 | 0 | 0 | 2153758.6782 | 5765641.8639 | 15001017.4341 | 10238502.6389 | 45788859.0238 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 66167484.9003 | 108589631.7498 | 56234.1325 | 18.8497 | 3510.264 | 5760.8094 | 71.5615 | 117.4419
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.5756 | 33.1151 | 4.8571 | 4 | 3425.4946 | 5609.0257 | 69.8333 | 114.3476 | 135.6729 | 14.8439 | 103.1232 | 7908681.9875 | 0 | 4920186.5834 | 0 | 0 | 0 | 2078750.0744 | 5813971.2717 | 15126760.6394 | 10324324.9602 | 46172675.5166 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 66551301.3931 | 108973448.2426 | 74989.4209 | 19.4282 | 3425.4946 | 5609.0257 | 69.8333 | 114.3476
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.2083 | 33.7539 | 4.9689 | 4 | 3361.7971 | 5496.1732 | 68.5348 | 112.0469 | 135.3816 | 14.7471 | 112.9609 | 7987920.4622 | 0 | 4990761.3335 | 0 | 0 | 0 | 2015030.841 | 5847547.9283 | 15214120.2125 | 10383949.6639 | 46439330.4414 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 66817956.318 | 109240103.1674 | 100000 | 19.8757 | 3361.7971 | 5496.1732 | 68.5348 | 112.0469
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2157 | 34.242 | 5.0548 | 4 | 3313.9454 | 5412.0412 | 67.5593 | 110.3318 | 135.1536 | 14.6719 | 113.3499 | 8047205.5844 | 0 | 5044404.437 | 0 | 0 | 0 | 1962764.2128 | 5871205.9513 | 15275673.5354 | 10425961.0716 | 46627214.7926 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67005840.6692 | 109427987.5186 | 133352.1432 | 20.2194 | 3313.9454 | 5412.0412 | 67.5593 | 110.3318
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.746 | 34.6146 | 5.1205 | 4 | 3278.0066 | 5349.18 | 66.8266 | 109.0503 | 134.9764 | 14.6138 | 116.7782 | 8091738.6547 | 0 | 5085201.8882 | 0 | 0 | 0 | 1920981.5358 | 5888189.6107 | 15319861.5333 | 10456120.2881 | 46762093.5108 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67140719.3873 | 109562866.2368 | 177827.941 | 20.4822 | 3278.0066 | 5349.18 | 66.8266 | 109.0503
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.8929 | 34.8945 | 5.1703 | 4 | 3251.0217 | 5302.2726 | 66.2765 | 108.094 | 134.8416 | 14.5699 | 114.3119 | 8124734.4468 | 0 | 5115724.1037 | 0 | 0 | 0 | 1887819.3049 | 5900028.3636 | 15350663.5399 | 10477143.2906 | 46856113.0495 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67234738.9261 | 109656885.7755 | 237137.3706 | 20.6811 | 3251.0217 | 5302.2726 | 66.2765 | 108.094
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7554 | 35.1053 | 5.2079 | 4 | 3230.7646 | 5267.2031 | 65.8635 | 107.3791 | 134.739 | 14.5366 | 117.2497 | 8149335.5248 | 0 | 5138649.7141 | 0 | 0 | 0 | 1861943.1882 | 5908472.0866 | 15372632.3751 | 10492137.472 | 46923170.3608 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67301796.2374 | 109723943.0868 | 316227.766 | 20.8315 | 3230.7646 | 5267.2031 | 65.8635 | 107.3791
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.4157 | 35.2665 | 5.2365 | 4 | 3215.561 | 5240.8803 | 65.5536 | 106.8424 | 134.6599 | 14.5109 | 107.896 | 8168045.5834 | 0 | 5156182.7412 | 0 | 0 | 0 | 1842180.7235 | 5914899.5287 | 15389355.2611 | 10503551.1853 | 46974215.0232 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67352840.8998 | 109774987.7492 | 421696.5034 | 20.9459 | 3215.561 | 5240.8803 | 65.5536 | 106.8424
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9151 | 35.3884 | 5.2581 | 4 | 3204.1524 | 5221.1515 | 65.321 | 106.4402 | 134.5998 | 14.4914 | 105.0775 | 8182123.0232 | 0 | 5169431.7696 | 0 | 0 | 0 | 1827085.134 | 5919669.5715 | 15401765.9338 | 10512021.7244 | 47012097.1566 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67390723.0331 | 109812869.8826 | 562341.3252 | 21.0323 | 3204.1524 | 5221.1515 | 65.321 | 106.4402
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.2855 | 35.479 | 5.2743 | 4 | 3195.5927 | 5206.4059 | 65.1465 | 106.1396 | 134.5549 | 14.4769 | 96.814 | 8192525.3211 | 0 | 5179255.1161 | 0 | 0 | 0 | 1815488.6124 | 5923034.9294 | 15410521.9047 | 10517997.8545 | 47038823.7382 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67417449.6147 | 109839596.4642 | 749894.2093 | 21.097 | 3195.5927 | 5206.4059 | 65.1465 | 106.1396
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5607 | 35.5465 | 5.2864 | 4 | 3189.1712 | 5195.3775 | 65.0156 | 105.9148 | 134.5214 | 14.4661 | 104.0289 | 8200231.1955 | 0 | 5186550.6134 | 0 | 0 | 0 | 1806630.8489 | 5925430.9366 | 15416755.8239 | 10522252.6325 | 47057852.0508 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67436477.9274 | 109858624.7768 | 1000000 | 21.1455 | 3189.1712 | 5195.3775 | 65.0156 | 105.9148
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.7628 | 35.5961 | 5.2954 | 4 | 3184.3543 | 5187.1429 | 64.9174 | 105.7469 | 134.4968 | 14.4582 | 116.006 | 8205875.7159 | 0 | 5191905.1684 | 0 | 0 | 0 | 1799844.6862 | 5927073.9725 | 15421030.6664 | 10525170.3003 | 47070900.5097 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67449526.3862 | 109871673.2357 | 1333521.4322 | 21.1815 | 3184.3543 | 5187.1429 | 64.9174 | 105.7469
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.924 | 35.6354 | 5.3023 | 4 | 3180.7413 | 5180.9071 | 64.8437 | 105.6198 | 134.4771 | 14.4519 | 110.3629 | 8210371.5771 | 0 | 5196174.2673 | 0 | 0 | 0 | 1794894.6429 | 5928561.79 | 15424901.6624 | 10527812.3346 | 47082716.2743 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67461342.1509 | 109883489.0003 | 1778279.41 | 21.2093 | 3180.7413 | 5180.9071 | 64.8437 | 105.6198
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.0406 | 35.664 | 5.3075 | 4 | 3178.0314 | 5176.2608 | 64.7885 | 105.5251 | 134.4628 | 14.4473 | 110.3908 | 8213622.3502 | 0 | 5199265.1363 | 0 | 0 | 0 | 1791086.0428 | 5929549.6764 | 15427471.9402 | 10529566.602 | 47090561.7479 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67469187.6245 | 109891334.4739 | 2371373.7057 | 21.2299 | 3178.0314 | 5176.2608 | 64.7885 | 105.5251
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.1332 | 35.6866 | 5.3114 | 4 | 3175.999 | 5172.7437 | 64.747 | 105.4534 | 134.4515 | 14.4436 | 109.6714 | 8216200.8785 | 0 | 5201717.8801 | 0 | 0 | 0 | 1788311.0016 | 5930429.6065 | 15429761.3377 | 10531129.1628 | 47097549.8672 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67476175.7437 | 109898322.5932 | 3162277.6602 | 21.2457 | 3175.999 | 5172.7437 | 64.747 | 105.4534
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.2038 | 35.7038 | 5.3144 | 4 | 3174.4747 | 5170.0995 | 64.716 | 105.3995 | 134.4429 | 14.4408 | 119.0676 | 8218164.2287 | 0 | 5203586.4432 | 0 | 0 | 0 | 1786243.4085 | 5931117.6913 | 15431551.5933 | 10532351.0491 | 47103014.4142 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67481640.2908 | 109903787.1402 | 4216965.0343 | 21.2576 | 3174.4747 | 5170.0995 | 64.716 | 105.3995
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.2381 | 35.7126 | 5.3163 | 4 | 3173.3316 | 5168.241 | 64.6927 | 105.3616 | 134.4386 | 14.4395 | 110.6455 | 8219113.8542 | 0 | 5204493.8036 | 0 | 0 | 0 | 1784351.0612 | 5931103.9004 | 15431515.7121 | 10532326.5595 | 47102904.8909 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67481530.7675 | 109903677.6169 | 5623413.2519 | 21.2652 | 3173.3316 | 5168.241 | 64.6927 | 105.3616
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.277 | 35.7221 | 5.318 | 4 | 3172.4744 | 5166.7598 | 64.6752 | 105.3314 | 134.4339 | 14.4379 | 113.9102 | 8220195.1355 | 0 | 5205523.7324 | 0 | 0 | 0 | 1783169.3325 | 5931466.3982 | 15432458.8569 | 10532970.2752 | 47105783.7307 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67484409.6072 | 109906556.4567 | 7498942.0933 | 21.2719 | 3172.4744 | 5166.7598 | 64.6752 | 105.3314
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3159 | 35.7313 | 5.3194 | 4 | 3171.8315 | 5165.5845 | 64.6621 | 105.3074 | 134.4291 | 14.4364 | 118.1271 | 8221277.8363 | 0 | 5206553.6102 | 0 | 0 | 0 | 1782458.1082 | 5932012.9263 | 15433880.8111 | 10533940.7881 | 47110124.0802 | 961560.8286 | 19417065.0479 | 19417065.0479 | 15071655.511 | 7933426.2906 | 0 | 67488749.9568 | 109910896.8062 | 10000000 | 21.2775 | 3171.8315 | 5165.5845 | 64.6621 | 105.3074
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.075779 | 0.0081245 | 4 | 692865.7966 | 2031905.2225 | 14125.0064 | 41423.1363 | 86.1111 | 15.1957 | 24.7035 | 219514.0095 | 0 | 99865.3302 | 0 | 0 | 0 | 195595.7862 | 200840.2991 | 522545.2602 | 356647.8773 | 1595008.5623 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 22516756.0315 | 66032865.8152 | 100 | 0.032498 | 692865.7966 | 2031905.2225 | 14125.0064 | 41423.1363
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7935 | 0.24393 | 0.021215 | 4 | 279678.8175 | 792471.1432 | 5701.631 | 16155.5962 | 103.8025 | 16.2286 | 48.6531 | 384640.3697 | 0 | 193920.9485 | 0 | 0 | 0 | 329371.6333 | 354093.8511 | 921279.5658 | 628792.2341 | 2812098.6025 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 23733846.0717 | 67249955.8553 | 133.3521 | 0.084861 | 279678.8175 | 792471.1432 | 5701.631 | 16155.5962
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8413 | 0.43331 | 0.039654 | 4 | 155412.3189 | 429760.4945 | 3168.2903 | 8761.249 | 112.6445 | 16.6583 | 48.8966 | 518397.782 | 0 | 267124.9096 | 0 | 0 | 0 | 418508.2974 | 469572.0857 | 1221730.2445 | 833855.9959 | 3729189.3152 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 24650936.7844 | 68167046.5681 | 177.8279 | 0.15862 | 155412.3189 | 429760.4945 | 3168.2903 | 8761.249
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1371 | 0.68817 | 0.066505 | 4 | 96376.6944 | 259958.557 | 1964.7693 | 5299.6068 | 119.6292 | 16.9627 | 51.4723 | 671808.8187 | 0 | 337058.931 | 0 | 0 | 0 | 513906.3962 | 593881.9169 | 1545158.9259 | 1054602.7168 | 4716417.7056 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 25638165.1748 | 69154274.9585 | 237.1374 | 0.26602 | 96376.6944 | 259958.557 | 1964.7693 | 5299.6068
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7519 | 1.0226 | 0.10358 | 4 | 64590.4101 | 169624.0667 | 1316.7629 | 3458.016 | 125.1991 | 17.1853 | 49.2721 | 848446.7839 | 0 | 419443.3808 | 0 | 0 | 0 | 617156.9205 | 735168.3632 | 1912757.2773 | 1305496.145 | 5838468.8707 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 26760216.3399 | 70276326.1236 | 316.2278 | 0.41431 | 64590.4101 | 169624.0667 | 1316.7629 | 3458.016
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8176 | 1.4629 | 0.15378 | 4 | 45649.7786 | 116393.3116 | 930.6325 | 2372.8351 | 129.7336 | 17.3533 | 58.3452 | 1057017.9794 | 0 | 519295.021 | 0 | 0 | 0 | 734950.3512 | 901392.7071 | 2345238.9229 | 1600673.7547 | 7158568.7365 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 28080316.2057 | 71596425.9893 | 421.6965 | 0.61512 | 45649.7786 | 116393.3116 | 930.6325 | 2372.8351
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4318 | 2.0314 | 0.22076 | 4 | 33537.0259 | 82816.6686 | 683.6976 | 1688.3298 | 133.3569 | 17.4778 | 53.4643 | 1300777.5484 | 0 | 639181.258 | 0 | 0 | 0 | 866699.8516 | 1094596.8766 | 2847916.5403 | 1943761.5576 | 8692933.6324 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 29614681.1017 | 73130790.8853 | 562.3413 | 0.88304 | 33537.0259 | 82816.6686 | 683.6976 | 1688.3298
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7567 | 2.7635 | 0.30935 | 4 | 25386.8388 | 60554.0833 | 517.545 | 1234.4769 | 136.2493 | 17.5684 | 71.7887 | 1587450.0704 | 0 | 784015.1008 | 0 | 0 | 0 | 1016066.0473 | 1321137.1752 | 3437327.9275 | 2346046.9405 | 10492043.2617 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 31413790.731 | 74929900.5146 | 749.8942 | 1.2374 | 25386.8388 | 60554.0833 | 517.545 | 1234.4769
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.9419 | 3.6942 | 0.42533 | 4 | 19690.7404 | 45268.6061 | 401.4224 | 922.8618 | 138.5206 | 17.6294 | 66.1373 | 1921572.2734 | 0 | 957351.4111 | 0 | 0 | 0 | 1182249.7151 | 1583857.6259 | 4120872.6486 | 2812580.2581 | 12578483.9322 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 33500231.4015 | 77016341.1851 | 1000 | 1.7013 | 19690.7404 | 45268.6061 | 401.4224 | 922.8618
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.189 | 4.8697 | 0.57584 | 4 | 15592.1527 | 34484.5157 | 317.8671 | 703.0135 | 140.2857 | 17.6628 | 82.0522 | 2310043.7255 | 0 | 1164198.5797 | 0 | 0 | 0 | 1366418.9199 | 1887857.8778 | 4911818.9452 | 3352417.3579 | 14992755.4061 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 35914502.8754 | 79430612.659 | 1333.5214 | 2.3034 | 15592.1527 | 34484.5157 | 317.8671 | 703.0135
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.713 | 6.3402 | 0.76909 | 4 | 12575.4851 | 26720.7625 | 256.3683 | 544.7389 | 141.6287 | 17.6674 | 62.9164 | 2758520.6235 | 0 | 1409255.6374 | 0 | 0 | 0 | 1567982.6317 | 2236945.9681 | 5820074.5484 | 3972320.4699 | 17765099.8791 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 38686847.3483 | 82202957.132 | 1778.2794 | 3.0764 | 12575.4851 | 26720.7625 | 256.3683 | 544.7389
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6861 | 8.1488 | 1.0133 | 4 | 10315.9159 | 21052.1576 | 210.3039 | 429.1767 | 142.6074 | 17.6388 | 62.9659 | 3268019.235 | 0 | 1695026.8178 | 0 | 0 | 0 | 1781864.5475 | 2630515.1341 | 6844060.7861 | 4671212.1179 | 20890698.6384 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 41812446.1076 | 85328555.8913 | 2371.3737 | 4.0532 | 10315.9159 | 21052.1576 | 210.3039 | 429.1767
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.2575 | 10.3336 | 1.3158 | 4 | 8601.4885 | 16869.2538 | 175.353 | 343.9026 | 143.2639 | 17.5694 | 77.3629 | 3837034.0239 | 0 | 2022946.2305 | 0 | 0 | 0 | 2002102.0786 | 3066212.1099 | 7977654.9433 | 5444913.4232 | 24350862.8095 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 45272610.2787 | 88788720.0624 | 3162.2777 | 5.2633 | 8601.4885 | 16869.2538 | 175.353 | 343.9026
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.3434 | 12.8828 | 1.6788 | 4 | 7289.9725 | 13770.3999 | 148.616 | 280.7282 | 143.6122 | 17.45 | 85.2016 | 4450360.8917 | 0 | 2386876.9552 | 0 | 0 | 0 | 2212864.8403 | 3529540.048 | 9183139.1967 | 6267681.1964 | 28030463.1283 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 48952210.5976 | 92468320.3812 | 4216.965 | 6.715 | 7289.9725 | 13770.3999 | 148.616 | 280.7282
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.6091 | 15.7259 | 2.0954 | 4 | 6284.1254 | 11475.9946 | 128.1104 | 233.9537 | 143.6584 | 17.2754 | 77.3185 | 5081977.5847 | 0 | 2774003.8039 | 0 | 0 | 0 | 2394778.8032 | 3997796.4748 | 10401446.3666 | 7099200.8735 | 31749203.9067 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 52670951.3759 | 96187061.1596 | 5623.4133 | 8.3816 | 6284.1254 | 11475.9946 | 128.1104 | 233.9537
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.4271 | 18.7224 | 2.548 | 4 | 5513.639 | 9783.3381 | 112.403 | 199.4466 | 143.418 | 17.0466 | 83.2346 | 5696278.2747 | 0 | 3164593.6591 | 0 | 0 | 0 | 2527411.937 | 4441430.7096 | 11555691.6437 | 7886996.9925 | 35272403.2165 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 56194150.6858 | 99710260.4694 | 7498.9421 | 10.1918 | 5513.639 | 9783.3381 | 112.403 | 199.4466
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.0212 | 21.6923 | 3.0101 | 4 | 4925.7719 | 8539.9538 | 100.4185 | 174.0985 | 142.9408 | 16.7765 | 97.808 | 6258488.4788 | 0 | 3536922.9756 | 0 | 0 | 0 | 2598278.3107 | 4833539.0084 | 12575877.0047 | 8583294.4641 | 38386400.2424 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 59308147.7117 | 102824257.4953 | 10000 | 12.0404 | 4925.7719 | 8539.9538 | 100.4185 | 174.0985
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.7191 | 24.4736 | 3.4545 | 4 | 4479.3109 | 7628.5115 | 91.3168 | 155.5175 | 142.306 | 16.486 | 100.4293 | 6746062.085 | 0 | 3874154.7035 | 0 | 0 | 0 | 2608928.3768 | 5159366.6145 | 13423613.5993 | 9161892.1092 | 40974017.4883 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 61895764.9575 | 105411874.7412 | 13335.2143 | 13.8181 | 4479.3109 | 7628.5115 | 91.3168 | 155.5175
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.9897 | 26.9355 | 3.8581 | 4 | 4141.6123 | 6961.4366 | 84.4324 | 141.9183 | 141.6059 | 16.1995 | 97.6587 | 7147462.3822 | 0 | 4164278.5559 | 0 | 0 | 0 | 2569094.19 | 5413525.7 | 14084883.4045 | 9613222.339 | 42992466.5716 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 63914214.0409 | 107430323.8245 | 17782.7941 | 15.4322 | 4141.6123 | 6961.4366 | 84.4324 | 141.9183
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.6519 | 29.0269 | 4.208 | 4 | 3886.9279 | 6472.2424 | 79.2403 | 131.9454 | 140.9151 | 15.9349 | 104.1529 | 7466807.7099 | 0 | 4405082.6247 | 0 | 0 | 0 | 2496699.0215 | 5603749.8489 | 14579807.6196 | 9951018.2855 | 44503165.1101 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 65424912.5794 | 108941022.363 | 23713.7371 | 16.832 | 3886.9279 | 6472.2424 | 79.2403 | 131.9454
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.7165 | 30.7435 | 4.5003 | 4 | 3695.1989 | 6112.5912 | 75.3316 | 124.6134 | 140.2843 | 15.7036 | 109.7863 | 7714227.2807 | 0 | 4599059.3424 | 0 | 0 | 0 | 2408301.5954 | 5741419.4052 | 14937995.5653 | 10195488.9184 | 45596492.1074 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 66518239.5766 | 110034349.3602 | 31622.7766 | 18.0013 | 3695.1989 | 6112.5912 | 75.3316 | 124.6134
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.3339 | 32.116 | 4.7375 | 4 | 3551.0067 | 5847.3739 | 72.3921 | 119.2066 | 139.7393 | 15.5096 | 105.2326 | 7902531.7462 | 0 | 4751846.5669 | 0 | 0 | 0 | 2316870.5245 | 5838787.0467 | 15191326.1956 | 10368392.279 | 46369754.3589 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 67291501.8282 | 110807611.6118 | 42169.6503 | 18.95 | 3551.0067 | 5847.3739 | 72.3921 | 119.2066
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.7313 | 33.1953 | 4.9261 | 4 | 3442.6208 | 5651.0872 | 70.1825 | 115.2051 | 139.2856 | 15.3514 | 113.3045 | 8044672.7286 | 0 | 4870599.1559 | 0 | 0 | 0 | 2231183.1587 | 5907117.4668 | 15369107.9323 | 10489731.9674 | 46912412.4097 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 67834159.8789 | 111350269.6626 | 56234.1325 | 19.7042 | 3442.6208 | 5651.0872 | 70.1825 | 115.2051
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1271 | 34.0319 | 5.0736 | 4 | 3361.1739 | 5505.4309 | 68.5221 | 112.2357 | 138.9189 | 15.2255 | 101.8863 | 8151233.5349 | 0 | 4961808.686 | 0 | 0 | 0 | 2155578.6852 | 5954762.1534 | 15493069.6334 | 10574338.3756 | 47290791.0685 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68212538.5378 | 111728648.3214 | 74989.4209 | 20.2943 | 3361.1739 | 5505.4309 | 68.5221 | 112.2357
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7212 | 34.673 | 5.1876 | 4 | 3299.9844 | 5397.1234 | 67.2746 | 110.0277 | 138.6289 | 15.1271 | 115.2806 | 8230733.829 | 0 | 5031202.2434 | 0 | 0 | 0 | 2091562.1764 | 5987864.317 | 15579194.673 | 10633120.4848 | 47553677.7236 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68475425.1929 | 111991534.9765 | 100000 | 20.7502 | 3299.9844 | 5397.1234 | 67.2746 | 110.0277
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.7091 | 35.1651 | 5.2753 | 4 | 3254.0241 | 5316.2976 | 66.3377 | 108.3799 | 138.4009 | 15.0503 | 113.0523 | 8290536.1927 | 0 | 5084219.9511 | 0 | 0 | 0 | 2039395.2768 | 6011519.054 | 15640739.4464 | 10675126.0572 | 47741535.9782 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68663283.4475 | 112179393.2311 | 133352.1432 | 21.101 | 3254.0241 | 5316.2976 | 66.3377 | 108.3799
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.2024 | 35.5358 | 5.3419 | 4 | 3219.5106 | 5256.0593 | 65.6341 | 107.1519 | 138.2263 | 14.9919 | 114.1259 | 8334807.3917 | 0 | 5123953.0322 | 0 | 0 | 0 | 1997316.7318 | 6027870.0907 | 15683281.4899 | 10704161.8761 | 47871390.6125 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68793138.0817 | 112309247.8653 | 177827.941 | 21.3676 | 3219.5106 | 5256.0593 | 65.6341 | 107.1519
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.3427 | 35.819 | 5.3927 | 4 | 3193.5989 | 5210.9579 | 65.1058 | 106.2324 | 138.091 | 14.9469 | 110.7977 | 8368243.7525 | 0 | 5154245.4594 | 0 | 0 | 0 | 1964402.7865 | 6039887.8793 | 15714549.3107 | 10725502.8062 | 47966831.9946 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68888579.4638 | 112404689.2475 | 237137.3706 | 21.5708 | 3193.5989 | 5210.9579 | 65.1058 | 106.2324
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.1929 | 36.0306 | 5.431 | 4 | 3174.1492 | 5177.2897 | 64.7093 | 105.5461 | 137.9891 | 14.913 | 98.6224 | 8392956.1978 | 0 | 5176799.7165 | 0 | 0 | 0 | 1938591.8423 | 6048255.6251 | 15736320.4686 | 10740362.0689 | 48033285.9191 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 68955033.3884 | 112471143.172 | 316227.766 | 21.7239 | 3174.1492 | 5177.2897 | 64.7093 | 105.5461
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.8313 | 36.1897 | 5.4599 | 4 | 3159.5527 | 5152.101 | 64.4118 | 105.0325 | 137.9119 | 14.8875 | 113.1626 | 8411393.9155 | 0 | 5193720.8694 | 0 | 0 | 0 | 1918660.2853 | 6054272.2774 | 15751974.5637 | 10751046.3105 | 48081068.2218 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69002815.691 | 112518925.4747 | 421696.5034 | 21.8394 | 3159.5527 | 5152.101 | 64.4118 | 105.0325
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3159 | 36.3103 | 5.4817 | 4 | 3148.6003 | 5133.21 | 64.1885 | 104.6474 | 137.8529 | 14.868 | 119.207 | 8425318.7803 | 0 | 5206553.6102 | 0 | 0 | 0 | 1903482.7923 | 6058788.5213 | 15763724.904 | 10759066.1592 | 48116934.7674 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69038682.2366 | 112554792.0203 | 562341.3252 | 21.9268 | 3148.6003 | 5133.21 | 64.1885 | 104.6474
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.6855 | 36.4023 | 5.4982 | 4 | 3140.3832 | 5119.0228 | 64.021 | 104.3582 | 137.8078 | 14.8531 | 121.6202 | 8435902.0666 | 0 | 5216337.4552 | 0 | 0 | 0 | 1892024.1558 | 6062262.8343 | 15772764.3537 | 10765235.7693 | 48144526.635 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69066274.1042 | 112582383.8878 | 749894.2093 | 21.9929 | 3140.3832 | 5119.0228 | 64.021 | 104.3582
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.9561 | 36.4698 | 5.5105 | 4 | 3134.219 | 5108.4385 | 63.8953 | 104.1424 | 137.7746 | 14.8422 | 116.6962 | 8443626.9116 | 0 | 5223497.4619 | 0 | 0 | 0 | 1883196.052 | 6064624.966 | 15778910.1358 | 10769430.3919 | 48163285.9192 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69085033.3884 | 112601143.1721 | 1000000 | 22.0422 | 3134.219 | 5108.4385 | 63.8953 | 104.1424
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1607 | 36.5209 | 5.5198 | 4 | 3129.5952 | 5100.4963 | 63.801 | 103.9805 | 137.7494 | 14.8339 | 114.5548 | 8449457.5653 | 0 | 5228911.346 | 0 | 0 | 0 | 1876545.8511 | 6066416.7574 | 15783572.0095 | 10772612.2165 | 48177515.7458 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69099263.215 | 112615372.9987 | 1333521.4322 | 22.0793 | 3129.5952 | 5100.4963 | 63.801 | 103.9805
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.3071 | 36.5576 | 5.5267 | 4 | 3126.1271 | 5094.5905 | 63.7303 | 103.8601 | 137.7314 | 14.828 | 105.7882 | 8453618.101 | 0 | 5232781.0467 | 0 | 0 | 0 | 1871389.6328 | 6067537.6244 | 15786488.2756 | 10774602.628 | 48186417.3084 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69108164.7776 | 112624274.5613 | 1778279.41 | 22.1066 | 3126.1271 | 5094.5905 | 63.7303 | 103.8601
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.4313 | 36.5884 | 5.5321 | 4 | 3123.526 | 5090.0692 | 63.6773 | 103.7679 | 137.7161 | 14.823 | 122.4873 | 8457150.4008 | 0 | 5236067.0481 | 0 | 0 | 0 | 1867774.3698 | 6068786.8093 | 15789738.3985 | 10776820.9036 | 48196337.9302 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69118085.3994 | 112634195.1831 | 2371373.7057 | 22.1282 | 3123.526 | 5090.0692 | 63.6773 | 103.7679
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.524 | 36.6113 | 5.5361 | 4 | 3121.5752 | 5086.6837 | 63.6375 | 103.6989 | 137.7047 | 14.8192 | 119.4404 | 8459780.033 | 0 | 5238515.4719 | 0 | 0 | 0 | 1865040.681 | 6069701.1125 | 15792117.2279 | 10778444.5036 | 48203599.0299 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69125346.4992 | 112641456.2828 | 3162277.6602 | 22.1444 | 3121.5752 | 5086.6837 | 63.6375 | 103.6989
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.5823 | 36.626 | 5.5389 | 4 | 3120.1121 | 5084.2176 | 63.6077 | 103.6487 | 137.6975 | 14.8168 | 114.1995 | 8461433.507 | 0 | 5240057.832 | 0 | 0 | 0 | 1862777.6491 | 6070064.9054 | 15793063.7423 | 10779090.5191 | 48206488.1549 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69128235.6241 | 112644345.4078 | 4216965.0343 | 22.1557 | 3120.1121 | 5084.2176 | 63.6077 | 103.6487
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6212 | 36.636 | 5.541 | 4 | 3119.0149 | 5082.3999 | 63.5853 | 103.6116 | 137.6926 | 14.8152 | 119.2277 | 8462534.2575 | 0 | 5241086.0091 | 0 | 0 | 0 | 1860986.9673 | 6070196.8212 | 15793406.9602 | 10779324.7724 | 48207535.7878 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69129283.257 | 112645393.0407 | 5623413.2519 | 22.1638 | 3119.0149 | 5082.3999 | 63.5853 | 103.6116
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6749 | 36.6489 | 5.5429 | 4 | 3118.1921 | 5080.8783 | 63.5686 | 103.5806 | 137.686 | 14.8131 | 112.8782 | 8464059.8395 | 0 | 5242505.7897 | 0 | 0 | 0 | 1860097.9807 | 6070998.8079 | 15795493.565 | 10780748.923 | 48213904.9058 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69135652.375 | 112651762.1587 | 7498942.0933 | 22.1717 | 3118.1921 | 5080.8783 | 63.5686 | 103.5806
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6944 | 36.654 | 5.544 | 4 | 3117.575 | 5079.8721 | 63.556 | 103.5601 | 137.6836 | 14.8123 | 115.0419 | 8464609.1935 | 0 | 5243019.8245 | 0 | 0 | 0 | 1859043.3702 | 6071002.2314 | 15795502.4723 | 10780755.0025 | 48213932.0943 | 961560.8286 | 19960186.6406 | 19960186.6406 | 15432221.3765 | 8123701.7665 | 0 | 69135679.5636 | 112651789.3472 | 10000000 | 22.1761 | 3117.575 | 5079.8721 | 63.556 | 103.5601
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.074752 | 0.0084071 | 4 | 686306.1418 | 2013281.9555 | 13991.279 | 41043.4758 | 86.8042 | 15.5672 | 24.8068 | 222108.4604 | 0 | 99624.0936 | 0 | 0 | 0 | 197608.0641 | 202542.8411 | 526974.9252 | 359671.2147 | 1608529.599 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 23079258.7518 | 67703102.6832 | 100 | 0.033628 | 686306.1418 | 2013281.9555 | 13991.279 | 41043.4758
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.2562 | 0.022675 | 4 | 269155.7577 | 761142.1886 | 5487.1042 | 15516.913 | 106.1129 | 16.6922 | 47.341 | 402814.9651 | 0 | 201572.2096 | 0 | 0 | 0 | 345508.2914 | 370459.2318 | 963858.9295 | 657853.5247 | 2942067.1521 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 24412796.3048 | 69036640.2362 | 133.3521 | 0.090701 | 269155.7577 | 761142.1886 | 5487.1042 | 15516.913
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9728 | 0.4554 | 0.042456 | 4 | 149364.6058 | 412130.09 | 3044.9995 | 8401.8293 | 115.229 | 17.1305 | 51.6947 | 543440.953 | 0 | 274416.1887 | 0 | 0 | 0 | 439689.8647 | 490443.3325 | 1276032.9474 | 870918.7065 | 3894941.9928 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 25365671.1456 | 69989515.0769 | 177.8279 | 0.16982 | 149364.6058 | 412130.09 | 3044.9995 | 8401.8293
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3003 | 0.72105 | 0.071117 | 4 | 92752.371 | 249620.6854 | 1890.8825 | 5088.8553 | 122.3459 | 17.4375 | 60.7225 | 702751.2372 | 0 | 345596.9059 | 0 | 0 | 0 | 538299.7159 | 618792.665 | 1609971.5825 | 1098838.6867 | 4914250.7933 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 26384979.946 | 71008823.8774 | 237.1374 | 0.28447 | 92752.371 | 249620.6854 | 1890.8825 | 5088.8553
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9734 | 1.0727 | 0.11068 | 4 | 62252.3214 | 163048.0446 | 1269.0978 | 3323.9549 | 128.0887 | 17.6646 | 65.8232 | 888225.6403 | 0 | 430416.4997 | 0 | 0 | 0 | 647405.3575 | 766758.5241 | 1994948.3958 | 1361593.2722 | 6089347.6897 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 27560076.8425 | 72183920.7739 | 316.2278 | 0.44272 | 62252.3214 | 163048.0446 | 1269.0978 | 3323.9549
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0929 | 1.5321 | 0.16415 | 4 | 44051.8184 | 112011.9554 | 898.0559 | 2283.5152 | 132.7183 | 17.8342 | 68.1251 | 1105104.8601 | 0 | 532222.1956 | 0 | 0 | 0 | 769477.5679 | 938653.8032 | 2442184.6516 | 1666841.2066 | 7454484.285 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 28925213.4377 | 73549057.3691 | 421.6965 | 0.65662 | 44051.8184 | 112011.9554 | 898.0559 | 2283.5152
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7756 | 2.1252 | 0.23545 | 4 | 32398.1305 | 79779.051 | 660.4797 | 1626.4039 | 136.4256 | 17.9602 | 59.4788 | 1358725.7826 | 0 | 654511.9473 | 0 | 0 | 0 | 906176.8062 | 1138571.6691 | 2962329.9297 | 2021851.0468 | 9042167.1816 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 30512896.3344 | 75136740.2658 | 562.3413 | 0.94181 | 32398.1305 | 79779.051 | 660.4797 | 1626.4039
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1829 | 2.8882 | 0.32967 | 4 | 24548.8324 | 58388.8819 | 500.4612 | 1190.3363 | 139.3859 | 18.0515 | 72.501 | 1656685.8705 | 0 | 802077.6074 | 0 | 0 | 0 | 1060828.6593 | 1372640.9335 | 3571330.1416 | 2437506.2052 | 10901069.4175 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 32371798.5703 | 76995642.5017 | 749.8942 | 1.3187 | 24548.8324 | 58388.8819 | 500.4612 | 1190.3363
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4903 | 3.8616 | 0.45308 | 4 | 19058.2348 | 43680.5492 | 388.5279 | 890.4871 | 141.7222 | 18.1127 | 67.0567 | 2005514.5103 | 0 | 979462.5943 | 0 | 0 | 0 | 1234615.1933 | 1645640.9962 | 4281620.3046 | 2922293.8364 | 13069147.435 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 34539876.5878 | 79163720.5192 | 1000 | 1.8123 | 19058.2348 | 43680.5492 | 388.5279 | 890.4871
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8734 | 5.0876 | 0.61303 | 4 | 15104.595 | 33302.687 | 307.9276 | 678.9203 | 143.5321 | 18.1452 | 73.892 | 2409814.6964 | 0 | 1190476.168 | 0 | 0 | 0 | 1425936.034 | 1960228.4904 | 5100112.4338 | 3480931.5329 | 15567499.3554 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 37038228.5082 | 81662072.4396 | 1333.5214 | 2.4521 | 15104.595 | 33302.687 | 307.9276 | 678.9203
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.5561 | 6.6194 | 0.81814 | 4 | 12192.8386 | 25828.5364 | 248.5675 | 526.5497 | 144.9082 | 18.1475 | 62.8159 | 2875922.3644 | 0 | 1440120.056 | 0 | 0 | 0 | 1634794.0296 | 2320826.2155 | 6038313.7458 | 4121273.2064 | 18431249.6176 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 39901978.7704 | 84525822.7018 | 1778.2794 | 3.2726 | 12192.8386 | 25828.5364 | 248.5675 | 526.5497
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.7339 | 8.5054 | 1.0772 | 4 | 10010.8459 | 20366.8382 | 204.0846 | 415.2055 | 145.912 | 18.1148 | 60.6251 | 3406175.1244 | 0 | 1731654.7793 | 0 | 0 | 0 | 1857362.1172 | 2728124.8882 | 7098021.3436 | 4844545.4168 | 21665883.6695 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 43136612.8223 | 87760456.7537 | 2371.3737 | 4.309 | 10010.8459 | 20366.8382 | 204.0846 | 415.2055
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.524 | 10.778 | 1.3975 | 4 | 8354.864 | 16337.4053 | 170.3252 | 333.0601 | 146.5822 | 18.039 | 86.9672 | 3996718.4689 | 0 | 2065306.6522 | 0 | 0 | 0 | 2085343.2916 | 3177473.6809 | 8267134.7283 | 5642489.3247 | 25234466.1467 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 46705195.2995 | 91329039.2308 | 3162.2777 | 5.5902 | 8354.864 | 16337.4053 | 170.3252 | 333.0601
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8197 | 13.42 | 1.7805 | 4 | 7088.3201 | 13353.9649 | 144.505 | 272.2386 | 146.9336 | 17.9113 | 77.0907 | 4630841.9358 | 0 | 2434265.723 | 0 | 0 | 0 | 2301964.2547 | 3653158.0463 | 9504767.8707 | 6487199.3752 | 29012197.2059 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 50482926.3586 | 95106770.29 | 4216.965 | 7.122 | 7088.3201 | 13353.9649 | 144.505 | 272.2386
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.2675 | 16.3557 | 2.2185 | 4 | 6116.9449 | 11145.5855 | 124.7022 | 227.2178 | 146.9718 | 17.7247 | 98.3881 | 5281121.5748 | 0 | 2825278.7996 | 0 | 0 | 0 | 2487068.39 | 4131452.8181 | 10749192.7553 | 7336544.9293 | 32810659.2671 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 54281388.4199 | 98905232.3513 | 5623.4133 | 8.8739 | 6116.9449 | 11145.5855 | 124.7022 | 227.2178
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.1982 | 19.4321 | 2.6917 | 4 | 5373.4551 | 9518.0795 | 109.5452 | 194.0389 | 146.7178 | 17.4833 | 82.7028 | 5909845.9364 | 0 | 3217591.0259 | 0 | 0 | 0 | 2619596.3895 | 4581343.0072 | 11919714.7421 | 8135450.2371 | 36383541.3382 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 57854270.491 | 102478114.4224 | 7498.9421 | 10.7667 | 5373.4551 | 9518.0795 | 109.5452 | 194.0389
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.8628 | 22.4715 | 3.1728 | 4 | 4806.5522 | 8322.6695 | 97.9881 | 169.6689 | 146.2246 | 17.2002 | 106.7459 | 6483472.8235 | 0 | 3590530.9783 | 0 | 0 | 0 | 2689018.1934 | 4977578.5781 | 12950638.4186 | 8839076.8297 | 39530315.8216 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 61001044.9744 | 105624888.9058 | 10000 | 12.6912 | 4806.5522 | 8322.6695 | 97.9881 | 169.6689
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.5561 | 25.3016 | 3.633 | 4 | 4376.2762 | 7447.0085 | 89.2163 | 151.8173 | 145.5767 | 16.8983 | 94.1514 | 6978068.671 | 0 | 3926434.9787 | 0 | 0 | 0 | 2696340.4526 | 5304329.1999 | 13800776.5105 | 9419313.546 | 42125263.3587 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 63595992.5115 | 108219836.4429 | 13335.2143 | 14.532 | 4376.2762 | 7447.0085 | 89.2163 | 151.8173
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7996 | 27.801 | 4.0493 | 4 | 4050.9914 | 6805.9941 | 82.5849 | 138.7494 | 144.8663 | 16.6019 | 98.9504 | 7384466.5712 | 0 | 4214876.275 | 0 | 0 | 0 | 2653524.8874 | 5558618.4161 | 14462384.8893 | 9870874.8592 | 44144745.8982 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 65615475.051 | 110239318.9824 | 17782.7941 | 16.1974 | 4050.9914 | 6805.9941 | 82.5849 | 138.7494
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4159 | 29.9187 | 4.4092 | 4 | 3805.7745 | 6335.9117 | 77.5859 | 129.1661 | 144.1688 | 16.3294 | 113.6446 | 7707033.9158 | 0 | 4453714.1839 | 0 | 0 | 0 | 2578579.7969 | 5748337.8797 | 14955996.0167 | 10207774.5964 | 45651436.3894 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 67122165.5422 | 111746009.4736 | 23713.7371 | 17.6369 | 3805.7745 | 6335.9117 | 77.5859 | 129.1661
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4 | 31.647 | 4.7085 | 4 | 3621.2362 | 5990.5642 | 73.8238 | 122.1258 | 143.5368 | 16.0929 | 109.1769 | 7955535.9853 | 0 | 4644979.6855 | 0 | 0 | 0 | 2487531.8188 | 5884338.5209 | 15309841.7877 | 10449281.6059 | 46731509.404 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 68202238.5568 | 112826082.4882 | 31622.7766 | 18.834 | 3621.2362 | 5990.5642 | 73.8238 | 122.1258
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9586 | 33.0299 | 4.9511 | 4 | 3482.4905 | 5735.7288 | 70.9953 | 116.9306 | 142.9911 | 15.8946 | 110.9562 | 8144945.7391 | 0 | 4795807.9505 | 0 | 0 | 0 | 2394642.2055 | 5980804.3991 | 15560826.2147 | 10620583.6345 | 47497610.1433 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 68968339.296 | 113592183.2274 | 42169.6503 | 19.8043 | 3482.4905 | 5735.7288 | 70.9953 | 116.9306
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2977 | 34.1145 | 5.1435 | 4 | 3378.2229 | 5547.1677 | 68.8696 | 113.0865 | 142.5386 | 15.7336 | 112.6714 | 8287580.4209 | 0 | 4912724.3039 | 0 | 0 | 0 | 2307881.7616 | 6048192.7297 | 15736156.8277 | 10740250.3806 | 48032786.4243 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 69503515.5771 | 114127359.5084 | 56234.1325 | 20.574 | 3378.2229 | 5547.1677 | 68.8696 | 113.0865
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.6493 | 34.9552 | 5.2939 | 4 | 3299.8864 | 5407.2029 | 67.2726 | 110.2331 | 142.1728 | 15.6054 | 113.8562 | 8394585.3409 | 0 | 5002558.4007 | 0 | 0 | 0 | 2231729.0899 | 6095260.4043 | 15858617.2621 | 10823832.1434 | 48406582.6414 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 69877311.7941 | 114501155.7255 | 74989.4209 | 21.1757 | 3299.8864 | 5407.2029 | 67.2726 | 110.2331
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.2 | 35.5974 | 5.4099 | 4 | 3241.0438 | 5303.1801 | 66.0731 | 108.1125 | 141.8849 | 15.5057 | 116.3625 | 8474145.0432 | 0 | 5070654.7884 | 0 | 0 | 0 | 2167257.0029 | 6127702.1655 | 15943024.07 | 10881441.5242 | 48664224.5942 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70134953.747 | 114758797.6784 | 100000 | 21.6396 | 3241.0438 | 5303.1801 | 66.0731 | 108.1125
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1512 | 36.0895 | 5.499 | 4 | 3196.8529 | 5225.5653 | 65.1722 | 106.5302 | 141.6591 | 15.4281 | 109.3276 | 8533907.7953 | 0 | 5122594.2791 | 0 | 0 | 0 | 2114793.0222 | 6150805.0877 | 16003133.1345 | 10922467.1958 | 48847700.5147 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70318429.6674 | 114942273.5988 | 133352.1432 | 21.9961 | 3196.8529 | 5225.5653 | 65.1722 | 106.5302
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.625 | 36.4619 | 5.5669 | 4 | 3163.6723 | 5167.6581 | 64.4957 | 105.3497 | 141.4852 | 15.3687 | 108.9368 | 8578407.7684 | 0 | 5161737.0648 | 0 | 0 | 0 | 2072731.0833 | 6167021.6074 | 16045325.1925 | 10951264.1423 | 48976486.8587 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70447216.0115 | 115071059.9428 | 177827.941 | 22.2675 | 3163.6723 | 5167.6581 | 64.4957 | 105.3497
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.7434 | 36.7448 | 5.6185 | 4 | 3138.7638 | 5124.3482 | 63.9879 | 104.4668 | 141.3514 | 15.3232 | 117.5336 | 8611807.4448 | 0 | 5191389.873 | 0 | 0 | 0 | 2039730.4462 | 6178741.828 | 16075818.8022 | 10972076.6575 | 49069565.0517 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70540294.2045 | 115164138.1358 | 237137.3706 | 22.4739 | 3138.7638 | 5124.3482 | 63.9879 | 104.4668
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5929 | 36.9598 | 5.6576 | 4 | 3120.0688 | 5091.9116 | 63.6068 | 103.8055 | 141.2487 | 15.2884 | 124.1817 | 8636966.1128 | 0 | 5213886.4324 | 0 | 0 | 0 | 2014194.141 | 6187368.2076 | 16098262.8724 | 10987395.1967 | 49138072.9628 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70608802.1156 | 115232646.047 | 316227.766 | 22.6305 | 3120.0688 | 5091.9116 | 63.6068 | 103.8055
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.2191 | 37.1188 | 5.6869 | 4 | 3106.0396 | 5067.7212 | 63.3208 | 103.3124 | 141.1723 | 15.2626 | 123.0507 | 8655390.923 | 0 | 5230454.4138 | 0 | 0 | 0 | 1994251.1969 | 6193237.6481 | 16113533.9527 | 10997818.0228 | 49184686.1574 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70655415.3101 | 115279259.2415 | 421696.5034 | 22.7478 | 3106.0396 | 5067.7212 | 63.3208 | 103.3124
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.6944 | 37.2393 | 5.7091 | 4 | 3095.5134 | 5049.5785 | 63.1062 | 102.9425 | 141.114 | 15.2429 | 115.6985 | 8669307.8263 | 0 | 5243019.8245 | 0 | 0 | 0 | 1979075.5893 | 6197647.2636 | 16125006.8677 | 11005648.523 | 49219705.8943 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70690435.0471 | 115314278.9785 | 562341.3252 | 22.8364 | 3095.5134 | 5049.5785 | 63.1062 | 102.9425
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.0498 | 37.3296 | 5.7258 | 4 | 3087.6165 | 5035.9987 | 62.9452 | 102.6656 | 141.0702 | 15.2282 | 108.6964 | 8679677.7781 | 0 | 5252412.4934 | 0 | 0 | 0 | 1967487.5632 | 6200835.3555 | 16133301.6289 | 11011309.8679 | 49245024.6871 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70715753.8399 | 115339597.7713 | 749894.2093 | 22.903 | 3087.6165 | 5035.9987 | 62.9452 | 102.6656
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.323 | 37.3989 | 5.7384 | 4 | 3081.6926 | 5025.7835 | 62.8245 | 102.4574 | 141.0365 | 15.2168 | 115.1625 | 8687627.2733 | 0 | 5259628.9006 | 0 | 0 | 0 | 1958817.9951 | 6203368.9259 | 16139893.4592 | 11015808.9275 | 49265145.4815 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70735874.6343 | 115359718.5657 | 1000000 | 22.9536 | 3081.6926 | 5025.7835 | 62.8245 | 102.4574
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5297 | 37.4512 | 5.7479 | 4 | 3077.2492 | 5018.1178 | 62.7339 | 102.3011 | 141.0109 | 15.2082 | 114.9185 | 8693629.1867 | 0 | 5265087.0301 | 0 | 0 | 0 | 1952290.0014 | 6205292.4251 | 16144898.0097 | 11019224.6361 | 49280421.2891 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70751150.4419 | 115374994.3732 | 1333521.4322 | 22.9917 | 3077.2492 | 5018.1178 | 62.7339 | 102.3011
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6734 | 37.488 | 5.7549 | 4 | 3073.9165 | 5012.4444 | 62.6659 | 102.1855 | 140.993 | 15.2022 | 121.1428 | 8697793.6966 | 0 | 5268881.3841 | 0 | 0 | 0 | 1947144.0291 | 6206389.4528 | 16147752.2507 | 11021172.7142 | 49289133.5274 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70759862.6802 | 115383706.6115 | 1778279.41 | 23.0194 | 3073.9165 | 5012.4444 | 62.6659 | 102.1855
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7808 | 37.5154 | 5.7601 | 4 | 3071.4169 | 5008.1938 | 62.615 | 102.0988 | 140.9796 | 15.1977 | 108.5048 | 8700902.9462 | 0 | 5271717.0982 | 0 | 0 | 0 | 1943259.3137 | 6207192.9496 | 16149842.7846 | 11022599.5466 | 49295514.6389 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70766243.7917 | 115390087.7231 | 2371373.7057 | 23.0403 | 3071.4169 | 5008.1938 | 62.615 | 102.0988
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.8781 | 37.5398 | 5.7643 | 4 | 3069.5423 | 5004.9019 | 62.5768 | 102.0317 | 140.9676 | 15.1937 | 118.0595 | 8703718.3783 | 0 | 5274283.5796 | 0 | 0 | 0 | 1940653.2562 | 6208275.5335 | 16152659.4457 | 11024521.9757 | 49304112.169 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70774841.3217 | 115398685.2531 | 3162277.6602 | 23.0571 | 3069.5423 | 5004.9019 | 62.5768 | 102.0317
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.9318 | 37.5537 | 5.7671 | 4 | 3068.1364 | 5002.5553 | 62.5481 | 101.9839 | 140.9608 | 15.1914 | 113.1978 | 8705269.0619 | 0 | 5275701.1212 | 0 | 0 | 0 | 1938326.7476 | 6208525.803 | 16153310.5956 | 11024966.3988 | 49306099.7281 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70776828.8809 | 115400672.8123 | 4216965.0343 | 23.0683 | 3068.1364 | 5002.5553 | 62.5481 | 101.9839
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.9829 | 37.5666 | 5.7694 | 4 | 3067.082 | 5000.7275 | 62.5266 | 101.9466 | 140.9545 | 15.1893 | 120.7186 | 8706746.5786 | 0 | 5277049.9086 | 0 | 0 | 0 | 1936784.8923 | 6209026.738 | 16154613.9258 | 11025855.9485 | 49310077.9918 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70780807.1445 | 115404651.0759 | 5623413.2519 | 23.0776 | 3067.082 | 5000.7275 | 62.5266 | 101.9466
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.0218 | 37.5764 | 5.7711 | 4 | 3066.2913 | 4999.3535 | 62.5105 | 101.9186 | 140.9496 | 15.1877 | 122.9073 | 8707870.6251 | 0 | 5278076.2792 | 0 | 0 | 0 | 1935637.416 | 6209417.8849 | 16155631.6098 | 11026550.5387 | 49313184.3536 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70783913.5064 | 115407757.4378 | 7498942.0933 | 23.0845 | 3066.2913 | 4999.3535 | 62.5105 | 101.9186
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.0561 | 37.5849 | 5.7725 | 4 | 3065.6984 | 4998.2912 | 62.4984 | 101.8969 | 140.9454 | 15.1862 | 115.6912 | 8708861.502 | 0 | 5278980.4215 | 0 | 0 | 0 | 1934872.6412 | 6209858.6802 | 16156778.4687 | 11027333.2935 | 49316685.007 | 961560.8286 | 20509168.3242 | 20509168.3242 | 15798354.3283 | 8316321.2789 | 0 | 70787414.1598 | 115411258.0911 | 10000000 | 23.0901 | 3065.6984 | 4998.2912 | 62.4984 | 101.8969
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.073729 | 0.0086736 | 4 | 681589.1916 | 2000104.935 | 13895.1176 | 40774.8444 | 87.4697 | 15.937 | 24.8342 | 224643.796 | 0 | 99374.8798 | 0 | 0 | 0 | 199632.171 | 204223.8302 | 531348.5141 | 362656.279 | 1621879.4701 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 23647450.3973 | 69392799.6899 | 100 | 0.034695 | 681589.1916 | 2000104.935 | 13895.1176 | 40774.8444
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9787 | 0.26877 | 0.024212 | 4 | 259168.3686 | 731519.4079 | 5283.4977 | 14913.0126 | 108.4252 | 17.1559 | 44.9144 | 421303.4576 | 0 | 209296.8332 | 0 | 0 | 0 | 361850.2912 | 387055.727 | 1007039.6055 | 687325.2233 | 3073871.1377 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 25099442.0649 | 70844791.3575 | 133.3521 | 0.096846 | 259168.3686 | 731519.4079 | 5283.4977 | 14913.0126
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0971 | 0.47696 | 0.045386 | 4 | 143660.748 | 395637.5049 | 2928.7187 | 8065.6057 | 117.768 | 17.6007 | 56.7869 | 568016.1594 | 0 | 281262.2163 | 0 | 0 | 0 | 460091.3554 | 510654.1951 | 1328617.4661 | 906808.721 | 4055450.1132 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 26081021.0404 | 71826370.333 | 177.8279 | 0.18155 | 143660.748 | 395637.5049 | 2928.7187 | 8065.6057
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4607 | 0.75423 | 0.075932 | 4 | 89348.1817 | 239961.3034 | 1821.4835 | 4891.9357 | 125.055 | 17.912 | 57.3632 | 733902.1511 | 0 | 353943.2829 | 0 | 0 | 0 | 562626.5694 | 643684.0813 | 1674733.9418 | 1143040.3276 | 5111930.3542 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 27137501.2813 | 72882850.574 | 237.1374 | 0.30373 | 89348.1817 | 239961.3034 | 1821.4835 | 4891.9357
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1781 | 1.1211 | 0.11803 | 4 | 60056.3447 | 156948.6768 | 1224.3298 | 3199.6111 | 130.9365 | 18.1422 | 65.8187 | 926862.204 | 0 | 440493.275 | 0 | 0 | 0 | 675927.6952 | 796880.4379 | 2073319.4368 | 1415083.1181 | 6328566.167 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 28354137.0941 | 74099486.3868 | 316.2278 | 0.47213 | 60056.3447 | 156948.6768 | 1224.3298 | 3199.6111
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3512 | 1.5998 | 0.17489 | 4 | 42550.4549 | 107943.5958 | 867.4486 | 2200.5762 | 135.6788 | 18.3143 | 58.9762 | 1152315.5248 | 0 | 544287.0543 | 0 | 0 | 0 | 802490.4666 | 974646.2878 | 2535829.7134 | 1730755.8855 | 7740324.9323 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 29765895.8595 | 75511245.1521 | 421.6965 | 0.69954 | 42550.4549 | 107943.5958 | 867.4486 | 2200.5762
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1091 | 2.2192 | 0.25069 | 4 | 31327.6246 | 76947.9552 | 638.656 | 1568.6881 | 139.4884 | 18.4422 | 61.428 | 1416690.6286 | 0 | 669302.9588 | 0 | 0 | 0 | 945047.9816 | 1182106.2119 | 3075597.88 | 2099158.7503 | 9387904.4111 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 31413475.3383 | 77158824.6309 | 562.3413 | 1.0027 | 31327.6246 | 76947.9552 | 638.656 | 1568.6881
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.6071 | 3.0152 | 0.35078 | 4 | 23760.6708 | 56363.3543 | 484.3934 | 1149.0432 | 142.5267 | 18.5345 | 55.96 | 1726873.6056 | 0 | 819953.7204 | 0 | 0 | 0 | 1105895.2828 | 1424561.8174 | 3706417.6311 | 2529706.1925 | 11313408.2498 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 33338979.1769 | 79084328.4696 | 749.8942 | 1.4031 | 23760.6708 | 56363.3543 | 484.3934 | 1149.0432
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.0286 | 4.0306 | 0.48184 | 4 | 18462.9495 | 42197.8 | 376.3922 | 860.2592 | 144.9251 | 18.5959 | 67.2167 | 2090014.4354 | 0 | 1001042.3682 | 0 | 0 | 0 | 1286687.1446 | 1707320.1398 | 4442096.7841 | 3031822.3311 | 13558983.2031 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 35584554.1303 | 81329903.4229 | 1000 | 1.9273 | 18462.9495 | 42197.8 | 376.3922 | 860.2592
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.5534 | 5.3094 | 0.6516 | 4 | 14645.4032 | 32196.5904 | 298.5664 | 656.371 | 146.7831 | 18.6274 | 65.3486 | 2510862.8679 | 0 | 1216439.8251 | 0 | 0 | 0 | 1485752.4605 | 2033091.5099 | 5289687.0643 | 3610320.1136 | 16146153.8413 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 38171724.7685 | 83917074.0611 | 1333.5214 | 2.6064 | 14645.4032 | 32196.5904 | 298.5664 | 656.371
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4233 | 6.9095 | 0.86931 | 4 | 11832.1903 | 24987.8135 | 241.2152 | 509.4104 | 148.1973 | 18.6273 | 78.2753 | 2996828.6965 | 0 | 1471694.3767 | 0 | 0 | 0 | 1704002.0816 | 2407284.8104 | 6263261.2746 | 4274804.5171 | 19117875.757 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 41143446.6842 | 86888795.9768 | 1778.2794 | 3.4772 | 11832.1903 | 24987.8135 | 241.2152 | 509.4104
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.7861 | 8.8705 | 1.1436 | 4 | 9723.1059 | 19723.3896 | 198.2187 | 402.088 | 149.2229 | 18.5903 | 60.6763 | 3546780.9025 | 0 | 1768244.6082 | 0 | 0 | 0 | 1933930.5454 | 2827092.8619 | 7355515.7101 | 5020290.6129 | 22451855.2409 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 44477426.1681 | 90222775.4607 | 2371.3737 | 4.5744 | 9723.1059 | 19723.3896 | 198.2187 | 402.088
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.766 | 11.2266 | 1.4818 | 4 | 8122.0906 | 15839.8518 | 165.5798 | 322.9168 | 149.9049 | 18.5081 | 82.6183 | 4157415.1713 | 0 | 2106642.6614 | 0 | 0 | 0 | 2168042.5316 | 3288519.1421 | 8556052.2397 | 5839681.4629 | 26116353.209 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 48141924.1362 | 93887273.4288 | 3162.2777 | 5.9273 | 8122.0906 | 15839.8518 | 165.5798 | 322.9168
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2741 | 13.9639 | 1.8854 | 4 | 6897.6714 | 12963.3671 | 140.6184 | 264.2758 | 150.2592 | 18.3711 | 75.0125 | 4812738.3028 | 0 | 2480722.2797 | 0 | 0 | 0 | 2390682.5746 | 3776815.8312 | 9826500.0614 | 6706788.2063 | 29994247.2559 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 52019818.1831 | 97765167.4757 | 4216.965 | 7.5416 | 6897.6714 | 12963.3671 | 140.6184 | 264.2758
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.905 | 16.9938 | 2.3452 | 4 | 5958.9493 | 10835.4095 | 121.4812 | 220.8945 | 150.2902 | 18.1726 | 91.237 | 5481992.0842 | 0 | 2875682.7309 | 0 | 0 | 0 | 2579256.0805 | 4265403.0493 | 11097703.7798 | 7574410.8647 | 33874448.5895 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 55900019.5167 | 101645368.8093 | 5623.4133 | 9.3809 | 5958.9493 | 10835.4095 | 121.4812 | 220.8945
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9692 | 20.1557 | 2.8397 | 4 | 5240.8706 | 9268.1313 | 106.8422 | 188.9434 | 150.022 | 17.9179 | 76.266 | 6126196.5909 | 0 | 3270371.0423 | 0 | 0 | 0 | 2712573.2887 | 4722564.9595 | 12287145.2934 | 8386229.1383 | 37505080.3131 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 59530651.2402 | 105276000.5329 | 7498.9421 | 11.3589 | 5240.8706 | 9268.1313 | 106.8422 | 188.9434
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6876 | 23.2615 | 3.3398 | 4 | 4693.6906 | 8117.9454 | 95.6872 | 165.4953 | 149.5133 | 17.6219 | 94.7771 | 6710415.856 | 0 | 3643451.9525 | 0 | 0 | 0 | 2779845.5422 | 5122148.2068 | 13326778.937 | 9095800.4624 | 40678440.957 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 62704011.8841 | 108449361.1768 | 10000 | 13.3592 | 4693.6906 | 8117.9454 | 95.6872 | 165.4953
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3855 | 26.1426 | 3.816 | 4 | 4278.6324 | 7275.5847 | 87.2257 | 148.3226 | 148.8518 | 17.3082 | 95.7381 | 7212301.6552 | 0 | 3978326.9918 | 0 | 0 | 0 | 2784102.5577 | 5450145.1699 | 14180159.7535 | 9678250.4049 | 43283286.5331 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 65308857.4602 | 111054206.7529 | 13335.2143 | 15.264 | 4278.6324 | 7275.5847 | 87.2257 | 148.3226
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.5823 | 28.6751 | 4.2448 | 4 | 3965.0125 | 6659.2116 | 80.8321 | 135.757 | 148.1328 | 17.0023 | 118.462 | 7622770.9655 | 0 | 4264561.8018 | 0 | 0 | 0 | 2737615.4376 | 5703729.7999 | 14839934.9435 | 10128560.5291 | 45297173.4775 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 67322744.4047 | 113068093.6973 | 17782.7941 | 16.9792 | 3965.0125 | 6659.2116 | 80.8321 | 135.757
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1233 | 30.8122 | 4.614 | 4 | 3728.6871 | 6207.3042 | 76.0143 | 126.5443 | 147.4315 | 16.7229 | 109.5031 | 7947361.8597 | 0 | 4500659.9846 | 0 | 0 | 0 | 2659254.5014 | 5891837.7748 | 15329353.308 | 10462598.6194 | 46791066.048 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 68816636.9752 | 114561986.2678 | 23713.7371 | 18.456 | 3728.6871 | 6207.3042 | 76.0143 | 126.5443
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.054 | 32.5578 | 4.9206 | 4 | 3550.8987 | 5875.0577 | 72.3899 | 119.771 | 146.7965 | 16.4804 | 104.1512 | 8197814.7617 | 0 | 4689984.8958 | 0 | 0 | 0 | 2566257.1105 | 6027082.1395 | 15681231.4025 | 10702762.6493 | 47865132.9592 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 69890703.8864 | 115636053.179 | 31622.7766 | 19.6825 | 3550.8987 | 5875.0577 | 72.3899 | 119.771
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.5398 | 33.9475 | 5.1683 | 4 | 3417.2636 | 5630.0574 | 69.6655 | 114.7763 | 146.2518 | 16.2784 | 97.2185 | 8387752.8512 | 0 | 4838495.0821 | 0 | 0 | 0 | 2471505.5975 | 6122123.877 | 15928510.5077 | 10871535.7197 | 48619923.6352 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 70645494.5624 | 116390843.855 | 42169.6503 | 20.6731 | 3417.2636 | 5630.0574 | 69.6655 | 114.7763
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8371 | 35.0406 | 5.3648 | 4 | 3316.8587 | 5448.595 | 67.6187 | 111.077 | 145.799 | 16.114 | 104.2315 | 8531351.5888 | 0 | 4954034.6434 | 0 | 0 | 0 | 2384014.088 | 6189066.1249 | 16102680.5049 | 10990410.3216 | 49151557.2716 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 71177128.1988 | 116922477.4914 | 56234.1325 | 21.4592 | 3316.8587 | 5448.595 | 67.6187 | 111.077
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.1233 | 35.8805 | 5.5177 | 4 | 3241.4385 | 5314.1172 | 66.0811 | 108.3355 | 145.4368 | 15.9845 | 113.5582 | 8638048.0608 | 0 | 5041937.4367 | 0 | 0 | 0 | 2306776.4537 | 6234837.161 | 16221767.3519 | 11071689.5416 | 49515056.0057 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 71540626.9329 | 117285976.2255 | 74989.4209 | 22.0706 | 3241.4385 | 5314.1172 | 66.0811 | 108.3355
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6519 | 36.5282 | 5.636 | 4 | 3184.7956 | 5213.9534 | 64.9264 | 106.2935 | 145.1488 | 15.8826 | 100.1784 | 8718292.6021 | 0 | 5109315.0202 | 0 | 0 | 0 | 2242269.9941 | 6267252.2704 | 16306104.8174 | 11129251.5948 | 49772486.299 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 71798057.2262 | 117543406.5188 | 100000 | 22.544 | 3184.7956 | 5213.9534 | 64.9264 | 106.2935
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5667 | 37.02 | 5.7265 | 4 | 3142.2625 | 5139.3461 | 64.0593 | 104.7725 | 144.9252 | 15.8042 | 101.1272 | 8777971.5711 | 0 | 5160188.8859 | 0 | 0 | 0 | 2189459.9702 | 6289771.9666 | 16364696.4474 | 11169241.5863 | 49951330.4275 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 71976901.3547 | 117722250.6473 | 133352.1432 | 22.9061 | 3142.2625 | 5139.3461 | 64.0593 | 104.7725
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.0212 | 37.3942 | 5.7956 | 4 | 3110.3303 | 5083.6219 | 63.4083 | 103.6365 | 144.7522 | 15.7439 | 108.4105 | 8822676.2915 | 0 | 5198750.0234 | 0 | 0 | 0 | 2147381.2687 | 6305834.9576 | 16406489.0551 | 11197765.8997 | 50078897.496 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72104468.4232 | 117849817.7158 | 177827.941 | 23.1823 | 3110.3303 | 5083.6219 | 63.4083 | 103.6365
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1265 | 37.6787 | 5.8481 | 4 | 3086.3613 | 5041.9327 | 62.9196 | 102.7866 | 144.6189 | 15.6976 | 122.8805 | 8856283.3459 | 0 | 5228005.0468 | 0 | 0 | 0 | 2114441.1559 | 6317504.524 | 16436850.873 | 11218488.4644 | 50171573.41 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72197144.3372 | 117942493.6298 | 237137.3706 | 23.3923 | 3086.3613 | 5041.9327 | 62.9196 | 102.7866
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.9501 | 37.8913 | 5.8876 | 4 | 3068.3727 | 5010.8112 | 62.5529 | 102.1522 | 144.5185 | 15.6629 | 121.7406 | 8881119.07 | 0 | 5249779.201 | 0 | 0 | 0 | 2088653.4924 | 6325625.1877 | 16457979.1744 | 11232908.9642 | 50236065.0897 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72261636.0169 | 118006985.3095 | 316227.766 | 23.5505 | 3068.3727 | 5010.8112 | 62.5529 | 102.1522
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5808 | 38.0539 | 5.9177 | 4 | 3054.8746 | 4987.4497 | 62.2778 | 101.6759 | 144.441 | 15.6361 | 120.8055 | 8900018.505 | 0 | 5266436.4967 | 0 | 0 | 0 | 2069012.9409 | 6331832.4976 | 16474129.3213 | 11243931.7713 | 50285361.5328 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72310932.4599 | 118056281.7526 | 421696.5034 | 23.6707 | 3054.8746 | 4987.4497 | 62.2778 | 101.6759
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.0366 | 38.172 | 5.94 | 4 | 3044.7473 | 4970.0722 | 62.0713 | 101.3216 | 144.3846 | 15.6167 | 111.407 | 8913609.5123 | 0 | 5278467.2644 | 0 | 0 | 0 | 2053619.2579 | 6335821.4535 | 16484507.7663 | 11251015.2733 | 50317040.5276 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72342611.4548 | 118087960.7475 | 562341.3252 | 23.7598 | 3044.7473 | 4970.0722 | 62.0713 | 101.3216
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3922 | 38.2638 | 5.957 | 4 | 3037.1499 | 4956.9723 | 61.9164 | 101.0546 | 144.3405 | 15.6016 | 115.2226 | 8924177.9849 | 0 | 5287848.739 | 0 | 0 | 0 | 2042165.9459 | 6339135.1412 | 16493129.3021 | 11256899.6486 | 50343356.7618 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72368927.6889 | 118114276.9816 | 749894.2093 | 23.8279 | 3037.1499 | 4956.9723 | 61.9164 | 101.0546
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6675 | 38.3346 | 5.9699 | 4 | 3031.451 | 4947.106 | 61.8002 | 100.8534 | 144.3062 | 15.5898 | 122.588 | 8932336.1915 | 0 | 5295106.5212 | 0 | 0 | 0 | 2033639.7402 | 6341822.1566 | 16500120.3649 | 11261671.1926 | 50364696.1671 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72390267.0943 | 118135616.3869 | 1000000 | 23.8797 | 3031.451 | 4947.106 | 61.8002 | 100.8534
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8675 | 38.3863 | 5.9795 | 4 | 3027.1763 | 4939.7529 | 61.7131 | 100.7035 | 144.2812 | 15.5812 | 109.9706 | 8938251.8308 | 0 | 5300379.9647 | 0 | 0 | 0 | 2027060.7153 | 6343620.0792 | 16504798.1908 | 11264863.9049 | 50378974.6858 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72404545.6129 | 118149894.9056 | 1333521.4322 | 23.9182 | 3027.1763 | 4939.7529 | 61.7131 | 100.7035
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.0159 | 38.4247 | 5.9867 | 4 | 3023.9702 | 4934.2523 | 61.6477 | 100.5914 | 144.2627 | 15.5749 | 127.9076 | 8942631.8364 | 0 | 5304290.0226 | 0 | 0 | 0 | 2022060.9456 | 6344903.2938 | 16508136.8518 | 11267142.6097 | 50389165.5599 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72414736.4871 | 118160085.7797 | 1778279.41 | 23.9469 | 3023.9702 | 4934.2523 | 61.6477 | 100.5914
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.1233 | 38.4526 | 5.992 | 4 | 3021.5657 | 4930.1528 | 61.5987 | 100.5078 | 144.2492 | 15.5702 | 115.3712 | 8945799.1244 | 0 | 5307120.9939 | 0 | 0 | 0 | 2018218.0389 | 6345743.8813 | 16510323.8881 | 11268635.3069 | 50395841.2336 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72421412.1608 | 118166761.4534 | 2371373.7057 | 23.9682 | 3021.5657 | 4930.1528 | 61.5987 | 100.5078
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.2009 | 38.4729 | 5.996 | 4 | 3019.7623 | 4927.0977 | 61.5619 | 100.4456 | 144.2394 | 15.5669 | 112.7154 | 8948084.9904 | 0 | 5309166.1796 | 0 | 0 | 0 | 2015268.3691 | 6346282.6202 | 16511725.5762 | 11269591.9878 | 50400119.7233 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72425690.6504 | 118171039.9431 | 3162277.6602 | 23.9839 | 3019.7623 | 4927.0977 | 61.5619 | 100.4456
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.2741 | 38.4915 | 5.9992 | 4 | 3018.4099 | 4924.7152 | 61.5344 | 100.397 | 144.2303 | 15.5638 | 108.9743 | 8950241.5783 | 0 | 5311093.767 | 0 | 0 | 0 | 2013341.8795 | 6347124.1176 | 16513914.9799 | 11271086.3008 | 50406802.6231 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72432373.5502 | 118177722.8429 | 4216965.0343 | 23.9969 | 3018.4099 | 4924.7152 | 61.5344 | 100.397
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.313 | 38.5018 | 6.0013 | 4 | 3017.3957 | 4923.0271 | 61.5137 | 100.3626 | 144.2254 | 15.5621 | 113.5825 | 8951384.6369 | 0 | 5312118.4891 | 0 | 0 | 0 | 2011582.7757 | 6347283.5016 | 16514329.6643 | 11271369.3314 | 50408068.399 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72433639.3261 | 118178988.6188 | 5623413.2519 | 24.0054 | 3017.3957 | 4923.0271 | 61.5137 | 100.3626
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3519 | 38.5117 | 6.0031 | 4 | 3016.635 | 4921.7015 | 61.4982 | 100.3355 | 144.2205 | 15.5604 | 117.4958 | 8952529.7939 | 0 | 5313143.1617 | 0 | 0 | 0 | 2010451.0934 | 6347688.3791 | 16515383.0725 | 11272088.3042 | 50411283.8047 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72436854.7319 | 118182204.0245 | 7498942.0933 | 24.0125 | 3016.635 | 4921.7015 | 61.4982 | 100.3355
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3861 | 38.5204 | 6.0046 | 4 | 3016.0647 | 4920.6763 | 61.4866 | 100.3146 | 144.2162 | 15.5589 | 110.3526 | 8953539.2764 | 0 | 5314045.8086 | 0 | 0 | 0 | 2009700.4372 | 6348141.3537 | 16516561.6194 | 11272892.6867 | 50414881.1821 | 961560.8286 | 21064010.0986 | 21064010.0986 | 16170054.3665 | 8511284.8276 | 0 | 72440452.1092 | 118185801.4019 | 10000000 | 24.0182 | 3016.0647 | 4920.6763 | 61.4866 | 100.3146
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.07271 | 0.0089247 | 4 | 678489.3626 | 1991711.8069 | 13831.9234 | 40603.7392 | 88.1085 | 16.3053 | 25.111 | 227122.5368 | 0 | 99118.2071 | 0 | 0 | 0 | 201667.6509 | 205884.274 | 535668.6482 | 365604.8593 | 1635066.1763 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 24221338.9688 | 71101964.8362 | 100 | 0.035699 | 678489.3626 | 1991711.8069 | 13831.9234 | 40603.7392
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0714 | 0.28163 | 0.025826 | 4 | 249685.871 | 703494.4066 | 5090.1842 | 14341.685 | 110.7396 | 17.6196 | 43.3243 | 440104.0994 | 0 | 217094.4037 | 0 | 0 | 0 | 378393.2883 | 403880.7986 | 1050814.9907 | 717202.8233 | 3207490.404 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 25793763.1965 | 72674389.0639 | 133.3521 | 0.1033 | 249685.871 | 703494.4066 | 5090.1842 | 14341.685
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.224 | 0.49938 | 0.048466 | 4 | 138276.8322 | 380099.6235 | 2818.9603 | 7748.8449 | 120.3275 | 18.0717 | 60.175 | 593345.3412 | 0 | 288208.8667 | 0 | 0 | 0 | 481125.7447 | 531445.1815 | 1382711.3479 | 943728.9068 | 4220565.3887 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 26806838.1812 | 73687464.0486 | 177.8279 | 0.19386 | 138276.8322 | 380099.6235 | 2818.9603 | 7748.8449
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6265 | 0.78902 | 0.080975 | 4 | 86147.741 | 230885.7954 | 1756.2382 | 4706.9192 | 127.7907 | 18.3874 | 51.4654 | 766189.5545 | 0 | 362513.2329 | 0 | 0 | 0 | 587967.3238 | 669501.3433 | 1741905.1617 | 1188886.0655 | 5316962.6817 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 27903235.4741 | 74783861.3415 | 237.1374 | 0.3239 | 86147.741 | 230885.7954 | 1756.2382 | 4706.9192
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3755 | 1.1692 | 0.12567 | 4 | 57991.4712 | 151255.1998 | 1182.2346 | 3083.5418 | 133.7692 | 18.6193 | 65.8761 | 965329.9979 | 0 | 450159.6368 | 0 | 0 | 0 | 703853.4434 | 826543.8005 | 2150497.4214 | 1467758.6784 | 6564142.9784 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 29150415.7709 | 76031041.6383 | 316.2278 | 0.50267 | 57991.4712 | 151255.1998 | 1182.2346 | 3083.5418
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.607 | 1.6684 | 0.18604 | 4 | 41138.2527 | 104136.0759 | 838.6589 | 2122.9548 | 138.6398 | 18.7943 | 66.3209 | 1200014.5866 | 0 | 556164.9165 | 0 | 0 | 0 | 835560.9722 | 1010778.7854 | 2629839.0603 | 1794919.1965 | 8027277.5175 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 30613550.31 | 77494176.1774 | 421.6965 | 0.74416 | 41138.2527 | 104136.0759 | 838.6589 | 2122.9548
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4575 | 2.3181 | 0.26661 | 4 | 30320.1004 | 74279.447 | 618.1163 | 1514.287 | 142.5728 | 18.9249 | 66.5721 | 1476962.5683 | 0 | 684664.2697 | 0 | 0 | 0 | 985911.0057 | 1227539.7591 | 3193806.65 | 2179838.6648 | 9748722.9177 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 32334995.7101 | 79215621.5775 | 562.3413 | 1.0665 | 30320.1004 | 74279.447 | 618.1163 | 1514.287
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0527 | 3.1491 | 0.37287 | 4 | 23018.4183 | 54450.634 | 469.2616 | 1110.0498 | 145.6877 | 19.0181 | 74.2069 | 1800029.1794 | 0 | 838630.6347 | 0 | 0 | 0 | 1153510.9451 | 1478946.5961 | 3847915.6693 | 2626281.511 | 11745314.5355 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 34331587.3279 | 81212213.1953 | 749.8942 | 1.4915 | 23018.4183 | 54450.634 | 469.2616 | 1110.0498
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5692 | 4.2037 | 0.5117 | 4 | 17901.9747 | 40806.1093 | 364.956 | 831.8877 | 148.1347 | 19.0791 | 54.2047 | 2176035.7982 | 0 | 1022603.0045 | 0 | 0 | 0 | 1339522.2056 | 1769882.7933 | 4604871.9752 | 3142919.7437 | 14055835.5206 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 36642108.313 | 83522734.1804 | 1000 | 2.0468 | 17901.9747 | 40806.1093 | 364.956 | 831.8877
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2501 | 5.5393 | 0.69178 | 4 | 14212.3695 | 31154.3424 | 289.7384 | 635.1234 | 150.0443 | 19.1096 | 76.7252 | 2614743.1571 | 0 | 1242903.8157 | 0 | 0 | 0 | 1547524.9909 | 2108017.0658 | 5484627.9916 | 3743371.3021 | 16741188.3232 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 39327461.1156 | 86208086.983 | 1333.5214 | 2.7671 | 14212.3695 | 31154.3424 | 289.7384 | 635.1234
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.2681 | 7.2011 | 0.92209 | 4 | 11491.8419 | 24202.2335 | 234.2767 | 493.3953 | 151.4886 | 19.1069 | 75.6216 | 3118076.0588 | 0 | 1502294.4392 | 0 | 0 | 0 | 1772354.603 | 2493162.7894 | 6486698.1599 | 4427304.7825 | 19799890.8327 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 42386163.6252 | 89266789.4926 | 1778.2794 | 3.6884 | 11491.8419 | 24202.2335 | 234.2767 | 493.3953
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8332 | 9.2422 | 1.2123 | 4 | 9451.3714 | 19119.4067 | 192.679 | 389.775 | 152.539 | 19.0654 | 81.7842 | 3689206.1817 | 0 | 1804469.708 | 0 | 0 | 0 | 2010954.1575 | 2926805.7184 | 7614948.1089 | 5197358.5558 | 23243742.4303 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 45830015.2227 | 92710641.0901 | 2371.3737 | 4.849 | 9451.3714 | 19119.4067 | 192.679 | 389.775
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0307 | 11.6894 | 1.5693 | 4 | 7902.1205 | 15370.3523 | 161.0954 | 313.3454 | 153.2341 | 18.9762 | 85.4477 | 4321842.7014 | 0 | 2148522.7314 | 0 | 0 | 0 | 2252853.0517 | 3402055.209 | 8851449.7963 | 6041296.3651 | 27018019.855 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 49604292.6474 | 96484918.5148 | 3162.2777 | 6.2773 | 7902.1205 | 15370.3523 | 161.0954 | 313.3454
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.7286 | 14.5189 | 1.9938 | 4 | 6717.3988 | 12595.6988 | 136.9433 | 256.7804 | 153.5899 | 18.8296 | 86.8468 | 4997240.8417 | 0 | 2526967.8629 | 0 | 0 | 0 | 2480246.6773 | 3901737.599 | 10151520.8761 | 6928621.5908 | 30986335.4478 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 53572608.2403 | 100453234.1077 | 4216.965 | 7.9752 | 6717.3988 | 12595.6988 | 136.9433 | 256.7804
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.5271 | 17.641 | 2.4756 | 4 | 5809.6182 | 10543.8752 | 118.4369 | 214.9512 | 153.614 | 18.6197 | 90.2646 | 5684838.025 | 0 | 2925396.0768 | 0 | 0 | 0 | 2671708.5066 | 4399957.6173 | 11447787.1647 | 7813349.9684 | 34943037.3589 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 57529310.1513 | 104409936.0187 | 5623.4133 | 9.9024 | 5809.6182 | 10543.8752 | 118.4369 | 214.9512
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.7083 | 20.8859 | 2.9916 | 4 | 5115.3274 | 9033.0644 | 104.2829 | 184.1512 | 153.3313 | 18.351 | 94.1409 | 6343743.7764 | 0 | 3321991.9753 | 0 | 0 | 0 | 2804997.2582 | 4863585.8739 | 12654052.7852 | 8636651.0407 | 38625022.7097 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 61211295.5021 | 108091921.3696 | 7498.9421 | 11.9663 | 5115.3274 | 9033.0644 | 104.2829 | 184.1512
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.4781 | 24.0582 | 3.5107 | 4 | 4586.7264 | 7925.1227 | 93.5066 | 161.5643 | 152.8076 | 18.0419 | 96.6547 | 6938457.0818 | 0 | 3695193.0246 | 0 | 0 | 0 | 2870079.8184 | 5266454.6707 | 13702234.7547 | 9352056.7729 | 41824476.1231 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 64410748.9155 | 111291374.7829 | 10000 | 14.0429 | 4586.7264 | 7925.1227 | 93.5066 | 161.5643
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.1707 | 26.9883 | 4.0028 | 4 | 4185.9948 | 7114.0049 | 85.3372 | 145.0286 | 152.1336 | 17.7165 | 103.7692 | 7447161.1966 | 0 | 4028803.1103 | 0 | 0 | 0 | 2870957.4726 | 5595299.494 | 14557821.5296 | 9936012.3273 | 44436055.1304 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 67022327.9229 | 113902953.7903 | 13335.2143 | 16.0111 | 4185.9948 | 7114.0049 | 85.3372 | 145.0286
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3339 | 29.5566 | 4.4443 | 4 | 3883.3505 | 6520.4911 | 79.1674 | 132.929 | 151.4056 | 17.4009 | 113.4135 | 7862140.5772 | 0 | 4313242.49 | 0 | 0 | 0 | 2821228.3568 | 5848678.4554 | 15217061.612 | 10385957.2295 | 46448308.7209 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 69034581.5133 | 115915207.3807 | 17782.7941 | 17.7771 | 3883.3505 | 6520.4911 | 79.1674 | 132.929
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.8166 | 31.7165 | 4.823 | 4 | 3655.3869 | 6085.4289 | 74.52 | 124.0597 | 150.6995 | 17.1139 | 110.6646 | 8189253.0309 | 0 | 4547095.8068 | 0 | 0 | 0 | 2739889.3321 | 6035732.8862 | 15703738.8709 | 10718124.459 | 47933834.3859 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 70520107.1783 | 117400733.0457 | 23713.7371 | 19.2921 | 3655.3869 | 6085.4289 | 74.52 | 124.0597
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.6734 | 33.4744 | 5.1366 | 4 | 3483.9435 | 5765.6563 | 71.0249 | 117.5407 | 150.0637 | 16.8663 | 117.8424 | 8440797.3198 | 0 | 4733946.3643 | 0 | 0 | 0 | 2644327.6077 | 6169437.8038 | 16051611.6397 | 10955554.7718 | 48995675.507 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 71581948.2995 | 118462574.1669 | 31622.7766 | 20.5462 | 3483.9435 | 5765.6563 | 71.0249 | 117.5407
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.1038 | 34.8743 | 5.3895 | 4 | 3355.1102 | 5529.7329 | 68.3985 | 112.7311 | 149.5187 | 16.6601 | 122.3052 | 8631757.2811 | 0 | 4880624.2347 | 0 | 0 | 0 | 2548093.8396 | 6263585.3886 | 16296564.3431 | 11122740.0251 | 49743365.1121 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 72329637.9046 | 119210263.772 | 42169.6503 | 21.5581 | 3355.1102 | 5529.7329 | 68.3985 | 112.7311
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3445 | 35.9724 | 5.5898 | 4 | 3258.3336 | 5355.0449 | 66.4255 | 109.1698 | 149.0673 | 16.4928 | 118.3811 | 8775743.7599 | 0 | 4994403.8313 | 0 | 0 | 0 | 2459458.7153 | 6329546.4595 | 16468181.5192 | 11239872.2741 | 50267206.5593 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 72853479.3518 | 119734105.2192 | 56234.1325 | 22.3591 | 3258.3336 | 5355.0449 | 66.4255 | 109.1698
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.5971 | 36.8182 | 5.7456 | 4 | 3185.6514 | 5225.4882 | 64.9438 | 106.5286 | 148.7055 | 16.3608 | 115.3347 | 8883087.4113 | 0 | 5081235.0878 | 0 | 0 | 0 | 2381798.3679 | 6374987.1381 | 16586408.8437 | 11320564.8525 | 50628081.7013 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73214354.4938 | 120094980.3612 | 74989.4209 | 22.9825 | 3185.6514 | 5225.4882 | 64.9438 | 106.5286
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.0797 | 37.4658 | 5.8658 | 4 | 3131.0732 | 5129.1155 | 63.8312 | 104.564 | 148.4202 | 16.2578 | 120.6226 | 8963193.9363 | 0 | 5147262.9116 | 0 | 0 | 0 | 2316669.0713 | 6406579.1085 | 16668604.6702 | 11376665.193 | 50878974.8909 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73465247.6833 | 120345873.5508 | 100000 | 23.4633 | 3131.0732 | 5129.1155 | 63.8312 | 104.564
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.9675 | 37.9593 | 5.9579 | 4 | 3090.0957 | 5057.2695 | 62.9958 | 103.0993 | 148.1979 | 16.1783 | 116.2903 | 9023036.6268 | 0 | 5197327.2642 | 0 | 0 | 0 | 2263665.6605 | 6428771.5251 | 16726344.786 | 11416074.0084 | 51055219.8711 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73641492.6636 | 120522118.531 | 133352.1432 | 23.8315 | 3090.0957 | 5057.2695 | 62.9958 | 103.0993
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.3971 | 38.3338 | 6.028 | 4 | 3059.3346 | 5003.6319 | 62.3687 | 102.0058 | 148.0265 | 16.1173 | 120.6409 | 9067736.9356 | 0 | 5235161.0588 | 0 | 0 | 0 | 2221411.7512 | 6444480.8007 | 16767217.0988 | 11443970.2018 | 51179977.8468 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73766250.6392 | 120646876.5066 | 177827.941 | 24.1119 | 3059.3346 | 5003.6319 | 62.3687 | 102.0058
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4862 | 38.6191 | 6.0813 | 4 | 3036.2467 | 4963.484 | 61.898 | 101.1873 | 147.8941 | 16.0704 | 108.9829 | 9101432.3311 | 0 | 5263937.7614 | 0 | 0 | 0 | 2188438.2036 | 6455985.2355 | 16797149.278 | 11464399.5292 | 51271342.3388 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73857615.1312 | 120738240.9986 | 237137.3706 | 24.3253 | 3036.2467 | 4963.484 | 61.898 | 101.1873
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.2996 | 38.8327 | 6.1215 | 4 | 3018.9207 | 4933.5001 | 61.5448 | 100.5761 | 147.7941 | 16.0351 | 118.8728 | 9126394.5103 | 0 | 5285406.0477 | 0 | 0 | 0 | 2162686.3085 | 6464049.8779 | 16818131.8235 | 11478720.5476 | 51335389.1155 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73921661.908 | 120802287.7754 | 316227.766 | 24.4861 | 3018.9207 | 4933.5001 | 61.5448 | 100.5761
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.9038 | 38.9918 | 6.1517 | 4 | 3005.9204 | 4911.1077 | 61.2798 | 100.1196 | 147.7193 | 16.0087 | 129.4173 | 9144819.0195 | 0 | 5301336.624 | 0 | 0 | 0 | 2142705.706 | 6469655.9263 | 16832717.6113 | 11488675.6475 | 51379910.5346 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 73966183.327 | 120846809.1944 | 421696.5034 | 24.6068 | 3005.9204 | 4911.1077 | 61.2798 | 100.1196
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3667 | 39.1134 | 6.1746 | 4 | 2996.1671 | 4894.2863 | 61.0809 | 99.7766 | 147.6616 | 15.9885 | 109.038 | 9158870.9125 | 0 | 5313533.5002 | 0 | 0 | 0 | 2127608.268 | 6474004.9455 | 16844032.8671 | 11496398.5421 | 51414449.0355 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74000721.8279 | 120881347.6953 | 562341.3252 | 24.6985 | 2996.1671 | 4894.2863 | 61.0809 | 99.7766
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.7151 | 39.205 | 6.1919 | 4 | 2988.8505 | 4881.6818 | 60.9318 | 99.5197 | 147.6181 | 15.9732 | 113.2971 | 9169409.7908 | 0 | 5322709.0379 | 0 | 0 | 0 | 2116132.3917 | 6477217.9759 | 16852392.5133 | 11502104.1724 | 51439965.882 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74026238.6745 | 120906864.5419 | 749894.2093 | 24.7675 | 2988.8505 | 4881.6818 | 60.9318 | 99.5197
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.9781 | 39.2741 | 6.2049 | 4 | 2983.3623 | 4872.229 | 60.8199 | 99.327 | 147.5851 | 15.9616 | 118.4007 | 9177344.8405 | 0 | 5329633.3692 | 0 | 0 | 0 | 2107459.4416 | 6479630.684 | 16858669.8848 | 11506388.6074 | 51459126.8277 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74045399.6201 | 120926025.4875 | 1000000 | 24.8194 | 2983.3623 | 4872.229 | 60.8199 | 99.327
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1755 | 39.326 | 6.2146 | 4 | 2979.2458 | 4865.1448 | 60.736 | 99.1826 | 147.5602 | 15.9529 | 118.2619 | 9183289.3187 | 0 | 5334829.7842 | 0 | 0 | 0 | 2100901.4374 | 6481418.0107 | 16863320.1423 | 11509562.5037 | 51473321.197 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74059593.9894 | 120940219.8568 | 1333521.4322 | 24.8585 | 2979.2458 | 4865.1448 | 60.736 | 99.1826
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3265 | 39.3656 | 6.222 | 4 | 2976.1584 | 4859.818 | 60.673 | 99.074 | 147.5412 | 15.9463 | 122.1583 | 9187827.888 | 0 | 5338801.9771 | 0 | 0 | 0 | 2096008.5903 | 6482828.9976 | 16866991.2406 | 11512068.1037 | 51484526.7971 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74070799.5896 | 120951425.457 | 1778279.41 | 24.8881 | 2976.1584 | 4859.818 | 60.673 | 99.074
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.4339 | 39.394 | 6.2274 | 4 | 2973.8429 | 4855.86 | 60.6258 | 98.9933 | 147.5277 | 15.9416 | 108.8229 | 9191052.851 | 0 | 5341628.3637 | 0 | 0 | 0 | 2092205.4563 | 6483705.8017 | 16869272.5051 | 11513625.1136 | 51491490.0915 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74077762.8839 | 120958388.7513 | 2371373.7057 | 24.9098 | 2973.8429 | 4855.86 | 60.6258 | 98.9933
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.5117 | 39.4146 | 6.2315 | 4 | 2972.1064 | 4852.9095 | 60.5904 | 98.9331 | 147.5178 | 15.9381 | 116.9848 | 9193385.6155 | 0 | 5343674.8241 | 0 | 0 | 0 | 2089288.0033 | 6484275.8928 | 16870755.7651 | 11514637.4691 | 51496017.5699 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74082290.3624 | 120962916.2298 | 3162277.6602 | 24.9259 | 2972.1064 | 4852.9095 | 60.5904 | 98.9331
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.5628 | 39.4284 | 6.2343 | 4 | 2970.804 | 4850.7409 | 60.5639 | 98.8889 | 147.5113 | 15.9359 | 126.1246 | 9194915.7532 | 0 | 5345019.3023 | 0 | 0 | 0 | 2086950.6236 | 6484485.4149 | 16871300.8987 | 11515009.5339 | 51497681.5267 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74083954.3191 | 120964580.1865 | 4216965.0343 | 24.9373 | 2970.804 | 4850.7409 | 60.5639 | 98.8889
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6165 | 39.4423 | 6.2368 | 4 | 2969.8274 | 4849.0225 | 60.5439 | 98.8539 | 147.5045 | 15.9335 | 119.3869 | 9196527.086 | 0 | 5346432.1313 | 0 | 0 | 0 | 2085500.9391 | 6485099.461 | 16872898.5208 | 11516099.9438 | 51502558.082 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74088830.8745 | 120969456.7419 | 5623413.2519 | 24.9472 | 2969.8274 | 4849.0225 | 60.5439 | 98.8539
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6554 | 39.4524 | 6.2386 | 4 | 2969.095 | 4847.7424 | 60.529 | 98.8278 | 147.4996 | 15.9318 | 122.9595 | 9197693.1708 | 0 | 5347455.1561 | 0 | 0 | 0 | 2084384.3067 | 6485517.7271 | 16873986.7634 | 11516842.6918 | 51505879.8159 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74092152.6084 | 120972778.4758 | 7498942.0933 | 24.9545 | 2969.095 | 4847.7424 | 60.529 | 98.8278
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6702 | 39.4567 | 6.2397 | 4 | 2968.5457 | 4846.8686 | 60.5178 | 98.81 | 147.4977 | 15.9311 | 113.1422 | 9198134.4811 | 0 | 5347844.867 | 0 | 0 | 0 | 2083260.5445 | 6485403.5581 | 16873689.719 | 11516639.9529 | 51504973.1225 | 961560.8286 | 21624711.9638 | 21624711.9638 | 16547321.491 | 8708592.4126 | 0 | 74091245.915 | 120971871.7824 | 10000000 | 24.9588 | 2968.5457 | 4846.8686 | 60.5178 | 98.81
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.071692 | 0.0091608 | 4 | 676823.9097 | 1987566.2459 | 13797.9709 | 40519.2263 | 88.7219 | 16.6719 | 24.3198 | 229547.0888 | 0 | 98854.575 | 0 | 0 | 0 | 203714.0197 | 207525.1166 | 539937.784 | 368518.6322 | 1648097.2162 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 24800931.9648 | 72830605.6205 | 100 | 0.036643 | 676823.9097 | 1987566.2459 | 13797.9709 | 40519.2263
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1567 | 0.29385 | 0.027514 | 4 | 240675.1712 | 677093.8308 | 4906.4889 | 13803.4736 | 112.9809 | 18.0795 | 58.7396 | 458203.949 | 0 | 224402.3813 | 0 | 0 | 0 | 393979.9042 | 419868.6314 | 1092412.0521 | 745593.6724 | 3334460.5904 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 26487295.339 | 74516968.9947 | 133.3521 | 0.11005 | 240675.1712 | 677093.8308 | 4906.4889 | 13803.4736
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3406 | 0.52078 | 0.051673 | 4 | 133192.5179 | 365564.955 | 2715.3096 | 7452.5361 | 122.8227 | 18.5398 | 59.8127 | 617777.1456 | 0 | 294560.9862 | 0 | 0 | 0 | 500874.8793 | 551153.0744 | 1433987.2424 | 978725.7584 | 4377079.0864 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 27529913.835 | 75559587.4907 | 177.8279 | 0.20669 | 133192.5179 | 365564.955 | 2715.3096 | 7452.5361
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7702 | 0.82092 | 0.086172 | 4 | 83135.4607 | 222477.1987 | 1694.8288 | 4535.4986 | 130.4364 | 18.8592 | 59.6459 | 796347.7927 | 0 | 369902.4395 | 0 | 0 | 0 | 610520.4131 | 692940.5517 | 1802889.1739 | 1230508.9068 | 5503109.2778 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 28655944.0263 | 76685617.682 | 237.1374 | 0.34469 | 83135.4607 | 222477.1987 | 1694.8288 | 4535.4986
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5802 | 1.2196 | 0.13364 | 4 | 56047.7462 | 145894.5664 | 1142.6091 | 2974.2581 | 136.6264 | 19.0972 | 64.7235 | 1005197.2228 | 0 | 460125.6234 | 0 | 0 | 0 | 733002.3177 | 857346.8139 | 2230640.5438 | 1522458.0063 | 6808770.528 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 29961605.2765 | 77991278.9323 | 316.2278 | 0.53457 | 56047.7462 | 145894.5664 | 1142.6091 | 2974.2581
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8823 | 1.7422 | 0.19774 | 4 | 39808.1917 | 100532.2789 | 811.5438 | 2049.4865 | 141.6395 | 19.2756 | 78.3883 | 1250444.8534 | 0 | 568875.4963 | 0 | 0 | 0 | 871265.3593 | 1049328.4265 | 2730137.3189 | 1863374.8189 | 8333426.2734 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 31486261.0219 | 79515934.6776 | 421.6965 | 0.79095 | 39808.1917 | 100532.2789 | 811.5438 | 2049.4865
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.7935 | 2.4166 | 0.28308 | 4 | 29370.7021 | 71787.7582 | 598.7615 | 1463.4906 | 145.6487 | 19.4072 | 55.5541 | 1537008.2772 | 0 | 699398.0704 | 0 | 0 | 0 | 1025901.1388 | 1272299.9197 | 3310263.4065 | 2259322.794 | 10104193.6067 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 33257028.3553 | 81286702.011 | 562.3413 | 1.1323 | 29370.7021 | 71787.7582 | 598.7615 | 1463.4906
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4741 | 3.281 | 0.39561 | 4 | 22318.5538 | 52670.1115 | 454.9939 | 1073.7515 | 148.8374 | 19.5012 | 63.7115 | 1872202.7536 | 0 | 856195.8905 | 0 | 0 | 0 | 1199291.1493 | 1531799.0194 | 3985426.8334 | 2720135.7061 | 12165051.3523 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 35317886.1009 | 83347559.7566 | 749.8942 | 1.5824 | 22318.5538 | 52670.1115 | 454.9939 | 1073.7515
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1345 | 4.3854 | 0.54291 | 4 | 17372.6688 | 39489.6146 | 354.1654 | 805.0492 | 151.3602 | 19.5625 | 62.608 | 2265375.8154 | 0 | 1045024.0207 | 0 | 0 | 0 | 1395077.4363 | 1835136.1362 | 4774647.7883 | 3258795.2247 | 14574056.4216 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 37726891.1702 | 85756564.8259 | 1000 | 2.1716 | 17372.6688 | 39489.6146 | 354.1654 | 805.0492
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.9345 | 5.7715 | 0.7333 | 4 | 13803.4983 | 30178.099 | 281.403 | 615.2214 | 153.3077 | 19.5915 | 70.9047 | 2719281.5156 | 0 | 1268760.7822 | 0 | 0 | 0 | 1608957.9969 | 2182830.1149 | 5679276.1991 | 3876222.7033 | 17335329.3121 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 40488164.0606 | 88517837.7163 | 1333.5214 | 2.9332 | 13803.4983 | 30178.099 | 281.403 | 615.2214
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.1112 | 7.4984 | 0.97672 | 4 | 11170.2582 | 23463.8206 | 227.7208 | 478.3417 | 154.7851 | 19.5862 | 77.7575 | 3241020.1284 | 0 | 1532675.7626 | 0 | 0 | 0 | 1841263.2065 | 2579834.048 | 6712198.9962 | 4581213.7368 | 20488205.8786 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 43641040.6271 | 91670714.2828 | 1778.2794 | 3.9069 | 11170.2582 | 23463.8206 | 227.7208 | 478.3417
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.866 | 9.6185 | 1.2831 | 4 | 9194.4417 | 18552.5817 | 187.4411 | 378.2195 | 155.8592 | 19.54 | 80.9985 | 3832809.8039 | 0 | 1840021.6043 | 0 | 0 | 0 | 2087809.9228 | 3026650.1191 | 7874722.7585 | 5374660.0921 | 24036674.3006 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 47189509.0492 | 95219182.7049 | 2371.3737 | 5.1324 | 9194.4417 | 18552.5817 | 187.4411 | 378.2195
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.283 | 12.159 | 1.6596 | 4 | 7694.0031 | 14929.1126 | 156.8527 | 304.3502 | 156.568 | 19.4435 | 80.4586 | 4487903.3879 | 0 | 2189792.3381 | 0 | 0 | 0 | 2337764.3924 | 3516029.4462 | 9147987.3822 | 6243689.3607 | 27923166.3076 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 51076001.0562 | 99105674.7119 | 3162.2777 | 6.6384 | 7694.0031 | 14929.1126 | 156.8527 | 304.3502
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.1823 | 15.0848 | 2.1057 | 4 | 6546.7394 | 12249.1969 | 133.4641 | 249.7164 | 156.9255 | 19.2869 | 104.9238 | 5184257.6578 | 0 | 2572976.6 | 0 | 0 | 0 | 2570596.2781 | 4027853.909 | 10479649.6448 | 7152576.2179 | 31987910.3076 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 55140745.0562 | 103170418.7119 | 4216.965 | 8.4226 | 6546.7394 | 12249.1969 | 133.4641 | 249.7164
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.1324 | 18.2971 | 2.6097 | 4 | 5668.0109 | 10269.0891 | 115.5501 | 209.3493 | 156.9417 | 19.0649 | 91.7066 | 5889408.6647 | 0 | 2974386.0615 | 0 | 0 | 0 | 2764029.7476 | 4534851.5448 | 11798753.4935 | 8052891.6995 | 36014321.2115 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 59167155.9601 | 107196829.6158 | 5623.4133 | 10.4388 | 5668.0109 | 10269.0891 | 115.5501 | 209.3493
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4233 | 21.6243 | 3.1473 | 4 | 4996.318 | 8811.5249 | 101.8567 | 179.6349 | 156.6454 | 18.7826 | 107.2397 | 6562762.9127 | 0 | 3372699.6917 | 0 | 0 | 0 | 2897150.1585 | 5004718.9776 | 13021252.1706 | 8887272.1664 | 39745856.0775 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 62898690.826 | 110928364.4817 | 7498.9421 | 12.589 | 4996.318 | 8811.5249 | 101.8567 | 179.6349
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.2419 | 24.863 | 3.6856 | 4 | 4485.2398 | 7743.1538 | 91.4377 | 157.8547 | 156.1071 | 18.4601 | 91.4291 | 7167835.6682 | 0 | 3745986.595 | 0 | 0 | 0 | 2959967.257 | 5410777.9129 | 14077734.2262 | 9608342.8779 | 42970644.5371 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 66123479.2857 | 114153152.9414 | 10000 | 14.7425 | 4485.2398 | 7743.1538 | 91.4377 | 157.8547
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9345 | 27.8434 | 4.1937 | 4 | 4098.0127 | 6961.2154 | 83.5435 | 141.9138 | 155.4206 | 18.1228 | 100.3203 | 7683500.3853 | 0 | 4078519.5136 | 0 | 0 | 0 | 2957646.2719 | 5740669.8066 | 14936045.2634 | 10194157.7973 | 45590539.038 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 68743373.7866 | 116773047.4423 | 13335.2143 | 16.7748 | 4098.0127 | 6961.2154 | 83.5435 | 141.9138
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0466 | 30.4433 | 4.6475 | 4 | 3805.7085 | 6389.3349 | 77.5845 | 130.2552 | 154.6853 | 17.7978 | 99.8037 | 8102164.5544 | 0 | 4360709.7143 | 0 | 0 | 0 | 2904085.6809 | 5993114.3803 | 15592854.2609 | 10642443.4341 | 47595372.0249 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 70748206.7735 | 118777880.4292 | 17782.7941 | 18.59 | 3805.7085 | 6389.3349 | 77.5845 | 130.2552
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4756 | 32.6268 | 5.0358 | 4 | 3585.6187 | 5970.0081 | 73.0977 | 121.7067 | 153.9745 | 17.5033 | 105.2269 | 8431878.1651 | 0 | 4592477.2323 | 0 | 0 | 0 | 2819895.5455 | 6179257.8677 | 16077161.4318 | 10972993.0298 | 49073663.2723 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 72226498.0209 | 120256171.6766 | 23713.7371 | 20.1434 | 3585.6187 | 5970.0081 | 73.0977 | 121.7067
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2741 | 34.4 | 5.3565 | 4 | 3420.1474 | 5661.8016 | 69.7243 | 115.4235 | 153.3368 | 17.25 | 104.2195 | 8684965.9726 | 0 | 4777297.6284 | 0 | 0 | 0 | 2722148.4754 | 6311920.7098 | 16422322.934 | 11208572.8474 | 50127228.5676 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 73280063.3162 | 121309736.9719 | 31622.7766 | 21.426 | 3420.1474 | 5661.8016 | 69.7243 | 115.4235
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6339 | 35.8063 | 5.6144 | 4 | 3295.8321 | 5434.5257 | 67.19 | 110.7902 | 152.7933 | 17.0402 | 98.4201 | 8876313.2364 | 0 | 4921753.3025 | 0 | 0 | 0 | 2623984.407 | 6404599.8689 | 16663455.0949 | 11373150.502 | 50863256.4118 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 74016091.1604 | 122045764.8161 | 42169.6503 | 22.4575 | 3295.8321 | 5434.5257 | 67.19 | 110.7902
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8092 | 36.9068 | 5.8181 | 4 | 3202.4678 | 5266.2621 | 65.2866 | 107.3599 | 152.3446 | 16.8706 | 111.4626 | 9020307.8866 | 0 | 5033551.5711 | 0 | 0 | 0 | 2533942.6167 | 6469242.809 | 16831642.7648 | 11487942.0427 | 51376629.6908 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 74529464.4394 | 122559138.0951 | 56234.1325 | 23.2725 | 3202.4678 | 5266.2621 | 65.2866 | 107.3599
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0197 | 37.7564 | 5.9768 | 4 | 3132.3602 | 5141.3807 | 63.8574 | 104.814 | 151.9844 | 16.7365 | 104.5797 | 9127977.3986 | 0 | 5119097.9188 | 0 | 0 | 0 | 2455636.4685 | 6514057.5965 | 16948241.6491 | 11567523.177 | 51732534.2084 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 74885368.957 | 122915042.6127 | 74989.4209 | 23.907 | 3132.3602 | 5141.3807 | 63.8574 | 104.814
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.4681 | 38.4063 | 6.099 | 4 | 3079.7226 | 5048.4865 | 62.7843 | 102.9202 | 151.7008 | 16.632 | 106.8414 | 9208280.6184 | 0 | 5184096.078 | 0 | 0 | 0 | 2390112.6423 | 6545170.8421 | 17029191.932 | 11622773.4085 | 51979625.5213 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75132460.2699 | 123162133.9256 | 100000 | 24.3959 | 3079.7226 | 5048.4865 | 62.7843 | 102.9202
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.3387 | 38.9036 | 6.1927 | 4 | 3040.2069 | 4979.1692 | 61.9787 | 101.5071 | 151.4788 | 16.5509 | 121.7283 | 9268572.6657 | 0 | 5233618.3381 | 0 | 0 | 0 | 2337102.563 | 6567324.491 | 17086831.1822 | 11662113.3811 | 52155562.6211 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75308397.3697 | 123338071.0254 | 133352.1432 | 24.7708 | 3040.2069 | 4979.1692 | 61.9787 | 101.5071
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.742 | 39.2778 | 6.2638 | 4 | 3010.5461 | 4927.5015 | 61.3741 | 100.4538 | 151.3091 | 16.4893 | 113.2945 | 9313189.1001 | 0 | 5270690.4182 | 0 | 0 | 0 | 2294607.0752 | 6582609.7715 | 17126600.3464 | 11689256.6529 | 52276953.3642 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75429788.1128 | 123459461.7685 | 177827.941 | 25.0552 | 3010.5461 | 4927.5015 | 61.3741 | 100.4538
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8092 | 39.5626 | 6.3179 | 4 | 2988.2858 | 4888.8366 | 60.9202 | 99.6655 | 151.1784 | 16.4421 | 114.1188 | 9346772.1815 | 0 | 5298842.0126 | 0 | 0 | 0 | 2261453.7674 | 6593756.505 | 17155601.8605 | 11709050.7822 | 52365477.1092 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75518311.8578 | 123547985.5135 | 237137.3706 | 25.2714 | 2988.2858 | 4888.8366 | 60.9202 | 99.6655
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6102 | 39.7766 | 6.3587 | 4 | 2971.5819 | 4859.9342 | 60.5797 | 99.0763 | 151.0793 | 16.4064 | 108.3401 | 9371779.1841 | 0 | 5319948.6626 | 0 | 0 | 0 | 2235674.3031 | 6601686.8384 | 17176234.9614 | 11723133.2975 | 52428457.247 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75581291.9956 | 123610965.6513 | 316227.766 | 25.4347 | 2971.5819 | 4859.9342 | 60.5797 | 99.0763
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.2144 | 39.9382 | 6.3895 | 4 | 2959.0491 | 4838.2934 | 60.3242 | 98.6352 | 151.0039 | 16.3793 | 118.2655 | 9390525.4486 | 0 | 5335853.3647 | 0 | 0 | 0 | 2215877.2305 | 6607479.8571 | 17191307.2077 | 11733420.4153 | 52474463.524 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75627298.2726 | 123656971.9283 | 421696.5034 | 25.558 | 2959.0491 | 4838.2934 | 60.3242 | 98.6352
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6554 | 40.0566 | 6.4124 | 4 | 2949.6469 | 4822.1671 | 60.1325 | 98.3064 | 150.9486 | 16.3595 | 120.5772 | 9404143.7969 | 0 | 5347455.1561 | 0 | 0 | 0 | 2200473.6562 | 6611308.3176 | 17201268.0765 | 11740218.9129 | 52504867.9161 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75657702.6647 | 123687376.3204 | 562341.3252 | 25.6497 | 2949.6469 | 4822.1671 | 60.1325 | 98.3064
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0038 | 40.1496 | 6.4301 | 4 | 2942.5939 | 4809.9849 | 59.9888 | 98.058 | 150.9047 | 16.3438 | 124.6049 | 9414868.944 | 0 | 5356616.1234 | 0 | 0 | 0 | 2189114.0565 | 6614633.6583 | 17209919.9309 | 11746123.9813 | 52531276.6944 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75684111.4429 | 123713785.0986 | 749894.2093 | 25.7202 | 2942.5939 | 4809.9849 | 59.9888 | 98.058
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2692 | 40.2204 | 6.4434 | 4 | 2937.3036 | 4800.8344 | 59.8809 | 97.8715 | 150.8712 | 16.3318 | 103.1117 | 9423019.267 | 0 | 5363593.2796 | 0 | 0 | 0 | 2180580.7012 | 6617205.3666 | 17216610.9886 | 11750690.7657 | 52551700.3687 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75704535.1173 | 123734208.773 | 1000000 | 25.7735 | 2937.3036 | 4800.8344 | 59.8809 | 97.8715
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.4519 | 40.2696 | 6.453 | 4 | 2933.3356 | 4794.0751 | 59.8 | 97.7337 | 150.848 | 16.3235 | 113.7209 | 9428611.8992 | 0 | 5368392.1243 | 0 | 0 | 0 | 2173787.6233 | 6618608.7423 | 17220262.284 | 11753182.8499 | 52562845.523 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75715680.2715 | 123745353.9273 | 1333521.4322 | 25.8121 | 2933.3356 | 4794.0751 | 59.8 | 97.7337
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5982 | 40.3087 | 6.4605 | 4 | 2930.3596 | 4788.9537 | 59.7393 | 97.6293 | 150.8295 | 16.3169 | 105.2411 | 9433088.6611 | 0 | 5372236.4523 | 0 | 0 | 0 | 2168853.9033 | 6619929.8165 | 17223699.4483 | 11755528.7851 | 52573337.0667 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75726171.8153 | 123755845.471 | 1778279.41 | 25.8419 | 2930.3596 | 4788.9537 | 59.7393 | 97.6293
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.7102 | 40.3386 | 6.4661 | 4 | 2928.1277 | 4785.1012 | 59.6938 | 97.5508 | 150.8153 | 16.3118 | 106.6621 | 9436513.6373 | 0 | 5375180.0613 | 0 | 0 | 0 | 2165183.4747 | 6620982.0976 | 17226437.2678 | 11757397.4031 | 52581693.9418 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75734528.6904 | 123764202.3461 | 2371373.7057 | 25.8645 | 2928.1277 | 4785.1012 | 59.6938 | 97.5508
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.7808 | 40.3579 | 6.4701 | 4 | 2926.4538 | 4782.2924 | 59.6597 | 97.4935 | 150.8062 | 16.3086 | 114.318 | 9438665.5833 | 0 | 5377033.3667 | 0 | 0 | 0 | 2162146.2967 | 6621359.6462 | 17227419.5718 | 11758067.8458 | 52584692.3105 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75737527.0591 | 123767200.7148 | 3162277.6602 | 25.8803 | 2926.4538 | 4782.2924 | 59.6597 | 97.4935
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8493 | 40.376 | 6.4734 | 4 | 2925.1985 | 4780.0948 | 59.6341 | 97.4487 | 150.7975 | 16.3055 | 112.2603 | 9440758.3847 | 0 | 5378833.2367 | 0 | 0 | 0 | 2160181.1509 | 6622111.3812 | 17229375.4321 | 11759402.7607 | 52590662.3464 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75743497.095 | 123773170.7507 | 4216965.0343 | 25.8935 | 2925.1985 | 4780.0948 | 59.6341 | 97.4487
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.8929 | 40.3878 | 6.4757 | 4 | 2924.2571 | 4778.4933 | 59.6149 | 97.416 | 150.792 | 16.3035 | 115.5488 | 9442085.3643 | 0 | 5379976.3192 | 0 | 0 | 0 | 2158544.1559 | 6622436.2774 | 17230220.7453 | 11759979.7043 | 52593242.5663 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75746077.3149 | 123775750.9706 | 5623413.2519 | 25.9027 | 2924.2571 | 4778.4933 | 59.6149 | 97.416
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.9271 | 40.3969 | 6.4774 | 4 | 2923.5512 | 4777.283 | 59.6005 | 97.3914 | 150.7876 | 16.302 | 108.5049 | 9443130.0265 | 0 | 5380876.15 | 0 | 0 | 0 | 2157347.8299 | 6622728.0625 | 17230979.9103 | 11760497.85 | 52595559.8292 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75748394.5778 | 123778068.2335 | 7498942.0933 | 25.9097 | 2923.5512 | 4777.283 | 59.6005 | 97.3914
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.9466 | 40.4024 | 6.4786 | 4 | 2923.0217 | 4776.412 | 59.5898 | 97.3736 | 150.7851 | 16.3011 | 110.2148 | 9443721.3959 | 0 | 5381386.848 | 0 | 0 | 0 | 2156322.7713 | 6622758.0959 | 17231058.0511 | 11760551.1827 | 52595798.345 | 961560.8286 | 22191273.92 | 22191273.92 | 16930155.7018 | 8908244.0339 | 0 | 75748633.0935 | 123778306.7492 | 10000000 | 25.9145 | 2923.0217 | 4776.412 | 59.5898 | 97.3736
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.070676 | 0.0093822 | 4 | 676443.5633 | 1987230.4195 | 13790.217 | 40512.38 | 89.3108 | 17.0369 | 23.8157 | 231919.7472 | 0 | 98584.4631 | 0 | 0 | 0 | 205770.7712 | 209147.2428 | 544158.2237 | 371399.169 | 1660979.6171 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 25386236.4127 | 74578729.0702 | 100 | 0.037529 | 676443.5633 | 1987230.4195 | 13790.217 | 40512.38
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2493 | 0.30729 | 0.029292 | 4 | 232119.1831 | 651966.9337 | 4732.0635 | 13291.2278 | 115.3 | 18.5433 | 54.6524 | 477610.7802 | 0 | 232341.9905 | 0 | 0 | 0 | 410897.4188 | 437131.5739 | 1137326.6874 | 776248.8338 | 3471557.2847 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 27196814.0803 | 76389306.7378 | 133.3521 | 0.11717 | 232119.1831 | 651966.9337 | 4732.0635 | 13291.2278
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4797 | 0.54604 | 0.055073 | 4 | 128393.7848 | 351700.236 | 2617.481 | 7169.885 | 125.4694 | 19.0144 | 65.2091 | 645539.2716 | 0 | 302088.2227 | 0 | 0 | 0 | 524254.2106 | 574033.8649 | 1493518.3659 | 1019356.9735 | 4558790.9092 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 28284047.7048 | 77476540.3623 | 177.8279 | 0.22029 | 128393.7848 | 351700.236 | 2617.481 | 7169.885
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9406 | 0.85795 | 0.091667 | 4 | 80297.2352 | 214458.0739 | 1636.9677 | 4372.0179 | 133.2001 | 19.3356 | 65.7459 | 830202.2631 | 0 | 378615.8832 | 0 | 0 | 0 | 637066.7233 | 719895.0992 | 1873019.3772 | 1278374.2116 | 5717173.5576 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 29442430.3532 | 78634923.0108 | 237.1374 | 0.36667 | 80297.2352 | 214458.0739 | 1636.9677 | 4372.0179
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7971 | 1.2733 | 0.14199 | 4 | 54215.8628 | 140828.7077 | 1105.2637 | 2870.9837 | 139.5214 | 19.5764 | 64.9324 | 1047049.1801 | 0 | 470627.8905 | 0 | 0 | 0 | 764053.3541 | 889874.8656 | 2315271.8619 | 1580220.6199 | 7067097.7721 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 30792354.5677 | 79984847.2252 | 316.2278 | 0.56796 | 54215.8628 | 140828.7077 | 1105.2637 | 2870.9837
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1601 | 1.8179 | 0.2099 | 4 | 38554.1807 | 97143.9597 | 785.9791 | 1980.411 | 144.6484 | 19.7571 | 67.982 | 1301926.06 | 0 | 581634.627 | 0 | 0 | 0 | 907677.2522 | 1088582.7963 | 2832269.1369 | 1933081.8833 | 8645171.7557 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 32370428.5513 | 81562921.2088 | 421.6965 | 0.83961 | 38554.1807 | 97143.9597 | 785.9791 | 1980.411
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1445 | 2.5202 | 0.30027 | 4 | 28475.0148 | 69432.4639 | 580.5017 | 1415.4747 | 148.7461 | 19.89 | 42.3735 | 1599400.8483 | 0 | 714706.871 | 0 | 0 | 0 | 1067934.0042 | 1318996.2722 | 3431757.7368 | 2342245.1709 | 10475040.9034 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 34200297.699 | 83392790.3565 | 562.3413 | 1.2011 | 28475.0148 | 69432.4639 | 580.5017 | 1415.4747
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9151 | 3.4196 | 0.41935 | 4 | 21657.8442 | 50984.8207 | 441.5244 | 1039.3945 | 152.0058 | 19.9846 | 63.1902 | 1947198.5962 | 0 | 874483.1598 | 0 | 0 | 0 | 1247466.6517 | 1586967.879 | 4128964.8893 | 2818103.3787 | 12603184.5547 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 36328441.3503 | 85520934.0079 | 749.8942 | 1.6774 | 21657.8442 | 50984.8207 | 441.5244 | 1039.3945
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.6681 | 4.5644 | 0.57493 | 4 | 16872.6431 | 38263.2126 | 343.9717 | 780.0473 | 154.5775 | 20.0455 | 59.8142 | 2353462.3298 | 0 | 1066079.2913 | 0 | 0 | 0 | 1448394.8401 | 1898495.2198 | 4939495.1271 | 3371306.9207 | 15077233.7287 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 38802490.5243 | 87994983.1819 | 1000 | 2.2997 | 16872.6431 | 38263.2126 | 343.9717 | 780.0473
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6145 | 6.0076 | 0.77622 | 4 | 13416.9787 | 29260.4942 | 273.5233 | 596.5148 | 156.5752 | 20.0733 | 57.8855 | 2825029.9472 | 0 | 1294319.5736 | 0 | 0 | 0 | 1670647.0405 | 2258098.6589 | 5875109.5107 | 4009882.9625 | 17933087.6934 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 41658344.4889 | 90850837.1465 | 1333.5214 | 3.1049 | 13416.9787 | 29260.4942 | 273.5233 | 596.5148
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.9855 | 7.8084 | 1.0336 | 4 | 10866.0423 | 22763.9212 | 221.519 | 464.0733 | 158.0919 | 20.065 | 75.1045 | 3367974.7063 | 0 | 1564020.9257 | 0 | 0 | 0 | 1913115.6328 | 2669593.3933 | 6945734.4004 | 4740606.4489 | 21201045.5075 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 44926302.303 | 94118794.9606 | 1778.2794 | 4.1346 | 10866.0423 | 22763.9212 | 221.519 | 464.0733
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.9138 | 10.0058 | 1.3565 | 4 | 8951.2261 | 18017.0427 | 182.4829 | 367.3018 | 159.1861 | 20.0139 | 75.7474 | 3979468.3463 | 0 | 1875914.9407 | 0 | 0 | 0 | 2166384.8023 | 3128489.5548 | 8139688.0802 | 5555504.3686 | 24845450.093 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 48570706.8885 | 97763199.5461 | 2371.3737 | 5.4262 | 8951.2261 | 18017.0427 | 182.4829 | 367.3018
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.525 | 12.6357 | 1.7527 | 4 | 7496.8744 | 14513.7147 | 152.8339 | 295.8817 | 159.9066 | 19.9099 | 75.5989 | 4655672.593 | 0 | 2230535.0107 | 0 | 0 | 0 | 2422871.6714 | 3630540.9173 | 9445922.7404 | 6447036.3646 | 28832579.2974 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 52557836.093 | 101750328.7505 | 3162.2777 | 7.0106 | 7496.8744 | 14513.7147 | 152.8339 | 295.8817
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.6197 | 15.6582 | 2.2207 | 4 | 6384.9991 | 11922.8815 | 130.1668 | 243.0641 | 160.2656 | 19.743 | 84.5692 | 5372873.0959 | 0 | 2618271.5213 | 0 | 0 | 0 | 2660903.5291 | 4154298.7771 | 10808633.254 | 7377114.2911 | 32992094.4685 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 56717351.264 | 105909843.9216 | 4216.965 | 8.8829 | 6384.9991 | 11922.8815 | 130.1668 | 243.0641
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.7332 | 18.9646 | 2.7476 | 4 | 5533.7235 | 10009.5959 | 112.8124 | 204.0592 | 160.2737 | 19.5083 | 91.644 | 6096338.4274 | 0 | 3023039.9742 | 0 | 0 | 0 | 2856924.3409 | 4670758.0696 | 12152354.3928 | 8294231.579 | 37093646.784 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 60818903.5796 | 110011396.2371 | 5623.4133 | 10.9906 | 5533.7235 | 10009.5959 | 112.8124 | 204.0592
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.1165 | 22.3712 | 3.3068 | 4 | 4883.3796 | 8602.4198 | 99.5543 | 175.372 | 159.9642 | 19.2124 | 97.2642 | 6783290.8625 | 0 | 3422580.8906 | 0 | 0 | 0 | 2989103.9408 | 5146040.5206 | 13388941.8366 | 9138227.9187 | 40868185.9697 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 64593442.7653 | 113785935.4228 | 7498.9421 | 13.2272 | 4883.3796 | 8602.4198 | 99.5543 | 175.372
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.9929 | 25.6789 | 3.8647 | 4 | 4388.8479 | 7570.9969 | 89.4726 | 154.345 | 159.4109 | 18.8761 | 108.6347 | 7399099.2578 | 0 | 3796239.7592 | 0 | 0 | 0 | 3050011.093 | 5555686.5429 | 14454756.7566 | 9865668.5019 | 44121461.9115 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 67846718.707 | 117039211.3646 | 10000 | 15.4589 | 4388.8479 | 7570.9969 | 89.4726 | 154.345
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.6667 | 28.7053 | 4.3885 | 4 | 4014.3658 | 6816.7122 | 81.8383 | 138.9679 | 158.7134 | 18.5273 | 94.2924 | 7920796.3926 | 0 | 4127196.3931 | 0 | 0 | 0 | 3043787.2024 | 5885794.1953 | 15313629.1538 | 10451866.5611 | 46743069.8983 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 70468326.6938 | 119660819.3514 | 13335.2143 | 17.554 | 4014.3658 | 6816.7122 | 81.8383 | 138.9679
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7445 | 31.3404 | 4.8549 | 4 | 3731.815 | 6264.9387 | 76.0781 | 127.7192 | 157.9698 | 18.1924 | 102.2082 | 8343721.0994 | 0 | 4407639.1098 | 0 | 0 | 0 | 2986923.858 | 6137930.7862 | 15969636.843 | 10899605.2886 | 48745456.9849 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 72470713.7805 | 121663206.438 | 17782.7941 | 19.4197 | 3731.815 | 6264.9387 | 76.0781 | 127.7192
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1003 | 33.5426 | 5.2524 | 4 | 3519.1487 | 5860.592 | 71.7426 | 119.4761 | 157.2564 | 17.891 | 98.4184 | 8675144.3405 | 0 | 4636812.9228 | 0 | 0 | 0 | 2899245.6186 | 6322369.1239 | 16449507.5642 | 11227126.9161 | 50210206.486 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 73935463.2816 | 123127955.9391 | 23713.7371 | 21.0095 | 3519.1487 | 5860.592 | 71.7426 | 119.4761
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8212 | 35.3263 | 5.5796 | 4 | 3359.3055 | 5563.4089 | 68.484 | 113.4176 | 156.6192 | 17.6328 | 111.4434 | 8928968.7246 | 0 | 4819105.5867 | 0 | 0 | 0 | 2798755.518 | 6453263.6334 | 16790068.2278 | 11459566.5668 | 51249728.2573 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 74974985.0529 | 124167477.7104 | 31622.7766 | 22.3186 | 3359.3055 | 5563.4089 | 68.484 | 113.4176
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1413 | 36.7458 | 5.843 | 4 | 3239.2466 | 5344.0101 | 66.0364 | 108.9449 | 156.0744 | 17.4184 | 111.3894 | 9121732.9837 | 0 | 4962188.1868 | 0 | 0 | 0 | 2699448.5977 | 6545514.2096 | 17030085.3038 | 11623383.1531 | 51982352.4346 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 75707609.2302 | 124900101.8877 | 42169.6503 | 23.372 | 3239.2466 | 5344.0101 | 66.0364 | 108.9449
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.2487 | 37.8477 | 6.0501 | 4 | 3149.096 | 5181.8098 | 64.1986 | 105.6382 | 155.629 | 17.2467 | 110.2685 | 9265552.7538 | 0 | 5071952.3095 | 0 | 0 | 0 | 2607873.0687 | 6608697.4715 | 17194475.1905 | 11735582.6287 | 52484133.4226 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 76209390.2182 | 125401882.8757 | 56234.1325 | 24.2004 | 3149.096 | 5181.8098 | 64.1986 | 105.6382
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.4204 | 38.7014 | 6.2115 | 4 | 3081.4122 | 5061.3066 | 62.8188 | 103.1816 | 155.2703 | 17.1104 | 110.2104 | 9373591.1147 | 0 | 5156305.6406 | 0 | 0 | 0 | 2528948.3936 | 6652949.6081 | 17309610.1726 | 11814164.6198 | 52835569.5495 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 76560826.345 | 125753319.0026 | 74989.4209 | 24.846 | 3081.4122 | 5061.3066 | 62.8188 | 103.1816
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.8318 | 39.3527 | 6.3356 | 4 | 3030.6013 | 4971.7044 | 61.7829 | 101.3549 | 154.9886 | 17.0046 | 114.5688 | 9453950.2671 | 0 | 5220209.4847 | 0 | 0 | 0 | 2462923.1165 | 6683462.3187 | 17388997.9866 | 11868348.434 | 53077891.6076 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 76803148.4032 | 125995641.0607 | 100000 | 25.3425 | 3030.6013 | 4971.7044 | 61.7829 | 101.3549
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6734 | 39.851 | 6.4308 | 4 | 2992.461 | 4904.8406 | 61.0054 | 99.9918 | 154.7684 | 16.9225 | 120.0792 | 9514276.5248 | 0 | 5268881.3841 | 0 | 0 | 0 | 2409611.6287 | 6705180.1196 | 17445503.2497 | 11906914.4372 | 53250367.3441 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 76975624.1397 | 126168116.7972 | 133352.1432 | 25.7232 | 2992.461 | 4904.8406 | 61.0054 | 99.9918
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.065 | 40.2283 | 6.5032 | 4 | 2963.8353 | 4854.9357 | 60.4218 | 98.9744 | 154.599 | 16.8598 | 118.6067 | 9559253.2742 | 0 | 5305583.5305 | 0 | 0 | 0 | 2367168.1584 | 6720481.9356 | 17485315.4361 | 11934087.0724 | 53371889.4072 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77097146.2028 | 126289638.8603 | 177827.941 | 26.0126 | 2963.8353 | 4854.9357 | 60.4218 | 98.9744
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1024 | 40.5103 | 6.5577 | 4 | 2942.3535 | 4817.7152 | 59.9839 | 98.2156 | 154.471 | 16.8126 | 119.7223 | 9592440.1909 | 0 | 5332904.345 | 0 | 0 | 0 | 2333631.625 | 6731000.7027 | 17512683.1104 | 11952766.0725 | 53455426.0465 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77180682.8421 | 126373175.4996 | 237137.3706 | 26.2309 | 2942.3535 | 4817.7152 | 59.9839 | 98.2156
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.8944 | 40.7255 | 6.5992 | 4 | 2926.2347 | 4789.8107 | 59.6553 | 97.6468 | 154.3723 | 16.7763 | 111.6801 | 9617581.1975 | 0 | 5353738.3785 | 0 | 0 | 0 | 2307876.5559 | 6738886.4915 | 17533200.3151 | 11966769.4863 | 53518052.4247 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77243309.2203 | 126435801.8778 | 316227.766 | 26.3968 | 2926.2347 | 4789.8107 | 59.6553 | 97.6468
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.4861 | 40.8866 | 6.6304 | 4 | 2914.1415 | 4768.9493 | 59.4087 | 97.2215 | 154.298 | 16.7491 | 107.111 | 9636253.9059 | 0 | 5369292.44 | 0 | 0 | 0 | 2287991.716 | 6744479.8442 | 17547753.0715 | 11976702.0415 | 53562473.0191 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77287729.8147 | 126480222.4722 | 421696.5034 | 26.5216 | 2914.1415 | 4768.9493 | 59.4087 | 97.2215
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.942 | 41.0104 | 6.6541 | 4 | 2905.0694 | 4753.2634 | 59.2238 | 96.9017 | 154.2405 | 16.7281 | 109.9103 | 9650573.5777 | 0 | 5381265.2543 | 0 | 0 | 0 | 2273034.9309 | 6748900.7675 | 17559255.4072 | 11984552.622 | 53597582.5595 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77322839.3551 | 126515332.0126 | 562341.3252 | 26.6165 | 2905.0694 | 4753.2634 | 59.2238 | 96.9017
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.2755 | 41.1013 | 6.6718 | 4 | 2898.2643 | 4741.565 | 59.085 | 96.6632 | 154.1982 | 16.7126 | 113.9519 | 9661014.7776 | 0 | 5390022.8743 | 0 | 0 | 0 | 2261472.4608 | 6751878.944 | 17567004.0114 | 11989841.2036 | 53621234.2718 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77346491.0674 | 126538983.725 | 749894.2093 | 26.6872 | 2898.2643 | 4741.565 | 59.085 | 96.6632
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.5145 | 41.1669 | 6.6848 | 4 | 2893.16 | 4732.8662 | 58.981 | 96.4859 | 154.1677 | 16.7015 | 103.5739 | 9668472.2188 | 0 | 5396293.6634 | 0 | 0 | 0 | 2252469.7998 | 6753721.916 | 17571799.0466 | 11993113.9137 | 53635870.5583 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77361127.3539 | 126553620.0114 | 1000000 | 26.7393 | 2893.16 | 4732.8662 | 58.981 | 96.4859
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.7165 | 41.2215 | 6.6951 | 4 | 2889.3316 | 4726.2155 | 58.9029 | 96.3503 | 154.142 | 16.6921 | 113.9091 | 9674772.1596 | 0 | 5401595.4452 | 0 | 0 | 0 | 2246143.4265 | 6755779.3022 | 17577151.9435 | 11996767.3758 | 53652209.6528 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77377466.4484 | 126569959.106 | 1333521.4322 | 26.7804 | 2889.3316 | 4726.2155 | 58.9029 | 96.3503
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.848 | 41.2577 | 6.7024 | 4 | 2886.4603 | 4721.3465 | 58.8444 | 96.251 | 154.1252 | 16.686 | 118.0175 | 9678861.8517 | 0 | 5405045.1859 | 0 | 0 | 0 | 2240949.511 | 6756694.0539 | 17579531.9397 | 11998391.7721 | 53659474.3142 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77384731.1098 | 126577223.7673 | 1778279.41 | 26.8096 | 2886.4603 | 4721.3465 | 58.8444 | 96.251
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.9601 | 41.2881 | 6.7081 | 4 | 2884.3069 | 4717.6194 | 58.8005 | 96.1751 | 154.1109 | 16.6808 | 117.8314 | 9682346.2791 | 0 | 5407984.3193 | 0 | 0 | 0 | 2237317.5238 | 6757782.7676 | 17582364.5495 | 12000325.0865 | 53668120.5259 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77393377.3214 | 126585869.979 | 2371373.7057 | 26.8326 | 2884.3069 | 4717.6194 | 58.8005 | 96.1751
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.0332 | 41.3082 | 6.7122 | 4 | 2882.692 | 4714.8879 | 58.7676 | 96.1194 | 154.1015 | 16.6774 | 111.9889 | 9684616.9814 | 0 | 5409903.0421 | 0 | 0 | 0 | 2234357.6713 | 6758262.301 | 17583612.197 | 12001176.6315 | 53671928.8244 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77397185.62 | 126589678.2775 | 3162277.6602 | 26.8489 | 2882.692 | 4714.8879 | 58.7676 | 96.1194
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1038 | 41.3271 | 6.7156 | 4 | 2881.4809 | 4712.7499 | 58.7429 | 96.0758 | 154.0925 | 16.6741 | 123.0937 | 9686809.476 | 0 | 5411753.3672 | 0 | 0 | 0 | 2232458.8511 | 6759098.4608 | 17585787.7131 | 12002661.466 | 53678569.3341 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77403826.1297 | 126596318.7873 | 4216965.0343 | 26.8625 | 2881.4809 | 4712.7499 | 58.7429 | 96.0758
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1381 | 41.3368 | 6.7178 | 4 | 2880.5727 | 4711.2538 | 58.7244 | 96.0453 | 154.0881 | 16.6725 | 116.1251 | 9687870.0529 | 0 | 5412651.8742 | 0 | 0 | 0 | 2230644.3372 | 6759154.8431 | 17585934.4085 | 12002761.5886 | 53679017.1045 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77404273.9001 | 126596766.5576 | 5623413.2519 | 26.8711 | 2880.5727 | 4711.2538 | 58.7244 | 96.0453
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.177 | 41.3473 | 6.7197 | 4 | 2879.8915 | 4710.0565 | 58.7105 | 96.0209 | 154.0831 | 16.6707 | 119.2682 | 9689077.5548 | 0 | 5413671.7559 | 0 | 0 | 0 | 2229556.0142 | 6759599.0767 | 17587090.2133 | 12003550.4491 | 53682545.0641 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77407801.8596 | 126600294.5172 | 7498942.0933 | 26.8787 | 2879.8915 | 4710.0565 | 58.7105 | 96.0209
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1964 | 41.3528 | 6.7209 | 4 | 2879.3808 | 4709.2143 | 58.7001 | 96.0037 | 154.0806 | 16.6698 | 121.6136 | 9689679.2008 | 0 | 5414181.6788 | 0 | 0 | 0 | 2228537.1782 | 6759635.2425 | 17587184.3093 | 12003614.6716 | 53682832.2812 | 961560.8286 | 22763695.9669 | 22763695.9669 | 17318556.9989 | 9110239.6917 | 0 | 77408089.0768 | 126600581.7343 | 10000000 | 26.8836 | 2879.3808 | 4709.2143 | 58.7001 | 96.0037
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.069659 | 0.0095896 | 4 | 677225.5359 | 1990344.417 | 13806.1586 | 40575.8631 | 89.8763 | 17.4004 | 24.8244 | 234242.7019 | 0 | 98308.3317 | 0 | 0 | 0 | 207837.3819 | 210751.4821 | 548332.1252 | 374247.9426 | 1673719.9654 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 25977258.8988 | 76346341.7717 | 100 | 0.038358 | 677225.5359 | 1990344.417 | 13806.1586 | 40575.8631
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3855 | 0.3268 | 0.031253 | 4 | 223650.446 | 626567.1778 | 4559.4169 | 12773.4194 | 118.0679 | 19.0289 | 56.8954 | 503562.3041 | 0 | 241450.5428 | 0 | 0 | 0 | 435148.7981 | 460263.0415 | 1197510.0211 | 817325.1958 | 3655259.9034 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 27958798.8369 | 78327881.7098 | 133.3521 | 0.12501 | 223650.446 | 626567.1778 | 4559.4169 | 12773.4194
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5964 | 0.56842 | 0.058575 | 4 | 123869.8627 | 338848.5476 | 2525.2547 | 6907.886 | 127.9716 | 19.4826 | 66.4549 | 670762.0375 | 0 | 308367.0609 | 0 | 0 | 0 | 544454.95 | 594197.7788 | 1545980.7338 | 1055163.6176 | 4718926.1786 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 29022465.112 | 79391547.9849 | 177.8279 | 0.2343 | 123869.8627 | 338848.5476 | 2525.2547 | 6907.886
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1038 | 0.89455 | 0.097364 | 4 | 77621.0311 | 206952.4761 | 1582.4097 | 4219.0061 | 135.9369 | 19.8109 | 75.7066 | 863690.5816 | 0 | 386912.7561 | 0 | 0 | 0 | 662879.8697 | 746258.4509 | 1941611.4106 | 1325189.6838 | 5926542.7527 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 30230081.6861 | 80599164.5591 | 237.1374 | 0.38946 | 77621.0311 | 206952.4761 | 1582.4097 | 4219.0061
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0017 | 1.3259 | 0.15061 | 4 | 52487.7046 | 136096.0948 | 1070.0329 | 2774.503 | 142.3875 | 20.0545 | 63.8722 | 1088150.6503 | 0 | 480485.1564 | 0 | 0 | 0 | 793838.3629 | 921364.9261 | 2397202.5399 | 1636139.991 | 7317181.6266 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 31620720.56 | 81989803.4329 | 316.2278 | 0.60244 | 52487.7046 | 136096.0948 | 1070.0329 | 2774.503
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4112 | 1.8902 | 0.22238 | 4 | 37370.4111 | 93995.8667 | 761.8464 | 1916.2329 | 147.6161 | 20.237 | 61.151 | 1351382.4907 | 0 | 593108.5194 | 0 | 0 | 0 | 941268.8656 | 1125446.3515 | 2928180.5459 | 1998543.3906 | 8937930.1637 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 33241469.0971 | 83610551.97 | 421.6965 | 0.88951 | 37370.4111 | 93995.8667 | 761.8464 | 1916.2329
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4781 | 2.6224 | 0.31796 | 4 | 27628.998 | 67231.9944 | 563.2545 | 1370.6151 | 151.8295 | 20.3723 | 58.4747 | 1661034.9032 | 0 | 729180.2871 | 0 | 0 | 0 | 1108500.7572 | 1364499.2195 | 3550147.0719 | 2423048.3248 | 10836410.5638 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 35139949.4972 | 85509032.3701 | 562.3413 | 1.2719 | 27628.998 | 67231.9944 | 563.2545 | 1370.6151
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3561 | 3.5611 | 0.44393 | 4 | 21033.383 | 49398.7088 | 428.794 | 1007.0595 | 155.1792 | 20.4681 | 65.9431 | 2023305.7724 | 0 | 892675.3104 | 0 | 0 | 0 | 1296141.9353 | 1642727.977 | 4274041.2264 | 2917120.9598 | 13046013.1814 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 37349552.1148 | 87718634.9877 | 749.8942 | 1.7757 | 21033.383 | 49398.7088 | 428.794 | 1007.0595
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2212 | 4.751 | 0.60827 | 4 | 16399.7269 | 37101.4229 | 334.3306 | 756.3627 | 157.8083 | 20.5287 | 62.8815 | 2444445.9726 | 0 | 1087792.8021 | 0 | 0 | 0 | 1503986.5855 | 1964127.8905 | 5110257.873 | 3487856.0036 | 15598467.1272 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 39902006.0606 | 90271088.9335 | 1000 | 2.4331 | 16399.7269 | 37101.4229 | 334.3306 | 756.3627
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.3159 | 6.253 | 0.82088 | 4 | 13051.1627 | 28391.1647 | 266.0656 | 578.7923 | 159.8537 | 20.555 | 82.6359 | 2933967.7211 | 0 | 1320554.1369 | 0 | 0 | 0 | 1734691.2888 | 2335793.1272 | 6077254.58 | 4147851.1259 | 18550111.9798 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 42853650.9132 | 93222733.7861 | 1333.5214 | 3.2835 | 13051.1627 | 28391.1647 | 266.0656 | 578.7923
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.8286 | 8.118 | 1.0921 | 4 | 10577.9264 | 22108.5726 | 215.6453 | 450.7132 | 161.399 | 20.5436 | 77.8803 | 3494521.4923 | 0 | 1594101.6247 | 0 | 0 | 0 | 1983383.3177 | 2758082.5095 | 7175964.9293 | 4897743.5156 | 21903797.3892 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 46207336.3226 | 96576419.1955 | 1778.2794 | 4.3683 | 10577.9264 | 22108.5726 | 215.6453 | 450.7132
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.966 | 10.4017 | 1.4325 | 4 | 8720.7333 | 17511.4211 | 177.7839 | 356.994 | 162.5186 | 20.4872 | 76.8655 | 4128490.6484 | 0 | 1911788.9567 | 0 | 0 | 0 | 2246002.4366 | 3231649.9963 | 8408090.3878 | 5738694.4586 | 25664716.8845 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 49968255.8179 | 100337338.6908 | 2371.3737 | 5.7298 | 8720.7333 | 17511.4211 | 177.7839 | 356.994
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.7749 | 13.1235 | 1.8488 | 4 | 7309.9479 | 14121.0428 | 149.0232 | 287.8766 | 163.2505 | 20.3754 | 88.4483 | 4826214.9018 | 0 | 2271345.2629 | 0 | 0 | 0 | 2509221.3831 | 3746644.8037 | 9748001.2366 | 6653211.1454 | 29754638.7334 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 54058177.6669 | 104427260.5398 | 3162.2777 | 7.3952 | 7309.9479 | 14121.0428 | 149.0232 | 287.8766
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.0593 | 16.243 | 2.3393 | 4 | 6231.5456 | 11614.4316 | 127.0385 | 236.7759 | 163.6103 | 20.1978 | 96.0531 | 5564073.1735 | 0 | 2663434.8871 | 0 | 0 | 0 | 2752114.4546 | 4282052.781 | 11141022.9663 | 7603977.0996 | 34006675.3622 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 58310214.2956 | 108679297.1686 | 4216.965 | 9.3573 | 6231.5456 | 11614.4316 | 127.0385 | 236.7759
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.3138 | 19.6399 | 2.8892 | 4 | 5406.2416 | 9764.7018 | 110.2135 | 199.0667 | 163.6102 | 19.9503 | 100.9392 | 6304727.5494 | 0 | 3070886.2555 | 0 | 0 | 0 | 2949614.5162 | 4806839.0452 | 12506409.1774 | 8535881.2446 | 38174357.7883 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 62477896.7218 | 112846979.5947 | 5623.4133 | 11.5566 | 5406.2416 | 9764.7018 | 110.2135 | 199.0667
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.8 | 23.129 | 3.4704 | 4 | 4776.2119 | 8404.741 | 97.3695 | 171.342 | 163.2879 | 19.6409 | 102.2043 | 7005908.1004 | 0 | 3471994.2126 | 0 | 0 | 0 | 3081527.8823 | 5288177.7762 | 13758753.8192 | 9390632.1957 | 41996993.9863 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 66300532.9197 | 116669615.7926 | 7498.9421 | 13.8814 | 4776.2119 | 8404.741 | 97.3695 | 171.342
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7056 | 26.4998 | 4.0475 | 4 | 4297.2008 | 7408.3438 | 87.6043 | 151.0291 | 162.7203 | 19.2907 | 97.7978 | 7630996.474 | 0 | 3845235.0059 | 0 | 0 | 0 | 3139200.2444 | 5700018.3724 | 14830278.5706 | 10121969.8562 | 45267698.5234 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 69571237.4568 | 119940320.3297 | 10000 | 16.1899 | 4297.2008 | 7408.3438 | 87.6043 | 151.0291
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.3575 | 29.5714 | 4.5869 | 4 | 3934.7611 | 6680.0223 | 80.2154 | 136.1813 | 162.0125 | 18.9303 | 105.6916 | 8158531.4393 | 0 | 4174573.9517 | 0 | 0 | 0 | 3129002.0894 | 6030221.9174 | 15689400.4604 | 10708338.1992 | 47890068.0573 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 72193606.9908 | 122562689.8637 | 13335.2143 | 18.3476 | 3934.7611 | 6680.0223 | 80.2154 | 136.1813
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3964 | 32.2405 | 5.0658 | 4 | 3661.4211 | 6147.1626 | 74.643 | 125.3182 | 161.2617 | 18.5858 | 109.1169 | 8585460.2804 | 0 | 4453178.7467 | 0 | 0 | 0 | 3068721.0644 | 6281870.4357 | 16344138.2849 | 11155210.2179 | 49888579.0299 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 74192117.9633 | 124561200.8362 | 17782.7941 | 20.2632 | 3661.4211 | 6147.1626 | 74.643 | 125.3182
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.6861 | 34.4625 | 5.4724 | 4 | 3455.7622 | 5756.8123 | 70.4504 | 117.3604 | 160.5457 | 18.2774 | 96.2885 | 8918778.8624 | 0 | 4679985.2397 | 0 | 0 | 0 | 2977772.4014 | 6464849.2363 | 16820211.59 | 11480140.031 | 51341737.3607 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 75645276.2941 | 126014359.167 | 23713.7371 | 21.8896 | 3455.7622 | 5756.8123 | 70.4504 | 117.3604
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.3487 | 36.2607 | 5.8066 | 4 | 3301.2296 | 5469.8353 | 67.3 | 111.51 | 159.9074 | 18.0137 | 104.8669 | 9173961.8165 | 0 | 4860294.5139 | 0 | 0 | 0 | 2875051.813 | 6594630.1759 | 17157874.9731 | 11710602.2282 | 52372415.5206 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 76675954.454 | 127045037.3269 | 31622.7766 | 23.2265 | 3301.2296 | 5469.8353 | 67.3 | 111.51
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.6003 | 37.6862 | 6.0748 | 4 | 3185.1854 | 5258.0715 | 64.9343 | 107.1929 | 159.3646 | 17.7958 | 119.9197 | 9367017.7854 | 0 | 5001245.7313 | 0 | 0 | 0 | 2773799.6689 | 6685404.6424 | 17394051.5145 | 11871797.5706 | 53093316.9131 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 77396855.8466 | 127765938.7195 | 42169.6503 | 24.299 | 3185.1854 | 5258.0715 | 64.9343 | 107.1929
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6714 | 38.7967 | 6.2858 | 4 | 3098.0652 | 5101.3533 | 63.1582 | 103.998 | 158.9195 | 17.6207 | 100.2179 | 9511703.211 | 0 | 5109832.3726 | 0 | 0 | 0 | 2681453.8834 | 6748165.8921 | 17557343.4121 | 11983247.6461 | 53591746.4174 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 77895285.3508 | 128264368.2237 | 56234.1325 | 25.1432 | 3098.0652 | 5101.3533 | 63.1582 | 103.998
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.7971 | 39.6526 | 6.4498 | 4 | 3032.6664 | 4985.0246 | 61.825 | 101.6265 | 158.5631 | 17.4826 | 108.8097 | 9619803.0098 | 0 | 5192813.0387 | 0 | 0 | 0 | 2601690.0132 | 6791579.3641 | 17670296.3608 | 12060340.3545 | 53936522.1412 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78240061.0746 | 128609143.9475 | 74989.4209 | 25.7991 | 3032.6664 | 4985.0246 | 61.825 | 101.6265
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.1741 | 40.3057 | 6.5758 | 4 | 2983.5769 | 4898.5091 | 60.8243 | 99.8627 | 158.2834 | 17.3754 | 112.0592 | 9700250.6417 | 0 | 5255695.4212 | 0 | 0 | 0 | 2535179.1074 | 6821538.8164 | 17748244.7103 | 12113541.7047 | 54174450.4018 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78477989.3352 | 128847072.2081 | 100000 | 26.3033 | 2983.5769 | 4898.5091 | 60.8243 | 99.8627
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.977 | 40.8023 | 6.6722 | 4 | 2946.7326 | 4834.0182 | 60.0731 | 98.548 | 158.0662 | 17.2929 | 122.251 | 9760245.816 | 0 | 5303264.9225 | 0 | 0 | 0 | 2481304.8308 | 6842478.072 | 17802724.3582 | 12150725.1839 | 54340743.1835 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78644282.1169 | 129013364.9898 | 133352.1432 | 26.6886 | 2946.7326 | 4834.0182 | 60.0731 | 98.548
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3413 | 41.1788 | 6.7454 | 4 | 2919.0821 | 4785.8662 | 59.5094 | 97.5664 | 157.899 | 17.2297 | 107.8194 | 9805056.038 | 0 | 5339191.8457 | 0 | 0 | 0 | 2438546.345 | 6857289.7492 | 17841261.3039 | 12177027.4412 | 54458372.723 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78761911.6564 | 129130994.5293 | 177827.941 | 26.9817 | 2919.0821 | 4785.8662 | 59.5094 | 97.5664
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.3741 | 41.464 | 6.801 | 4 | 2898.3334 | 4749.8574 | 59.0864 | 96.8323 | 157.7707 | 17.1815 | 106.7679 | 9838637.1875 | 0 | 5366348.0241 | 0 | 0 | 0 | 2405156.4366 | 6867955.2428 | 17869010.7305 | 12195966.995 | 54543074.6165 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78846613.5499 | 129215696.4228 | 237137.3706 | 27.2041 | 2898.3334 | 4749.8574 | 59.0864 | 96.8323
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.1512 | 41.679 | 6.843 | 4 | 2882.7657 | 4722.9268 | 58.7691 | 96.2833 | 157.6733 | 17.145 | 108.7548 | 9863712.6828 | 0 | 5386760.6023 | 0 | 0 | 0 | 2379283.4403 | 6875605.1229 | 17888914.1492 | 12209551.4872 | 54603827.4846 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78907366.4181 | 129276449.291 | 316227.766 | 27.3721 | 2882.7657 | 4722.9268 | 58.7691 | 96.2833
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.736 | 41.8408 | 6.8747 | 4 | 2871.0864 | 4702.7694 | 58.531 | 95.8723 | 157.5994 | 17.1174 | 116.843 | 9882468.255 | 0 | 5402105.6528 | 0 | 0 | 0 | 2359409.7495 | 6881153.6264 | 17903350.2171 | 12219404.4003 | 54647891.9012 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78951430.8346 | 129320513.7075 | 421696.5034 | 27.4988 | 2871.0864 | 4702.7694 | 58.531 | 95.8723
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.177 | 41.9629 | 6.8986 | 4 | 2862.3252 | 4687.6663 | 58.3524 | 95.5644 | 157.5434 | 17.0965 | 118.5265 | 9896551.2117 | 0 | 5413671.7559 | 0 | 0 | 0 | 2344267.2224 | 6885251.1741 | 17914011.1958 | 12226680.7373 | 54680433.2972 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 78983972.2306 | 129353055.1035 | 562341.3252 | 27.5943 | 2862.3252 | 4687.6663 | 58.3524 | 95.5644
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.513 | 42.0558 | 6.9167 | 4 | 2855.7534 | 4676.3258 | 58.2184 | 95.3332 | 157.5005 | 17.0805 | 109.033 | 9907245.7866 | 0 | 5422479.8797 | 0 | 0 | 0 | 2332858.0109 | 6888407.6341 | 17922223.6573 | 12232285.911 | 54705500.8796 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79009039.813 | 129378122.6859 | 749894.2093 | 27.6666 | 2855.7534 | 4676.3258 | 58.2184 | 95.3332
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.7519 | 42.1223 | 6.9299 | 4 | 2850.8242 | 4667.9041 | 58.1179 | 95.1615 | 157.4699 | 17.0691 | 98.9035 | 9914828.5842 | 0 | 5428741.2708 | 0 | 0 | 0 | 2323927.7633 | 6890324.0711 | 17927209.8333 | 12235689.0785 | 54720720.6013 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79024259.5347 | 129393342.4076 | 1000000 | 27.7198 | 2850.8242 | 4667.9041 | 58.1179 | 95.1615
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.9493 | 42.1767 | 6.9403 | 4 | 2847.1272 | 4661.4902 | 58.0425 | 95.0308 | 157.4446 | 17.0597 | 111.1052 | 9921086.7546 | 0 | 5433913.8193 | 0 | 0 | 0 | 2317567.568 | 6892301.5753 | 17932354.8936 | 12239200.6879 | 54736425.2988 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79039964.2322 | 129409047.1051 | 1333521.4322 | 27.7613 | 2847.1272 | 4661.4902 | 58.0425 | 95.0308
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0855 | 42.2146 | 6.9479 | 4 | 2844.3545 | 4656.7505 | 57.986 | 94.9342 | 157.4271 | 17.0532 | 112.1903 | 9925392.8963 | 0 | 5437479.7 | 0 | 0 | 0 | 2312513.0767 | 6893400.4125 | 17935213.8425 | 12241151.9793 | 54745151.9073 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79048690.8407 | 129417773.7136 | 1778279.41 | 27.7914 | 2844.3545 | 4656.7505 | 57.986 | 94.9342
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.1922 | 42.2441 | 6.9536 | 4 | 2842.2751 | 4653.1713 | 57.9436 | 94.8612 | 157.4134 | 17.0481 | 120.4232 | 9928767.6876 | 0 | 5440276.0082 | 0 | 0 | 0 | 2308805.2792 | 6894361.1003 | 17937713.355 | 12242857.9479 | 54752781.3783 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79056320.3117 | 129425403.1846 | 2371373.7057 | 27.8145 | 2842.2751 | 4653.1713 | 57.9436 | 94.8612
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.2628 | 42.264 | 6.9577 | 4 | 2840.7156 | 4650.5415 | 57.9118 | 94.8076 | 157.4043 | 17.0447 | 130.0392 | 9930993.9409 | 0 | 5442123.7458 | 0 | 0 | 0 | 2305813.2466 | 6894783.064 | 17938811.218 | 12243607.262 | 54756132.4773 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79059671.4108 | 129428754.2837 | 3162277.6602 | 27.8309 | 2840.7156 | 4650.5415 | 57.9118 | 94.8076
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.3313 | 42.2826 | 6.9611 | 4 | 2839.5461 | 4648.4823 | 57.888 | 94.7656 | 157.3955 | 17.0414 | 125.6091 | 9933158.9732 | 0 | 5443918.2108 | 0 | 0 | 0 | 2303895.529 | 6895579.3581 | 17940883.012 | 12245021.3039 | 54762456.3871 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79065995.3205 | 129435078.1934 | 4216965.0343 | 27.8446 | 2839.5461 | 4648.4823 | 57.888 | 94.7656
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.3749 | 42.2947 | 6.9635 | 4 | 2838.6691 | 4646.9824 | 57.8701 | 94.735 | 157.3898 | 17.0393 | 130.3712 | 9934531.771 | 0 | 5445057.8618 | 0 | 0 | 0 | 2302287.4696 | 6895932.0699 | 17941800.6958 | 12245647.642 | 54765257.5101 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79068796.4436 | 129437879.3165 | 5623413.2519 | 27.8542 | 2838.6691 | 4646.9824 | 57.8701 | 94.735
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4091 | 42.3042 | 6.9654 | 4 | 2838.0114 | 4645.8488 | 57.8567 | 94.7119 | 157.3854 | 17.0377 | 122.1198 | 9935612.5013 | 0 | 5445954.9919 | 0 | 0 | 0 | 2301114.2971 | 6896245.8982 | 17942617.2126 | 12246204.9315 | 54767749.8327 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79071288.7661 | 129440371.639 | 7498942.0933 | 27.8615 | 2838.0114 | 4645.8488 | 57.8567 | 94.7119
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4286 | 42.3098 | 6.9666 | 4 | 2837.5182 | 4645.0337 | 57.8466 | 94.6953 | 157.3829 | 17.0368 | 125.8941 | 9936224.3032 | 0 | 5446464.1574 | 0 | 0 | 0 | 2300101.2765 | 6896287.9975 | 17942726.7463 | 12246279.6905 | 54768084.1714 | 961560.8286 | 23341978.1048 | 23341978.1048 | 17712525.3824 | 9314579.3857 | 0 | 79071623.1048 | 129440705.9777 | 10000000 | 27.8665 | 2837.5182 | 4645.0337 | 57.8466 | 94.6953
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.06864 | 0.0097833 | 4 | 679068.2262 | 1996610.6742 | 13843.7243 | 40703.6092 | 90.4195 | 17.7624 | 25.2977 | 236518.0421 | 0 | 98026.621 | 0 | 0 | 0 | 209913.3159 | 212338.6118 | 552461.5113 | 377066.3334 | 1686324.4356 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 26574005.5977 | 78133449.8995 | 100 | 0.039133 | 679068.2262 | 1996610.6742 | 13843.7243 | 40703.6092
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4929 | 0.3429 | 0.033292 | 4 | 215461.613 | 602641.9772 | 4392.4764 | 12285.6718 | 120.5403 | 19.4997 | 43.2989 | 525807.7697 | 0 | 247560.683 | 0 | 0 | 0 | 455004.4342 | 479065.4259 | 1246429.9683 | 850714.0649 | 3804582.3459 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 28692263.508 | 80251707.8098 | 133.3521 | 0.13317 | 215461.613 | 602641.9772 | 4392.4764 | 12285.6718
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7233 | 0.59285 | 0.062247 | 4 | 119600.5777 | 326675.3582 | 2438.2195 | 6659.719 | 130.5443 | 19.9538 | 55.1981 | 697727.2841 | 0 | 315157.9943 | 0 | 0 | 0 | 566451.2925 | 615941.2627 | 1602552.8185 | 1093775.2278 | 4891605.88 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 29779287.0421 | 81338731.3439 | 177.8279 | 0.24899 | 119600.5777 | 326675.3582 | 2438.2195 | 6659.719
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2696 | 0.93236 | 0.1033 | 4 | 75094.8657 | 199878.8001 | 1530.9104 | 4074.7997 | 138.6887 | 20.2866 | 69.8341 | 898001.9941 | 0 | 395296.6275 | 0 | 0 | 0 | 689344.5224 | 773230.8261 | 2011787.9982 | 1373086.6468 | 6140748.6151 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 31028429.7772 | 82587874.079 | 237.1374 | 0.41319 | 75094.8657 | 199878.8001 | 1530.9104 | 4074.7997
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2233 | 1.3826 | 0.15963 | 4 | 50855.6037 | 131602.157 | 1036.7603 | 2682.888 | 145.3038 | 20.5343 | 81.8213 | 1131792.1336 | 0 | 491097.1353 | 0 | 0 | 0 | 826172.8446 | 955134.2242 | 2485063.3265 | 1696106.7833 | 7585366.4475 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 32473047.6096 | 84032491.9114 | 316.2278 | 0.63853 | 50855.6037 | 131602.157 | 1036.7603 | 2682.888
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6935 | 1.9699 | 0.23549 | 4 | 36251.7631 | 90988.0281 | 739.0412 | 1854.914 | 150.6422 | 20.7189 | 57.7955 | 1404855.6865 | 0 | 605939.0609 | 0 | 0 | 0 | 978975.7241 | 1166010.4839 | 3033720.0974 | 2070576.3032 | 9260077.356 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 34147758.5182 | 85707202.82 | 421.6965 | 0.94196 | 36251.7631 | 90988.0281 | 739.0412 | 1854.914
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8265 | 2.7297 | 0.3364 | 4 | 26829.0213 | 65146.4421 | 546.9459 | 1328.0983 | 154.9339 | 20.8551 | 65.2715 | 1725010.5551 | 0 | 744220.3541 | 0 | 0 | 0 | 1151110.5751 | 1411933.1789 | 3673560.5042 | 2507280.5282 | 11213115.6957 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 36100796.8578 | 87660241.1596 | 562.3413 | 1.3456 | 26829.0213 | 65146.4421 | 546.9459 | 1328.0983
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7971 | 3.7054 | 0.46938 | 4 | 20442.5115 | 47904.0137 | 416.7482 | 976.5881 | 158.3577 | 20.9515 | 69.2183 | 2100512.7428 | 0 | 910775.2359 | 0 | 0 | 0 | 1345309.3864 | 1699072.9724 | 4420639.3464 | 3017177.189 | 13493486.873 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 38381168.0351 | 89940612.3369 | 749.8942 | 1.8775 | 20442.5115 | 47904.0137 | 416.7482 | 976.5881
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.7741 | 4.9414 | 0.64275 | 4 | 15951.9459 | 36006.0807 | 325.202 | 734.0327 | 161.044 | 21.0117 | 54.9036 | 2536716.2785 | 0 | 1109391.6921 | 0 | 0 | 0 | 1560111.3713 | 2030425.5434 | 5282750.7663 | 3605585.9477 | 16124981.5992 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 41012662.7614 | 92572107.0632 | 1000 | 2.571 | 15951.9459 | 36006.0807 | 325.202 | 734.0327
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.0003 | 6.4996 | 0.86683 | 4 | 12704.5549 | 27574.6824 | 258.9995 | 562.1472 | 163.1327 | 21.0364 | 77.5863 | 3043120.8445 | 0 | 1346027.0772 | 0 | 0 | 0 | 1797958.1353 | 2412971.3622 | 6278056.5161 | 4284902.5734 | 19163036.5087 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 44050717.6709 | 95610161.9727 | 1333.5214 | 3.4673 | 12704.5549 | 27574.6824 | 258.9995 | 562.1472
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6936 | 8.4384 | 1.1527 | 4 | 10304.7571 | 21486.964 | 210.0764 | 438.0408 | 164.7146 | 21.0217 | 64.5459 | 3624420.4072 | 0 | 1624816.0555 | 0 | 0 | 0 | 2055937.647 | 2849017.9028 | 7412560.1692 | 5059224.6283 | 22625976.8101 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 47513657.9722 | 99073102.274 | 1778.2794 | 4.6108 | 10304.7571 | 21486.964 | 210.0764 | 438.0408
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.0092 | 10.8033 | 1.5107 | 4 | 8502.0601 | 17034.6376 | 173.326 | 347.2741 | 165.8553 | 20.9599 | 76.5879 | 4278945.5102 | 0 | 1947187.8083 | 0 | 0 | 0 | 2325751.6789 | 3335235.149 | 8677597.7068 | 5922638.7417 | 26487356.5948 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 51375037.7569 | 102934482.0587 | 2371.3737 | 6.0427 | 8502.0601 | 17034.6376 | 173.326 | 347.2741
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.007 | 13.6167 | 1.9476 | 4 | 7132.5065 | 13750.88 | 145.4058 | 280.3303 | 166.5984 | 20.8401 | 94.2902 | 4997915.4124 | 0 | 2311399.6675 | 0 | 0 | 0 | 2595278.7189 | 3862791.5816 | 10050191.3277 | 6859462.0919 | 30677038.8001 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 55564719.9622 | 107124164.264 | 3162.2777 | 7.7903 | 7132.5065 | 13750.88 | 145.4058 | 280.3303
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4702 | 16.8323 | 2.4609 | 4 | 6085.8017 | 11323.7203 | 124.0673 | 230.8494 | 166.9591 | 20.6517 | 87.2798 | 5756035.5571 | 0 | 2707517.941 | 0 | 0 | 0 | 2842559.7247 | 4409384.1569 | 11472313.0872 | 7830089.4145 | 35017899.8815 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 59905581.0436 | 111465025.3454 | 4216.965 | 9.8435 | 6085.8017 | 11323.7203 | 124.0673 | 230.8494
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.8802 | 20.3243 | 3.0343 | 4 | 5285.0955 | 9533.1405 | 107.7438 | 194.346 | 166.9508 | 20.3908 | 100.907 | 6514831.9627 | 0 | 3118120.6486 | 0 | 0 | 0 | 3042363.873 | 4943373.4289 | 12861643.6367 | 8778336.0624 | 39258669.6123 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 64146350.7745 | 115705795.0763 | 5623.4133 | 12.1372 | 5285.0955 | 9533.1405 | 107.7438 | 194.346
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.454 | 23.8933 | 3.6376 | 4 | 4674.1856 | 8217.7232 | 95.2896 | 167.5294 | 166.6155 | 20.0673 | 100.4366 | 7229427.6354 | 0 | 3520370.8052 | 0 | 0 | 0 | 3173182.2307 | 5429962.4618 | 14127648.4871 | 9642410.3866 | 43123002.0068 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 68010683.169 | 119570127.4708 | 7498.9421 | 14.5503 | 4674.1856 | 8217.7232 | 95.2896 | 167.5294
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3964 | 27.3291 | 4.2341 | 4 | 4209.9786 | 7254.2517 | 85.8261 | 147.8877 | 166.0344 | 19.7033 | 112.1674 | 7864195.8142 | 0 | 3893451.8324 | 0 | 0 | 0 | 3228137.2934 | 5844456.1266 | 15206075.9787 | 10378459.3091 | 46414776.3544 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 71302457.5165 | 122861901.8183 | 10000 | 16.9365 | 4209.9786 | 7254.2517 | 85.8261 | 147.8877
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.036 | 30.4482 | 4.7894 | 4 | 3858.9301 | 6550.2374 | 78.6695 | 133.5354 | 165.3161 | 19.3311 | 105.1388 | 8397883.0457 | 0 | 4221471.7583 | 0 | 0 | 0 | 3214289.2673 | 6175121.1878 | 16066398.6392 | 10965647.2027 | 49040811.101 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 73928492.2632 | 125487936.565 | 13335.2143 | 19.1578 | 3858.9301 | 6550.2374 | 78.6695 | 133.5354
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.0112 | 33.1451 | 5.2802 | 4 | 3594.2986 | 6035.458 | 73.2746 | 123.041 | 164.5602 | 18.9777 | 112.5446 | 8827640.3669 | 0 | 4497582.7066 | 0 | 0 | 0 | 3149721.7871 | 6425228.4957 | 16717126.5501 | 11409782.373 | 51027082.2794 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 75914763.4416 | 127474207.7433 | 17782.7941 | 21.1209 | 3594.2986 | 6035.458 | 73.2746 | 123.041
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.2519 | 35.3906 | 5.6963 | 4 | 3395.2619 | 5658.1242 | 69.217 | 115.3485 | 163.8405 | 18.6617 | 118.2653 | 9163433.7616 | 0 | 4722512.7952 | 0 | 0 | 0 | 3056014.9501 | 6607364.9876 | 17191008.3409 | 11733216.4326 | 52473551.2679 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 77361232.4301 | 128920676.7319 | 23713.7371 | 22.7851 | 3395.2619 | 5658.1242 | 69.217 | 115.3485
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8567 | 37.2032 | 6.0373 | 4 | 3245.7462 | 5380.7659 | 66.1689 | 109.6942 | 163.2015 | 18.3925 | 110.9949 | 9419889.6994 | 0 | 4900873.5922 | 0 | 0 | 0 | 2951035.7727 | 6736001.635 | 17525694.5105 | 11961646.6204 | 53495141.8301 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 78382822.9923 | 129942267.294 | 31622.7766 | 24.1494 | 3245.7462 | 5380.7659 | 66.1689 | 109.6942
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0307 | 38.632 | 6.31 | 4 | 3133.4934 | 5176.2709 | 63.8805 | 105.5253 | 162.6619 | 18.1716 | 118.5811 | 9612793.3926 | 0 | 5039465.4819 | 0 | 0 | 0 | 2847532.6493 | 6824918.6942 | 17757038.4591 | 12119543.619 | 54201292.296 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 79088973.4582 | 130648417.7599 | 42169.6503 | 25.2399 | 3133.4934 | 5176.2709 | 63.8805 | 105.5253
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.0481 | 39.7465 | 6.5245 | 4 | 3049.2341 | 5024.8389 | 62.1628 | 102.4381 | 162.2191 | 17.994 | 102.8389 | 9757666.2378 | 0 | 5146422.13 | 0 | 0 | 0 | 2753942.4305 | 6886632.0114 | 17917603.8511 | 12229132.7983 | 54691399.4591 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 79579080.6212 | 131138524.923 | 56234.1325 | 26.0981 | 3049.2341 | 5024.8389 | 62.1628 | 102.4381
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1413 | 40.6076 | 6.6913 | 4 | 2985.9919 | 4912.3551 | 60.8735 | 100.145 | 161.8638 | 17.8536 | 115.2155 | 9866250.1579 | 0 | 5228396.9648 | 0 | 0 | 0 | 2673646.4188 | 6929634.4812 | 18029487.4565 | 12305495.658 | 55032911.1372 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 79920592.2993 | 131480036.6011 | 74989.4209 | 26.7652 | 2985.9919 | 4912.3551 | 60.8735 | 100.145
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4776 | 41.2607 | 6.8191 | 4 | 2938.5269 | 4828.7888 | 59.9058 | 98.4414 | 161.5869 | 17.7454 | 115.0714 | 9946530.093 | 0 | 5290100.418 | 0 | 0 | 0 | 2606468.9442 | 6958808.7875 | 18105393.0172 | 12357302.7629 | 55264604.0228 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80152285.185 | 131711729.4867 | 100000 | 27.2763 | 2938.5269 | 4828.7888 | 59.9058 | 98.4414
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.2681 | 41.7618 | 6.9171 | 4 | 2902.9054 | 4766.3776 | 59.1797 | 97.1691 | 161.3699 | 17.6613 | 113.3875 | 10007040.9866 | 0 | 5337266.8 | 0 | 0 | 0 | 2552611.8854 | 6979798.6721 | 18160004.3912 | 12394576.1477 | 55431298.883 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80318980.0451 | 131878424.3469 | 133352.1432 | 27.6685 | 2902.9054 | 4766.3776 | 59.1797 | 97.1691
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6176 | 42.1403 | 6.9915 | 4 | 2876.1745 | 4719.8091 | 58.6347 | 96.2197 | 161.2034 | 17.5971 | 110.2929 | 10052059.1847 | 0 | 5372747.3555 | 0 | 0 | 0 | 2509784.5273 | 6994490.5163 | 18198229.5562 | 12420665.6083 | 55547976.7483 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80435657.9104 | 131995102.2122 | 177827.941 | 27.9662 | 2876.1745 | 4719.8091 | 58.6347 | 96.2197
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.6387 | 42.427 | 7.048 | 4 | 2856.1174 | 4684.9862 | 58.2258 | 95.5098 | 161.0758 | 17.5482 | 117.9018 | 10085784.501 | 0 | 5399554.4943 | 0 | 0 | 0 | 2476361.6249 | 7005063.2419 | 18225737.6193 | 12439440.4266 | 55631941.9081 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80519623.0702 | 132079067.372 | 237137.3706 | 28.192 | 2856.1174 | 4684.9862 | 58.2258 | 95.5098
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.4035 | 42.6422 | 7.0905 | 4 | 2841.0693 | 4658.9623 | 57.919 | 94.9792 | 160.9793 | 17.5113 | 95.7403 | 10110851.7326 | 0 | 5419610.9164 | 0 | 0 | 0 | 2450400.9379 | 7012536.7989 | 18245182.2816 | 12452711.8082 | 55691294.4754 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80578975.6375 | 132138419.9393 | 316227.766 | 28.3622 | 2841.0693 | 4658.9623 | 57.919 | 94.9792
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.9734 | 42.8028 | 7.1225 | 4 | 2829.7803 | 4639.514 | 57.6889 | 94.5828 | 160.9068 | 17.4837 | 113.6424 | 10129422.9994 | 0 | 5434544.5619 | 0 | 0 | 0 | 2430351.1013 | 7017784.2784 | 18258835.1469 | 12462030.1693 | 55732968.2573 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80620649.4194 | 132180093.7212 | 421696.5034 | 28.4901 | 2829.7803 | 4639.514 | 57.6889 | 94.5828
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4091 | 42.9254 | 7.1468 | 4 | 2821.3121 | 4624.9087 | 57.5163 | 94.285 | 160.8511 | 17.4625 | 123.4206 | 10143561.309 | 0 | 5445954.9919 | 0 | 0 | 0 | 2415213.5268 | 7021844.6328 | 18269399.3562 | 12469240.4592 | 55765214.2759 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80652895.438 | 132212339.7398 | 562341.3252 | 28.587 | 2821.3121 | 4624.9087 | 57.5163 | 94.285
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.7381 | 43.018 | 7.165 | 4 | 2814.9603 | 4613.9587 | 57.3868 | 94.0618 | 160.8089 | 17.4464 | 125.5857 | 10154199.8155 | 0 | 5454565.3316 | 0 | 0 | 0 | 2403745.9828 | 7024879.3406 | 18277295.0434 | 12474629.428 | 55789314.9419 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80676996.1041 | 132236440.4059 | 749894.2093 | 28.6601 | 2814.9603 | 4613.9587 | 57.3868 | 94.0618
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.9692 | 43.0836 | 7.1784 | 4 | 2810.1962 | 4605.8416 | 57.2897 | 93.8963 | 160.7791 | 17.4351 | 112.4667 | 10161654.2458 | 0 | 5460614.4867 | 0 | 0 | 0 | 2394715.0843 | 7026623.6886 | 18281833.479 | 12477727.0035 | 55803167.9879 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80690849.15 | 132250293.4518 | 1000000 | 28.7136 | 2810.1962 | 4605.8416 | 57.2897 | 93.8963
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.1667 | 43.1388 | 7.189 | 4 | 2806.6231 | 4599.6257 | 57.2168 | 93.7696 | 160.7537 | 17.4255 | 113.2685 | 10168014.8168 | 0 | 5465779.4753 | 0 | 0 | 0 | 2388415.3351 | 7028661.7546 | 18287136.1087 | 12481346.1572 | 55819353.6477 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80707034.8098 | 132266479.1116 | 1333521.4322 | 28.7559 | 2806.6231 | 4599.6257 | 57.2168 | 93.7696
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.2936 | 43.175 | 7.1965 | 4 | 2803.9433 | 4595.0841 | 57.1622 | 93.677 | 160.7372 | 17.4193 | 115.5013 | 10172091.61 | 0 | 5469097.945 | 0 | 0 | 0 | 2383200.5734 | 7029512.1501 | 18289348.6633 | 12482856.2713 | 55826107.2131 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80713788.3753 | 132273232.6771 | 1778279.41 | 28.7858 | 2803.9433 | 4595.0841 | 57.1622 | 93.677
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.3908 | 43.2026 | 7.2021 | 4 | 2801.9336 | 4591.6681 | 57.1212 | 93.6074 | 160.7246 | 17.4145 | 113.1336 | 10175213.5907 | 0 | 5471640.957 | 0 | 0 | 0 | 2379319.3314 | 7030207.8129 | 18291158.6352 | 12484091.6142 | 55831631.9414 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80719313.1036 | 132278757.4054 | 2371373.7057 | 28.8084 | 2801.9336 | 4591.6681 | 57.1212 | 93.6074
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.4808 | 43.2275 | 7.2067 | 4 | 2800.4264 | 4589.0133 | 57.0905 | 93.5532 | 160.713 | 17.4101 | 125.7658 | 10178105.3748 | 0 | 5473994.5656 | 0 | 0 | 0 | 2376769.4955 | 7031259.08 | 18293893.8166 | 12485958.4318 | 55839980.7643 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80727661.9264 | 132287106.2282 | 3162277.6602 | 28.8269 | 2800.4264 | 4589.0133 | 57.0905 | 93.5532
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.5345 | 43.2428 | 7.2099 | 4 | 2799.2962 | 4587.0987 | 57.0674 | 93.5142 | 160.706 | 17.4074 | 118.7909 | 10179827.1071 | 0 | 5475398.9993 | 0 | 0 | 0 | 2374553.5307 | 7031614.0585 | 18294817.3979 | 12486588.795 | 55842799.8886 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80730481.0507 | 132289925.3525 | 4216965.0343 | 28.8396 | 2799.2962 | 4587.0987 | 57.0674 | 93.5142
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.5734 | 43.254 | 7.2122 | 4 | 2798.4486 | 4585.6707 | 57.0502 | 93.4851 | 160.7009 | 17.4055 | 123.006 | 10181072.9973 | 0 | 5476415.9468 | 0 | 0 | 0 | 2372858.9893 | 7031835.694 | 18295394.048 | 12486982.3705 | 55844560.0459 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80732241.2081 | 132291685.5099 | 5623413.2519 | 28.8489 | 2798.4486 | 4585.6707 | 57.0502 | 93.4851
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6077 | 43.2636 | 7.2141 | 4 | 2797.8129 | 4584.5721 | 57.0372 | 93.4627 | 160.6965 | 17.4038 | 115.0436 | 10182171.601 | 0 | 5477311.7901 | 0 | 0 | 0 | 2371696.7798 | 7032160.2666 | 18296238.5194 | 12487558.7396 | 55847137.6965 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80734818.8586 | 132294263.1604 | 7498942.0933 | 28.8564 | 2797.8129 | 4584.5721 | 57.0372 | 93.4627
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6271 | 43.2693 | 7.2154 | 4 | 2797.3362 | 4583.7826 | 57.0275 | 93.4466 | 160.6939 | 17.4029 | 117.2544 | 10182793.5288 | 0 | 5477820.2253 | 0 | 0 | 0 | 2370689.3542 | 7032208.2123 | 18296363.2641 | 12487643.8804 | 55847518.4651 | 961560.8286 | 23926120.3335 | 23926120.3335 | 18112060.8521 | 9521263.1161 | 0 | 80735199.6273 | 132294643.929 | 10000000 | 28.8615 | 2797.3362 | 4583.7826 | 57.0275 | 93.4466
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.067618 | 0.0099637 | 4 | 681887.1608 | 2005782.0373 | 13901.1921 | 40890.5799 | 90.9411 | 18.1229 | 25.2138 | 238747.7604 | 0 | 97739.752 | 0 | 0 | 0 | 211998.0289 | 213909.3611 | 556548.2788 | 379855.6362 | 1698798.8176 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 27176482.2993 | 79940059.2435 | 100 | 0.039855 | 681887.1608 | 2005782.0373 | 13901.1921 | 40890.5799
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5829 | 0.35699 | 0.035404 | 4 | 207695.2771 | 580273.7135 | 4234.1492 | 11829.6645 | 122.8391 | 19.962 | 56.9495 | 545856.3828 | 0 | 252651.1473 | 0 | 0 | 0 | 472158.4154 | 495559.7187 | 1289344.7349 | 880004.275 | 3935574.6741 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 29413258.1558 | 82176835.1 | 133.3521 | 0.14162 | 207695.2771 | 580273.7135 | 4234.1492 | 11829.6645
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8593 | 0.61921 | 0.066094 | 4 | 115568.5418 | 315145.894 | 2356.021 | 6424.6753 | 133.1796 | 20.4276 | 58.8591 | 726330.3006 | 0 | 322394.9248 | 0 | 0 | 0 | 590124.0568 | 639151.22 | 1662940.3666 | 1134990.9702 | 5075931.839 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 30553615.3207 | 83317192.2649 | 177.8279 | 0.26438 | 115568.5418 | 315145.894 | 2356.021 | 6424.6753
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4398 | 0.97172 | 0.10948 | 4 | 72708.178 | 193198.7015 | 1482.2546 | 3938.6169 | 141.4632 | 20.7631 | 63.2665 | 933377.2627 | 0 | 403859.8601 | 0 | 0 | 0 | 716742.6751 | 801052.1212 | 2084173.3009 | 1422491.1033 | 6361696.3232 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 31839379.8049 | 84602956.7491 | 237.1374 | 0.43791 | 72708.178 | 193198.7015 | 1482.2546 | 3938.6169
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4233 | 1.4365 | 0.16889 | 4 | 49312.5591 | 127414.5499 | 1005.3032 | 2597.5179 | 148.1663 | 21.012 | 63.3931 | 1173570.8853 | 0 | 500631.1891 | 0 | 0 | 0 | 855954.9192 | 986761.2275 | 2567350.3014 | 1752269.3345 | 7836537.8569 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 33314221.3386 | 86077798.2828 | 316.2278 | 0.67557 | 49312.5591 | 127414.5499 | 1005.3032 | 2597.5179
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9519 | 2.0466 | 0.24893 | 4 | 35193.5431 | 88183.9669 | 717.468 | 1797.7494 | 153.6317 | 21.1994 | 47.49 | 1456530.5118 | 0 | 617623.8167 | 0 | 0 | 0 | 1014129.9287 | 1204430.8603 | 3133682.0359 | 2138802.3802 | 9565199.5337 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 35042883.0154 | 87806459.9596 | 421.6965 | 0.99572 | 35193.5431 | 88183.9669 | 717.468 | 1797.7494
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1749 | 2.8391 | 0.35547 | 4 | 26071.7513 | 63179.5581 | 531.5079 | 1288.0007 | 158.043 | 21.3379 | 68.805 | 1789896.0732 | 0 | 759184.8091 | 0 | 0 | 0 | 1194148.3627 | 1459859.4056 | 3798254.7149 | 2592386.8893 | 11593730.2547 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 37071413.7364 | 89834990.6806 | 562.3413 | 1.4219 | 26071.7513 | 63179.5581 | 531.5079 | 1288.0007
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.2186 | 3.8484 | 0.49552 | 4 | 19882.8047 | 46503.2674 | 405.3379 | 948.032 | 161.5277 | 21.4345 | 68.2473 | 2177014.187 | 0 | 927993.2622 | 0 | 0 | 0 | 1392975.7279 | 1754213.4391 | 4564103.5298 | 3115094.442 | 13931394.588 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 39409078.0697 | 92172655.0139 | 749.8942 | 1.9821 | 19882.8047 | 46503.2674 | 405.3379 | 948.032
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.3271 | 5.1355 | 0.67839 | 4 | 15527.5006 | 34971.9902 | 316.5491 | 712.9513 | 164.2848 | 21.4946 | 56.2315 | 2630288.9421 | 0 | 1130892.7144 | 0 | 0 | 0 | 1616793.0857 | 2097410.1494 | 5457030.9709 | 3724535.7684 | 16656951.6308 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 42134635.1126 | 94898212.0568 | 1000 | 2.7135 | 15527.5006 | 34971.9902 | 316.5491 | 712.9513
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.6996 | 6.7543 | 0.91447 | 4 | 12375.7906 | 26800.461 | 252.2972 | 546.3636 | 166.4206 | 21.5176 | 68.3385 | 3154966.0127 | 0 | 1371934.1114 | 0 | 0 | 0 | 1863069.573 | 2492088.1819 | 6483902.2516 | 4425396.5176 | 19791356.6482 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 45269040.1299 | 98032617.0741 | 1333.5214 | 3.6579 | 12375.7906 | 26800.461 | 252.2972 | 546.3636
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5413 | 8.7613 | 1.2151 | 4 | 10045.4812 | 20901.7162 | 204.7907 | 426.1098 | 168.0325 | 21.4995 | 65.0983 | 3754823.4152 | 0 | 1654777.9146 | 0 | 0 | 0 | 2127870.0661 | 2939613.8444 | 7648272.2255 | 5220102.9502 | 23345460.416 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 48823143.8977 | 101586720.8419 | 1778.2794 | 4.8602 | 10045.4812 | 20901.7162 | 204.7907 | 426.1098
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.0466 | 11.2114 | 1.5912 | 4 | 8294.3822 | 16584.2018 | 169.0922 | 338.0914 | 169.1963 | 21.4321 | 72.7038 | 4431016.7812 | 0 | 1982233.3247 | 0 | 0 | 0 | 2405831.8514 | 3439441.9634 | 8948722.4621 | 6107686.9583 | 27314933.3412 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 52792616.8229 | 105556193.7671 | 2371.3737 | 6.3649 | 8294.3822 | 16584.2018 | 169.0922 | 338.0914
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.2398 | 14.1193 | 2.0494 | 4 | 6963.8953 | 13400.4897 | 141.9684 | 273.1871 | 169.9509 | 21.3038 | 74.6398 | 5171875.7144 | 0 | 2351302.4601 | 0 | 0 | 0 | 2682124.4215 | 3980068.0125 | 10355320.5442 | 7067719.052 | 31608410.2048 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 57086093.6865 | 109849670.6307 | 3162.2777 | 8.1974 | 6963.8953 | 13400.4897 | 141.9684 | 273.1871
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.8929 | 17.4352 | 2.5861 | 4 | 5947.24 | 11047.885 | 121.2425 | 225.2261 | 170.3123 | 21.1039 | 75.7578 | 5951055.8278 | 0 | 2751785.2449 | 0 | 0 | 0 | 2934400.1995 | 4538524.0962 | 11808308.7189 | 8059413.3371 | 36043487.4244 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 61521170.9061 | 114284747.8503 | 4216.965 | 10.3445 | 5947.24 | 11047.885 | 121.2425 | 225.2261
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.442 | 21.0197 | 3.1833 | 4 | 5169.8556 | 9313.6863 | 105.3945 | 189.8721 | 170.2953 | 20.8295 | 97.546 | 6727114.3532 | 0 | 3165037.9794 | 0 | 0 | 0 | 3135619.3905 | 5080830.972 | 13219279.9674 | 9022430.2068 | 40350312.8691 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 65827996.3508 | 118591573.295 | 5623.4133 | 12.733 | 5169.8556 | 9313.6863 | 105.3945 | 189.8721
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.1077 | 24.6706 | 3.809 | 4 | 4577.0689 | 8040.187 | 93.3097 | 163.9101 | 169.9467 | 20.4914 | 103.0742 | 7455322.7815 | 0 | 3568574.2931 | 0 | 0 | 0 | 3265501.3174 | 5572865.3729 | 14499452.5483 | 9896174.2982 | 44257890.6114 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 69735574.0931 | 122499151.0373 | 7498.9421 | 15.2359 | 4577.0689 | 8040.187 | 93.3097 | 163.9101
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.0534 | 28.1638 | 4.4244 | 4 | 4126.888 | 7108.2957 | 84.1322 | 144.9122 | 169.3538 | 20.1144 | 92.4812 | 8098045.559 | 0 | 3940558.4973 | 0 | 0 | 0 | 3316314.4901 | 5988418.2331 | 15580635.849 | 10634104.117 | 47558076.7456 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 73035760.2273 | 125799337.1715 | 10000 | 17.6975 | 4126.888 | 7108.2957 | 84.1322 | 144.9122
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.6897 | 31.3326 | 4.9958 | 4 | 3786.6266 | 6427.0338 | 77.1955 | 131.0238 | 168.6247 | 19.7299 | 108.9524 | 8638238.5312 | 0 | 4267551.4123 | 0 | 0 | 0 | 3299189.8464 | 6319942.1181 | 16443192.9929 | 11222817.0915 | 50190931.9923 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 75668615.474 | 128432192.4182 | 13335.2143 | 19.9831 | 3786.6266 | 6427.0338 | 77.1955 | 131.0238
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.6165 | 34.0606 | 5.4987 | 4 | 3530.2378 | 5929.1421 | 71.9687 | 120.8736 | 167.863 | 19.3671 | 113.0438 | 9071337.8995 | 0 | 4541616.2057 | 0 | 0 | 0 | 3230812.9367 | 6569069.1464 | 17091370.4175 | 11665211.5025 | 52169418.1084 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 77647101.5901 | 130410678.5343 | 17782.7941 | 21.9949 | 3530.2378 | 5929.1421 | 71.9687 | 120.8736
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7944 | 36.326 | 5.9238 | 4 | 3337.4664 | 5564.2224 | 68.0388 | 113.4342 | 167.141 | 19.044 | 108.7866 | 9408918.0407 | 0 | 4764315.4669 | 0 | 0 | 0 | 3133865.2257 | 6749768.506 | 17561513.0846 | 11986093.5333 | 53604473.8571 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 79082157.3388 | 131845734.283 | 23713.7371 | 23.6953 | 3337.4664 | 5564.2224 | 68.0388 | 113.4342
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.3307 | 38.1498 | 6.2714 | 4 | 3192.6954 | 5296.0252 | 65.0874 | 107.9666 | 166.5027 | 18.7699 | 105.3178 | 9666126.0316 | 0 | 4940454.3133 | 0 | 0 | 0 | 3026277.4321 | 6876814.533 | 17892060.7863 | 12211699.1317 | 54613432.228 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 80091115.7097 | 132854692.6539 | 31622.7766 | 25.0857 | 3192.6954 | 5296.0252 | 65.0874 | 107.9666
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4534 | 39.5879 | 6.549 | 4 | 3084.0272 | 5098.2018 | 62.8721 | 103.9337 | 165.9639 | 18.5451 | 106.1039 | 9859762.2686 | 0 | 5077406.1622 | 0 | 0 | 0 | 2921198.6696 | 6964763.1691 | 18120885.0967 | 12367876.4255 | 55311891.7917 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 80789575.2735 | 133553152.2177 | 42169.6503 | 26.1961 | 3084.0272 | 5098.2018 | 62.8721 | 103.9337
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.4144 | 40.7054 | 6.7669 | 4 | 3002.4721 | 4951.7871 | 61.2095 | 100.9489 | 165.5239 | 18.3651 | 112.1207 | 10004633.5133 | 0 | 5182672.3143 | 0 | 0 | 0 | 2826230.4361 | 7025279.1428 | 18278335.2468 | 12475339.3882 | 55792490.0414 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 81270173.5232 | 134033750.4674 | 56234.1325 | 27.0678 | 3002.4721 | 4951.7871 | 61.2095 | 100.9489
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4519 | 41.5657 | 6.9359 | 4 | 2941.2679 | 4843.0852 | 59.9617 | 98.7328 | 165.1725 | 18.2235 | 103.3698 | 10112817.8081 | 0 | 5263032.9738 | 0 | 0 | 0 | 2744774.2869 | 7067043.7768 | 18386998.2573 | 12549504.1256 | 56124171.2285 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 81601854.7102 | 134365431.6544 | 74989.4209 | 27.7438 | 2941.2679 | 4843.0852 | 59.9617 | 98.7328
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.7734 | 42.225 | 7.066 | 4 | 2895.3375 | 4762.1473 | 59.0254 | 97.0828 | 164.8956 | 18.1132 | 116.435 | 10193781.3641 | 0 | 5324245.2634 | 0 | 0 | 0 | 2677524.3937 | 7096264.8983 | 18463025.6213 | 12601394.3638 | 56356235.9046 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 81833919.3864 | 134597496.3306 | 100000 | 28.264 | 2895.3375 | 4762.1473 | 59.0254 | 97.0828
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.525 | 42.7239 | 7.1651 | 4 | 2860.871 | 4701.8584 | 58.3227 | 95.8537 | 164.6818 | 18.0287 | 110.5619 | 10253870.2417 | 0 | 5370314.3743 | 0 | 0 | 0 | 2623027.2832 | 7116412.6407 | 18515445.9141 | 12637172.2907 | 56516242.7447 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 81993926.2264 | 134757503.1706 | 133352.1432 | 28.6605 | 2860.871 | 4701.8584 | 58.3227 | 95.8537
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.848 | 43.1015 | 7.2404 | 4 | 2835.0088 | 4656.8516 | 57.7955 | 94.9362 | 164.5176 | 17.9642 | 115.1161 | 10298682.3672 | 0 | 5405045.1859 | 0 | 0 | 0 | 2579842.5301 | 7130592.3325 | 18552338.5634 | 12662352.282 | 56628853.2611 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82106536.7428 | 134870113.687 | 177827.941 | 28.9617 | 2835.0088 | 4656.8516 | 57.7955 | 94.9362
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8567 | 43.3894 | 7.2977 | 4 | 2815.6046 | 4623.1508 | 57.3999 | 94.2492 | 164.3908 | 17.9146 | 112.4289 | 10332517.8429 | 0 | 5431487.7158 | 0 | 0 | 0 | 2546360.6269 | 7141042.8124 | 18579528.5686 | 12680910.0192 | 56711847.5857 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82189531.0675 | 134953108.0117 | 237137.3706 | 29.1907 | 2815.6046 | 4623.1508 | 57.3999 | 94.2492
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6138 | 43.6058 | 7.3409 | 4 | 2801.0471 | 4597.956 | 57.1031 | 93.7356 | 164.2947 | 17.8771 | 119.5343 | 10357721.7566 | 0 | 5451312.7567 | 0 | 0 | 0 | 2520407.6154 | 7148482.4302 | 18598884.9279 | 12694121.1322 | 56770930.6189 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82248614.1006 | 135012191.0448 | 316227.766 | 29.3635 | 2801.0471 | 4597.956 | 57.1031 | 93.7356
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.1861 | 43.7694 | 7.3735 | 4 | 2790.1266 | 4579.082 | 56.8805 | 93.3508 | 164.2216 | 17.8487 | 113.2651 | 10376667.4005 | 0 | 5466288.1785 | 0 | 0 | 0 | 2500556.421 | 7153969.68 | 18613161.6264 | 12703865.2722 | 56814508.5786 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82292192.0604 | 135055769.0045 | 421696.5034 | 29.4941 | 2790.1266 | 4579.082 | 56.8805 | 93.3508
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6077 | 43.8903 | 7.3979 | 4 | 2781.9351 | 4564.9956 | 56.7135 | 93.0636 | 164.1674 | 17.8276 | 113.7738 | 10390559.7064 | 0 | 5477311.7901 | 0 | 0 | 0 | 2485216.4095 | 7157704.2833 | 18622878.2982 | 12710497.1004 | 56844167.5879 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82321851.0696 | 135085428.0138 | 562341.3252 | 29.5916 | 2781.9351 | 4564.9956 | 56.7135 | 93.0636
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.9218 | 43.9805 | 7.4162 | 4 | 2775.7909 | 4554.4568 | 56.5883 | 92.8488 | 164.1268 | 17.8119 | 126.4096 | 10400877.8741 | 0 | 5485522.5569 | 0 | 0 | 0 | 2473509.2465 | 7160364.7742 | 18629800.3497 | 12715221.5428 | 56865296.3442 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82342979.826 | 135106556.7702 | 749894.2093 | 29.6647 | 2775.7909 | 4554.4568 | 56.5883 | 92.8488
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.1607 | 44.0491 | 7.43 | 4 | 2771.1826 | 4546.5431 | 56.4943 | 92.6874 | 164.0958 | 17.8 | 116.6105 | 10408707.9755 | 0 | 5491765.893 | 0 | 0 | 0 | 2464715.0518 | 7162423.6789 | 18635157.1973 | 12718877.7014 | 56881647.4978 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82359330.9795 | 135122907.9237 | 1000000 | 29.7199 | 2771.1826 | 4546.5431 | 56.4943 | 92.6874
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3434 | 44.1014 | 7.4404 | 4 | 2767.7264 | 4540.5943 | 56.4238 | 92.5662 | 164.0722 | 17.7908 | 124.6735 | 10414682.2787 | 0 | 5496536.5046 | 0 | 0 | 0 | 2458145.3417 | 7164052.0087 | 18639393.7776 | 12721769.2545 | 56894579.1658 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82372262.6475 | 135135839.5917 | 1333521.4322 | 29.7617 | 2767.7264 | 4540.5943 | 56.4238 | 92.5662
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.4897 | 44.1429 | 7.4485 | 4 | 2765.1343 | 4536.0852 | 56.371 | 92.4742 | 164.0532 | 17.7834 | 118.5767 | 10419464.5704 | 0 | 5500358.2376 | 0 | 0 | 0 | 2453397.0147 | 7165555.7308 | 18643306.154 | 12724439.5318 | 56906521.2393 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82384204.721 | 135147781.6652 | 1778279.41 | 29.7939 | 2765.1343 | 4536.0852 | 56.371 | 92.4742
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.5823 | 44.1698 | 7.4541 | 4 | 2763.1904 | 4532.7977 | 56.3314 | 92.4072 | 164.0411 | 17.7788 | 115.9115 | 10422484.1846 | 0 | 5502776.7129 | 0 | 0 | 0 | 2449441.0327 | 7166133.7528 | 18644810.0486 | 12725465.9707 | 56911111.7023 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82388795.184 | 135152372.1282 | 2371373.7057 | 29.8165 | 2763.1904 | 4532.7977 | 56.3314 | 92.4072
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.6601 | 44.1921 | 7.4586 | 4 | 2761.7326 | 4530.2881 | 56.3017 | 92.3561 | 164.031 | 17.7749 | 124.1314 | 10425021.0212 | 0 | 5504808.0269 | 0 | 0 | 0 | 2446649.7374 | 7166826.7263 | 18646613.0236 | 12726696.5382 | 56916615.0737 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82394298.5554 | 135157875.4996 | 3162277.6602 | 29.8343 | 2761.7326 | 4530.2881 | 56.3017 | 92.3561
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7138 | 44.2076 | 7.4618 | 4 | 2760.6394 | 4528.4315 | 56.2794 | 92.3182 | 164.024 | 17.7722 | 118.4963 | 10426770.489 | 0 | 5506210.4915 | 0 | 0 | 0 | 2444449.3727 | 7167197.8377 | 18647578.5794 | 12727355.5498 | 56919562.3201 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82397245.8018 | 135160822.746 | 4216965.0343 | 29.8472 | 2760.6394 | 4528.4315 | 56.2794 | 92.3182
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7675 | 44.2226 | 7.4645 | 4 | 2759.8195 | 4526.9673 | 56.2627 | 92.2884 | 164.017 | 17.7695 | 112.7691 | 10428522.7023 | 0 | 5507612.8667 | 0 | 0 | 0 | 2443092.4872 | 7167898.9419 | 18649402.7087 | 12728600.5556 | 56925130.2625 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82402813.7442 | 135166390.6884 | 5623413.2519 | 29.858 | 2759.8195 | 4526.9673 | 56.2627 | 92.2884
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7844 | 44.228 | 7.466 | 4 | 2759.2047 | 4525.9954 | 56.2501 | 92.2685 | 164.0147 | 17.7686 | 128.0645 | 10429067.385 | 0 | 5508052.6737 | 0 | 0 | 0 | 2441557.0181 | 7167684.0599 | 18648843.6298 | 12728218.9728 | 56923423.7393 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82401107.221 | 135164684.1652 | 7498942.0933 | 29.8641 | 2759.2047 | 4525.9954 | 56.2501 | 92.2685
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.8233 | 44.2386 | 7.4677 | 4 | 2758.7436 | 4525.1255 | 56.2407 | 92.2508 | 164.0097 | 17.7667 | 131.4149 | 10430337.2595 | 0 | 5509068.1108 | 0 | 0 | 0 | 2440983.0618 | 7168351.4885 | 18650580.1421 | 12729404.1781 | 56928724.2409 | 961560.8286 | 24516122.6531 | 24516122.6531 | 18517163.4082 | 9730290.8829 | 0 | 82406407.7226 | 135169984.6668 | 10000000 | 29.871 | 2758.7436 | 4525.1255 | 56.2407 | 92.2508
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.066592 | 0.010131 | 4 | 685611.8485 | 2017652.5128 | 13977.1249 | 41132.5756 | 91.4421 | 18.4819 | 24.9853 | 240933.7575 | 0 | 97448.1265 | 0 | 0 | 0 | 214090.9722 | 215464.4139 | 560594.2072 | 382617.0655 | 1711148.5428 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 27784694.435 | 81766175.2351 | 100 | 0.040525 | 685611.8485 | 2017652.5128 | 13977.1249 | 41132.5756
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6903 | 0.37377 | 0.03764 | 4 | 200329.6343 | 558866.456 | 4083.9906 | 11393.2486 | 125.3153 | 20.4326 | 55.9699 | 568783.2268 | 0 | 258693.4467 | 0 | 0 | 0 | 492461.3163 | 514775.816 | 1339341.0783 | 914127.8067 | 4088182.6909 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 30161728.583 | 84143209.3832 | 133.3521 | 0.15056 | 200329.6343 | 558866.456 | 4083.9906 | 11393.2486
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9861 | 0.64468 | 0.070076 | 4 | 111757.3142 | 304339.8516 | 2278.324 | 6204.3795 | 135.7588 | 20.8988 | 47.6753 | 754103.4525 | 0 | 329111.7349 | 0 | 0 | 0 | 612601.6806 | 661368.5785 | 1720745.3758 | 1174444.0768 | 5252374.899 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 31325920.7911 | 85307401.5913 | 177.8279 | 0.2803 | 111757.3142 | 304339.8516 | 2278.324 | 6204.3795
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.601 | 1.0103 | 0.11586 | 4 | 70450.737 | 186931.9511 | 1436.2336 | 3810.8607 | 144.2033 | 21.2382 | 56.511 | 968103.4415 | 0 | 411924.3615 | 0 | 0 | 0 | 743077.9926 | 828011.2603 | 2154315.4509 | 1470364.562 | 6575797.0688 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 32649342.961 | 86630823.7611 | 237.1374 | 0.46344 | 70450.737 | 186931.9511 | 1436.2336 | 3810.8607
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6324 | 1.4932 | 0.17853 | 4 | 47852.3409 | 123444.0903 | 975.5347 | 2516.5748 | 151.0577 | 21.4906 | 62.4542 | 1216996.7066 | 0 | 510550.0419 | 0 | 0 | 0 | 887255.2657 | 1019772.7855 | 2653239.6038 | 1810890.5482 | 8098704.9517 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 34172250.8439 | 88153731.644 | 316.2278 | 0.71412 | 47852.3409 | 123444.0903 | 975.5347 | 2516.5748
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2271 | 2.1281 | 0.26294 | 4 | 34191.4027 | 85515.8889 | 697.038 | 1743.3571 | 156.6547 | 21.6808 | 55.6145 | 1510749.0206 | 0 | 630009.9349 | 0 | 0 | 0 | 1051713.3354 | 1245064.1934 | 3239401.6336 | 2210958.178 | 9887896.2958 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 35961442.188 | 89942922.9881 | 421.6965 | 1.0518 | 34191.4027 | 85515.8889 | 697.038 | 1743.3571
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5056 | 2.9469 | 0.37506 | 4 | 25354.1466 | 61335.6876 | 516.8786 | 1250.411 | 161.1376 | 21.8201 | 65.2075 | 1853900.8024 | 0 | 773322.0856 | 0 | 0 | 0 | 1235597.7282 | 1506500.0403 | 3919604.0793 | 2675210.3239 | 11964135.0598 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 38037680.9519 | 92019161.7521 | 562.3413 | 1.5003 | 25354.1466 | 61335.6876 | 516.8786 | 1250.411
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6667 | 3.9999 | 0.52277 | 4 | 19352.0576 | 45167.2288 | 394.5179 | 920.7951 | 164.7206 | 21.9179 | 55.566 | 2257024.7637 | 0 | 946206.8086 | 0 | 0 | 0 | 1443812.603 | 1812347.2284 | 4715355.7246 | 3218327.1729 | 14393074.3012 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 40466620.1934 | 94448100.9935 | 749.8942 | 2.0911 | 19352.0576 | 45167.2288 | 394.5179 | 920.7951
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.8749 | 5.3323 | 0.71512 | 4 | 15124.7504 | 33996.1719 | 308.3385 | 693.0579 | 167.5281 | 21.9773 | 67.3169 | 2724678.4466 | 0 | 1152087.9501 | 0 | 0 | 0 | 1673514.0732 | 2164609.3833 | 5631869.5928 | 3843866.7204 | 17190626.1664 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 43264172.0586 | 97245652.8587 | 1000 | 2.8605 | 15124.7504 | 33996.1719 | 308.3385 | 693.0579
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.377 | 7.009 | 0.96334 | 4 | 12063.6246 | 26072.5151 | 245.9333 | 531.5235 | 169.7076 | 21.9985 | 73.6919 | 3266552.7082 | 0 | 1396908.2757 | 0 | 0 | 0 | 1926926.126 | 2570250.9729 | 6687265.8005 | 4564196.3184 | 20412100.2017 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 46485646.0938 | 100467126.894 | 1333.5214 | 3.8534 | 12063.6246 | 26072.5151 | 245.9333 | 531.5235
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4085 | 9.0947 | 1.2796 | 4 | 9799.1382 | 20345.5405 | 199.7687 | 414.7714 | 171.3583 | 21.9768 | 80.537 | 3888406.6706 | 0 | 1685287.4599 | 0 | 0 | 0 | 2201931.2245 | 3032493.8885 | 7889927.0477 | 5385037.3319 | 24083083.6231 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 50156629.5153 | 104138110.3154 | 1778.2794 | 5.1185 | 9799.1382 | 20345.5405 | 199.7687 | 414.7714
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.0944 | 11.6296 | 1.6744 | 4 | 8096.9463 | 16156.8756 | 165.0672 | 329.3798 | 172.5431 | 21.9034 | 68.9918 | 4585785.6891 | 0 | 2017472.3333 | 0 | 0 | 0 | 2487329.8212 | 3545329.259 | 9224219.4849 | 6295719.3372 | 28155855.9246 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 54229401.8167 | 108210882.6169 | 2371.3737 | 6.6975 | 8096.9463 | 16156.8756 | 165.0672 | 329.3798
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.4897 | 14.6354 | 2.1544 | 4 | 6803.5154 | 13067.5813 | 138.6989 | 266.4003 | 173.3088 | 21.7662 | 84.0441 | 5349128.3985 | 0 | 2391584.0816 | 0 | 0 | 0 | 2770766.9635 | 4099476.983 | 10665998.1914 | 7279762.93 | 32556717.548 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 58630263.4402 | 112611744.2403 | 3162.2777 | 8.6176 | 6803.5154 | 13067.5813 | 138.6989 | 266.4003
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.3083 | 18.0474 | 2.7147 | 4 | 5815.3777 | 10786.5669 | 118.5543 | 219.8988 | 173.6695 | 21.5548 | 79.8993 | 6147990.2788 | 0 | 2795651.5235 | 0 | 0 | 0 | 3026597.3251 | 4668393.2597 | 12146201.6426 | 8290032.2005 | 37074866.2302 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 63148412.1223 | 117129892.9225 | 4216.965 | 10.8589 | 5815.3777 | 10786.5669 | 118.5543 | 219.8988
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9935 | 21.7249 | 3.3359 | 4 | 5060.1284 | 9105.6233 | 103.1576 | 185.6304 | 173.6438 | 21.2665 | 89.1711 | 6941220.3136 | 0 | 3211477.7212 | 0 | 0 | 0 | 3229093.2334 | 5218898.5946 | 13578503.5998 | 9267607.7172 | 41446801.1799 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 67520347.072 | 121501827.8722 | 5623.4133 | 13.3436 | 5060.1284 | 9105.6233 | 103.1576 | 185.6304
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.7324 | 25.4539 | 3.9839 | 4 | 4484.5381 | 7872.0114 | 91.4234 | 160.4816 | 173.2824 | 20.914 | 106.6545 | 7682061.9469 | 0 | 3615775.0501 | 0 | 0 | 0 | 3357191.4992 | 5715461.1135 | 14870457.415 | 10149392.7431 | 45390339.7676 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 71463885.6597 | 125445366.4599 | 7498.9421 | 15.9356 | 4484.5381 | 7872.0114 | 91.4234 | 160.4816
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.7144 | 29.0126 | 4.6189 | 4 | 4047.7528 | 6969.4932 | 82.5189 | 142.0825 | 172.677 | 20.5235 | 110.9316 | 8334371.1207 | 0 | 3987639.6248 | 0 | 0 | 0 | 3405442.214 | 6133706.6542 | 15958646.5179 | 10892104.1659 | 48711910.2975 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 74785456.1896 | 128766936.9897 | 10000 | 18.4758 | 4047.7528 | 6969.4932 | 82.5189 | 142.0825
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3144 | 32.2232 | 5.2058 | 4 | 3717.6244 | 6310.0164 | 75.7888 | 128.6382 | 171.9387 | 20.127 | 113.2889 | 8879328.091 | 0 | 4312702.7453 | 0 | 0 | 0 | 3383522.8806 | 6464465.9496 | 16819214.3566 | 11479459.3987 | 51338693.4218 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 77412239.3139 | 131393720.1141 | 13335.2143 | 20.823 | 3717.6244 | 6310.0164 | 75.7888 | 128.6382
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1977 | 34.9834 | 5.7209 | 4 | 3469.0457 | 5828.0037 | 70.7212 | 118.8117 | 171.1712 | 19.7547 | 114.8048 | 9315879.1053 | 0 | 4584885.1209 | 0 | 0 | 0 | 3311501.0325 | 6712783.4509 | 17465285.558 | 11920416.2691 | 53310750.5367 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 79384296.4288 | 133365777.229 | 17782.7941 | 22.8836 | 3469.0457 | 5828.0037 | 70.7212 | 118.8117
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.2876 | 37.2619 | 6.1544 | 4 | 3282.2084 | 5475.0161 | 66.9123 | 111.6156 | 170.4497 | 19.4256 | 113.3751 | 9654100.963 | 0 | 4804696.0435 | 0 | 0 | 0 | 3210493.5766 | 6891023.3274 | 17929029.1547 | 12236930.8028 | 54726273.8679 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 80799819.7601 | 134781300.5602 | 23713.7371 | 24.6175 | 3282.2084 | 5475.0161 | 66.9123 | 111.6156
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.7675 | 39.0995 | 6.5087 | 4 | 3141.9297 | 5215.3624 | 64.0525 | 106.3222 | 169.8113 | 19.1461 | 110.3444 | 9912470.1451 | 0 | 4978961.9576 | 0 | 0 | 0 | 3100662.2459 | 7016916.796 | 18256578.1356 | 12460489.7127 | 55726078.9929 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 81799624.885 | 135781105.6851 | 31622.7766 | 26.0348 | 3141.9297 | 5215.3624 | 64.0525 | 106.3222
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.8345 | 40.5454 | 6.7911 | 4 | 3036.6544 | 5023.8671 | 61.9063 | 102.4183 | 169.2742 | 18.9176 | 109.9349 | 10106610.4332 | 0 | 5114172.4547 | 0 | 0 | 0 | 2993873.041 | 7103715.8122 | 18482411.3709 | 12614625.5362 | 56415408.6482 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 82488954.5403 | 136470435.3405 | 42169.6503 | 27.1644 | 3036.6544 | 5023.8671 | 61.9063 | 102.4183
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7586 | 41.6704 | 7.0127 | 4 | 2957.6582 | 4882.0646 | 60.2959 | 99.5275 | 168.8351 | 18.7346 | 119.2743 | 10252131.8279 | 0 | 5218273.5598 | 0 | 0 | 0 | 2898015.2404 | 7163684.0449 | 18638436.4113 | 12721115.8323 | 56891656.9165 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 82965202.8087 | 136946683.6088 | 56234.1325 | 28.051 | 2957.6582 | 4882.0646 | 60.2959 | 99.5275
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.7601 | 42.5344 | 7.1844 | 4 | 2898.382 | 4776.82 | 59.0874 | 97.3819 | 168.4855 | 18.5909 | 122.0392 | 10360550.5837 | 0 | 5297548.0934 | 0 | 0 | 0 | 2815849.6342 | 7204839.8414 | 18745515.3514 | 12794199.4092 | 57218502.9133 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83292048.8054 | 137273529.6056 | 74989.4209 | 28.7374 | 2898.382 | 4776.82 | 59.0874 | 97.3819
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0381 | 43.1925 | 7.316 | 4 | 2853.9032 | 4698.5416 | 58.1807 | 95.7861 | 168.212 | 18.4798 | 117.863 | 10441145.3562 | 0 | 5357516.9335 | 0 | 0 | 0 | 2747783.5357 | 7233113.8719 | 18819078.579 | 12844407.8236 | 57443046.0998 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83516591.992 | 137498072.7921 | 100000 | 29.264 | 2853.9032 | 4698.5416 | 58.1807 | 95.7861
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.7749 | 43.6951 | 7.4167 | 4 | 2820.5288 | 4640.1217 | 57.5003 | 94.5952 | 167.9988 | 18.3939 | 123.8784 | 10501605.796 | 0 | 5403126.0319 | 0 | 0 | 0 | 2693193.1023 | 7253190.7228 | 18871314.4267 | 12880059.863 | 57602489.9427 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83676035.8349 | 137657516.635 | 133352.1432 | 29.6668 | 2820.5288 | 4640.1217 | 57.5003 | 94.5952
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0756 | 44.0726 | 7.4929 | 4 | 2795.4879 | 4596.5712 | 56.9898 | 93.7073 | 167.8364 | 18.3288 | 123.1332 | 10546317.3183 | 0 | 5437219.9678 | 0 | 0 | 0 | 2649714.6144 | 7266968.2412 | 18907160.7035 | 12904525.6834 | 57711906.5286 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83785452.4208 | 137766933.2209 | 177827.941 | 29.9717 | 2795.4879 | 4596.5712 | 56.9898 | 93.7073
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.0546 | 44.3572 | 7.5506 | 4 | 2776.7011 | 4564.0289 | 56.6068 | 93.0439 | 167.7125 | 18.2795 | 114.6862 | 10579651.242 | 0 | 5462848.1451 | 0 | 0 | 0 | 2615746.8723 | 7276716.0412 | 18932522.4794 | 12921835.6166 | 57789320.3967 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83862866.2888 | 137844347.089 | 237137.3706 | 30.2023 | 2776.7011 | 4564.0289 | 56.6068 | 93.0439
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8124 | 44.5769 | 7.5946 | 4 | 2762.6074 | 4539.5729 | 56.3195 | 92.5453 | 167.6159 | 18.241 | 115.0043 | 10605264.0712 | 0 | 5482661.875 | 0 | 0 | 0 | 2589982.6607 | 7284384.3567 | 18952473.8634 | 12935452.8462 | 57850219.6732 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83923765.5653 | 137905246.3655 | 316227.766 | 30.3785 | 2762.6074 | 4539.5729 | 56.3195 | 92.5453
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3628 | 44.7374 | 7.6274 | 4 | 2752.0351 | 4521.3734 | 56.104 | 92.1743 | 167.5451 | 18.213 | 131.0265 | 10623761.5522 | 0 | 5497044.4947 | 0 | 0 | 0 | 2569767.2498 | 7289323.5857 | 18965324.7242 | 12944223.8227 | 57889445.4293 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83962991.3215 | 137944472.1216 | 421696.5034 | 30.5094 | 2752.0351 | 4521.3734 | 56.104 | 92.1743
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7844 | 44.8601 | 7.6522 | 4 | 2744.1051 | 4507.7019 | 55.9423 | 91.8956 | 167.4906 | 18.1914 | 129.9302 | 10637869.6893 | 0 | 5508052.6737 | 0 | 0 | 0 | 2554534.4842 | 7293178.1704 | 18975353.5629 | 12951068.7112 | 57920057.2918 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 83993603.184 | 137975083.9841 | 562341.3252 | 30.6087 | 2744.1051 | 4507.7019 | 55.9423 | 91.8956
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.1035 | 44.9529 | 7.6709 | 4 | 2738.1571 | 4497.4469 | 55.821 | 91.6865 | 167.4492 | 18.1751 | 104.2931 | 10648517.0202 | 0 | 5516383.2266 | 0 | 0 | 0 | 2543023.3646 | 7296090.2084 | 18982930.0884 | 12956239.8455 | 57943183.7536 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84016729.6457 | 137998210.4459 | 749894.2093 | 30.6837 | 2738.1571 | 4497.4469 | 55.821 | 91.6865
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3445 | 45.023 | 7.685 | 4 | 2733.6961 | 4489.7557 | 55.7301 | 91.5297 | 167.4179 | 18.1627 | 120.0609 | 10656536.4281 | 0 | 5522670.7441 | 0 | 0 | 0 | 2534338.6687 | 7298282.8779 | 18988634.9647 | 12960133.5408 | 57960597.2243 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84034143.1165 | 138015623.9166 | 1000000 | 30.7401 | 2733.6961 | 4489.7557 | 55.7301 | 91.5297
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.5102 | 45.0718 | 7.6953 | 4 | 2730.3504 | 4484.0716 | 55.6619 | 91.4139 | 167.3962 | 18.1542 | 115.3685 | 10662039.8053 | 0 | 5526995.2502 | 0 | 0 | 0 | 2527438.1465 | 7299424.5488 | 18991605.3581 | 12962160.8954 | 57969664.0044 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84043209.8965 | 138024690.6967 | 1333521.4322 | 30.7811 | 2730.3504 | 4484.0716 | 55.6619 | 91.4139
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.6493 | 45.1121 | 7.7033 | 4 | 2727.8412 | 4479.7329 | 55.6107 | 91.3254 | 167.378 | 18.147 | 119.6112 | 10666655.2355 | 0 | 5530623.0873 | 0 | 0 | 0 | 2522569.1089 | 7300740.4984 | 18995029.189 | 12964497.7303 | 57980114.8494 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84053660.7416 | 138035141.5417 | 1778279.41 | 30.8133 | 2727.8412 | 4479.7329 | 55.6107 | 91.3254
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.7466 | 45.1406 | 7.7092 | 4 | 2725.9595 | 4476.5181 | 55.5724 | 91.2599 | 167.3653 | 18.142 | 118.9955 | 10669876.8297 | 0 | 5533158.9992 | 0 | 0 | 0 | 2518742.4442 | 7301493.5265 | 18996988.4138 | 12965834.9415 | 57986095.155 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84059641.0471 | 138041121.8473 | 2371373.7057 | 30.8367 | 2725.9595 | 4476.5181 | 55.5724 | 91.2599
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8197 | 45.162 | 7.7136 | 4 | 2724.5483 | 4474.1068 | 55.5436 | 91.2107 | 167.3557 | 18.1382 | 115.4399 | 10672298.9233 | 0 | 5535066.7795 | 0 | 0 | 0 | 2515869.3426 | 7302061.6677 | 18998466.6006 | 12966843.8343 | 57990607.148 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84064153.0401 | 138045633.8403 | 3162277.6602 | 30.8543 | 2724.5483 | 4474.1068 | 55.5436 | 91.2107
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8781 | 45.1789 | 7.717 | 4 | 2723.49 | 4472.2806 | 55.522 | 91.1735 | 167.3481 | 18.1352 | 121.4763 | 10674230.2537 | 0 | 5536588.0562 | 0 | 0 | 0 | 2513787.9634 | 7302596.4466 | 18999857.9854 | 12967793.4831 | 57994854.1883 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84068400.0805 | 138049880.8806 | 4216965.0343 | 30.8679 | 2723.49 | 4472.2806 | 55.522 | 91.1735
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9124 | 45.1892 | 7.7193 | 4 | 2722.6964 | 4470.9614 | 55.5058 | 91.1466 | 167.3436 | 18.1334 | 112.3425 | 10675361.706 | 0 | 5537481.4556 | 0 | 0 | 0 | 2512011.2463 | 7302693.2191 | 19000109.7678 | 12967965.3297 | 57995622.7246 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84069168.6168 | 138050649.4169 | 5623413.2519 | 30.8772 | 2722.6964 | 4470.9614 | 55.5058 | 91.1466
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9512 | 45.2003 | 7.7213 | 4 | 2722.1013 | 4469.9027 | 55.4937 | 91.125 | 167.3385 | 18.1314 | 114.4726 | 10676649.8218 | 0 | 5538495.5411 | 0 | 0 | 0 | 2510973.6415 | 7303186.4117 | 19001392.9537 | 12968841.1305 | 57999539.5003 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84073085.3925 | 138054566.1926 | 7498942.0933 | 30.8854 | 2722.1013 | 4469.9027 | 55.4937 | 91.125
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9661 | 45.2049 | 7.7225 | 4 | 2721.655 | 4469.1845 | 55.4846 | 91.1104 | 167.3365 | 18.1307 | 105.1681 | 10677137.4077 | 0 | 5538881.8471 | 0 | 0 | 0 | 2509872.6281 | 7303097.8343 | 19001162.4936 | 12968683.8367 | 57998836.0476 | 961560.8286 | 25111985.0635 | 25111985.0635 | 18927833.0506 | 9941662.686 | 0 | 84072381.9398 | 138053862.7399 | 10000000 | 30.8902 | 2721.655 | 4469.1845 | 55.4846 | 91.1104
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.065561 | 0.010287 | 4 | 690183.3181 | 2032050.0268 | 14070.3205 | 41426.0883 | 91.9234 | 18.8395 | 24.5185 | 243077.8462 | 0 | 97152.1274 | 0 | 0 | 0 | 216191.5958 | 217004.412 | 564600.9664 | 385351.761 | 1723378.7088 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 28398647.1023 | 83611802.9719 | 100 | 0.041147 | 690183.3181 | 2032050.0268 | 14070.3205 | 41426.0883
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7876 | 0.38949 | 0.039963 | 4 | 193338.4041 | 538736.9767 | 3941.4649 | 10982.882 | 127.6917 | 20.8984 | 54.3137 | 590534.7834 | 0 | 264132.4868 | 0 | 0 | 0 | 511234.4048 | 532701.6532 | 1385980.4296 | 945960.1222 | 4230543.88 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 30905812.2735 | 86118968.1431 | 133.3521 | 0.15985 | 193338.4041 | 538736.9767 | 3941.4649 | 10982.882
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1176 | 0.67142 | 0.074226 | 4 | 108152.34 | 294114.6481 | 2204.8317 | 5995.9249 | 138.3714 | 21.3713 | 49.8085 | 782914.1291 | 0 | 336037.7077 | 0 | 0 | 0 | 636058.4303 | 684454.0042 | 1780808.918 | 1215438.6785 | 5435711.8678 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 32110980.2612 | 87324136.1308 | 177.8279 | 0.29691 | 108152.34 | 294114.6481 | 2204.8317 | 5995.9249
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7519 | 1.0478 | 0.12244 | 4 | 68314.0647 | 181051.1025 | 1392.6746 | 3690.9716 | 146.9046 | 21.7116 | 47.6363 | 1001993.7883 | 0 | 419443.3808 | 0 | 0 | 0 | 768135.1905 | 853933.2202 | 2221759.0732 | 1516396.2201 | 6781660.873 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 33456929.2665 | 88670085.1361 | 237.1374 | 0.48975 | 68314.0647 | 181051.1025 | 1392.6746 | 3690.9716
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8519 | 1.553 | 0.18856 | 4 | 46469.0417 | 119673.3063 | 947.3343 | 2439.7022 | 153.9813 | 21.9703 | 49.0328 | 1262253.4107 | 0 | 520908.7958 | 0 | 0 | 0 | 920287.5676 | 1054345.4119 | 2743190.4857 | 1872283.8734 | 8373269.5451 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 35048537.9386 | 90261693.8082 | 316.2278 | 0.75423 | 46469.0417 | 119673.3063 | 947.3343 | 2439.7022
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5024 | 2.2112 | 0.27743 | 4 | 33241.4374 | 82994.9918 | 677.6717 | 1691.9652 | 159.6822 | 22.1623 | 65.4194 | 1565711.1101 | 0 | 642335.4671 | 0 | 0 | 0 | 1089664.6715 | 1286107.387 | 3346187.604 | 2283841.797 | 10213848.0367 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 36889116.4302 | 92102272.2998 | 421.6965 | 1.1097 | 33241.4374 | 82994.9918 | 677.6717 | 1691.9652
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.854 | 3.0606 | 0.39544 | 4 | 24673.4242 | 59579.434 | 503.0011 | 1214.6073 | 164.256 | 22.3029 | 70.9873 | 1920558.591 | 0 | 788145.4422 | 0 | 0 | 0 | 1279450.6906 | 1555380.3423 | 4046780.5982 | 2762010.9113 | 12352326.5755 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 39027594.9689 | 94240750.8385 | 562.3413 | 1.5818 | 24673.4242 | 59579.434 | 503.0011 | 1214.6073
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1077 | 4.1528 | 0.55084 | 4 | 18848.2602 | 43906.9479 | 384.2473 | 895.1025 | 167.9133 | 22.4012 | 59.2993 | 2337451.0716 | 0 | 964048.2453 | 0 | 0 | 0 | 1494400.4809 | 1870400.9211 | 4866399.5248 | 3321417.6702 | 14854117.9138 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 41529386.3072 | 96742542.1768 | 749.8942 | 2.2034 | 18848.2602 | 43906.9479 | 384.2473 | 895.1025
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.4324 | 5.5349 | 0.75313 | 4 | 14742.1929 | 33069.9884 | 300.5395 | 674.1764 | 170.7802 | 22.4599 | 73.7328 | 2821172.2518 | 0 | 1173560.5207 | 0 | 0 | 0 | 1731672.138 | 2233297.9151 | 5810583.0626 | 3965842.3358 | 17736128.224 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 44411396.6174 | 99624552.487 | 1000 | 3.0125 | 14742.1929 | 33069.9884 | 300.5395 | 674.1764
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.0808 | 7.2745 | 1.0141 | 4 | 11766.9168 | 25378.4558 | 239.8845 | 517.3741 | 173.0063 | 22.4792 | 69.3591 | 3381752.1539 | 0 | 1422742.0576 | 0 | 0 | 0 | 1993610.8811 | 2651260.9861 | 6898037.2374 | 4708052.155 | 21055455.4711 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 47730723.8645 | 102943879.7341 | 1333.5214 | 4.0563 | 11766.9168 | 25378.4558 | 239.8845 | 517.3741
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.2586 | 9.4305 | 1.3459 | 4 | 9564.8482 | 19820.6933 | 194.9924 | 404.0716 | 174.6861 | 22.4537 | 67.2569 | 4022446.0309 | 0 | 1715064.7104 | 0 | 0 | 0 | 2275346.5664 | 3125014.35 | 8130646.3101 | 5549333.1747 | 24817851.1424 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 51493119.5359 | 106706275.4055 | 1778.2794 | 5.3836 | 9564.8482 | 19820.6933 | 194.9924 | 404.0716
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.1413 | 12.0554 | 1.76 | 4 | 7909.0633 | 15751.8925 | 161.237 | 321.1236 | 175.8943 | 22.374 | 80.1594 | 4742468.558 | 0 | 2052530.3871 | 0 | 0 | 0 | 2569482.2287 | 3652147.6578 | 9502139.047 | 6485405.149 | 29004173.0276 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 55679441.421 | 110892597.2906 | 2371.3737 | 7.04 | 7909.0633 | 15751.8925 | 161.237 | 321.1236
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.7077 | 15.1533 | 2.2619 | 4 | 6650.8182 | 12753.4212 | 135.5859 | 259.9957 | 176.6696 | 22.228 | 79.1752 | 5526489.8329 | 0 | 2430677.0266 | 0 | 0 | 0 | 2858173.3241 | 4217982.6716 | 10974325.6843 | 7490202.7794 | 33497851.3189 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 60173119.7123 | 115386275.5819 | 3162.2777 | 9.0475 | 6650.8182 | 12753.4212 | 135.5859 | 259.9957
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.7085 | 18.6668 | 2.8465 | 4 | 5689.7724 | 10539.0105 | 115.9937 | 214.852 | 177.0305 | 22.0045 | 109.515 | 6346302.1358 | 0 | 2838875.0076 | 0 | 0 | 0 | 3118679.3538 | 4798504.0339 | 12484723.1877 | 8521080.111 | 38108163.8299 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 64783432.2234 | 119996588.093 | 4216.965 | 11.3859 | 5689.7724 | 10539.0105 | 115.9937 | 214.852
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.5166 | 22.4353 | 3.4918 | 4 | 4955.5528 | 8908.5984 | 101.0256 | 181.6138 | 176.9963 | 21.7023 | 95.787 | 7156058.2824 | 0 | 3256900.6705 | 0 | 0 | 0 | 3321838.7113 | 5356571.089 | 13936699.1898 | 9512083.5676 | 42540151.5105 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 69215419.904 | 124428575.7736 | 5623.4133 | 13.9672 | 4955.5528 | 8908.5984 | 101.0256 | 181.6138
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.3332 | 26.2443 | 4.1624 | 4 | 4396.2958 | 7712.4498 | 89.6244 | 157.2287 | 176.6223 | 21.335 | 108.2964 | 7909824.0361 | 0 | 3662131.166 | 0 | 0 | 0 | 3448443.5301 | 5857955.5056 | 15241198.5936 | 10402431.2155 | 46521984.047 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 73197252.4405 | 128410408.3101 | 7498.9421 | 16.6498 | 4396.2958 | 7712.4498 | 89.6244 | 157.2287
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.3487 | 29.8682 | 4.8172 | 4 | 3972.1406 | 6837.5551 | 80.9775 | 139.3928 | 176.0043 | 20.9302 | 115.404 | 8571478.277 | 0 | 4033826.9232 | 0 | 0 | 0 | 3493858.3358 | 6278673.7791 | 16335821.24 | 11149533.6639 | 49863192.219 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 76538460.6125 | 131751616.4821 | 10000 | 19.2688 | 3972.1406 | 6837.5551 | 80.9775 | 139.3928
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9151 | 33.1211 | 5.4194 | 4 | 3651.7155 | 6198.7199 | 74.4452 | 126.3693 | 175.2577 | 20.5223 | 105.81 | 9121295.9717 | 0 | 4357069.6618 | 0 | 0 | 0 | 3467442.2399 | 6608865.0706 | 17194911.2492 | 11735880.2476 | 52485464.4408 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 79160732.8343 | 134373888.7039 | 13335.2143 | 21.6777 | 3651.7155 | 6198.7199 | 74.4452 | 126.3693
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.7371 | 35.9086 | 5.9463 | 4 | 3410.5447 | 5731.8739 | 69.5286 | 116.852 | 174.4863 | 20.141 | 106.6541 | 9560420.0429 | 0 | 4626910.9567 | 0 | 0 | 0 | 3391157.5979 | 6855610.553 | 17836892.3799 | 12174045.5607 | 54445037.0911 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 81120305.4845 | 136333461.3541 | 17782.7941 | 23.7851 | 3410.5447 | 5731.8739 | 69.5286 | 116.852
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.7808 | 38.2103 | 6.389 | 4 | 3229.3336 | 5389.8059 | 65.8343 | 109.8785 | 173.7619 | 19.8044 | 114.6859 | 9900914.962 | 0 | 4844991.9529 | 0 | 0 | 0 | 3287415.1812 | 7032995.6175 | 18298411.931 | 12489042.1376 | 55853771.7823 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 82529040.1757 | 137742196.0453 | 23713.7371 | 25.5561 | 3229.3336 | 5389.8059 | 65.8343 | 109.8785
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.183 | 40.0559 | 6.7495 | 4 | 3093.3127 | 5138.4096 | 63.0614 | 104.7534 | 173.1257 | 19.5205 | 115.4904 | 10159461.4022 | 0 | 5016823.5606 | 0 | 0 | 0 | 3174627.396 | 7156855.8199 | 18620670.7705 | 12708990.4174 | 56837429.3667 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 83512697.7602 | 138725853.6297 | 31622.7766 | 26.9978 | 3093.3127 | 5138.4096 | 63.0614 | 104.7534
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1964 | 41.5097 | 7.0366 | 4 | 2991.2523 | 4952.8902 | 60.9807 | 100.9714 | 172.5902 | 19.2883 | 118.5439 | 10354100.1955 | 0 | 5150361.0946 | 0 | 0 | 0 | 3066147.0709 | 7242537.2608 | 18843596.3039 | 12861141.6746 | 57517883.6003 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 84193151.9937 | 139406307.8633 | 42169.6503 | 28.1465 | 2991.2523 | 4952.8902 | 60.9807 | 100.9714
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.0692 | 42.6383 | 7.2616 | 4 | 2914.6801 | 4815.5452 | 59.4197 | 98.1714 | 172.1539 | 19.1029 | 108.9052 | 10499675.9229 | 0 | 5252926.2857 | 0 | 0 | 0 | 2968981.7897 | 7301417.7593 | 18996791.283 | 12965700.3957 | 57985493.4361 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 84660761.8296 | 139873917.6992 | 56234.1325 | 29.0463 | 2914.6801 | 4815.5452 | 59.4197 | 98.1714
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.0272 | 43.5039 | 7.4356 | 4 | 2857.2299 | 4713.6157 | 58.2485 | 96.0934 | 171.8071 | 18.9577 | 109.3219 | 10608013.8315 | 0 | 5330925.3369 | 0 | 0 | 0 | 2885891.224 | 7341683.853 | 19101555.3992 | 13037204.0576 | 58305273.7023 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 84980542.0957 | 140193697.9653 | 74989.4209 | 29.7423 | 2857.2299 | 4713.6157 | 58.2485 | 96.0934
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.2755 | 44.164 | 7.5691 | 4 | 2814.1256 | 4637.7724 | 57.3698 | 94.5473 | 171.5356 | 18.8452 | 111.3754 | 10688693.5827 | 0 | 5390022.8743 | 0 | 0 | 0 | 2817330.8197 | 7369458.4379 | 19173819.1717 | 13086525.5673 | 58525850.4536 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85201118.847 | 140414274.7166 | 100000 | 30.2762 | 2814.1256 | 4637.7724 | 57.3698 | 94.5473
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.983 | 44.6663 | 7.671 | 4 | 2781.7852 | 4581.203 | 56.7105 | 93.394 | 171.3248 | 18.7586 | 121.7344 | 10748991.3208 | 0 | 5434794.2333 | 0 | 0 | 0 | 2762274.0149 | 7388963.2319 | 19224566.6447 | 13121161.7603 | 58680751.2059 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85356019.5994 | 140569175.469 | 133352.1432 | 30.6839 | 2781.7852 | 4581.203 | 56.7105 | 93.394
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.2787 | 45.0481 | 7.7485 | 4 | 2757.5219 | 4538.9341 | 56.2158 | 92.5323 | 171.1621 | 18.6922 | 111.4816 | 10794188.9327 | 0 | 5468710.4125 | 0 | 0 | 0 | 2718905.6681 | 7402903.9552 | 19260837.5469 | 13145917.3964 | 58791463.9118 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85466732.3052 | 140679888.1748 | 177827.941 | 30.994 | 2757.5219 | 4538.9341 | 56.2158 | 92.5323
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.2534 | 45.3357 | 7.8071 | 4 | 2739.3193 | 4507.3537 | 55.8447 | 91.8885 | 171.0382 | 18.6418 | 113.3414 | 10827860.0021 | 0 | 5494185.3135 | 0 | 0 | 0 | 2685022.2139 | 7412756.3365 | 19286471.4221 | 13163413.043 | 58869708.3311 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85544976.7245 | 140758132.5941 | 237137.3706 | 31.2286 | 2739.3193 | 4507.3537 | 55.8447 | 91.8885
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.9696 | 45.5479 | 7.851 | 4 | 2725.6645 | 4483.8235 | 55.5664 | 91.4088 | 170.9463 | 18.6046 | 123.7867 | 10852422.362 | 0 | 5512887.6696 | 0 | 0 | 0 | 2658443.4139 | 7419263.8438 | 19303402.6212 | 13174968.9343 | 58921388.8449 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85596657.2384 | 140809813.108 | 316227.766 | 31.404 | 2725.6645 | 4483.8235 | 55.5664 | 91.4088
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.5297 | 45.7132 | 7.8846 | 4 | 2715.4218 | 4466.0958 | 55.3575 | 91.0474 | 170.8739 | 18.5753 | 114.1142 | 10871531.2622 | 0 | 5527502.5391 | 0 | 0 | 0 | 2638582.556 | 7424670.3793 | 19317469.3177 | 13184569.7436 | 58964325.7979 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85639594.1914 | 140852750.061 | 421696.5034 | 31.5382 | 2715.4218 | 4466.0958 | 55.3575 | 91.0474
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9318 | 45.8327 | 7.9094 | 4 | 2707.7392 | 4452.9198 | 55.2009 | 90.7788 | 170.8217 | 18.5543 | 111.8076 | 10885187.5525 | 0 | 5537988.5041 | 0 | 0 | 0 | 2623000.0448 | 7428008.6796 | 19326154.8901 | 13190497.8253 | 58990837.4964 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85666105.8899 | 140879261.7595 | 562341.3252 | 31.6375 | 2707.7392 | 4452.9198 | 55.2009 | 90.7788
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2413 | 45.9244 | 7.9282 | 4 | 2701.9769 | 4443.0096 | 55.0835 | 90.5768 | 170.7813 | 18.538 | 111.5284 | 10895667.9826 | 0 | 5546056.0285 | 0 | 0 | 0 | 2611347.4123 | 7430697.8551 | 19333151.5733 | 13195273.2053 | 59012194.0571 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85687462.4505 | 140900618.3201 | 749894.2093 | 31.7129 | 2701.9769 | 4443.0096 | 55.0835 | 90.5768
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.4823 | 45.9954 | 7.9426 | 4 | 2697.6552 | 4435.5388 | 54.9954 | 90.4245 | 170.7498 | 18.5253 | 125.4527 | 10903810.3119 | 0 | 5552335.1251 | 0 | 0 | 0 | 2602726.8008 | 7432960.1728 | 19339037.6597 | 13199290.5802 | 59030160.6505 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85705429.044 | 140918584.9136 | 1000000 | 31.7703 | 2697.6552 | 4435.5388 | 54.9954 | 90.4245
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.648 | 46.0449 | 7.953 | 4 | 2694.4141 | 4430.0185 | 54.9293 | 90.3119 | 170.728 | 18.5166 | 120.3237 | 10909398.0751 | 0 | 5556653.8464 | 0 | 0 | 0 | 2595868.8644 | 7434149.1065 | 19342131.0214 | 13201401.8632 | 59039602.7769 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85714871.1704 | 140928027.04 | 1333521.4322 | 31.8121 | 2694.4141 | 4430.0185 | 54.9293 | 90.3119
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.7944 | 46.0877 | 7.9614 | 4 | 2691.9833 | 4425.7665 | 54.8797 | 90.2252 | 170.7089 | 18.5089 | 113.9311 | 10914329.5696 | 0 | 5560465.2048 | 0 | 0 | 0 | 2591204.2611 | 7435739.6239 | 19346269.2214 | 13204226.2697 | 59052234.1507 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85727502.5441 | 140940658.4137 | 1778279.41 | 31.8455 | 2691.9833 | 4425.7665 | 54.8797 | 90.2252
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.8844 | 46.1147 | 7.9672 | 4 | 2690.1604 | 4422.6817 | 54.8426 | 90.1623 | 170.697 | 18.5041 | 126.8726 | 10917355.2614 | 0 | 5562809.3598 | 0 | 0 | 0 | 2587237.6822 | 7436286.8983 | 19347693.1172 | 13205198.1078 | 59056580.4266 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85731848.8201 | 140945004.6897 | 2371373.7057 | 31.8687 | 2690.1604 | 4422.6817 | 54.8426 | 90.1623
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.9575 | 46.1364 | 7.9717 | 4 | 2688.7934 | 4420.3397 | 54.8147 | 90.1146 | 170.6874 | 18.5003 | 121.9638 | 10919814.4993 | 0 | 5564714.5934 | 0 | 0 | 0 | 2584384.3831 | 7436876.2556 | 19349226.5039 | 13206244.6757 | 59061260.911 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85736529.3044 | 140949685.174 | 3162277.6602 | 31.8866 | 2688.7934 | 4420.3397 | 54.8147 | 90.1146
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.0159 | 46.1536 | 7.9751 | 4 | 2687.7682 | 4418.5658 | 54.7938 | 90.0784 | 170.6797 | 18.4972 | 127.6589 | 10921775.4448 | 0 | 5566233.84 | 0 | 0 | 0 | 2582319.3621 | 7437428.1723 | 19350662.478 | 13207224.7576 | 59065644.0547 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85740912.4482 | 140954068.3178 | 4216965.0343 | 31.9004 | 2687.7682 | 4418.5658 | 54.7938 | 90.0784
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.065 | 46.1678 | 7.9778 | 4 | 2686.9994 | 4417.2082 | 54.7781 | 90.0508 | 170.6733 | 18.4946 | 118.4826 | 10923425.6801 | 0 | 5567511.8561 | 0 | 0 | 0 | 2580889.8247 | 7438012.6708 | 19352183.2231 | 13208262.6974 | 59070285.9522 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85745554.3456 | 140958710.2152 | 5623413.2519 | 31.9113 | 2686.9994 | 4417.2082 | 54.7781 | 90.0508
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.089 | 46.1753 | 7.9795 | 4 | 2686.4229 | 4416.2562 | 54.7664 | 90.0314 | 170.6701 | 18.4933 | 124.1789 | 10924232.1201 | 0 | 5568138.7806 | 0 | 0 | 0 | 2579525.1934 | 7438039.4767 | 19352252.9667 | 13208310.2988 | 59070498.8363 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85745767.2297 | 140958923.0993 | 7498942.0933 | 31.9182 | 2686.4229 | 4416.2562 | 54.7664 | 90.0314
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1038 | 46.18 | 7.9808 | 4 | 2685.9905 | 4415.559 | 54.7575 | 90.0171 | 170.6681 | 18.4925 | 115.7429 | 10924727.1953 | 0 | 5568524.5715 | 0 | 0 | 0 | 2578427.0833 | 7437954.7515 | 19352032.5292 | 13208159.8457 | 59069825.9766 | 961560.8286 | 25713707.5648 | 25713707.5648 | 19344069.7794 | 10155378.5254 | 0 | 85745094.37 | 140958250.2396 | 10000000 | 31.9231 | 2685.9905 | 4415.559 | 54.7575 | 90.0171
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7398 | 0.19271 | 0.018398 | 4 | 414067.3389 | 1181251.4965 | 8441.3228 | 24081.4095 | 115.8567 | 20.6489 | 53.8071 | 433282.2159 | 0 | 194079.0618 | 0 | 0 | 0 | 402320.2649 | 401575.8016 | 1044817.8612 | 713109.6591 | 3189184.8645 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 30472035.8501 | 86930638.0027 | 100 | 0.073592 | 414067.3389 | 1181251.4965 | 8441.3228 | 24081.4095
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8802 | 0.40489 | 0.042383 | 4 | 186702.4224 | 519731.646 | 3806.1814 | 10595.4326 | 130.0247 | 21.362 | 52.0354 | 611899.8266 | 0 | 269286.6113 | 0 | 0 | 0 | 529385.5609 | 550123.0795 | 1431307.4072 | 976896.7159 | 4368899.2015 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 31651750.1871 | 88110352.3397 | 133.3521 | 0.16953 | 186702.4224 | 519731.646 | 3806.1814 | 10595.4326
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2445 | 0.69794 | 0.078525 | 4 | 104738.8777 | 284485.1827 | 2135.2437 | 5799.6152 | 140.9574 | 21.8425 | 37.281 | 811474.5931 | 0 | 342686.1417 | 0 | 0 | 0 | 658993.4038 | 707130.1141 | 1839807.5045 | 1255706.4261 | 5615798.1833 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 32898649.1689 | 89357251.3215 | 177.8279 | 0.3141 | 104738.8777 | 284485.1827 | 2135.2437 | 5799.6152
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9345 | 1.0917 | 0.12938 | 4 | 66289.3735 | 175387.69 | 1351.3985 | 3575.5153 | 149.7428 | 22.1902 | 58.8044 | 1040462.7484 | 0 | 428494.8109 | 0 | 0 | 0 | 798223.761 | 884200.7149 | 2300508.8858 | 1570144.5853 | 7022035.5063 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 34304886.4919 | 90763488.6445 | 237.1374 | 0.5175 | 66289.3735 | 175387.69 | 1351.3985 | 3575.5153
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.054 | 1.6106 | 0.19884 | 4 | 45157.4908 | 116141.6256 | 920.5965 | 2367.7041 | 156.8622 | 22.4483 | 62.6849 | 1306026.4221 | 0 | 530400.0823 | 0 | 0 | 0 | 951214.5358 | 1087180.0057 | 2828619.3635 | 1930590.8379 | 8634031.2473 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 35916882.233 | 92375484.3855 | 316.2278 | 0.79537 | 45157.4908 | 116141.6256 | 920.5965 | 2367.7041
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7756 | 2.2955 | 0.29239 | 4 | 32340.035 | 80612.7919 | 659.2954 | 1643.4008 | 162.7106 | 22.6436 | 57.7314 | 1621183.6594 | 0 | 654511.9473 | 0 | 0 | 0 | 1127719.7579 | 1327331.9922 | 3453445.5704 | 2357047.563 | 10541240.4901 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 37824091.4757 | 94282693.6283 | 421.6965 | 1.1696 | 32340.035 | 80612.7919 | 659.2954 | 1643.4008
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2024 | 3.1764 | 0.41648 | 4 | 24027.0556 | 57917.3916 | 489.824 | 1180.7244 | 167.3789 | 22.7856 | 74.3526 | 1988099.9782 | 0 | 802899.4201 | 0 | 0 | 0 | 1323714.0459 | 1604738.2433 | 4175199.7319 | 2849659.6088 | 12744311.0282 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 40027162.0138 | 96485764.1664 | 562.3413 | 1.6659 | 24027.0556 | 57917.3916 | 489.824 | 1180.7244
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5487 | 4.3085 | 0.5798 | 4 | 18369.5647 | 42713.691 | 374.4884 | 870.7764 | 171.1106 | 22.8843 | 59.9358 | 2418933.7855 | 0 | 981807.5087 | 0 | 0 | 0 | 1545453.7786 | 1929016.0784 | 5018904.1404 | 3425505.204 | 15319620.4956 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 42602471.4812 | 99061073.6338 | 749.8942 | 2.3192 | 18369.5647 | 42713.691 | 374.4884 | 870.7764
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9808 | 5.7393 | 0.79222 | 4 | 14378.4596 | 32195.1016 | 293.1243 | 656.3407 | 174.0331 | 22.9423 | 60.2008 | 2918118.8066 | 0 | 1194587.7011 | 0 | 0 | 0 | 1789490.8372 | 2301856.9645 | 5988959.6459 | 4087588.0192 | 18280601.9746 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 45563452.9602 | 102022055.1128 | 1000 | 3.1689 | 14378.4596 | 32195.1016 | 293.1243 | 656.3407
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.7756 | 7.5429 | 1.0663 | 4 | 11484.6274 | 24722.2619 | 234.1297 | 503.9967 | 176.3072 | 22.9595 | 62.4265 | 3497695.4496 | 0 | 1448127.8079 | 0 | 0 | 0 | 2060113.7533 | 2732315.4342 | 7108924.2848 | 4851986.8982 | 21699163.628 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 48982014.6136 | 105440616.7662 | 1333.5214 | 4.265 | 11484.6274 | 24722.2619 | 234.1297 | 503.9967
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.1166 | 9.7743 | 1.4143 | 4 | 9341.807 | 19322.0725 | 190.4454 | 393.9066 | 178.0197 | 22.93 | 69.7016 | 4158773.4893 | 0 | 1744983.2833 | 0 | 0 | 0 | 2349999.5308 | 3218964.9583 | 8375086.521 | 5716168.6414 | 25563976.424 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 52846827.4096 | 109305429.5622 | 1778.2794 | 5.657 | 9341.807 | 19322.0725 | 190.4454 | 393.9066
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.1741 | 12.4857 | 1.8478 | 4 | 7730.1013 | 15368.6314 | 157.5886 | 313.3103 | 179.2488 | 22.844 | 76.3413 | 4900092.8167 | 0 | 2086968.1328 | 0 | 0 | 0 | 2651342.7164 | 3758977.4297 | 9780088.1998 | 6675111.1571 | 29852580.4525 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 57135431.4381 | 113594033.5907 | 2371.3737 | 7.3913 | 7730.1013 | 15368.6314 | 157.5886 | 313.3103
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.9381 | 15.6836 | 2.3725 | 4 | 6505.3006 | 12454.4778 | 132.6194 | 253.9014 | 180.0352 | 22.6885 | 87.3143 | 5706788.126 | 0 | 2470008.6927 | 0 | 0 | 0 | 2947073.5609 | 4338309.448 | 11287391.2741 | 7703876.4773 | 34453447.579 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 61736298.5647 | 118194900.7173 | 3162.2777 | 9.4902 | 6505.3006 | 12454.4778 | 132.6194 | 253.9014
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0922 | 19.293 | 2.9814 | 4 | 5570.0177 | 10304.2765 | 113.5523 | 210.0666 | 180.3952 | 22.453 | 94.2599 | 6545863.7489 | 0 | 2881432.2333 | 0 | 0 | 0 | 3210554.771 | 4928761.7937 | 12823627.1592 | 8752389.0353 | 39142628.7413 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 66425479.727 | 122884081.8796 | 4216.965 | 11.9255 | 5570.0177 | 10304.2765 | 113.5523 | 210.0666
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.0286 | 23.155 | 3.6513 | 4 | 4855.7973 | 8721.4244 | 98.992 | 177.798 | 180.3524 | 22.1364 | 110.3296 | 7372542.3268 | 0 | 3301838.9156 | 0 | 0 | 0 | 3414705.5354 | 5494743.8433 | 14296196.3534 | 9757447.7687 | 43637474.7431 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 70920325.7288 | 127378927.8813 | 5623.4133 | 14.6053 | 4855.7973 | 8721.4244 | 98.992 | 177.798
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9145 | 27.0425 | 4.3446 | 4 | 4312.0689 | 7560.8403 | 87.9074 | 154.138 | 179.9663 | 21.7542 | 93.5094 | 8138759.8118 | 0 | 3707775.4928 | 0 | 0 | 0 | 3539422.1136 | 6000523.3931 | 15612130.9923 | 10655600.1994 | 47654212.003 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 74937062.9886 | 131395665.1412 | 7498.9421 | 17.3784 | 4312.0689 | 7560.8403 | 87.9074 | 154.138
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9345 | 30.7248 | 5.0185 | 4 | 3899.9163 | 6712.4273 | 79.5051 | 136.8419 | 179.3374 | 21.336 | 114.1659 | 8808283.1138 | 0 | 4078519.5136 | 0 | 0 | 0 | 3580827.4319 | 6422375.7231 | 16709704.2212 | 11404716.481 | 51004426.4846 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 78287277.4703 | 134745879.6229 | 10000 | 20.0741 | 3899.9163 | 6712.4273 | 79.5051 | 136.8419
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4887 | 34.0251 | 5.6366 | 4 | 3588.7083 | 6092.8047 | 73.1607 | 124.2101 | 178.5818 | 20.9157 | 102.558 | 9363932.4215 | 0 | 4400577.4387 | 0 | 0 | 0 | 3550813.2775 | 6752976.0237 | 17569858.3878 | 11991789.3742 | 53629946.9233 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 80912797.909 | 137371400.0616 | 13335.2143 | 22.5465 | 3588.7083 | 6092.8047 | 73.1607 | 124.2101
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.2575 | 36.8416 | 6.1753 | 4 | 3354.5709 | 5640.2243 | 68.3875 | 114.9836 | 177.8062 | 20.5254 | 112.0376 | 9805873.8825 | 0 | 4668326.7603 | 0 | 0 | 0 | 3470536.2013 | 6998447.3692 | 18208524.4756 | 12427692.1024 | 55579400.7911 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 82862251.7768 | 139320853.9293 | 17782.7941 | 24.7013 | 3354.5709 | 5640.2243 | 68.3875 | 114.9836
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.2307 | 39.1599 | 6.6266 | 4 | 3178.6996 | 5308.69 | 64.8021 | 108.2248 | 177.0815 | 20.1822 | 110.4674 | 10147514.7499 | 0 | 4884037.9479 | 0 | 0 | 0 | 3363249.8772 | 7173973.0043 | 18665206.1729 | 12739386.7446 | 56973368.4968 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 84256219.4824 | 140714821.635 | 23713.7371 | 26.5065 | 3178.6996 | 5308.69 | 64.8021 | 108.2248
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.5714 | 41.0172 | 6.9935 | 4 | 3046.7184 | 5064.9821 | 62.1115 | 103.2565 | 176.4463 | 19.8935 | 103.8534 | 10406814.2924 | 0 | 5053892.7712 | 0 | 0 | 0 | 3247992.0831 | 7296392.6672 | 18983717.0242 | 12956776.9454 | 57945585.7836 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 85228436.7693 | 141687038.9219 | 31622.7766 | 27.9738 | 3046.7184 | 5064.9821 | 62.1115 | 103.2565
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5265 | 42.4773 | 7.2852 | 4 | 2947.7074 | 4885.1538 | 60.093 | 99.5905 | 175.9133 | 19.6579 | 113.7765 | 10601690.1567 | 0 | 5185642.4692 | 0 | 0 | 0 | 3137656.456 | 7380745.742 | 19203186.4215 | 13106569.3187 | 58615490.564 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 85898341.5496 | 142356943.7022 | 42169.6503 | 29.1407 | 2947.7074 | 4885.1538 | 60.093 | 99.5905
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3534 | 43.6105 | 7.5135 | 4 | 2873.4338 | 4751.9971 | 58.5788 | 96.8759 | 175.4794 | 19.4699 | 110.8555 | 10747460.1819 | 0 | 5286822.843 | 0 | 0 | 0 | 3039301.7338 | 7438698.0559 | 19353966.4547 | 13209479.7896 | 59075729.059 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 86358580.0447 | 142817182.1972 | 56234.1325 | 30.0541 | 2873.4338 | 4751.9971 | 58.5788 | 96.8759
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2692 | 44.4778 | 7.6899 | 4 | 2817.7148 | 4653.2005 | 57.4429 | 94.8618 | 175.1355 | 19.3231 | 104.7983 | 10855718.0014 | 0 | 5363593.2796 | 0 | 0 | 0 | 2955292.7487 | 7478095.5716 | 19456470.7089 | 13279441.0493 | 59388611.3595 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 86671462.3451 | 143130064.4977 | 74989.4209 | 30.7595 | 2817.7148 | 4653.2005 | 57.4429 | 94.8618
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.4935 | 45.1411 | 7.8253 | 4 | 2775.9134 | 4579.6338 | 56.5907 | 93.362 | 174.8654 | 19.2091 | 107.9924 | 10936645.9733 | 0 | 5421970.152 | 0 | 0 | 0 | 2886353.7642 | 7505538.2569 | 19527870.9469 | 13328173.1789 | 59606552.2723 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 86889403.2579 | 143348005.4105 | 100000 | 31.3012 | 2775.9134 | 4579.6338 | 56.5907 | 93.362
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.1861 | 45.6469 | 7.9287 | 4 | 2744.5531 | 4524.7397 | 55.9514 | 92.2429 | 174.6553 | 19.1211 | 115.2061 | 10997263.4084 | 0 | 5466288.1785 | 0 | 0 | 0 | 2831163.2335 | 7524938.78 | 19578347.1283 | 13362624.2099 | 59760624.9387 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87043475.9243 | 143502078.0769 | 133352.1432 | 31.715 | 2744.5531 | 4524.7397 | 55.9514 | 92.2429
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.4554 | 46.0272 | 8.0071 | 4 | 2721.0265 | 4483.8034 | 55.4718 | 91.4084 | 174.4951 | 19.0544 | 125.6089 | 11042164.6466 | 0 | 5499463.3343 | 0 | 0 | 0 | 2787358.1947 | 7538304.6085 | 19613122.2725 | 13386358.9603 | 59866772.017 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87149623.0026 | 143608225.1552 | 177827.941 | 32.0282 | 2721.0265 | 4483.8034 | 55.4718 | 91.4084
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3982 | 46.3106 | 8.066 | 4 | 2703.3775 | 4453.2795 | 55.112 | 90.7861 | 174.3746 | 19.0045 | 113.3658 | 11075202.809 | 0 | 5524072.0734 | 0 | 0 | 0 | 2752888.8803 | 7547343.8675 | 19636640.57 | 13402410.6816 | 59938558.8818 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87221409.8674 | 143680012.02 | 237137.3706 | 32.2639 | 2703.3775 | 4453.2795 | 55.112 | 90.7861
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.1339 | 46.531 | 8.1111 | 4 | 2690.1385 | 4430.3076 | 54.8421 | 90.3178 | 174.2798 | 18.9653 | 124.3587 | 11100806.5057 | 0 | 5543256.0634 | 0 | 0 | 0 | 2726926.2339 | 7554685.6332 | 19655742.3384 | 13415448.0311 | 59996864.8056 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87279715.7912 | 143738317.9438 | 316227.766 | 32.4443 | 2690.1385 | 4430.3076 | 54.8421 | 90.3178
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.6675 | 46.6917 | 8.1446 | 4 | 2680.2081 | 4413.2154 | 54.6397 | 89.9694 | 174.2105 | 18.9368 | 122.7156 | 11119271.5318 | 0 | 5557160.457 | 0 | 0 | 0 | 2706558.6124 | 7559366.3345 | 19667920.563 | 13423759.9196 | 60034037.4183 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87316888.404 | 143775490.5566 | 421696.5034 | 32.5784 | 2680.2081 | 4413.2154 | 54.6397 | 89.9694
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.0696 | 46.8128 | 8.1699 | 4 | 2672.7599 | 4400.4094 | 54.4878 | 89.7083 | 174.158 | 18.9152 | 120.1424 | 11133129.8113 | 0 | 5567632.4199 | 0 | 0 | 0 | 2691068.5473 | 7562814.0036 | 19676890.691 | 13429882.2163 | 60061417.6894 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87344268.675 | 143802870.8276 | 562341.3252 | 32.6794 | 2672.7599 | 4400.4094 | 54.4878 | 89.7083
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.3861 | 46.9077 | 8.1892 | 4 | 2667.1735 | 4390.741 | 54.3739 | 89.5112 | 174.1165 | 18.8982 | 110.1775 | 11144009.3404 | 0 | 5575872.8971 | 0 | 0 | 0 | 2679656.5964 | 7565820.1452 | 19684712.0547 | 13435220.4577 | 60085291.4915 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87368142.4771 | 143826744.6297 | 749894.2093 | 32.7568 | 2667.1735 | 4390.741 | 54.3739 | 89.5112
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.6102 | 46.9753 | 8.2034 | 4 | 2662.9838 | 4383.5659 | 54.2885 | 89.3649 | 174.0871 | 18.8861 | 109.5551 | 11151690.2576 | 0 | 5581705.2482 | 0 | 0 | 0 | 2670700.6793 | 7567597.5122 | 19689336.399 | 13438376.6677 | 60099406.7639 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87382257.7496 | 143840859.9021 | 1000000 | 32.8137 | 2662.9838 | 4383.5659 | 54.2885 | 89.3649
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.7734 | 47.0248 | 8.214 | 4 | 2659.8417 | 4378.214 | 54.2245 | 89.2558 | 174.0655 | 18.8773 | 118.5469 | 11157271.5144 | 0 | 5585950.5904 | 0 | 0 | 0 | 2663822.3658 | 7568747.3435 | 19692328.0243 | 13440418.5134 | 60108538.3518 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87391389.3374 | 143849991.49 | 1333521.4322 | 32.8559 | 2659.8417 | 4378.214 | 54.2245 | 89.2558
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.9197 | 47.0682 | 8.2225 | 4 | 2657.4852 | 4374.0805 | 54.1764 | 89.1715 | 174.0463 | 18.8694 | 110.1627 | 11162276.4964 | 0 | 5589756.9438 | 0 | 0 | 0 | 2659197.6624 | 7570380.13 | 19696576.1997 | 13443317.9805 | 60121505.4128 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87404356.3984 | 143862958.551 | 1778279.41 | 32.8899 | 2657.4852 | 4374.0805 | 54.1764 | 89.1715
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0124 | 47.0963 | 8.2284 | 4 | 2655.7181 | 4371.0693 | 54.1404 | 89.1102 | 174.0341 | 18.8644 | 107.3463 | 11165436.7897 | 0 | 5592165.6934 | 0 | 0 | 0 | 2655313.8276 | 7571037.3612 | 19698286.1804 | 13444485.0774 | 60126724.9296 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87409575.9153 | 143868178.0679 | 2371373.7057 | 32.9137 | 2655.7181 | 4371.0693 | 54.1404 | 89.1102
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0855 | 47.1183 | 8.233 | 4 | 2654.3928 | 4368.7931 | 54.1134 | 89.0638 | 174.0244 | 18.8604 | 104.3446 | 11167932.632 | 0 | 5594068.4221 | 0 | 0 | 0 | 2652479.43 | 7571647.3888 | 19699873.3473 | 13445568.3514 | 60131569.5716 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87414420.5573 | 143873022.7099 | 3162277.6602 | 32.932 | 2654.3928 | 4368.7931 | 54.1134 | 89.0638
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.1413 | 47.1351 | 8.2364 | 4 | 2653.3989 | 4367.082 | 54.0931 | 89.0289 | 174.017 | 18.8574 | 124.1448 | 11169833.374 | 0 | 5595518.0117 | 0 | 0 | 0 | 2650369.4839 | 7572131.1391 | 19701131.9663 | 13446427.3848 | 60135411.3598 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87418262.3455 | 143876864.4981 | 4216965.0343 | 32.9458 | 2653.3989 | 4367.082 | 54.0931 | 89.0289
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.1755 | 47.1457 | 8.2388 | 4 | 2652.6537 | 4365.8374 | 54.0779 | 89.0035 | 174.0125 | 18.8555 | 115.6316 | 11170999.3238 | 0 | 5596409.0498 | 0 | 0 | 0 | 2648609.0763 | 7572246.8055 | 19701432.9064 | 13446632.7826 | 60136329.9444 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87419180.93 | 143877783.0826 | 5623413.2519 | 32.9554 | 2652.6537 | 4365.8374 | 54.0779 | 89.0035
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.2144 | 47.157 | 8.241 | 4 | 2652.0948 | 4364.8371 | 54.0665 | 88.9831 | 174.0074 | 18.8534 | 119.6311 | 11172326.6734 | 0 | 5597420.4555 | 0 | 0 | 0 | 2647594.6325 | 7572763.2869 | 19702776.6852 | 13447549.9392 | 60140431.6727 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87423282.6583 | 143881884.8109 | 7498942.0933 | 32.9639 | 2652.0948 | 4364.8371 | 54.0665 | 88.9831
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.2339 | 47.163 | 8.2423 | 4 | 2651.6756 | 4364.1365 | 54.058 | 88.9688 | 174.0048 | 18.8524 | 121.4845 | 11172988.0976 | 0 | 5597926.1412 | 0 | 0 | 0 | 2646606.8633 | 7572833.2298 | 19702958.6623 | 13447674.1423 | 60140987.1366 | 961560.8286 | 26321290.157 | 26321290.157 | 19765873.5944 | 10371438.4012 | 0 | 87423838.1222 | 143882440.2748 | 10000000 | 32.9693 | 2651.6756 | 4364.1365 | 54.058 | 88.9688
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8083 | 0.20085 | 0.019516 | 4 | 399636.2912 | 1138987.6462 | 8147.1263 | 23219.8038 | 117.9233 | 21.104 | 50.8153 | 449038.5686 | 0 | 200130.1669 | 0 | 0 | 0 | 416777.5271 | 415719.0425 | 1081615.6728 | 738224.9216 | 3301505.8995 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 31197799.5682 | 88915619.2173 | 100 | 0.078065 | 399636.2912 | 1138987.6462 | 8147.1263 | 23219.8038
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 0.42336 | 0.044939 | 4 | 180399.2445 | 501485.7533 | 3677.6826 | 10223.4654 | 132.5531 | 21.8345 | 55.1303 | 636548.4853 | 0 | 275490.346 | 0 | 0 | 0 | 551156.2425 | 570646.0788 | 1484704.0414 | 1013341.0159 | 4531886.2098 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 32428179.8785 | 90145999.5276 | 133.3521 | 0.17976 | 180399.2445 | 501485.7533 | 3677.6826 | 10223.4654
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3734 | 0.72531 | 0.082992 | 4 | 101504.7767 | 275371.0058 | 2069.3122 | 5613.8104 | 143.56 | 22.3143 | 57.3631 | 840709.419 | 0 | 349408.0144 | 0 | 0 | 0 | 682484.9757 | 730314.9395 | 1900129.6645 | 1296877.5398 | 5799924.5529 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 33696218.2215 | 91414037.8706 | 177.8279 | 0.33197 | 101504.7767 | 275371.0058 | 2069.3122 | 5613.8104
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1003 | 1.1335 | 0.13649 | 4 | 64369.3652 | 170085.5421 | 1312.2566 | 3467.4238 | 152.5141 | 22.666 | 53.9251 | 1077241.444 | 0 | 436670.047 | 0 | 0 | 0 | 826040.0716 | 912581.1094 | 2374348.8505 | 1620541.8785 | 7247423.4009 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 35143717.0696 | 92861536.7187 | 237.1374 | 0.54597 | 64369.3652 | 170085.5421 | 1312.2566 | 3467.4238
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2781 | 1.6736 | 0.20959 | 4 | 43912.5863 | 112758.4186 | 895.2175 | 2298.7329 | 159.8066 | 22.9284 | 64.0794 | 1353053.6991 | 0 | 540877.6848 | 0 | 0 | 0 | 985525.2441 | 1122988.0849 | 2921784.6404 | 1994178.0537 | 8918407.4069 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 36814701.0755 | 94532520.7246 | 316.2278 | 0.83836 | 43912.5863 | 112758.4186 | 895.2175 | 2298.7329
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0554 | 2.3827 | 0.30789 | 4 | 31483.9102 | 78349.9363 | 641.8421 | 1597.2694 | 165.7547 | 23.1253 | 69.9823 | 1678131.3023 | 0 | 666926.7833 | 0 | 0 | 0 | 1166986.4616 | 1369697.3734 | 3563671.602 | 2432279.0945 | 10877692.617 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 38773986.2856 | 96491805.9347 | 421.6965 | 1.2315 | 31483.9102 | 78349.9363 | 641.8421 | 1597.2694
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5534 | 3.2949 | 0.43821 | 4 | 23412.7129 | 56341.102 | 477.2998 | 1148.5896 | 170.5091 | 23.2684 | 64.2222 | 2056787.896 | 0 | 817695.3582 | 0 | 0 | 0 | 1368687.953 | 1654836.7708 | 4305545.8239 | 2938623.495 | 13142177.2969 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 41038470.9656 | 98756290.6147 | 562.3413 | 1.7528 | 23412.7129 | 56341.102 | 477.2998 | 1148.5896
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9897 | 4.4672 | 0.60965 | 4 | 17914.2819 | 41582.6714 | 365.2069 | 847.719 | 174.3123 | 23.3673 | 63.1942 | 2501462.6545 | 0 | 999486.8186 | 0 | 0 | 0 | 1596966.5337 | 1988187.2427 | 5172855.3722 | 3530580.0831 | 15789538.7048 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 43685832.3735 | 101403652.0226 | 749.8942 | 2.4386 | 17914.2819 | 41582.6714 | 365.2069 | 847.719
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.5534 | 5.953 | 0.83278 | 4 | 14032.2894 | 31359.1654 | 286.0672 | 639.299 | 177.3007 | 23.4247 | 66.8019 | 3018450.6186 | 0 | 1216439.8251 | 0 | 0 | 0 | 1850138.6925 | 2373161.3631 | 6174479.0646 | 4214208.8344 | 18846878.3984 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 46743172.067 | 104460991.7161 | 1000 | 3.3311 | 14032.2894 | 31359.1654 | 286.0672 | 639.299
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4723 | 7.8167 | 1.12 | 4 | 11215.8006 | 24099.332 | 228.6493 | 491.2975 | 179.613 | 23.4396 | 70.3576 | 3615267.0438 | 0 | 1473476.4232 | 0 | 0 | 0 | 2127373.3688 | 2814285.566 | 7322193.7533 | 4997547.6926 | 22350143.8477 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 50246437.5163 | 107964257.1654 | 1333.5214 | 4.48 | 11215.8006 | 24099.332 | 228.6493 | 491.2975
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.9714 | 10.1237 | 1.4845 | 4 | 9129.2759 | 18849.0445 | 186.1126 | 384.2633 | 181.3572 | 23.406 | 56.5871 | 4296549.224 | 0 | 1774665.728 | 0 | 0 | 0 | 2425043.8977 | 3313540.9514 | 8621153.8548 | 5884114.6529 | 26315068.3088 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 54211361.9775 | 111929181.6266 | 1778.2794 | 5.9382 | 9129.2759 | 18849.0445 | 186.1126 | 384.2633
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.207 | 12.9237 | 1.9381 | 4 | 7559.4806 | 15004.5322 | 154.1102 | 305.8877 | 182.6077 | 23.3133 | 88.0102 | 5059633.9932 | 0 | 2121270.1624 | 0 | 0 | 0 | 2733891.8388 | 3866770.4378 | 10060543.4955 | 6866527.6592 | 30708637.5869 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 58604931.2555 | 116322750.9047 | 2371.3737 | 7.7525 | 7559.4806 | 15004.5322 | 154.1102 | 305.8877
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.1561 | 16.2202 | 2.486 | 4 | 6366.5005 | 12170.8872 | 129.7897 | 248.12 | 183.4043 | 23.1481 | 82.3209 | 5888367.6221 | 0 | 2508790.6608 | 0 | 0 | 0 | 3035902.1458 | 4458893.5672 | 11601126.417 | 7918007.1589 | 35411087.5719 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 63307381.2405 | 121025200.8896 | 3162.2777 | 9.9438 | 6366.5005 | 12170.8872 | 129.7897 | 248.12
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.4734 | 19.9294 | 3.1197 | 4 | 5455.7403 | 10081.0373 | 111.2226 | 205.5156 | 183.7637 | 22.9 | 99.0017 | 6747468.5181 | 0 | 2923753.3112 | 0 | 0 | 0 | 3302982.4896 | 5059939.6844 | 13164925.1224 | 8985331.9082 | 40184401.0339 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 68080694.7026 | 125798514.3517 | 4216.965 | 12.4787 | 5455.7403 | 10081.0373 | 111.2226 | 205.5156
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.5413 | 23.8868 | 3.8147 | 4 | 4760.5569 | 8543.1748 | 97.0504 | 174.1642 | 183.712 | 22.5686 | 117.8869 | 7591295.1036 | 0 | 3346644.1587 | 0 | 0 | 0 | 3508278.5263 | 5634024.9375 | 14658577.1901 | 10004780.1359 | 44743600.0521 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 72639893.7207 | 130357713.3698 | 5623.4133 | 15.2587 | 4760.5569 | 8543.1748 | 97.0504 | 174.1642
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.5003 | 27.8545 | 4.5309 | 4 | 4231.606 | 7416.2495 | 86.267 | 151.1903 | 183.3133 | 22.171 | 96.5257 | 8370107.4858 | 0 | 3753412.8245 | 0 | 0 | 0 | 3631229.1593 | 6144352.2931 | 15986344.2868 | 10911008.4623 | 48796454.5118 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 76692748.1805 | 134410567.8296 | 7498.9421 | 18.1238 | 4231.606 | 7416.2495 | 86.267 | 151.1903
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.5204 | 31.5943 | 5.224 | 4 | 3830.8706 | 6593.0314 | 78.0975 | 134.4079 | 182.6736 | 21.7392 | 116.4543 | 9047106.1773 | 0 | 4123089.9992 | 0 | 0 | 0 | 3668325.5413 | 6567023.4699 | 17086047.987 | 11661578.8343 | 52153172.0089 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 80049465.6776 | 137767285.3267 | 10000 | 20.8959 | 3830.8706 | 6593.0314 | 78.0975 | 134.4079
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0286 | 34.9331 | 5.8571 | 4 | 3528.4974 | 5992.0894 | 71.9332 | 122.1568 | 181.9122 | 21.3085 | 119.19 | 9606933.6694 | 0 | 4443048.5437 | 0 | 0 | 0 | 3633577.9372 | 6896588.4586 | 17943508.4845 | 12246813.2429 | 54770470.3363 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 82666764.0049 | 140384583.654 | 13335.2143 | 23.4283 | 3528.4974 | 5992.0894 | 71.9332 | 122.1568
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.7534 | 37.7809 | 6.4078 | 4 | 3300.973 | 5552.827 | 67.2948 | 113.2019 | 181.1314 | 20.9079 | 104.0941 | 10051928.2772 | 0 | 4708982.87 | 0 | 0 | 0 | 3549424.1326 | 7141030.7591 | 18579497.2083 | 12680888.6152 | 56711751.8624 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 84608045.531 | 142325865.1801 | 17782.7941 | 25.6312 | 3300.973 | 5552.827 | 67.2948 | 113.2019
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6534 | 40.1147 | 6.8675 | 4 | 3130.1746 | 5231.2927 | 63.8128 | 106.647 | 180.407 | 20.5585 | 106.3483 | 10394491.3355 | 0 | 4922275.5145 | 0 | 0 | 0 | 3438482.4368 | 7314547.2219 | 19030951.4514 | 12989015.4125 | 58089763.3727 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 85986057.0414 | 143703876.6905 | 23713.7371 | 27.4701 | 3130.1746 | 5231.2927 | 63.8128 | 106.647
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9332 | 41.9833 | 7.2407 | 4 | 3002.0299 | 4994.8659 | 61.2004 | 101.8271 | 179.7732 | 20.2649 | 116.9905 | 10654484.1521 | 0 | 5090188.3639 | 0 | 0 | 0 | 3320754.0085 | 7435516.3445 | 19345688.2944 | 13203829.775 | 59050460.9384 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 86946754.6071 | 144664574.2562 | 31622.7766 | 28.9627 | 3002.0299 | 4994.8659 | 61.2004 | 101.8271
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.8318 | 43.4498 | 7.5369 | 4 | 2905.9141 | 4820.4222 | 59.241 | 98.2708 | 179.2427 | 20.0259 | 112.2854 | 10849588.3804 | 0 | 5220209.4847 | 0 | 0 | 0 | 3208584.217 | 7518569.012 | 19561774.2987 | 13351312.9131 | 59710038.306 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 87606331.9746 | 145324151.6237 | 42169.6503 | 30.1476 | 2905.9141 | 4820.4222 | 59.241 | 98.2708
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6102 | 44.5866 | 7.7685 | 4 | 2833.8226 | 4691.2532 | 57.7713 | 95.6375 | 178.8116 | 19.8356 | 106.9628 | 10995396.175 | 0 | 5319948.6626 | 0 | 0 | 0 | 3108941.7772 | 7575471.7798 | 19709823.628 | 13452359.6225 | 60161941.6451 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88058235.3138 | 145776054.9629 | 56234.1325 | 31.074 | 2833.8226 | 4691.2532 | 57.7713 | 95.6375
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.4996 | 45.4593 | 7.9475 | 4 | 2779.7466 | 4595.3393 | 56.6689 | 93.6822 | 178.4689 | 19.6866 | 112.1837 | 11104103.5328 | 0 | 5395904.8303 | 0 | 0 | 0 | 3024398.9032 | 7614518.8339 | 19811416.0531 | 13521698.5402 | 60472040.6935 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88368334.3621 | 146086154.0112 | 74989.4209 | 31.7901 | 2779.7466 | 4595.3393 | 56.6689 | 93.6822
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6844 | 46.1217 | 8.0845 | 4 | 2739.1815 | 4524.0208 | 55.8419 | 92.2283 | 178.2021 | 19.5718 | 129.0942 | 11184669.9706 | 0 | 5453159.5585 | 0 | 0 | 0 | 2954650.0861 | 7641067.05 | 19880489.0657 | 13568842.2905 | 60682878.0215 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88579171.6901 | 146296991.3392 | 100000 | 32.3378 | 2739.1815 | 4524.0208 | 55.8419 | 92.2283
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3434 | 46.6257 | 8.1889 | 4 | 2708.751 | 4470.8169 | 55.2216 | 91.1437 | 177.9952 | 19.4834 | 126.2011 | 11244905.3659 | 0 | 5496536.5046 | 0 | 0 | 0 | 2898835.8764 | 7659708.3213 | 19928989.8298 | 13601945.0586 | 60830920.9566 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88727214.6253 | 146445034.2744 | 133352.1432 | 32.7558 | 2708.751 | 4470.8169 | 55.2216 | 91.1437
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.6003 | 47.0081 | 8.2683 | 4 | 2685.9233 | 4431.069 | 54.7562 | 90.3333 | 177.8358 | 19.4158 | 123.1424 | 11289994.6865 | 0 | 5529342.9451 | 0 | 0 | 0 | 2854930.7213 | 7672964.6577 | 19963480.0978 | 13625485.3752 | 60936198.4837 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88832492.1523 | 146550311.8015 | 177827.941 | 33.0734 | 2685.9233 | 4431.069 | 54.7562 | 90.3333
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.536 | 47.2937 | 8.3281 | 4 | 2668.7995 | 4401.4191 | 54.4071 | 89.7289 | 177.7157 | 19.3651 | 121.0677 | 11323250.6918 | 0 | 5553734.5793 | 0 | 0 | 0 | 2820459.0196 | 7682003.2733 | 19986996.7217 | 13641535.9543 | 61007980.2399 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88904273.9085 | 146622093.5576 | 237137.3706 | 33.3125 | 2668.7995 | 4401.4191 | 54.4071 | 89.7289
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.2593 | 47.5139 | 8.3737 | 4 | 2655.9549 | 4379.14 | 54.1452 | 89.2747 | 177.622 | 19.3256 | 120.0712 | 11348780.6661 | 0 | 5572570.4355 | 0 | 0 | 0 | 2794344.9415 | 7689121.4568 | 20005516.7749 | 13654176.2711 | 61064510.5458 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88960804.2145 | 146678623.8636 | 316227.766 | 33.4948 | 2655.9549 | 4379.14 | 54.1452 | 89.2747
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.7929 | 47.6769 | 8.4078 | 4 | 2646.3207 | 4362.5164 | 53.9488 | 88.9358 | 177.5524 | 19.2964 | 118.4637 | 11367511.2858 | 0 | 5586456.5355 | 0 | 0 | 0 | 2774090.4752 | 7693942.7356 | 20018060.7534 | 13662737.7942 | 61102799.5796 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 88999093.2482 | 146716912.8973 | 421696.5034 | 33.6313 | 2646.3207 | 4362.5164 | 53.9488 | 88.9358
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.1903 | 47.7985 | 8.4334 | 4 | 2639.0947 | 4350.0849 | 53.8015 | 88.6824 | 177.5003 | 19.2746 | 115.4917 | 11381406.0669 | 0 | 5596794.3526 | 0 | 0 | 0 | 2758577.7442 | 7697343.4838 | 20026908.8027 | 13668776.7697 | 61129807.2198 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89026100.8885 | 146743920.5376 | 562341.3252 | 33.7336 | 2639.0947 | 4350.0849 | 53.8015 | 88.6824
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.4922 | 47.8908 | 8.4527 | 4 | 2633.6752 | 4340.7548 | 53.691 | 88.4922 | 177.4606 | 19.258 | 112.7406 | 11391928.8753 | 0 | 5604643.4539 | 0 | 0 | 0 | 2746889.9613 | 7699950.2933 | 20033691.1862 | 13673405.8858 | 61150509.6559 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89046803.3245 | 146764622.9736 | 749894.2093 | 33.8109 | 2633.6752 | 4340.7548 | 53.691 | 88.4922
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.724 | 47.9614 | 8.4674 | 4 | 2629.6106 | 4333.7381 | 53.6082 | 88.3491 | 177.43 | 19.2452 | 114.9185 | 11399987.1794 | 0 | 5610665.4261 | 0 | 0 | 0 | 2738168.1205 | 7702040.0831 | 20039128.3907 | 13677116.8895 | 61167106.0894 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89063399.758 | 146781219.4071 | 1000000 | 33.8694 | 2629.6106 | 4333.7381 | 53.6082 | 88.3491
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8944 | 48.0135 | 8.4783 | 4 | 2626.5624 | 4328.497 | 53.546 | 88.2423 | 177.4075 | 19.2358 | 111.6006 | 11405902.1772 | 0 | 5615093.1922 | 0 | 0 | 0 | 2731499.9381 | 7703473.1699 | 20042856.9885 | 13679661.7342 | 61178487.2002 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89074780.8688 | 146792600.518 | 1333521.4322 | 33.9131 | 2626.5624 | 4328.497 | 53.546 | 88.2423
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0233 | 48.0529 | 8.4865 | 4 | 2624.2764 | 4324.5632 | 53.4994 | 88.1621 | 177.3904 | 19.2286 | 126.7498 | 11410371.0824 | 0 | 5618442.0845 | 0 | 0 | 0 | 2726499.316 | 7704571.8684 | 20045715.5765 | 13681612.7792 | 61187212.7069 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89083506.3756 | 146801326.0247 | 1778279.41 | 33.9459 | 2624.2764 | 4324.5632 | 53.4994 | 88.1621
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.1159 | 48.0814 | 8.4925 | 4 | 2622.562 | 4321.6346 | 53.4645 | 88.1024 | 177.3781 | 19.2235 | 124.686 | 11413577.464 | 0 | 5620847.7545 | 0 | 0 | 0 | 2722637.9179 | 7705254.6232 | 20047491.9645 | 13682825.2006 | 61192634.9247 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89088928.5934 | 146806748.2425 | 2371373.7057 | 33.9702 | 2622.562 | 4321.6346 | 53.4645 | 88.1024
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.187 | 48.1031 | 8.4971 | 4 | 2621.2764 | 4319.4308 | 53.4383 | 88.0574 | 177.3687 | 19.2196 | 121.1749 | 11416038.9598 | 0 | 5622695.3634 | 0 | 0 | 0 | 2719773.8587 | 7705818.1909 | 20048958.2521 | 13683825.972 | 61197110.5968 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89093404.2655 | 146811223.9146 | 3162277.6602 | 33.9886 | 2621.2764 | 4319.4308 | 53.4383 | 88.0574
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2427 | 48.1201 | 8.5006 | 4 | 2620.3122 | 4317.7665 | 53.4186 | 88.0235 | 177.3613 | 19.2165 | 115.3948 | 11417967.4522 | 0 | 5624143.1047 | 0 | 0 | 0 | 2717678.2046 | 7706317.617 | 20050257.6563 | 13684712.842 | 61201076.8767 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89097370.5453 | 146815190.1944 | 4216965.0343 | 34.0026 | 2620.3122 | 4317.7665 | 53.4186 | 88.0235
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2692 | 48.1288 | 8.5029 | 4 | 2619.5892 | 4316.5949 | 53.4039 | 87.9996 | 177.3577 | 19.215 | 105.5233 | 11418880.0448 | 0 | 5624831.4908 | 0 | 0 | 0 | 2715741.717 | 7706186.7686 | 20049917.2155 | 13684480.4842 | 61200037.721 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89096331.3896 | 146814151.0387 | 5623413.2519 | 34.0116 | 2619.5892 | 4316.5949 | 53.4039 | 87.9996
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.3009 | 48.1384 | 8.5049 | 4 | 2619.0471 | 4315.6577 | 53.3928 | 87.9805 | 177.3535 | 19.2132 | 112.4749 | 11419974.901 | 0 | 5625653.7961 | 0 | 0 | 0 | 2714567.305 | 7706476.4408 | 20050670.8833 | 13684994.8779 | 61202338.2041 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89098631.8728 | 146816451.5219 | 7498942.0933 | 34.0195 | 2619.0471 | 4315.6577 | 53.3928 | 87.9805
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.3204 | 48.1445 | 8.5062 | 4 | 2618.6405 | 4314.9763 | 53.3845 | 87.9666 | 177.3509 | 19.2122 | 114.1411 | 11420646.0755 | 0 | 5626158.8462 | 0 | 0 | 0 | 2713584.0773 | 7706551.7096 | 20050866.7173 | 13685128.5387 | 61202935.9646 | 961560.8286 | 26934732.84 | 26934732.84 | 20193244.4958 | 10589842.3133 | 0 | 89099229.6332 | 146817049.2823 | 10000000 | 34.025 | 2618.6405 | 4314.9763 | 53.3845 | 87.9666
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.21023 | 0.020695 | 4 | 385872.9091 | 1098480.8568 | 7866.5412 | 22394.0181 | 120.1343 | 21.5667 | 45.1664 | 466538.4021 | 0 | 207014.8852 | 0 | 0 | 0 | 433095.1254 | 431592.8809 | 1122916.1443 | 766413.3421 | 3427570.7799 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 31943167.2224 | 90933975.5816 | 100 | 0.082782 | 385872.9091 | 1098480.8568 | 7866.5412 | 22394.0181
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0971 | 0.44118 | 0.047589 | 4 | 174429.718 | 484329.4543 | 3555.9857 | 9873.711 | 135.0117 | 22.3035 | 55.5475 | 660426.0053 | 0 | 281262.2163 | 0 | 0 | 0 | 571873.5802 | 590289.1027 | 1535811.1603 | 1048222.6747 | 4687884.7394 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 33203481.182 | 92194289.5411 | 133.3521 | 0.19035 | 174429.718 | 484329.4543 | 3555.9857 | 9873.711
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5003 | 0.75289 | 0.087617 | 4 | 98437.855 | 266758.7495 | 2006.7888 | 5438.2379 | 146.1529 | 22.7856 | 44.2781 | 870040.2153 | 0 | 355992.6774 | 0 | 0 | 0 | 705858.8384 | 753437.7751 | 1960290.5395 | 1337938.5731 | 5983558.6188 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 34499155.0613 | 93489963.4205 | 177.8279 | 0.35047 | 98437.855 | 266758.7495 | 2006.7888 | 5438.2379
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2512 | 1.1733 | 0.14379 | 4 | 62546.9931 | 165109.6075 | 1275.1051 | 3365.9827 | 155.2274 | 23.1396 | 55.8531 | 1112524.2675 | 0 | 444081.3744 | 0 | 0 | 0 | 851811.2701 | 939282.5957 | 2443820.6406 | 1667957.8027 | 7459477.9509 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 35975074.3935 | 94965882.7526 | 237.1374 | 0.57517 | 62546.9931 | 165109.6075 | 1275.1051 | 3365.9827
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4903 | 1.7354 | 0.22063 | 4 | 42730.0371 | 109574.3732 | 871.1096 | 2233.8218 | 162.7232 | 23.4073 | 63.8746 | 1399237.346 | 0 | 550754.1015 | 0 | 0 | 0 | 1018476.2021 | 1157702.3833 | 3012104.124 | 2055822.9572 | 9194097.1142 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 37709693.5567 | 96700501.9158 | 316.2278 | 0.88251 | 42730.0371 | 109574.3732 | 871.1096 | 2233.8218
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 2.4671 | 0.32372 | 4 | 30669.9812 | 76227.1311 | 625.2491 | 1553.9932 | 168.7664 | 23.6058 | 56.8394 | 1733366.6946 | 0 | 678337.7917 | 0 | 0 | 0 | 1203818.4189 | 1410053.933 | 3668671.0918 | 2503943.4038 | 11198191.3338 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 39713787.7764 | 98704596.1355 | 421.6965 | 1.2949 | 30669.9812 | 76227.1311 | 625.2491 | 1553.9932
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9017 | 3.4151 | 0.46058 | 4 | 22828.2649 | 54847.8986 | 465.3851 | 1118.1486 | 173.6407 | 23.751 | 66.607 | 2126074.4115 | 0 | 832315.7133 | 0 | 0 | 0 | 1413759.2759 | 1705138.2663 | 4436419.9969 | 3027947.8072 | 13541655.4711 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 42057251.9136 | 101048060.2728 | 562.3413 | 1.8423 | 22828.2649 | 54847.8986 | 465.3851 | 1118.1486
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.4307 | 4.6288 | 0.64041 | 4 | 17480.8622 | 40509.5222 | 356.371 | 825.8414 | 177.5184 | 23.8502 | 65.4543 | 2585027.6603 | 0 | 1017088.2875 | 0 | 0 | 0 | 1648933.0552 | 2047909.1112 | 5328239.4234 | 3636632.8908 | 16263830.4285 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 44779426.8711 | 103770235.2302 | 749.8942 | 2.5616 | 17480.8622 | 40509.5222 | 356.371 | 825.8414
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1038 | 6.1655 | 0.87427 | 4 | 13702.5293 | 30571.2001 | 279.3446 | 623.2353 | 180.5633 | 23.9068 | 83.4979 | 3118047.7066 | 0 | 1237358.1519 | 0 | 0 | 0 | 1909181.3591 | 2443189.0148 | 6356676.6496 | 4338562.43 | 19403015.3121 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 47918611.7546 | 106909420.1137 | 1000 | 3.4971 | 13702.5293 | 30571.2001 | 279.3446 | 623.2353
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.1561 | 8.0923 | 1.1751 | 4 | 10959.5589 | 23509.7456 | 223.4254 | 479.278 | 182.9199 | 23.9193 | 73.778 | 3733189.3479 | 0 | 1498244.8932 | 0 | 0 | 0 | 2194059.3097 | 2895942.4848 | 7534648.306 | 5142552.2904 | 22998636.6319 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 51514233.0745 | 110505041.4336 | 1333.5214 | 4.7004 | 10959.5589 | 23509.7456 | 223.4254 | 479.278
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8332 | 10.481 | 1.5569 | 4 | 8926.5768 | 18398.7898 | 181.9803 | 375.0842 | 184.7003 | 23.8813 | 80.3188 | 4436548.1173 | 0 | 1804469.708 | 0 | 0 | 0 | 2501279.6602 | 3409496.0193 | 8870809.2585 | 6054509.5958 | 27077112.359 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 55592708.8015 | 114583517.1607 | 1778.2794 | 6.2278 | 8926.5768 | 18398.7898 | 181.9803 | 375.0842
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.2398 | 13.3694 | 2.0309 | 4 | 7396.6682 | 14658.3141 | 150.7911 | 298.8296 | 185.9707 | 23.7818 | 84.2427 | 5221046.3284 | 0 | 2155428.3183 | 0 | 0 | 0 | 2817098.5797 | 3975493.5583 | 10343418.7528 | 7059595.8348 | 31572081.3723 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 60087677.8148 | 119078486.174 | 2371.3737 | 8.1236 | 7396.6682 | 14658.3141 | 150.7911 | 298.8296
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.3734 | 16.766 | 2.6023 | 4 | 6233.9925 | 11901.0658 | 127.0884 | 242.6193 | 186.7775 | 23.6066 | 95.9634 | 6071969.8668 | 0 | 2547402.5625 | 0 | 0 | 0 | 3125387.3622 | 4580456.3187 | 11917407.7604 | 8133875.6747 | 36376499.5454 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 64892095.9879 | 123882904.3471 | 3162.2777 | 10.4094 | 6233.9925 | 11901.0658 | 127.0884 | 242.6193
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.8501 | 20.5754 | 3.2613 | 4 | 5346.5963 | 9868.5843 | 108.9976 | 201.1844 | 187.1357 | 23.3456 | 95.4261 | 6950966.3339 | 0 | 2965785.9752 | 0 | 0 | 0 | 3395847.1296 | 5191913.7811 | 13508294.6505 | 9219688.6666 | 41232496.5369 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 69748092.9795 | 128738901.3386 | 4216.965 | 13.0453 | 5346.5963 | 9868.5843 | 108.9976 | 201.1844
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.0371 | 24.6262 | 3.9815 | 4 | 4669.5507 | 8373.6482 | 95.1951 | 170.7081 | 187.0751 | 22.9991 | 101.084 | 7811263.481 | 0 | 3390803.4263 | 0 | 0 | 0 | 3601645.0434 | 5773447.6607 | 15021326.5163 | 10252364.0048 | 45850850.1324 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 74366446.575 | 133357254.9341 | 5623.4133 | 15.9258 | 4669.5507 | 8373.6482 | 95.1951 | 170.7081
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.0466 | 28.6691 | 4.7204 | 4 | 4154.6751 | 7278.9412 | 84.6987 | 148.3911 | 186.6649 | 22.5866 | 111.7948 | 8601437.8906 | 0 | 3797778.7317 | 0 | 0 | 0 | 3721798.3436 | 6287195.8367 | 16357993.8859 | 11164666.9503 | 49930871.6386 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 78446468.0812 | 137437276.4403 | 7498.9421 | 18.8815 | 4154.6751 | 7278.9412 | 84.6987 | 148.3911
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.0823 | 32.4704 | 5.4329 | 4 | 3764.81 | 6479.3068 | 76.7507 | 132.0894 | 186.0143 | 22.1406 | 108.9223 | 9286700.7407 | 0 | 4166871.2098 | 0 | 0 | 0 | 3755342.7166 | 6711476.7201 | 17461885.7126 | 11918095.8047 | 53300372.9045 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 81815969.3471 | 140806777.7062 | 10000 | 21.7318 | 3764.81 | 6479.3068 | 76.7507 | 132.0894
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5554 | 35.8505 | 6.0813 | 4 | 3470.7771 | 5895.8573 | 70.7565 | 120.195 | 185.2459 | 21.6984 | 133.535 | 9851033.0855 | 0 | 4485059.8625 | 0 | 0 | 0 | 3716063.3888 | 7040340.9714 | 18317523.035 | 12502085.8588 | 55912106.202 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 84427702.6446 | 143418511.0037 | 13335.2143 | 24.3253 | 3470.7771 | 5895.8573 | 70.7565 | 120.195
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.207 | 38.7215 | 6.6432 | 4 | 3249.6111 | 5469.5726 | 66.2477 | 111.5046 | 184.4633 | 21.2895 | 120.2769 | 10297725.4093 | 0 | 4748409.3454 | 0 | 0 | 0 | 3627178.4264 | 7282592.1407 | 18947810.8849 | 12932270.2675 | 57835986.4743 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 86351582.9168 | 145342391.276 | 17782.7941 | 26.5729 | 3249.6111 | 5469.5726 | 66.2477 | 111.5046
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.0681 | 41.0792 | 7.1121 | 4 | 3083.6366 | 5157.246 | 62.8641 | 105.1374 | 183.7366 | 20.9324 | 119.4445 | 10642606.8602 | 0 | 4960227.5665 | 0 | 0 | 0 | 3513727.8551 | 7455459.2899 | 19397575.7473 | 13239244.0278 | 59208841.3467 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 87724437.7892 | 146715246.1484 | 23713.7371 | 28.4484 | 3083.6366 | 5157.246 | 62.8641 | 105.1374
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.2755 | 42.9557 | 7.4912 | 4 | 2959.139 | 4927.8202 | 60.3261 | 100.4603 | 183.1054 | 20.6345 | 111.1385 | 10902690.7472 | 0 | 5125897.8032 | 0 | 0 | 0 | 3393107.6287 | 7574461.5099 | 19707195.1129 | 13450565.6069 | 60153918.4088 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 88669514.8514 | 147660323.2105 | 31622.7766 | 29.9646 | 2959.139 | 4927.8202 | 60.3261 | 100.4603
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.1204 | 44.429 | 7.7919 | 4 | 2865.7748 | 4758.4726 | 58.4227 | 97.0079 | 182.5773 | 20.3922 | 115.3021 | 11098053.1741 | 0 | 5254276.5324 | 0 | 0 | 0 | 3279149.5332 | 7656276.9035 | 19920061.9845 | 13595851.6208 | 60803669.7485 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 89319266.191 | 148310074.5502 | 42169.6503 | 31.1676 | 2865.7748 | 4758.4726 | 58.4227 | 97.0079
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.8601 | 45.5717 | 8.0269 | 4 | 2795.7566 | 4633.0358 | 56.9953 | 94.4507 | 182.1482 | 20.1991 | 120.2819 | 11244203.5419 | 0 | 5352837.4095 | 0 | 0 | 0 | 3178451.2343 | 7712441.9524 | 20066191.9207 | 13695588.3049 | 61249714.3637 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 89765310.8062 | 148756119.1654 | 56234.1325 | 32.1077 | 2795.7566 | 4633.0358 | 56.9953 | 94.4507
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.6929 | 46.4416 | 8.2078 | 4 | 2743.2414 | 4540.0331 | 55.9247 | 92.5547 | 181.8103 | 20.0494 | 113.868 | 11352168.7718 | 0 | 5427195.3114 | 0 | 0 | 0 | 3092525.9005 | 7750037.0937 | 20164006.7665 | 13762348.9471 | 61548282.791 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90063879.2336 | 149054687.5927 | 74989.4209 | 32.8312 | 2743.2414 | 4540.0331 | 55.9247 | 92.5547
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8707 | 47.1114 | 8.347 | 4 | 2703.8507 | 4470.6706 | 55.1217 | 91.1407 | 181.5431 | 19.9322 | 120.7198 | 11433551.4893 | 0 | 5484186.7732 | 0 | 0 | 0 | 3022803.9047 | 7776811.4452 | 20233668.137 | 13809894.2638 | 61760916.013 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90276512.4556 | 149267320.8147 | 100000 | 33.3881 | 2703.8507 | 4470.6706 | 55.1217 | 91.1407
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.4908 | 47.6121 | 8.4524 | 4 | 2674.3032 | 4419.1039 | 54.5193 | 90.0894 | 181.3399 | 19.8439 | 112.1361 | 11493161.7895 | 0 | 5526487.9498 | 0 | 0 | 0 | 2966189.9956 | 7794477.4966 | 20279631.579 | 13841265.2574 | 61901214.0678 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90416810.5103 | 149407618.8695 | 133352.1432 | 33.8095 | 2674.3032 | 4419.1039 | 54.5193 | 90.0894
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.7406 | 47.9979 | 8.533 | 4 | 2652.1392 | 4380.4582 | 54.0674 | 89.3016 | 181.1808 | 19.775 | 123.6391 | 11538611.8857 | 0 | 5559066.1745 | 0 | 0 | 0 | 2922301.2432 | 7807791.9283 | 20314272.9991 | 13864908.7385 | 62006952.9692 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90522549.4118 | 149513357.7709 | 177827.941 | 34.1319 | 2652.1392 | 4380.4582 | 54.0674 | 89.3016
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.6614 | 48.2835 | 8.5934 | 4 | 2635.514 | 4351.6804 | 53.7285 | 88.7149 | 181.0621 | 19.7239 | 121.2839 | 11571783.5461 | 0 | 5583035.1598 | 0 | 0 | 0 | 2887613.9942 | 7816548.753 | 20337056.4608 | 13880458.9192 | 62076496.8331 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90592093.2756 | 149582901.6348 | 237137.3706 | 34.3736 | 2635.514 | 4351.6804 | 53.7285 | 88.7149
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3607 | 48.5003 | 8.6392 | 4 | 2623.0439 | 4330.1185 | 53.4743 | 88.2753 | 180.9711 | 19.6849 | 115.2077 | 11596808.91 | 0 | 5601224.8582 | 0 | 0 | 0 | 2861047.8532 | 7823041.8323 | 20353950.1212 | 13891989.1896 | 62128062.7645 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90643659.207 | 149634467.5662 | 316227.766 | 34.5567 | 2623.0439 | 4330.1185 | 53.4743 | 88.2753
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8944 | 48.6655 | 8.6739 | 4 | 2613.6908 | 4313.9394 | 53.2836 | 87.9455 | 180.9012 | 19.655 | 113.428 | 11615803.5671 | 0 | 5615093.1922 | 0 | 0 | 0 | 2840904.4002 | 7828002.4522 | 20366856.6365 | 13900798.1515 | 62167458.3995 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90683054.8421 | 149673863.2012 | 421696.5034 | 34.6954 | 2613.6908 | 4313.9394 | 53.2836 | 87.9455
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2887 | 48.788 | 8.6998 | 4 | 2606.6758 | 4301.8563 | 53.1406 | 87.6992 | 180.8493 | 19.6328 | 110.9674 | 11629782.6396 | 0 | 5625336.5593 | 0 | 0 | 0 | 2825400.2297 | 7831402.5771 | 20375703.0642 | 13906836.0201 | 62194461.09 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90710057.5325 | 149700865.8917 | 562341.3252 | 34.7991 | 2606.6758 | 4301.8563 | 53.1406 | 87.6992
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5787 | 48.8784 | 8.7191 | 4 | 2601.4147 | 4292.8345 | 53.0334 | 87.5152 | 180.811 | 19.6165 | 108.5524 | 11640032.0493 | 0 | 5632867.7223 | 0 | 0 | 0 | 2813490.8962 | 7833692.3604 | 20381660.6106 | 13910902.168 | 62212645.8068 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90728242.2494 | 149719050.6085 | 749894.2093 | 34.8765 | 2601.4147 | 4292.8345 | 53.0334 | 87.5152
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.8151 | 48.9512 | 8.7341 | 4 | 2597.4689 | 4285.9823 | 52.9529 | 87.3755 | 180.7797 | 19.6031 | 112.4259 | 11648369.44 | 0 | 5639002.3223 | 0 | 0 | 0 | 2804936.064 | 7836000.0523 | 20387664.7514 | 13915000.1174 | 62230972.7474 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90746569.19 | 149737377.5491 | 1000000 | 34.9365 | 2597.4689 | 4285.9823 | 52.9529 | 87.3755
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.966 | 48.9988 | 8.7447 | 4 | 2594.5098 | 4280.9771 | 52.8926 | 87.2735 | 180.7596 | 19.5946 | 116.9484 | 11653678.7864 | 0 | 5642919.8547 | 0 | 0 | 0 | 2797836.7063 | 7836829.7855 | 20389823.547 | 13916473.5398 | 62237562.2198 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90753158.6624 | 149743967.0215 | 1333521.4322 | 34.9789 | 2594.5098 | 4280.9771 | 52.8926 | 87.2735
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.0929 | 49.0382 | 8.753 | 4 | 2592.2907 | 4277.1582 | 52.8474 | 87.1957 | 180.7427 | 19.5874 | 107.0662 | 11658140.0168 | 0 | 5646211.9789 | 0 | 0 | 0 | 2792818.5647 | 7837896.5185 | 20392598.9676 | 13918367.8214 | 62246033.8678 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90761630.3103 | 149752438.6695 | 1778279.41 | 35.0121 | 2592.2907 | 4277.1582 | 52.8474 | 87.1957
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.1977 | 49.0704 | 8.7595 | 4 | 2590.6265 | 4274.248 | 52.8134 | 87.1363 | 180.7288 | 19.5815 | 119.3572 | 11661824.8537 | 0 | 5648931.5957 | 0 | 0 | 0 | 2789274.3582 | 7839012.015 | 20395501.2605 | 13920348.6959 | 62254892.779 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90770489.2216 | 149761297.5807 | 2371373.7057 | 35.038 | 2590.6265 | 4274.248 | 52.8134 | 87.1363
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.2561 | 49.089 | 8.7639 | 4 | 2589.3784 | 4272.1658 | 52.788 | 87.0939 | 180.721 | 19.5782 | 114.9296 | 11663869.1308 | 0 | 5650445.149 | 0 | 0 | 0 | 2786119.0116 | 7839168.9836 | 20395909.6607 | 13920627.4374 | 62256139.373 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90771735.8155 | 149762544.1747 | 3162277.6602 | 35.0554 | 2589.3784 | 4272.1658 | 52.788 | 87.0939
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3144 | 49.1069 | 8.7675 | 4 | 2588.4425 | 4270.5331 | 52.7689 | 87.0606 | 180.7132 | 19.5749 | 120.1091 | 11665917.356 | 0 | 5651958.6009 | 0 | 0 | 0 | 2784100.2038 | 7839770.7027 | 20397475.2102 | 13921695.9572 | 62260918.0307 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90776514.4733 | 149767322.8324 | 4216965.0343 | 35.0699 | 2588.4425 | 4270.5331 | 52.7689 | 87.0606
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3487 | 49.1178 | 8.77 | 4 | 2587.7407 | 4269.3554 | 52.7546 | 87.0366 | 180.7086 | 19.5729 | 112.7306 | 11667117.3401 | 0 | 5652847.4063 | 0 | 0 | 0 | 2782355.0393 | 7839904.7164 | 20397823.8865 | 13921933.9359 | 62261982.3246 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90777578.7671 | 149768387.1263 | 5623413.2519 | 35.0799 | 2587.7407 | 4269.3554 | 52.7546 | 87.0366
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3876 | 49.1295 | 8.7722 | 4 | 2587.2144 | 4268.4078 | 52.7439 | 87.0173 | 180.7035 | 19.5707 | 115.9644 | 11668483.3925 | 0 | 5653856.2783 | 0 | 0 | 0 | 2781362.7728 | 7840443.953 | 20399226.8695 | 13922891.5007 | 62266264.7668 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90781861.2094 | 149772669.5685 | 7498942.0933 | 35.0887 | 2587.2144 | 4268.4078 | 52.7439 | 87.0173
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.407 | 49.1357 | 8.7736 | 4 | 2586.8197 | 4267.7448 | 52.7358 | 87.0037 | 180.7009 | 19.5696 | 117.141 | 11669164.1235 | 0 | 5654360.6974 | 0 | 0 | 0 | 2780383.77 | 7840524.3505 | 20399436.0473 | 13923034.2687 | 62266903.2575 | 961560.8286 | 27554035.6139 | 27554035.6139 | 20626182.4834 | 10810590.2618 | 0 | 90782499.7 | 149773308.0591 | 10000000 | 35.0943 | 2586.8197 | 4267.7448 | 52.7358 | 87.0037
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9593 | 0.21927 | 0.021926 | 4 | 372733.1793 | 1060030.4712 | 7598.67 | 21610.155 | 122.2753 | 22.0255 | 41.5382 | 483513.3036 | 0 | 213563.0975 | 0 | 0 | 0 | 448714.8034 | 446858.5698 | 1162634.3352 | 793521.8235 | 3548805.933 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 32689565.2403 | 92967133.5231 | 100 | 0.087702 | 372733.1793 | 1060030.4712 | 7598.67 | 21610.155
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1897 | 0.45757 | 0.050322 | 4 | 168768.4357 | 468225.3219 | 3440.5728 | 9545.4065 | 137.3532 | 22.767 | 55.1786 | 682713.0558 | 0 | 286336.9286 | 0 | 0 | 0 | 590582.7309 | 608256.759 | 1582559.3162 | 1080129.2517 | 4830578.0422 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 33971337.3495 | 94248905.6322 | 133.3521 | 0.20129 | 168768.4357 | 468225.3219 | 3440.5728 | 9545.4065
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6265 | 0.78088 | 0.092405 | 4 | 95527.3749 | 258606.6655 | 1947.4547 | 5272.0467 | 148.7451 | 23.2567 | 49.3453 | 899654.47 | 0 | 362513.2329 | 0 | 0 | 0 | 729334.2692 | 776685.7691 | 2020777.051 | 1379221.8601 | 6168186.6523 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 35308945.9596 | 95586514.2423 | 177.8279 | 0.36962 | 95527.3749 | 258606.6655 | 1947.4547 | 5272.0467
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4339 | 1.2197 | 0.15147 | 4 | 60815.7364 | 160301.9047 | 1239.811 | 3267.9712 | 158.0767 | 23.6181 | 71.9945 | 1152508.1665 | 0 | 453006.1919 | 0 | 0 | 0 | 882761.8149 | 970427.7076 | 2524853.833 | 1723264.6216 | 7706822.3354 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 36847581.6426 | 97125149.9254 | 237.1374 | 0.60589 | 60815.7364 | 160301.9047 | 1239.811 | 3267.9712
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6996 | 1.7978 | 0.232 | 4 | 41605.6765 | 106559.6654 | 848.188 | 2172.3629 | 165.6359 | 23.886 | 63.7401 | 1445634.9671 | 0 | 560449.8603 | 0 | 0 | 0 | 1051294.5447 | 1192377.9551 | 3102322.8488 | 2117399.0907 | 9469479.2666 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 38610238.5739 | 98887806.8566 | 316.2278 | 0.928 | 41605.6765 | 106559.6654 | 848.188 | 2172.3629
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.589 | 2.5565 | 0.34016 | 4 | 29895.5096 | 74195.8839 | 609.4604 | 1512.5835 | 171.811 | 24.0872 | 68.6572 | 1791217.2024 | 0 | 690440.2464 | 0 | 0 | 0 | 1243172.8281 | 1452683.808 | 3779585.282 | 2579644.6176 | 11536743.9845 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 40677503.2918 | 100955071.5745 | 421.6965 | 1.3607 | 29895.5096 | 74195.8839 | 609.4604 | 1512.5835
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2501 | 3.5374 | 0.48363 | 4 | 22271.7504 | 53430.3658 | 454.0398 | 1089.2503 | 176.7766 | 24.2336 | 74.2126 | 2196219.8338 | 0 | 846872.1397 | 0 | 0 | 0 | 1459225.4411 | 1755903.7917 | 4568501.4806 | 3118096.1338 | 13944818.8208 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 43085578.1281 | 103363146.4108 | 562.3413 | 1.9345 | 22271.7504 | 53430.3658 | 454.0398 | 1089.2503
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8593 | 4.7904 | 0.67193 | 4 | 17067.8832 | 39494.8917 | 347.9519 | 805.1568 | 180.7204 | 24.3329 | 52.4738 | 2668395.6567 | 0 | 1034122.5584 | 0 | 0 | 0 | 1699999.9752 | 2106982.0942 | 5481935.2076 | 3741533.4217 | 16732968.9136 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 45873728.2209 | 106151296.5036 | 749.8942 | 2.6877 | 17067.8832 | 39494.8917 | 347.9519 | 805.1568
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.6593 | 6.3829 | 0.91702 | 4 | 13388.1211 | 29821.2019 | 272.935 | 607.9455 | 183.8323 | 24.3886 | 59.9383 | 3219312.9565 | 0 | 1258378.362 | 0 | 0 | 0 | 1969215.7912 | 2514293.7728 | 6541676.6442 | 4464828.7277 | 19967706.2543 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 49108465.5616 | 109386033.8443 | 1000 | 3.6681 | 13388.1211 | 29821.2019 | 272.935 | 607.9455
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.8601 | 8.3777 | 1.2321 | 4 | 10715.0971 | 22946.0898 | 218.4417 | 467.7871 | 186.2363 | 24.3987 | 82.6584 | 3854247.1653 | 0 | 1523641.4374 | 0 | 0 | 0 | 2263098.2672 | 2979984.8793 | 7753309.377 | 5291792.9644 | 23666074.0906 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 52806833.3979 | 113084401.6806 | 1333.5214 | 4.9283 | 10715.0971 | 22946.0898 | 218.4417 | 467.7871
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.6808 | 10.8411 | 1.6311 | 4 | 8733.0854 | 17971.8942 | 178.0358 | 366.3814 | 188.0453 | 24.3562 | 85.1284 | 4577075.6638 | 0 | 1833658.4057 | 0 | 0 | 0 | 2576994.22 | 3505214.0329 | 9119847.8954 | 6224483.5827 | 27837273.8005 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 56978033.1078 | 117255601.3905 | 1778.2794 | 6.5244 | 8733.0854 | 17971.8942 | 178.0358 | 366.3814
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.283 | 13.8255 | 2.1264 | 4 | 7241.1737 | 14328.1092 | 147.6211 | 292.0979 | 189.3389 | 24.2493 | 80.5847 | 5385083.9961 | 0 | 2189792.3381 | 0 | 0 | 0 | 2901719.3641 | 4085872.3223 | 10630601.6551 | 7255604.0666 | 32448673.7423 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 61589433.0496 | 121867001.3323 | 2371.3737 | 8.5054 | 7241.1737 | 14328.1092 | 147.6211 | 292.0979
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5844 | 17.3195 | 2.7216 | 4 | 6107.3853 | 11644.3478 | 124.5073 | 237.3858 | 190.1542 | 24.064 | 105.8419 | 6257176.1491 | 0 | 2585666.7651 | 0 | 0 | 0 | 3215148.4738 | 4702616.6413 | 12235243.8614 | 8350805.3446 | 37346657.2354 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 66487416.5427 | 126764984.8254 | 3162.2777 | 10.8864 | 6107.3853 | 11644.3478 | 124.5073 | 237.3858
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.2145 | 21.229 | 3.4061 | 4 | 5242.269 | 9666.442 | 106.8707 | 197.0635 | 190.5112 | 23.7898 | 81.7865 | 7155816.0759 | 0 | 3007293.938 | 0 | 0 | 0 | 3488673.3492 | 5324195.5116 | 13852464.5785 | 9454591.7145 | 42283035.1676 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 71423794.4749 | 131701362.7576 | 4216.965 | 13.6246 | 5242.269 | 9666.442 | 106.8707 | 197.0635
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.5038 | 25.3699 | 4.1513 | 4 | 4582.5195 | 8212.5267 | 93.4209 | 167.4235 | 190.442 | 23.4285 | 116.7729 | 8031660.8364 | 0 | 3433964.202 | 0 | 0 | 0 | 3694133.2022 | 5912305.7138 | 15382606.6867 | 10498945.1446 | 46953615.7856 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 76094375.0929 | 136371943.3756 | 5623.4133 | 16.6054 | 4582.5195 | 8212.5267 | 93.4209 | 167.4235
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5741 | 29.4911 | 4.9133 | 4 | 4081.0625 | 7148.1133 | 83.198 | 145.724 | 190.0203 | 23.0005 | 106.8323 | 8833792.8827 | 0 | 3841478.5876 | 0 | 0 | 0 | 3812061.4228 | 6430059.8283 | 16729696.6866 | 11418361.7495 | 51065451.1573 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 80206210.4646 | 140483778.7474 | 7498.9421 | 19.6533 | 4081.0625 | 7148.1133 | 83.198 | 145.724
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6144 | 33.3514 | 5.6452 | 4 | 3701.5562 | 6370.9675 | 75.4612 | 129.8808 | 189.3596 | 22.5405 | 118.1894 | 9526693.1119 | 0 | 4209705.4042 | 0 | 0 | 0 | 3841599.5408 | 6855419.2422 | 17836394.6283 | 12173705.8351 | 54443517.7624 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 83584277.0697 | 143861845.3524 | 10000 | 22.5808 | 3701.5562 | 6370.9675 | 75.4612 | 129.8808
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.0512 | 36.7723 | 6.3088 | 4 | 3415.4676 | 5804.099 | 69.6289 | 118.3244 | 188.5849 | 22.0868 | 122.5717 | 10095396.6173 | 0 | 4526122.7951 | 0 | 0 | 0 | 3797772.4118 | 7183523.8114 | 18690055.414 | 12756346.8623 | 57049217.9118 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 86189977.2191 | 146467545.5019 | 13335.2143 | 25.2352 | 3415.4676 | 5804.099 | 69.6289 | 118.3244
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6614 | 39.6744 | 6.8826 | 4 | 3200.3556 | 5389.8519 | 65.2436 | 109.8794 | 187.7983 | 21.6684 | 122.6036 | 10545125.7948 | 0 | 4787771.8775 | 0 | 0 | 0 | 3705293.6097 | 7424894.5999 | 19318052.6938 | 13184967.9098 | 58966106.4854 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 88106865.7927 | 148384434.0754 | 17782.7941 | 27.5303 | 3200.3556 | 5389.8519 | 65.2436 | 109.8794
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.4325 | 42.0422 | 7.3592 | 4 | 3038.9724 | 5086.667 | 61.9536 | 103.6986 | 187.0741 | 21.3059 | 107.5234 | 10889975.2458 | 0 | 4996757.4732 | 0 | 0 | 0 | 3587569.737 | 7594977.9579 | 19760574.7021 | 13486998.2734 | 60316853.3894 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 89457612.6967 | 149735180.9795 | 23713.7371 | 29.4368 | 3038.9724 | 5086.667 | 61.9536 | 103.6986
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.601 | 43.935 | 7.745 | 4 | 2917.9451 | 4863.6499 | 59.4863 | 99.1521 | 186.4427 | 21.0023 | 107.6094 | 11151497.637 | 0 | 5161098.1479 | 0 | 0 | 0 | 3465129.4366 | 7713312.8364 | 20068457.7823 | 13697134.802 | 61256630.6422 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 90397389.9495 | 150674958.2322 | 31622.7766 | 30.9798 | 2917.9451 | 4863.6499 | 59.4863 | 99.1521
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3922 | 45.4148 | 8.0501 | 4 | 2827.1985 | 4699.1473 | 57.6363 | 95.7985 | 185.9172 | 20.7566 | 117.8969 | 11347042.1805 | 0 | 5287848.739 | 0 | 0 | 0 | 3349349.8924 | 7793853.9167 | 20278009.1519 | 13840157.9176 | 61896261.798 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 91037021.1053 | 151314589.388 | 42169.6503 | 32.2004 | 2827.1985 | 4699.1473 | 57.6363 | 95.7985
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0781 | 46.5589 | 8.2881 | 4 | 2759.1521 | 4577.3479 | 56.249 | 93.3154 | 185.4919 | 20.5617 | 115.2347 | 11492879.4741 | 0 | 5384839.8215 | 0 | 0 | 0 | 3247133.6628 | 7848692.6537 | 20420688.2968 | 13937539.3657 | 62331773.2745 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 91472532.5818 | 151750100.8646 | 56234.1325 | 33.1524 | 2759.1521 | 4577.3479 | 56.249 | 93.3154
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.887 | 47.4345 | 8.4716 | 4 | 2708.1211 | 4486.9313 | 55.2087 | 91.4722 | 185.1551 | 20.4096 | 128.689 | 11601298.3657 | 0 | 5458462.4736 | 0 | 0 | 0 | 3160689.5355 | 7885975.6462 | 20517690.9953 | 14003745.7007 | 62627862.7171 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 91768622.0244 | 152046190.3071 | 74989.4209 | 33.8865 | 2708.1211 | 4486.9313 | 55.2087 | 91.4722
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.0233 | 48.1024 | 8.6122 | 4 | 2669.8469 | 4419.6164 | 54.4284 | 90.0999 | 184.8917 | 20.2919 | 117.2295 | 11682161.4448 | 0 | 5514289.6201 | 0 | 0 | 0 | 3090047.4478 | 7911734.42 | 20584710.0409 | 14049487.5764 | 62832430.5501 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 91973189.8574 | 152250758.1401 | 100000 | 34.4489 | 2669.8469 | 4419.6164 | 54.4284 | 90.0999
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.6286 | 48.6059 | 8.719 | 4 | 2641.1389 | 4369.4808 | 53.8432 | 89.0778 | 184.6895 | 20.2023 | 119.5054 | 11742006.0737 | 0 | 5556147.2242 | 0 | 0 | 0 | 3033237.4467 | 7929242.3904 | 20630262.1886 | 14080577.8532 | 62971473.1768 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92112232.4841 | 152389800.7668 | 133352.1432 | 34.876 | 2641.1389 | 4369.4808 | 53.8432 | 89.0778
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.8466 | 48.9884 | 8.8001 | 4 | 2619.6058 | 4332.0104 | 53.4042 | 88.3139 | 184.5337 | 20.1337 | 113.9401 | 11786885.8917 | 0 | 5587853.8481 | 0 | 0 | 0 | 2988713.6737 | 7941746.8313 | 20662796.1787 | 14102782.9699 | 63070779.3933 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92211538.7006 | 152489106.9833 | 177827.941 | 35.2005 | 2619.6058 | 4332.0104 | 53.4042 | 88.3139
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.7675 | 49.2779 | 8.8616 | 4 | 2603.4545 | 4303.9851 | 53.0749 | 87.7426 | 184.4145 | 20.0814 | 122.5561 | 11820514.5449 | 0 | 5611796.5146 | 0 | 0 | 0 | 2954185.8309 | 7950733.7872 | 20686178.3946 | 14118741.8128 | 63142150.885 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92282910.1923 | 152560478.475 | 237137.3706 | 35.4463 | 2603.4545 | 4303.9851 | 53.0749 | 87.7426
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4472 | 49.4924 | 8.9076 | 4 | 2591.3403 | 4283.0851 | 52.828 | 87.3165 | 184.3257 | 20.0426 | 104.4444 | 11845164.7966 | 0 | 5629453.4187 | 0 | 0 | 0 | 2927253.2317 | 7956729.8643 | 20701778.9572 | 14129389.5173 | 63189769.7857 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92330529.093 | 152608097.3757 | 316227.766 | 35.6304 | 2591.3403 | 4283.0851 | 52.828 | 87.3165
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.966 | 49.6558 | 8.9425 | 4 | 2582.2544 | 4267.4016 | 52.6427 | 86.9968 | 184.2575 | 20.0128 | 113.3773 | 11863883.0482 | 0 | 5642919.8547 | 0 | 0 | 0 | 2906847.0215 | 7961323.4705 | 20713730.5782 | 14137546.7443 | 63226250.7174 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92367010.0246 | 152644578.3074 | 421696.5034 | 35.7699 | 2582.2544 | 4267.4016 | 52.6427 | 86.9968
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3681 | 49.7821 | 8.969 | 4 | 2575.4399 | 4255.596 | 52.5038 | 86.7561 | 184.2044 | 19.9897 | 113.1372 | 11878336.7182 | 0 | 5653351.8479 | 0 | 0 | 0 | 2891618.9689 | 7965089.9386 | 20723530.1557 | 14144235.1572 | 63256162.7866 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92396922.0939 | 152674490.3766 | 562341.3252 | 35.8762 | 2575.4399 | 4255.596 | 52.5038 | 86.7561
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6628 | 49.875 | 8.9888 | 4 | 2570.3292 | 4246.7878 | 52.3996 | 86.5765 | 184.1653 | 19.9727 | 121.7601 | 11888894.7185 | 0 | 5660993.7347 | 0 | 0 | 0 | 2879885.2205 | 7967611.7327 | 20730091.3467 | 14148713.3049 | 63276190.058 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92416949.3653 | 152694517.648 | 749894.2093 | 35.9553 | 2570.3292 | 4246.7878 | 52.3996 | 86.5765
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8823 | 49.9442 | 9.0036 | 4 | 2566.4963 | 4240.196 | 52.3215 | 86.4421 | 184.1361 | 19.9601 | 111.0864 | 11896740.5001 | 0 | 5666684.0181 | 0 | 0 | 0 | 2870968.4396 | 7969413.2536 | 20734778.5344 | 14151912.4068 | 63290497.1527 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92431256.4599 | 152708824.7427 | 1000000 | 36.0146 | 2566.4963 | 4240.196 | 52.3215 | 86.4421
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0324 | 49.9923 | 9.0144 | 4 | 2563.6219 | 4235.3263 | 52.2629 | 86.3429 | 184.116 | 19.9514 | 124.7465 | 11902093.9328 | 0 | 5670575.2478 | 0 | 0 | 0 | 2863879.987 | 7970254.1754 | 20736966.4404 | 14153405.6976 | 63297175.4809 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92437934.7882 | 152715503.0709 | 1333521.4322 | 36.0576 | 2563.6219 | 4235.3263 | 52.2629 | 86.3429
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1593 | 50.0322 | 9.0228 | 4 | 2561.4663 | 4231.607 | 52.219 | 86.267 | 184.0991 | 19.944 | 114.181 | 11906617.2964 | 0 | 5673863.3522 | 0 | 0 | 0 | 2858891.1701 | 7971355.0093 | 20739830.5844 | 14155360.5348 | 63305917.9471 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92446677.2544 | 152724245.5371 | 1778279.41 | 36.0913 | 2561.4663 | 4231.607 | 52.219 | 86.267
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2519 | 50.0614 | 9.0291 | 4 | 2559.8497 | 4228.8313 | 52.186 | 86.2104 | 184.0868 | 19.9387 | 111.8782 | 11909915.0961 | 0 | 5676263.1276 | 0 | 0 | 0 | 2855073.1766 | 7972088.0461 | 20741737.7959 | 14156662.2458 | 63311739.4881 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92452498.7954 | 152730067.0781 | 2371373.7057 | 36.1164 | 2559.8497 | 4228.8313 | 52.186 | 86.2104
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3297 | 50.0856 | 9.034 | 4 | 2558.6375 | 4226.7102 | 52.1613 | 86.1672 | 184.0764 | 19.9342 | 120.2428 | 11912685.5827 | 0 | 5678278.7429 | 0 | 0 | 0 | 2852406.5107 | 7972914.6262 | 20743888.3877 | 14158130.0689 | 63318303.919 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92459063.2263 | 152736631.5091 | 3162277.6602 | 36.1361 | 2558.6375 | 4226.7102 | 52.1613 | 86.1672
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3808 | 50.1018 | 9.0375 | 4 | 2557.7284 | 4225.1548 | 52.1428 | 86.1355 | 184.0695 | 19.9312 | 128.1659 | 11914502.9557 | 0 | 5679602.9643 | 0 | 0 | 0 | 2850224.899 | 7973289.0194 | 20744862.482 | 14158794.9083 | 63321277.2286 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92462036.5359 | 152739604.8186 | 4216965.0343 | 36.1501 | 2557.7284 | 4225.1548 | 52.1428 | 86.1355
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4151 | 50.1129 | 9.04 | 4 | 2557.0466 | 4224.0082 | 52.1289 | 86.1121 | 184.0649 | 19.9292 | 120.6647 | 11915719.6607 | 0 | 5680490.6863 | 0 | 0 | 0 | 2848486.8533 | 7973431.9081 | 20745234.2491 | 14159048.647 | 63322412.0045 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92463171.3118 | 152740739.5946 | 5623413.2519 | 36.1601 | 2557.0466 | 4224.0082 | 52.1289 | 86.1121
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4493 | 50.1235 | 9.0422 | 4 | 2556.5354 | 4223.1072 | 52.1184 | 86.0938 | 184.0604 | 19.9272 | 124.2996 | 11916938.8456 | 0 | 5681378.3737 | 0 | 0 | 0 | 2847391.9058 | 7973826.5588 | 20746261.0492 | 14159749.4591 | 63325546.1921 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92466305.4994 | 152743873.7821 | 7498942.0933 | 36.1686 | 2556.5354 | 4223.1072 | 52.1184 | 86.0938
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4734 | 50.131 | 9.0437 | 4 | 2556.152 | 4222.4393 | 52.1106 | 86.0801 | 184.0571 | 19.9258 | 125.2804 | 11917794.9451 | 0 | 5682002.1333 | 0 | 0 | 0 | 2846530.3509 | 7974067.6974 | 20746888.4425 | 14160177.6679 | 63327461.2371 | 961560.8286 | 28179198.4787 | 28179198.4787 | 21064687.5574 | 11033682.2466 | 0 | 92468220.5444 | 152745788.8271 | 10000000 | 36.1748 | 2556.152 | 4222.4393 | 52.1106 | 86.0801
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0325 | 0.2285 | 0.023212 | 4 | 360191.23 | 1023402.626 | 7342.9854 | 20863.4468 | 124.4178 | 22.4842 | 35.6498 | 500718.2277 | 0 | 220164.4761 | 0 | 0 | 0 | 464486.0361 | 462293.8085 | 1202793.6603 | 820931.3881 | 3671387.5969 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 33443169.8598 | 95021269.2796 | 100 | 0.092848 | 360191.23 | 1023402.626 | 7342.9854 | 20863.4468
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2823 | 0.47429 | 0.053161 | 4 | 163401.3158 | 452983.9884 | 3331.1568 | 9234.6913 | 139.6977 | 23.2306 | 51.1876 | 705281.6054 | 0 | 291389.2538 | 0 | 0 | 0 | 609453.0859 | 626388.3386 | 1629733.9671 | 1112326.9202 | 4974573.1711 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 34746355.434 | 96324454.8538 | 133.3521 | 0.21264 | 163401.3158 | 452983.9884 | 3331.1568 | 9234.6913
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7554 | 0.80986 | 0.09737 | 4 | 92763.2575 | 250866.8374 | 1891.1045 | 5114.2598 | 151.3579 | 23.7284 | 68.5623 | 930037.5645 | 0 | 369142.3354 | 0 | 0 | 0 | 753478.1767 | 800536.6499 | 2082832.1504 | 1421575.7406 | 6357602.6175 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 36129384.8804 | 97707484.3002 | 177.8279 | 0.38948 | 92763.2575 | 250866.8374 | 1891.1045 | 5114.2598
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5996 | 1.2638 | 0.15933 | 4 | 59169.6768 | 155788.9412 | 1206.2539 | 3175.9683 | 160.8595 | 24.0939 | 64.096 | 1190717.6489 | 0 | 461069.7976 | 0 | 0 | 0 | 911344.8919 | 999621.6119 | 2600810.3837 | 1775106.5282 | 7938670.8622 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 37710453.1251 | 99288552.5449 | 237.1374 | 0.63733 | 59169.6768 | 155788.9412 | 1206.2539 | 3175.9683
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9165 | 1.8628 | 0.24378 | 4 | 40535.6772 | 103685.7962 | 826.3746 | 2113.7752 | 168.573 | 24.3654 | 65.5481 | 1493556.4596 | 0 | 570452.9633 | 0 | 0 | 0 | 1085498.6078 | 1228308.132 | 3195805.7988 | 2181203.1249 | 9754825.0865 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 39526607.3494 | 101104706.7692 | 316.2278 | 0.97511 | 40535.6772 | 103685.7962 | 826.3746 | 2113.7752
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8667 | 2.6481 | 0.35713 | 4 | 29157.9257 | 72264.4522 | 594.4238 | 1473.2086 | 174.8639 | 24.5687 | 48.7269 | 1850060.2845 | 0 | 702595.9448 | 0 | 0 | 0 | 1283194.6934 | 1495981.8598 | 3892237.9312 | 2656532.3655 | 11880603.0793 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 41652385.3422 | 103230484.762 | 421.6965 | 1.4285 | 29157.9257 | 72264.4522 | 594.4238 | 1473.2086
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6009 | 3.6625 | 0.50739 | 4 | 21741.3678 | 52081.9574 | 443.2272 | 1061.7611 | 179.9193 | 24.7161 | 62.5794 | 2267477.713 | 0 | 861467.06 | 0 | 0 | 0 | 1505375.6429 | 1807384.9622 | 4702444.926 | 3209515.2876 | 14353665.5918 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 44125447.8547 | 105703547.2745 | 562.3413 | 2.0296 | 21741.3678 | 52081.9574 | 443.2272 | 1061.7611
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3003 | 4.9577 | 0.7045 | 4 | 16674.0347 | 38525.6618 | 339.9228 | 785.3977 | 183.935 | 24.8155 | 53.7879 | 2753990.7456 | 0 | 1051576.3395 | 0 | 0 | 0 | 1752844.6667 | 2167780.5832 | 5640120.4046 | 3849498.069 | 17215810.8086 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 46987593.0715 | 108565692.4913 | 749.8942 | 2.818 | 16674.0347 | 38525.6618 | 339.9228 | 785.3977
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.2124 | 6.6036 | 0.96094 | 4 | 13088.0882 | 29108.3662 | 266.8184 | 593.4134 | 187.1045 | 24.8703 | 60.3983 | 3321559.3147 | 0 | 1279219.8559 | 0 | 0 | 0 | 2029509.1294 | 2585812.437 | 6727753.538 | 4591830.0312 | 20535684.3062 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 50307466.5691 | 111885565.9889 | 1000 | 3.8438 | 13088.0882 | 29108.3662 | 266.8184 | 593.4134
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.5398 | 8.6623 | 1.2902 | 4 | 10481.6728 | 22413.2388 | 213.6831 | 456.9242 | 189.5506 | 24.8777 | 60.4948 | 3974652.9091 | 0 | 1548063.0409 | 0 | 0 | 0 | 2330533.3813 | 3062767.2392 | 7968692.0965 | 5438796.0961 | 24323504.7631 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 54095287.026 | 115673386.4458 | 1333.5214 | 5.1609 | 10481.6728 | 22413.2388 | 213.6831 | 456.9242
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5387 | 11.2101 | 1.7074 | 4 | 8548.2279 | 17564.423 | 174.2672 | 358.0745 | 191.3961 | 24.8305 | 86.3191 | 4720052.7523 | 0 | 1863086.1105 | 0 | 0 | 0 | 2654151.668 | 3602543.307 | 9373078.7016 | 6397318.8113 | 28610231.3506 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 58382013.6135 | 119960113.0333 | 1778.2794 | 6.8297 | 8548.2279 | 17564.423 | 174.2672 | 358.0745
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.3009 | 14.2831 | 2.2238 | 4 | 7092.5448 | 14015.0764 | 144.5911 | 285.7163 | 192.7088 | 24.7164 | 76.3751 | 5549109.1241 | 0 | 2223197.3919 | 0 | 0 | 0 | 2985171.9569 | 4195416.6044 | 10915613.4064 | 7450130.4433 | 33318638.927 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 63090421.1899 | 124668520.6098 | 2371.3737 | 8.8953 | 7092.5448 | 14015.0764 | 144.5911 | 285.7163
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.7829 | 17.8791 | 2.8436 | 4 | 5986.3175 | 11400.115 | 122.0392 | 232.4068 | 193.5341 | 24.5204 | 94.511 | 6443534.8193 | 0 | 2623400.5573 | 0 | 0 | 0 | 3304775.0013 | 4824967.0474 | 12553574.5205 | 8568072.5604 | 38318324.5063 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 68090106.7692 | 129668206.189 | 3162.2777 | 11.3743 | 5986.3175 | 11400.115 | 122.0392 | 232.4068
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5808 | 21.8938 | 3.5544 | 4 | 5142.4659 | 9473.5287 | 104.8361 | 193.1307 | 193.89 | 24.2323 | 95.0066 | 7362892.4731 | 0 | 3048720.56 | 0 | 0 | 0 | 3582290.2856 | 5457622.2943 | 14199613.6975 | 9691528.1214 | 43342667.4318 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 73114449.6947 | 134692549.1146 | 4216.965 | 14.2178 | 5142.4659 | 9473.5287 | 104.8361 | 193.1307
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9756 | 26.1267 | 4.3251 | 4 | 4499.2241 | 8058.5706 | 91.7228 | 164.2849 | 193.8118 | 23.8556 | 98.7784 | 8254443.0641 | 0 | 3477137.0861 | 0 | 0 | 0 | 3787513.6899 | 6052446.5976 | 15747224.5195 | 10747804.3077 | 48066569.2648 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 77838351.5277 | 139416450.9475 | 5623.4133 | 17.3004 | 4499.2241 | 8058.5706 | 91.7228 | 164.2849
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.1017 | 30.3255 | 5.1102 | 4 | 4010.5704 | 7023.0717 | 81.7609 | 143.1748 | 193.3786 | 23.412 | 110.1489 | 9068164.7541 | 0 | 3885059.4775 | 0 | 0 | 0 | 3902903.0712 | 6573889.6481 | 17103912.3741 | 11673771.6456 | 52207700.9704 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 81979483.2333 | 143557582.6531 | 7498.9421 | 20.4409 | 4010.5704 | 7023.0717 | 81.7609 | 143.1748
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.1413 | 34.2434 | 5.8614 | 4 | 3640.9441 | 6267.3902 | 74.2256 | 127.7692 | 192.7081 | 22.938 | 133.3369 | 9768278.7195 | 0 | 4252283.6835 | 0 | 0 | 0 | 3928124.7701 | 6999987.9975 | 18212532.8746 | 12430427.917 | 55591635.9623 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 85363418.2252 | 146941517.645 | 10000 | 23.4454 | 3640.9441 | 6267.3902 | 74.2256 | 127.7692
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5445 | 37.7057 | 6.5402 | 4 | 3362.4292 | 5716.2705 | 68.5477 | 116.5339 | 191.927 | 22.4726 | 123.4875 | 10341333.1438 | 0 | 4567021.6167 | 0 | 0 | 0 | 3879794.9017 | 7327378.3682 | 19064335.4622 | 13011800.6859 | 58191664.1785 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 87963446.4414 | 149541545.8612 | 13335.2143 | 26.1607 | 3362.4292 | 5716.2705 | 68.5477 | 116.5339
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.0796 | 40.6297 | 7.1249 | 4 | 3153.0865 | 5313.7594 | 64.2799 | 108.3282 | 191.1394 | 22.0461 | 110.7239 | 10792408.5449 | 0 | 4826079.0312 | 0 | 0 | 0 | 3782445.3523 | 7566363.8421 | 19686126.6424 | 13436185.9429 | 60089609.3557 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 89861391.6186 | 151439491.0385 | 17782.7941 | 28.4995 | 3153.0865 | 5313.7594 | 64.2799 | 108.3282
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7944 | 43.016 | 7.61 | 4 | 2996.0772 | 5019.009 | 61.0791 | 102.3193 | 190.415 | 21.6769 | 117.2125 | 11138607.3667 | 0 | 5033155.914 | 0 | 0 | 0 | 3661578.0983 | 7735003.1378 | 20124891.4973 | 13735651.9721 | 61428887.9861 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 91200670.249 | 152778769.6689 | 23713.7371 | 30.44 | 2996.0772 | 5019.009 | 61.0791 | 102.3193
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.889 | 44.9154 | 8.0014 | 4 | 2878.3548 | 4802.3259 | 58.6792 | 97.9019 | 189.787 | 21.3693 | 131.6744 | 11399992.7348 | 0 | 5195249.1734 | 0 | 0 | 0 | 3536162.8661 | 7851247.862 | 20427336.4244 | 13942076.8495 | 62352065.9101 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 92123848.173 | 153701947.5929 | 31622.7766 | 32.0057 | 2878.3548 | 4802.3259 | 58.6792 | 97.9019
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6297 | 46.402 | 8.311 | 4 | 2790.1004 | 4642.4076 | 56.88 | 94.6418 | 189.2642 | 21.1202 | 112.3282 | 11595785.2964 | 0 | 5320460.8165 | 0 | 0 | 0 | 3418645.5898 | 7930607.764 | 20633814.6107 | 14083002.4543 | 62982316.5317 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 92754098.7946 | 154332198.2144 | 42169.6503 | 33.244 | 2790.1004 | 4642.4076 | 56.88 | 94.6418
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2696 | 47.5494 | 8.5521 | 4 | 2723.9311 | 4524.0205 | 55.531 | 92.2283 | 188.8419 | 20.9231 | 116.0169 | 11741570.0804 | 0 | 5416099.8525 | 0 | 0 | 0 | 3315120.622 | 7984388.3164 | 20773740.576 | 14178504.8008 | 63409424.2482 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93181206.5111 | 154759305.9309 | 56234.1325 | 34.2084 | 2723.9311 | 4524.0205 | 55.531 | 92.2283
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.0487 | 48.4288 | 8.738 | 4 | 2674.3129 | 4436.0954 | 54.5195 | 90.4358 | 188.5072 | 20.7691 | 116.2648 | 11850182.3782 | 0 | 5488838.0378 | 0 | 0 | 0 | 3227981.7554 | 8021130.8468 | 20869337.1033 | 14243751.395 | 63701221.5165 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93473003.7794 | 155051103.1992 | 74989.4209 | 34.9522 | 2674.3129 | 4436.0954 | 54.5195 | 90.4358
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.1487 | 49.0959 | 8.8801 | 4 | 2637.1012 | 4370.7012 | 53.7609 | 89.1027 | 188.2471 | 20.6507 | 114.636 | 11930683.2236 | 0 | 5543642.2865 | 0 | 0 | 0 | 3156535.873 | 8046035.9394 | 20934135.0455 | 14287977.322 | 63899009.69 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93670791.9529 | 155248891.3727 | 100000 | 35.5204 | 2637.1012 | 4370.7012 | 53.7609 | 89.1027
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.7345 | 49.6009 | 8.9881 | 4 | 2609.192 | 4321.9504 | 53.1919 | 88.1088 | 188.0466 | 20.5602 | 114.5722 | 11990569.6956 | 0 | 5584938.6659 | 0 | 0 | 0 | 3099396.7738 | 8063213.0027 | 20978826.2407 | 14318479.981 | 64035424.3596 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93807206.6225 | 155385306.0423 | 133352.1432 | 35.9526 | 2609.192 | 4321.9504 | 53.1919 | 88.1088
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.9332 | 49.9833 | 9.0701 | 4 | 2588.2591 | 4285.5359 | 52.7652 | 87.3664 | 187.8926 | 20.4911 | 118.1759 | 12035317.7747 | 0 | 5616103.7556 | 0 | 0 | 0 | 3054543.4184 | 8075326.33 | 21010342.6334 | 14339990.5667 | 64131624.4788 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93903406.7417 | 155481506.1615 | 177827.941 | 36.2805 | 2588.2591 | 4285.5359 | 52.7652 | 87.3664
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.8493 | 50.2754 | 9.1325 | 4 | 2572.5586 | 4258.2506 | 52.4451 | 86.8102 | 187.7736 | 20.4379 | 115.3618 | 12069214.9983 | 0 | 5639891.6378 | 0 | 0 | 0 | 3020043.6346 | 8084368.6056 | 21033868.7797 | 14356047.6449 | 64203435.3008 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 93975217.5637 | 155553316.9835 | 237137.3706 | 36.5299 | 2572.5586 | 4258.2506 | 52.4451 | 86.8102
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.5339 | 50.4941 | 9.1794 | 4 | 2560.783 | 4237.862 | 52.205 | 86.3945 | 187.6839 | 20.3979 | 106.8457 | 12094371.3083 | 0 | 5657651.1556 | 0 | 0 | 0 | 2993352.3829 | 8090696.1903 | 21050331.8571 | 14367284.0335 | 64253686.9278 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94025469.1907 | 155603568.6105 | 316227.766 | 36.7175 | 2560.783 | 4237.862 | 52.205 | 86.3945
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0324 | 50.6542 | 9.2143 | 4 | 2551.9511 | 4222.6782 | 52.025 | 86.085 | 187.618 | 20.3686 | 125.4096 | 12112592.7628 | 0 | 5670575.2478 | 0 | 0 | 0 | 2972527.2263 | 8094721.1424 | 21060803.957 | 14374431.4569 | 64285651.7932 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94057434.0561 | 155635533.4759 | 421696.5034 | 36.8571 | 2551.9511 | 4222.6782 | 52.025 | 86.085
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4151 | 50.7768 | 9.2407 | 4 | 2545.3274 | 4211.2674 | 51.8899 | 85.8524 | 187.5672 | 20.3461 | 121.0915 | 12126528.3064 | 0 | 5680490.6863 | 0 | 0 | 0 | 2956890.5493 | 8097924.7214 | 21069139.0122 | 14380120.3034 | 64311093.579 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94082875.8419 | 155660975.2617 | 562341.3252 | 36.963 | 2545.3274 | 4211.2674 | 51.8899 | 85.8524
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.7124 | 50.8716 | 9.2609 | 4 | 2540.3598 | 4202.6713 | 51.7887 | 85.6771 | 187.5277 | 20.3286 | 117.3229 | 12137325.3612 | 0 | 5688190.8204 | 0 | 0 | 0 | 2945284.9953 | 8100612.459 | 21076131.9541 | 14384893.1299 | 64332438.7199 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94104220.9828 | 155682320.4026 | 749894.2093 | 37.0437 | 2540.3598 | 4202.6713 | 51.7887 | 85.6771
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.9339 | 50.9424 | 9.276 | 4 | 2536.6344 | 4196.2381 | 51.7127 | 85.546 | 187.4982 | 20.3155 | 130.4484 | 12145351.9503 | 0 | 5693926.8171 | 0 | 0 | 0 | 2936466.2363 | 8102540.5514 | 21081148.4553 | 14388316.995 | 64347751.0054 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94119533.2683 | 155697632.6881 | 1000000 | 37.1041 | 2536.6344 | 4196.2381 | 51.7127 | 85.546
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0802 | 50.99 | 9.2868 | 4 | 2533.8405 | 4191.5114 | 51.6558 | 85.4496 | 187.4785 | 20.3069 | 122.6744 | 12150639.6764 | 0 | 5697715.003 | 0 | 0 | 0 | 2929312.6735 | 8103290.2676 | 21083099.063 | 14389648.3248 | 64353705.0083 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94125487.2712 | 155703586.691 | 1333521.4322 | 37.1474 | 2533.8405 | 4191.5114 | 51.6558 | 85.4496
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.2117 | 51.0318 | 9.2955 | 4 | 2531.7453 | 4187.865 | 51.6131 | 85.3753 | 187.4609 | 20.2991 | 123.9744 | 12155393.2325 | 0 | 5701119.0379 | 0 | 0 | 0 | 2924468.1392 | 8104582.3598 | 21086460.8217 | 14391942.7942 | 64363966.3853 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94135748.6482 | 155713848.068 | 1778279.41 | 37.1822 | 2531.7453 | 4187.865 | 51.6131 | 85.3753
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.2971 | 51.0594 | 9.3017 | 4 | 2530.1741 | 4185.1945 | 51.581 | 85.3209 | 187.4495 | 20.294 | 126.0848 | 12158472.7725 | 0 | 5703328.7631 | 0 | 0 | 0 | 2920490.2149 | 8105093.7827 | 21087791.4393 | 14392850.9681 | 64368027.9406 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94139810.2035 | 155717909.6234 | 2371373.7057 | 37.2069 | 2530.1741 | 4185.1945 | 51.581 | 85.3209
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.3749 | 51.0839 | 9.3067 | 4 | 2528.9958 | 4183.1272 | 51.557 | 85.2787 | 187.4391 | 20.2894 | 132.4624 | 12161281.0648 | 0 | 5705341.9834 | 0 | 0 | 0 | 2917842.4993 | 8105941.5635 | 21089997.1911 | 14394356.439 | 64374760.7411 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94146543.004 | 155724642.4238 | 3162277.6602 | 37.2268 | 2528.9958 | 4183.1272 | 51.557 | 85.2787
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.424 | 51.0998 | 9.3102 | 4 | 2528.1122 | 4181.6211 | 51.539 | 85.248 | 187.4325 | 20.2865 | 126.2833 | 12163049.5391 | 0 | 5706612.1382 | 0 | 0 | 0 | 2915621.7558 | 8106260.5389 | 21090827.0996 | 14394922.8686 | 64377293.9403 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94149076.2032 | 155727175.623 | 4216965.0343 | 37.2409 | 2528.1122 | 4181.6211 | 51.539 | 85.248
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4675 | 51.1135 | 9.313 | 4 | 2527.4495 | 4180.4601 | 51.5255 | 85.2243 | 187.4266 | 20.2839 | 132.2161 | 12164619.2608 | 0 | 5707738.4427 | 0 | 0 | 0 | 2914121.1683 | 8106726.76 | 21092040.1112 | 14395750.774 | 64380996.5171 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94152778.78 | 155730878.1998 | 5623413.2519 | 37.2521 | 2527.4495 | 4180.4601 | 51.5255 | 85.2243
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4823 | 51.1189 | 9.3147 | 4 | 2526.9526 | 4179.674 | 51.5153 | 85.2083 | 187.4246 | 20.2831 | 120.5691 | 12165148.7836 | 0 | 5708121.8529 | 0 | 0 | 0 | 2912550.979 | 8106470.43 | 21091373.1932 | 14395295.5888 | 64378960.8275 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94150743.0904 | 155728842.5103 | 7498942.0933 | 37.2586 | 2526.9526 | 4179.674 | 51.5153 | 85.2083
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5166 | 51.1293 | 9.3165 | 4 | 2526.58 | 4178.9749 | 51.5078 | 85.1941 | 187.42 | 20.281 | 123.3853 | 12166386.5206 | 0 | 5709008.4641 | 0 | 0 | 0 | 2911948.7079 | 8107064.0401 | 21092917.645 | 14396349.7088 | 64383675.0866 | 961560.8286 | 28810221.4343 | 28810221.4343 | 21508759.7178 | 11259118.2678 | 0 | 94155457.3495 | 155733556.7693 | 10000000 | 37.266 | 2526.58 | 4178.9749 | 51.5078 | 85.1941
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.164 | 0.2449 | 0.024658 | 4 | 347510.3586 | 985158.0079 | 7084.4687 | 20083.7785 | 127.4389 | 22.9885 | 40.2687 | 528087.8816 | 0 | 228726.9684 | 0 | 0 | 0 | 491692.2294 | 486917.7609 | 1266860.1334 | 864658.0724 | 3866943.0461 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 34275608.3555 | 97168010.126 | 100 | 0.098632 | 347510.3586 | 985158.0079 | 7084.4687 | 20083.7785
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3944 | 0.49422 | 0.056145 | 4 | 158306.7379 | 438350.7494 | 3227.297 | 8936.3729 | 142.2349 | 23.7027 | 51.2871 | 731241.5905 | 0 | 297473.4622 | 0 | 0 | 0 | 632088.0572 | 647713.2129 | 1685216.9157 | 1150195.1727 | 5143928.4112 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 35552593.7206 | 98444995.491 | 133.3521 | 0.22458 | 158306.7379 | 438350.7494 | 3227.297 | 8936.3729
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8823 | 0.83903 | 0.1025 | 4 | 90136.061 | 243535.0651 | 1837.5455 | 4964.7917 | 153.9612 | 24.1997 | 57.8448 | 960498.204 | 0 | 375638.1751 | 0 | 0 | 0 | 777484.6957 | 824312.2192 | 2144691.3046 | 1463795.8844 | 6546420.4829 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 36955085.7923 | 99847487.5628 | 177.8279 | 0.40999 | 90136.061 | 243535.0651 | 1837.5455 | 4964.7917
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7628 | 1.3083 | 0.16743 | 4 | 57603.3271 | 151510.8471 | 1174.3217 | 3088.7536 | 163.6353 | 24.5693 | 72.984 | 1229037.3629 | 0 | 468972.5523 | 0 | 0 | 0 | 939758.6628 | 1028729.7454 | 2676543.7762 | 1826796.1247 | 8169838.2244 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 38578503.5337 | 101470905.3042 | 237.1374 | 0.66973 | 57603.3271 | 151510.8471 | 1174.3217 | 3088.7536
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1406 | 1.9305 | 0.25596 | 4 | 39516.5996 | 100944.6623 | 805.5993 | 2057.8935 | 171.5332 | 24.8454 | 64.9409 | 1542981.1295 | 0 | 580743.7799 | 0 | 0 | 0 | 1121066.4978 | 1265468.6488 | 3292489.8408 | 2247191.9702 | 10049941.8668 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 40458607.1762 | 103351008.9466 | 316.2278 | 1.0238 | 39516.5996 | 100944.6623 | 805.5993 | 2057.8935
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1445 | 2.7414 | 0.3746 | 4 | 28454.8773 | 70428.3016 | 580.0912 | 1435.7762 | 177.921 | 25.0501 | 42.5804 | 1909633.4572 | 0 | 714706.871 | 0 | 0 | 0 | 1323586.7808 | 1539691.5725 | 4005961.6375 | 2734151.1319 | 12227731.4508 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 42636396.7602 | 105528798.5306 | 421.6965 | 1.4984 | 28454.8773 | 70428.3016 | 580.0912 | 1435.7762
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9493 | 3.7893 | 0.53181 | 4 | 21235.4577 | 50800.8052 | 432.9135 | 1035.6431 | 183.0634 | 25.1985 | 68.3649 | 2339320.2463 | 0 | 875900.0599 | 0 | 0 | 0 | 1551620.4135 | 1859067.8807 | 4836913.2783 | 3301292.7011 | 14764114.5798 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 45172779.8892 | 108065181.6596 | 562.3413 | 2.1272 | 21235.4577 | 50800.8052 | 432.9135 | 1035.6431
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7413 | 5.128 | 0.73799 | 4 | 16298.1117 | 37603.3264 | 332.2591 | 766.5947 | 187.1536 | 25.2981 | 57.0166 | 2840593.3311 | 0 | 1068957.9921 | 0 | 0 | 0 | 1806127.6569 | 2229114.8022 | 5799699.461 | 3958414.0541 | 17702907.2974 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 48111572.6067 | 111003974.3772 | 749.8942 | 2.952 | 16298.1117 | 37603.3264 | 332.2591 | 766.5947
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.7628 | 6.8276 | 1.006 | 4 | 12801.5328 | 28430.2395 | 260.9766 | 579.5889 | 190.3796 | 25.3517 | 79.5175 | 3424752.0268 | 0 | 1299879.3421 | 0 | 0 | 0 | 2090031.5225 | 2657718.5277 | 6914838.4359 | 4719519.3182 | 21106739.1733 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 51515404.4827 | 114407806.2531 | 1000 | 4.0242 | 12801.5328 | 28430.2395 | 260.9766 | 579.5889
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.2413 | 8.9571 | 1.3503 | 4 | 10258.6016 | 21902.5968 | 209.1355 | 446.5141 | 192.8745 | 25.3564 | 83.7402 | 4098315.928 | 0 | 1573161.9451 | 0 | 0 | 0 | 2400462.6766 | 3148056.8144 | 8190598.0757 | 5590251.4866 | 25000846.9264 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 55409512.2358 | 118301914.0062 | 1333.5214 | 5.4013 | 10258.6016 | 21902.5968 | 209.1355 | 446.5141
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.3935 | 11.5846 | 1.7857 | 4 | 8371.474 | 17176.3709 | 170.6638 | 350.1636 | 194.7505 | 25.3042 | 72.1528 | 4864399.5408 | 0 | 1892291.3628 | 0 | 0 | 0 | 2731665.34 | 3700458.935 | 9627835.0804 | 6571195.2746 | 29387845.5336 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 59796510.843 | 122688912.6134 | 1778.2794 | 7.1429 | 8371.474 | 17176.3709 | 170.6638 | 350.1636
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.3339 | 14.7523 | 2.3241 | 4 | 6950.3644 | 13715.6617 | 141.6926 | 279.6123 | 196.084 | 25.1823 | 84.8707 | 5716060.8836 | 0 | 2256966.6321 | 0 | 0 | 0 | 3070362.8679 | 4306922.2496 | 11205728.2223 | 7648139.7664 | 34204180.622 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 64612845.9314 | 127505247.7018 | 2371.3737 | 9.2963 | 6950.3644 | 13715.6617 | 141.6926 | 279.6123
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.9887 | 18.4499 | 2.9687 | 4 | 5870.4556 | 11166.7738 | 119.6772 | 227.6498 | 196.9179 | 24.9754 | 83.9845 | 6632366.7385 | 0 | 2661225.6187 | 0 | 0 | 0 | 3395542.5096 | 4948762.5981 | 12875665.1493 | 8787906.0329 | 39301468.6471 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 69710133.9565 | 132602535.7269 | 3162.2777 | 11.8747 | 5870.4556 | 11166.7738 | 119.6772 | 227.6498
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.925 | 22.5635 | 3.7056 | 4 | 5046.9168 | 9289.9249 | 102.8882 | 189.3877 | 197.272 | 24.6738 | 98.2926 | 7570604.6997 | 0 | 3089339.2635 | 0 | 0 | 0 | 3675256.9127 | 5590728.3416 | 14545928.3287 | 9927894.9733 | 44399752.5195 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 74808417.8288 | 137700819.5993 | 4216.965 | 14.8226 | 5046.9168 | 9289.9249 | 102.8882 | 189.3877
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.4151 | 26.8865 | 4.5018 | 4 | 4419.4433 | 7912.0678 | 90.0963 | 161.2982 | 197.1853 | 24.2817 | 93.7449 | 8477342.3225 | 0 | 3519235.0546 | 0 | 0 | 0 | 3879794.6765 | 6191785.1009 | 16109754.7228 | 10995238.6206 | 49173150.4979 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 79581815.8073 | 142474217.5777 | 5623.4133 | 18.0072 | 4419.4433 | 7912.0678 | 90.0963 | 161.2982
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.5903 | 31.1617 | 5.31 | 4 | 3943.0159 | 6904.0378 | 80.3837 | 140.7481 | 196.7413 | 23.8225 | 114.0319 | 9302320.0655 | 0 | 3927408.5145 | 0 | 0 | 0 | 3992429.3733 | 6716641.6018 | 17475323.6752 | 11927267.4903 | 53341390.7207 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 83750056.0301 | 146642457.8005 | 7498.9421 | 21.2401 | 3943.0159 | 6904.0378 | 80.3837 | 140.7481
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.6371 | 35.1395 | 6.0806 | 4 | 3582.8207 | 6168.5838 | 73.0406 | 125.7549 | 196.0613 | 23.3341 | 118.8488 | 10010070.607 | 0 | 4293894.1389 | 0 | 0 | 0 | 4013791.5318 | 7143924.9483 | 18587027.2949 | 12686028.054 | 56734736.5748 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 87143401.8842 | 150035803.6546 | 10000 | 24.3226 | 3582.8207 | 6168.5838 | 73.0406 | 125.7549
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.9944 | 38.6397 | 6.7743 | 4 | 3311.5323 | 5632.5229 | 67.5101 | 114.8266 | 195.2751 | 22.8576 | 117.6651 | 10586802.8 | 0 | 4606645.6033 | 0 | 0 | 0 | 3960510.0631 | 7470043.8019 | 19435521.6558 | 13265142.8901 | 59324666.8143 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 89733332.1236 | 152625733.8941 | 13335.2143 | 27.0972 | 3311.5323 | 5632.5229 | 67.5101 | 114.8266
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4756 | 41.5904 | 7.3703 | 4 | 3107.7488 | 5241.043 | 63.3557 | 106.8458 | 194.4861 | 22.4228 | 121.0185 | 11040241.964 | 0 | 4863711.7897 | 0 | 0 | 0 | 3859355.109 | 7707690.4564 | 20053829.5029 | 13687150.7007 | 61211979.5228 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 91620644.8322 | 154513046.6026 | 17782.7941 | 29.4814 | 3107.7488 | 5241.043 | 63.3557 | 106.8458
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.1218 | 43.9918 | 7.8636 | 4 | 2954.8533 | 4954.3322 | 60.2387 | 101.0008 | 193.7623 | 22.0468 | 126.0277 | 11387054.271 | 0 | 5068570.6782 | 0 | 0 | 0 | 3734669.0482 | 7874214.659 | 20487091.3191 | 13982860.7929 | 62534460.7685 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 92943126.0779 | 155835527.8483 | 23713.7371 | 31.4544 | 2954.8533 | 4954.3322 | 60.2387 | 101.0008
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1607 | 45.9023 | 8.2611 | 4 | 2840.2812 | 4743.5556 | 57.903 | 96.7038 | 193.1362 | 21.7345 | 120.3229 | 11648995.766 | 0 | 5228911.346 | 0 | 0 | 0 | 3606848.7127 | 7989054.7716 | 20785881.7354 | 14186791.3915 | 63446483.7233 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 93855149.0326 | 156747550.8031 | 31622.7766 | 33.0443 | 2840.2812 | 4743.5556 | 57.903 | 96.7038
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.8406 | 47.3926 | 8.5747 | 4 | 2754.4019 | 4588.0648 | 56.1522 | 93.5339 | 192.6172 | 21.4827 | 117.8635 | 11844540.3829 | 0 | 5352326.0318 | 0 | 0 | 0 | 3487251.3343 | 8066805.9221 | 20988174.2799 | 14324860.2099 | 64063958.1609 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 94472623.4703 | 157365025.2407 | 42169.6503 | 34.2988 | 2754.4019 | 4588.0648 | 56.1522 | 93.5339
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.446 | 48.546 | 8.8191 | 4 | 2690.0211 | 4472.8629 | 54.8397 | 91.1854 | 192.197 | 21.2828 | 128.6408 | 11990678.5293 | 0 | 5446920.2026 | 0 | 0 | 0 | 3382729.6728 | 8119928.0778 | 21126387.2322 | 14419193.3898 | 64485837.1046 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 94894502.4139 | 157786904.1844 | 56234.1325 | 35.2765 | 2690.0211 | 4472.8629 | 54.8397 | 91.1854
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.1741 | 49.4232 | 9.0069 | 4 | 2641.7486 | 4387.4254 | 53.8556 | 89.4436 | 191.8669 | 21.1281 | 111.764 | 12098603.5391 | 0 | 5518224.5591 | 0 | 0 | 0 | 3294270.8785 | 8155328.6009 | 21218492.1317 | 14482056.8763 | 64766976.5856 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95175641.895 | 158068043.6654 | 74989.4209 | 36.0275 | 2641.7486 | 4387.4254 | 53.8556 | 89.4436
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.2593 | 50.0952 | 9.1509 | 4 | 2605.549 | 4323.7484 | 53.1176 | 88.1455 | 191.6077 | 21.0079 | 121.3902 | 12179541.25 | 0 | 5572570.4355 | 0 | 0 | 0 | 3222595.1865 | 8180135.6801 | 21283035.063 | 14526108.7531 | 64963986.3682 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95372651.6776 | 158265053.448 | 100000 | 36.6037 | 2605.549 | 4323.7484 | 53.1176 | 88.1455
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8406 | 50.6058 | 9.2606 | 4 | 2578.4005 | 4276.2425 | 52.5642 | 87.177 | 191.407 | 20.9156 | 119.8444 | 12240015.8566 | 0 | 5613697.5775 | 0 | 0 | 0 | 3165511.3155 | 8197497.6523 | 21328207.3534 | 14556939.7695 | 65101869.5249 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95510534.8343 | 158402936.6047 | 133352.1432 | 37.0426 | 2578.4005 | 4276.2425 | 52.5642 | 87.177
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.0197 | 50.9878 | 9.3434 | 4 | 2558.0392 | 4240.838 | 52.1491 | 86.4552 | 191.2549 | 20.846 | 109.492 | 12284588.4243 | 0 | 5644313.6593 | 0 | 0 | 0 | 3120293.3579 | 8209186.2222 | 21358618.6144 | 14577696.0801 | 65194696.3581 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95603361.6675 | 158495763.438 | 177827.941 | 37.3737 | 2558.0392 | 4240.838 | 52.1491 | 86.4552
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.9157 | 51.2782 | 9.4062 | 4 | 2542.7681 | 4214.3333 | 51.8378 | 85.9149 | 191.1381 | 20.7928 | 123.61 | 12318165.1366 | 0 | 5667550.731 | 0 | 0 | 0 | 3085408.3526 | 8217738.4459 | 21380869.7464 | 14592882.9348 | 65262615.3475 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95671280.6569 | 158563682.4273 | 237137.3706 | 37.6249 | 2542.7681 | 4214.3333 | 51.8378 | 85.9149
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5855 | 51.4957 | 9.4535 | 4 | 2531.3147 | 4194.5256 | 51.6043 | 85.5111 | 191.0499 | 20.7528 | 127.0534 | 12343094.7509 | 0 | 5684904.7893 | 0 | 0 | 0 | 3058449.5822 | 8223715.1577 | 21396419.9244 | 14603496.2509 | 65310080.4554 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95718745.7647 | 158611147.5352 | 316227.766 | 37.8138 | 2531.3147 | 4194.5256 | 51.6043 | 85.5111
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0802 | 51.6568 | 9.4888 | 4 | 2522.7249 | 4179.7398 | 51.4292 | 85.2096 | 190.9844 | 20.7232 | 123.347 | 12361414.2101 | 0 | 5697715.003 | 0 | 0 | 0 | 3037615.4774 | 8227730.4293 | 21406866.8374 | 14610626.4837 | 65341968.4408 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95750633.7502 | 158643035.5206 | 421696.5034 | 37.9552 | 2522.7249 | 4179.7398 | 51.4292 | 85.2096
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4675 | 51.7823 | 9.5158 | 4 | 2516.2827 | 4168.5921 | 51.2978 | 84.9824 | 190.9329 | 20.6999 | 131.6693 | 12375705.356 | 0 | 5707738.4427 | 0 | 0 | 0 | 3022170.8745 | 8231189.7226 | 21415867.2089 | 14616769.4221 | 65369441.0268 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95778106.3362 | 158670508.1067 | 562341.3252 | 38.0633 | 2516.2827 | 4168.5921 | 51.2978 | 84.9824
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.7381 | 51.871 | 9.5356 | 4 | 2511.4514 | 4160.3364 | 51.1993 | 84.8141 | 190.8966 | 20.6836 | 126.4035 | 12385655.9998 | 0 | 5714739.228 | 0 | 0 | 0 | 3009943.6383 | 8233032.1577 | 21420660.8473 | 14620041.1789 | 65384073.0499 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95792738.3593 | 158685140.1297 | 749894.2093 | 38.1424 | 2511.4514 | 4160.3364 | 51.1993 | 84.8141
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.9692 | 51.9454 | 9.5512 | 4 | 2507.8282 | 4154.018 | 51.1255 | 84.6853 | 190.8658 | 20.6697 | 114.621 | 12394147.0674 | 0 | 5720718.3726 | 0 | 0 | 0 | 3001418.2994 | 8235350.6583 | 21426693.1103 | 14624158.3223 | 65402485.8303 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95811151.1397 | 158703552.9101 | 1000000 | 38.2048 | 2507.8282 | 4154.018 | 51.1255 | 84.6853
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.113 | 51.9929 | 9.5621 | 4 | 2505.111 | 4149.4222 | 51.0701 | 84.5916 | 190.8464 | 20.661 | 120.7845 | 12399408.995 | 0 | 5724434.8409 | 0 | 0 | 0 | 2994226.2016 | 8236047.3146 | 21428505.6671 | 14625395.4295 | 65408018.4488 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95816683.7582 | 158709085.5286 | 1333521.4322 | 38.2485 | 2505.111 | 4149.4222 | 51.0701 | 84.5916
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.2445 | 52.0352 | 9.571 | 4 | 2503.0733 | 4145.8664 | 51.0285 | 84.5191 | 190.8288 | 20.653 | 122.8916 | 12404225.8057 | 0 | 5727834.8981 | 0 | 0 | 0 | 2989411.3702 | 8237374.1089 | 21431957.7135 | 14627751.5222 | 65418555.4187 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95827220.728 | 158719622.4985 | 1778279.41 | 38.2838 | 2503.0733 | 4145.8664 | 51.0285 | 84.5191
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.3371 | 52.0653 | 9.5774 | 4 | 2501.5452 | 4143.2291 | 50.9974 | 84.4653 | 190.8164 | 20.6474 | 120.6696 | 12407612.8966 | 0 | 5730229.0019 | 0 | 0 | 0 | 2985633.9033 | 8238155.5627 | 21433990.8961 | 14629139.211 | 65424761.4715 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95833426.7809 | 158725828.5514 | 2371373.7057 | 38.3097 | 2501.5452 | 4143.2291 | 50.9974 | 84.4653
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.3908 | 52.0834 | 9.5818 | 4 | 2500.3993 | 4141.3254 | 50.974 | 84.4265 | 190.809 | 20.6441 | 115.3864 | 12409571.4702 | 0 | 5731617.4675 | 0 | 0 | 0 | 2982394.8784 | 8238197.6883 | 21434100.4982 | 14629214.0167 | 65425096.0192 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95833761.3286 | 158726163.099 | 3162277.6602 | 38.3274 | 2500.3993 | 4141.3254 | 50.974 | 84.4265
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.4419 | 52.1 | 9.5855 | 4 | 2499.54 | 4139.8475 | 50.9565 | 84.3964 | 190.8022 | 20.6411 | 124.6532 | 12411438.4443 | 0 | 5732938.5976 | 0 | 0 | 0 | 2980235.9684 | 8238599.074 | 21435144.8215 | 14629926.7889 | 65428283.6947 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95836949.0041 | 158729350.7746 | 4216965.0343 | 38.3418 | 2499.54 | 4139.8475 | 50.9565 | 84.3964
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.4808 | 52.1126 | 9.5882 | 4 | 2498.8955 | 4138.7368 | 50.9434 | 84.3737 | 190.7969 | 20.6387 | 126.6982 | 12412858.8157 | 0 | 5733943.9278 | 0 | 0 | 0 | 2978628.849 | 8238918.3211 | 21435975.4369 | 14630493.7009 | 65430819.0513 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95839484.3607 | 158731886.1312 | 5623413.2519 | 38.3527 | 2498.8955 | 4138.7368 | 50.9434 | 84.3737
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.5151 | 52.1235 | 9.5904 | 4 | 2498.4123 | 4137.8802 | 50.9335 | 84.3563 | 190.7923 | 20.6366 | 120.1014 | 12414111.2092 | 0 | 5734829.5393 | 0 | 0 | 0 | 2977551.0845 | 8239331.8149 | 21437051.2629 | 14631227.9743 | 65434102.8851 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95842768.1944 | 158735169.9649 | 7498942.0933 | 38.3615 | 2498.4123 | 4137.8802 | 50.9335 | 84.3563
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.5345 | 52.13 | 9.5918 | 4 | 2498.0499 | 4137.2671 | 50.9261 | 84.3438 | 190.7897 | 20.6354 | 121.7249 | 12414820.2703 | 0 | 5735332.1685 | 0 | 0 | 0 | 2976584.1577 | 8239427.2726 | 21437299.6245 | 14631397.4861 | 65434860.9797 | 961560.8286 | 29447104.4808 | 29447104.4808 | 21958398.9644 | 11486898.3253 | 0 | 95843526.2891 | 158735928.0595 | 10000000 | 38.3673 | 2498.0499 | 4137.2671 | 50.9261 | 84.3438
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2345 | 0.25428 | 0.02612 | 4 | 335308.0416 | 949972.6035 | 6835.708 | 19366.4765 | 129.5436 | 23.4446 | 52.6141 | 545409.2234 | 0 | 232798.6477 | 0 | 0 | 0 | 507366.9801 | 501374.192 | 1304472.8015 | 890329.4913 | 3981751.3359 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 35033159.7826 | 99253635.1172 | 100 | 0.10448 | 335308.0416 | 949972.6035 | 6835.708 | 19366.4765
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4844 | 0.51122 | 0.059196 | 4 | 153468.9016 | 424689.5474 | 3128.6711 | 8657.8709 | 144.5601 | 24.1651 | 66.1146 | 753978.8398 | 0 | 302338.0012 | 0 | 0 | 0 | 650821.2186 | 665783.8432 | 1732232.9891 | 1182284.6089 | 5287439.5008 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 36338847.9475 | 100559323.2821 | 133.3521 | 0.23678 | 153468.9016 | 424689.5474 | 3128.6711 | 8657.8709
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0138 | 0.86955 | 0.10781 | 4 | 87637.0202 | 236553.0064 | 1786.5992 | 4822.453 | 156.5975 | 24.6721 | 60.646 | 992023.8841 | 0 | 382341.585 | 0 | 0 | 0 | 802506.658 | 848980.1296 | 2208872.1473 | 1507600.6283 | 6742325.0323 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 37793733.479 | 102014208.8136 | 177.8279 | 0.43125 | 87637.0202 | 236553.0064 | 1786.5992 | 4822.453
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9286 | 1.354 | 0.1758 | 4 | 56111.69 | 147438.8213 | 1143.9127 | 3005.7398 | 166.4256 | 25.0452 | 66.1132 | 1268175.3825 | 0 | 476967.3759 | 0 | 0 | 0 | 968830.3191 | 1058449.5002 | 2753868.4817 | 1879571.8251 | 8405862.8846 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 39457271.3313 | 103677746.6659 | 237.1374 | 0.70319 | 56111.69 | 147438.8213 | 1143.9127 | 3005.7398
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3575 | 1.998 | 0.26846 | 4 | 38545.1859 | 98348.8734 | 785.7958 | 2004.9748 | 174.478 | 25.3246 | 68.1774 | 1592074.5482 | 0 | 590659.2746 | 0 | 0 | 0 | 1155876.7101 | 1302058.1078 | 3387688.1077 | 2312166.7435 | 10340523.4919 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 41391931.9386 | 105612407.2732 | 316.2278 | 1.0739 | 38545.1859 | 98348.8734 | 785.7958 | 2004.9748
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4197 | 2.8358 | 0.39255 | 4 | 27784.1856 | 68683.5255 | 566.4182 | 1400.2066 | 180.9777 | 25.5313 | 52.5948 | 1969601.521 | 0 | 726653.9961 | 0 | 0 | 0 | 1363969.0515 | 1583487.5817 | 4119909.8697 | 2811923.1418 | 12575545.1618 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 43626953.6086 | 107847428.9431 | 421.6965 | 1.5702 | 27784.1856 | 68683.5255 | 566.4182 | 1400.2066
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.2977 | 3.9182 | 0.55692 | 4 | 20752.4911 | 49581.1214 | 423.0676 | 1010.7782 | 186.2115 | 25.6808 | 72.9114 | 2411998.5861 | 0 | 890273.8435 | 0 | 0 | 0 | 1598246.4469 | 1911202.3618 | 4972556.5039 | 3393871.9897 | 15178149.7319 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 46229558.1786 | 110450033.5132 | 562.3413 | 2.2277 | 20752.4911 | 49581.1214 | 423.0676 | 1010.7782
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2017 | 5.3059 | 0.77265 | 4 | 15939.0009 | 36718.3784 | 324.9381 | 748.5538 | 190.3894 | 25.7807 | 60.1667 | 2930175.3064 | 0 | 1087031.1019 | 0 | 0 | 0 | 1862022.1212 | 2292899.1265 | 5965653.1889 | 4071680.8833 | 18209461.7283 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 49260870.175 | 113481345.5096 | 749.8942 | 3.0906 | 15939.0009 | 36718.3784 | 324.9381 | 748.5538
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.3307 | 7.0596 | 1.0526 | 4 | 12527.6247 | 27780.3458 | 255.3926 | 566.3399 | 193.6661 | 25.8329 | 71.1326 | 3530765.0086 | 0 | 1321106.9413 | 0 | 0 | 0 | 2152800.2342 | 2731822.1518 | 7107640.8651 | 4851110.9379 | 21695246.1388 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 52746654.5856 | 116967129.9201 | 1000 | 4.2104 | 12527.6247 | 27780.3458 | 255.3926 | 566.3399
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9406 | 9.2564 | 1.412 | 4 | 10045.2536 | 21416.0503 | 204.7861 | 436.5952 | 196.202 | 25.8347 | 75.9342 | 4223202.4033 | 0 | 1598088.971 | 0 | 0 | 0 | 2470766.8391 | 3233902.7032 | 8413951.4692 | 5742694.7671 | 25682607.153 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 56734015.5997 | 120954490.9343 | 1333.5214 | 5.6478 | 10045.2536 | 21416.0503 | 204.7861 | 436.5952
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.2413 | 11.9636 | 1.8659 | 4 | 8202.3347 | 16806.816 | 167.2157 | 342.6297 | 198.1076 | 25.7774 | 85.7467 | 5009771.3474 | 0 | 1921144.5842 | 0 | 0 | 0 | 2809197.682 | 3798644.3093 | 9883293.2837 | 6745550.7475 | 30167601.9541 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 61219010.4009 | 125439485.7354 | 1778.2794 | 7.4636 | 8202.3347 | 16806.816 | 167.2157 | 342.6297
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.3692 | 15.2299 | 2.4269 | 4 | 6814.2472 | 13429.759 | 138.9176 | 273.7838 | 199.4631 | 25.6474 | 68.0279 | 5885001.4608 | 0 | 2290688.9418 | 0 | 0 | 0 | 3156382.1423 | 4419508.2925 | 11498654.0113 | 7848067.6364 | 35098302.4852 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 66149710.9319 | 130370186.2665 | 2371.3737 | 9.7076 | 6814.2472 | 13429.759 | 138.9176 | 273.7838
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1802 | 19.0263 | 3.0965 | 4 | 5759.4912 | 10944.474 | 117.415 | 223.1179 | 200.3047 | 25.4295 | 88.426 | 6822146.0317 | 0 | 2698470.8164 | 0 | 0 | 0 | 3486018.2773 | 5072587.6989 | 13197832.6617 | 9007791.98 | 40284847.466 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 71336255.9127 | 135556731.2473 | 3162.2777 | 12.3859 | 5759.4912 | 10944.474 | 117.415 | 223.1179
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.2675 | 23.2433 | 3.8602 | 4 | 4955.3718 | 9114.4962 | 101.022 | 185.8113 | 200.6571 | 25.1136 | 108.9461 | 7780218.7199 | 0 | 3129771.605 | 0 | 0 | 0 | 3768760.9156 | 5724712.9838 | 14894528.8837 | 10165822.0151 | 45463815.1232 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 76515223.5699 | 140735698.9045 | 4216.965 | 15.4409 | 4955.3718 | 9114.4962 | 101.022 | 185.8113
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8519 | 27.6572 | 4.6821 | 4 | 4342.9722 | 7771.9864 | 88.5374 | 158.4425 | 200.5618 | 24.7058 | 97.4401 | 8702073.7383 | 0 | 3561129.346 | 0 | 0 | 0 | 3972528.7366 | 6331935.4101 | 16474397.0786 | 11244114.5212 | 50286178.8308 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 81337587.2775 | 145558062.6121 | 5623.4133 | 18.7286 | 4342.9722 | 7771.9864 | 88.5374 | 158.4425
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0714 | 32.0079 | 5.5135 | 4 | 3878.2298 | 6790.1917 | 79.063 | 138.4272 | 200.1071 | 24.2309 | 95.9779 | 9537950.8317 | 0 | 3969428.7683 | 0 | 0 | 0 | 4082125.9179 | 6859907.152 | 17848071.249 | 12181675.3686 | 54479159.2875 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 85530567.7342 | 149751043.0688 | 7498.9421 | 22.054 | 3878.2298 | 6790.1917 | 79.063 | 138.4272
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.1038 | 36.0399 | 6.3031 | 4 | 3527.0443 | 6074.24 | 71.9036 | 123.8316 | 199.4189 | 23.7288 | 134.5067 | 10252091.9939 | 0 | 4334597.2168 | 0 | 0 | 0 | 4098649.3472 | 7287282.0376 | 18960013.0347 | 12940598.4855 | 57873232.1156 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 88924640.5623 | 153145115.8969 | 10000 | 25.2122 | 3527.0443 | 6074.24 | 71.9036 | 123.8316
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4144 | 39.5774 | 7.0115 | 4 | 3262.6569 | 5552.4915 | 66.5137 | 113.195 | 198.6283 | 23.2412 | 124.2736 | 10832387.0739 | 0 | 4645372.4913 | 0 | 0 | 0 | 4040417.5727 | 7612089.0838 | 19805094.3418 | 13517383.8423 | 60452744.4057 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 91504152.8524 | 155724628.187 | 13335.2143 | 28.0459 | 3262.6569 | 5552.4915 | 66.5137 | 113.195
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.8419 | 42.555 | 7.6188 | 4 | 3064.1264 | 5171.4314 | 62.4664 | 105.4266 | 197.8376 | 22.7976 | 121.2374 | 11288024.7926 | 0 | 4900475.284 | 0 | 0 | 0 | 3935249.9928 | 7848262.5271 | 20419569.1954 | 13936775.5561 | 62328357.348 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 93379765.7947 | 157600241.1293 | 17782.7941 | 30.4752 | 3064.1264 | 5171.4314 | 62.4664 | 105.4266
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.4324 | 44.9743 | 8.1204 | 4 | 2915.2101 | 4892.3489 | 59.4305 | 99.7372 | 197.1142 | 22.4149 | 116.8845 | 11636033.6712 | 0 | 5103475.4213 | 0 | 0 | 0 | 3807419.1205 | 8013302.0031 | 20848968.0577 | 14229849.1029 | 63639047.3767 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 94690455.8234 | 158910931.158 | 23713.7371 | 32.4815 | 2915.2101 | 4892.3489 | 59.4305 | 99.7372
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4176 | 46.896 | 8.5239 | 4 | 2803.6433 | 4687.1901 | 57.1561 | 95.5547 | 196.4901 | 22.0978 | 118.0747 | 11898529.6202 | 0 | 5262128.1473 | 0 | 0 | 0 | 3677229.626 | 8126776.0835 | 21144204.3382 | 14431353.9308 | 64540221.746 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 95591630.1927 | 159812105.5273 | 31622.7766 | 34.0955 | 2803.6433 | 4687.1901 | 57.1561 | 95.5547
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0392 | 48.3902 | 8.8415 | 4 | 2720.0293 | 4535.9084 | 55.4515 | 92.4706 | 195.9748 | 21.8432 | 110.6488 | 12093840.4059 | 0 | 5383818.5771 | 0 | 0 | 0 | 3555584.3888 | 8202964.915 | 21342432.0494 | 14566648.4168 | 65145288.7529 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 96196697.1997 | 160417172.5343 | 42169.6503 | 35.3661 | 2720.0293 | 4535.9084 | 55.4515 | 92.4706
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6077 | 49.5488 | 9.0892 | 4 | 2657.354 | 4423.7582 | 54.1738 | 90.1843 | 195.557 | 21.6408 | 117.9839 | 12240179.6211 | 0 | 5477311.7901 | 0 | 0 | 0 | 3449967.4241 | 8255308.9458 | 21478620.4801 | 14659599.8192 | 65560988.0804 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 96612396.5271 | 160832871.8617 | 56234.1325 | 36.3566 | 2657.354 | 4423.7582 | 54.1738 | 90.1843
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2996 | 50.4276 | 9.2791 | 4 | 2610.3647 | 4340.6172 | 53.2158 | 88.4894 | 195.2299 | 21.4847 | 118.312 | 12347947.4232 | 0 | 5547576.5511 | 0 | 0 | 0 | 3360573.9141 | 8289878.1765 | 21568562.5273 | 14720987.1146 | 65835525.7068 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 96886934.1535 | 161107409.4881 | 74989.4209 | 37.1162 | 2610.3647 | 4340.6172 | 53.2158 | 88.4894
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3607 | 51.1017 | 9.4248 | 4 | 2575.1299 | 4278.6274 | 52.4975 | 87.2256 | 194.9726 | 21.3632 | 112.7155 | 12428923.6272 | 0 | 5601224.8582 | 0 | 0 | 0 | 3288384.2759 | 8314227.7769 | 21631915.1929 | 14764226.6106 | 66028902.3418 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97080310.7885 | 161300786.1231 | 100000 | 37.6992 | 2575.1299 | 4278.6274 | 52.4975 | 87.2256
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.9077 | 51.6093 | 9.5353 | 4 | 2548.7066 | 4232.4572 | 51.9588 | 86.2844 | 194.7755 | 21.2708 | 108.0716 | 12488809.2374 | 0 | 5641405.7971 | 0 | 0 | 0 | 3230525.4281 | 8330688.7804 | 21674743.3474 | 14793457.706 | 66159630.2964 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97211038.7431 | 161431514.0777 | 133352.1432 | 38.1413 | 2548.7066 | 4232.4572 | 51.9588 | 86.2844
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.0667 | 51.9907 | 9.6189 | 4 | 2528.8901 | 4198.0169 | 51.5548 | 85.5823 | 194.6255 | 21.201 | 116.764 | 12533171.8439 | 0 | 5671463.323 | 0 | 0 | 0 | 3184921.173 | 8341926.9726 | 21703982.8181 | 14813414.2456 | 66248880.3761 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97300288.8228 | 161520764.1574 | 177827.941 | 38.4755 | 2528.8901 | 4198.0169 | 51.5548 | 85.5823
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.9487 | 52.281 | 9.6823 | 4 | 2514.0281 | 4172.2266 | 51.2519 | 85.0565 | 194.5101 | 21.1474 | 119.5359 | 12566644.1878 | 0 | 5694310.4595 | 0 | 0 | 0 | 3149802.4705 | 8350195.276 | 21725495.2475 | 14828096.9207 | 66314544.5619 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97365953.0086 | 161586428.3432 | 237137.3706 | 38.7291 | 2514.0281 | 4172.2266 | 51.2519 | 85.0565
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6138 | 52.5 | 9.7301 | 4 | 2502.882 | 4152.9246 | 51.0246 | 84.663 | 194.4223 | 21.1069 | 121.4835 | 12591719.4551 | 0 | 5711524.3358 | 0 | 0 | 0 | 3122834.7772 | 8356170.6415 | 21741041.923 | 14838707.8462 | 66361998.9788 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97413407.4255 | 161633882.7601 | 316227.766 | 38.9205 | 2502.882 | 4152.9246 | 51.0246 | 84.663
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.113 | 52.6645 | 9.7661 | 4 | 2494.5227 | 4138.4792 | 50.8542 | 84.3685 | 194.356 | 21.0763 | 120.0238 | 12610443.7283 | 0 | 5724434.8409 | 0 | 0 | 0 | 3102204.1526 | 8360462.2615 | 21752207.8378 | 14846328.8125 | 66396081.6337 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97447490.0804 | 161667965.415 | 421696.5034 | 39.0646 | 2494.5227 | 4138.4792 | 50.8542 | 84.3685
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.4808 | 52.7862 | 9.793 | 4 | 2488.2536 | 4127.6944 | 50.7264 | 84.1486 | 194.3069 | 21.0537 | 126.6399 | 12624187.4617 | 0 | 5733943.9278 | 0 | 0 | 0 | 3086326.2838 | 8363338.4926 | 21759691.2011 | 14851436.3617 | 66418923.7286 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97470332.1753 | 161690807.5099 | 562341.3252 | 39.1722 | 2488.2536 | 4127.6944 | 50.7264 | 84.1486
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.7586 | 52.8781 | 9.8133 | 4 | 2483.5522 | 4119.607 | 50.6306 | 83.9838 | 194.2696 | 21.0366 | 120.4916 | 12634539.3505 | 0 | 5741123.5769 | 0 | 0 | 0 | 3074337.218 | 8365500.0567 | 21765315.1475 | 14855274.8207 | 66436090.1703 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97487498.617 | 161707973.9516 | 749894.2093 | 39.2533 | 2483.5522 | 4119.607 | 50.6306 | 83.9838
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.9755 | 52.9494 | 9.8288 | 4 | 2480.0263 | 4113.5082 | 50.5587 | 83.8594 | 194.2405 | 21.0232 | 122.0492 | 12642605.4241 | 0 | 5746726.702 | 0 | 0 | 0 | 3065491.464 | 8367381.2002 | 21770209.4969 | 14858615.3147 | 66451029.6019 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97502438.0486 | 161722913.3832 | 1000000 | 39.3151 | 2480.0263 | 4113.5082 | 50.5587 | 83.8594
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1413 | 53.0038 | 9.8405 | 4 | 2477.3822 | 4108.9235 | 50.5048 | 83.766 | 194.2183 | 21.013 | 115.6459 | 12648761.1288 | 0 | 5751008.4463 | 0 | 0 | 0 | 3058895.0234 | 8368879.1934 | 21774106.9681 | 14861275.4189 | 66462926.1789 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97514334.6257 | 161734809.9602 | 1333521.4322 | 39.3618 | 2477.3822 | 4108.9235 | 50.5048 | 83.766
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.2534 | 53.0411 | 9.8489 | 4 | 2475.3994 | 4105.5437 | 50.4644 | 83.6971 | 194.2031 | 21.0061 | 116.0428 | 12652913.5074 | 0 | 5753902.3584 | 0 | 0 | 0 | 3053607.6478 | 8369565.1703 | 21775891.7392 | 14862493.5618 | 66468373.9847 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97519782.4315 | 161740257.766 | 1778279.41 | 39.3956 | 2475.3994 | 4105.5437 | 50.4644 | 83.6971
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.3434 | 53.0708 | 9.8554 | 4 | 2473.9124 | 4102.9826 | 50.434 | 83.6449 | 194.191 | 21.0005 | 127.8729 | 12656247.7717 | 0 | 5756226.5634 | 0 | 0 | 0 | 3049783.0543 | 8370280.3819 | 21777752.573 | 14863763.6191 | 66474053.9634 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97525462.4101 | 161745937.7447 | 2371373.7057 | 39.4216 | 2473.9124 | 4102.9826 | 50.434 | 83.6449
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4165 | 53.0947 | 9.8604 | 4 | 2472.7973 | 4101.0366 | 50.4113 | 83.6052 | 194.1811 | 20.996 | 123.7943 | 12658957.7606 | 0 | 5758115.59 | 0 | 0 | 0 | 3047052.852 | 8371009.219 | 21779648.8578 | 14865057.8725 | 66479842.1521 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97531250.5988 | 161751725.9334 | 3162277.6602 | 39.4417 | 2472.7973 | 4101.0366 | 50.4113 | 83.6052
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4554 | 53.1081 | 9.8637 | 4 | 2471.961 | 4099.6509 | 50.3943 | 83.5769 | 194.1758 | 20.9936 | 127.7671 | 12660393.2625 | 0 | 5759119.8196 | 0 | 0 | 0 | 3044590.682 | 8371000.468 | 21779626.0895 | 14865042.3326 | 66479772.6543 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97531181.101 | 161751656.4356 | 4216965.0343 | 39.455 | 2471.961 | 4099.6509 | 50.3943 | 83.5769
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4897 | 53.1196 | 9.8664 | 4 | 2471.334 | 4098.5885 | 50.3815 | 83.5553 | 194.1712 | 20.9914 | 121.0432 | 12661659.4967 | 0 | 5760004.4618 | 0 | 0 | 0 | 3042873.0148 | 8371169.4196 | 21780065.6667 | 14865342.3531 | 66481114.4126 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97532522.8594 | 161752998.194 | 5623413.2519 | 39.4655 | 2471.334 | 4098.5885 | 50.3815 | 83.5553
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.524 | 53.1306 | 9.8686 | 4 | 2470.8637 | 4097.7526 | 50.3719 | 83.5382 | 194.1666 | 20.9893 | 123.5873 | 12662928.2696 | 0 | 5760889.07 | 0 | 0 | 0 | 3041803.578 | 8371592.1578 | 21781165.545 | 14866093.0427 | 66484471.6631 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97535880.1098 | 161756355.4444 | 7498942.0933 | 39.4744 | 2470.8637 | 4097.7526 | 50.3719 | 83.5382
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.546 | 53.1378 | 9.8702 | 4 | 2470.5111 | 4097.1426 | 50.3647 | 83.5258 | 194.1636 | 20.9879 | 126.7592 | 12663743.5881 | 0 | 5761458.2979 | 0 | 0 | 0 | 3040907.2083 | 8371782.5468 | 21781660.898 | 14866431.1312 | 66485983.6703 | 961560.8286 | 30089847.6181 | 30089847.6181 | 22413605.2974 | 11717022.4191 | 0 | 97537392.117 | 161757867.4516 | 10000000 | 39.4807 | 2470.5111 | 4097.1426 | 50.3647 | 83.5258
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3077 | 0.26416 | 0.027649 | 4 | 323707.0164 | 916510.1632 | 6599.2054 | 18684.2993 | 131.689 | 23.9026 | 48.5226 | 563400.4571 | 0 | 237001.7562 | 0 | 0 | 0 | 523690.7508 | 516396.256 | 1343557.1307 | 917005.349 | 4101051.6999 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 35801063.3748 | 101363383.4871 | 100 | 0.1106 | 323707.0164 | 916510.1632 | 6599.2054 | 18684.2993
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5964 | 0.53189 | 0.062403 | 4 | 148871.5319 | 411529.9166 | 3034.9475 | 8389.594 | 147.1021 | 24.6369 | 66.3009 | 780581.0901 | 0 | 308367.0609 | 0 | 0 | 0 | 673872.467 | 687500.041 | 1788734.0811 | 1220847.7652 | 5459902.5054 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 37159914.1803 | 102722234.2926 | 133.3521 | 0.24961 | 148871.5319 | 411529.9166 | 3034.9475 | 8389.594
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1381 | 0.89934 | 0.11328 | 4 | 85258.4021 | 229952.1534 | 1738.1078 | 4687.8857 | 159.1912 | 25.1427 | 65.9399 | 1022834.1353 | 0 | 388649.4305 | 0 | 0 | 0 | 826467.5564 | 872800.9376 | 2270849.0036 | 1549901.1063 | 6931502.1697 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 38631513.8446 | 104193833.9569 | 177.8279 | 0.45311 | 85258.4021 | 229952.1534 | 1738.1078 | 4687.8857
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0944 | 1.4006 | 0.18442 | 4 | 54690.0529 | 143565.9534 | 1114.9307 | 2926.7861 | 169.2197 | 25.5209 | 59.7783 | 1307773.7742 | 0 | 484928.8352 | 0 | 0 | 0 | 998143.8826 | 1088430.1319 | 2831871.9354 | 1932810.7851 | 8643959.3444 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 40343971.0193 | 105906291.1316 | 237.1374 | 0.73768 | 54690.0529 | 143565.9534 | 1114.9307 | 2926.7861
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5692 | 2.0655 | 0.2813 | 4 | 37618.4393 | 95885.4087 | 766.9028 | 1954.7538 | 177.413 | 25.8034 | 51.1607 | 1641073.3006 | 0 | 600298.9907 | 0 | 0 | 0 | 1190205.5017 | 1338315.3393 | 3482021.9866 | 2376551.5542 | 10628466.673 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 42328478.348 | 107890798.4602 | 316.2278 | 1.1252 | 37618.4393 | 95885.4087 | 766.9028 | 1954.7538
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6903 | 2.9307 | 0.41098 | 4 | 27143.8448 | 67025.7397 | 553.364 | 1366.4104 | 184.0305 | 26.0122 | 61.3375 | 2029705.9202 | 0 | 738352.4323 | 0 | 0 | 0 | 1404049.7235 | 1627122.1497 | 4233438.0648 | 2889408.4677 | 12922076.7583 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 44622088.4332 | 110184408.5455 | 421.6965 | 1.6439 | 27143.8448 | 67025.7397 | 553.364 | 1366.4104
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6534 | 4.051 | 0.58279 | 4 | 20291.0578 | 48415.2449 | 413.6607 | 987.0103 | 189.3714 | 26.1631 | 61.5672 | 2486308.2055 | 0 | 904886.4298 | 0 | 0 | 0 | 1646150.7363 | 1964564.6949 | 5111394.3486 | 3488631.6716 | 15601936.0868 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 47301947.7617 | 112864267.874 | 562.3413 | 2.3312 | 20291.0578 | 48415.2449 | 413.6607 | 987.0103
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6427 | 5.4821 | 0.808 | 4 | 15595.6774 | 35881.1078 | 317.939 | 731.4849 | 193.616 | 26.2629 | 63.4885 | 3018785.6041 | 0 | 1104270.6855 | 0 | 0 | 0 | 1916187.8916 | 2355305.2307 | 6128021.0706 | 4182500.2989 | 18705070.7814 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 50405082.4563 | 115967402.5686 | 749.8942 | 3.232 | 15595.6774 | 35881.1078 | 317.939 | 731.4849
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8862 | 7.2925 | 1.1002 | 4 | 12265.5992 | 27163.0547 | 250.0508 | 553.7556 | 196.9513 | 26.3138 | 59.7511 | 3636791.3779 | 0 | 1341789.2032 | 0 | 0 | 0 | 2214809.3237 | 2805422.0629 | 7299132.7364 | 4981808.0748 | 22279752.779 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 53979764.4539 | 119542084.5662 | 1000 | 4.4009 | 12265.5992 | 27163.0547 | 250.0508 | 553.7556
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.625 | 9.5569 | 1.4749 | 4 | 9841.0448 | 20953.7129 | 200.623 | 427.1698 | 199.5294 | 26.3126 | 69.7329 | 4348143.9319 | 0 | 1622387.9078 | 0 | 0 | 0 | 2540236.7127 | 3319199.7354 | 8635876.8501 | 5894163.3997 | 26360008.5376 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 58060020.2125 | 123622340.3247 | 1333.5214 | 5.8998 | 9841.0448 | 20953.7129 | 200.623 | 427.1698
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.1038 | 12.3528 | 1.9484 | 4 | 8040.3578 | 16452.7452 | 163.9136 | 335.4115 | 201.471 | 26.2499 | 88.2702 | 5157938.5934 | 0 | 1950391.3654 | 0 | 0 | 0 | 2888552.0339 | 3898783.9771 | 10143836.158 | 6923376.6128 | 30962878.7406 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 62662890.4155 | 128225210.5278 | 1778.2794 | 7.7935 | 8040.3578 | 16452.7452 | 163.9136 | 335.4115
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.3897 | 15.7115 | 2.5319 | 4 | 6683.8362 | 13157.4792 | 136.259 | 268.233 | 202.8447 | 26.1118 | 87.2885 | 6054585.4397 | 0 | 2323803.4454 | 0 | 0 | 0 | 3241924.2706 | 4531922.1307 | 11791131.7591 | 8047689.7091 | 35991056.7547 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 67691068.4296 | 133253388.5419 | 2371.3737 | 10.1276 | 6683.8362 | 13157.4792 | 136.259 | 268.233
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.3787 | 19.6138 | 3.2274 | 4 | 5653.1387 | 10731.7292 | 115.2469 | 218.7808 | 203.6953 | 25.8822 | 77.7787 | 7014341.9603 | 0 | 2735807.4284 | 0 | 0 | 0 | 3577615.7012 | 5197828.3851 | 13523683.2368 | 9230191.693 | 41279468.4048 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 72979480.0797 | 138541800.192 | 3162.2777 | 12.9096 | 5653.1387 | 10731.7292 | 115.2469 | 218.7808
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.5929 | 23.9291 | 4.0178 | 4 | 4867.5992 | 8947.1322 | 99.2326 | 182.3994 | 204.0452 | 25.5521 | 87.3179 | 7990696.2481 | 0 | 3169563.6043 | 0 | 0 | 0 | 3861871.1327 | 5858631.0842 | 15242956.3106 | 10403630.8934 | 46527349.2735 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 78227360.9484 | 143789681.0607 | 4216.965 | 16.071 | 4867.5992 | 8947.1322 | 99.2326 | 182.3994
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2844 | 28.4382 | 4.8661 | 4 | 4269.6212 | 7637.9735 | 87.042 | 155.7104 | 203.9412 | 25.128 | 117.4559 | 8928502.0045 | 0 | 3602773.8096 | 0 | 0 | 0 | 4065620.0565 | 6472789.3895 | 16840870.2399 | 11494239.984 | 51404795.4841 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 83104807.159 | 148667127.2712 | 5623.4133 | 19.4642 | 4269.6212 | 7637.9735 | 87.042 | 155.7104
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.5445 | 32.864 | 5.7206 | 4 | 3816.0548 | 6681.2316 | 77.7954 | 136.2059 | 203.476 | 24.6371 | 119.5165 | 9774999.8841 | 0 | 4011115.1816 | 0 | 0 | 0 | 4171970.3721 | 7003653.3207 | 18222069.2937 | 12436936.719 | 55620744.7711 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 87320756.4461 | 152883076.5583 | 7498.9421 | 22.8825 | 3816.0548 | 6681.2316 | 77.7954 | 136.2059
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.5607 | 36.9497 | 6.5291 | 4 | 3473.4835 | 5983.8869 | 70.8117 | 121.9896 | 202.7799 | 24.1214 | 113.8885 | 10495304.5803 | 0 | 4374934.2823 | 0 | 0 | 0 | 4183527.6991 | 7430968.9591 | 19333856.9301 | 13195754.6259 | 59014347.0768 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 90714358.7517 | 156276678.864 | 10000 | 26.1162 | 3473.4835 | 5983.8869 | 70.8117 | 121.9896
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.8371 | 40.5277 | 7.2525 | 4 | 3215.6912 | 5475.6748 | 65.5562 | 111.629 | 201.984 | 23.6221 | 115.3555 | 11079646.5619 | 0 | 4684089.5686 | 0 | 0 | 0 | 4120806.2933 | 7754971.5453 | 20176845.1975 | 13771111.44 | 61587470.6067 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 93287482.2816 | 158849802.3938 | 13335.2143 | 29.0101 | 3215.6912 | 5475.6748 | 65.5562 | 111.629
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.2038 | 43.5297 | 7.8708 | 4 | 3022.179 | 5104.6253 | 61.6112 | 104.0647 | 201.1923 | 23.1699 | 134.4195 | 11536983.6474 | 0 | 4937050.3918 | 0 | 0 | 0 | 4011281.23 | 7989272.955 | 20786449.4037 | 14187178.8368 | 63448216.4647 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 95148228.1397 | 160710548.2519 | 17782.7941 | 31.4833 | 3022.179 | 5104.6253 | 61.6112 | 104.0647
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7313 | 45.9645 | 8.3804 | 4 | 2877.0631 | 4832.8772 | 58.6528 | 98.5247 | 200.4701 | 22.7809 | 119.6282 | 11885734.1687 | 0 | 5138010.0807 | 0 | 0 | 0 | 3879998.2949 | 8152459.5923 | 21211027.5597 | 14476962.1525 | 64744191.8488 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 96444203.5237 | 162006523.636 | 23713.7371 | 33.5218 | 2877.0631 | 4832.8772 | 58.6528 | 98.5247
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.646 | 47.8924 | 8.7894 | 4 | 2768.3657 | 4633.1839 | 56.4369 | 94.4537 | 199.8499 | 22.46 | 126.2154 | 12147954.7803 | 0 | 5294540.2688 | 0 | 0 | 0 | 3746849.4309 | 8263844.3472 | 21500827.8438 | 14674756.8012 | 65628773.4721 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 97328785.147 | 162891105.2593 | 31622.7766 | 35.1575 | 2768.3657 | 4633.1839 | 56.4369 | 94.4537
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2307 | 49.3961 | 9.1116 | 4 | 2686.9141 | 4485.7926 | 54.7764 | 91.449 | 199.3363 | 22.2016 | 115.3675 | 12343875.2456 | 0 | 5415080.0851 | 0 | 0 | 0 | 3623809.1773 | 8339278.1581 | 21697091.1463 | 14808710.538 | 66227844.3506 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 97927856.0255 | 163490176.1377 | 42169.6503 | 36.4462 | 2686.9141 | 4485.7926 | 54.7764 | 91.449
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.7332 | 50.5514 | 9.3615 | 4 | 2625.8666 | 4376.7141 | 53.5318 | 89.2252 | 198.9243 | 21.9984 | 122.7606 | 12489155.0306 | 0 | 5506718.2583 | 0 | 0 | 0 | 3516189.5275 | 8389704.4984 | 21828290.1398 | 14898256.5469 | 66628314.0014 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 98328325.6763 | 163890645.7886 | 56234.1325 | 37.446 | 2625.8666 | 4376.7141 | 53.5318 | 89.2252
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.4056 | 51.4362 | 9.554 | 4 | 2580.1017 | 4295.6766 | 52.5989 | 87.5732 | 198.5984 | 21.8399 | 113.1919 | 12597400.0605 | 0 | 5576379.0707 | 0 | 0 | 0 | 3426331.3548 | 8424043.0895 | 21917632.1101 | 14959234.2775 | 66901019.9631 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 98601031.638 | 164163351.7503 | 74989.4209 | 38.2159 | 2580.1017 | 4295.6766 | 52.5989 | 87.5732
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4324 | 52.1093 | 9.7011 | 4 | 2545.7875 | 4235.3479 | 51.8993 | 86.3433 | 198.3444 | 21.7178 | 113.8128 | 12677979.6545 | 0 | 5629068.6759 | 0 | 0 | 0 | 3353322.0276 | 8447544.4396 | 21978777.8023 | 15000967.4688 | 67087660.0688 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 98787671.7438 | 164349991.856 | 100000 | 38.8044 | 2545.7875 | 4235.3479 | 51.8993 | 86.3433
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.9593 | 52.6179 | 9.8128 | 4 | 2520.056 | 4190.3827 | 51.3748 | 85.4266 | 198.1492 | 21.6246 | 128.6616 | 12737805.2426 | 0 | 5668678.971 | 0 | 0 | 0 | 3295064.2805 | 8463603.9127 | 22020561.2569 | 15029485.5351 | 67215199.1988 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 98915210.8738 | 164477530.986 | 133352.1432 | 39.2512 | 2520.056 | 4190.3827 | 51.3748 | 85.4266
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.1191 | 53.0045 | 9.8977 | 4 | 2500.7592 | 4156.7636 | 50.9814 | 84.7412 | 197.9987 | 21.5532 | 127.8547 | 12782746.6958 | 0 | 5698721.8832 | 0 | 0 | 0 | 3249626.942 | 8475127.2532 | 22050542.6251 | 15049948.435 | 67306713.8342 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99006725.5092 | 164569045.6214 | 177827.941 | 39.5907 | 2500.7592 | 4156.7636 | 50.9814 | 84.7412
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.9887 | 53.295 | 9.9617 | 4 | 2486.2876 | 4131.6497 | 50.6863 | 84.2293 | 197.8845 | 21.4993 | 117.4406 | 12816153.0372 | 0 | 5721221.3114 | 0 | 0 | 0 | 3214297.5017 | 8483152.0216 | 22071421.4265 | 15064198.646 | 67370443.9444 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99070455.6193 | 164632775.7316 | 237137.3706 | 39.8467 | 2486.2876 | 4131.6497 | 50.6863 | 84.2293
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.6271 | 53.5092 | 10.0095 | 4 | 2475.4345 | 4112.934 | 50.4651 | 83.8477 | 197.7999 | 21.4595 | 118.7757 | 12840515.8046 | 0 | 5737725.4896 | 0 | 0 | 0 | 3186719.7299 | 8488334.7994 | 22084905.9512 | 15073402.1111 | 67411603.886 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99111615.5609 | 164673935.6732 | 316227.766 | 40.0381 | 2475.4345 | 4112.934 | 50.4651 | 83.8477
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1265 | 53.676 | 10.0461 | 4 | 2467.2951 | 4098.8329 | 50.2991 | 83.5603 | 197.7334 | 21.4283 | 126.7655 | 12859483.2649 | 0 | 5750625.753 | 0 | 0 | 0 | 3166180.2989 | 8492752.8336 | 22096400.7698 | 15081247.561 | 67446690.4813 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99146702.1562 | 164709022.2685 | 421696.5034 | 40.1844 | 2467.2951 | 4098.8329 | 50.2991 | 83.5603
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4897 | 53.7979 | 10.0733 | 4 | 2461.1911 | 4088.3273 | 50.1747 | 83.3461 | 197.6848 | 21.4055 | 121.5469 | 12873224.2056 | 0 | 5760004.4618 | 0 | 0 | 0 | 3150244.6624 | 8495554.5986 | 22103690.3877 | 15086222.875 | 67468941.191 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99168952.8659 | 164731272.9782 | 562341.3252 | 40.2931 | 2461.1911 | 4088.3273 | 50.1747 | 83.3461
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.7649 | 53.8902 | 10.0938 | 4 | 2456.6134 | 4080.4453 | 50.0814 | 83.1854 | 197.6478 | 21.3882 | 126.6647 | 12883608.3638 | 0 | 5767108.831 | 0 | 0 | 0 | 3138238.119 | 8497692.5724 | 22109252.957 | 15090019.4428 | 67485920.286 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99185931.961 | 164748252.0732 | 749894.2093 | 40.3751 | 2456.6134 | 4080.4453 | 50.0814 | 83.1854
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.9696 | 53.9589 | 10.1091 | 4 | 2453.1805 | 4074.5476 | 50.0114 | 83.0652 | 197.6202 | 21.3753 | 124.5363 | 12891313.435 | 0 | 5772390.4408 | 0 | 0 | 0 | 3129114.1922 | 8499199.0465 | 22113172.4936 | 15092694.6071 | 67497884.2152 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99197895.8901 | 164760216.0024 | 1000000 | 40.4364 | 2453.1805 | 4074.5476 | 50.0114 | 83.0652
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.1398 | 54.0153 | 10.1211 | 4 | 2450.6061 | 4070.0518 | 49.9589 | 82.9735 | 197.5973 | 21.3645 | 121.5798 | 12897716.6887 | 0 | 5776782.381 | 0 | 0 | 0 | 3122668.7842 | 8500895.463 | 22117586.2214 | 15095707.067 | 67511356.6054 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99211368.2803 | 164773688.3926 | 1333521.4322 | 40.4844 | 2450.6061 | 4070.0518 | 49.9589 | 82.9735
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.2519 | 54.0531 | 10.1297 | 4 | 2448.6755 | 4066.7529 | 49.9196 | 82.9063 | 197.5821 | 21.3575 | 121.9618 | 12901922.046 | 0 | 5779673.0608 | 0 | 0 | 0 | 3117402.39 | 8501609.0237 | 22119442.7599 | 15096974.1928 | 67517023.4732 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99217035.1481 | 164779355.2604 | 1778279.41 | 40.5187 | 2448.6755 | 4066.7529 | 49.9196 | 82.9063
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.3445 | 54.0839 | 10.1363 | 4 | 2447.2277 | 4064.2412 | 49.89 | 82.8551 | 197.5696 | 21.3516 | 119.6039 | 12905397.221 | 0 | 5782061.7796 | 0 | 0 | 0 | 3113663.9815 | 8502437.963 | 22121599.4898 | 15098446.2052 | 67523606.64 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99223618.3149 | 164785938.4272 | 2371373.7057 | 40.5453 | 2447.2277 | 4064.2412 | 49.89 | 82.8551
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.3982 | 54.1025 | 10.1409 | 4 | 2446.142 | 4062.4294 | 49.8679 | 82.8181 | 197.5623 | 21.3482 | 114.0757 | 12907406.7712 | 0 | 5783447.1234 | 0 | 0 | 0 | 3110442.0664 | 8502505.4248 | 22121775.0117 | 15098566.0025 | 67524142.4001 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99224154.075 | 164786474.1873 | 3162277.6602 | 40.5635 | 2446.142 | 4062.4294 | 49.8679 | 82.8181
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4519 | 54.1204 | 10.1447 | 4 | 2445.3278 | 4061.0102 | 49.8513 | 82.7892 | 197.555 | 21.3448 | 108.2967 | 12909420.5876 | 0 | 5784832.3843 | 0 | 0 | 0 | 3108372.4373 | 8503023.9096 | 22123124.0028 | 15099486.7166 | 67528260.0382 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99228271.7131 | 164790591.8254 | 4216965.0343 | 40.5787 | 2445.3278 | 4061.0102 | 49.8513 | 82.7892
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4862 | 54.132 | 10.1474 | 4 | 2444.7173 | 4059.9733 | 49.8389 | 82.768 | 197.5503 | 21.3426 | 110.9971 | 12910703.0007 | 0 | 5785716.0419 | 0 | 0 | 0 | 3106661.1367 | 8503201.2699 | 22123585.4579 | 15099801.6692 | 67529668.5763 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99229680.2512 | 164792000.3635 | 5623413.2519 | 40.5894 | 2444.7173 | 4059.9733 | 49.8389 | 82.768
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.5102 | 54.1402 | 10.1493 | 4 | 2444.2594 | 4059.2031 | 49.8295 | 82.7523 | 197.5471 | 21.3411 | 113.5604 | 12911603.3632 | 0 | 5786336.9703 | 0 | 0 | 0 | 3105334.3928 | 8503277.1433 | 22123782.8648 | 15099936.4035 | 67530271.1378 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99230282.8127 | 164792602.925 | 7498942.0933 | 40.5973 | 2444.2594 | 4059.2031 | 49.8295 | 82.7523
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.5445 | 54.1511 | 10.1513 | 4 | 2443.9161 | 4058.5525 | 49.8225 | 82.7391 | 197.5425 | 21.339 | 106.3033 | 12912890.2729 | 0 | 5787220.5704 | 0 | 0 | 0 | 3104761.0084 | 8503900.0222 | 22125403.468 | 15101042.4985 | 67535217.8403 | 961560.8286 | 30738450.8463 | 30738450.8463 | 22874378.7166 | 11949490.5493 | 0 | 99235229.5153 | 164797549.6275 | 10000000 | 40.605 | 2443.9161 | 4058.5525 | 49.8225 | 82.7391
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.27664 | 0.029266 | 4 | 312663.6417 | 884293.829 | 6374.0712 | 18027.5258 | 134.1224 | 24.3752 | 44.9337 | 585030.8742 | 0 | 242295.6006 | 0 | 0 | 0 | 544056.4197 | 534839.3288 | 1391542.223 | 949756.1605 | 4247520.6068 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 36601995.6007 | 103519931.7042 | 100 | 0.11707 | 312663.6417 | 884293.829 | 6374.0712 | 18027.5258
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.689 | 0.54996 | 0.065681 | 4 | 144499.7802 | 399206.1318 | 2945.8235 | 8138.357 | 149.4587 | 25.1004 | 65.2907 | 804315.0478 | 0 | 313327.5826 | 0 | 0 | 0 | 693429.2268 | 706318.0243 | 1837694.6134 | 1254264.3345 | 5609348.8294 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 37963823.8234 | 104881759.9269 | 133.3521 | 0.26273 | 144499.7802 | 399206.1318 | 2945.8235 | 8138.357
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2696 | 0.93096 | 0.11894 | 4 | 82992.2218 | 223643.6621 | 1691.9087 | 4559.2786 | 161.8343 | 25.615 | 68.4865 | 1055107.9081 | 0 | 395296.6275 | 0 | 0 | 0 | 851910.1822 | 897902.7399 | 2336158.7441 | 1594476.3461 | 7130852.5478 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 39485327.5418 | 106403263.6453 | 177.8279 | 0.47577 | 82992.2218 | 223643.6621 | 1691.9087 | 4559.2786
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2723 | 1.4504 | 0.19337 | 4 | 53334.1153 | 139851.3652 | 1087.2881 | 2851.0592 | 172.0677 | 25.9985 | 70.701 | 1349558.4074 | 0 | 493440.7629 | 0 | 0 | 0 | 1029712.7108 | 1120357.6336 | 2914940.7457 | 1989506.955 | 8897517.2154 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 41251992.2094 | 108169928.3129 | 237.1374 | 0.77346 | 53334.1153 | 139851.3652 | 1087.2881 | 2851.0592
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7861 | 2.1353 | 0.29454 | 4 | 36733.6725 | 93531.7936 | 748.8656 | 1906.7721 | 180.3654 | 26.2826 | 54.6703 | 1691303.3301 | 0 | 610133.5692 | 0 | 0 | 0 | 1225589.9291 | 1375540.4631 | 3578874.1227 | 2442655.1273 | 10924096.5414 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 43278571.5354 | 110196507.6388 | 316.2278 | 1.1782 | 36733.6725 | 93531.7936 | 748.8656 | 1906.7721
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9682 | 3.0289 | 0.42998 | 4 | 26532.0062 | 65439.7154 | 540.8908 | 1334.0771 | 187.0994 | 26.4934 | 54.9402 | 2091360.8756 | 0 | 750315.5244 | 0 | 0 | 0 | 1445447.2592 | 1671978.2271 | 4350144.377 | 2969062.9238 | 13278309.1872 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 45632784.1812 | 112550720.2846 | 421.6965 | 1.7199 | 26532.0062 | 65439.7154 | 540.8908 | 1334.0771
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.0017 | 4.1844 | 0.60929 | 4 | 19849.8497 | 47307.0144 | 404.666 | 964.4175 | 192.5273 | 26.6452 | 66.8678 | 2560644.1363 | 0 | 919144.8474 | 0 | 0 | 0 | 1693535.3541 | 2017596.4917 | 5249372.2055 | 3582804.3941 | 16023097.429 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 48377572.423 | 115295508.5264 | 562.3413 | 2.4372 | 19849.8497 | 47307.0144 | 404.666 | 964.4175
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0862 | 5.6619 | 0.84431 | 4 | 15267.1934 | 35081.4817 | 311.2424 | 715.1835 | 196.848 | 26.745 | 49.8758 | 3108628.5785 | 0 | 1121537.59 | 0 | 0 | 0 | 1971055.0383 | 2418476.2707 | 6292379.1586 | 4294678.0712 | 19206754.7072 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 51561229.7012 | 118479165.8047 | 749.8942 | 3.3773 | 15267.1934 | 35081.4817 | 311.2424 | 715.1835
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.4413 | 7.5292 | 1.1491 | 4 | 12014.7483 | 26573.8643 | 244.9369 | 541.7442 | 200.2401 | 26.7945 | 78.9095 | 3743941.1933 | 0 | 1362377.2971 | 0 | 0 | 0 | 2277257.2559 | 2879594.5411 | 7492114.3098 | 5113521.964 | 22868806.5611 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 55223281.5551 | 122141217.6586 | 1000 | 4.5963 | 12014.7483 | 26573.8643 | 244.9369 | 541.7442
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.3218 | 9.8656 | 1.5397 | 4 | 9645.4359 | 20510.5891 | 196.6353 | 418.1361 | 202.8638 | 26.7901 | 81.3916 | 4475540.6298 | 0 | 1647033.6333 | 0 | 0 | 0 | 2611384.0537 | 3406243.7435 | 8862347.504 | 6048734.2745 | 27051283.8388 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 59405758.8328 | 126323694.9363 | 1333.5214 | 6.159 | 9645.4359 | 20510.5891 | 196.6353 | 418.1361
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.9493 | 12.7439 | 2.0326 | 4 | 7885.124 | 16115.8042 | 160.7489 | 328.5425 | 204.8354 | 26.7219 | 75.867 | 5306271.2494 | 0 | 1978954.9868 | 0 | 0 | 0 | 2967077.2556 | 3998398.3618 | 10403012.3532 | 7100269.6916 | 31753983.8985 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 64108458.8925 | 131026394.996 | 1778.2794 | 8.1303 | 7885.124 | 16115.8042 | 160.7489 | 328.5425
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.4102 | 16.2008 | 2.6394 | 4 | 6558.8014 | 12897.1556 | 133.71 | 262.926 | 206.2298 | 26.5753 | 83.2731 | 6225927.4031 | 0 | 2356804.5418 | 0 | 0 | 0 | 3328097.3036 | 4645223.4069 | 12085918.4385 | 8248887.675 | 36890858.7689 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 69245333.7629 | 136163269.8664 | 2371.3737 | 10.5576 | 6558.8014 | 12897.1556 | 133.71 | 262.926
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.5554 | 20.2047 | 3.3608 | 4 | 5551.1335 | 10528.9963 | 113.1674 | 214.6478 | 207.0882 | 26.3341 | 95.9607 | 7206865.1187 | 0 | 2772339.0613 | 0 | 0 | 0 | 3668371.0442 | 5322554.3375 | 13848194.5801 | 9451677.3529 | 42270001.4947 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 74624476.4887 | 141542412.5921 | 3162.2777 | 13.4431 | 5551.1335 | 10528.9963 | 113.1674 | 214.6478
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9157 | 24.6247 | 4.1786 | 4 | 4783.3843 | 8786.9818 | 97.5158 | 179.1345 | 207.4364 | 25.9891 | 96.4321 | 8202944.3989 | 0 | 3209153.3492 | 0 | 0 | 0 | 3955442.226 | 5993340.5899 | 15593442.8117 | 10642845.1322 | 47597168.5077 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 79951643.5017 | 146869579.6052 | 4216.965 | 16.7145 | 4783.3843 | 8786.9818 | 97.5158 | 179.1345
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6876 | 29.2225 | 5.0529 | 4 | 4199.214 | 7510.1103 | 85.6067 | 153.1038 | 207.324 | 25.549 | 107.9359 | 9155047.9756 | 0 | 3643451.9525 | 0 | 0 | 0 | 4157693.0333 | 6612915.2549 | 17205448.9979 | 11743072.4777 | 52517629.6919 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 84872104.6859 | 151790040.7894 | 5623.4133 | 20.2114 | 4199.214 | 7510.1103 | 85.6067 | 153.1038
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.9749 | 33.7201 | 5.9304 | 4 | 3756.345 | 6577.3365 | 76.5782 | 134.0879 | 206.8494 | 25.0426 | 112.5178 | 10011413.3941 | 0 | 4051489.9703 | 0 | 0 | 0 | 4260226.5754 | 7146020.6765 | 18592479.9499 | 12689749.6031 | 56751380.1694 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 89105855.1634 | 156023791.2669 | 7498.9421 | 23.7214 | 3756.345 | 6577.3365 | 76.5782 | 134.0879
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0003 | 37.8665 | 6.7584 | 4 | 3422.0159 | 5897.3772 | 69.7624 | 120.226 | 206.1445 | 24.512 | 123.0672 | 10739254.7112 | 0 | 4414697.9535 | 0 | 0 | 0 | 4268075.9545 | 7574591.1615 | 19707532.4399 | 13450795.8395 | 60154948.0601 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 92509423.0541 | 159427359.1576 | 10000 | 27.0336 | 3422.0159 | 5897.3772 | 69.7624 | 120.226
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.2324 | 41.4822 | 7.4966 | 4 | 3170.5316 | 5402.1546 | 64.6356 | 110.1302 | 205.3445 | 24.0015 | 129.9187 | 11327039.5334 | 0 | 4721985.1459 | 0 | 0 | 0 | 4200456.6568 | 7897297.7211 | 20547148.7117 | 14023851.1974 | 62717778.9662 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 95072253.9602 | 161990190.0637 | 13335.2143 | 29.9862 | 3170.5316 | 5402.1546 | 64.6356 | 110.1302
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.524 | 44.5041 | 8.1253 | 4 | 2981.8173 | 5040.7484 | 60.7884 | 102.7625 | 204.5533 | 23.5416 | 137.3528 | 11785295.2584 | 0 | 4972439.5871 | 0 | 0 | 0 | 4086040.3038 | 8129072.3082 | 21150178.644 | 14435431.5173 | 64558457.6188 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 96912932.6128 | 163830868.7163 | 17782.7941 | 32.5013 | 2981.8173 | 5040.7484 | 60.7884 | 102.7625
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9971 | 46.9561 | 8.6431 | 4 | 2840.3794 | 4775.9781 | 57.905 | 97.3648 | 203.8329 | 23.1467 | 150.0213 | 12135240.3347 | 0 | 5171608.5108 | 0 | 0 | 0 | 3951898.8379 | 8290911.5965 | 21571251.2744 | 14722822.2397 | 65843732.794 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 98198207.788 | 165116143.8915 | 23713.7371 | 34.5722 | 2840.3794 | 4775.9781 | 57.905 | 97.3648
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.8466 | 48.8913 | 9.0575 | 4 | 2734.378 | 4581.4073 | 55.744 | 93.3982 | 203.2155 | 22.8213 | 118.195 | 12397245.0523 | 0 | 5326171.4849 | 0 | 0 | 0 | 3815711.1115 | 8400259.783 | 21855752.8251 | 14917000.3939 | 66712140.6507 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 99066615.6447 | 165984551.7481 | 31622.7766 | 36.23 | 2734.378 | 4581.4073 | 55.744 | 93.3982
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.3897 | 50.403 | 9.384 | 4 | 2654.9922 | 4437.7532 | 54.1256 | 90.4696 | 202.7043 | 22.5593 | 126.9476 | 12593530.7001 | 0 | 5445445.8145 | 0 | 0 | 0 | 3691125.9165 | 8474739.9481 | 22049534.9369 | 15049260.667 | 67303637.9832 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 99658112.9772 | 166576049.0806 | 42169.6503 | 37.5361 | 2654.9922 | 4437.7532 | 54.1256 | 90.4696
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8586 | 51.5638 | 9.6372 | 4 | 2595.4995 | 4331.4354 | 52.9128 | 88.3022 | 202.2946 | 22.3535 | 119.3371 | 12739034.943 | 0 | 5536080.9756 | 0 | 0 | 0 | 3582458.3036 | 8524453.9466 | 22178880.5632 | 15137541.7148 | 67698450.4468 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100052925.4408 | 166970861.5443 | 56234.1325 | 38.5486 | 2595.4995 | 4331.4354 | 52.9128 | 88.3022
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.4922 | 52.4489 | 9.8316 | 4 | 2550.9039 | 4252.5071 | 52.0036 | 86.6931 | 201.9722 | 22.1939 | 117.1931 | 12846932.9332 | 0 | 5604643.4539 | 0 | 0 | 0 | 3491544.7742 | 8557817.2529 | 22265685.0424 | 15196787.5555 | 67963411.0123 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100317886.0063 | 167235822.1097 | 74989.4209 | 39.3264 | 2550.9039 | 4252.5071 | 52.0036 | 86.6931
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.4802 | 53.1196 | 9.9799 | 4 | 2517.4689 | 4193.7885 | 51.322 | 85.4961 | 201.7222 | 22.0715 | 114.1657 | 12926890.1457 | 0 | 5656258.1733 | 0 | 0 | 0 | 3417558.1653 | 8580275.5289 | 22324116.8698 | 15236668.4783 | 68141767.3614 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100496242.3554 | 167414178.4589 | 100000 | 39.9196 | 2517.4689 | 4193.7885 | 51.322 | 85.4961
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.005 | 53.6341 | 10.0933 | 4 | 2492.3979 | 4149.8876 | 50.8109 | 84.6011 | 201.5267 | 21.9764 | 128.0291 | 12987351.2956 | 0 | 5695768.4702 | 0 | 0 | 0 | 3359396.7126 | 8596581.4266 | 22366541.4706 | 15265624.1401 | 68271263.5156 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100625738.5096 | 167543674.6131 | 133352.1432 | 40.3731 | 2492.3979 | 4149.8876 | 50.8109 | 84.6011
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.1324 | 54.0163 | 10.1785 | 4 | 2473.5973 | 4117.2094 | 50.4276 | 83.9349 | 201.3799 | 21.9055 | 124.4589 | 13031556.31 | 0 | 5724937.6981 | 0 | 0 | 0 | 3313200.0361 | 8607180.6772 | 22394118.5467 | 15284446.0612 | 68355439.3293 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100709914.3233 | 167627850.4268 | 177827.941 | 40.7139 | 2473.5973 | 4117.2094 | 50.4276 | 83.9349
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.9903 | 54.3071 | 10.2431 | 4 | 2459.4983 | 4092.7372 | 50.1402 | 83.436 | 201.2669 | 21.8512 | 125.1362 | 13064915.0917 | 0 | 5747109.4602 | 0 | 0 | 0 | 3277674.7564 | 8614982.7302 | 22414417.8881 | 15298300.7789 | 68417400.7055 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100771875.6995 | 167689811.803 | 237137.3706 | 40.9725 | 2459.4983 | 4092.7372 | 50.1402 | 83.436
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.6406 | 54.5276 | 10.292 | 4 | 2448.9249 | 4074.4053 | 49.9246 | 83.0623 | 201.1806 | 21.8098 | 124.9192 | 13090039.1061 | 0 | 5763901.2648 | 0 | 0 | 0 | 3250515.7728 | 8620737.896 | 22429391.649 | 15308520.6784 | 68463106.3671 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100817581.3611 | 167735517.4646 | 316227.766 | 41.1681 | 2448.9249 | 4074.4053 | 49.9246 | 83.0623
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.1204 | 54.6907 | 10.3286 | 4 | 2440.9955 | 4060.7235 | 49.763 | 82.7833 | 201.1165 | 21.7792 | 120.5921 | 13108479.5753 | 0 | 5776280.656 | 0 | 0 | 0 | 3229529.5373 | 8624573.0097 | 22439369.8282 | 15315330.9907 | 68493563.5971 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100848038.5911 | 167765974.6946 | 421696.5034 | 41.3143 | 2440.9955 | 4060.7235 | 49.763 | 82.7833
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4862 | 54.815 | 10.3562 | 4 | 2435.049 | 4050.4519 | 49.6418 | 82.5739 | 201.0674 | 21.7557 | 111.7408 | 13122491.1755 | 0 | 5785716.0419 | 0 | 0 | 0 | 3213725.7822 | 8627553.8698 | 22447125.4147 | 15320624.3378 | 68517236.622 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100871711.616 | 167789647.7195 | 562341.3252 | 41.4249 | 2435.049 | 4050.4519 | 49.6418 | 82.5739
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.7466 | 54.9041 | 10.3766 | 4 | 2430.5896 | 4042.8211 | 49.5509 | 82.4184 | 201.0323 | 21.739 | 117.9892 | 13132433.7576 | 0 | 5792430.5101 | 0 | 0 | 0 | 3201371.9666 | 8629232.1314 | 22451491.9069 | 15323604.5585 | 68530564.8311 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100885039.8251 | 167802975.9285 | 749894.2093 | 41.5064 | 2430.5896 | 4042.8211 | 49.5509 | 82.4184
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9512 | 54.9738 | 10.3922 | 4 | 2427.2453 | 4037.0613 | 49.4827 | 82.301 | 201.0046 | 21.7258 | 116.1232 | 13140235.1424 | 0 | 5797706.3416 | 0 | 0 | 0 | 3192285.7194 | 8630788.6093 | 22455541.5433 | 15326368.5185 | 68542925.8746 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100897400.8685 | 167815336.972 | 1000000 | 41.5687 | 2427.2453 | 4037.0613 | 49.4827 | 82.301
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.1144 | 55.0288 | 10.4041 | 4 | 2424.7374 | 4032.7015 | 49.4316 | 82.2121 | 200.9826 | 21.7153 | 125.0893 | 13146447.7281 | 0 | 5801911.596 | 0 | 0 | 0 | 3185687.8184 | 8632278.3856 | 22459417.6355 | 15329014.0311 | 68554757.1948 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100909232.1888 | 167827168.2922 | 1333521.4322 | 41.6166 | 2424.7374 | 4032.7015 | 49.4316 | 82.2121
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.2265 | 55.0671 | 10.4128 | 4 | 2422.8567 | 4029.4799 | 49.3932 | 82.1464 | 200.9674 | 21.7081 | 125.1759 | 13150705.9127 | 0 | 5804799.1417 | 0 | 0 | 0 | 3180442.294 | 8633019.4659 | 22461345.7745 | 15330330.0256 | 68560642.6144 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100915117.6084 | 167833053.7118 | 1778279.41 | 41.6513 | 2422.8567 | 4029.4799 | 49.3932 | 82.1464
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.3191 | 55.0983 | 10.4196 | 4 | 2421.4464 | 4027.0266 | 49.3645 | 82.0964 | 200.9549 | 21.7021 | 121.7454 | 13154224.7282 | 0 | 5807185.272 | 0 | 0 | 0 | 3176722.9937 | 8633871.8676 | 22463563.5489 | 15331843.7022 | 68567412.1125 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100921887.1065 | 167839823.21 | 2371373.7057 | 41.6783 | 2421.4464 | 4027.0266 | 49.3645 | 82.0964
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.3728 | 55.1172 | 10.4242 | 4 | 2420.3887 | 4025.2576 | 49.3429 | 82.0603 | 200.9475 | 21.6987 | 116.1203 | 13156259.5357 | 0 | 5808569.1153 | 0 | 0 | 0 | 3173509.384 | 8633951.8337 | 22463771.6041 | 15331985.7042 | 68568047.177 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100922522.171 | 167840458.2745 | 3162277.6602 | 41.6968 | 2420.3887 | 4025.2576 | 49.3429 | 82.0603
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4239 | 55.1345 | 10.428 | 4 | 2419.5956 | 4023.883 | 49.3267 | 82.0323 | 200.9406 | 21.6954 | 126.629 | 13158199.1191 | 0 | 5809885.8486 | 0 | 0 | 0 | 3171382.3645 | 8634392.2595 | 22464917.5019 | 15332767.803 | 68571544.8966 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100926019.8906 | 167843955.9941 | 4216965.0343 | 41.7119 | 2419.5956 | 4023.883 | 49.3267 | 82.0323
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4628 | 55.1476 | 10.4308 | 4 | 2419.0008 | 4022.8498 | 49.3146 | 82.0112 | 200.9353 | 21.6929 | 129.4962 | 13159674.7277 | 0 | 5810887.8338 | 0 | 0 | 0 | 3169799.9031 | 8634741.3612 | 22465825.7929 | 15333387.7302 | 68574317.349 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100928792.343 | 167846728.4464 | 5623413.2519 | 41.7233 | 2419.0008 | 4022.8498 | 49.3146 | 82.0112
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4971 | 55.1589 | 10.4331 | 4 | 2418.5548 | 4022.0525 | 49.3055 | 81.995 | 200.9307 | 21.6906 | 121.1975 | 13160975.8038 | 0 | 5811770.4992 | 0 | 0 | 0 | 3168746.6557 | 8635182.2539 | 22466972.9052 | 15334170.6579 | 68577818.7758 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100932293.7698 | 167850229.8732 | 7498942.0933 | 41.7325 | 2418.5548 | 4022.0525 | 49.3055 | 81.995
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.5165 | 55.1656 | 10.4347 | 4 | 2418.2204 | 4021.4824 | 49.2987 | 81.9834 | 200.928 | 21.6894 | 122.8437 | 13161712.4498 | 0 | 5812271.4566 | 0 | 0 | 0 | 3167790.8079 | 8635292.1386 | 22467258.8026 | 15334365.7888 | 68578691.4443 | 961560.8286 | 31392914.1654 | 31392914.1654 | 23340719.2222 | 12184302.7159 | 0 | 100933166.4383 | 167851102.5417 | 10000000 | 41.7386 | 2418.2204 | 4021.4824 | 49.2987 | 81.9834
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4781 | 0.28751 | 0.030937 | 4 | 302143.6279 | 853960.6858 | 6159.6065 | 17409.1436 | 136.3391 | 24.8364 | 53.7559 | 604330.2919 | 0 | 246720.1643 | 0 | 0 | 0 | 561638.1791 | 550948.5678 | 1433455.1582 | 978362.6 | 4375454.9613 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 37390253.3652 | 105677576.6734 | 100 | 0.12375 | 302143.6279 | 853960.6858 | 6159.6065 | 17409.1436
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8035 | 0.57176 | 0.069122 | 4 | 140341.2393 | 387321.5823 | 2861.046 | 7896.0743 | 152.0289 | 25.5731 | 34.5619 | 831957.663 | 0 | 319432.8623 | 0 | 0 | 0 | 717360.6879 | 728812.9732 | 1896221.8561 | 1294210.3802 | 5787996.4227 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 38802794.8266 | 107090118.1348 | 133.3521 | 0.27649 | 140341.2393 | 387321.5823 | 2861.046 | 7896.0743
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4009 | 0.96312 | 0.12479 | 4 | 80831.8819 | 217641.4951 | 1647.8672 | 4436.9163 | 164.4797 | 26.0873 | 56.8566 | 1087729.7238 | 0 | 401907.24 | 0 | 0 | 0 | 877534.1714 | 923196.7427 | 2401968.5508 | 1639392.8914 | 7331729.3201 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 40346527.724 | 108633851.0322 | 177.8279 | 0.49914 | 80831.8819 | 217641.4951 | 1647.8672 | 4436.9163
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4427 | 1.4995 | 0.20254 | 4 | 52039.8137 | 136330.2001 | 1060.902 | 2779.2755 | 174.8881 | 26.4749 | 63.7013 | 1390744.6867 | 0 | 501555.6806 | 0 | 0 | 0 | 1060292.0405 | 1151511.039 | 2995995.5161 | 2044828.5013 | 9144927.4641 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 42159725.868 | 110447049.1762 | 237.1374 | 0.81014 | 52039.8137 | 136330.2001 | 1060.902 | 2779.2755
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9908 | 2.2036 | 0.30807 | 4 | 35888.3108 | 91303.6117 | 731.6318 | 1861.3476 | 183.2892 | 26.7607 | 51.9753 | 1740483.4145 | 0 | 619378.0103 | 0 | 0 | 0 | 1259393.5573 | 1411509.443 | 3672458.0302 | 2506528.0671 | 11209750.5223 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 44224548.9263 | 112511872.2345 | 316.2278 | 1.2323 | 35888.3108 | 91303.6117 | 731.6318 | 1861.3476
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.246 | 3.1288 | 0.4495 | 4 | 25946.9556 | 63926.7848 | 528.9638 | 1303.234 | 190.1721 | 26.9746 | 64.7342 | 2153701.7926 | 0 | 762231.1178 | 0 | 0 | 0 | 1487176.9487 | 1717212.845 | 4467835.574 | 3049389.5841 | 13637547.8622 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 46652346.2661 | 114939669.5743 | 421.6965 | 1.798 | 25946.9556 | 63926.7848 | 528.9638 | 1303.234
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3501 | 4.32 | 0.6365 | 4 | 19427.6628 | 46249.2287 | 396.0592 | 942.8531 | 195.687 | 27.1272 | 71.3997 | 2635794.1816 | 0 | 933348.1788 | 0 | 0 | 0 | 1741289.2506 | 2071068.3283 | 5388494.9557 | 3677758.5298 | 16447753.4248 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 49462551.8287 | 117749875.1369 | 562.3413 | 2.546 | 19427.6628 | 46249.2287 | 396.0592 | 942.8531
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5272 | 5.844 | 0.88154 | 4 | 14952.6695 | 34318.6148 | 304.8304 | 699.6314 | 200.0822 | 27.2268 | 54.6726 | 3199193.6537 | 0 | 1138644.2967 | 0 | 0 | 0 | 2026067.9564 | 2481923.3037 | 6457455.3237 | 4407345.9459 | 19710630.4801 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 52725428.884 | 121012752.1922 | 749.8942 | 3.5262 | 14952.6695 | 34318.6148 | 304.8304 | 699.6314
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30 | 7.7707 | 1.1992 | 4 | 11774.417 | 26010.2745 | 240.0374 | 530.2546 | 203.5343 | 27.2749 | 66.3098 | 3852597.8208 | 0 | 1383022.7577 | 0 | 0 | 0 | 2340560.8843 | 2954710.7705 | 7687551.3302 | 5246911.7463 | 23465355.3097 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 56480153.7137 | 124767477.0219 | 1000 | 4.7969 | 11774.417 | 26010.2745 | 240.0374 | 530.2546
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.0166 | 10.1788 | 1.6061 | 4 | 9457.9274 | 20087.2895 | 192.8126 | 409.5066 | 206.2014 | 27.2671 | 73.8212 | 4604108.5083 | 0 | 1671516.1452 | 0 | 0 | 0 | 2682877.9681 | 3493816.0224 | 9090192.6101 | 6204243.2412 | 27746754.4953 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 60761552.8992 | 129048876.2074 | 1333.5214 | 6.4244 | 9457.9274 | 20087.2895 | 192.8126 | 409.5066
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.7971 | 13.1419 | 2.1188 | 4 | 7736.2458 | 15793.4015 | 157.7138 | 321.9699 | 208.2038 | 27.1933 | 75.8324 | 5456328.8727 | 0 | 2007489.9225 | 0 | 0 | 0 | 3046362.5538 | 4098970.7261 | 10664681.0148 | 7278863.9299 | 32552697.0199 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 65567495.4238 | 133854818.732 | 1778.2794 | 8.4754 | 7736.2458 | 15793.4015 | 157.7138 | 321.9699
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.4165 | 16.6942 | 2.7491 | 4 | 6438.8363 | 12648.7997 | 131.2644 | 257.8629 | 209.6172 | 27.0381 | 91.953 | 6397882.1926 | 0 | 2389230.8082 | 0 | 0 | 0 | 3413794.7257 | 4758354.0133 | 12380261.0701 | 8449782.5693 | 37789305.3792 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 70804103.7831 | 139091427.0913 | 2371.3737 | 10.9964 | 6438.8363 | 12648.7997 | 131.2644 | 257.8629
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.7345 | 20.8055 | 3.4972 | 4 | 5453.2301 | 10334.8163 | 111.1715 | 210.6892 | 210.4844 | 26.7846 | 85.0891 | 7401415.01 | 0 | 2808825.737 | 0 | 0 | 0 | 3759913.7131 | 5448360.2395 | 14175515.7307 | 9675080.7639 | 43269111.1943 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 76283909.5982 | 144571232.9064 | 3162.2777 | 13.9888 | 5453.2301 | 10334.8163 | 111.1715 | 210.6892
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.2265 | 25.3275 | 4.3425 | 4 | 4702.5276 | 8633.8444 | 95.8674 | 176.0126 | 210.8303 | 26.4246 | 87.0753 | 8416297.2613 | 0 | 3248262.6388 | 0 | 0 | 0 | 4048885.2185 | 6128243.5962 | 15944432.7618 | 10882402.9853 | 48668524.4619 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 81683322.8659 | 149970646.1741 | 4216.965 | 17.3701 | 4702.5276 | 8633.8444 | 95.8674 | 176.0126
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0908 | 30.0182 | 5.2433 | 4 | 4131.5871 | 7387.5246 | 84.228 | 150.6047 | 210.7095 | 25.9679 | 97.6057 | 9383469.0895 | 0 | 3684016.8681 | 0 | 0 | 0 | 4250331.0765 | 6753948.6433 | 17572388.9445 | 11993516.5311 | 53637671.153 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 86652469.5569 | 154939792.8651 | 5623.4133 | 20.9732 | 4131.5871 | 7387.5246 | 84.228 | 150.6047
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4144 | 34.5905 | 6.1441 | 4 | 3698.965 | 6477.5348 | 75.4084 | 132.0533 | 210.2249 | 25.4453 | 78.3522 | 10250120.2871 | 0 | 4092019.9421 | 0 | 0 | 0 | 4349435.1457 | 7289714.3962 | 18966341.5329 | 12944917.8155 | 57892549.1195 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 90907347.5234 | 159194670.8316 | 7498.9421 | 24.5764 | 3698.965 | 6477.5348 | 75.4084 | 132.0533
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.4159 | 38.7884 | 6.9908 | 4 | 3372.528 | 5814.5602 | 68.7535 | 118.5377 | 209.5131 | 24.9012 | 82.5003 | 10983536.2789 | 0 | 4453714.1839 | 0 | 0 | 0 | 4351983.0123 | 7717801.0553 | 20080135.2072 | 13705104.8844 | 61292274.6219 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 94307073.0258 | 162594396.334 | 10000 | 27.9633 | 3372.528 | 5814.5602 | 68.7535 | 118.5377
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.5897 | 42.4373 | 7.7432 | 4 | 3127.0812 | 5331.838 | 63.7498 | 108.6967 | 208.7105 | 24.3801 | 83.4744 | 11573950.8064 | 0 | 4758774.0786 | 0 | 0 | 0 | 4278897.9125 | 8038532.891 | 20914613.6525 | 14274653.5702 | 63839422.9111 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 96854221.315 | 165141544.6232 | 13335.2143 | 30.9727 | 3127.0812 | 5331.838 | 63.7498 | 108.6967
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8346 | 45.4869 | 8.3831 | 4 | 2942.9575 | 4979.4067 | 59.9962 | 101.5119 | 207.918 | 23.9111 | 86.6814 | 12034443.2792 | 0 | 5007511.0947 | 0 | 0 | 0 | 4160718.4182 | 8269042.3889 | 21514352.0821 | 14683987.3718 | 65670054.6349 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 98684853.0388 | 166972176.347 | 17782.7941 | 33.5325 | 2942.9575 | 4979.4067 | 59.9962 | 101.5119
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.225 | 47.9478 | 8.9081 | 4 | 2804.9941 | 4721.4381 | 57.1836 | 96.2529 | 207.2014 | 23.5113 | 116.1034 | 12384057.2328 | 0 | 5204148.3563 | 0 | 0 | 0 | 4022428.7868 | 8428147.4066 | 21928310.7013 | 14966522.6353 | 66933615.1191 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 99948413.523 | 168235736.8312 | 23713.7371 | 35.6323 | 2804.9941 | 4721.4381 | 57.1836 | 96.2529
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0381 | 49.898 | 9.3288 | 4 | 2701.6145 | 4531.6343 | 55.0761 | 92.3835 | 206.585 | 23.1804 | 122.6221 | 12647177.1169 | 0 | 5357516.9335 | 0 | 0 | 0 | 3884420.8673 | 8536754.8179 | 22210884.9069 | 15159385.337 | 67796139.9793 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 100810938.3833 | 169098261.6915 | 31622.7766 | 37.3151 | 2701.6145 | 4531.6343 | 55.0761 | 92.3835
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.5151 | 51.4102 | 9.6588 | 4 | 2624.2036 | 4391.6895 | 53.4979 | 89.5305 | 206.079 | 22.9165 | 121.4506 | 12842696.197 | 0 | 5474890.5079 | 0 | 0 | 0 | 3757473.3048 | 8609273.4038 | 22399563.3918 | 15288162.2799 | 68372059.0852 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 101386857.4891 | 169674180.7973 | 42169.6503 | 38.6353 | 2624.2036 | 4391.6895 | 53.4979 | 89.5305
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.9575 | 52.5783 | 9.9153 | 4 | 2566.1971 | 4287.9693 | 52.3154 | 87.4161 | 205.671 | 22.7078 | 124.7357 | 12988694.8436 | 0 | 5564714.5934 | 0 | 0 | 0 | 3647976.9091 | 8658540.675 | 22527746.7254 | 15375650.039 | 68763323.7855 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 101778122.1894 | 170065445.4976 | 56234.1325 | 39.6611 | 2566.1971 | 4287.9693 | 52.3154 | 87.4161
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5593 | 53.4656 | 10.1118 | 4 | 2522.7193 | 4211.022 | 51.429 | 85.8474 | 205.3514 | 22.5467 | 105.9603 | 13096490.2853 | 0 | 5632362.8227 | 0 | 0 | 0 | 3556195.0809 | 8691168.7937 | 22612638.3973 | 15433590.3494 | 69022445.7293 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102037244.1333 | 170324567.4415 | 74989.4209 | 40.4473 | 2522.7193 | 4211.022 | 51.429 | 85.8474
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5271 | 54.1389 | 10.2618 | 4 | 2490.1244 | 4153.7529 | 50.7646 | 84.6799 | 205.1032 | 22.4229 | 81.1846 | 13176546.1123 | 0 | 5683393.5353 | 0 | 0 | 0 | 3481749.6818 | 8713258.8385 | 22670112.1625 | 15472817.3752 | 69197877.7056 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102212676.1095 | 170499999.4177 | 100000 | 41.0472 | 2490.1244 | 4153.7529 | 50.7646 | 84.6799
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.0204 | 54.6507 | 10.376 | 4 | 2465.6847 | 4111.0099 | 50.2663 | 83.8085 | 204.9111 | 22.3278 | 84.2724 | 13236440.0714 | 0 | 5722040.1314 | 0 | 0 | 0 | 3422831.2678 | 8728711.4736 | 22710316.7493 | 15500257.8317 | 69320597.5253 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102335395.9292 | 170622719.2374 | 133352.1432 | 41.5038 | 2465.6847 | 4111.0099 | 50.2663 | 83.8085
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1413 | 55.0359 | 10.4623 | 4 | 2447.3582 | 4079.1115 | 49.8927 | 83.1582 | 204.7647 | 22.2558 | 87.4385 | 13280910.6315 | 0 | 5751008.4463 | 0 | 0 | 0 | 3376582.7142 | 8739315.6989 | 22737906.7683 | 15519088.5867 | 69404812.8459 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102419611.2498 | 170706934.558 | 177827.941 | 41.849 | 2447.3582 | 4079.1115 | 49.8927 | 83.1582
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.987 | 55.3268 | 10.5275 | 4 | 2433.6152 | 4055.2563 | 49.6125 | 82.6719 | 204.6531 | 22.2011 | 123.567 | 13314183.3619 | 0 | 5772839.9079 | 0 | 0 | 0 | 3340832.6771 | 8746863.8193 | 22757545.4293 | 15532492.3763 | 69464757.5717 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102479555.9757 | 170766879.2839 | 237137.3706 | 42.11 | 2433.6152 | 4055.2563 | 49.6125 | 82.6719
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.6151 | 55.5435 | 10.5765 | 4 | 2423.309 | 4037.4447 | 49.4024 | 82.3088 | 204.5694 | 22.1603 | 118.9632 | 13338735.0404 | 0 | 5789039.9755 | 0 | 0 | 0 | 3313159.3484 | 8751964.4021 | 22770816.0995 | 15541549.8814 | 69505264.7472 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102520063.1511 | 170807386.4593 | 316227.766 | 42.3058 | 2423.309 | 4037.4447 | 49.4024 | 82.3088
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.1 | 55.7103 | 10.6137 | 4 | 2415.5802 | 4024.0526 | 49.2449 | 82.0358 | 204.5045 | 22.1287 | 124.5552 | 13357603.7646 | 0 | 5801540.0273 | 0 | 0 | 0 | 3292392.8438 | 8756099.2879 | 22781574.2242 | 15548892.5225 | 69538102.6702 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102552901.0741 | 170840224.3823 | 421696.5034 | 42.4548 | 2415.5802 | 4024.0526 | 49.2449 | 82.0358
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.4628 | 55.8352 | 10.6417 | 4 | 2409.7842 | 4014.0295 | 49.1267 | 81.8314 | 204.4557 | 22.105 | 130.8587 | 13371668.1841 | 0 | 5810887.8338 | 0 | 0 | 0 | 3276569.2386 | 8759058.85 | 22789274.3977 | 15554148.0492 | 69561606.5534 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102576404.9573 | 170863728.2655 | 562341.3252 | 42.5666 | 2409.7842 | 4014.0295 | 49.1267 | 81.8314
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.7212 | 55.9249 | 10.6623 | 4 | 2405.4377 | 4006.5828 | 49.0381 | 81.6796 | 204.4208 | 22.088 | 123.6542 | 13381652.6142 | 0 | 5817542.7824 | 0 | 0 | 0 | 3264202.926 | 8760725.3458 | 22793610.2779 | 15557107.3765 | 69574841.3227 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102589639.7266 | 170876963.0348 | 749894.2093 | 42.6491 | 2405.4377 | 4006.5828 | 49.0381 | 81.6796
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.9186 | 55.9933 | 10.6778 | 4 | 2402.1781 | 4000.9869 | 48.9717 | 81.5655 | 204.394 | 22.0751 | 121.6879 | 13389267.789 | 0 | 5822626.7029 | 0 | 0 | 0 | 3254957.5193 | 8762072.2843 | 22797114.7357 | 15559499.241 | 69585538.2721 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102600336.676 | 170887659.9842 | 1000000 | 42.7114 | 2402.1781 | 4000.9869 | 48.9717 | 81.5655
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.0696 | 56.0454 | 10.6896 | 4 | 2399.7338 | 3996.7804 | 48.9218 | 81.4798 | 204.3735 | 22.0651 | 82.465 | 13395082.1201 | 0 | 5826512.9903 | 0 | 0 | 0 | 3248061.9187 | 8763166.2414 | 22799960.9875 | 15561441.8663 | 69594226.1242 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102609024.5282 | 170896347.8363 | 1333521.4322 | 42.7585 | 2399.7338 | 3996.7804 | 48.9218 | 81.4798
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.1887 | 56.0863 | 10.6986 | 4 | 2397.9007 | 3993.6014 | 48.8844 | 81.415 | 204.3574 | 22.0573 | 74.8552 | 13399666.5903 | 0 | 5829579.155 | 0 | 0 | 0 | 3243027.0818 | 8764186.4025 | 22802615.2376 | 15563253.4465 | 69602327.9136 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102617126.3175 | 170904449.6257 | 1778279.41 | 42.7946 | 2397.9007 | 3993.6014 | 48.8844 | 81.415
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.2741 | 56.1158 | 10.7053 | 4 | 2396.5261 | 3991.2358 | 48.8564 | 81.3667 | 204.3458 | 22.0517 | 76.1868 | 13402948.3105 | 0 | 5831776.6079 | 0 | 0 | 0 | 3239131.9149 | 8764804.165 | 22804222.5287 | 15564350.4557 | 69607233.9826 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102622032.3865 | 170909355.6947 | 2371373.7057 | 42.8212 | 2396.5261 | 3991.2358 | 48.8564 | 81.3667
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.3324 | 56.1362 | 10.7101 | 4 | 2395.4953 | 3989.4873 | 48.8354 | 81.3311 | 204.3378 | 22.0478 | 82.1801 | 13405187.6076 | 0 | 5833278.1573 | 0 | 0 | 0 | 3236050.927 | 8765061.5099 | 22804892.0873 | 15564807.4433 | 69609277.7324 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102624076.1363 | 170911399.4445 | 3162277.6602 | 42.8404 | 2395.4953 | 3989.4873 | 48.8354 | 81.3311
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.3861 | 56.1545 | 10.714 | 4 | 2394.7223 | 3988.1326 | 48.8197 | 81.3035 | 204.3305 | 22.0443 | 81.3119 | 13407251.7779 | 0 | 5834660.4507 | 0 | 0 | 0 | 3234004.0496 | 8765607.3485 | 22806312.2475 | 15565776.7317 | 69613612.6058 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102628411.0098 | 170915734.3179 | 4216965.0343 | 42.8561 | 2394.7223 | 3988.1326 | 48.8197 | 81.3035
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.425 | 56.1678 | 10.7169 | 4 | 2394.1426 | 3987.123 | 48.8078 | 81.2829 | 204.3253 | 22.0417 | 110.9553 | 13408745.4948 | 0 | 5835661.3706 | 0 | 0 | 0 | 3232429.4968 | 8765966.1813 | 22807245.8568 | 15566413.9393 | 69616462.3396 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102631260.7435 | 170918584.0517 | 5623413.2519 | 42.8676 | 2394.1426 | 3987.123 | 48.8078 | 81.2829
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.4593 | 56.1792 | 10.7192 | 4 | 2393.7079 | 3986.3436 | 48.799 | 81.267 | 204.3206 | 22.0395 | 110.1879 | 13410062.5299 | 0 | 5836543.0979 | 0 | 0 | 0 | 3231384.1618 | 8766416.018 | 22808416.2395 | 15567212.7496 | 69620034.7967 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102634833.2006 | 170922156.5088 | 7498942.0933 | 42.8769 | 2393.7079 | 3986.3436 | 48.799 | 81.267
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.4787 | 56.186 | 10.7208 | 4 | 2393.3819 | 3985.7866 | 48.7923 | 81.2557 | 204.318 | 22.0382 | 111.445 | 13410808.2189 | 0 | 5837043.5229 | 0 | 0 | 0 | 3230431.8429 | 8766530.5981 | 22808714.3535 | 15567416.2184 | 69620944.7547 | 961560.8286 | 32053237.5753 | 32053237.5753 | 23812626.8141 | 12421458.9187 | 0 | 102635743.1586 | 170923066.4668 | 10000000 | 42.8831 | 2393.3819 | 3985.7866 | 48.7923 | 81.2557
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5512 | 0.29802 | 0.032674 | 4 | 292124.9122 | 825202.3548 | 5955.3615 | 16822.8662 | 138.4902 | 25.2941 | 49.9177 | 623042.6471 | 0 | 250863.3302 | 0 | 0 | 0 | 578426.6912 | 566409.7407 | 1473681.9587 | 1005818.2179 | 4498242.5858 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 38179224.4905 | 107849706.2169 | 100 | 0.13069 | 292124.9122 | 825202.3548 | 5955.3615 | 16822.8662
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8935 | 0.59012 | 0.072624 | 4 | 136379.8247 | 376212.8393 | 2780.2872 | 7669.6076 | 154.3668 | 26.0355 | 49.6383 | 855831.0598 | 0 | 324212.3747 | 0 | 0 | 0 | 736746.1354 | 747547.9322 | 1944966.3765 | 1327479.5171 | 5936783.3957 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 39617765.3004 | 109288247.0269 | 133.3521 | 0.2905 | 136379.8247 | 376212.8393 | 2780.2872 | 7669.6076
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5324 | 0.99587 | 0.13081 | 4 | 78770.952 | 211924.9429 | 1605.8524 | 4320.3766 | 167.1295 | 26.5596 | 61.0466 | 1120750.3325 | 0 | 408499.4989 | 0 | 0 | 0 | 903399.5605 | 948733.2628 | 2468409.3379 | 1684740.0939 | 7534532.0864 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 41215513.9911 | 110885995.7176 | 177.8279 | 0.52323 | 78770.952 | 211924.9429 | 1605.8524 | 4320.3766
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6083 | 1.5486 | 0.21194 | 4 | 50803.3846 | 132983.352 | 1035.6957 | 2711.0455 | 177.6923 | 26.9505 | 57.2831 | 1431699.6924 | 0 | 509410.4528 | 0 | 0 | 0 | 1090310.9539 | 1182254.2286 | 3075982.9892 | 2099421.5952 | 9389079.912 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 43070061.8167 | 112740543.5431 | 237.1374 | 0.84778 | 50803.3846 | 132983.352 | 1035.6957 | 2711.0455
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2077 | 2.2757 | 0.32206 | 4 | 35080.0071 | 89162.1532 | 715.1534 | 1817.6911 | 186.2492 | 27.2398 | 54.2863 | 1791822.7034 | 0 | 629136.7203 | 0 | 0 | 0 | 1295329.8786 | 1449352.8279 | 3770918.7551 | 2573729.535 | 11510290.4202 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 45191272.3249 | 114861754.0514 | 316.2278 | 1.2882 | 35080.0071 | 89162.1532 | 715.1534 | 1817.6911
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5233 | 3.2302 | 0.46953 | 4 | 25387.1047 | 62482.8306 | 517.5505 | 1273.797 | 193.2475 | 27.4556 | 72.0742 | 2216652.203 | 0 | 774075.8772 | 0 | 0 | 0 | 1529154.6522 | 1762754.2657 | 4586325.0087 | 3130261.058 | 13999223.0648 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 47680204.9695 | 117350686.6959 | 421.6965 | 1.8781 | 25387.1047 | 62482.8306 | 517.5505 | 1273.797
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.7009 | 4.4585 | 0.66443 | 4 | 19023.3797 | 45237.6731 | 387.8173 | 922.2312 | 198.853 | 27.6091 | 61.1086 | 2712028.8064 | 0 | 947596.0854 | 0 | 0 | 0 | 1789719.5689 | 2125244.3397 | 5529449.8243 | 3773963.1239 | 16878001.7487 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 50558983.6534 | 120229465.3798 | 562.3413 | 2.6577 | 19023.3797 | 45237.6731 | 387.8173 | 922.2312
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9649 | 6.0283 | 0.91966 | 4 | 14651.2933 | 33590.4537 | 298.6864 | 684.7868 | 203.3179 | 27.7084 | 82.5646 | 3290377.1166 | 0 | 1155561.3282 | 0 | 0 | 0 | 2081118.803 | 2545552.3266 | 6623004.9893 | 4520336.9944 | 20215951.5581 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 53896933.4628 | 123567415.1892 | 749.8942 | 3.6786 | 14651.2933 | 33590.4537 | 298.6864 | 684.7868
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.5498 | 8.0138 | 1.2505 | 4 | 11543.9976 | 25473.0164 | 235.34 | 519.3019 | 206.8282 | 27.7549 | 53.4195 | 3961522.7517 | 0 | 1403262.8425 | 0 | 0 | 0 | 2403401.7802 | 3029593.076 | 7882379.7288 | 5379886.1316 | 24060046.3108 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 57741028.2155 | 127411509.942 | 1000 | 5.0018 | 11543.9976 | 25473.0164 | 235.34 | 519.3019
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.7056 | 10.4956 | 1.674 | 4 | 9278.0558 | 19683.0267 | 189.1457 | 401.2651 | 209.5412 | 27.7438 | 65.8489 | 4733491.778 | 0 | 1695708.4759 | 0 | 0 | 0 | 2754357.3006 | 3581587.4463 | 9318555.8505 | 6360105.8452 | 28443806.6965 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 62124788.6012 | 131795270.3276 | 1333.5214 | 6.6959 | 9278.0558 | 19683.0267 | 189.1457 | 401.2651
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.6519 | 13.5481 | 2.2073 | 4 | 7593.3634 | 15484.3129 | 154.801 | 315.6687 | 211.5769 | 27.664 | 74.6687 | 5608514.4071 | 0 | 2036160.1298 | 0 | 0 | 0 | 3126824.0114 | 4200884.4338 | 10929839.577 | 7459840.097 | 33362062.6562 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 67043044.5609 | 136713526.2873 | 1778.2794 | 8.8292 | 7593.3634 | 15484.3129 | 154.801 | 315.6687
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.4371 | 17.1991 | 2.8616 | 4 | 6323.6564 | 12410.2697 | 128.9163 | 253.0001 | 213.0092 | 27.4997 | 84.0716 | 6572656.386 | 0 | 2422005.5831 | 0 | 0 | 0 | 3501188.307 | 4873381.6077 | 12679539.2752 | 8654046.0938 | 38702817.2527 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 72383799.1574 | 142054280.8838 | 2371.3737 | 11.4465 | 6323.6564 | 12410.2697 | 128.9163 | 253.0001
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.9083 | 21.414 | 3.6364 | 4 | 5359.2001 | 10148.9478 | 109.2545 | 206.9 | 213.8836 | 27.2339 | 94.7477 | 7597410.2679 | 0 | 2845031.5124 | 0 | 0 | 0 | 3851710.0663 | 5574719.2202 | 14504275.8788 | 9899466.3203 | 44272613.2659 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 77953595.1706 | 147624076.8971 | 3162.2777 | 14.5458 | 5359.2001 | 10148.9478 | 109.2545 | 206.9
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.5345 | 26.0399 | 4.5097 | 4 | 4624.8437 | 8487.0926 | 94.2837 | 173.0209 | 214.2271 | 26.8585 | 90.7834 | 8631340.3887 | 0 | 3287172.097 | 0 | 0 | 0 | 4142757.3746 | 6263895.2455 | 16297370.5272 | 11123290.2623 | 49745825.8954 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 83426807.8001 | 153097289.5265 | 4216.965 | 18.0388 | 4624.8437 | 8487.0926 | 94.2837 | 173.0209
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4797 | 30.8211 | 5.4369 | 4 | 4066.5883 | 7270.1555 | 82.9029 | 148.212 | 214.0979 | 26.3852 | 109.9741 | 9612835.9123 | 0 | 3724058.9945 | 0 | 0 | 0 | 4342734.2147 | 6895055.3574 | 17939519.6696 | 12244090.7948 | 54758294.9433 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 88439276.848 | 158109758.5745 | 5623.4133 | 21.7478 | 4066.5883 | 7270.1555 | 82.9029 | 148.212
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.8176 | 35.4622 | 6.3605 | 4 | 3643.7884 | 6382.1735 | 74.2836 | 130.1092 | 213.6046 | 25.8471 | 109.9151 | 10488434.9954 | 0 | 4131431.666 | 0 | 0 | 0 | 4437318.1547 | 7432302.0783 | 19337325.4329 | 13198121.9503 | 59024934.2775 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 92705916.1822 | 162376397.9087 | 7498.9421 | 25.4422 | 3643.7884 | 6382.1735 | 74.2836 | 130.1092
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8092 | 39.7156 | 7.2263 | 4 | 3324.9138 | 5735.2135 | 67.7829 | 116.9201 | 212.8857 | 25.2887 | 123.099 | 11228176.2967 | 0 | 4492032.3448 | 0 | 0 | 0 | 4435297.4974 | 7860647.3942 | 20451792.0792 | 13958768.3364 | 62426713.9487 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 96107695.8534 | 165778177.5799 | 10000 | 28.9053 | 3324.9138 | 5735.2135 | 67.7829 | 116.9201
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9392 | 43.4017 | 7.9932 | 4 | 3085.25 | 5264.2984 | 62.897 | 107.3198 | 212.0797 | 24.7564 | 121.0064 | 11821871.9504 | 0 | 4795282.329 | 0 | 0 | 0 | 4357359.6566 | 8180060.435 | 21282839.2909 | 14525975.1346 | 64963388.7966 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 98644370.7013 | 168314852.4277 | 13335.2143 | 31.9729 | 3085.25 | 5264.2984 | 62.897 | 107.3198
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.1233 | 46.4744 | 8.6438 | 4 | 2905.5218 | 4920.5536 | 59.233 | 100.3121 | 211.2872 | 24.2792 | 129.5799 | 12283787.5941 | 0 | 5041937.4367 | 0 | 0 | 0 | 4234835.7211 | 8408618.6932 | 21877500.9949 | 14931843.9667 | 66778524.4067 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 100459506.3114 | 170129988.0379 | 17782.7941 | 34.5754 | 2905.5218 | 4920.5536 | 59.233 | 100.3121
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.4554 | 48.9508 | 9.1766 | 4 | 2770.8842 | 4668.9303 | 56.4882 | 95.1825 | 210.5724 | 23.8732 | 91.3891 | 12634106.3181 | 0 | 5236703.6659 | 0 | 0 | 0 | 4093249.9807 | 8565983.3862 | 22286931.6461 | 15211288.7991 | 68028263.7959 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 101709245.7006 | 171379727.4271 | 23713.7371 | 36.7064 | 2770.8842 | 4668.9303 | 56.4882 | 95.1825
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.2024 | 50.907 | 9.6026 | 4 | 2670.0135 | 4483.867 | 54.4318 | 91.4097 | 209.9601 | 23.5386 | 79.8427 | 12896904.4512 | 0 | 5388102.3843 | 0 | 0 | 0 | 3952363.2434 | 8672574.3308 | 22564259.4191 | 15400570.7027 | 68874774.5314 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 102555756.4361 | 172226238.1626 | 31622.7766 | 38.4102 | 2670.0135 | 4483.867 | 54.4318 | 91.4097
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.6406 | 52.4274 | 9.9369 | 4 | 2594.4923 | 4347.3204 | 52.8922 | 88.626 | 209.4565 | 23.2712 | 82.961 | 13092784.658 | 0 | 5504300.216 | 0 | 0 | 0 | 3823916.8747 | 8744190.682 | 22750590.4744 | 15527745.4767 | 69443528.3818 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 103124510.2865 | 172794992.0129 | 42169.6503 | 39.7475 | 2594.4923 | 4347.3204 | 52.8922 | 88.626
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0272 | 53.5939 | 10.1957 | 4 | 2537.9077 | 4246.2396 | 51.7387 | 86.5653 | 209.0537 | 23.0614 | 76.5419 | 13237966.8644 | 0 | 5592551.0692 | 0 | 0 | 0 | 3712642.3007 | 8791832.4914 | 22874544.6898 | 15612346.7757 | 69821884.1912 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 103502866.0959 | 173173347.8224 | 56234.1325 | 40.7828 | 2537.9077 | 4246.2396 | 51.7387 | 86.5653
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6038 | 54.4849 | 10.3945 | 4 | 2495.4989 | 4171.1527 | 50.8741 | 85.0346 | 208.7362 | 22.8984 | 107.4926 | 13345909.6556 | 0 | 5659463.8845 | 0 | 0 | 0 | 3620185.0527 | 8823967.8512 | 22958154.304 | 15669412.0554 | 70077092.8033 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 103758074.708 | 173428556.4345 | 74989.4209 | 41.5781 | 2495.4989 | 4171.1527 | 50.8741 | 85.0346
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5601 | 55.1634 | 10.5464 | 4 | 2463.7075 | 4115.2293 | 50.226 | 83.8945 | 208.4888 | 22.7728 | 127.5303 | 13426392.5454 | 0 | 5710134.6505 | 0 | 0 | 0 | 3545522.0665 | 8845999.2123 | 23015475.3865 | 15708534.872 | 70252058.7333 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 103933040.638 | 173603522.3645 | 100000 | 42.1856 | 2463.7075 | 4115.2293 | 50.226 | 83.8945
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.0144 | 55.6701 | 10.6611 | 4 | 2439.8714 | 4073.6293 | 49.7401 | 83.0464 | 208.3011 | 22.6782 | 127.5045 | 13485385.6643 | 0 | 5747731.4287 | 0 | 0 | 0 | 3485609.6478 | 8860303.4289 | 23052692.0239 | 15733935.9918 | 70365658.1854 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104046640.0901 | 173717121.8165 | 133352.1432 | 42.6443 | 2439.8714 | 4073.6293 | 49.7401 | 83.0464
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.1398 | 56.0614 | 10.7488 | 4 | 2421.9983 | 4042.4267 | 49.3757 | 82.4103 | 208.1539 | 22.6045 | 124.4355 | 13530553.7886 | 0 | 5776782.381 | 0 | 0 | 0 | 3439616.6273 | 8871311.5908 | 23081333.0031 | 15753484.0486 | 70453081.4394 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104134063.3442 | 173804545.0706 | 177827.941 | 42.9951 | 2421.9983 | 4042.4267 | 49.3757 | 82.4103
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9707 | 56.3516 | 10.8145 | 4 | 2408.5957 | 4019.1742 | 49.1025 | 81.9363 | 208.0439 | 22.5496 | 118.862 | 13563620.2518 | 0 | 5798207.6024 | 0 | 0 | 0 | 3403556.2191 | 8878499.7886 | 23100035.2192 | 15766248.6954 | 70510167.7765 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104191149.6813 | 173861631.4077 | 237137.3706 | 43.258 | 2408.5957 | 4019.1742 | 49.1025 | 81.9363
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.5897 | 56.5683 | 10.8639 | 4 | 2398.5451 | 4001.8031 | 48.8976 | 81.5822 | 207.9612 | 22.5086 | 117.8494 | 13588098.3861 | 0 | 5814155.9139 | 0 | 0 | 0 | 3375716.1899 | 8883408.4911 | 23112806.6561 | 15774965.4635 | 70549151.1005 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104230133.0052 | 173900614.7316 | 316227.766 | 43.4556 | 2398.5451 | 4001.8031 | 48.8976 | 81.5822
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.065 | 56.7342 | 10.9014 | 4 | 2391.008 | 3988.7538 | 48.7439 | 81.3161 | 207.8975 | 22.4769 | 123.4514 | 13606807.0593 | 0 | 5826393.7887 | 0 | 0 | 0 | 3354757.3424 | 8887303.6942 | 23122941.1757 | 15781882.4814 | 70580085.5416 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104261067.4464 | 173931549.1728 | 421696.5034 | 43.6055 | 2391.008 | 3988.7538 | 48.7439 | 81.3161
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.423 | 56.8593 | 10.9296 | 4 | 2385.3559 | 3978.9762 | 48.6287 | 81.1168 | 207.8492 | 22.453 | 112.6915 | 13620850.6008 | 0 | 5835609.1695 | 0 | 0 | 0 | 3338862.0188 | 8890175.4977 | 23130413.0194 | 15786982.1682 | 70602892.4744 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104283874.3791 | 173954356.1056 | 562341.3252 | 43.7184 | 2385.3559 | 3978.9762 | 48.6287 | 81.1168
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.6808 | 56.9499 | 10.9505 | 4 | 2381.1173 | 3971.6993 | 48.5423 | 80.9685 | 207.8142 | 22.4358 | 121.057 | 13630931.4298 | 0 | 5842242.3155 | 0 | 0 | 0 | 3326521.0151 | 8891880.9566 | 23134850.2734 | 15790010.6852 | 70616436.6757 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104297418.5804 | 173967900.3069 | 749894.2093 | 43.8019 | 2381.1173 | 3971.6993 | 48.5423 | 80.9685
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.8855 | 57.0213 | 10.9665 | 4 | 2377.9388 | 3966.1975 | 48.4775 | 80.8563 | 207.7865 | 22.4221 | 120.8924 | 13638921.86 | 0 | 5847506.8716 | 0 | 0 | 0 | 3317506.7788 | 8893534.849 | 23139153.3623 | 15792947.6319 | 70629571.3536 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104310553.2583 | 173981034.9847 | 1000000 | 43.866 | 2377.9388 | 3966.1975 | 48.4775 | 80.8563
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.0272 | 57.0714 | 10.9782 | 4 | 2375.5552 | 3962.1257 | 48.4289 | 80.7733 | 207.7672 | 22.4126 | 111.6148 | 13644441.3114 | 0 | 5851150.8701 | 0 | 0 | 0 | 3310383.5883 | 8894330.5503 | 23141223.6137 | 15794360.621 | 70635890.5548 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104316872.4595 | 173987354.186 | 1333521.4322 | 43.9126 | 2375.5552 | 3962.1257 | 48.4289 | 80.7733
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.1413 | 57.1112 | 10.9871 | 4 | 2373.7677 | 3959.0396 | 48.3925 | 80.7104 | 207.7517 | 22.4049 | 125.6314 | 13648883.1033 | 0 | 5854084.4834 | 0 | 0 | 0 | 3305233.5778 | 8895198.4542 | 23143481.7217 | 15795901.8261 | 70642783.1665 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104323765.0712 | 173994246.7977 | 1778279.41 | 43.9486 | 2373.7677 | 3959.0396 | 48.3925 | 80.7104
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.2144 | 57.1375 | 10.9935 | 4 | 2372.4272 | 3956.78 | 48.3651 | 80.6643 | 207.7416 | 22.4 | 121.7927 | 13651725.0415 | 0 | 5855965.5674 | 0 | 0 | 0 | 3301020.5762 | 8895397.3622 | 23143999.2395 | 15796255.0426 | 70644362.8294 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104325344.7341 | 173995826.4605 | 2371373.7057 | 43.9741 | 2372.4272 | 3956.78 | 48.3651 | 80.6643
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.2876 | 57.1626 | 10.9989 | 4 | 2371.422 | 3955.0066 | 48.3446 | 80.6282 | 207.7317 | 22.3951 | 118.4279 | 13654572.2472 | 0 | 5857846.5003 | 0 | 0 | 0 | 3298353.2056 | 8896201.0617 | 23146090.3008 | 15797682.2349 | 70650745.5505 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104331727.4552 | 174002209.1816 | 3162277.6602 | 43.9954 | 2371.422 | 3955.0066 | 48.3446 | 80.6282
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.3413 | 57.1811 | 11.0028 | 4 | 2370.6683 | 3953.6821 | 48.3293 | 80.6012 | 207.7244 | 22.3915 | 105.1335 | 13656661.0852 | 0 | 5859227.3422 | 0 | 0 | 0 | 3296317.2347 | 8896760.2082 | 23147545.0854 | 15798675.1553 | 70655186.111 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104336168.0157 | 174006649.7422 | 4216965.0343 | 44.0113 | 2370.6683 | 3953.6821 | 48.3293 | 80.6012
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.3756 | 57.1931 | 11.0056 | 4 | 2370.103 | 3952.715 | 48.3178 | 80.5814 | 207.7197 | 22.3892 | 114.148 | 13657991.2962 | 0 | 5860108.1817 | 0 | 0 | 0 | 3294624.2797 | 8896962.2654 | 23148070.7968 | 15799033.9641 | 70656790.7838 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104337772.6885 | 174008254.415 | 5623413.2519 | 44.0225 | 2370.103 | 3952.715 | 48.3178 | 80.5814
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.3996 | 57.2017 | 11.0077 | 4 | 2369.6791 | 3951.9969 | 48.3091 | 80.5668 | 207.7164 | 22.3875 | 119.1276 | 13658925.2243 | 0 | 5860727.1301 | 0 | 0 | 0 | 3293309.4578 | 8897055.1067 | 23148312.3508 | 15799198.8297 | 70657528.0994 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104338510.0041 | 174008991.7306 | 7498942.0933 | 44.0306 | 2369.6791 | 3951.9969 | 48.3091 | 80.5668
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.4191 | 57.2086 | 11.0092 | 4 | 2369.3612 | 3951.4524 | 48.3026 | 80.5557 | 207.7138 | 22.3862 | 121.6166 | 13659679.9262 | 0 | 5861227.0381 | 0 | 0 | 0 | 3292360.6498 | 8897174.3695 | 23148622.6481 | 15799410.6139 | 70658475.2456 | 961560.8286 | 32719421.0761 | 32719421.0761 | 24290101.4924 | 12660959.158 | 0 | 104339457.1503 | 174009938.8768 | 10000000 | 44.037 | 2369.3612 | 3951.4524 | 48.3026 | 80.5557
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6413 | 0.31087 | 0.034502 | 4 | 282578.913 | 797528.5611 | 5760.7534 | 16258.6985 | 140.8878 | 25.7639 | 63.4497 | 645023.9966 | 0 | 255937.168 | 0 | 0 | 0 | 598837.5593 | 584921.5023 | 1521845.7651 | 1038691.0055 | 4645256.9969 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 38998282.4932 | 110065693.8515 | 100 | 0.13801 | 282578.913 | 797528.5611 | 5760.7534 | 16258.6985
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.001 | 0.61158 | 0.076283 | 4 | 132606.6491 | 365514.6737 | 2703.3659 | 7451.511 | 156.8746 | 26.505 | 49.3847 | 882913.9504 | 0 | 329893.9361 | 0 | 0 | 0 | 759696.7653 | 769276.8142 | 2001500.4701 | 1366065.1976 | 6109347.1337 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 40462372.6301 | 111529783.9883 | 133.3521 | 0.30513 | 132606.6491 | 365514.6737 | 2703.3659 | 7451.511
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6787 | 1.0319 | 0.13707 | 4 | 76803.4871 | 206421.7431 | 1565.743 | 4208.1864 | 169.8758 | 27.0354 | 49.8344 | 1156470.7052 | 0 | 415803.4392 | 0 | 0 | 0 | 932195.1028 | 976743.0064 | 2541284.945 | 1734479.1931 | 7756976.3916 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 42110001.8879 | 113177413.2462 | 177.8279 | 0.54828 | 76803.4871 | 206421.7431 | 1565.743 | 4208.1864
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7787 | 1.5994 | 0.22165 | 4 | 49621.5263 | 129780.2161 | 1011.6019 | 2645.7452 | 180.5198 | 27.4268 | 51.7419 | 1473799.3883 | 0 | 517461.6477 | 0 | 0 | 0 | 1121375.7443 | 1213928.3443 | 3158392.541 | 2155667.8077 | 9640625.4734 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 43993650.9697 | 115061062.328 | 237.1374 | 0.88658 | 49621.5263 | 129780.2161 | 1011.6019 | 2645.7452
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4272 | 2.3496 | 0.33644 | 4 | 34306.5761 | 87114.2643 | 699.386 | 1775.9421 | 189.2196 | 27.719 | 53.9674 | 1844067.7588 | 0 | 638974.1272 | 0 | 0 | 0 | 1331951.1614 | 1487847.2884 | 3871073.4451 | 2642087.1689 | 11816000.9497 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 46169026.4461 | 117236437.8043 | 316.2278 | 1.3458 | 34306.5761 | 87114.2643 | 699.386 | 1775.9421
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.8003 | 3.3332 | 0.49009 | 4 | 24850.9823 | 61103.3889 | 506.6209 | 1245.6752 | 196.3261 | 27.9365 | 75.3595 | 2280243.953 | 0 | 785864.5911 | 0 | 0 | 0 | 1571419.8883 | 1808636.0886 | 4705700.1004 | 3211737.011 | 14363601.6324 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 48716627.1287 | 119784038.487 | 421.6965 | 1.9604 | 24850.9823 | 61103.3889 | 506.6209 | 1245.6752
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0493 | 4.5985 | 0.69305 | 4 | 18635.9637 | 44271.7165 | 379.9193 | 902.5388 | 202.02 | 28.0908 | 65.0457 | 2788789.0866 | 0 | 961692.5892 | 0 | 0 | 0 | 1838203.9376 | 2179587.3892 | 5670839.292 | 3870464.3409 | 17309576.6355 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 51662602.1319 | 122730013.4901 | 562.3413 | 2.7722 | 18635.9637 | 44271.7165 | 379.9193 | 902.5388
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.4083 | 6.217 | 0.95881 | 4 | 14362.3108 | 32892.4135 | 292.7951 | 670.5563 | 206.561 | 28.1899 | 69.9278 | 3383117.1421 | 0 | 1172635.177 | 0 | 0 | 0 | 2137241.3503 | 2610267.5311 | 6791380.6763 | 4635256.8605 | 20729898.7372 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 55082924.2336 | 126150335.5918 | 749.8942 | 3.8352 | 14362.3108 | 32892.4135 | 292.7951 | 670.5563
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.1151 | 8.2648 | 1.3032 | 4 | 11322.9264 | 24956.2091 | 230.8332 | 508.7661 | 210.1323 | 28.2348 | 60.4008 | 4073104.0007 | 0 | 1423996.7451 | 0 | 0 | 0 | 2468339.433 | 3106521.6697 | 8082532.1495 | 5516494.2714 | 24670988.2695 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 59024013.7658 | 130091425.1241 | 1000 | 5.2128 | 11322.9264 | 24956.2091 | 230.8332 | 508.7661
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.4024 | 10.8194 | 1.7436 | 4 | 9105.3908 | 19295.1416 | 185.6257 | 393.3576 | 212.8865 | 28.22 | 74.1903 | 4864907.2845 | 0 | 1720085.8168 | 0 | 0 | 0 | 2827095.2839 | 3670714.4702 | 9550446.0844 | 6518375.6947 | 29151624.6345 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 63504650.1309 | 134572061.4891 | 1333.5214 | 6.9744 | 9105.3908 | 19295.1416 | 185.6257 | 393.3576
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.4897 | 13.9562 | 2.2974 | 4 | 7456.1416 | 15189.5012 | 152.0035 | 309.6585 | 214.9507 | 28.1342 | 82.6876 | 5760770.6625 | 0 | 2064163.382 | 0 | 0 | 0 | 3206397.3746 | 4302219.2534 | 11193491.9909 | 7639788.2871 | 34166830.9505 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 68519856.4469 | 139587267.8051 | 1778.2794 | 9.1897 | 7456.1416 | 15189.5012 | 152.0035 | 309.6585
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.4434 | 17.708 | 2.9763 | 4 | 6212.9976 | 12182.3768 | 126.6604 | 248.3542 | 216.4033 | 27.9606 | 91.459 | 6747987.2149 | 0 | 2454213.2192 | 0 | 0 | 0 | 3588079.7484 | 4988209.2712 | 12978297.3011 | 8857954.5854 | 39614741.3401 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 73967766.8365 | 145035178.1947 | 2371.3737 | 11.9053 | 6212.9976 | 12182.3768 | 126.6604 | 248.3542
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.0728 | 22.0291 | 3.7784 | 4 | 5268.8315 | 9971.0358 | 107.4123 | 203.2731 | 217.2854 | 27.682 | 91.4567 | 7794518.4735 | 0 | 2880835.2094 | 0 | 0 | 0 | 3943463.5001 | 5701338.7014 | 14833713.7956 | 10124314.4678 | 45278184.1478 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 79631209.6442 | 150698621.0024 | 3162.2777 | 15.1136 | 5268.8315 | 9971.0358 | 107.4123 | 203.2731
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.823 | 26.7571 | 4.6797 | 4 | 4550.1603 | 8346.7354 | 92.7612 | 170.1595 | 217.6265 | 27.2912 | 103.6341 | 8846893.6972 | 0 | 3325388.3235 | 0 | 0 | 0 | 4236000.4917 | 6399230.1798 | 16649484.2653 | 11363615.1238 | 50820612.0814 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 85173637.5777 | 156241048.936 | 4216.965 | 18.7188 | 4550.1603 | 8346.7354 | 92.7612 | 170.1595
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.8487 | 31.6295 | 5.6336 | 4 | 4004.076 | 7157.7969 | 81.6285 | 145.9214 | 217.4892 | 26.801 | 62.8921 | 9842736.4045 | 0 | 3763420.1925 | 0 | 0 | 0 | 4434562.0798 | 7035880.284 | 18305917.2413 | 12494164.6662 | 55876680.8683 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 90229706.3647 | 161297117.7229 | 5623.4133 | 22.5345 | 4004.076 | 7157.7969 | 81.6285 | 145.9214
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.2138 | 36.3434 | 6.5805 | 4 | 3590.6979 | 6290.64 | 73.2012 | 128.2432 | 216.987 | 26.2468 | 73.6204 | 10728014.2953 | 0 | 4170552.0855 | 0 | 0 | 0 | 4525321.1968 | 7575316.1552 | 19709418.725 | 13452083.2678 | 60160705.7256 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 94513731.222 | 165581142.5802 | 7498.9421 | 26.3218 | 3590.6979 | 6290.64 | 73.2012 | 128.2432
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1755 | 40.6465 | 7.4647 | 4 | 3279.0747 | 5659.1916 | 66.8484 | 115.3703 | 216.2623 | 25.6749 | 88.8419 | 11472859.0056 | 0 | 4529530.112 | 0 | 0 | 0 | 4517782.5002 | 8002866.9309 | 20821818.1405 | 14211318.7265 | 63556175.4155 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 97909200.9119 | 168976612.2701 | 10000 | 29.8588 | 3279.0747 | 5659.1916 | 66.8484 | 115.3703
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2692 | 44.3716 | 8.2463 | 4 | 3044.954 | 5199.4828 | 62.0755 | 105.9985 | 215.4528 | 25.131 | 103.7258 | 12070158.5789 | 0 | 4831196.5809 | 0 | 0 | 0 | 4435345.4452 | 8321313.236 | 21650350.104 | 14776808.8162 | 66085172.7611 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 100438198.2575 | 171505609.6157 | 13335.2143 | 32.9851 | 3044.954 | 5199.4828 | 62.0755 | 105.9985
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3996 | 47.4693 | 8.9077 | 4 | 2869.4374 | 4863.9928 | 58.4974 | 99.1591 | 214.66 | 24.6453 | 127.9145 | 12533747.1813 | 0 | 5075974.9761 | 0 | 0 | 0 | 4308744.3817 | 8548201.9503 | 22240667.9972 | 15179712.9081 | 67887049.3948 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 102240074.8911 | 173307486.2493 | 17782.7941 | 35.6307 | 2869.4374 | 4863.9928 | 58.4974 | 99.1591
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6734 | 49.9607 | 9.4482 | 4 | 2737.9856 | 4618.4436 | 55.8175 | 94.1532 | 213.9472 | 24.2332 | 133.7735 | 12884668.4217 | 0 | 5268881.3841 | 0 | 0 | 0 | 4163831.9117 | 8703778.8698 | 22645447.2287 | 15455983.051 | 69122590.867 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 103475616.3634 | 174543027.7216 | 23713.7371 | 37.7926 | 2737.9856 | 4618.4436 | 55.8175 | 94.1532
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.3567 | 51.9232 | 9.8793 | 4 | 2639.5175 | 4437.9062 | 53.8101 | 90.4727 | 213.3389 | 23.8948 | 131.8219 | 13147160.1617 | 0 | 5418384.5343 | 0 | 0 | 0 | 4020110.5516 | 8808405.5466 | 22917664.3798 | 15641776.8501 | 69953502.0241 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 104306527.5205 | 175373938.8787 | 31622.7766 | 39.5173 | 2639.5175 | 4437.9062 | 53.8101 | 90.4727
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.742 | 53.4471 | 10.2174 | 4 | 2565.8058 | 4304.6908 | 52.3074 | 87.7569 | 212.8395 | 23.6248 | 122.3113 | 13342703.2866 | 0 | 5533038.2481 | 0 | 0 | 0 | 3889668.2968 | 8878509.8343 | 23100061.356 | 15766266.5343 | 70510247.556 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 104863273.0524 | 175930684.4106 | 42169.6503 | 40.8695 | 2565.8058 | 4304.6908 | 52.3074 | 87.7569
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0964 | 54.6187 | 10.4792 | 4 | 2510.5822 | 4206.0166 | 51.1816 | 85.7453 | 212.4392 | 23.4126 | 127.3967 | 13488038.169 | 0 | 5620342.5852 | 0 | 0 | 0 | 3777340.6319 | 8925431.3406 | 23222141.4905 | 15849588.7345 | 70882882.9517 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105235908.448 | 176303319.8062 | 56234.1325 | 41.9169 | 2510.5822 | 4206.0166 | 51.1816 | 85.7453
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.6346 | 55.5095 | 10.6799 | 4 | 2469.1968 | 4132.7788 | 50.3379 | 84.2523 | 212.1255 | 23.2487 | 125.2203 | 13595517.0373 | 0 | 5686176.0839 | 0 | 0 | 0 | 3683769.1681 | 8956530.2928 | 23303054.5849 | 15904813.5841 | 71129860.751 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105482886.2474 | 176550297.6056 | 74989.4209 | 42.7195 | 2469.1968 | 4132.7788 | 50.3379 | 84.2523
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.554 | 56.1853 | 10.8329 | 4 | 2438.1744 | 4078.2621 | 49.7055 | 83.1409 | 211.882 | 23.1228 | 126.6355 | 13675354.8427 | 0 | 5735834.7866 | 0 | 0 | 0 | 3608124.9584 | 8977532.6892 | 23357698.5121 | 15942109.1872 | 71296654.9763 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105649680.4726 | 176717091.8309 | 100000 | 43.3315 | 2438.1744 | 4078.2621 | 49.7055 | 83.1409
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.0085 | 56.6984 | 10.9492 | 4 | 2414.9161 | 4037.5773 | 49.2313 | 82.3115 | 211.6939 | 23.0264 | 133.786 | 13735022.2235 | 0 | 5773394.049 | 0 | 0 | 0 | 3548344.384 | 8992136.656 | 23395695.0382 | 15968042.597 | 71412634.9477 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105765660.4441 | 176833071.8023 | 133352.1432 | 43.7968 | 2414.9161 | 4037.5773 | 49.2313 | 82.3115
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.1 | 57.0844 | 11.0371 | 4 | 2397.4769 | 4007.2134 | 48.8758 | 81.6925 | 211.5507 | 22.9534 | 122.8366 | 13779321.3778 | 0 | 5801540.0273 | 0 | 0 | 0 | 3501497.8246 | 9002120.0996 | 23421669.9104 | 15985770.981 | 71491920.2206 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105844945.717 | 176912357.0752 | 177827.941 | 44.1485 | 2397.4769 | 4007.2134 | 48.8758 | 81.6925
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.9186 | 57.3744 | 11.1034 | 4 | 2384.4 | 3984.5258 | 48.6092 | 81.2299 | 211.4421 | 22.8982 | 120.6263 | 13812274.4221 | 0 | 5822626.7029 | 0 | 0 | 0 | 3465194.7597 | 9009037.395 | 23439667.2942 | 15998054.5653 | 71546855.1391 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105899880.6355 | 176967291.9937 | 237137.3706 | 44.4136 | 2384.4 | 3984.5258 | 48.6092 | 81.2299
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.5519 | 57.5981 | 11.1539 | 4 | 2374.5939 | 3967.4733 | 48.4093 | 80.8823 | 211.3575 | 22.8554 | 107.1813 | 13837613.051 | 0 | 5838925.978 | 0 | 0 | 0 | 3437846.0321 | 9014610.1738 | 23454166.5216 | 16007950.5859 | 71591112.3424 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105944137.8388 | 177011549.197 | 316227.766 | 44.6157 | 2374.5939 | 3967.4733 | 48.4093 | 80.8823
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.0124 | 57.7616 | 11.1915 | 4 | 2367.2403 | 3954.7754 | 48.2594 | 80.6234 | 211.2955 | 22.8241 | 111.3085 | 13855943.8343 | 0 | 5850769.8249 | 0 | 0 | 0 | 3416541.0265 | 9018069.3274 | 23463166.5295 | 16014093.2763 | 71618583.8188 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105971609.3152 | 177039020.6734 | 421696.5034 | 44.7659 | 2367.2403 | 3954.7754 | 48.2594 | 80.6234
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.3607 | 57.8853 | 11.2198 | 4 | 2361.7259 | 3945.2541 | 48.147 | 80.4293 | 211.2484 | 22.8004 | 115.1672 | 13869765.2233 | 0 | 5859727.2822 | 0 | 0 | 0 | 3400432.7349 | 9020670.8438 | 23469935.1415 | 16018712.993 | 71639244.2186 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 105992269.715 | 177059681.0732 | 562341.3252 | 44.8792 | 2361.7259 | 3945.2541 | 48.147 | 80.4293
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.6165 | 57.9765 | 11.2409 | 4 | 2357.5906 | 3938.1458 | 48.0627 | 80.2844 | 211.2137 | 22.7829 | 121.2574 | 13879883.5846 | 0 | 5866301.4644 | 0 | 0 | 0 | 3388076.1299 | 9022361.8598 | 23474334.8183 | 16021715.8628 | 71652673.7198 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106005699.2162 | 177073110.5744 | 749894.2093 | 44.9636 | 2357.5906 | 3938.1458 | 48.0627 | 80.2844
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.8166 | 58.0473 | 11.257 | 4 | 2354.4895 | 3932.7844 | 47.9995 | 80.1751 | 211.1865 | 22.7693 | 74.9497 | 13887783.7042 | 0 | 5871441.645 | 0 | 0 | 0 | 3378968.9876 | 9023895.7914 | 23478325.7935 | 16024439.7854 | 71664855.7071 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106017881.2035 | 177085292.5617 | 1000000 | 45.028 | 2354.4895 | 3932.7844 | 47.9995 | 80.1751
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.9675 | 58.1008 | 11.2691 | 4 | 2352.164 | 3928.7624 | 47.952 | 80.0931 | 211.166 | 22.7589 | 72.3129 | 13893736.3777 | 0 | 5875319.8329 | 0 | 0 | 0 | 3372125.6541 | 9025060.9272 | 23481357.2381 | 16026508.8086 | 71674108.8385 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106027134.3349 | 177094545.6931 | 1333521.4322 | 45.0764 | 2352.164 | 3928.7624 | 47.952 | 80.0931
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.0723 | 58.1384 | 11.2779 | 4 | 2350.4201 | 3925.7837 | 47.9165 | 80.0324 | 211.1517 | 22.7518 | 80.2257 | 13897862.4908 | 0 | 5878012.548 | 0 | 0 | 0 | 3366739.1991 | 9025619.5527 | 23482810.6671 | 16027500.8038 | 71678545.2615 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106031570.7578 | 177098982.116 | 1778279.41 | 45.1118 | 2350.4201 | 3925.7837 | 47.9165 | 80.0324
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.1501 | 58.1663 | 11.2845 | 4 | 2349.1124 | 3923.5542 | 47.8898 | 79.987 | 211.141 | 22.7464 | 79.0923 | 13900921.7213 | 0 | 5880010.6446 | 0 | 0 | 0 | 3362664.9969 | 9026002.9715 | 23483808.244 | 16028181.6706 | 71681590.2489 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106034615.7452 | 177102027.1035 | 2371373.7057 | 45.1382 | 2349.1124 | 3923.5542 | 47.8898 | 79.987
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.2233 | 58.1917 | 11.2899 | 4 | 2348.1317 | 3921.8194 | 47.8698 | 79.9516 | 211.1311 | 22.7414 | 79.2294 | 13903802.3849 | 0 | 5881889.652 | 0 | 0 | 0 | 3360012.5912 | 9026824.8049 | 23485946.4861 | 16029641.0647 | 71688116.9837 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106041142.4801 | 177108553.8383 | 3162277.6602 | 45.1598 | 2348.1317 | 3921.8194 | 47.8698 | 79.9516
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.2692 | 58.2081 | 11.2937 | 4 | 2347.3963 | 3920.5568 | 47.8548 | 79.9259 | 211.1248 | 22.7383 | 90.752 | 13905608.1929 | 0 | 5883069.8135 | 0 | 0 | 0 | 3357773.1191 | 9027115.9389 | 23486703.957 | 16030158.0541 | 71690429.0754 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106043454.5718 | 177110865.93 | 4216965.0343 | 45.1749 | 2347.3963 | 3920.5568 | 47.8548 | 79.9259
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.3035 | 58.2203 | 11.2966 | 4 | 2346.8448 | 3919.611 | 47.8436 | 79.9066 | 211.1201 | 22.7359 | 100.1678 | 13906954.1347 | 0 | 5883949.7592 | 0 | 0 | 0 | 3356086.1127 | 9027326.1026 | 23487250.7597 | 16030531.2582 | 71692098.1271 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106045123.6235 | 177112534.9817 | 5623413.2519 | 45.1863 | 2346.8448 | 3919.611 | 47.8436 | 79.9066
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.3204 | 58.2268 | 11.2984 | 4 | 2346.4313 | 3918.9396 | 47.8352 | 79.8929 | 211.1177 | 22.7347 | 118.0091 | 13907612.5541 | 0 | 5884382.3588 | 0 | 0 | 0 | 3354575.5638 | 9027162.4859 | 23486825.0627 | 16030240.7113 | 71690798.7365 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106043824.2329 | 177111235.5911 | 7498942.0933 | 45.1937 | 2346.4313 | 3918.9396 | 47.8352 | 79.8929
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.3398 | 58.2337 | 11.3 | 4 | 2346.1211 | 3918.407 | 47.8289 | 79.882 | 211.1151 | 22.7334 | 119.2019 | 13908376.229 | 0 | 5884881.7636 | 0 | 0 | 0 | 3353630.2399 | 9027286.4107 | 23487147.4895 | 16030460.7742 | 71691782.9068 | 961560.8286 | 33391464.6677 | 33391464.6677 | 24773143.2569 | 12902803.4336 | 0 | 106044808.4032 | 177112219.7614 | 10000000 | 45.2001 | 2346.1211 | 3918.407 | 47.8289 | 79.882
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7144 | 0.3218 | 0.036383 | 4 | 273484.8788 | 771500.9081 | 5575.3592 | 15728.0895 | 143.0432 | 26.2215 | 56.6328 | 664212.7658 | 0 | 260042.899 | 0 | 0 | 0 | 615926.6952 | 600671.1204 | 1562823.0408 | 1066658.8381 | 4770335.3594 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 39801264.5383 | 112279376.7418 | 100 | 0.14553 | 273484.8788 | 771500.9081 | 5575.3592 | 15728.0895
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0982 | 0.63178 | 0.080035 | 4 | 129009.4512 | 355404.8481 | 2630.0322 | 7245.4085 | 159.2878 | 26.9703 | 45.5151 | 908567.6923 | 0 | 335015.7078 | 0 | 0 | 0 | 780820.9806 | 789517.7085 | 2054163.1252 | 1402008.5418 | 6270093.7563 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 41301022.9351 | 113779135.1387 | 133.3521 | 0.32014 | 129009.4512 | 355404.8481 | 2630.0322 | 7245.4085
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8102 | 1.0658 | 0.14346 | 4 | 74923.935 | 201227.961 | 1527.4258 | 4102.3042 | 172.532 | 27.5075 | 51.7612 | 1190248.1019 | 0 | 422340.4664 | 0 | 0 | 0 | 958498.5832 | 1002723.9891 | 2608882.1327 | 1780615.6627 | 7963308.936 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 42994238.1148 | 115472350.3184 | 177.8279 | 0.57384 | 74923.935 | 201227.961 | 1527.4258 | 4102.3042
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9445 | 1.6501 | 0.23159 | 4 | 48490.9388 | 126730.8636 | 988.5534 | 2583.5801 | 183.3319 | 27.9024 | 45.2259 | 1515673.5694 | 0 | 525264.1165 | 0 | 0 | 0 | 1151890.2488 | 1245202.8945 | 3239762.5053 | 2211204.4803 | 9888997.8149 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 44919926.9937 | 117398039.1973 | 237.1374 | 0.92636 | 48490.9388 | 126730.8636 | 988.5534 | 2583.5801
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6487 | 2.4252 | 0.35123 | 4 | 33566.0064 | 85155.1197 | 684.2884 | 1736.0023 | 192.1989 | 28.1983 | 54.6167 | 1897145.7198 | 0 | 648864.2143 | 0 | 0 | 0 | 1369175.4268 | 1526922.2908 | 3972738.5857 | 2711475.7164 | 12126321.9537 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 47157251.1326 | 119635363.3361 | 316.2278 | 1.4049 | 33566.0064 | 85155.1197 | 684.2884 | 1736.0023
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0781 | 3.438 | 0.51118 | 4 | 24337.2246 | 59783.8248 | 496.1472 | 1218.7741 | 199.4097 | 28.4173 | 67.7771 | 2344607.2388 | 0 | 797644.3838 | 0 | 0 | 0 | 1614124.2541 | 1854986.5919 | 4826294.602 | 3294045.2363 | 14731702.3069 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 49762631.4858 | 122240743.6893 | 421.6965 | 2.0447 | 24337.2246 | 59783.8248 | 496.1472 | 1218.7741
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4024 | 4.742 | 0.72244 | 4 | 18264.4527 | 43345.5999 | 372.3456 | 883.6587 | 205.1956 | 28.5724 | 67.3917 | 2866882.1021 | 0 | 975923.9552 | 0 | 0 | 0 | 1887650.2212 | 2234877.9486 | 5814693.9858 | 3968648.1253 | 17748676.3381 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 52779605.517 | 125257717.7206 | 562.3413 | 2.8897 | 18264.4527 | 43345.5999 | 372.3456 | 883.6587
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.854 | 6.4093 | 0.99894 | 4 | 14085.0209 | 32223.6943 | 287.1422 | 656.9236 | 209.8091 | 28.6713 | 70.3664 | 3477046.8611 | 0 | 1189731.4594 | 0 | 0 | 0 | 2194037.687 | 2675718.2429 | 6961670.0028 | 4751482.8249 | 21249687.078 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 56280616.2569 | 128758728.4604 | 749.8942 | 3.9958 | 14085.0209 | 32223.6943 | 287.1422 | 656.9236
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.6681 | 8.5166 | 1.357 | 4 | 11110.6799 | 24463.3919 | 226.5062 | 498.7193 | 213.4347 | 28.7143 | 61.5562 | 4184601.4266 | 0 | 1444209.7888 | 0 | 0 | 0 | 2532451.7827 | 3182892.5693 | 8281233.5642 | 5652112.0699 | 25277501.2014 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 60308430.3802 | 132786542.5838 | 1000 | 5.428 | 11110.6799 | 24463.3919 | 226.5062 | 498.7193
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.1017 | 11.149 | 1.8149 | 4 | 8939.5331 | 18923.2656 | 182.2445 | 385.7764 | 216.2359 | 28.6957 | 45.4233 | 4997883.3391 | 0 | 1744467.6375 | 0 | 0 | 0 | 2900608.6014 | 3760754.2354 | 9784711.0838 | 6678266.3704 | 29866691.2677 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 64897620.4466 | 137375732.6501 | 1333.5214 | 7.2596 | 8939.5331 | 18923.2656 | 182.2445 | 385.7764
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.3445 | 14.3752 | 2.39 | 4 | 7324.2703 | 14905.7297 | 149.3152 | 303.8735 | 218.3307 | 28.6035 | 55.1948 | 5915979.5844 | 0 | 2092636.4588 | 0 | 0 | 0 | 3287997.7726 | 4405679.3882 | 11462674.0389 | 7823510.5659 | 34988477.8087 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 70019406.9876 | 142497519.1911 | 1778.2794 | 9.5599 | 7324.2703 | 14905.7297 | 149.3152 | 303.8735
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.4593 | 18.2273 | 3.0938 | 4 | 6106.6136 | 11963.3857 | 124.4916 | 243.8898 | 219.8016 | 28.4203 | 48.7724 | 6925752.3328 | 0 | 2486623.1992 | 0 | 0 | 0 | 3676315.4519 | 5104589.4837 | 13281094.7414 | 9064620.0602 | 40538995.2692 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 75569924.448 | 148048036.6516 | 2371.3737 | 12.3751 | 6106.6136 | 11963.3857 | 124.4916 | 243.8898
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.2371 | 22.6533 | 3.9233 | 4 | 5181.9267 | 9800.3344 | 105.6406 | 199.7931 | 220.6902 | 28.1288 | 63.0799 | 7993387.2154 | 0 | 2916522.6683 | 0 | 0 | 0 | 4035802.7439 | 5828827.9247 | 15165414.6032 | 10350707.0848 | 46290662.2403 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 81321591.4191 | 153799703.6227 | 3162.2777 | 15.6933 | 5181.9267 | 9800.3344 | 105.6406 | 199.7931
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.1091 | 27.484 | 4.853 | 4 | 4478.3166 | 8212.0303 | 91.2965 | 167.4133 | 221.0286 | 27.7223 | 84.6049 | 9064091.5523 | 0 | 3363425.8024 | 0 | 0 | 0 | 4329672.2456 | 6535303.9441 | 17003520.2874 | 11605251.9836 | 51901265.8155 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 86932194.9943 | 159410307.1979 | 4216.965 | 19.4118 | 4478.3166 | 8212.0303 | 91.2965 | 167.4133
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.1929 | 32.4419 | 5.8331 | 4 | 3943.9181 | 7050.2395 | 80.4021 | 143.7287 | 220.8836 | 27.2157 | 101.3828 | 10072806.0344 | 0 | 3801970.3145 | 0 | 0 | 0 | 4525516.9095 | 7176114.3708 | 18670777.5693 | 12743189.3371 | 56990374.5355 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 92021303.7144 | 164499415.9179 | 5623.4133 | 23.3325 | 3943.9181 | 7050.2395 | 80.4021 | 143.7287
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.6 | 37.2332 | 6.8037 | 4 | 3539.5838 | 6202.7613 | 72.1592 | 126.4517 | 220.3723 | 26.6445 | 115.2382 | 10968649.3728 | 0 | 4209302.807 | 0 | 0 | 0 | 4613289.0177 | 7718584.067 | 20082172.4431 | 13706495.3398 | 61298493.0475 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 96329422.2263 | 168807534.4299 | 7498.9421 | 27.2149 | 3539.5838 | 6202.7613 | 72.1592 | 126.4517
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.5445 | 41.5896 | 7.7068 | 4 | 3234.9184 | 5586.0334 | 65.9482 | 113.8788 | 219.6412 | 26.0585 | 124.9558 | 11719180.1233 | 0 | 4567021.6167 | 0 | 0 | 0 | 4600787.226 | 8145925.6968 | 21194027.7038 | 14465359.4016 | 64692301.7682 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 99723230.9471 | 172201343.1506 | 10000 | 30.8271 | 3234.9184 | 5586.0334 | 65.9482 | 113.8788
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5922 | 45.3506 | 8.5027 | 4 | 3006.1145 | 5137.15 | 61.2837 | 104.7278 | 218.8289 | 25.5034 | 122.3407 | 12319415.7037 | 0 | 4866854.1559 | 0 | 0 | 0 | 4513366.6604 | 8462858.2428 | 22018621.1768 | 15028161.3906 | 67209277.3301 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 102240206.509 | 174718318.7125 | 13335.2143 | 34.0107 | 3006.1145 | 5137.15 | 61.2837 | 104.7278
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6371 | 48.4633 | 9.1737 | 4 | 2834.6363 | 4809.7871 | 57.7879 | 98.054 | 218.0389 | 25.0109 | 125.1932 | 12782959.0725 | 0 | 5108920.8383 | 0 | 0 | 0 | 4381394.3914 | 8686576.9778 | 22600691.4344 | 15425436.3017 | 68985979.0161 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 104016908.1949 | 176495020.3985 | 17782.7941 | 36.695 | 2834.6363 | 4809.7871 | 57.7879 | 98.054
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8527 | 50.9694 | 9.7218 | 4 | 2706.2382 | 4570.036 | 55.1703 | 93.1664 | 217.3284 | 24.5928 | 140.1784 | 13134450.4314 | 0 | 5299989.3843 | 0 | 0 | 0 | 4233201.2732 | 8840380.0247 | 23000855.4129 | 15698556.4396 | 70207432.966 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 105238362.1449 | 177716474.3485 | 23713.7371 | 38.8873 | 2706.2382 | 4570.036 | 55.1703 | 93.1664
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4823 | 52.9405 | 10.1584 | 4 | 2610.1113 | 4393.8124 | 53.2106 | 89.5738 | 216.7243 | 24.251 | 106.8248 | 13397161.3004 | 0 | 5447870.3623 | 0 | 0 | 0 | 4087272.5699 | 8943598.6507 | 23269409.1048 | 15881849.8525 | 71027161.8405 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 106058091.0194 | 178536203.2229 | 31622.7766 | 40.6336 | 2610.1113 | 4393.8124 | 53.2106 | 89.5738
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.8332 | 54.4735 | 10.5007 | 4 | 2538.0946 | 4263.6417 | 51.7425 | 86.9201 | 216.2263 | 23.9767 | 117.8863 | 13593039.3822 | 0 | 5561478.2409 | 0 | 0 | 0 | 3955181.7013 | 9012782.7365 | 23449411.9044 | 16004705.462 | 71576599.4272 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 106607528.606 | 179085640.8096 | 42169.6503 | 42.003 | 2538.0946 | 4263.6417 | 51.7425 | 86.9201
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.1318 | 55.6428 | 10.7648 | 4 | 2484.1751 | 4167.3929 | 50.6433 | 84.9579 | 215.8314 | 23.7636 | 107.5926 | 13737438.836 | 0 | 5647221.1471 | 0 | 0 | 0 | 3841016.7012 | 9058013.9069 | 23567094.1316 | 16085026.0001 | 71935810.7229 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 106966739.9018 | 179444852.1053 | 56234.1325 | 43.0593 | 2484.1751 | 4167.3929 | 50.6433 | 84.9579
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6527 | 56.5393 | 10.9679 | 4 | 2443.77 | 4095.8234 | 49.8196 | 83.4989 | 215.519 | 23.5974 | 85.0836 | 13845330.147 | 0 | 5712530.6069 | 0 | 0 | 0 | 3746979.2387 | 9088887.5971 | 23647421.1405 | 16139850.8343 | 72180999.5645 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107211928.7433 | 179690040.9469 | 74989.4209 | 43.8715 | 2443.77 | 4095.8234 | 49.8196 | 83.4989
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.548 | 57.2162 | 11.1223 | 4 | 2413.4841 | 4042.5975 | 49.2021 | 82.4138 | 215.278 | 23.4706 | 86.1015 | 13925017.1447 | 0 | 5761510.6662 | 0 | 0 | 0 | 3670710.9853 | 9109323.1305 | 23700590.2065 | 16176139.8144 | 72343291.9477 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107374221.1265 | 179852333.3301 | 100000 | 44.4893 | 2413.4841 | 4042.5975 | 49.2021 | 82.4138
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9855 | 57.7304 | 11.2398 | 4 | 2390.7791 | 4002.868 | 48.7393 | 81.6039 | 215.0917 | 23.3733 | 75.4432 | 13984631.3507 | 0 | 5798589.5082 | 0 | 0 | 0 | 3610544.3093 | 9123568.4156 | 23737653.5162 | 16201436.2848 | 72456423.3849 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107487352.5637 | 179965464.7673 | 133352.1432 | 44.9591 | 2390.7791 | 4002.868 | 48.7393 | 81.6039
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.065 | 58.1174 | 11.3285 | 4 | 2373.7554 | 3973.2127 | 48.3922 | 80.9993 | 214.9497 | 23.2997 | 94.2409 | 14028923.8109 | 0 | 5826393.7887 | 0 | 0 | 0 | 3563454.8611 | 9133321.2597 | 23763028.4159 | 16218755.1752 | 72533877.3114 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107564806.4903 | 180042918.6938 | 177827.941 | 45.3142 | 2373.7554 | 3973.2127 | 48.3922 | 80.9993
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.866 | 58.4057 | 11.3952 | 4 | 2360.9905 | 3951.0911 | 48.132 | 80.5483 | 214.8432 | 23.2446 | 76.2884 | 14061527.4087 | 0 | 5847006.6706 | 0 | 0 | 0 | 3526739.974 | 9139756.8808 | 23779772.5819 | 16230183.4126 | 72584986.9287 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107615916.1075 | 180094028.3111 | 237137.3706 | 45.5808 | 2360.9905 | 3951.0911 | 48.132 | 80.5483
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.4922 | 58.6299 | 11.4462 | 4 | 2351.4185 | 3934.4357 | 47.9368 | 80.2088 | 214.7594 | 23.2014 | 74.6496 | 14086865.6023 | 0 | 5863107.5488 | 0 | 0 | 0 | 3499277.1097 | 9145207.6017 | 23793954.2397 | 16239862.6855 | 72628274.7878 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107659203.9666 | 180137316.1702 | 316227.766 | 45.7848 | 2351.4185 | 3934.4357 | 47.9368 | 80.2088
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.9332 | 58.7895 | 11.4837 | 4 | 2344.2406 | 3922.0947 | 47.7905 | 79.9572 | 214.6998 | 23.1709 | 105.3336 | 14104616.6167 | 0 | 5874439.5642 | 0 | 0 | 0 | 3477483.2529 | 9148050.3792 | 23801350.5635 | 16244910.8284 | 72650851.2049 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107681780.3838 | 180159892.5873 | 421696.5034 | 45.9346 | 2344.2406 | 3922.0947 | 47.7905 | 79.9572
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.2887 | 58.9169 | 11.5126 | 4 | 2338.858 | 3912.7477 | 47.6808 | 79.7667 | 214.6518 | 23.1462 | 107.8309 | 14118882.6859 | 0 | 5883569.2462 | 0 | 0 | 0 | 3461629.4171 | 9150991.7262 | 23809003.345 | 16250134.0091 | 72674210.4294 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107705139.6082 | 180183251.8118 | 562341.3252 | 46.0503 | 2338.858 | 3912.7477 | 47.6808 | 79.7667
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.5445 | 59.0091 | 11.534 | 4 | 2334.8216 | 3905.7925 | 47.5985 | 79.6249 | 214.617 | 23.1284 | 119.0814 | 14129117.1382 | 0 | 5890136.7628 | 0 | 0 | 0 | 3449311.8787 | 9152740.6541 | 23813553.6966 | 16253239.7175 | 72688099.8478 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107719029.0267 | 180197141.2302 | 749894.2093 | 46.1359 | 2334.8216 | 3905.7925 | 47.5985 | 79.6249
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.7445 | 59.0809 | 11.5503 | 4 | 2331.7947 | 3900.5463 | 47.5368 | 79.5179 | 214.5898 | 23.1145 | 104.6995 | 14137107.8692 | 0 | 5895271.7382 | 0 | 0 | 0 | 3440237.7569 | 9154320.7721 | 23817664.8395 | 16256045.657 | 72700648.6329 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107731577.8118 | 180209690.0153 | 1000000 | 46.2011 | 2331.7947 | 3900.5463 | 47.5368 | 79.5179
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.8929 | 59.1342 | 11.5625 | 4 | 2329.5249 | 3896.6217 | 47.4905 | 79.4379 | 214.5696 | 23.1041 | 65.5281 | 14143024.2131 | 0 | 5899079.2298 | 0 | 0 | 0 | 3433346.7412 | 9155425.5718 | 23820539.3018 | 16258007.5366 | 72709422.5944 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107740351.7733 | 180218463.9768 | 1333521.4322 | 46.2499 | 2329.5249 | 3896.6217 | 47.4905 | 79.4379
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.0003 | 59.173 | 11.5715 | 4 | 2327.8227 | 3893.6963 | 47.4558 | 79.3783 | 214.5549 | 23.0966 | 67.6939 | 14147302.2428 | 0 | 5901835.9954 | 0 | 0 | 0 | 3428049.5658 | 9156103.2435 | 23822302.4647 | 16259210.9315 | 72714804.4437 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107745733.6226 | 180223845.8261 | 1778279.41 | 46.2861 | 2327.8227 | 3893.6963 | 47.4558 | 79.3783
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.0728 | 59.1996 | 11.578 | 4 | 2326.5463 | 3891.5372 | 47.4298 | 79.3343 | 214.5449 | 23.0915 | 127.3403 | 14150184.3953 | 0 | 5903696.4395 | 0 | 0 | 0 | 3423839.0273 | 9156310.7462 | 23822842.344 | 16259579.4103 | 72716452.3626 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107747381.5415 | 180225493.745 | 2371373.7057 | 46.3122 | 2326.5463 | 3891.5372 | 47.4298 | 79.3343
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.1387 | 59.2232 | 11.5833 | 4 | 2325.5891 | 3889.8698 | 47.4103 | 79.3003 | 214.5359 | 23.0869 | 137.2164 | 14152808.0992 | 0 | 5905388.0042 | 0 | 0 | 0 | 3420998.7221 | 9156885.982 | 23824338.9895 | 16260600.9015 | 72721020.6986 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107751949.8775 | 180230062.081 | 3162277.6602 | 46.3332 | 2325.5891 | 3889.8698 | 47.4103 | 79.3003
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.1823 | 59.239 | 11.5871 | 4 | 2324.8713 | 3888.6447 | 47.3956 | 79.2753 | 214.5299 | 23.0839 | 73.8156 | 14154537.4715 | 0 | 5906504.71 | 0 | 0 | 0 | 3418699.1161 | 9157099.1061 | 23824893.4947 | 16260979.3627 | 72722713.2611 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107753642.44 | 180231754.6435 | 4216965.0343 | 46.3482 | 2324.8713 | 3888.6447 | 47.3956 | 79.2753
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.2165 | 59.2514 | 11.5899 | 4 | 2324.333 | 3887.7192 | 47.3847 | 79.2564 | 214.5252 | 23.0815 | 73.832 | 14155899.024 | 0 | 5907383.7817 | 0 | 0 | 0 | 3417017.9649 | 9157317.3005 | 23825461.192 | 16261366.8278 | 72724446.0909 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107755375.2698 | 180233487.4733 | 5623413.2519 | 46.3597 | 2324.333 | 3887.7192 | 47.3847 | 79.2564
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.236 | 59.2587 | 11.5919 | 4 | 2323.9293 | 3887.0515 | 47.3764 | 79.2428 | 214.5225 | 23.0801 | 82.6734 | 14156669.3779 | 0 | 5907882.6997 | 0 | 0 | 0 | 3415581.2553 | 9157251.9998 | 23825291.2929 | 16261250.8682 | 72723927.4939 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107754856.6728 | 180232968.8763 | 7498942.0933 | 46.3675 | 2323.9293 | 3887.0515 | 47.3764 | 79.2428
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | CO2 | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.2554 | 59.2657 | 11.5935 | 4 | 2323.6266 | 3886.5305 | 47.3703 | 79.2322 | 214.5199 | 23.0788 | 88.097 | 14157441.8919 | 0 | 5908381.6072 | 0 | 0 | 0 | 3414639.2866 | 9157380.4864 | 23825625.5887 | 16261479.0319 | 72724947.8927 | 961560.8286 | 34069368.3502 | 34069368.3502 | 25261752.1078 | 13146991.7455 | 0 | 107755877.0716 | 180233989.2751 | 10000000 | 46.374 | 2323.6266 | 3886.5305 | 47.3703 | 79.2322

## Water (R245fa)
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4482 | [19 empty] | 100 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.6776 | [19 empty] | 133.3521 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8531 | [19 empty] | 177.8279 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.5688 | [19 empty] | 237.1374 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8952 | [19 empty] | 316.2278 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.642 | [19 empty] | 421.6965 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0923 | [19 empty] | 562.3413 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9332 | [19 empty] | 749.8942 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 2262.7343 | [19 empty] | 1000 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4225 | [19 empty] | 1333.5214 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5926 | [19 empty] | 1778.2794 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.9459 | [19 empty] | 2371.3737 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.3779 | [19 empty] | 3162.2777 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 39.2421 | [19 empty] | 4216.965 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 38.5741 | [19 empty] | 5623.4133 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.7634 | [19 empty] | 7498.9421 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.1244 | [19 empty] | 10000 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.04259 | 0.00010539 | 4 | 10396608.9942 | 26268544.7027 | 211948.9368 | 535519.8146 | 50.7034 | 0 | 2313.0586 | 21144.6822 | 504.795 | 28875.9658 | 40598.0558 | 0 | 14808.3258 | 0 | 41313.4116 | 107489.0224 | 73363.4665 | 328097.725 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4382837.7523 | 11073877.0194 | 13335.2143 | 0.00042156 | 10396608.9942 | 26268544.7027 | 211948.9368 | 535519.8146
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.418 | 0.061469 | 0.00024649 | 4 | 4525671.3298 | 11312087.7768 | 92261.9315 | 230612.2101 | 51.7209 | 0 | 221.1085 | 27846.8091 | 674.9918 | 38687.9133 | 47518.7054 | 0 | 16783.8752 | 0 | 51289.795 | 133445.5256 | 91079.3132 | 407326.9287 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4462066.956 | 11153106.2231 | 17782.7941 | 0.00098595 | 4525671.3298 | 11312087.7768 | 92261.9315 | 230612.2101
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9042 | 0.08529 | 0.00044355 | 4 | 2567356.701 | 6338640.6424 | 52339.039 | 129221.7631 | 52.434 | 0 | 300.7451 | 35420.5988 | 868.3959 | 50242.1804 | 56219.8343 | 0 | 18773.6442 | 0 | 62994.615 | 163899.0661 | 111864.4804 | 500282.8152 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4555022.8425 | 11246062.1096 | 23713.7371 | 0.0017742 | 2567356.701 | 6338640.6424 | 52339.039 | 129221.7631
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.1168 | 0.00071323 | 4 | 1637185.5589 | 3982502.5165 | 33376.2421 | 81188.7005 | 52.9702 | 0 | 405.3335 | 44472.1082 | 1100.4688 | 64578.7595 | 67712.063 | 0 | 21037.218 | 0 | 77571.2408 | 201824.4566 | 137749.3387 | 616045.6536 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4670785.6809 | 11361824.948 | 31622.7766 | 0.0028529 | 1637185.5589 | 3982502.5165 | 33376.2421 | 81188.7005
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.366 | 0.15702 | 0.0010776 | 4 | 1116040.1966 | 2668394.6841 | 22751.989 | 54398.8349 | 53.3643 | 0 | 82.3984 | 54976.6419 | 1370.7015 | 81793.3713 | 82376.2879 | 0 | 23465.1593 | 0 | 95153.0432 | 247568.6997 | 168970.7246 | 755674.6294 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4810414.6567 | 11501453.9237 | 42169.6503 | 0.0043103 | 1116040.1966 | 2668394.6841 | 22751.989 | 54398.8349
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4332 | 0.20939 | 0.0015646 | 4 | 796257.4911 | 1865414.0988 | 16232.786 | 38028.9896 | 53.6623 | 0 | 82.7827 | 67454.1103 | 1692.3986 | 102941.3453 | 101463.5092 | 0 | 26208.0475 | 0 | 116906.1702 | 304165.8742 | 207599.4591 | 928430.9145 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4983170.9418 | 11674210.2089 | 56234.1325 | 0.0062582 | 796257.4911 | 1865414.0988 | 16232.786 | 38028.9896
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7749 | 0.27523 | 0.002207 | 4 | 587895.0463 | 1345828.3417 | 11985.0357 | 27436.5311 | 53.8802 | 0 | 116.0341 | 81816.9359 | 2063.2926 | 128080.3813 | 125455.2609 | 0 | 29102.5987 | 0 | 142942.2031 | 371906.2909 | 253833.6854 | 1135200.6488 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5189940.6761 | 11880979.9432 | 74989.4209 | 0.008828 | 587895.0463 | 1345828.3417 | 11985.0357 | 27436.5311
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3755 | 0.35361 | 0.0030307 | 4 | 447488.4147 | 999418.6238 | 9122.6566 | 20374.5005 | 54.0239 | 0 | 102.2111 | 97549.4346 | 2469.8173 | 156489.3869 | 154038.5816 | 0 | 31829.6593 | 0 | 172526.9831 | 448879.8198 | 306369.7006 | 1370153.3832 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5424893.4105 | 12115932.6776 | 100000 | 0.012123 | 447488.4147 | 999418.6238 | 9122.6566 | 20374.5005
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.6802 | 0.46717 | 0.00416 | 4 | 345754.9826 | 747859.9078 | 7048.683 | 15246.1358 | 54.1796 | 0 | 92.1559 | 118621.3637 | 3015.4979 | 195513.0276 | 195353.7261 | 0 | 35928.8182 | 0 | 213888.6491 | 556494.3903 | 379818.8562 | 1698634.329 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5753374.3564 | 12444413.6234 | 133352.1432 | 0.01664 | 345754.9826 | 747859.9078 | 7048.683 | 15246.1358
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3527 | 0.59855 | 0.0055754 | 4 | 274286.1729 | 574311.4561 | 5591.6946 | 11708.1158 | 54.2753 | 0 | 2348.2675 | 141072.8936 | 3597.0234 | 238361.8032 | 243192.5879 | 0 | 39616 | 0 | 259677.7202 | 675628.1608 | 461130.1025 | 2062276.2917 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 6117016.319 | 12808055.5861 | 177827.941 | 0.022302 | 274286.1729 | 574311.4561 | 5591.6946 | 11708.1158
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5682 | 0.75663 | 0.0073556 | 4 | 222239.7665 | 449654.3417 | 4530.6582 | 9166.812 | 54.3473 | 0 | 100.6212 | 166171.2443 | 4247.4346 | 287498.1341 | 300752.3124 | 0 | 43346.2254 | 0 | 312785.9868 | 813804.9765 | 555438.6185 | 2484044.9325 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 6538784.9598 | 13229824.2269 | 237137.3706 | 0.029422 | 222239.7665 | 449654.3417 | 4530.6582 | 9166.812
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3124 | 0.94072 | 0.0095327 | 4 | 183935.867 | 359412.5738 | 3749.7814 | 7327.1115 | 54.4012 | 0 | 86.3805 | 193460.1104 | 4954.8272 | 342195.2226 | 367778.7893 | 0 | 46925.9251 | 0 | 372572.8011 | 969358.0033 | 661606.7555 | 2958852.4345 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 7013592.4618 | 13704631.7289 | 316227.766 | 0.038131 | 183935.867 | 359412.5738 | 3749.7814 | 7327.1115
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5124 | 1.1472 | 0.012101 | 4 | 155569.0839 | 293802.0241 | 3171.4862 | 5989.5517 | 54.4415 | 0 | 77.9868 | 222207.8886 | 5700.1384 | 401061.8668 | 442968.3124 | 0 | 50165.4044 | 0 | 437620.4082 | 1138598.5338 | 777116.8952 | 3475439.4479 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 7530179.4753 | 14221218.7423 | 421696.5034 | 0.048404 | 155569.0839 | 293802.0241 | 3171.4862 | 5989.5517
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.9823 | 1.3671 | 0.01499 | 4 | 134504.0718 | 246092.7899 | 2742.0474 | 5016.9344 | 54.4715 | 0 | 98.5636 | 251133.4742 | 6450.0616 | 461427.0949 | 522994.5748 | 0 | 52800.2145 | 0 | 504974.1138 | 1313839.0597 | 896722.1549 | 4010340.7485 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 8065080.7758 | 14756120.0429 | 562341.3252 | 0.059962 | 134504.0718 | 246092.7899 | 2742.0474 | 5016.9344
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4936 | 1.5889 | 0.018072 | 4 | 118858.477 | 211418.2797 | 2423.0908 | 4310.0476 | 54.4937 | 0 | 102.2915 | 278938.4347 | 7170.8681 | 520411.1579 | 603765.3512 | 0 | 54689.3128 | 0 | 571340.2987 | 1486510.2592 | 1014573.7966 | 4537399.4793 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 8592139.5066 | 15283178.7737 | 749894.2093 | 0.072289 | 118858.477 | 211418.2797 | 2423.0908 | 4310.0476
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.7519 | 1.7984 | 0.021164 | 4 | 107251.1575 | 186290.7287 | 2186.4599 | 3797.7885 | 54.5099 | 0 | 87.9896 | 304132.6785 | 7823.9018 | 574592.7903 | 680011.5967 | 0 | 55692.7659 | 0 | 632678.9559 | 1646100.863 | 1123497.663 | 5024531.2151 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9079271.2424 | 15770310.5094 | 1000000 | 0.084654 | 107251.1575 | 186290.7287 | 2186.4599 | 3797.7885
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.6009 | 1.9877 | 0.024105 | 4 | 98650.5854 | 168044.6434 | 2011.1256 | 3425.8174 | 54.5217 | 0 | 102.1425 | 326157.0702 | 8394.6751 | 622487.4338 | 748930.1172 | 0 | 55991.9025 | 0 | 687164.8675 | 1787862.0283 | 1220252.5712 | 5457240.6656 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9511980.693 | 16203019.96 | 1333521.4322 | 0.096421 | 98650.5854 | 168044.6434 | 2011.1256 | 3425.8174
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.9092 | 2.1504 | 0.026762 | 4 | 92281.6186 | 154787.4962 | 1881.2856 | 3155.5525 | 54.5301 | 0 | 117.1988 | 344587.7442 | 8872.2282 | 662925.0688 | 808164.9832 | 0 | 55725.4272 | 0 | 733307.4261 | 1907915.5007 | 1302191.533 | 5823689.9113 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9878429.9386 | 16569469.2057 | 1778279.41 | 0.10705 | 92281.6186 | 154787.4962 | 1881.2856 | 3155.5525
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.6593 | 2.2856 | 0.029063 | 4 | 87563.628 | 145120.2794 | 1785.103 | 2958.4732 | 54.5361 | 0 | 2350.6464 | 359590.5441 | 9260.8928 | 696072.3836 | 857403.3641 | 0 | 55118.6466 | 0 | 771203.8741 | 2006514.2849 | 1369487.2292 | 6124651.2193 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10179391.2466 | 16870430.5137 | 2371373.7057 | 0.11625 | 87563.628 | 145120.2794 | 1785.103 | 2958.4732
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.8714 | 2.3944 | 0.030985 | 4 | 84064.8337 | 138050.8703 | 1713.7753 | 2814.3537 | 54.5402 | 0 | 91.7343 | 371463.2849 | 9568.4189 | 722446.3826 | 897004.6893 | 0 | 54328.2573 | 0 | 801376.3029 | 2085016.7552 | 1423066.7782 | 6364270.8693 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10419010.8966 | 17110050.1637 | 3162277.6602 | 0.12394 | 84064.8337 | 138050.8703 | 1713.7753 | 2814.3537
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6151 | 2.4801 | 0.032548 | 4 | 81466.2643 | 132859.4943 | 1660.8 | 2708.5205 | 54.5431 | 0 | 122.2136 | 380706.5808 | 9807.803 | 743064.5551 | 928218.5675 | 0 | 53495.2339 | 0 | 824964.1687 | 2146387.5436 | 1464953.6024 | 6551598.0551 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10606338.0824 | 17297377.3495 | 4216965.0343 | 0.13019 | 81466.2643 | 132859.4943 | 1660.8 | 2708.5205
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.977 | 2.5471 | 0.033796 | 4 | 79533.1652 | 129028.4405 | 1621.3911 | 2630.4193 | 54.5451 | 0 | 140.8835 | 387857.754 | 9992.9826 | 759066.4535 | 952595.147 | 0 | 52720.619 | 0 | 843270.8529 | 2194017.7806 | 1497462.2178 | 6696983.8074 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10751723.8348 | 17442763.1018 | 5623413.2519 | 0.13519 | 79533.1652 | 129028.4405 | 1621.3911 | 2630.4193
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0272 | 2.5987 | 0.034777 | 4 | 78092.9049 | 126192.8871 | 1592.0295 | 2572.6127 | 54.5466 | 0 | 117.578 | 393332.6853 | 10134.7418 | 771346.9254 | 971391.0362 | 0 | 52039.4224 | 0 | 857315.4763 | 2230559.0098 | 1522402.3576 | 6808521.6548 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10863261.6821 | 17554300.9492 | 7498942.0933 | 0.13911 | 78092.9049 | 126192.8871 | 1592.0295 | 2572.6127
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.8406 | 2.6387 | 0.035541 | 4 | 77018.3892 | 124083.4143 | 1570.124 | 2529.6082 | 54.5476 | 0 | 129.8422 | 397550.3476 | 10243.9386 | 780824.5783 | 985948.9615 | 0 | 51483.2381 | 0 | 868159.915 | 2258774.0148 | 1541659.6783 | 6894644.6722 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10949384.6995 | 17640423.9666 | 10000000 | 0.14217 | 77018.3892 | 124083.4143 | 1570.124 | 2529.6082
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4582 | [19 empty] | 100 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.1766 | [19 empty] | 133.3521 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.378 | [19 empty] | 177.8279 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 2255.2244 | [19 empty] | 237.1374 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1887 | [19 empty] | 316.2278 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9341 | [19 empty] | 421.6965 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2772 | [19 empty] | 562.3413 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.877 | [19 empty] | 749.8942 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.17 | [19 empty] | 1000 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0209 | [19 empty] | 1333.5214 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.5761 | [19 empty] | 1778.2794 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5133 | [19 empty] | 2371.3737 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 2247.9488 | [19 empty] | 3162.2777 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 39.3602 | [19 empty] | 4216.965 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 37.4091 | [19 empty] | 5623.4133 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.042769 | 0.00013641 | 4 | 8532501.3179 | 21474386.9164 | 173946.5804 | 437784.4235 | 53.3263 | 0 | 62.6182 | 22590.6265 | 550.8629 | 28898.3163 | 39965.8434 | 0 | 16554.3483 | 0 | 42338.399 | 110155.8293 | 75183.617 | 336237.8426 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4655703.2889 | 11717358.1424 | 7498.9421 | 0.00054564 | 8532501.3179 | 21474386.9164 | 173946.5804 | 437784.4235
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.063276 | 0.00033154 | 4 | 3576710.1826 | 8901626.9563 | 72916.0749 | 181471.7058 | 54.7199 | 0 | 192.227 | 30439.2794 | 756.0921 | 39478.3971 | 47081.0251 | 0 | 19076.0514 | 0 | 53364.0297 | 138842.2587 | 94762.6945 | 423799.8281 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4743265.2743 | 11804920.1279 | 10000 | 0.0013262 | 3576710.1826 | 8901626.9563 | 72916.0749 | 181471.7058
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.088779 | 0.00060629 | 4 | 1997239.9271 | 4909060.0877 | 40716.4374 | 100077.8299 | 55.6679 | 0 | 268.1897 | 39130.3064 | 984.7632 | 51715.873 | 55878.5321 | 0 | 21530.181 | 0 | 66003.4657 | 171727.4787 | 117207.5329 | 524178.133 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4843643.5793 | 11905298.4328 | 13335.2143 | 0.0024252 | 1997239.9271 | 4909060.0877 | 40716.4374 | 100077.8299
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.12213 | 0.00098439 | 4 | 1261365.1062 | 3054781.5602 | 25714.6338 | 62275.854 | 56.3724 | 0 | 367.4265 | 49384.4608 | 1255.7985 | 66702.2379 | 67358.877 | 0 | 24262.533 | 0 | 81495.9238 | 212035.6766 | 144718.7062 | 647214.2138 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4966679.6601 | 12028334.5136 | 17782.7941 | 0.0039375 | 1261365.1062 | 3054781.5602 | 25714.6338 | 62275.854
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0714 | 0.16554 | 0.0014966 | 4 | 854883.1021 | 2034510.3062 | 17427.9484 | 41476.2445 | 56.8987 | 0 | 67.6618 | 61489.6443 | 1576.7945 | 85029.8622 | 82285.4272 | 0 | 27317.3283 | 0 | 100502.632 | 261487.2326 | 178470.4092 | 798159.3302 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5117624.7765 | 12179279.63 | 23713.7371 | 0.0059863 | 854883.1021 | 2034510.3062 | 17427.9484 | 41476.2445
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0434 | 0.22125 | 0.0021818 | 4 | 607408.8 | 1416574.3828 | 12382.85 | 28878.7849 | 57.2901 | 0 | 91.9702 | 75636.335 | 1952.649 | 107203.0313 | 101426.0009 | 0 | 30656.6838 | 0 | 123581.133 | 321532.7581 | 219452.7142 | 981441.3054 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5300906.7516 | 12362561.6052 | 31622.7766 | 0.0087271 | 607408.8 | 1416574.3828 | 12382.85 | 28878.7849
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3 | 0.29333 | 0.0030924 | 4 | 446763.8306 | 1017647.6212 | 9107.885 | 20746.1232 | 57.5852 | 0 | 2353.6608 | 92368.0779 | 2397.8193 | 134296.2955 | 126176.9946 | 0 | 34417.0304 | 0 | 151965.9249 | 395384.1642 | 269857.8164 | 1206864.1232 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5526329.5694 | 12587984.423 | 42169.6503 | 0.01237 | 446763.8306 | 1017647.6212 | 9107.885 | 20746.1232
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8251 | 0.3807 | 0.0042759 | 4 | 338310.7192 | 751187.9047 | 6896.9216 | 15313.9815 | 57.7894 | 0 | 70.0982 | 110992.3567 | 2893.6904 | 165408.8951 | 156188.2843 | 0 | 38110.5601 | 0 | 184701.5767 | 480555.6152 | 327989.0818 | 1466840.0603 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5786305.5065 | 12847960.3601 | 56234.1325 | 0.017104 | 338310.7192 | 751187.9047 | 6896.9216 | 15313.9815
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2735 | 0.52134 | 0.0059168 | 4 | 261561.339 | 559936.5116 | 5332.2817 | 11415.0632 | 57.9955 | 0 | 74.2075 | 138453.15 | 3625.8932 | 212668.6447 | 204445.6934 | 0 | 44862.8122 | 0 | 235581.9155 | 612935.8196 | 418341.2915 | 1870915.2201 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 6190380.6664 | 13252035.52 | 74989.4209 | 0.023667 | 261561.339 | 559936.5116 | 5332.2817 | 11415.0632
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4707 | 0.64758 | 0.0079197 | 4 | 206167.9294 | 429082.3599 | 4203.0121 | 8747.4243 | 58.1068 | 0 | 89.7697 | 161199.909 | 4232.75 | 252925.2213 | 247755.572 | 0 | 47964.614 | 0 | 278490.4458 | 724575.0138 | 494537.3355 | 2211680.8614 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 6531146.3077 | 13592801.1612 | 100000 | 0.031679 | 206167.9294 | 429082.3599 | 4203.0121 | 8747.4243
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5593 | 0.82491 | 0.010528 | 4 | 166146.3933 | 333827.9629 | 3387.119 | 6805.5346 | 58.2027 | 0 | 89.9078 | 190969.3755 | 5027.0175 | 306932.824 | 308609.481 | 0 | 52949.05 | 0 | 337150.2217 | 877195.7179 | 598704.1021 | 2677537.7898 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 6997003.236 | 14058658.0896 | 133352.1432 | 0.042113 | 166146.3933 | 333827.9629 | 3387.119 | 6805.5346
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.277 | 1.0384 | 0.013799 | 4 | 136568.4572 | 264510.2883 | 2784.1327 | 5392.4 | 58.2756 | 0 | 115.0816 | 224329.5091 | 5917.1716 | 368953.66 | 381860.663 | 0 | 58030.4219 | 0 | 405245.656 | 1054366.0696 | 719626.5075 | 3218329.6587 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 7537795.105 | 14599449.9585 | 177827.941 | 0.055194 | 136568.4572 | 264510.2883 | 2784.1327 | 5392.4
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6233 | 1.288 | 0.01779 | 4 | 114516.3826 | 213750.2357 | 2334.5714 | 4357.5877 | 58.3308 | 0 | 92.9061 | 260798.6846 | 6890.218 | 438315.7084 | 467502.0183 | 0 | 62982.6884 | 0 | 482230.8339 | 1254665.7107 | 856335.1283 | 3829720.9906 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 8149186.4368 | 15210841.2904 | 237137.3706 | 0.071162 | 114516.3826 | 213750.2357 | 2334.5714 | 4357.5877
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4487 | 1.5651 | 0.022469 | 4 | 97991.2877 | 176561.5753 | 1997.6849 | 3599.4465 | 58.372 | 0 | 101.5968 | 298873.051 | 7905.892 | 512244.3502 | 562588.0109 | 0 | 67313.9425 | 0 | 565080.8462 | 1470224.4479 | 1003458.3958 | 4487688.9367 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 8807154.383 | 15868809.2365 | 316227.766 | 0.089877 | 97991.2877 | 176561.5753 | 1997.6849 | 3599.4465
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.6102 | 1.8615 | 0.027727 | 4 | 85585.6151 | 149258.0405 | 1744.7785 | 3042.827 | 58.4031 | 0 | 108.694 | 337421.5726 | 8933.9191 | 588480.9825 | 664304.6616 | 0 | 70884.824 | 0 | 651310.1243 | 1694575.3413 | 1156582.4905 | 5172493.9158 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 9491959.3621 | 16553614.2156 | 421696.5034 | 0.11091 | 85585.6151 | 149258.0405 | 1744.7785 | 3042.827
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.7823 | 2.1586 | 0.033303 | 4 | 76280.0273 | 129290.6594 | 1555.0715 | 2635.765 | 58.426 | 0 | 2383.638 | 374244.284 | 9915.5863 | 662470.6788 | 766232.5446 | 0 | 73308.9603 | 0 | 735607.1011 | 1913898.7833 | 1306275.2463 | 5841953.1847 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 10161418.6309 | 17223073.4845 | 562341.3252 | 0.13321 | 76280.0273 | 129290.6594 | 1555.0715 | 2635.765
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.7003 | 2.4411 | 0.038896 | 4 | 69316.2906 | 114703.8111 | 1413.1063 | 2338.3923 | 58.4427 | 0 | 133.7519 | 407874.4691 | 10811.8108 | 730953.2909 | 863155.1515 | 0 | 74592.27 | 0 | 814080.927 | 2118071.581 | 1445627.3761 | 6465166.8763 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 10784632.3225 | 17846287.1761 | 749894.2093 | 0.15559 | 69316.2906 | 114703.8111 | 1413.1063 | 2338.3923
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.1197 | 2.6949 | 0.044193 | 4 | 64118.8024 | 104066.4223 | 1307.1485 | 2121.5348 | 58.4544 | 0 | 104.3819 | 437109.0459 | 11590.5951 | 791141.2484 | 950246.4183 | 0 | 74821.9572 | 0 | 883314.6133 | 2298203.431 | 1568571.065 | 7014998.3741 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 11334463.8204 | 18396118.6739 | 1000000 | 0.17677 | 64118.8024 | 104066.4223 | 1307.1485 | 2121.5348
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.9124 | 2.9127 | 0.048961 | 4 | 60247.0492 | 96304.7372 | 1228.2176 | 1963.3023 | 58.4623 | 0 | 115.4617 | 461536.2478 | 12241.0669 | 841877.2332 | 1024971.8594 | 0 | 74259.0179 | 0 | 941805.3158 | 2450384.241 | 1672437.5948 | 7479512.5769 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 11798978.0231 | 18860632.8767 | 1333521.4322 | 0.19584 | 60247.0492 | 96304.7372 | 1228.2176 | 1963.3023
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.0575 | 3.0932 | 0.053077 | 4 | 57365.2772 | 90626.3501 | 1169.4688 | 1847.5407 | 58.4674 | 0 | 134.3142 | 481370.6758 | 12769.048 | 883362.5033 | 1086926.5606 | 0 | 73222.7861 | 0 | 989684.1138 | 2574955.0519 | 1757459.733 | 7859750.4725 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12179215.9188 | 19240870.7723 | 1778279.41 | 0.21231 | 57365.2772 | 90626.3501 | 1169.4688 | 1847.5407
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.5855 | 3.2383 | 0.056508 | 4 | 55220.1096 | 86462.0074 | 1125.7366 | 1762.645 | 58.4705 | 0 | 144.1093 | 497053.0066 | 13186.3686 | 916342.5693 | 1136710.3464 | 0 | 71952.6999 | 0 | 1027745.5464 | 2673983.0922 | 1825048.4053 | 8162022.0347 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12481487.4809 | 19543142.3345 | 2371373.7057 | 0.22603 | 55220.1096 | 86462.0074 | 1125.7366 | 1762.645
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.5929 | 3.3534 | 0.059301 | 4 | 53622.1342 | 83392.2754 | 1093.1597 | 1700.0643 | 58.4725 | 0 | 143.842 | 509349.1512 | 13513.4896 | 942310.6579 | 1176232.5515 | 0 | 70682.1209 | 0 | 1057714.3088 | 2751955.6644 | 1878266.288 | 8400024.2323 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12719489.6786 | 19781144.5321 | 3162277.6602 | 0.23721 | 53622.1342 | 83392.2754 | 1093.1597 | 1700.0643
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1398 | 3.4421 | 0.061517 | 4 | 52430.6109 | 81128.6811 | 1068.8689 | 1653.9179 | 58.4737 | 0 | 138.8127 | 518733.5786 | 13763.0918 | 962193.5384 | 1206682.3853 | 0 | 69466.1007 | 0 | 1080627.091 | 2811570.0237 | 1918954.3131 | 8581990.1227 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12901455.5689 | 19963110.4225 | 4216965.0343 | 0.24607 | 52430.6109 | 81128.6811 | 1068.8689 | 1653.9179
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.3534 | 3.5116 | 0.063268 | 4 | 51541.2566 | 79445.1141 | 1050.7382 | 1619.5961 | 58.4744 | 0 | 124.3258 | 526041.3726 | 13957.4251 | 977714.7922 | 1230565.0083 | 0 | 68451.5768 | 0 | 1098524.7682 | 2858136.1086 | 1950736.6229 | 8724127.6747 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13043593.121 | 20105247.9745 | 5623413.2519 | 0.25307 | 51541.2566 | 79445.1141 | 1050.7382 | 1619.5961
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2546 | 3.5633 | 0.064609 | 4 | 50876.8198 | 78201.3313 | 1037.1928 | 1594.2399 | 58.4748 | 0 | 2370.3776 | 531438.5616 | 14100.9296 | 989199.4203 | 1248299.3073 | 0 | 67541.6383 | 0 | 1111726.1442 | 2892483.3808 | 1974179.342 | 8828968.7239 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13148434.1702 | 20210089.0238 | 7498942.0933 | 0.25844 | 50876.8198 | 78201.3313 | 1037.1928 | 1594.2399
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.9586 | 3.6036 | 0.065652 | 4 | 50380.0207 | 77270.4479 | 1027.0649 | 1575.2626 | 58.475 | 0 | 130.4172 | 535636.8598 | 14212.5445 | 998145.4603 | 1262150.345 | 0 | 66841.1583 | 0 | 1122024.6835 | 2919278.0675 | 1992467.2662 | 8910756.3851 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13230221.8314 | 20291876.6849 | 10000000 | 0.26261 | 50380.0207 | 77270.4479 | 1027.0649 | 1575.2626
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 16.602 | [19 empty] | 100 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9137 | [19 empty] | 133.3521 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5774 | [19 empty] | 177.8279 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8794 | [19 empty] | 237.1374 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.818 | [19 empty] | 316.2278 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9675 | [19 empty] | 421.6965 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.4513 | [19 empty] | 562.3413 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 2247.895 | [19 empty] | 749.8942 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.1935 | [19 empty] | 1000 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.8107 | [19 empty] | 1333.5214 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.4453 | [19 empty] | 1778.2794 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 36.2726 | [19 empty] | 2371.3737 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 39.6325 | [19 empty] | 3162.2777 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.0365 | 8.5739e-05 | 4 | 14299073.7213 | 35994200.0758 | 291505.9587 | 733790.4543 | 54.93 | 0 | 78.0096 | 21020.0829 | 517.6032 | 25416.4769 | 37303.6059 | 0 | 17090.9573 | 0 | 39526.0032 | 102838.5525 | 70189.4252 | 313902.7071 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 4903953.6632 | 12344428.2304 | 4216.965 | 0.00034296 | 14299073.7213 | 35994200.0758 | 291505.9587 | 733790.4543
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0485 | 0.056778 | 0.00030168 | 4 | 4138957.4803 | 10304737.8194 | 84378.2466 | 210076.0186 | 57.0209 | 0 | 164.791 | 29638.6279 | 748.0792 | 36120.2701 | 44006.2799 | 0 | 20112.6968 | 0 | 50944.122 | 132546.1553 | 90465.4746 | 404581.7057 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 4994632.6617 | 12435107.229 | 5623.4133 | 0.0012067 | 4138957.4803 | 10304737.8194 | 84378.2466 | 210076.0186
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.082088 | 0.00061797 | 4 | 2062374.701 | 5072442.4356 | 42044.2978 | 103408.6 | 58.4131 | 0 | 245.5122 | 39154.0472 | 1005.1831 | 48445.9302 | 52305.2038 | 0 | 23059.5545 | 0 | 63948.2684 | 166380.2767 | 113557.9576 | 507856.4217 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5097907.3777 | 12538381.945 | 7498.9421 | 0.0024719 | 2062374.701 | 5072442.4356 | 42044.2978 | 103408.6
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.11516 | 0.0010608 | 4 | 1230957.5389 | 2984418.6176 | 25094.7344 | 60841.4102 | 59.4274 | 0 | 2589.0179 | 50299.413 | 1308.2182 | 63452.1412 | 63107.5473 | 0 | 26297.8283 | 0 | 79741.4077 | 207470.7857 | 141603.0743 | 633280.4157 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5223331.3717 | 12663805.939 | 10000 | 0.0042433 | 1230957.5389 | 2984418.6176 | 25094.7344 | 60841.4102
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5849 | 0.15725 | 0.0016653 | 4 | 806558.2527 | 1923534.1275 | 16442.7809 | 39213.845 | 60.1627 | 0 | 490.114 | 63116.0435 | 1658.0275 | 81355.7628 | 76829.6793 | 0 | 29731.7551 | 0 | 98549.5946 | 256405.8298 | 175002.2474 | 782648.94 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5372699.896 | 12813174.4633 | 13335.2143 | 0.0066613 | 806558.2527 | 1923534.1275 | 16442.7809 | 39213.845
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4197 | 0.21214 | 0.0024802 | 4 | 560061.8302 | 1310034.2433 | 11417.6179 | 26706.82 | 60.7168 | 0 | 84.9383 | 78294.4303 | 2073.2462 | 103318.3825 | 94695.601 | 0 | 33611.2486 | 0 | 121677.2344 | 316579.2044 | 216071.8121 | 966321.1595 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5556372.1155 | 12996846.6828 | 17782.7941 | 0.009921 | 560061.8302 | 1310034.2433 | 11417.6179 | 26706.82
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5038 | 0.28344 | 0.0035704 | 4 | 404889.1895 | 925877.3973 | 8254.2138 | 18875.2631 | 61.1355 | 0 | 117.8906 | 96283.6119 | 2566.2115 | 130219.292 | 117893.3121 | 0 | 38010.7661 | 0 | 150139.5455 | 390632.2995 | 266614.5711 | 1192359.6098 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5782410.5658 | 13222885.1331 | 23713.7371 | 0.014281 | 404889.1895 | 925877.3973 | 8254.2138 | 18875.2631
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.848 | 0.37177 | 0.0050072 | 4 | 301973.1836 | 673465.1045 | 6156.1318 | 13729.4971 | 61.4388 | 0 | 125.0863 | 116715.6222 | 3126.7594 | 161733.0125 | 146636.195 | 0 | 42546.9177 | 0 | 183595.8177 | 477678.6569 | 326025.4986 | 1458058.48 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6048109.4361 | 13488584.0033 | 31622.7766 | 0.020029 | 301973.1836 | 673465.1045 | 6156.1318 | 13729.4971
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4876 | 0.47922 | 0.0068587 | 4 | 231680.0651 | 502887.1011 | 4723.1115 | 10252.0338 | 61.6431 | 0 | 114.5895 | 139588.8652 | 3754.1576 | 198119.1017 | 181635.5539 | 0 | 47089.5182 | 0 | 222373.0067 | 578568.9483 | 394885.1956 | 1766014.3472 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6356065.3032 | 13796539.8705 | 42169.6503 | 0.027435 | 231680.0651 | 502887.1011 | 4723.1115 | 10252.0338
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8434 | 0.63461 | 0.0094114 | 4 | 180236.1246 | 377881.6803 | 3674.3572 | 7703.6292 | 61.8649 | 0 | 122.2231 | 170182.0839 | 4595.1757 | 247976.3446 | 232117.1744 | 0 | 53833.247 | 0 | 276394.57 | 719121.9749 | 490815.5243 | 2195036.0949 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6785087.0509 | 14225561.6182 | 56234.1325 | 0.037646 | 180236.1246 | 377881.6803 | 3674.3572 | 7703.6292
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6085 | 0.81654 | 0.012637 | 4 | 143700.8705 | 290893.9141 | 2929.5366 | 5930.2659 | 62.0017 | 0 | 119.4603 | 203139.6438 | 5500.5664 | 303337.1864 | 291275.9095 | 0 | 60059.0942 | 0 | 336691.8361 | 876003.0926 | 597890.1108 | 2673897.4398 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 7263948.3958 | 14704422.9631 | 74989.4209 | 0.050549 | 143700.8705 | 290893.9141 | 2929.5366 | 5930.2659
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9749 | 1.0382 | 0.016746 | 4 | 116809.4677 | 227888.6594 | 2381.319 | 4645.8186 | 62.1048 | 0 | 107.3435 | 240389.3961 | 6523.6807 | 367549.1072 | 363327.2682 | 0 | 66444.5879 | 0 | 407251.2757 | 1059584.2806 | 723188.0438 | 3234257.6403 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 7824308.5963 | 15264783.1636 | 100000 | 0.066984 | 116809.4677 | 227888.6594 | 2381.319 | 4645.8186
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.046 | 1.3062 | 0.021902 | 4 | 96766.5195 | 181694.2229 | 1972.7164 | 3704.0825 | 62.1837 | 0 | 2367.0156 | 282356.2005 | 7676.1077 | 441651.2819 | 450464.0765 | 0 | 73034.1812 | 0 | 489520.9206 | 1273633.021 | 869280.7073 | 3887616.4967 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 8477667.4528 | 15918142.0201 | 133352.1432 | 0.08761 | 96766.5195 | 181694.2229 | 1972.7164 | 3704.0825
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7808 | 1.618 | 0.028188 | 4 | 81700.0598 | 147690.2641 | 1665.5662 | 3010.8658 | 62.2434 | 0 | 130.836 | 328023.1715 | 8929.7001 | 524110.8562 | 551811.6208 | 0 | 79326.8488 | 0 | 581958.857 | 1514137.5696 | 1033430.0037 | 4621728.6276 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 9211779.5836 | 16652254.1509 | 177827.941 | 0.11275 | 81700.0598 | 147690.2641 | 1665.5662 | 3010.8658
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.1166 | 1.9693 | 0.035602 | 4 | 70316.9003 | 122564.9789 | 1433.5051 | 2498.6529 | 62.2887 | 0 | 115.1195 | 376427.5769 | 10257.8322 | 613317.7962 | 666028.8616 | 0 | 85049.6753 | 0 | 682921.8795 | 1776822.6439 | 1212717.9645 | 5423544.2302 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 10013595.1862 | 17454069.7535 | 237137.3706 | 0.14241 | 70316.9003 | 122564.9789 | 1433.5051 | 2498.6529
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.824 | 2.3452 | 0.04395 | 4 | 61701.6839 | 104025.3866 | 1257.8723 | 2120.6982 | 62.3227 | 0 | 130.4135 | 425424.9139 | 11601.5334 | 705282.4064 | 788208.9633 | 0 | 89677.7157 | 0 | 787876.2577 | 2049892.407 | 1399093.6889 | 6257057.8863 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 10847108.8423 | 18287583.4096 | 316227.766 | 0.1758 | 61701.6839 | 104025.3866 | 1257.8723 | 2120.6982
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.6091 | 2.7263 | 0.052867 | 4 | 55189.194 | 90373.9508 | 1125.1064 | 1842.3952 | 62.3478 | 0 | 138.2522 | 472750.4791 | 12898.6619 | 795532.796 | 912057.6264 | 0 | 92894.1369 | 0 | 891592.1432 | 2319739.8658 | 1583270.1243 | 7080735.8337 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 11670786.7897 | 19111261.357 | 421696.5034 | 0.21147 | 55189.194 | 90373.9508 | 1125.1064 | 1842.3952
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.1586 | 3.0917 | 0.061869 | 4 | 50281.8841 | 80347.4657 | 1025.0642 | 1637.9918 | 62.3657 | 0 | 122.6883 | 516316.4752 | 14092.0404 | 879745.5984 | 1030851.7122 | 0 | 94611.3853 | 0 | 988890.7125 | 2572890.7845 | 1756050.828 | 7853449.5364 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 12443500.4924 | 19883975.0597 | 562341.3252 | 0.24747 | 50281.8841 | 80347.4657 | 1025.0642 | 1637.9918
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.1498 | 3.4203 | 0.070415 | 4 | 46597.9202 | 73014.5373 | 949.9616 | 1488.5001 | 62.3774 | 0 | 116.5262 | 554181.9887 | 15128.6355 | 953766.6952 | 1137669.3904 | 0 | 94812.8088 | 0 | 1074668.2123 | 2796066.2436 | 1908372.6647 | 8534666.6391 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 13124717.5952 | 20565192.1624 | 749894.2093 | 0.28166 | 46597.9202 | 73014.5373 | 949.9616 | 1488.5001
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4734 | 3.7047 | 0.078153 | 4 | 43840.7271 | 67641.8255 | 893.7525 | 1378.9701 | 62.3845 | 0 | 158.6867 | 586085.0984 | 16001.4764 | 1016705.2924 | 1230166.9691 | 0 | 93978.426 | 0 | 1147745.5323 | 2986198.44 | 2038141.7956 | 9115023.0302 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 13705073.9862 | 21145548.5535 | 1000000 | 0.31261 | 43840.7271 | 67641.8255 | 893.7525 | 1378.9701
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.0498 | 3.9399 | 0.084836 | 4 | 41780.8928 | 63706.9091 | 851.76 | 1298.7515 | 62.3883 | 0 | 128.2861 | 611896.7604 | 16707.2582 | 1068000.7436 | 1306644.4548 | 0 | 92418.5627 | 0 | 1207310.4341 | 3141174.0961 | 2143915.8653 | 9588068.1752 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14178119.1313 | 21618593.6985 | 1333521.4322 | 0.33934 | 41780.8928 | 63706.9091 | 851.76 | 1298.7515
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.9586 | 4.1309 | 0.090441 | 4 | 40243.1034 | 60810.381 | 820.4101 | 1239.7019 | 62.39 | 0 | 2390.5618 | 632528.9337 | 17271.1278 | 1109240.165 | 1368818.3595 | 0 | 90607.0186 | 0 | 1255201.5858 | 3265777.049 | 2228959.941 | 9968404.1804 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14558455.1364 | 21998929.7037 | 1778279.41 | 0.36176 | 40243.1034 | 60810.381 | 820.4101 | 1239.7019
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2554 | 4.2817 | 0.094998 | 4 | 39094.9811 | 58675.6307 | 797.0041 | 1196.1821 | 62.3904 | 0 | 171.3894 | 648601.3092 | 17710.1889 | 1141510.3006 | 1417888.6557 | 0 | 88741.3621 | 0 | 1292636.2084 | 3363174.2582 | 2295435.5375 | 10265697.8206 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14855748.7766 | 22296223.3439 | 2371373.7057 | 0.37999 | 39094.9811 | 58675.6307 | 797.0041 | 1196.1821
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.0413 | 4.3989 | 0.098627 | 4 | 38237.3901 | 57097.459 | 779.5209 | 1164.0089 | 62.3903 | 0 | 146.3933 | 660969.8811 | 18047.9497 | 1166429.8763 | 1456029.0162 | 0 | 86995.9155 | 0 | 1321504.3291 | 3438283.1866 | 2346698.9245 | 10494959.0791 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15085010.0351 | 22525484.6024 | 3162277.6602 | 0.39451 | 38237.3901 | 57097.459 | 779.5209 | 1164.0089
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.4297 | 4.4899 | 0.10149 | 4 | 37596.4194 | 55925.025 | 766.4539 | 1140.1073 | 62.3898 | 0 | 145.5012 | 670509.9328 | 18308.3944 | 1185701.62 | 1485671.1697 | 0 | 85496.5807 | 0 | 1343818.2021 | 3496339.3068 | 2386323.4195 | 10672168.6259 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15262219.582 | 22702694.1492 | 4216965.0343 | 0.40595 | 37596.4194 | 55925.025 | 766.4539 | 1140.1073
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.4897 | 4.5594 | 0.1037 | 4 | 37117.055 | 55053.8097 | 756.6814 | 1122.3464 | 62.3893 | 0 | 146.5376 | 677749.6505 | 18505.9946 | 1200356.0436 | 1508295.8135 | 0 | 84229.5584 | 0 | 1360763.4536 | 3540427.3754 | 2416414.4322 | 10806742.3218 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15396793.2779 | 22837267.8451 | 5623413.2519 | 0.41482 | 37117.055 | 55053.8097 | 756.6814 | 1122.3464
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.2861 | 4.6115 | 0.1054 | 4 | 36758.3513 | 54406.4604 | 749.3687 | 1109.1493 | 62.3888 | 0 | 140.5578 | 683164.8491 | 18653.7706 | 1211333.989 | 1525291.9001 | 0 | 83170.936 | 0 | 1373430.0235 | 3573383.1918 | 2438907.4541 | 10907336.1141 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15497387.0701 | 22937861.6374 | 7498942.0933 | 0.4216 | 36758.3513 | 54406.4604 | 749.3687 | 1109.1493
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.8929 | 4.6513 | 0.1067 | 4 | 36489.8108 | 53923.0092 | 743.8941 | 1099.2935 | 62.3884 | 0 | 128.2148 | 687276.4239 | 18765.9567 | 1219678.6845 | 1538238.2489 | 0 | 82334.0754 | 0 | 1383054.4219 | 3598423.9022 | 2455998.2535 | 10983769.967 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15573820.9231 | 23014295.4903 | 10000000 | 0.4268 | 36489.8108 | 53923.0092 | 743.8941 | 1099.2935
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.1506 | [19 empty] | 100 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.1548 | [19 empty] | 133.3521 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 2251.7907 | [19 empty] | 177.8279 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.896 | [19 empty] | 237.1374 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.129 | [19 empty] | 316.2278 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9595 | [19 empty] | 421.6965 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7918 | [19 empty] | 562.3413 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.664 | [19 empty] | 749.8942 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2853 | [19 empty] | 1000 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5418 | [19 empty] | 1333.5214 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.9842 | [19 empty] | 1778.2794 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.2855 | [19 empty] | 2371.3737 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79142 | 0.044851 | 0.00016323 | 4 | 8002898.3347 | 19991496.3132 | 163149.9073 | 407553.6928 | 58.2087 | 0 | 81.3702 | 25818.5786 | 654.8368 | 29876.596 | 39545.8598 | 0 | 19913.5295 | 0 | 45165.6663 | 117511.7989 | 80204.2173 | 358691.0831 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5225187.6398 | 13052686.048 | 3162.2777 | 0.00065291 | 8002898.3347 | 19991496.3132 | 163149.9073 | 407553.6928
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.067795 | 0.00048316 | 4 | 2755057.6893 | 6805209.2667 | 56165.5775 | 138733.3956 | 60.3548 | 0 | 174.4477 | 35590.8419 | 924.5187 | 41494.3553 | 46758.9574 | 0 | 23119.5378 | 0 | 57676.4023 | 150062.1678 | 102420.513 | 458047.2943 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5324543.851 | 13152042.2592 | 4216.965 | 0.0019326 | 2755057.6893 | 6805209.2667 | 56165.5775 | 138733.3956
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4764 | 0.094912 | 0.00093844 | 4 | 1447098.29 | 3532337.4443 | 29501.056 | 72011.4766 | 61.7776 | 0 | 240.7233 | 45923.4716 | 1212.6096 | 54236.7885 | 55226.7425 | 0 | 26004.3599 | 0 | 71215.5491 | 185288.2505 | 126463.0382 | 565570.8098 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5432067.3665 | 13259565.7747 | 5623.4133 | 0.0037538 | 1447098.29 | 3532337.4443 | 29501.056 | 72011.4766
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.1323 | 0.00156 | 4 | 892846.2257 | 2147282.9731 | 18201.878 | 43775.2678 | 62.9061 | 0 | 330.0535 | 58753.7835 | 1572.2826 | 70669.5187 | 66850.0211 | 0 | 29688.513 | 0 | 88738.3064 | 230878.8704 | 157579.5732 | 704730.8688 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5571227.4255 | 13398725.8337 | 7498.9421 | 0.0062399 | 892846.2257 | 2147282.9731 | 18201.878 | 43775.2678
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6426 | 0.18149 | 0.0024233 | 4 | 592398.6627 | 1399921.3751 | 12076.848 | 28539.2908 | 63.7531 | 0 | 68.0158 | 73976.3128 | 2000.2252 | 90932.595 | 82085.0874 | 0 | 33758.3069 | 0 | 110273.4857 | 286908.9896 | 195821.2808 | 875756.2834 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5742252.8401 | 13569751.2483 | 10000 | 0.0096932 | 592398.6627 | 1399921.3751 | 12076.848 | 28539.2908
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5246 | 0.24722 | 0.0035902 | 4 | 414869.5269 | 959922.5879 | 8457.6765 | 19569.3203 | 64.4025 | 0 | 74.9673 | 92441.4327 | 2520.6413 | 116374.2376 | 102426.713 | 0 | 38625.9995 | 0 | 137431.7194 | 357569.1428 | 244048.2873 | 1091438.1736 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5957934.7303 | 13785433.1385 | 13335.2143 | 0.014361 | 414869.5269 | 959922.5879 | 8457.6765 | 19569.3203
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.687 | 0.33391 | 0.0051134 | 4 | 304467.2062 | 687160.8461 | 6206.9758 | 14008.7033 | 64.892 | 0 | 64.6303 | 114591.9821 | 3145.8733 | 147939.8319 | 129234.2172 | 0 | 44503.9553 | 0 | 171372.1853 | 445875.2729 | 304319.0356 | 1360982.3536 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6227478.9103 | 14054977.3185 | 17782.7941 | 0.020454 | 304467.2062 | 687160.8461 | 6206.9758 | 14008.7033
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.287 | 0.45332 | 0.0072277 | 4 | 227569.2386 | 498316.0464 | 4639.3067 | 10158.8466 | 65.267 | 0 | 82.9706 | 142337.7823 | 3929.2689 | 188870.2623 | 166154.8831 | 0 | 51683.2272 | 0 | 215660.4153 | 561104.1626 | 382965.1205 | 1712705.1222 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6579201.6789 | 14406700.0871 | 23713.7371 | 0.028911 | 227569.2386 | 498316.0464 | 4639.3067 | 10158.8466
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.387 | 0.60924 | 0.0099295 | 4 | 176642.6673 | 373718.5323 | 3601.0997 | 7618.7578 | 65.4969 | 0 | 78.2001 | 175240.7753 | 4857.0156 | 239209.1027 | 214458.0149 | 0 | 60215.0887 | 0 | 270652.1989 | 704181.5031 | 480618.3453 | 2149432.0444 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7015928.6011 | 14843427.0093 | 31622.7766 | 0.039718 | 176642.6673 | 373718.5323 | 3601.0997 | 7618.7578
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3038 | 0.75378 | 0.013395 | 4 | 138004.6561 | 284090.9921 | 2813.4116 | 5791.5791 | 65.7173 | 0 | 111.3091 | 203760.3931 | 5664.7672 | 283568.7513 | 258963.2546 | 0 | 64241.6731 | 0 | 318317.5473 | 828196.9622 | 565261.4444 | 2527974.7931 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7394471.3498 | 15221969.758 | 42169.6503 | 0.053581 | 138004.6561 | 284090.9921 | 2813.4116 | 5791.5791
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1808 | 0.96895 | 0.017959 | 4 | 110588.9494 | 219552.6539 | 2254.5053 | 4475.8778 | 65.8697 | 0 | 94.2257 | 243090.9867 | 6775.8196 | 346611.8678 | 325425.9444 | 0 | 71799.1825 | 0 | 387544.4824 | 1008311.2468 | 688193.1447 | 3077752.6749 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7944249.2316 | 15771747.6398 | 56234.1325 | 0.071836 | 110588.9494 | 219552.6539 | 2254.5053 | 4475.8778
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.7176 | 1.2335 | 0.023791 | 4 | 90301.6008 | 172554.6722 | 1840.9203 | 3517.7604 | 65.9858 | 0 | 94.9736 | 287977.8449 | 8043.4406 | 420404.2781 | 407135.3292 | 0 | 79740.2823 | 0 | 469287.4583 | 1220989.7024 | 833350.5607 | 3726928.8965 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 8593425.4531 | 16420923.8613 | 74989.4209 | 0.095164 | 90301.6008 | 172554.6722 | 1840.9203 | 3517.7604
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9714 | 1.5516 | 0.031107 | 4 | 75102.2143 | 138009.5691 | 1531.0602 | 2813.5117 | 66.0741 | 0 | 78.1117 | 338266.0677 | 9463.0706 | 505052.4819 | 505370.1949 | 0 | 87773.0019 | 0 | 563910.6786 | 1467179.9118 | 1001380.4374 | 4478395.8448 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 9344892.4015 | 17172390.8097 | 100000 | 0.12443 | 75102.2143 | 138009.5691 | 1531.0602 | 2813.5117
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9749 | 1.9257 | 0.04008 | 4 | 63612.7369 | 112437.0567 | 1296.8317 | 2292.1815 | 66.1415 | 0 | 98.3463 | 393606.6016 | 11024.434 | 600297.091 | 620920.1427 | 0 | 95636.8223 | 0 | 671379.1857 | 1746790.9225 | 1192220.6976 | 5331875.8975 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 10198372.4541 | 18025870.8623 | 133352.1432 | 0.16032 | 63612.7369 | 112437.0567 | 1296.8317 | 2292.1815
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.6487 | 2.35 | 0.050727 | 4 | 54878.8309 | 93455.5301 | 1118.7792 | 1905.2174 | 66.1928 | 0 | 92.0622 | 452601.9063 | 12687.795 | 703930.927 | 751955.9315 | 0 | 102818.2878 | 0 | 789357.9906 | 2053747.5719 | 1401724.9181 | 6268825.3282 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 11135321.8849 | 18962820.2931 | 177827.941 | 0.20291 | 54878.8309 | 93455.5301 | 1118.7792 | 1905.2174
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8165 | 2.8113 | 0.062853 | 4 | 48225.0422 | 79359.2418 | 983.1327 | 1617.8455 | 66.2316 | 0 | 113.6391 | 513237.5581 | 14396.1665 | 812429.8375 | 894409.9778 | 0 | 108840.4436 | 0 | 913892.4536 | 2377760.699 | 1622870.5352 | 7257837.6713 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 12124334.228 | 19951832.6361 | 237137.3706 | 0.25141 | 48225.0422 | 79359.2418 | 983.1327 | 1617.8455
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.1501 | 3.285 | 0.075954 | 4 | 43161.6323 | 68925.6977 | 879.9083 | 1405.1436 | 66.2602 | 0 | 123.7453 | 572487.5802 | 16064.2209 | 920186.951 | 1040691.3155 | 0 | 113133.9811 | 0 | 1038399.979 | 2701703.7401 | 1843968.3171 | 8246636.0847 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 13113132.6414 | 20940631.0496 | 316227.766 | 0.30381 | 43161.6323 | 68925.6977 | 879.9083 | 1405.1436
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.2861 | 3.7438 | 0.089316 | 4 | 39322.475 | 61232.1245 | 801.6418 | 1248.2997 | 66.2797 | 0 | 117.1326 | 627483.4838 | 17611.2503 | 1021617.0342 | 1182384.2527 | 0 | 115450.7526 | 0 | 1156173.2417 | 3008125.6111 | 2053107.5404 | 9181953.1666 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 14048449.7233 | 21875948.1315 | 421696.5034 | 0.35726 | 39322.475 | 61232.1245 | 801.6418 | 1248.2997
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.9035 | 4.1635 | 0.10217 | 4 | 36424.9178 | 55577.245 | 742.5712 | 1133.0173 | 66.2917 | 0 | 109.2533 | 676047.8396 | 18976.19 | 1112249.6397 | 1312050.62 | 0 | 115883.0418 | 0 | 1261730.8591 | 3282764.8787 | 2240554.4838 | 10020257.5526 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 14886754.1093 | 22714252.5174 | 562341.3252 | 0.4087 | 36424.9178 | 55577.245 | 742.5712 | 1133.0173
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.7855 | 4.5279 | 0.11389 | 4 | 34246.815 | 51428.6065 | 698.1676 | 1048.4417 | 66.2977 | 0 | 133.5396 | 717021.0238 | 20126.7793 | 1189464.9614 | 1424676.2983 | 0 | 114783.0613 | 0 | 1351768.1284 | 3517023.3843 | 2400440.7274 | 10735304.3641 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 15601800.9208 | 23429299.329 | 749894.2093 | 0.45557 | 34246.815 | 51428.6065 | 698.1676 | 1048.4417
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.8681 | 4.8323 | 0.12411 | 4 | 32614.0016 | 48381.8782 | 664.8805 | 986.33 | 66.2996 | 0 | 141.296 | 750478.2183 | 21065.5393 | 1253015.4561 | 1518798.596 | 0 | 112708.6533 | 0 | 1425865.9206 | 3709810.6401 | 2532021.9908 | 11323765.0145 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 16190261.5712 | 24017759.9794 | 1000000 | 0.49642 | 32614.0016 | 48381.8782 | 664.8805 | 986.33
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.1861 | 5.0794 | 0.13269 | 4 | 31391.7608 | 46138.9254 | 639.9635 | 940.6044 | 66.2991 | 0 | 125.3787 | 777160.981 | 21813.6699 | 1304016.9784 | 1595239.9795 | 0 | 110180.7288 | 0 | 1485280.8117 | 3864395.999 | 2637529.6747 | 11795618.823 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 16662115.3797 | 24489613.7879 | 1333521.4322 | 0.53078 | 31391.7608 | 46138.9254 | 639.9635 | 940.6044
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.8346 | 5.2764 | 0.13973 | 4 | 30477.3625 | 44481.8161 | 621.3223 | 906.822 | 66.2974 | 0 | 124.473 | 798147.4558 | 22401.7184 | 1344328.5168 | 1656216.7597 | 0 | 107609.3925 | 0 | 1532194.4989 | 3986455.7897 | 2720837.9899 | 12168192.1217 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17034688.6784 | 24862187.0866 | 1778279.41 | 0.55893 | 30477.3625 | 44481.8161 | 621.3223 | 906.822
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.8996 | 5.4299 | 0.14536 | 4 | 29793.2837 | 43255.9602 | 607.3764 | 881.8313 | 66.2953 | 0 | 150.5181 | 814326.1063 | 22854.8146 | 1375523.8161 | 1703736.3975 | 0 | 105179.416 | 0 | 1568432.0147 | 4080738.3727 | 2785187.7902 | 12455978.7282 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17322475.2849 | 25149973.6931 | 2371373.7057 | 0.58142 | 29793.2837 | 43255.9602 | 607.3764 | 881.8313
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.5003 | 5.5488 | 0.14979 | 4 | 29281.3864 | 42345.7177 | 596.9407 | 863.2747 | 66.2932 | 0 | 131.6336 | 826757.517 | 23202.8209 | 1399564.0348 | 1740552.253 | 0 | 103051.476 | 0 | 1596319.9597 | 4153297.0848 | 2834710.6021 | 12677455.7484 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17543952.305 | 25371450.7132 | 3162277.6602 | 0.59915 | 29281.3864 | 42345.7177 | 596.9407 | 863.2747
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.7307 | 5.6401 | 0.15324 | 4 | 28898.2034 | 41668.348 | 589.129 | 849.4656 | 66.2913 | 0 | 146.2863 | 836249.9773 | 23468.4661 | 1417961.9575 | 1768841.2813 | 0 | 101263.8971 | 0 | 1617636.3759 | 4208758.0273 | 2872563.835 | 12846743.8175 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17713240.3741 | 25540738.7823 | 4216965.0343 | 0.61295 | 28898.2034 | 41668.348 | 589.129 | 849.4656
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6781 | 5.7104 | 0.15591 | 4 | 28611.2723 | 41162.5922 | 583.2795 | 839.1551 | 66.2897 | 0 | 144.2748 | 843522.2477 | 23671.927 | 1432080.9034 | 1790617.4213 | 0 | 99826.3984 | 0 | 1633990.3701 | 4251307.7656 | 2901604.9057 | 12976621.9392 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17843118.4959 | 25670616.904 | 5623413.2519 | 0.62364 | 28611.2723 | 41162.5922 | 583.2795 | 839.1551
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.3897 | 5.7631 | 0.15794 | 4 | 28396.3498 | 40785.9614 | 578.898 | 831.477 | 66.2884 | 0 | 138.6215 | 848963.5739 | 23824.132 | 1442658.8042 | 1806969.7715 | 0 | 98654.0887 | 0 | 1646217.4444 | 4283120.1048 | 2923317.4808 | 13073725.4003 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17940221.957 | 25767720.3652 | 7498942.0933 | 0.63178 | 28396.3498 | 40785.9614 | 578.898 | 831.477
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.9233 | 5.8027 | 0.15949 | 4 | 28235.3233 | 40505.0597 | 575.6153 | 825.7504 | 66.2873 | 0 | 140.7752 | 853032.2257 | 23937.9232 | 1450575.8976 | 1819229.8328 | 0 | 97718.0507 | 0 | 1655352.6327 | 4306887.9908 | 2939539.5514 | 13146274.105 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 18012770.6617 | 25840269.0699 | 10000000 | 0.63795 | 28235.3233 | 40505.0597 | 575.6153 | 825.7504
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.8735 | [19 empty] | 100 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.067 | [19 empty] | 133.3521 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.092 | [19 empty] | 177.8279 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8802 | [19 empty] | 237.1374 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.786 | [19 empty] | 316.2278 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9746 | [19 empty] | 421.6965 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6606 | [19 empty] | 562.3413 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7913 | [19 empty] | 749.8942 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.2076 | [19 empty] | 1000 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5565 | [19 empty] | 1333.5214 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.3985 | [19 empty] | 1778.2794 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79142 | 0.049426 | 0.00021819 | 4 | 6340788.8808 | 15762271.2858 | 129265.5579 | 321335.2202 | 60.91 | 0 | 76.9425 | 28962.9401 | 751.4078 | 32208.3713 | 40486.6746 | 0 | 21961.1547 | 0 | 48504.5139 | 126198.7955 | 86133.2711 | 385207.129 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5534009.3772 | 13756735.7535 | 2371.3737 | 0.00087276 | 6340788.8808 | 15762271.2858 | 129265.5579 | 321335.2202
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.076622 | 0.00062345 | 4 | 2266183.8575 | 5563461.8406 | 46199.2232 | 113418.6948 | 63.4692 | 0 | 168.2787 | 40771.5677 | 1086.7373 | 45628.4988 | 48661.024 | 0 | 26121.5965 | 0 | 63285.0755 | 164654.7848 | 112380.274 | 502589.5586 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5651391.8068 | 13874118.1831 | 3162.2777 | 0.0024938 | 2266183.8575 | 5563461.8406 | 46199.2232 | 113418.6948
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5347 | 0.11035 | 0.0012139 | 4 | 1191167.5322 | 2884616.9491 | 24283.5613 | 58806.8182 | 65.1798 | 0 | 240.9276 | 53733.405 | 1458.5813 | 60993.9891 | 58700.9646 | 0 | 30146.396 | 0 | 79963.0011 | 208047.3261 | 141996.575 | 635040.2383 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5783842.4865 | 14006568.8628 | 4216.965 | 0.0048556 | 1191167.5322 | 2884616.9491 | 24283.5613 | 58806.8182
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.15568 | 0.0020403 | 4 | 728968.1033 | 1736493.0374 | 14861.0008 | 35400.7593 | 66.4666 | 0 | 333.1166 | 69345.8558 | 1909.1014 | 80233.0833 | 72130.7502 | 0 | 34847.1724 | 0 | 100801.7256 | 262265.4128 | 179001.5332 | 800534.6348 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5949336.883 | 14172063.2593 | 5623.4133 | 0.0081613 | 728968.1033 | 1736493.0374 | 14861.0008 | 35400.7593
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7546 | 0.21198 | 0.0031653 | 4 | 485029.119 | 1134479.6996 | 9887.9746 | 23127.9032 | 67.3821 | 0 | 68.7706 | 86893.4999 | 2417.5113 | 102622.4113 | 88772.2085 | 0 | 39634.8654 | 0 | 124932.7936 | 325049.5017 | 221852.964 | 992175.7557 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6140978.0039 | 14363704.3802 | 7498.9421 | 0.012661 | 485029.119 | 1134479.6996 | 9887.9746 | 23127.9032
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6561 | 0.2873 | 0.004686 | 4 | 340534.6631 | 779221.8034 | 6942.2597 | 15885.4904 | 68.0918 | 0 | 77.3597 | 108231.0537 | 3036.9454 | 130795.2389 | 111009.7541 | 0 | 45396.0819 | 0 | 155402.9389 | 404326.5694 | 275961.1917 | 1234159.7739 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6382962.0221 | 14605688.3984 | 10000 | 0.018744 | 340534.6631 | 779221.8034 | 6942.2597 | 15885.4904
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7887 | 0.38209 | 0.0067105 | 4 | 248495.488 | 554832.6463 | 5065.9166 | 11311.014 | 68.6121 | 0 | 66.815 | 132732.3003 | 3748.8577 | 164229.2269 | 138969.0266 | 0 | 51508.4632 | 0 | 191563.2711 | 498408.3364 | 340173.9308 | 1521333.413 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6670135.6612 | 14892862.0375 | 13335.2143 | 0.026842 | 248495.488 | 554832.6463 | 5065.9166 | 11311.014
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2159 | 0.50152 | 0.0093777 | 4 | 186966.5445 | 406175.9256 | 3811.5659 | 8280.4456 | 68.995 | 0 | 117.4673 | 161042.7526 | 4571.6213 | 204076.6181 | 174189.9761 | 0 | 58093.7889 | 0 | 234770.1553 | 610823.786 | 416899.7851 | 1864468.4835 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7013270.7317 | 15235997.108 | 17782.7941 | 0.037511 | 186966.5445 | 406175.9256 | 3811.5659 | 8280.4456
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8897 | 0.641 | 0.012771 | 4 | 144732.227 | 305697.3249 | 2950.5622 | 6232.0535 | 69.2364 | 0 | 95.0032 | 191507.3785 | 5455.8788 | 248288.4137 | 215391.9697 | 0 | 64090.5669 | 0 | 282646.3409 | 735387.8004 | 501917.2844 | 2244685.6332 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7393487.8814 | 15616214.2577 | 23713.7371 | 0.051084 | 144732.227 | 305697.3249 | 2950.5622 | 6232.0535
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4159 | 0.85358 | 0.017554 | 4 | 113271.122 | 230376.7785 | 2309.185 | 4696.5422 | 69.5382 | 0 | 111.5779 | 234557.4209 | 6709.1083 | 312137.805 | 277933.6781 | 0 | 74198.842 | 0 | 353159.3732 | 918848.2461 | 627132.8084 | 2804677.2821 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7953479.5303 | 16176205.9066 | 31622.7766 | 0.070216 | 113271.122 | 230376.7785 | 2309.185 | 4696.5422
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3271 | 1.0976 | 0.023544 | 4 | 90935.1686 | 178247.6562 | 1853.8364 | 3633.8196 | 69.7129 | 0 | 79.8 | 279988.4701 | 8029.2912 | 381625.9564 | 349837.2164 | 0 | 83138.8597 | 0 | 430021.7196 | 1118828.3048 | 763623.3077 | 3415093.126 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8563895.3742 | 16786621.7505 | 42169.6503 | 0.094176 | 90935.1686 | 178247.6562 | 1853.8364 | 3633.8196
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9151 | 1.3984 | 0.031214 | 4 | 74372.4835 | 140230.672 | 1516.1837 | 2858.7919 | 69.8461 | 0 | 94.5758 | 331967.0986 | 9538.923 | 463158.0896 | 438457.8881 | 0 | 92569.9551 | 0 | 520919.8622 | 1355326.6262 | 925038.2715 | 4136976.7144 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9285778.9626 | 17508505.3389 | 56234.1325 | 0.12486 | 74372.4835 | 140230.672 | 1516.1837 | 2858.7919
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.382 | 1.689 | 0.040163 | 4 | 61923.67 | 113107.5357 | 1262.3978 | 2305.8501 | 69.9308 | 0 | 140.4925 | 379067.9493 | 10906.0591 | 538650.8087 | 524093.0271 | 0 | 96810.3307 | 0 | 604315.9882 | 1572306.2391 | 1073131.3159 | 4799281.7182 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9948083.9664 | 18170810.3427 | 74989.4209 | 0.16065 | 61923.67 | 113107.5357 | 1262.3978 | 2305.8501
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.3887 | 2.1927 | 0.052788 | 4 | 52492.6855 | 91435.0219 | 1070.1344 | 1864.0266 | 70.0256 | 0 | 96.2221 | 455315.7194 | 13117.4767 | 663647.4032 | 672469.1209 | 0 | 111695.8423 | 0 | 747335.7694 | 1944414.3723 | 1327102.7628 | 5935098.467 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 11083900.7152 | 19306627.0915 | 100000 | 0.21115 | 52492.6855 | 91435.0219 | 1070.1344 | 1864.0266
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2935 | 2.6878 | 0.067072 | 4 | 45286.6184 | 75935.5085 | 923.229 | 1548.0481 | 70.0851 | 0 | 110.8949 | 525303.2488 | 15145.4435 | 781006.6877 | 818337.0411 | 0 | 120613.2131 | 0 | 881558.1973 | 2293633.5969 | 1565452.0594 | 7001049.4877 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 12149851.7359 | 20372578.1122 | 133352.1432 | 0.26829 | 45286.6184 | 75935.5085 | 923.229 | 1548.0481
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.7936 | 3.2329 | 0.083532 | 4 | 39767.8374 | 64377.2213 | 810.7212 | 1312.4167 | 70.1303 | 0 | 100.0675 | 598046.7807 | 17251.3528 | 905302.4756 | 978917.0787 | 0 | 128234.1502 | 0 | 1024823.2168 | 2666379.79 | 1819858.9953 | 8138813.84 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 13287616.0882 | 21510342.4645 | 177827.941 | 0.33413 | 39767.8374 | 64377.2213 | 810.7212 | 1312.4167
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.5922 | 3.803 | 0.1016 | 4 | 35543.7225 | 55777.1984 | 724.6069 | 1137.0936 | 70.1634 | 0 | 121.7955 | 670321.0373 | 19341.6725 | 1030882.3583 | 1146868.5645 | 0 | 133919.1144 | 0 | 1170519.7714 | 3045452.3384 | 2078583.7988 | 9295888.6556 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 14444690.9038 | 22667417.2801 | 237137.3706 | 0.40639 | 35543.7225 | 55777.1984 | 724.6069 | 1137.0936
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.3083 | 4.366 | 0.12034 | 4 | 32322.4165 | 49404.3816 | 658.9362 | 1007.1751 | 70.1856 | 0 | 129.7772 | 738575.0669 | 21313.6747 | 1151227.6282 | 1312736.3542 | 0 | 137255.0381 | 0 | 1310832.0272 | 3410516.046 | 2327747.2805 | 10410203.1157 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 15559005.3639 | 23781731.7402 | 316227.766 | 0.48137 | 32322.4165 | 49404.3816 | 658.9362 | 1007.1751
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.5345 | 4.8873 | 0.13863 | 4 | 29878.5409 | 44707.0221 | 609.1145 | 911.4131 | 70.1981 | 0 | 130.4179 | 799463.2904 | 23070.8996 | 1259942.2418 | 1466419.1969 | 0 | 138087.1507 | 0 | 1437923.284 | 3741181.4262 | 2553433.197 | 11419520.6866 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 16568322.9348 | 24791049.3111 | 421696.5034 | 0.55452 | 29878.5409 | 44707.0221 | 609.1145 | 911.4131
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.025 | 5.3465 | 0.15553 | 4 | 28033.526 | 41250.7077 | 571.5013 | 840.9515 | 70.2028 | 0 | 140.0552 | 851464.5421 | 24569.9262 | 1353771.1227 | 1601833.4876 | 0 | 136885.8346 | 0 | 1547724.7161 | 4026862.2293 | 2748416.2153 | 12291528.0738 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 17440330.322 | 25663056.6983 | 562341.3252 | 0.62212 | 28033.526 | 41250.7077 | 571.5013 | 840.9515
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.6855 | 5.7356 | 0.17046 | 4 | 26645.6708 | 38705.5922 | 543.208 | 789.0659 | 70.2024 | 0 | 140.9158 | 894465.2706 | 25808.1239 | 1432033.1146 | 1716667.225 | 0 | 134368.5642 | 0 | 1639303.4963 | 4265131.4301 | 2911039.8407 | 13018817.0653 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 18167619.3135 | 26390345.6898 | 749894.2093 | 0.68182 | 26645.6708 | 38705.5922 | 543.208 | 789.0659
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.4929 | 6.0529 | 0.1831 | 4 | 25604.0452 | 36830.9674 | 521.9731 | 750.8491 | 70.199 | 0 | 133.9367 | 928868.9357 | 26797.7756 | 1495084.8916 | 1810392.6651 | 0 | 131099.7722 | 0 | 1712975.1757 | 4456810.0277 | 3041864.4222 | 13603893.6659 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 18752695.9141 | 26975422.2904 | 1000000 | 0.73241 | 25604.0452 | 36830.9674 | 521.9731 | 750.8491
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.5527 | 6.3076 | 0.19354 | 4 | 24823.1999 | 35444.6808 | 506.0545 | 722.5878 | 70.1943 | 0 | 150.6201 | 956066.4276 | 27579.4571 | 1545204.3729 | 1885647.2764 | 0 | 127696.8298 | 0 | 1771455.8019 | 4608964.621 | 3145713.0586 | 14068327.8454 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 19217130.0936 | 27439856.4699 | 1333521.4322 | 0.77416 | 24823.1999 | 35444.6808 | 506.0545 | 722.5878
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.9427 | 6.5063 | 0.20191 | 4 | 24238.1395 | 34419.1954 | 494.1273 | 701.6819 | 70.1895 | 0 | 142.7016 | 977041.5628 | 28181.8681 | 1584023.1046 | 1944384.4699 | 0 | 124406.369 | 0 | 1816634.576 | 4726510.5238 | 3225940.5526 | 14427123.0268 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 19575925.275 | 27798651.6513 | 1778279.41 | 0.80765 | 24238.1395 | 34419.1954 | 494.1273 | 701.6819
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.8038 | 6.6608 | 0.20854 | 4 | 23799.8279 | 33657.2345 | 485.1917 | 686.1482 | 70.1851 | 0 | 161.3252 | 993215.2989 | 28646.112 | 1614054.6796 | 1990092.3522 | 0 | 121499.5575 | 0 | 1851528.1201 | 4817296.3678 | 3287903.7565 | 14704236.2445 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 19853038.4927 | 28075764.869 | 2371373.7057 | 0.83417 | 23799.8279 | 33657.2345 | 485.1917 | 686.1482
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.2406 | 6.78 | 0.21372 | 4 | 23471.4365 | 33089.8386 | 478.497 | 674.5811 | 70.1812 | 0 | 162.3137 | 1005608.8614 | 29001.6872 | 1637125.5397 | 2025362.6615 | 0 | 119044.6952 | 0 | 1878295.9436 | 4886940.7537 | 3335437.481 | 14916817.6232 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20065619.8714 | 28288346.2477 | 3162277.6602 | 0.8549 | 23471.4365 | 33089.8386 | 478.497 | 674.5811
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.342 | 6.8713 | 0.21773 | 4 | 23225.3674 | 32666.6488 | 473.4805 | 665.9538 | 70.178 | 0 | 151.1425 | 1015054.1627 | 29272.5778 | 1654742.2214 | 2052385.7367 | 0 | 117033.8329 | 0 | 1898710.5273 | 4940055.313 | 3371689.2591 | 15078943.631 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20227745.8792 | 28450472.2555 | 4216965.0343 | 0.87093 | 23225.3674 | 32666.6488 | 473.4805 | 665.9538
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.1749 | 6.9403 | 0.2208 | 4 | 23040.9572 | 32351.105 | 469.7211 | 659.521 | 70.1755 | 0 | 168.6071 | 1022166.7196 | 29476.5085 | 1668027.5255 | 2072816.5788 | 0 | 115402.9308 | 0 | 1914077.2027 | 4980036.2501 | 3398977.0702 | 15200980.7863 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20349783.0345 | 28572509.4108 | 5623413.2519 | 0.8832 | 23040.9572 | 32351.105 | 469.7211 | 659.521
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.8009 | 6.9921 | 0.22313 | 4 | 22902.7375 | 32115.6767 | 466.9033 | 654.7215 | 70.1735 | 0 | 148.3438 | 1027495.3779 | 29629.2588 | 1677991.7311 | 2088169.227 | 0 | 114099.564 | 0 | 1925580.2119 | 5009964.7206 | 3419403.8663 | 15292333.9577 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20441136.2059 | 28663862.5822 | 7498942.0933 | 0.89252 | 22902.7375 | 32115.6767 | 466.9033 | 654.7215
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.2808 | 7.0319 | 0.22491 | 4 | 22799.127 | 31939.105 | 464.791 | 651.1219 | 70.1719 | 0 | 155.7992 | 1031570.0502 | 29746.0437 | 1685617.4278 | 2099935.588 | 0 | 113104.3708 | 0 | 1934389.6574 | 5032885.0906 | 3435047.4897 | 15362295.718 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20511097.9662 | 28733824.3425 | 10000000 | 0.89964 | 22799.127 | 31939.105 | 464.791 | 651.1219
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1647 | [19 empty] | 100 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.8524 | [19 empty] | 133.3521 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6867 | [19 empty] | 177.8279 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.56 | [19 empty] | 237.1374 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4247 | [19 empty] | 316.2278 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0415 | [19 empty] | 421.6965 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4959 | [19 empty] | 562.3413 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5042 | [19 empty] | 749.8942 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6555 | [19 empty] | 1000 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.9199 | [19 empty] | 1333.5214 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.76734 | 0.051805 | 0.00023192 | 4 | 6294043.5634 | 15592797.4554 | 128312.5914 | 317880.2669 | 63.2431 | 0 | 72.548 | 31095.6058 | 822.0331 | 33368.8403 | 40749.4823 | 0 | 23697.0893 | 0 | 50595.8898 | 131640.1267 | 89847.0914 | 401816.1587 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5838784.1893 | 14464942.6609 | 1778.2794 | 0.00092767 | 6294043.5634 | 15592797.4554 | 128312.5914 | 317880.2669
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0874 | 0.080695 | 0.00071868 | 4 | 2074380.3761 | 5075089.1854 | 42289.0498 | 103462.5576 | 66.173 | 0 | 166.4667 | 43997.016 | 1197.4024 | 47441.7433 | 49077.408 | 0 | 28200.7232 | 0 | 66266.5742 | 172412.033 | 117674.7552 | 526267.6553 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5963235.6858 | 14589394.1575 | 2371.3737 | 0.0028747 | 2074380.3761 | 5075089.1854 | 42289.0498 | 103462.5576
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5153 | 0.11979 | 0.0014405 | 4 | 1061665.8588 | 2558746.7917 | 21643.4945 | 52163.5143 | 68.2966 | 0 | 245.0054 | 59456.1139 | 1653.4511 | 64951.1454 | 60234.9071 | 0 | 33361.9345 | 0 | 85666.4452 | 222886.5179 | 152124.6283 | 680335.1433 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6117303.1739 | 14743461.6456 | 3162.2777 | 0.005762 | 1061665.8588 | 2558746.7917 | 21643.4945 | 52163.5143
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.16822 | 0.0024532 | 4 | 641281.9651 | 1520357.6423 | 13073.4003 | 30994.547 | 69.7511 | 0 | 345.7609 | 76573.0412 | 2161.8825 | 85109.6365 | 73982.5178 | 0 | 38475.0821 | 0 | 107757.8424 | 280363.8019 | 191354.0557 | 855777.8601 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6292745.8907 | 14918904.3623 | 4216.965 | 0.0098128 | 641281.9651 | 1520357.6423 | 13073.4003 | 30994.547
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7157 | 0.23077 | 0.0038395 | 4 | 423513.4873 | 985187.5706 | 8633.8953 | 20084.3812 | 70.8282 | 0 | 96.6928 | 96553.1119 | 2757.6435 | 109494.4264 | 91688.5379 | 0 | 44110.9013 | 0 | 134395.8022 | 349670.309 | 238657.1709 | 1067327.9032 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6504295.9338 | 15130454.4054 | 5623.4133 | 0.015358 | 423513.4873 | 985187.5706 | 8633.8953 | 20084.3812
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5829 | 0.3113 | 0.0057088 | 4 | 296041.856 | 673799.5912 | 6035.2137 | 13736.316 | 71.6339 | 0 | 102.1171 | 119933.5907 | 3456.1471 | 139020.2274 | 114446.8802 | 0 | 50358.8128 | 0 | 166614.1067 | 433495.7285 | 295869.7421 | 1323195.2356 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6760163.2662 | 15386321.7378 | 7498.9421 | 0.022835 | 296041.856 | 673799.5912 | 6035.2137 | 13736.316
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7085 | 0.41595 | 0.0082094 | 4 | 215433.4927 | 478124.1572 | 4391.9031 | 9747.2077 | 72.2468 | 0 | 116.2423 | 147669.8769 | 4285.6015 | 175198.2165 | 143996.9949 | 0 | 57502.6261 | 0 | 206174.7932 | 536424.5196 | 366120.7571 | 1637373.3858 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7074341.4164 | 15700499.888 | 10000 | 0.032838 | 215433.4927 | 478124.1572 | 4391.9031 | 9747.2077
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1038 | 0.54566 | 0.0115 | 4 | 161799.4309 | 349328.7889 | 3298.5002 | 7121.5399 | 72.6916 | 0 | 145.3487 | 179192.1102 | 5228.4121 | 217600.2915 | 180617.7328 | 0 | 64915.8332 | 0 | 252546.2082 | 657073.4293 | 448466.117 | 2005640.1344 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7442608.165 | 16068766.6366 | 13335.2143 | 0.045999 | 161799.4309 | 349328.7889 | 3298.5002 | 7121.5399
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7776 | 0.70069 | 0.015712 | 4 | 125069.3623 | 262325.4424 | 2549.7081 | 5347.859 | 72.9832 | 0 | 116.8254 | 213889.479 | 6264.6376 | 265723.4272 | 224448.4687 | 0 | 72073.4372 | 0 | 305135.7854 | 793900.7217 | 541853.5556 | 2423289.5125 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7860257.5431 | 16486416.0147 | 17782.7941 | 0.062847 | 125069.3623 | 262325.4424 | 2549.7081 | 5347.859
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2527 | 0.93212 | 0.021611 | 4 | 97884.0358 | 197675.0085 | 1995.4985 | 4029.8724 | 73.3249 | 0 | 119.7324 | 261861.3804 | 7701.0605 | 333773.4939 | 289620.7409 | 0 | 83505.3335 | 0 | 380820.1836 | 990816.0007 | 676252.2797 | 3024350.4731 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8461318.5037 | 17087476.9753 | 23713.7371 | 0.086442 | 97884.0358 | 197675.0085 | 1995.4985 | 4029.8724
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1297 | 1.2001 | 0.029032 | 4 | 78549.6297 | 152831.4995 | 1601.3404 | 3115.6768 | 73.5287 | 0 | 97.7201 | 312953.3947 | 9227.8516 | 408491.0292 | 365209.1478 | 0 | 93815.863 | 0 | 463981.9416 | 1207185.8364 | 823929.1385 | 3684794.2028 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9121762.2334 | 17747920.705 | 31622.7766 | 0.11613 | 78549.6297 | 152831.4995 | 1601.3404 | 3115.6768
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6593 | 1.529 | 0.038535 | 4 | 64214.0581 | 120176.5911 | 1309.0904 | 2449.9624 | 73.6833 | 0 | 100.782 | 371140.4618 | 10965.3917 | 495751.8069 | 457948.6538 | 0 | 104532.4161 | 0 | 561732.1048 | 1461511.7096 | 997511.7728 | 4461094.3174 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9898062.348 | 18524220.8196 | 42169.6503 | 0.15414 | 64214.0581 | 120176.5911 | 1309.0904 | 2449.9624
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9908 | 1.9326 | 0.050593 | 4 | 53436.2777 | 96061.3405 | 1089.3708 | 1958.3404 | 73.8028 | 0 | 97.1103 | 437632.5276 | 12949.2201 | 597874.6379 | 571763.8346 | 0 | 115862.2211 | 0 | 677072.1521 | 1761602.8532 | 1202330.1446 | 5377087.5912 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10814055.6218 | 19440214.0934 | 56234.1325 | 0.20237 | 53436.2777 | 96061.3405 | 1089.3708 | 1958.3404
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1575 | 2.4141 | 0.065567 | 4 | 45245.7065 | 78136.4701 | 922.3949 | 1592.9176 | 73.8943 | 0 | 139.3794 | 511731.4751 | 15157.8744 | 714274.5366 | 707532.5958 | 0 | 127169.3594 | 0 | 809587.6781 | 2106381.0691 | 1437648.3615 | 6429482.95 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 11866450.9806 | 20492609.4522 | 74989.4209 | 0.26227 | 45245.7065 | 78136.4701 | 922.3949 | 1592.9176
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.1498 | 2.9726 | 0.083679 | 4 | 38973.5442 | 64745.0164 | 794.5284 | 1319.9147 | 73.9644 | 0 | 117.5689 | 592358.5825 | 17558.6351 | 843612.6165 | 865004.9574 | 0 | 137884.26 | 0 | 958003.4301 | 2492528.4116 | 1701201.8573 | 7608152.7506 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 13045120.7811 | 21671279.2528 | 100000 | 0.33472 | 38973.5442 | 64745.0164 | 794.5284 | 1319.9147
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.8714 | 3.5992 | 0.10487 | 4 | 34150.1497 | 54713.7338 | 696.197 | 1115.4135 | 74.0179 | 0 | 106.5718 | 677619.6568 | 20094.643 | 983040.8897 | 1041651.836 | 0 | 147419.1768 | 0 | 1119232.2189 | 2912012.6475 | 1987508.4678 | 8888579.5366 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 14325547.5672 | 22951706.0388 | 133352.1432 | 0.41949 | 34150.1497 | 54713.7338 | 696.197 | 1115.4135
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4 | 4.3941 | 0.13084 | 4 | 30408.0843 | 46890.3962 | 619.9099 | 955.9242 | 74.0631 | 0 | 120.3795 | 779700.3109 | 23127.1449 | 1153149.3603 | 1265775.2556 | 0 | 161039.0976 | 0 | 1319288.5561 | 3432518.1996 | 2342764.2024 | 10477362.1274 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 15914330.1579 | 24540488.6296 | 177827.941 | 0.52336 | 30408.0843 | 46890.3962 | 619.9099 | 955.9242
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.283 | 4.9421 | 0.15361 | 4 | 27594.0045 | 41632.9807 | 562.5411 | 848.7446 | 74.0834 | 0 | 147.0655 | 846868.5575 | 25119.998 | 1266807.2936 | 1420319.6878 | 0 | 159659.7992 | 0 | 1450322.3811 | 3773441.3336 | 2575451.2466 | 11517990.2975 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 16954958.3281 | 25581116.7997 | 237137.3706 | 0.61444 | 27594.0045 | 41632.9807 | 562.5411 | 848.7446
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1204 | 5.5783 | 0.17852 | 4 | 25423.9115 | 37503.8405 | 518.3008 | 764.5665 | 74.0971 | 0 | 155.161 | 922102.1216 | 27349.3587 | 1395652.4367 | 1599821.218 | 0 | 161292.3786 | 0 | 1601424.8303 | 4166578.911 | 2843775.7214 | 12717996.9762 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 18154965.0068 | 26781123.4784 | 316227.766 | 0.71409 | 25423.9115 | 37503.8405 | 518.3008 | 764.5665
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.2714 | 6.1496 | 0.20198 | 4 | 23778.1585 | 34455.2479 | 484.7499 | 702.4168 | 74.1008 | 0 | 145.8932 | 987462.2251 | 29283.3371 | 1508874.2561 | 1761136.2856 | 0 | 160317.0858 | 0 | 1734358.544 | 4512445.1656 | 3079836.547 | 13773713.4462 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 19210681.4768 | 27836839.9484 | 421696.5034 | 0.80791 | 23778.1585 | 34455.2479 | 484.7499 | 702.4168
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.5501 | 6.6389 | 0.22297 | 4 | 22535.6705 | 32207.6492 | 459.4201 | 656.5965 | 74.0976 | 0 | 187.654 | 1041957.7257 | 30893.5302 | 1604178.7301 | 1899407.97 | 0 | 157415.8087 | 0 | 1846202.9682 | 4803441.4149 | 3278447.4665 | 14661945.6141 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 20098913.6447 | 28725072.1163 | 562341.3252 | 0.89187 | 22535.6705 | 32207.6492 | 459.4201 | 656.5965
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.9204 | 7.0431 | 0.24099 | 4 | 21600.5066 | 30549.2905 | 440.3555 | 622.7886 | 74.0906 | 0 | 170.2401 | 1086033.3028 | 32194.1257 | 1681859.6917 | 2013737.9343 | 0 | 153410.3233 | 0 | 1937221.7974 | 5040253.7379 | 3440076.743 | 15384787.6561 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 20821755.6866 | 29447914.1583 | 749894.2093 | 0.96395 | 21600.5066 | 30549.2905 | 440.3555 | 622.7886
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.4501 | 7.3689 | 0.25597 | 4 | 20897.9567 | 29322.824 | 426.0331 | 597.7854 | 74.0821 | 0 | 195.3923 | 1120979.5944 | 33224.1432 | 1743832.6078 | 2105972.8585 | 0 | 149037.7884 | 0 | 2009688.327 | 5228796.7831 | 3568761.2455 | 15960293.3479 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 21397261.3785 | 30023419.8501 | 1000000 | 1.0239 | 20897.9567 | 29322.824 | 426.0331 | 597.7854
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.2493 | 7.6268 | 0.26813 | 4 | 20370.6996 | 28413.4682 | 415.2843 | 579.247 | 74.0736 | 0 | 182.1769 | 1148294.1412 | 34028.441 | 1792507.6891 | 2179042.9088 | 0 | 144801.605 | 0 | 2066483.1662 | 5376565.3044 | 3669616.2976 | 16411339.5533 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 21848307.5839 | 30474466.0555 | 1333521.4322 | 1.0725 | 20370.6996 | 28413.4682 | 415.2843 | 579.247
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.4271 | 7.8272 | 0.27779 | 4 | 19975.2019 | 27738.3784 | 407.2215 | 565.4844 | 74.066 | 0 | 168.7903 | 1169308.0137 | 34646.7227 | 1830096.4718 | 2235842.9357 | 0 | 140947.0687 | 0 | 2110228.0729 | 5490380.5783 | 3747297.5607 | 16758747.4245 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22195715.455 | 30821873.9267 | 1778279.41 | 1.1112 | 19975.2019 | 27738.3784 | 407.2215 | 565.4844
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.1056 | 7.9814 | 0.28535 | 4 | 19678.6074 | 27236.078 | 401.175 | 555.2443 | 74.0595 | 0 | 164.9102 | 1185365.2335 | 35118.8709 | 1858902.3477 | 2279588.9351 | 0 | 137621.5651 | 0 | 2143672.8114 | 5577396.9276 | 3806688.0071 | 17024354.6985 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22461322.7291 | 31087481.2007 | 2371373.7057 | 1.1414 | 19678.6074 | 27236.078 | 401.175 | 555.2443
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.4085 | 8.101 | 0.29125 | 4 | 19456.2036 | 26860.6235 | 396.641 | 547.5901 | 74.0541 | 0 | 218.6857 | 1197747.9713 | 35482.7946 | 1881165.8651 | 2313527.9671 | 0 | 134917.8115 | 0 | 2169508.5398 | 5644616.1931 | 3852566.537 | 17229533.6795 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22666501.7101 | 31292660.1817 | 3162277.6602 | 1.165 | 19456.2036 | 26860.6235 | 396.641 | 547.5901
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.3855 | 8.1907 | 0.29575 | 4 | 19289.4366 | 26581.2205 | 393.2413 | 541.8941 | 74.0498 | 0 | 171.3107 | 1206987.4666 | 35754.2356 | 1897806.1583 | 2338967.679 | 0 | 132675.0414 | 0 | 2188754.3266 | 5694689.7825 | 3886742.7907 | 17382377.4807 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22819345.5113 | 31445503.9829 | 4216965.0343 | 1.183 | 19289.4366 | 26581.2205 | 393.2413 | 541.8941
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.1212 | 8.2581 | 0.29917 | 4 | 19164.388 | 26372.7172 | 390.692 | 537.6435 | 74.0465 | 0 | 196.8858 | 1213918.5583 | 35957.8004 | 1910304.862 | 2358116.5596 | 0 | 130876.2705 | 0 | 2203177.8798 | 5732216.9094 | 3912355.8259 | 17496924.6659 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22933892.6965 | 31560051.1681 | 5623413.2519 | 1.1967 | 19164.388 | 26372.7172 | 390.692 | 537.6435
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.6935 | 8.3106 | 0.30181 | 4 | 19070.6205 | 26215.9095 | 388.7804 | 534.4468 | 74.0438 | 0 | 184.1263 | 1219295.4258 | 36115.6826 | 1920010.2238 | 2373009.9414 | 0 | 129521.7607 | 0 | 2214401.6834 | 5761418.944 | 3932286.8146 | 17586060.4763 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23023028.5069 | 31649186.9785 | 7498942.0933 | 1.2073 | 19070.6205 | 26215.9095 | 388.7804 | 534.4468
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.1151 | 8.3492 | 0.30379 | 4 | 19000.3081 | 26099.1125 | 387.347 | 532.0657 | 74.0418 | 0 | 183.0975 | 1223247.2415 | 36231.7009 | 1927148.5651 | 2383977.5187 | 0 | 128437.6042 | 0 | 2222626.6259 | 5782818.5571 | 3946892.4902 | 17651380.3036 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23088348.3342 | 31714506.8058 | 10000000 | 1.2152 | 19000.3081 | 26099.1125 | 387.347 | 532.0657
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7443 | [19 empty] | 100 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9637 | [19 empty] | 133.3521 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7983 | [19 empty] | 177.8279 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2625 | [19 empty] | 237.1374 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0211 | [19 empty] | 316.2278 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.95 | [19 empty] | 421.6965 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.4348 | [19 empty] | 562.3413 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6983 | [19 empty] | 749.8942 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.2914 | [19 empty] | 1000 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.71826 | 0.051408 | 0.00019185 | 4 | 7996436.3915 | 19773880.1019 | 163018.1718 | 403117.292 | 65.0386 | 0 | 84.0211 | 31797.5634 | 851.8437 | 33109.3795 | 40236.5892 | 0 | 24870.5606 | 0 | 51037.7152 | 132789.6656 | 90631.6754 | 405324.9926 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6136318.8964 | 15174113.5906 | 1333.5214 | 0.00076738 | 7996436.3915 | 19773880.1019 | 163018.1718 | 403117.292
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.082154 | 0.00074035 | 4 | 2117433.6944 | 5169318.9518 | 43166.7499 | 105383.5589 | 68.5876 | 0 | 60.777 | 46093.4267 | 1277.6008 | 48020.4626 | 48787.1894 | 0 | 30018.8046 | 0 | 67937.0188 | 176758.187 | 120641.0947 | 539533.7845 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6270527.6883 | 15308322.3825 | 1778.2794 | 0.0029614 | 2117433.6944 | 5169318.9518 | 43166.7499 | 105383.5589
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.12304 | 0.0015711 | 4 | 1023557.4196 | 2461669.409 | 20866.6025 | 50184.4606 | 71.09 | 0 | 233.9162 | 62857.3238 | 1785.0413 | 66188.3095 | 60017.3441 | 0 | 35655.3555 | 0 | 88336.3159 | 229832.9738 | 156865.7272 | 701538.3911 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6432532.295 | 15470326.9891 | 2371.3737 | 0.0062845 | 1023557.4196 | 2461669.409 | 20866.6025 | 50184.4606
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.17433 | 0.002749 | 4 | 601949.6189 | 1423866.845 | 12271.5572 | 29027.4516 | 72.8259 | 0 | 337.6835 | 81639.6738 | 2358.5164 | 87330.8163 | 74015.3697 | 0 | 41373.7951 | 0 | 111820.0868 | 290932.9283 | 198567.7017 | 888038.888 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6619032.7918 | 15656827.486 | 3162.2777 | 0.010996 | 601949.6189 | 1423866.845 | 12271.5572 | 29027.4516
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.24182 | 0.0043727 | 4 | 391504.9199 | 908227.2714 | 7981.3573 | 18515.4414 | 74.1244 | 0 | 467.3222 | 103907.6778 | 3041.3614 | 113333.9286 | 92365.611 | 0 | 47887.0193 | 0 | 140608.8833 | 365835.4714 | 249690.2264 | 1116670.1792 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6847664.083 | 15885458.7772 | 4216.965 | 0.017491 | 391504.9199 | 908227.2714 | 7981.3573 | 18515.4414
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4197 | 0.3253 | 0.0065574 | 4 | 271131.1009 | 615694.454 | 5527.3742 | 12551.7642 | 75.0578 | 0 | 80.0119 | 128916.9565 | 3809.8589 | 143560.8269 | 114990.8022 | 0 | 54501.8315 | 0 | 173854.3076 | 452333.2459 | 308726.7349 | 1380694.5643 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7111688.4681 | 16149483.1623 | 5623.4133 | 0.02623 | 271131.1009 | 615694.454 | 5527.3742 | 12551.7642
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4844 | 0.43402 | 0.0094499 | 4 | 196702.9865 | 435800.2012 | 4010.0564 | 8884.3766 | 75.7784 | 0 | 105.2845 | 158618.8388 | 4722.4647 | 180701.0632 | 144031.8562 | 0 | 62191.7131 | 0 | 214603.715 | 558354.8452 | 381088.6549 | 1704313.1511 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7435307.0549 | 16473101.7491 | 7498.9421 | 0.0378 | 196702.9865 | 435800.2012 | 4010.0564 | 8884.3766
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.846 | 0.57314 | 0.01328 | 4 | 147351.7213 | 317496.6368 | 3003.9641 | 6472.5984 | 76.32 | 0 | 118.9675 | 193433.3792 | 5792.0371 | 225615.219 | 181140.6297 | 0 | 70768.9175 | 0 | 263932.5712 | 686698.4103 | 468685.7752 | 2096066.9393 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7827060.8431 | 16864855.5373 | 10000 | 0.053118 | 147351.7213 | 317496.6368 | 3003.9641 | 6472.5984
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.483 | 0.73996 | 0.018212 | 4 | 113543.4831 | 237604.608 | 2314.7375 | 4843.8913 | 76.6839 | 0 | 106.9552 | 231833.7876 | 6970.1062 | 276690.6595 | 225687.7029 | 0 | 79091.3971 | 0 | 319906.7247 | 832331.6759 | 568083.4715 | 2540595.5253 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8271589.4291 | 17309384.1232 | 13335.2143 | 0.07285 | 113543.4831 | 237604.608 | 2314.7375 | 4843.8913
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8434 | 0.98231 | 0.025039 | 4 | 88787.8188 | 179026.3705 | 1810.0598 | 3649.6947 | 77.0683 | 0 | 114.4777 | 283435.6036 | 8556.5014 | 346967.4367 | 290220.9374 | 0 | 91563.6378 | 0 | 398090.2056 | 1035749.0554 | 706920.0128 | 3161503.3907 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8892497.2945 | 17930291.9887 | 17782.7941 | 0.10015 | 88787.8188 | 179026.3705 | 1810.0598 | 3649.6947
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6233 | 1.2674 | 0.033743 | 4 | 71025.071 | 137984.6846 | 1447.9421 | 2813.0044 | 77.3101 | 0 | 92.8074 | 339356.0807 | 10273.512 | 425333.3233 | 366701.8472 | 0 | 103157.781 | 0 | 485480.7922 | 1263121.4356 | 862106.3344 | 3855531.1065 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9586525.0103 | 18624319.7044 | 23713.7371 | 0.13497 | 71025.071 | 137984.6846 | 1447.9421 | 2813.0044
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0527 | 1.6192 | 0.044934 | 4 | 57894.7536 | 108178.8083 | 1180.2629 | 2205.3713 | 77.4941 | 0 | 116.9222 | 403352.3586 | 12236.7098 | 517319.5678 | 461058.0734 | 0 | 115340.8488 | 0 | 588629.9478 | 1531494.3796 | 1045276.3831 | 4674708.269 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10405702.1728 | 19443496.867 | 31622.7766 | 0.17973 | 57894.7536 | 108178.8083 | 1180.2629 | 2205.3713
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2675 | 2.0515 | 0.059181 | 4 | 48039.7708 | 86218.6516 | 979.3557 | 1757.6838 | 77.6358 | 0 | 88.6152 | 476540.2892 | 14479.5756 | 625079.6052 | 577031.5099 | 0 | 128190.3108 | 0 | 710315.3033 | 1848094.7136 | 1261362.6166 | 5641093.9242 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11372087.828 | 20409882.5221 | 42169.6503 | 0.23672 | 48039.7708 | 86218.6516 | 979.3557 | 1757.6838
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.3487 | 2.5728 | 0.077015 | 4 | 40553.394 | 69891.3314 | 826.7358 | 1424.8293 | 77.7448 | 0 | 107.3111 | 558897.2326 | 17000.597 | 749136.072 | 716852.0401 | 0 | 141278.8844 | 0 | 851434.2821 | 2215257.3489 | 1511958.6596 | 6761815.1167 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12492809.0205 | 21530603.7147 | 56234.1325 | 0.30806 | 40553.394 | 69891.3314 | 826.7358 | 1424.8293
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.3197 | 3.1855 | 0.098828 | 4 | 34814.8948 | 57677.3549 | 709.7487 | 1175.8309 | 77.8285 | 0 | 91.9676 | 649573.7095 | 19772.9921 | 888674.064 | 881171.7422 | 0 | 153987.5915 | 0 | 1011340.2387 | 2631299.8467 | 1795916.2132 | 8031736.3978 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 13762730.3016 | 22800524.9958 | 74989.4209 | 0.39531 | 34814.8948 | 57677.3549 | 709.7487 | 1175.8309
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.1332 | 3.8847 | 0.12474 | 4 | 30391.0984 | 48504.4415 | 619.5636 | 988.8286 | 77.8928 | 0 | 113.5329 | 746943.161 | 22746.3601 | 1041504.1071 | 1068687.1272 | 0 | 165682.957 | 0 | 1187769.8478 | 3090333.4988 | 2109216.1129 | 9432883.1717 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 15163877.0755 | 24201671.7697 | 100000 | 0.49896 | 30391.0984 | 48504.4415 | 619.5636 | 988.8286
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.5682 | 4.6476 | 0.15427 | 4 | 26974.6389 | 41620.5147 | 549.9145 | 848.4905 | 77.9405 | 0 | 114.3074 | 847430.1508 | 25810.9598 | 1202099.721 | 1273295.4105 | 0 | 175367.3813 | 0 | 1374361.4131 | 3575806.4766 | 2440561.3957 | 10914732.9087 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 16645726.8125 | 25683521.5066 | 133352.1432 | 0.61709 | 26974.6389 | 41620.5147 | 549.9145 | 848.4905
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.2339 | 5.4338 | 0.1862 | 4 | 24342.1784 | 36476.9698 | 496.2482 | 743.6324 | 77.9725 | 0 | 139.0028 | 945963.8341 | 28811.6927 | 1362149.1372 | 1484178.5951 | 0 | 182012.127 | 0 | 1561215.0006 | 4061961.1823 | 2772371.9719 | 12398663.5409 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 18129657.4447 | 27167452.1389 | 177827.941 | 0.74478 | 24342.1784 | 36476.9698 | 496.2482 | 743.6324
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.654 | 6.1937 | 0.21868 | 4 | 22324.4424 | 32656.7378 | 455.114 | 665.7518 | 77.9891 | 0 | 134.6356 | 1037215.0225 | 31586.1495 | 1512510.6638 | 1688132.5971 | 0 | 184982.4359 | 0 | 1737226.4789 | 4519906.9438 | 3084929.364 | 13796489.6555 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 19527483.5593 | 28565278.2535 | 237137.3706 | 0.87471 | 22324.4424 | 32656.7378 | 455.114 | 665.7518
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.4823 | 6.8916 | 0.24995 | 4 | 20787.3053 | 29827.0803 | 423.7773 | 608.0654 | 77.9926 | 0 | 137.8975 | 1118047.3672 | 34039.4839 | 1647373.2514 | 1875572.1117 | 0 | 184678.8725 | 0 | 1895287.3238 | 4931148.8397 | 3365610.4081 | 15051757.6583 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 20782751.5621 | 29820546.2562 | 316227.766 | 0.99978 | 20787.3053 | 29827.0803 | 423.7773 | 608.0654
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.4332 | 7.4983 | 0.27841 | 4 | 19622.4868 | 27737.9649 | 400.0309 | 565.4759 | 77.9868 | 0 | 160.3739 | 1186270.9413 | 36106.4108 | 1762407.2033 | 2038661.9046 | 0 | 181671.5176 | 0 | 2029996.0112 | 5281633.2118 | 3604823.1938 | 16121570.3944 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 21852564.2982 | 30890358.9924 | 421696.5034 | 1.1136 | 19622.4868 | 27737.9649 | 400.0309 | 565.4759
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.4297 | 8.0062 | 0.30322 | 4 | 18743.2177 | 26194.6602 | 382.1058 | 534.0136 | 77.9756 | 0 | 151.0367 | 1242068.441 | 37794.0072 | 1857312.0131 | 2175358.9257 | 0 | 177008.7884 | 0 | 2140921.4484 | 5570238.4454 | 3801802.1959 | 17002504.2652 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 22733498.169 | 31771292.8632 | 562341.3252 | 1.2129 | 18743.2177 | 26194.6602 | 382.1058 | 534.0136
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.5124 | 8.4203 | 0.32412 | 4 | 18081.1866 | 25052.2986 | 368.6094 | 510.725 | 77.9625 | 0 | 149.7674 | 1286711.085 | 39142.1866 | 1933779.9793 | 2286874.4115 | 0 | 171658.535 | 0 | 2230084.817 | 5802223.2405 | 3960136.5854 | 17710610.8403 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 23441604.7441 | 32479399.4383 | 749894.2093 | 1.2965 | 18081.1866 | 25052.2986 | 368.6094 | 510.725
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.7696 | 8.7498 | 0.34121 | 4 | 17583.4984 | 24205.345 | 358.4634 | 493.4587 | 77.9494 | 0 | 162.3256 | 1321740.5001 | 40198.6925 | 1994117.7412 | 2375715.7033 | 0 | 166277.6605 | 0 | 2300239.616 | 5984751.6369 | 4084715.9665 | 18267757.517 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 23998751.4209 | 33036546.115 | 1000000 | 1.3648 | 17583.4984 | 24205.345 | 358.4634 | 493.4587
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.3318 | 9.0085 | 0.35492 | 4 | 17209.7014 | 23575.8174 | 350.843 | 480.6249 | 77.9375 | 0 | 159.8238 | 1348940.6747 | 41018.1956 | 2041175.1237 | 2445515.4121 | 0 | 161323.1803 | 0 | 2354809.3087 | 6126730.7834 | 4181619.6514 | 18701132.3297 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 24432126.2336 | 33469920.9277 | 1333521.4322 | 1.4197 | 17209.7014 | 23575.8174 | 350.843 | 480.6249
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.3197 | 9.209 | 0.36572 | 4 | 16929.1062 | 23107.1839 | 345.1227 | 471.0712 | 77.9274 | 0 | 154.5999 | 1369834.1984 | 41647.152 | 2077444.4839 | 2499616.6463 | 0 | 156992.3959 | 0 | 2396758.6018 | 6235874.2392 | 4256112.3026 | 19034280.0201 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 24765273.924 | 33803068.6181 | 1778279.41 | 1.4629 | 16929.1062 | 23107.1839 | 345.1227 | 471.0712
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.8519 | 9.3633 | 0.37414 | 4 | 16718.5415 | 22757.6107 | 340.8301 | 463.9447 | 77.9191 | 0 | 164.966 | 1385813.9283 | 42127.8653 | 2105256.2883 | 2541279.6445 | 0 | 153365.7582 | 0 | 2428858.959 | 6319392.7838 | 4313115.4255 | 19289210.6529 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25020204.5567 | 34057999.2508 | 2371373.7057 | 1.4966 | 16718.5415 | 22757.6107 | 340.8301 | 463.9447
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.0117 | 9.4799 | 0.3806 | 4 | 16560.5606 | 22497.0896 | 337.6094 | 458.6336 | 77.9125 | 0 | 162.4782 | 1397840.3896 | 42489.4645 | 2126229.2156 | 2572799.1086 | 0 | 150364.8477 | 0 | 2452991.9801 | 6382181.9544 | 4355970.3246 | 19480867.2852 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25211861.189 | 34249655.8831 | 3162277.6602 | 1.5224 | 16560.5606 | 22497.0896 | 337.6094 | 458.6336
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8935 | 9.5686 | 0.38555 | 4 | 16442.0474 | 22302.3763 | 335.1934 | 454.6641 | 77.9073 | 0 | 150.525 | 1406944.0406 | 42763.074 | 2142128.8771 | 2596751.962 | 0 | 147967.397 | 0 | 2471256.5868 | 6429702.7143 | 4388404.2197 | 19625918.8714 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25356912.7752 | 34394707.4694 | 4216965.0343 | 1.5422 | 16442.0474 | 22302.3763 | 335.1934 | 454.6641
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.5586 | 9.6354 | 0.38931 | 4 | 16353.1501 | 22156.8556 | 333.3811 | 451.6975 | 77.9032 | 0 | 154.7594 | 1413787.6904 | 42968.6963 | 2154094.9661 | 2614811.6717 | 0 | 146071.1578 | 0 | 2484976.3311 | 6465398.6747 | 4412767.4461 | 19734876.6341 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25465870.5379 | 34503665.2321 | 5623413.2519 | 1.5572 | 16353.1501 | 22156.8556 | 333.3811 | 451.6975
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.0675 | 9.6865 | 0.39218 | 4 | 16286.4723 | 22047.6775 | 332.0218 | 449.4717 | 77.9001 | 0 | 168.8014 | 1419010.5767 | 43125.5849 | 2163234.997 | 2628625.1018 | 0 | 144620.3016 | 0 | 2495460.4592 | 6492676.2256 | 4431384.9351 | 19818138.1821 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25549132.0859 | 34586926.7801 | 7498942.0933 | 1.5687 | 16286.4723 | 22047.6775 | 332.0218 | 449.4717
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.4398 | 9.7239 | 0.39432 | 4 | 16236.4628 | 21966.3967 | 331.0023 | 447.8147 | 77.8978 | 0 | 183.4418 | 1422824.4521 | 43240.1285 | 2169913.5663 | 2638728.8485 | 0 | 143460.952 | 0 | 2503085.4995 | 6512515.0163 | 4444925.3174 | 19878693.7807 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25609687.6845 | 34647482.3787 | 10000000 | 1.5773 | 16236.4628 | 21966.3967 | 331.0023 | 447.8147
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7354 | [19 empty] | 100 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8557 | [19 empty] | 133.3521 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3633 | [19 empty] | 177.8279 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9293 | [19 empty] | 237.1374 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8976 | [19 empty] | 316.2278 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7 | [19 empty] | 421.6965 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5721 | [19 empty] | 562.3413 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5857 | [19 empty] | 749.8942 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.62825 | 0.0459 | 9.7089e-05 | 4 | 16515978.8191 | 40868894.1966 | 336700.5677 | 833167.6875 | 65.6764 | 0 | 58.0608 | 29706.7983 | 797.9762 | 30222.2327 | 38387.3812 | 0 | 24615.4939 | 0 | 48254.6541 | 125548.7116 | 85689.5754 | 383222.8234 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6414102.6913 | 15871737.7352 | 1000 | 0.00038836 | 16515978.8191 | 40868894.1966 | 336700.5677 | 833167.6875
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | 0.07877 | 0.00067426 | 4 | 2433203.297 | 5939852.3913 | 49604.1404 | 121091.9252 | 70.4133 | 0 | 66.9112 | 45892.0768 | 1288.5056 | 46355.1887 | 47265.7212 | 0 | 30837.6307 | 0 | 66939.258 | 174162.2181 | 118869.2925 | 531609.8916 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6562489.7595 | 16020124.8034 | 1333.5214 | 0.0026971 | 2433203.297 | 5939852.3913 | 49604.1404 | 121091.9252
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2625 | 0.11419 | 0.0015665 | 4 | 1069932.1846 | 2579320.0861 | 21812.0148 | 52582.9287 | 73.1332 | 0 | 205.1621 | 61271.5089 | 1764.5809 | 62237.8606 | 56677.0595 | 0 | 35396.6559 | 0 | 84765.5897 | 220542.6766 | 150524.9085 | 673180.8406 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6704060.7085 | 16161695.7524 | 1778.2794 | 0.0062659 | 1069932.1846 | 2579320.0861 | 21812.0148 | 52582.9287
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.16149 | 0.0028431 | 4 | 604869.4524 | 1436509.1271 | 12331.0819 | 29285.1816 | 75.2384 | 0 | 292.6616 | 79708.7175 | 2341.1218 | 81971.6692 | 69083.7022 | 0 | 40641.1356 | 0 | 106761.0751 | 277770.4177 | 189584.0177 | 847861.8568 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6878741.7247 | 16336376.7686 | 2371.3737 | 0.011372 | 604869.4524 | 1436509.1271 | 12331.0819 | 29285.1816
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.22384 | 0.0045758 | 4 | 387462.013 | 904187.0366 | 7898.9372 | 18433.0757 | 76.8595 | 0 | 405.3663 | 101566.2337 | 3027.418 | 106296.2454 | 84896.3973 | 0 | 46726.8459 | 0 | 133580.1247 | 347548.0834 | 237208.7083 | 1060850.0567 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7091729.9246 | 16549364.9685 | 3162.2777 | 0.018303 | 387462.013 | 904187.0366 | 7898.9372 | 18433.0757
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1788 | 0.32704 | 0.0070381 | 4 | 263834.1375 | 599777.7394 | 5378.6158 | 12227.2805 | 78.3209 | 0 | 73.9935 | 134068.9298 | 4052.8707 | 143780.8088 | 111453.0882 | 0 | 57591.2873 | 0 | 175869.3241 | 457575.9054 | 312304.9577 | 1396697.172 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7427577.0399 | 16885212.0838 | 4216.965 | 0.028152 | 263834.1375 | 599777.7394 | 5378.6158 | 12227.2805
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1897 | 0.43963 | 0.010243 | 4 | 189466.4978 | 420308.3355 | 3862.5308 | 8568.5539 | 79.2024 | 0 | 93.84 | 165968.2241 | 5059.017 | 182049.0015 | 139834.9685 | 0 | 66164.5584 | 0 | 218039.5501 | 567294.1833 | 387189.9368 | 1731599.4396 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7762479.3075 | 17220114.3514 | 5623.4133 | 0.04097 | 189466.4978 | 420308.3355 | 3862.5308 | 8568.5539
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.407 | 0.57552 | 0.014526 | 4 | 140126.7536 | 302895.8031 | 2856.6734 | 6174.9406 | 79.8337 | 0 | 122.2126 | 201276.4156 | 6173.0934 | 225704.5479 | 174170.905 | 0 | 74289.5492 | 0 | 265829.6594 | 691634.2445 | 472054.5835 | 2111132.9985 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8142012.8665 | 17599647.9104 | 7498.9421 | 0.058105 | 140126.7536 | 302895.8031 | 2856.6734 | 6174.9406
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0808 | 0.76233 | 0.020187 | 4 | 107025.1924 | 224152.3395 | 2181.8533 | 4569.6486 | 80.3293 | 0 | 93.4948 | 245878.6494 | 7579.8485 | 282506.1764 | 221693.637 | 0 | 85364.4503 | 0 | 328778.8771 | 855415.1963 | 583838.4485 | 2611055.2835 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8641935.1514 | 18099570.1953 | 10000 | 0.080747 | 107025.1924 | 224152.3395 | 2181.8533 | 4569.6486
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3829 | 1.0207 | 0.027918 | 4 | 83290.468 | 167982.3399 | 1697.9888 | 3424.5472 | 80.7746 | 0 | 113.8887 | 302567.121 | 9370.109 | 356660.2836 | 287404.6732 | 0 | 99855.4415 | 0 | 411784.475 | 1071378.7354 | 731238.0015 | 3270258.8402 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9301138.7081 | 18758773.752 | 13335.2143 | 0.11167 | 83290.468 | 167982.3399 | 1697.9888 | 3424.5472
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8682 | 1.2991 | 0.037568 | 4 | 66336.4113 | 129272.3739 | 1352.3575 | 2635.3922 | 81.0485 | 0 | 95.1769 | 358889.1316 | 11145.7741 | 432478.9627 | 358174.2962 | 0 | 110681.4111 | 0 | 495834.1345 | 1290058.7085 | 880491.5766 | 3937753.9954 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9968633.8633 | 19426268.9072 | 17782.7941 | 0.15027 | 66336.4113 | 129272.3739 | 1352.3575 | 2635.3922
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1318 | 1.6643 | 0.050135 | 4 | 53898.8379 | 101059.3781 | 1098.8007 | 2060.2321 | 81.2707 | 0 | 108.9581 | 427443.4511 | 13303.4415 | 527187.8151 | 450547.4008 | 0 | 124194.9285 | 0 | 601644.0444 | 1565354.3895 | 1068386.5356 | 4778062.0066 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 10808941.8745 | 20266576.9184 | 23713.7371 | 0.20054 | 53898.8379 | 101059.3781 | 1098.8007 | 2060.2321
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.164 | 2.1156 | 0.066212 | 4 | 44567.7434 | 80277.2288 | 908.5737 | 1636.5599 | 81.4417 | 0 | 109.7917 | 506191.7665 | 15779.1351 | 638654.5558 | 564677.1713 | 0 | 138561.3196 | 0 | 726906.9398 | 1891262.7483 | 1290825.6873 | 5772859.3238 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11803739.1917 | 21261374.2356 | 31622.7766 | 0.26485 | 44567.7434 | 80277.2288 | 908.5737 | 1636.5599
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0575 | 2.6634 | 0.086471 | 4 | 37478.0784 | 64821.5736 | 764.0413 | 1321.4755 | 81.5732 | 0 | 134.8878 | 595310.1163 | 18577.3832 | 767744.5575 | 703189.833 | 0 | 153331.8121 | 0 | 872879.9438 | 2271054.5615 | 1550041.4038 | 6932129.6112 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 12963009.4791 | 22420644.5231 | 42169.6503 | 0.34588 | 37478.0784 | 64821.5736 | 764.0413 | 1321.4755
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8971 | 3.3171 | 0.11155 | 4 | 32038.0977 | 53234.8218 | 653.14 | 1085.2638 | 81.6747 | 0 | 114.929 | 694810.3951 | 21697.5378 | 915045.6487 | 868484.5574 | 0 | 168132.3157 | 0 | 1040586.4773 | 2707392.5604 | 1847851.0538 | 8264000.5464 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 14294880.4143 | 23752515.4582 | 56234.1325 | 0.44618 | 32038.0977 | 53234.8218 | 653.14 | 1085.2638
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6593 | 4.0742 | 0.14175 | 4 | 27835.2924 | 44514.847 | 567.4601 | 907.4954 | 81.7527 | 0 | 100.2414 | 803037.3504 | 25086.7579 | 1078556.1279 | 1059901.38 | 0 | 182103.9203 | 0 | 1227987.3593 | 3194971.214 | 2180633.5036 | 9752277.6134 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 15783157.4813 | 25240792.5252 | 74989.4209 | 0.56702 | 27835.2924 | 44514.847 | 567.4601 | 907.4954
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.2233 | 4.921 | 0.17693 | 4 | 24577.8537 | 37941.6525 | 501.0528 | 773.4919 | 81.8115 | 0 | 126.0151 | 917265.5483 | 28658.8715 | 1254397.0514 | 1274013.1048 | 0 | 194401.0067 | 0 | 1430806.8772 | 3722665.9958 | 2540796.0352 | 11363004.4909 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 17393884.3588 | 26851519.4027 | 100000 | 0.70771 | 24577.8537 | 37941.6525 | 501.0528 | 773.4919
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.2157 | 5.8154 | 0.21586 | 4 | 22055.7124 | 33009.2356 | 449.6355 | 672.9379 | 81.8519 | 0 | 133.7485 | 1031743.2315 | 32233.2716 | 1433647.3195 | 1500227.01 | 0 | 203533.6966 | 0 | 1638539.9664 | 4263144.8817 | 2909683.9806 | 13012753.3578 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 19043633.2258 | 28501268.2697 | 133352.1432 | 0.86343 | 22055.7124 | 33009.2356 | 449.6355 | 672.9379
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.1935 | 6.7071 | 0.25661 | 4 | 20112.0525 | 29326.1703 | 410.0114 | 597.8536 | 81.8738 | 0 | 133.861 | 1140736.6561 | 35630.4677 | 1606929.859 | 1725957.6222 | 0 | 208702.0505 | 0 | 1840003.0956 | 4787310.6183 | 3267437.8664 | 14612708.2359 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 20643588.1038 | 30101223.1477 | 177827.941 | 1.0264 | 20112.0525 | 29326.1703 | 410.0114 | 597.8536
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.6844 | 7.5426 | 0.29675 | 4 | 18623.7817 | 26591.479 | 379.671 | 542.1033 | 81.8789 | 0 | 167.9642 | 1238937.3234 | 38685.2886 | 1765157.8907 | 1937800.495 | 0 | 209661.894 | 0 | 2024194.7277 | 5266539.4622 | 3594521.3995 | 16075498.481 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 22106378.349 | 31564013.3929 | 237137.3706 | 1.187 | 18623.7817 | 26591.479 | 379.671 | 542.1033
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.3734 | 8.2866 | 0.33419 | 4 | 17491.1748 | 24566.1256 | 356.5813 | 500.8137 | 81.8711 | 0 | 162.7687 | 1323598.0604 | 41313.552 | 1903144.9535 | 2126842.3672 | 0 | 207137.9765 | 0 | 2184794.3947 | 5684386.8521 | 3879710.829 | 17350928.9853 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 23381808.8532 | 32839443.8971 | 316227.766 | 1.3368 | 17491.1748 | 24566.1256 | 356.5813 | 500.8137
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.1003 | 8.9217 | 0.3675 | 4 | 16633.3859 | 23067.1334 | 339.0941 | 470.2547 | 81.8556 | 0 | 182.2549 | 1393995.0123 | 43494.6969 | 2018991.4761 | 2288572.4493 | 0 | 202236.3458 | 0 | 2319443.0923 | 6034715.1431 | 4118817.0862 | 18420265.3019 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 24451145.1699 | 33908780.2138 | 421696.5034 | 1.47 | 16633.3859 | 23067.1334 | 339.0941 | 470.2547
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.8339 | 9.4451 | 0.39596 | 4 | 15985.9265 | 21957.2682 | 325.8947 | 447.6286 | 81.8368 | 0 | 174.0887 | 1450821.35 | 45252.2284 | 2113242.3701 | 2422157.9293 | 0 | 196053.2208 | 0 | 2428735.5685 | 6319071.747 | 4312896.3113 | 19288230.7253 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 25319110.5933 | 34776745.6372 | 562341.3252 | 1.5838 | 15985.9265 | 21957.2682 | 325.8947 | 447.6286
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.6413 | 9.8651 | 0.41951 | 4 | 15498.3048 | 21134.4866 | 315.9539 | 430.8551 | 81.818 | 0 | 167.4456 | 1495677.496 | 46637.4052 | 2188107.3592 | 2529537.0389 | 0 | 189500.0738 | 0 | 2515289.1555 | 6544266.4259 | 4466596.3069 | 19975611.2615 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 26006491.1294 | 35464126.1733 | 749894.2093 | 1.678 | 15498.3048 | 21134.4866 | 315.9539 | 430.8551
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.6498 | 10.1961 | 0.43853 | 4 | 15131.5757 | 20523.221 | 308.4776 | 418.3936 | 81.8007 | 0 | 152.3781 | 1530603.8152 | 47714.5631 | 2246687.1234 | 2614338.0217 | 0 | 183245.7142 | 0 | 2582809.8026 | 6719941.2993 | 4586498.0178 | 20511838.3573 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 26542718.2253 | 36000353.2692 | 1000000 | 1.7541 | 15131.5757 | 20523.221 | 308.4776 | 418.3936
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.0056 | 10.4549 | 0.45366 | 4 | 14856.0098 | 20067.8366 | 302.8599 | 409.11 | 81.7859 | 0 | 157.8039 | 1557642.2505 | 48547.5859 | 2292211.136 | 2680710.4827 | 0 | 177700.5632 | 0 | 2635156.6872 | 6856137.155 | 4679454.4878 | 20927560.3484 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 26958440.2163 | 36416075.2602 | 1333521.4322 | 1.8146 | 14856.0098 | 20067.8366 | 302.8599 | 409.11
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.8102 | 10.6528 | 0.46546 | 4 | 14649.0626 | 19728.8332 | 298.641 | 402.1989 | 81.7737 | 0 | 175.5745 | 1578174.723 | 49179.6466 | 2326883.3056 | 2731537.2412 | 0 | 172909.7959 | 0 | 2674887.0378 | 6959507.3775 | 4750006.7887 | 21243085.9163 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27273965.7842 | 36731600.8281 | 1778279.41 | 1.8618 | 14649.0626 | 19728.8332 | 298.641 | 402.1989
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.2038 | 10.8054 | 0.47462 | 4 | 14493.706 | 19475.3567 | 295.4738 | 397.0315 | 81.7638 | 0 | 207.8069 | 1593924.3154 | 49664.1618 | 2353538.8722 | 2770774.2701 | 0 | 168997.8952 | 0 | 2705390.8107 | 7038871.9375 | 4804174.7317 | 21485336.9947 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27516216.8626 | 36973851.9065 | 2371373.7057 | 1.8985 | 14493.706 | 19475.3567 | 295.4738 | 397.0315
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.2586 | 10.9209 | 0.48164 | 4 | 14377.1098 | 19286.1694 | 293.0968 | 393.1747 | 81.7561 | 0 | 178.3415 | 1605785.226 | 50028.8649 | 2373647.5317 | 2800467.3769 | 0 | 165815.1285 | 0 | 2728340.2099 | 7098581.5666 | 4844927.7805 | 21667593.685 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27698473.5529 | 37156108.5968 | 3162277.6602 | 1.9266 | 14377.1098 | 19286.1694 | 293.0968 | 393.1747
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.0675 | 11.0093 | 0.48703 | 4 | 14289.6207 | 19144.3807 | 291.3132 | 390.2841 | 81.75 | 0 | 194.7735 | 1614845.1395 | 50307.3354 | 2389027.4995 | 2823231.9637 | 0 | 163327.8949 | 0 | 2745888.5349 | 7144238.7085 | 4876089.718 | 21806956.7944 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27837836.6623 | 37295471.7062 | 4216965.0343 | 1.9481 | 14289.6207 | 19144.3807 | 291.3132 | 390.2841
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.6546 | 11.0735 | 0.49104 | 4 | 14223.9818 | 19039.092 | 289.9751 | 388.1376 | 81.7455 | 0 | 164.2968 | 1621402.9667 | 50508.842 | 2400170.8393 | 2839754.9996 | 0 | 161287.0731 | 0 | 2758518.6411 | 7177099.654 | 4898517.9885 | 21907261.0043 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27938140.8722 | 37395775.9161 | 5623413.2519 | 1.9642 | 14223.9818 | 19039.092 | 289.9751 | 388.1376
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1151 | 11.1238 | 0.49414 | 4 | 14174.7416 | 18959.6762 | 288.9713 | 386.5186 | 81.7419 | 0 | 171.2146 | 1626534.6252 | 50666.4915 | 2408897.1321 | 2852711.243 | 0 | 159777.564 | 0 | 2768448.9518 | 7202936.2856 | 4916152.0205 | 21986124.3138 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28017004.1817 | 37474639.2256 | 7498942.0933 | 1.9765 | 14174.7416 | 18959.6762 | 288.9713 | 386.5186
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.4707 | 11.1627 | 0.49651 | 4 | 14137.8064 | 18899.9066 | 288.2183 | 385.3002 | 81.7391 | 0 | 175.1458 | 1630491.3832 | 50788.0263 | 2415629.3469 | 2862717.0937 | 0 | 158652.443 | 0 | 2776128.5343 | 7222916.984 | 4929789.2577 | 22047113.069 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28077992.937 | 37535627.9809 | 10000000 | 1.986 | 14137.8064 | 18899.9066 | 288.2183 | 385.3002
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7894 | [19 empty] | 100 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.2463 | [19 empty] | 133.3521 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.018 | [19 empty] | 177.8279 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2517 | [19 empty] | 237.1374 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8507 | [19 empty] | 316.2278 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.7287 | [19 empty] | 421.6965 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8807 | [19 empty] | 562.3413 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.5241 | [19 empty] | 749.8942 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | 0.07375 | 0.00051048 | 4 | 3356268.3905 | 8197631.9239 | 68422.0708 | 167119.8149 | 71.793 | 0 | 74.4799 | 44652.1284 | 1265.2521 | 43921.6151 | 45447.7082 | 0 | 31508.6012 | 0 | 65050.1689 | 169247.1959 | 115514.6889 | 516607.3586 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6853233.2815 | 16738912.8023 | 1000 | 0.0020419 | 3356268.3905 | 8197631.9239 | 68422.0708 | 167119.8149
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1847 | 0.11371 | 0.0014403 | 4 | 1218106.6754 | 2934052.3994 | 24832.7522 | 59814.6268 | 75.4325 | 0 | 196.9852 | 62766.4102 | 1837.7783 | 61903.9991 | 55672.6552 | 0 | 37681.4006 | 0 | 85746.275 | 223094.2185 | 152266.3882 | 680969.1251 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7017595.048 | 16903274.5688 | 1333.5214 | 0.0057611 | 1218106.6754 | 2934052.3994 | 24832.7522 | 59814.6268
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.16476 | 0.0027908 | 4 | 645685.1143 | 1531240.6462 | 13163.1644 | 31216.4117 | 78.0142 | 0 | 285.2483 | 83300.2636 | 2495.2708 | 83101.7582 | 68327.7757 | 0 | 44095.0311 | 0 | 109714.8388 | 285455.5049 | 194829.2476 | 871319.6908 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7207945.6136 | 17093625.1345 | 1778.2794 | 0.011163 | 645685.1143 | 1531240.6462 | 13163.1644 | 31216.4117
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 0.23702 | 0.0046665 | 4 | 399494.6292 | 929107.9933 | 8144.2384 | 18941.1232 | 80.0597 | 0 | 408.1788 | 109222.2594 | 3330.1047 | 110978.2273 | 85696.6232 | 0 | 52473.1688 | 0 | 141063.1496 | 367017.3791 | 250496.9027 | 1120277.8149 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7456903.7377 | 17342583.2586 | 2371.3737 | 0.018666 | 399494.6292 | 929107.9933 | 8144.2384 | 18941.1232
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.923 | 0.32262 | 0.0072507 | 4 | 266515.4823 | 607369.2643 | 5433.2786 | 12382.044 | 81.4324 | 0 | 95.2259 | 137009.1108 | 4229.5783 | 141864.311 | 106528.3143 | 0 | 60135.6321 | 0 | 175409.1091 | 456378.5206 | 311487.718 | 1393042.2942 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7729668.2171 | 17615347.7379 | 3162.2777 | 0.029003 | 266515.4823 | 607369.2643 | 5433.2786 | 12382.044
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8607 | 0.43606 | 0.010707 | 4 | 188386.3301 | 419201.7618 | 3840.5102 | 8545.9949 | 82.5024 | 0 | 91.7414 | 170459.9642 | 5312.648 | 180379.2884 | 133697.8151 | 0 | 69304.3379 | 0 | 218070.0809 | 567373.6181 | 387244.1527 | 1731841.9053 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8068467.8282 | 17954147.3491 | 4216.965 | 0.042829 | 188386.3301 | 419201.7618 | 3840.5102 | 8545.9949
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0929 | 0.58572 | 0.015379 | 4 | 138028.9057 | 298724.6297 | 2813.9059 | 6089.9056 | 83.323 | 0 | 99.4826 | 210797.3142 | 6620.6537 | 228249.5011 | 169886.4587 | 0 | 80106.3433 | 0 | 271307.5057 | 705886.477 | 481782.0251 | 2154636.2787 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8491262.2016 | 18376941.7225 | 5623.4133 | 0.061518 | 138028.9057 | 298724.6297 | 2813.9059 | 6089.9056
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5861 | 0.76744 | 0.021531 | 4 | 104216.6283 | 219000.3629 | 2124.5969 | 4464.6186 | 83.8986 | 0 | 108.8329 | 255756.1653 | 8078.7676 | 283190.7633 | 214233.0635 | 0 | 90776.0825 | 0 | 332293.5884 | 864559.7543 | 590079.7972 | 2638967.9821 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8975593.905 | 18861273.4258 | 7498.9421 | 0.086124 | 104216.6283 | 219000.3629 | 2124.5969 | 4464.6186
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3035 | 0.97479 | 0.029221 | 4 | 81240.5038 | 165817.8051 | 1656.1976 | 3380.4202 | 84.247 | 0 | 115.403 | 302997.9705 | 9604.514 | 342809.4703 | 264526.9992 | 0 | 100009.0066 | 0 | 397779.7047 | 1034941.1957 | 706368.632 | 3159037.493 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9495663.4159 | 19381342.9367 | 10000 | 0.11688 | 81240.5038 | 165817.8051 | 1656.1976 | 3380.4202
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9862 | 1.303 | 0.040263 | 4 | 63900.2597 | 125281.8595 | 1302.6932 | 2554.0402 | 84.7381 | 0 | 92.2935 | 372472.2451 | 11857.5273 | 432220.0369 | 343148.7967 | 0 | 117139.3215 | 0 | 497966.7917 | 1295607.445 | 884278.7033 | 3954690.8675 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 10291316.7904 | 20176996.3113 | 13335.2143 | 0.16105 | 63900.2597 | 125281.8595 | 1302.6932 | 2554.0402
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0434 | 1.6749 | 0.053979 | 4 | 51607.8854 | 97393.0626 | 1052.0965 | 1985.4893 | 85.0086 | 0 | 121.0164 | 444823.1327 | 14195.3459 | 528274.127 | 432602.4951 | 0 | 131886.1916 | 0 | 605194.704 | 1574592.4773 | 1074691.7204 | 4806260.194 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11142886.1169 | 21028565.6378 | 17782.7941 | 0.21591 | 51607.8854 | 97393.0626 | 1052.0965 | 1985.4893
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.064 | 2.0425 | 0.070418 | 4 | 42367.7879 | 77464.0785 | 863.7247 | 1579.21 | 85.1816 | 0 | 169.1234 | 511711.9753 | 16354.4612 | 619064.0978 | 521063.5085 | 0 | 138967.797 | 0 | 704793.1175 | 1833727.1189 | 1251556.438 | 5597238.5142 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11933864.4371 | 21819543.9579 | 23713.7371 | 0.28167 | 42367.7879 | 77464.0785 | 863.7247 | 1579.21
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.587 | 2.7147 | 0.094428 | 4 | 35391.3102 | 61563.9601 | 721.4997 | 1255.0646 | 85.3796 | 0 | 115.0177 | 625428.4697 | 20020.0294 | 777167.2343 | 682813.4465 | 0 | 164658.2632 | 0 | 885334.1028 | 2303457.7285 | 1572157.231 | 7031036.5054 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13367662.4283 | 23253341.9492 | 31622.7766 | 0.37771 | 35391.3102 | 61563.9601 | 721.4997 | 1255.0646
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1844 | 3.396 | 0.12245 | 4 | 30095.8763 | 50279.2187 | 613.5451 | 1025.0099 | 85.5021 | 0 | 132.5869 | 732378.8601 | 23462.0546 | 929549.1821 | 846747.3685 | 0 | 181283.5589 | 0 | 1058234.1994 | 2753308.3132 | 1879189.4986 | 8404153.0352 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14740778.9581 | 24626458.479 | 42169.6503 | 0.48979 | 30095.8763 | 50279.2187 | 613.5451 | 1025.0099
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8003 | 4.2014 | 0.15674 | 4 | 26006.1279 | 41773.7061 | 530.1701 | 851.6135 | 85.5971 | 0 | 135.5335 | 850913.1503 | 27271.2219 | 1101998.3225 | 1040519.1031 | 0 | 197710.7279 | 0 | 1255180.8851 | 3265723.19 | 2228923.181 | 9968239.7819 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 16304865.7048 | 26190545.2256 | 56234.1325 | 0.62696 | 26006.1279 | 41773.7061 | 530.1701 | 851.6135
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.3324 | 5.1184 | 0.19736 | 4 | 22831.4425 | 35353.6533 | 465.4498 | 720.732 | 85.6695 | 0 | 130.8377 | 977965.8943 | 31347.8625 | 1290466.7755 | 1261129.5266 | 0 | 212656.6995 | 0 | 1471691.0358 | 3829038.1897 | 2613397.2433 | 11687693.2271 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 18024319.15 | 27909998.6709 | 74989.4209 | 0.78945 | 22831.4425 | 35353.6533 | 465.4498 | 720.732
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.5102 | 6.1136 | 0.24344 | 4 | 20365.0047 | 30517.0314 | 415.1682 | 622.131 | 85.7208 | 0 | 123.7167 | 1108457.3555 | 35527.8742 | 1487517.1571 | 1500623.2503 | 0 | 224664.9462 | 0 | 1699148.3275 | 4420835.4049 | 3017311.0029 | 13494085.3186 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 19830711.2414 | 29716390.7623 | 100000 | 0.97376 | 20365.0047 | 30517.0314 | 415.1682 | 622.131
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.9218 | 7.1361 | 0.29304 | 4 | 18455.4394 | 26889.2883 | 376.2391 | 548.1745 | 85.7507 | 0 | 153.5439 | 1236080.0716 | 39608.1449 | 1683382.2236 | 1746866.8395 | 0 | 232564.8903 | 0 | 1926015.8463 | 5011098.1518 | 3420177.4564 | 15295793.6244 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 21632419.5473 | 31518099.0682 | 133352.1432 | 1.1721 | 18455.4394 | 26889.2883 | 376.2391 | 548.1745
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.0265 | 8.1192 | 0.3432 | 4 | 16986.1023 | 24187.2005 | 346.2847 | 493.0888 | 85.7595 | 0 | 155.9783 | 1353655.4867 | 43358.8648 | 1866461.0286 | 1983953.6735 | 0 | 235468.1391 | 0 | 2138329.9052 | 5563495.7815 | 3797200.1893 | 16981923.0688 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 23318548.9917 | 33204228.5125 | 177827.941 | 1.3728 | 16986.1023 | 24187.2005 | 346.2847 | 493.0888
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.442 | 9.0159 | 0.39118 | 4 | 15862.9598 | 22180.8172 | 323.3879 | 452.186 | 85.7511 | 0 | 152.9803 | 1457132.4526 | 46651.9091 | 2029640.3652 | 2200660.2678 | 0 | 233934.0623 | 0 | 2327527.4322 | 6055748.9371 | 4133173.0828 | 18484468.5092 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 24821094.4321 | 34706773.9529 | 237137.3706 | 1.5647 | 15862.9598 | 22180.8172 | 323.3879 | 452.186
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.9956 | 9.4445 | 0.42492 | 4 | 14985.74 | 20801.8808 | 305.5046 | 424.0745 | 85.7417 | 0 | 149.6838 | 1505440.1822 | 48186.3408 | 2106478.052 | 2304418.1875 | 0 | 213401.3688 | 0 | 2409390.4112 | 6268739.6161 | 4278543.5977 | 19134597.7564 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 25471223.6793 | 35356903.2002 | 316227.766 | 1.6997 | 14985.74 | 20801.8808 | 305.5046 | 424.0745
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.3413 | 10.4475 | 0.47263 | 4 | 14363.0285 | 19592.1034 | 292.8098 | 399.4115 | 85.7067 | 0 | 190.8392 | 1615861.3621 | 51686.0214 | 2283688.3805 | 2547813.3271 | 0 | 222063.8213 | 0 | 2621234.0358 | 6819913.2722 | 4654730.9435 | 20816991.164 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 27153617.0868 | 37039296.6077 | 421696.5034 | 1.8905 | 14363.0285 | 19592.1034 | 292.8098 | 399.4115
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.7802 | 10.9788 | 0.50448 | 4 | 13875.2823 | 18774.2732 | 282.8664 | 382.739 | 85.6809 | 0 | 163.4612 | 1672950.2319 | 53490.768 | 2376178.591 | 2677094.1045 | 0 | 214328.4711 | 0 | 2727676.445 | 7096854.5864 | 4843749.081 | 21662322.2789 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 27998948.2018 | 37884627.7226 | 562341.3252 | 2.0179 | 13875.2823 | 18774.2732 | 282.8664 | 382.739
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.3144 | 11.4006 | 0.53047 | 4 | 13507.8507 | 18166.8066 | 275.3758 | 370.3549 | 85.6569 | 0 | 189.4869 | 1717628.4073 | 54900.8018 | 2448980.9191 | 2779929.2402 | 0 | 206630.8598 | 0 | 2811147.389 | 7314028.8605 | 4991974.9856 | 22325221.4633 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 28661847.3861 | 38547526.907 | 749894.2093 | 2.1219 | 13507.8507 | 18166.8066 | 275.3758 | 370.3549
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.0944 | 11.7316 | 0.55128 | 4 | 13231.4061 | 17714.4428 | 269.7401 | 361.1329 | 85.636 | 0 | 171.568 | 1752302.7072 | 55993.6078 | 2505738.012 | 2860753.2224 | 0 | 199599.5941 | 0 | 2876010.9859 | 7482790.6344 | 5107158.3639 | 22840347.1276 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29176973.0504 | 39062652.5713 | 1000000 | 2.2051 | 13231.4061 | 17714.4428 | 269.7401 | 361.1329
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.2527 | 11.988 | 0.56768 | 4 | 13023.5953 | 17377.1374 | 265.5036 | 354.2564 | 85.6186 | 0 | 180.1024 | 1778945.8889 | 56832.3743 | 2549502.502 | 2923465.0112 | 0 | 193489.5846 | 0 | 2925871.7908 | 7612518.2208 | 5195700.1073 | 23236325.48 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29572951.4029 | 39458630.9237 | 1333521.4322 | 2.2707 | 13023.5953 | 17377.1374 | 265.5036 | 354.2564
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.9117 | 12.1849 | 0.58043 | 4 | 12867.4714 | 17125.3568 | 262.3208 | 349.1236 | 85.6045 | 0 | 172.346 | 1799262.6652 | 57471.4191 | 2582965.2726 | 2971643.63 | 0 | 188366.1437 | 0 | 2963886.5609 | 7711424.8548 | 5263205.9174 | 23538226.4637 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29874852.3866 | 39760531.9074 | 1778279.41 | 2.3217 | 12867.4714 | 17125.3568 | 262.3208 | 349.1236
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.1614 | 12.333 | 0.59019 | 4 | 12750.2297 | 16937.7054 | 259.9307 | 345.298 | 85.5935 | 0 | 170.3935 | 1814474.5188 | 57949.5711 | 2608071.3377 | 3007920.4743 | 0 | 184114.3873 | 0 | 2992286.8128 | 7785316.4845 | 5313638.4729 | 23763772.0593 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30100397.9822 | 39986077.5031 | 2371373.7057 | 2.3608 | 12750.2297 | 16937.7054 | 259.9307 | 345.298
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.1307 | 12.4477 | 0.59774 | 4 | 12662.2153 | 16796.8119 | 258.1364 | 342.4257 | 85.5847 | 0 | 193.0031 | 1826219.9617 | 58318.5725 | 2627486.5439 | 3036050.6547 | 0 | 180803.458 | 0 | 3014262.8844 | 7842493.7149 | 5352663.1075 | 23938298.8976 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30274924.8204 | 40160604.3413 | 3162277.6602 | 2.391 | 12662.2153 | 16796.8119 | 258.1364 | 342.4257
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.8493 | 12.5328 | 0.60343 | 4 | 12596.1585 | 16691.8003 | 256.7897 | 340.2849 | 85.5781 | 0 | 187.2929 | 1834897.8038 | 58591.0917 | 2641847.9977 | 3056901.4248 | 0 | 178133.1223 | 0 | 3030444.8617 | 7884595.9005 | 5381398.7144 | 24066810.917 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30403436.8399 | 40289116.3607 | 4216965.0343 | 2.4137 | 12596.1585 | 16691.8003 | 256.7897 | 340.2849
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.405 | 12.5985 | 0.60779 | 4 | 12546.5912 | 16612.8254 | 255.7792 | 338.6749 | 85.5729 | 0 | 187.9928 | 1841589.9414 | 58801.1884 | 2652933.0629 | 3073020.2272 | 0 | 176111.9128 | 0 | 3042957.9697 | 7917152.4408 | 5403619.222 | 24166185.9652 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30502811.8881 | 40388491.4089 | 5623413.2519 | 2.4312 | 12546.5912 | 16612.8254 | 255.7792 | 338.6749
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.8091 | 12.6462 | 0.61103 | 4 | 12509.4025 | 16554.0711 | 255.0211 | 337.4771 | 85.569 | 0 | 188.9391 | 1846447.5579 | 58953.6561 | 2660984.7838 | 3084741.8562 | 0 | 174492.0145 | 0 | 3051991.7487 | 7940656.4804 | 5419661.2121 | 24237929.3096 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30574555.2324 | 40460234.7533 | 7498942.0933 | 2.4441 | 12509.4025 | 16554.0711 | 255.0211 | 337.4771
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1233 | 12.6833 | 0.61352 | 4 | 12481.5045 | 16509.7859 | 254.4524 | 336.5743 | 85.566 | 0 | 208.8076 | 1850217.7556 | 59071.9723 | 2667237.1844 | 3093851.9282 | 0 | 173293.9851 | 0 | 3059032.402 | 7958974.8161 | 5432163.8526 | 24293843.8962 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30630469.8191 | 40516149.3399 | 10000000 | 2.4541 | 12481.5045 | 16509.7859 | 254.4524 | 336.5743
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.7094 | [19 empty] | 100 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3939 | [19 empty] | 133.3521 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.161 | [19 empty] | 177.8279 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9577 | [19 empty] | 237.1374 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2322 | [19 empty] | 316.2278 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9255 | [19 empty] | 421.6965 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8035 | [19 empty] | 562.3413 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.064723 | 0.00028312 | 4 | 6295787.6633 | 15410154.5097 | 128348.1472 | 314156.8435 | 72.2251 | 0 | 72.926 | 41058.1183 | 1164.7525 | 39550.3068 | 42741.3206 | 0 | 31005.1156 | 0 | 60652.6494 | 157805.7521 | 107705.6684 | 481683.6837 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7129915.7524 | 17451843.8774 | 749.8942 | 0.0011325 | 6295787.6633 | 15410154.5097 | 128348.1472 | 314156.8435
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0485 | 0.10416 | 0.0011789 | 4 | 1547455.0596 | 3736263.8936 | 31546.9645 | 76168.7931 | 76.8769 | 0 | 177.2152 | 60017.0244 | 1772.6485 | 57637.5595 | 52369.1331 | 0 | 37814.0144 | 0 | 81748.0482 | 212691.6526 | 145166.4233 | 649216.504 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7297448.5727 | 17619376.6977 | 1000 | 0.0047158 | 1547455.0596 | 3736263.8936 | 31546.9645 | 76168.7931
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4764 | 0.15887 | 0.0025454 | 4 | 737339.2424 | 1751137.063 | 15031.6578 | 35699.2976 | 80.3092 | 0 | 255.2486 | 83124.0301 | 2527.809 | 80568.0479 | 65270.3371 | 0 | 45835.4273 | 0 | 108157.0041 | 281402.3386 | 192062.8783 | 858947.8724 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7507179.9411 | 17829108.0661 | 1333.5214 | 0.010181 | 737339.2424 | 1751137.063 | 15031.6578 | 35699.2976
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.22428 | 0.0044818 | 4 | 431432.576 | 1007200.0842 | 8795.3366 | 20533.1361 | 82.5886 | 0 | 349.5228 | 107749.3765 | 3340.291 | 105962.6945 | 80388.7091 | 0 | 53246.2696 | 0 | 136768.0629 | 355842.4446 | 242869.7802 | 1086167.6283 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7734399.697 | 18056327.822 | 1778.2794 | 0.017927 | 431432.576 | 1007200.0842 | 8795.3366 | 20533.1361
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6498 | 0.31165 | 0.0072018 | 4 | 278337.2208 | 636648.3924 | 5674.2807 | 12978.9386 | 84.3353 | 0 | 75.0061 | 137517.4825 | 4329.099 | 137665.5014 | 100849.8993 | 0 | 61924.5206 | 0 | 172491.7361 | 448788.1144 | 306307.1098 | 1369873.4632 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8018105.5319 | 18340033.6569 | 2371.3737 | 0.028807 | 278337.2208 | 636648.3924 | 5674.2807 | 12978.9386
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5124 | 0.42448 | 0.010842 | 4 | 192738.9551 | 430747.9719 | 3929.2443 | 8781.38 | 85.647 | 0 | 80.6941 | 172288.3176 | 5484.8446 | 176089.7257 | 126700.4859 | 0 | 71678.4397 | 0 | 215374.3073 | 560359.7681 | 382457.056 | 1710432.9448 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8358665.0135 | 18680593.1385 | 3162.2777 | 0.043368 | 192738.9551 | 430747.9719 | 3929.2443 | 8781.38
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6307 | 0.57133 | 0.015754 | 4 | 139263.5477 | 303062.7801 | 2839.0758 | 6178.3447 | 86.6412 | 0 | 94.9793 | 213568.5079 | 6858.9402 | 223158.7498 | 160511.1664 | 0 | 82821.5213 | 0 | 267898.3653 | 697016.5931 | 475728.1471 | 2127561.991 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8775794.0597 | 19097722.1847 | 4216.965 | 0.063016 | 139263.5477 | 303062.7801 | 2839.0758 | 6178.3447
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0138 | 0.75313 | 0.022236 | 4 | 104126.9339 | 220176.9981 | 2122.7684 | 4488.6059 | 87.3627 | 0 | 112.6119 | 260376.2462 | 8416.4917 | 278194.0254 | 202384.1499 | 0 | 94346.9215 | 0 | 329049.9555 | 856120.4867 | 584319.8237 | 2613208.1005 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9261440.1692 | 19583368.2942 | 5623.4133 | 0.088944 | 104126.9339 | 220176.9981 | 2122.7684 | 4488.6059
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6728 | 0.97045 | 0.030553 | 4 | 80265.4904 | 164725.9415 | 1636.3206 | 3358.1611 | 87.847 | 0 | 107.4966 | 311879.1633 | 10126.1214 | 340613.5824 | 252483.7215 | 0 | 105488.3991 | 0 | 398030.4852 | 1035593.6752 | 706813.9627 | 3161029.1108 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9809261.1795 | 20131189.3045 | 7498.9421 | 0.12221 | 80265.4904 | 164725.9415 | 1636.3206 | 3358.1611
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1017 | 1.2916 | 0.042167 | 4 | 62771.9547 | 123969.2448 | 1279.6912 | 2527.2807 | 88.3781 | 0 | 108.7253 | 382340.3076 | 12471.2994 | 427955.9447 | 326206.0325 | 0 | 122891.6333 | 0 | 496027.4348 | 1290561.6361 | 880834.835 | 3939289.1234 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 10587521.1921 | 20909449.3171 | 10000 | 0.16867 | 62771.9547 | 123969.2448 | 1279.6912 | 2527.2807
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9445 | 1.6662 | 0.056847 | 4 | 50331.4825 | 95724.6635 | 1026.0753 | 1951.4767 | 88.7072 | 0 | 104.2753 | 457958.1188 | 14980.7803 | 524521.6983 | 412386.0783 | 0 | 138820.0045 | 0 | 603980.0053 | 1571432.0805 | 1072534.6846 | 4796613.4506 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 11444845.5193 | 21766773.6444 | 13335.2143 | 0.22739 | 50331.4825 | 95724.6635 | 1026.0753 | 1951.4767
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4741 | 2.1314 | 0.075769 | 4 | 41115.0781 | 75172.2831 | 838.1865 | 1532.4887 | 88.9593 | 0 | 107.6918 | 545078.4651 | 17867.9361 | 638597.205 | 519396.3359 | 0 | 155809.6246 | 0 | 731932.331 | 1904337.7853 | 1299749.6687 | 5812769.3517 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 12461001.4204 | 22782929.5454 | 17782.7941 | 0.30308 | 41115.0781 | 75172.2831 | 838.1865 | 1532.4887
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.825 | 2.7049 | 0.099925 | 4 | 34175.6376 | 59999.914 | 696.7166 | 1223.1794 | 89.1537 | 0 | 108.2661 | 645002.3253 | 21174.5508 | 772588.7803 | 651308.6752 | 0 | 173777.6849 | 0 | 882902.2865 | 2297130.6412 | 1567838.8639 | 7011723.8081 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 13659955.8768 | 23981884.0019 | 23713.7371 | 0.3997 | 34175.6376 | 59999.914 | 696.7166 | 1223.1794
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.1233 | 3.4033 | 0.13037 | 4 | 28881.5843 | 48675.5401 | 588.7902 | 992.3167 | 89.3041 | 0 | 152.9974 | 758535.5466 | 24925.6382 | 928323.3732 | 811946.6516 | 0 | 192420.1852 | 0 | 1059299.044 | 2756078.8203 | 1881080.4266 | 8412609.6856 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15060841.7544 | 25382769.8794 | 31622.7766 | 0.52147 | 28881.5843 | 48675.5401 | 588.7902 | 992.3167
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.4445 | 4.2367 | 0.16802 | 4 | 24801.0734 | 40159.4139 | 505.6034 | 818.704 | 89.4204 | 0 | 135.113 | 885323.3375 | 29107.8717 | 1106013.0928 | 1003610.9608 | 0 | 211037.6719 | 0 | 1261686.2446 | 3282648.8009 | 2240475.2583 | 10019903.2387 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16668135.3074 | 26990063.4324 | 42169.6503 | 0.67207 | 24801.0734 | 40159.4139 | 505.6034 | 818.704
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.546 | 5.173 | 0.2131 | 4 | 21590.1845 | 33699.7124 | 440.1451 | 687.0142 | 89.5075 | 0 | 122.4199 | 1019274.1992 | 33519.1936 | 1297494.2286 | 1218942.5349 | 0 | 226011.2192 | 0 | 1480144.1364 | 3851031.4237 | 2628408.0775 | 11754825.013 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 18403057.0817 | 28724985.2068 | 56234.1325 | 0.85238 | 21590.1845 | 33699.7124 | 440.1451 | 687.0142
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.1861 | 6.312 | 0.26728 | 4 | 19134.1465 | 28788.6067 | 390.0755 | 586.8947 | 89.5769 | 0 | 126.0054 | 1172924.5581 | 38570.2474 | 1521318.8117 | 1480904.0632 | 0 | 244673.1883 | 0 | 1738772.4388 | 4523929.2145 | 3087674.6463 | 13808767.1683 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 20456999.237 | 30778927.362 | 74989.4209 | 1.0691 | 19134.1465 | 28788.6067 | 390.0755 | 586.8947
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.8755 | 7.4564 | 0.32577 | 4 | 17225.649 | 25146.7424 | 351.1682 | 512.6504 | 89.6179 | 0 | 140.6521 | 1319195.6177 | 43368.6816 | 1738174.617 | 1744241.957 | 0 | 255797.7536 | 0 | 1989303.6645 | 5175760.0727 | 3532562.6008 | 15798404.9649 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 22446637.0336 | 32768565.1586 | 100000 | 1.3031 | 17225.649 | 25146.7424 | 351.1682 | 512.6504
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5092 | 8.5909 | 0.38671 | 4 | 15749.886 | 22422.7896 | 321.0827 | 457.1189 | 89.6337 | 0 | 142.1854 | 1457677.2999 | 47900.5729 | 1946699.5301 | 2005640.2324 | 0 | 261457.3141 | 0 | 2230556.2302 | 5803449.7611 | 3960973.7109 | 17714354.6516 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 24362586.7203 | 34684514.8453 | 133352.1432 | 1.5468 | 15749.886 | 22422.7896 | 321.0827 | 457.1189
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.6159 | 9.6528 | 0.44659 | 4 | 14616.4368 | 20394.6781 | 297.9758 | 415.7731 | 89.6272 | 0 | 168.5705 | 1582273.3361 | 51966.8412 | 2136935.3134 | 2250727.3088 | 0 | 261649.8729 | 0 | 2450585.5422 | 6375920.8966 | 4351697.024 | 19461756.1351 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 26109988.2038 | 36431916.3288 | 177827.941 | 1.7863 | 14616.4368 | 20394.6781 | 297.9758 | 415.7731
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8534 | 10.5971 | 0.5023 | 4 | 13751.3432 | 18888.6712 | 280.3397 | 385.0711 | 89.6047 | 0 | 146.3209 | 1689496.167 | 55456.0634 | 2302631.0067 | 2469148.5078 | 0 | 257330.78 | 0 | 2641884.3847 | 6873641.244 | 4691401.3882 | 20980989.5417 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 27629221.6104 | 37951149.7354 | 237137.3706 | 2.0092 | 13751.3432 | 18888.6712 | 280.3397 | 385.0711
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.0601 | 11.4034 | 0.5518 | 4 | 13094.3375 | 17770.8006 | 266.9458 | 362.2818 | 89.5736 | 0 | 173.5761 | 1778658.9498 | 58349.5042 | 2441830.2022 | 2656113.3139 | 0 | 250025.7188 | 0 | 2802141.2986 | 7290596.8609 | 4975982.1643 | 22253698.0127 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 28901930.0814 | 39223858.2064 | 316227.766 | 2.2072 | 13094.3375 | 17770.8006 | 266.9458 | 362.2818
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.2003 | 12.0686 | 0.59407 | 4 | 12597.1614 | 16940.872 | 256.8102 | 345.3626 | 89.5399 | 0 | 165.8688 | 1850662.7719 | 60680.2088 | 2555190.1845 | 2810674.5137 | 0 | 241166.6857 | 0 | 2932166.0022 | 7628894.4678 | 5206877.2324 | 23286312.067 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 29934544.1357 | 40256472.2607 | 421696.5034 | 2.3763 | 12597.1614 | 16940.872 | 256.8102 | 345.3626
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.3561 | 12.6044 | 0.6291 | 4 | 12221.8752 | 16323.7444 | 249.1595 | 332.7816 | 89.5076 | 0 | 163.8301 | 1907714.4746 | 62522.8876 | 2645621.0911 | 2935438.5075 | 0 | 232001.3989 | 0 | 3035486.3603 | 7897712.8455 | 5390351.2988 | 24106848.8642 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 30755080.9329 | 41077009.0579 | 562341.3252 | 2.5164 | 12221.8752 | 16323.7444 | 249.1595 | 332.7816
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.6398 | 13.0265 | 0.65738 | 4 | 11939.0833 | 15864.5131 | 243.3944 | 323.4196 | 89.4791 | 0 | 164.2906 | 1952083.0501 | 63953.3104 | 2716326.8866 | 3033888.1381 | 0 | 223284.586 | 0 | 3115919.0287 | 8106982.1499 | 5533181.8991 | 24745619.0489 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 31393851.1176 | 41715779.2427 | 749894.2093 | 2.6295 | 11939.0833 | 15864.5131 | 243.3944 | 323.4196
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.195 | 13.3541 | 0.67977 | 4 | 11726.2443 | 15522.3371 | 239.0554 | 316.4438 | 89.4551 | 0 | 183.8423 | 1986184.1067 | 65051.0924 | 2770898.1556 | 3110409.662 | 0 | 215486.3038 | 0 | 3177731.435 | 8267805.3515 | 5642947.0388 | 25236513.1457 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 31884745.2144 | 42206673.3394 | 1000000 | 2.7191 | 11726.2443 | 15522.3371 | 239.0554 | 316.4438
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1707 | 13.607 | 0.69731 | 4 | 11566.1917 | 15266.8406 | 235.7925 | 311.2352 | 89.4355 | 0 | 174.693 | 2012302.8414 | 65890.9237 | 2812830.7009 | 3169525.9113 | 0 | 208851.4275 | 0 | 3225066.7039 | 8390962.0113 | 5727003.9897 | 25612434.5097 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32260666.5784 | 42582594.7034 | 1333521.4322 | 2.7892 | 11566.1917 | 15266.8406 | 235.7925 | 311.2352
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.6787 | 13.7996 | 0.71085 | 4 | 11445.9104 | 15076.0576 | 233.3404 | 307.3458 | 89.4199 | 0 | 160.1774 | 2032094.7192 | 66526.7365 | 2844684.5095 | 3214617.0827 | 0 | 203344.7667 | 0 | 3260894.4477 | 8484178.4515 | 5790626.1256 | 25896966.8394 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32545198.9081 | 42867127.0331 | 1778279.41 | 2.8434 | 11445.9104 | 15076.0576 | 233.3404 | 307.3458
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.8313 | 13.9467 | 0.72126 | 4 | 11355.5612 | 14933.2864 | 231.4985 | 304.4352 | 89.4076 | 0 | 180.6439 | 2047138.3526 | 67009.6702 | 2868942.0257 | 3249061.5396 | 0 | 198920.5645 | 0 | 3288118.1395 | 8555008.9132 | 5838969.3711 | 26113168.5764 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32761400.6451 | 43083328.7701 | 2371373.7057 | 2.8851 | 11355.5612 | 14933.2864 | 231.4985 | 304.4352
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7056 | 14.0582 | 0.72921 | 4 | 11287.7211 | 14826.4469 | 230.1155 | 302.2572 | 89.3981 | 0 | 163.7272 | 2058501.1431 | 67374.2422 | 2887290.5761 | 3275176.592 | 0 | 195413.6405 | 0 | 3308664.9156 | 8608467.4099 | 5875455.8936 | 26276344.413 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32924576.4817 | 43246504.6067 | 3162277.6602 | 2.9168 | 11287.7211 | 14826.4469 | 230.1155 | 302.2572
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3707 | 14.1429 | 0.73527 | 4 | 11236.7974 | 14746.3652 | 229.0773 | 300.6246 | 89.3908 | 0 | 166.3051 | 2067118.4607 | 67650.6113 | 2901220.9081 | 3295038.3795 | 0 | 192689.1561 | 0 | 3324249.8312 | 8649016.1633 | 5903131.2509 | 26400114.7611 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33048346.8298 | 43370274.9548 | 4216965.0343 | 2.9411 | 11236.7974 | 14746.3652 | 229.0773 | 300.6246
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8628 | 14.2055 | 0.73981 | 4 | 11198.5805 | 14686.6033 | 228.2982 | 299.4063 | 89.3853 | 0 | 184.7764 | 2073479.1108 | 67854.5416 | 2911511.6468 | 3309730.3105 | 0 | 190536.2226 | 0 | 3335713.6147 | 8678842.5764 | 5923488.3908 | 26491156.4143 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33139388.483 | 43461316.608 | 5623413.2519 | 2.9592 | 11198.5805 | 14686.6033 | 228.2982 | 299.4063
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2332 | 14.2527 | 0.74324 | 4 | 11169.905 | 14641.8337 | 227.7136 | 298.4936 | 89.3811 | 0 | 169.5436 | 2078258.6326 | 68007.7429 | 2919249.0295 | 3320787.7319 | 0 | 188881.9426 | 0 | 3344322.181 | 8701240.3001 | 5938775.2975 | 26559522.8581 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33207754.9268 | 43529683.0518 | 7498942.0933 | 2.973 | 11169.905 | 14641.8337 | 227.7136 | 298.4936
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.5233 | 14.2896 | 0.74588 | 4 | 11148.3917 | 14608.0337 | 227.275 | 297.8045 | 89.3778 | 0 | 163.1089 | 2081995.8275 | 68127.5123 | 2925301.8359 | 3329444.2328 | 0 | 187669.7173 | 0 | 3351090.2591 | 8718849.451 | 5950793.9047 | 26613272.7406 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33261504.8093 | 43583432.9343 | 10000000 | 2.9835 | 11148.3917 | 14608.0337 | 227.275 | 297.8045
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0782 | [19 empty] | 100 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0695 | [19 empty] | 133.3521 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2117 | [19 empty] | 177.8279 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2553 | [19 empty] | 237.1374 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7587 | [19 empty] | 316.2278 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4227 | [19 empty] | 421.6965 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.5225 | [19 empty] | 562.3413 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.093195 | 0.00083639 | 4 | 2264697.9155 | 5482808.2989 | 46168.9302 | 111774.4632 | 77.7404 | 0 | 58.9036 | 56144.0261 | 1666.1523 | 52692.138 | 49172.1358 | 0 | 37591.9544 | 0 | 76933.8986 | 200166.2228 | 136617.5601 | 610984.0881 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7576682.3935 | 18343063.2498 | 749.8942 | 0.0033456 | 2264697.9155 | 5482808.2989 | 46168.9302 | 111774.4632
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.14261 | 0.0021513 | 4 | 903038.4633 | 2154180.5864 | 18409.6605 | 43915.885 | 81.8006 | 0 | 210.5277 | 78301.1975 | 2402.4544 | 73810.755 | 60306.8105 | 0 | 45140.1517 | 0 | 101384.9339 | 263782.8011 | 180037.182 | 805166.286 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7770864.5914 | 18537245.4478 | 1000 | 0.0086052 | 903038.4633 | 2154180.5864 | 18409.6605 | 43915.885
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.21012 | 0.0041114 | 4 | 487282.0635 | 1141952.8421 | 9933.904 | 23280.2533 | 84.8356 | 0 | 307.3393 | 105218.5845 | 3310.7373 | 100392.8642 | 75458.0519 | 0 | 53949.6093 | 0 | 131948.6404 | 343303.2959 | 234311.5537 | 1047893.3372 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8013591.6426 | 18779972.499 | 1333.5214 | 0.016445 | 487282.0635 | 1141952.8421 | 9933.904 | 23280.2533
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.29732 | 0.0068537 | 4 | 302808.4412 | 695527.9011 | 6173.1597 | 14179.277 | 87.0285 | 0 | 442.9383 | 136335.4777 | 4368.4622 | 132294.8796 | 94757.0056 | 0 | 63522.1532 | 0 | 168198.4115 | 437617.7645 | 298683.1164 | 1335777.2708 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8301475.5762 | 19067856.4325 | 1778.2794 | 0.027415 | 302808.4412 | 695527.9011 | 6173.1597 | 14179.277
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1808 | 0.40881 | 0.010616 | 4 | 203539.7504 | 457072.7537 | 4149.4331 | 9318.0463 | 88.633 | 0 | 102.7572 | 172310.8922 | 5596.2484 | 170462.0114 | 119430.9555 | 0 | 73872.9993 | 0 | 211252.5117 | 549635.7015 | 375137.6601 | 1677698.9801 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8643397.2855 | 19409778.1419 | 2371.3737 | 0.042465 | 203539.7504 | 457072.7537 | 4149.4331 | 9318.0463
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1897 | 0.55162 | 0.015692 | 4 | 144232.4322 | 315755.9411 | 2940.3732 | 6437.112 | 89.8317 | 0 | 91.4038 | 214257.7245 | 7030.2956 | 216425.3657 | 151033.2644 | 0 | 85284.5308 | 0 | 262872.1606 | 683939.4394 | 466802.7209 | 2087645.502 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9053343.8074 | 19819724.6638 | 3162.2777 | 0.062769 | 144232.4322 | 315755.9411 | 2940.3732 | 6437.112
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4607 | 0.7318 | 0.022428 | 4 | 106329.93 | 226341.1551 | 2167.6794 | 4614.2706 | 90.7242 | 0 | 103.4082 | 262644.7231 | 8683.8171 | 271148.2334 | 190769.1327 | 0 | 97591.3673 | 0 | 324026.5367 | 843050.5815 | 575399.3448 | 2573313.7365 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9539012.0419 | 20305392.8983 | 4216.965 | 0.089711 | 106329.93 | 226341.1551 | 2167.6794 | 4614.2706
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0271 | 0.95359 | 0.03121 | 4 | 80926.2428 | 167166.6118 | 1649.7909 | 3407.9175 | 91.3615 | 0 | 99.8861 | 317390.4608 | 10551.8924 | 334939.5269 | 239748.0742 | 0 | 110286.4063 | 0 | 395037.3806 | 1027806.2311 | 701498.872 | 3137258.8443 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10102957.1497 | 20869338.0061 | 5623.4133 | 0.12484 | 80926.2428 | 167166.6118 | 1649.7909 | 3407.9175
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3318 | 1.2816 | 0.043348 | 4 | 62878.4046 | 124971.0757 | 1281.8613 | 2547.7044 | 91.9731 | 0 | 93.2412 | 391913.9331 | 13097.0309 | 424095.2975 | 312026.7058 | 0 | 129968.163 | 0 | 495729.4408 | 1289786.3169 | 880305.6637 | 3936922.5517 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10902620.8571 | 21669001.7135 | 7498.9421 | 0.17339 | 62878.4046 | 124971.0757 | 1281.8613 | 2547.7044
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7996 | 1.6324 | 0.058503 | 4 | 50005.1998 | 96012.919 | 1019.4236 | 1957.3532 | 92.3521 | 0 | 102.8249 | 465388.8549 | 15601.0901 | 514514.3727 | 389275.5976 | 0 | 144362.8449 | 0 | 596365.6765 | 1551621.1587 | 1059013.3235 | 4736142.9188 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 11701841.2242 | 22468222.0806 | 10000 | 0.23401 | 50005.1998 | 96012.919 | 1019.4236 | 1957.3532
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0781 | 2.0984 | 0.078521 | 4 | 40500.1438 | 74778.8602 | 825.6502 | 1524.4682 | 92.6617 | 0 | 68.5284 | 555998.7049 | 18684.0438 | 628840.8496 | 491882.9368 | 0 | 162604.2191 | 0 | 724624.1941 | 1885323.5122 | 1286772.0366 | 5754730.497 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 12720428.8024 | 23486809.6588 | 13335.2143 | 0.31408 | 40500.1438 | 74778.8602 | 825.6502 | 1524.4682
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1077 | 2.6712 | 0.10398 | 4 | 33461.6608 | 59348.321 | 682.1612 | 1209.8958 | 92.8982 | 0 | 57.9479 | 659503.5474 | 22200.0588 | 762647.3855 | 618007.0997 | 0 | 181939.9146 | 0 | 875276.2224 | 2277289.1868 | 1554296.6636 | 6951160.079 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 13916858.3844 | 24683239.2408 | 17782.7941 | 0.4159 | 33461.6608 | 59348.321 | 682.1612 | 1209.8958
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0723 | 3.3772 | 0.13635 | 4 | 28107.9654 | 47848.3873 | 573.0189 | 975.4541 | 93.0819 | 0 | 76.6578 | 778381.8702 | 26231.8232 | 919905.812 | 773545.2605 | 0 | 202496.0181 | 0 | 1053218.7058 | 2740259.0275 | 1870283.093 | 8364321.6103 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15330019.9157 | 26096400.772 | 23713.7371 | 0.5454 | 28107.9654 | 47848.3873 | 573.0189 | 975.4541
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.0286 | 4.2246 | 0.17672 | 4 | 23989.2258 | 39219.8968 | 489.0528 | 799.5506 | 93.2233 | 0 | 66.8063 | 911725.7574 | 30746.7045 | 1100195.6108 | 960325.8088 | 0 | 223090.4355 | 0 | 1258172.8836 | 3273507.7565 | 2234236.3077 | 9992001.2649 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 16957699.5702 | 27724080.4266 | 31622.7766 | 0.70689 | 23989.2258 | 39219.8968 | 489.0528 | 799.5506
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0855 | 5.2286 | 0.22619 | 4 | 20794.2894 | 32693.8101 | 423.9197 | 666.5075 | 93.3332 | 0 | 71.6709 | 1059889.9821 | 35754.5138 | 1304708.7165 | 1181634.603 | 0 | 243478.9852 | 0 | 1491932.0523 | 3881701.1627 | 2649340.8045 | 11848440.8202 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 18814139.1256 | 29580519.9819 | 42169.6503 | 0.90477 | 20794.2894 | 32693.8101 | 423.9197 | 666.5075
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.1318 | 6.3733 | 0.28486 | 4 | 18302.9391 | 27751.7332 | 373.1302 | 565.7566 | 93.4159 | 0 | 67.2853 | 1218927.5086 | 41119.9202 | 1528514.614 | 1433964.2256 | 0 | 261928.3976 | 0 | 1748937.3197 | 4550376.1496 | 3105725.223 | 13889493.3583 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 20855191.6637 | 31621572.5201 | 56234.1325 | 1.1394 | 18302.9391 | 27751.7332 | 373.1302 | 565.7566
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.646 | 7.2996 | 0.34283 | 4 | 16344.4819 | 24195.6187 | 333.2044 | 493.2604 | 93.4605 | 0 | 277.4452 | 1341488.2352 | 45247.3091 | 1703726.4379 | 1638189.9551 | 0 | 258906.5314 | 0 | 1945147.8028 | 5060875.5783 | 3454151.5728 | 15447733.4227 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 22413431.7281 | 33179812.5845 | 74989.4209 | 1.3713 | 16344.4819 | 24195.6187 | 333.2044 | 493.2604
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.2091 | 8.9408 | 0.42512 | 4 | 14826.5304 | 21157.8844 | 302.2589 | 431.3321 | 93.5001 | 0 | 83.5686 | 1547864.9003 | 52179.9232 | 2003775.7477 | 2000366.6706 | 0 | 287036.5346 | 0 | 2297577.2728 | 5977824.766 | 4079988.2348 | 18246614.0501 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 25212312.3555 | 35978693.2118 | 100000 | 1.7005 | 14826.5304 | 21157.8844 | 302.2589 | 431.3321
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9445 | 10.1762 | 0.49789 | 4 | 13666.2172 | 19072.2008 | 278.6043 | 388.8126 | 93.499 | 0 | 83.5304 | 1695637.3958 | 57127.1523 | 2222369.9859 | 2273460.7711 | 0 | 289937.5199 | 0 | 2550027.8017 | 6634649.2575 | 4528284.4466 | 20251494.3308 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 27217192.6361 | 37983573.4925 | 133352.1432 | 1.9916 | 13666.2172 | 19072.2008 | 278.6043 | 388.8126
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.9714 | 11.3064 | 0.56758 | 4 | 12776.5081 | 17518.7434 | 260.4664 | 357.1433 | 93.476 | 0 | 75.0452 | 1825994.8377 | 61477.0486 | 2417785.0757 | 2523844.0425 | 0 | 287214.7438 | 0 | 2775363.1418 | 7220925.5898 | 4928430.0902 | 22041034.5701 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 29006732.8755 | 39773113.7319 | 177827.941 | 2.2703 | 12776.5081 | 17518.7434 | 260.4664 | 357.1433
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.9823 | 12.2889 | 0.63085 | 4 | 12098.2592 | 16364.8896 | 246.6394 | 333.6204 | 93.4395 | 0 | 85.7762 | 1935953.9764 | 65134.1865 | 2584522.5503 | 2741994.1573 | 0 | 280087.3346 | 0 | 2966999.96 | 7719525.2804 | 5268734.6243 | 23562952.0697 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 30528650.3751 | 41295031.2315 | 237137.3706 | 2.5234 | 12098.2592 | 16364.8896 | 246.6394 | 333.6204
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.8996 | 13.1142 | 0.68597 | 4 | 11583.5084 | 15507.2964 | 236.1455 | 316.1372 | 93.3977 | 0 | 83.9483 | 2026115.3296 | 68123.6357 | 2722557.7519 | 2925664.3405 | 0 | 270441.9263 | 0 | 3125032.1638 | 8130692.6579 | 5549364.808 | 24817992.6136 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 31783690.919 | 42550071.7754 | 316227.766 | 2.7439 | 11583.5084 | 15507.2964 | 236.1455 | 316.1372
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.725 | 13.7842 | 0.73222 | 4 | 11194.0953 | 14870.0154 | 228.2068 | 303.1454 | 93.3563 | 0 | 86.1435 | 2097935.4625 | 70498.4742 | 2833377.4084 | 3075105.1362 | 0 | 259701.9809 | 0 | 3251281.2003 | 8459166.7536 | 5773555.1278 | 25820621.5438 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 32786319.8492 | 43552700.7056 | 421696.5034 | 2.9289 | 11194.0953 | 14870.0154 | 228.2068 | 303.1454
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.6085 | 14.3214 | 0.77017 | 4 | 10900.1662 | 14394.9547 | 222.2146 | 293.4606 | 93.3187 | 0 | 93.0803 | 2154667.1715 | 72370.0647 | 2921466.0839 | 3195140.6609 | 0 | 249259.181 | 0 | 3351232.2332 | 8719218.8385 | 5951046.0193 | 26614400.2529 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 33580098.5583 | 44346479.4147 | 562341.3252 | 3.0807 | 10900.1662 | 14394.9547 | 222.2146 | 293.4606
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.6387 | 14.7393 | 0.80043 | 4 | 10678.6618 | 14041.3451 | 217.699 | 286.2518 | 93.2866 | 0 | 98.8127 | 2198291.9506 | 73806.5284 | 2989538.7098 | 3288652.832 | 0 | 239568.1876 | 0 | 3428044.7013 | 8919069.1241 | 6087447.9457 | 27224419.9795 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 34190118.2849 | 44956499.1413 | 749894.2093 | 3.2017 | 10678.6618 | 14041.3451 | 217.699 | 286.2518
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0017 | 15.0643 | 0.82431 | 4 | 10511.9279 | 13777.1819 | 214.2999 | 280.8665 | 93.26 | 0 | 88.685 | 2231928.3378 | 74912.4191 | 3042226.8022 | 3361479.0638 | 0 | 231190.307 | 0 | 3487277.4026 | 9073180.4627 | 6192632.101 | 27694826.8962 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 34660525.2015 | 45426906.0579 | 1000000 | 3.2973 | 10511.9279 | 13777.1819 | 214.2999 | 280.8665
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.8117 | 15.3128 | 0.84285 | 4 | 10386.5282 | 13579.9671 | 211.7434 | 276.846 | 93.2388 | 0 | 89.55 | 2257469.1844 | 75751.1425 | 3082352.3819 | 3417202.6627 | 0 | 224123.0966 | 0 | 3532190.4026 | 9190034.8756 | 6272387.6389 | 28051511.3851 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35017209.6905 | 45783590.5469 | 1333521.4322 | 3.3714 | 10386.5282 | 13579.9671 | 211.7434 | 276.846
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.1876 | 15.5014 | 0.8571 | 4 | 10292.277 | 13432.6234 | 209.822 | 273.8422 | 93.2221 | 0 | 100.4338 | 2276756.8764 | 76383.9353 | 3112722.2804 | 3459528.2587 | 0 | 218322.2847 | 0 | 3566048.3178 | 9278126.2259 | 6332511.7956 | 28320399.9749 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35286098.2803 | 46052479.1367 | 1778279.41 | 3.4284 | 10292.277 | 13432.6234 | 209.822 | 273.8422
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2398 | 15.6454 | 0.86804 | 4 | 10221.4729 | 13322.239 | 208.3786 | 271.5919 | 93.2091 | 0 | 100.3789 | 2291433.6242 | 76865.1086 | 3135871.4794 | 3491877.2596 | 0 | 213716.081 | 0 | 3591807.7855 | 9345147.0769 | 6378254.9036 | 28524973.3187 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35490671.6241 | 46257052.4805 | 2371373.7057 | 3.4722 | 10221.4729 | 13322.239 | 208.3786 | 271.5919
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.0272 | 15.7531 | 0.87632 | 4 | 10168.3041 | 13239.7799 | 207.2946 | 269.9108 | 93.1991 | 0 | 92.1882 | 2302374.3528 | 77223.6019 | 3153150.3453 | 3516071.8217 | 0 | 210043.5614 | 0 | 3610956.8365 | 9394968.9793 | 6412259.3757 | 28677048.8747 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35642747.1801 | 46409128.0365 | 3162277.6602 | 3.5053 | 10168.3041 | 13239.7799 | 207.2946 | 269.9108
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.6313 | 15.8356 | 0.88265 | 4 | 10128.3906 | 13177.8394 | 206.4809 | 268.6481 | 93.1914 | 0 | 101.6633 | 2310745.5796 | 77497.7874 | 3166384.0871 | 3534630.4307 | 0 | 207232.3009 | 0 | 3625631.1724 | 9433148.5915 | 6438317.7455 | 28793587.6951 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35759286.0005 | 46525666.8569 | 4216965.0343 | 3.5306 | 10128.3906 | 13177.8394 | 206.4809 | 268.6481
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.077 | 15.8965 | 0.88738 | 4 | 10098.4352 | 13131.6194 | 205.8703 | 267.7058 | 93.1857 | 0 | 102.4644 | 2316906.7921 | 77699.5239 | 3176131.3124 | 3548315.3075 | 0 | 205017.1897 | 0 | 3636387.349 | 9461133.9564 | 6457418.3321 | 28879009.7631 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35844708.0685 | 46611088.9249 | 5623413.2519 | 3.5495 | 10098.4352 | 13131.6194 | 205.8703 | 267.7058
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.413 | 15.9424 | 0.89096 | 4 | 10075.9578 | 13096.9729 | 205.412 | 266.9995 | 93.1813 | 0 | 93.3919 | 2321544.825 | 77851.3513 | 3183472.8517 | 3558631.4134 | 0 | 203323.7021 | 0 | 3644481.416 | 9482193.0584 | 6471791.602 | 28943290.2199 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35908988.5253 | 46675369.3816 | 7498942.0933 | 3.5638 | 10075.9578 | 13096.9729 | 205.412 | 266.9995
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.6714 | 15.9776 | 0.89368 | 4 | 10059.094 | 13070.8995 | 205.0682 | 266.468 | 93.1779 | 0 | 92.6349 | 2325107.1126 | 77967.9432 | 3189113.9393 | 3566563.1981 | 0 | 202060.7892 | 0 | 3650717.0631 | 9498416.9331 | 6482864.7298 | 28992811.7083 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35958510.0137 | 46724890.8701 | 10000000 | 3.5747 | 10059.094 | 13070.8995 | 205.0682 | 266.468
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0131 | [19 empty] | 100 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4791 | [19 empty] | 133.3521 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.937 | [19 empty] | 177.8279 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6743 | [19 empty] | 237.1374 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6409 | [19 empty] | 316.2278 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.3027 | [19 empty] | 421.6965 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.76734 | 0.077021 | 0.00042194 | 4 | 4642290.0219 | 11289558.2645 | 94639.3613 | 230152.9155 | 77.2987 | 0 | 74.8996 | 49024.2606 | 1446.1399 | 45257.0701 | 44900.6106 | 0 | 35682.2115 | 0 | 68761.0141 | 178902.0539 | 122104.3279 | 546077.6885 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7835102.3214 | 19054140.0364 | 562.3413 | 0.0016878 | 4642290.0219 | 11289558.2645 | 94639.3613 | 230152.9155
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.12565 | 0.0016336 | 4 | 1229787.4382 | 2946744.4372 | 25070.8803 | 60073.3711 | 82.7375 | 0 | 184.1307 | 72401.1008 | 2231.9433 | 66650.0535 | 55557.5712 | 0 | 44251.03 | 0 | 94025.7626 | 244635.7469 | 166968.924 | 746722.1324 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8035746.7653 | 19254784.4803 | 749.8942 | 0.0065343 | 1229787.4382 | 2946744.4372 | 25070.8803 | 60073.3711
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5542 | 0.19172 | 0.0035292 | 4 | 586636.0324 | 1381355.0083 | 11959.369 | 28160.7903 | 86.6337 | 0 | 266.3007 | 100362.1148 | 3193.4203 | 93163.4221 | 69864.5419 | 0 | 53864.5278 | 0 | 124974.7305 | 325158.6129 | 221927.4346 | 992508.8049 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8281533.4378 | 19500571.1528 | 1000 | 0.014117 | 586636.0324 | 1381355.0083 | 11959.369 | 28160.7903
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.27632 | 0.0062568 | 4 | 342362.7783 | 790640.0353 | 6979.5283 | 16118.2665 | 89.37 | 0 | 376.5103 | 132243.3908 | 4302.6988 | 124532.3561 | 87998.0015 | 0 | 63963.9185 | 0 | 161085.7426 | 419112.059 | 286052.5921 | 1279290.7593 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8568315.3922 | 19787353.1072 | 1333.5214 | 0.025027 | 342362.7783 | 790640.0353 | 6979.5283 | 16118.2665
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8324 | 0.38432 | 0.010032 | 4 | 221944.8809 | 501523.7237 | 4524.6466 | 10224.2395 | 91.3556 | 0 | 88.9097 | 168891.7576 | 5584.9885 | 161894.3464 | 111002.8151 | 0 | 74784.5852 | 0 | 203641.8122 | 529834.2227 | 361622.744 | 1617257.2717 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8906281.9046 | 20125319.6196 | 1778.2794 | 0.040128 | 221944.8809 | 501523.7237 | 4524.6466 | 10224.2395
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7144 | 0.51826 | 0.015167 | 4 | 153218.8461 | 338142.419 | 3123.5734 | 6893.4906 | 92.7969 | 0 | 65.1632 | 210201.893 | 7033.9453 | 205414.2287 | 139441.5214 | 0 | 85751.5614 | 0 | 252658.8284 | 657366.4441 | 448666.1056 | 2006534.5279 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9295559.1608 | 20514596.8758 | 2371.3737 | 0.060669 | 153218.8461 | 338142.419 | 3123.5734 | 6893.4906
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8929 | 0.69797 | 0.022017 | 4 | 111155.0832 | 238543.1295 | 2266.0467 | 4863.0243 | 93.9353 | 0 | 70.7173 | 260818.3988 | 8811.1019 | 260416.9753 | 177729.1778 | 0 | 99513.5946 | 0 | 314842.8069 | 819156.4004 | 559091.0753 | 2500379.531 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9789404.164 | 21008441.8789 | 3162.2777 | 0.08807 | 111155.0832 | 238543.1295 | 2266.0467 | 4863.0243
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3233 | 0.916 | 0.030988 | 4 | 83508.1449 | 174020.072 | 1702.4265 | 3547.6345 | 94.7466 | 0 | 68.9898 | 317098.131 | 10785.1454 | 323475.0407 | 224056.6071 | 0 | 113166.6229 | 0 | 385546.8033 | 1003113.6957 | 684645.7092 | 3061887.7552 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10350912.3882 | 21569950.1031 | 4216.965 | 0.12395 | 83508.1449 | 174020.072 | 1702.4265 | 3547.6345
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0601 | 1.1794 | 0.042573 | 4 | 64539.5462 | 130420.6161 | 1315.7259 | 2658.8007 | 95.2851 | 0 | 112.564 | 379702.5281 | 12973.0722 | 395802.9549 | 280101.507 | 0 | 126530.9764 | 0 | 466093.3051 | 1212679.171 | 827678.4523 | 3701561.9671 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10990586.6 | 22209624.315 | 5623.4133 | 0.17029 | 64539.5462 | 130420.6161 | 1315.7259 | 2658.8007
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6398 | 1.5756 | 0.058908 | 4 | 50569.5945 | 98182.0704 | 1030.9296 | 2001.5743 | 95.9298 | 0 | 116.7374 | 466984.4954 | 16035.6771 | 498761.3819 | 363730.345 | 0 | 148329.5393 | 0 | 582598.1611 | 1515800.9079 | 1034565.2663 | 4626805.7741 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 11915830.4071 | 23134868.122 | 7498.9421 | 0.23563 | 50569.5945 | 98182.0704 | 1030.9296 | 2001.5743
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6218 | 2.0315 | 0.079368 | 4 | 40692.0587 | 76030.8527 | 829.5627 | 1549.9918 | 96.3089 | 0 | 120.8215 | 559295.0452 | 19261.4226 | 611019.3042 | 460286.5245 | 0 | 167721.7296 | 0 | 708857.7702 | 1844302.5114 | 1258774.3606 | 5629518.6684 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 12918543.3014 | 24137581.0163 | 10000 | 0.31747 | 40692.0587 | 76030.8527 | 829.5627 | 1549.9918
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3413 | 2.6002 | 0.10577 | 4 | 33355.9934 | 59874.5604 | 680.007 | 1220.6239 | 96.6009 | 0 | 141.1706 | 666168.5284 | 22989.667 | 744246.5626 | 580751.7249 | 0 | 188659.1593 | 0 | 859098.1005 | 2235197.0321 | 1525567.9031 | 6822678.6779 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 14111703.3109 | 25330741.0258 | 13335.2143 | 0.42306 | 33355.9934 | 59874.5604 | 680.007 | 1220.6239
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.9117 | 3.2992 | 0.13942 | 4 | 27816.959 | 47934.1929 | 567.0863 | 977.2034 | 96.8254 | 0 | 114.4147 | 788390.0308 | 27245.6295 | 900248.2387 | 728788.5381 | 0 | 210589.0633 | 0 | 1035551.9851 | 2694293.8444 | 1838910.911 | 8224018.2409 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 15513042.8739 | 26732080.5888 | 17782.7941 | 0.55768 | 27816.959 | 47934.1929 | 567.0863 | 977.2034
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4681 | 4.1492 | 0.1818 | 4 | 23577.6993 | 39005.3968 | 480.6633 | 795.1778 | 96.999 | 0 | 124.86 | 927081.8196 | 32066.1791 | 1081288.1825 | 908772.3901 | 0 | 233192.3962 | 0 | 1241136.3773 | 3229182.2617 | 2203983.2467 | 9856702.8532 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 17145727.4861 | 28364765.2011 | 23713.7371 | 0.7272 | 23577.6993 | 39005.3968 | 480.6633 | 795.1778
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.1159 | 5.1659 | 0.23426 | 4 | 20299.2038 | 32271.8448 | 413.8267 | 657.9052 | 97.1337 | 0 | 162.5081 | 1082392.5699 | 37453.8101 | 1288391.8669 | 1123922.5949 | 0 | 255862.9615 | 0 | 1477329.2833 | 3843707.7532 | 2623409.5219 | 11732470.3618 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19021494.9947 | 30240532.7097 | 31622.7766 | 0.93706 | 20299.2038 | 32271.8448 | 413.8267 | 657.9052
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.8797 | 6.3535 | 0.29773 | 4 | 17743.6443 | 27164.2069 | 361.7282 | 553.7791 | 97.2372 | 0 | 166.0166 | 1252799.7288 | 43353.7792 | 1520211.1023 | 1375198.6268 | 0 | 277573.6055 | 0 | 1742963.3686 | 4534833.1542 | 3095116.8092 | 13842050.1747 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 21131074.8076 | 32350112.5225 | 42169.6503 | 1.1909 | 17743.6443 | 27164.2069 | 361.7282 | 553.7791
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6003 | 7.6868 | 0.37181 | 4 | 15745.3404 | 23288.9253 | 320.9901 | 474.7762 | 97.3118 | 0 | 164.53 | 1433294.4397 | 49589.9042 | 1770385.2555 | 1657393.6053 | 0 | 296498.7905 | 0 | 2030793.1781 | 5283707.2765 | 3606238.7855 | 16127901.2353 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 23416925.8683 | 34635963.5832 | 56234.1325 | 1.4872 | 15745.3404 | 23288.9253 | 320.9901 | 474.7762
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8381 | 9.0972 | 0.4539 | 4 | 14185.5802 | 20364.8824 | 289.1922 | 415.1657 | 97.3548 | 0 | 163.7597 | 1614354.6424 | 55829.8887 | 2025739.728 | 1956160.9592 | 0 | 309995.881 | 0 | 2325211.6287 | 6049723.6915 | 4129060.7288 | 18466077.1483 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 25755101.7812 | 36974139.4962 | 74989.4209 | 1.8156 | 14185.5802 | 20364.8824 | 289.1922 | 415.1657
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.105 | 10.508 | 0.53997 | 4 | 12974.8703 | 18169.1693 | 264.5103 | 370.4031 | 97.3647 | 0 | 168.617 | 1787145.3249 | 61766.6608 | 2273361.4978 | 2255532.2608 | 0 | 316859.7188 | 0 | 2610919.5306 | 6793077.0454 | 4636414.6673 | 20735076.7065 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 28024101.3394 | 39243139.0544 | 100000 | 2.1599 | 12974.8703 | 18169.1693 | 264.5103 | 370.4031
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.113 | 11.8734 | 0.62695 | 4 | 12027.6014 | 16501.2706 | 245.1989 | 336.4007 | 97.3446 | 0 | 144.1117 | 1947666.4963 | 67262.1894 | 2506798.2453 | 2546050.5661 | 0 | 317382.431 | 0 | 2880212.372 | 7493721.7791 | 5114619.0948 | 22873713.174 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 30162737.807 | 41381775.5219 | 133352.1432 | 2.5078 | 12027.6014 | 16501.2706 | 245.1989 | 336.4007
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9741 | 13.0588 | 0.70631 | 4 | 11317.2565 | 15288.2874 | 230.7176 | 311.6724 | 97.3043 | 0 | 139.6731 | 2082327.9308 | 71855.009 | 2705172.3957 | 2799072.9302 | 0 | 311445.4605 | 0 | 3108250.7532 | 8087030.87 | 5519564.7406 | 24684720.09 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 31973744.7229 | 43192782.4379 | 177827.941 | 2.8252 | 11317.2565 | 15288.2874 | 230.7176 | 311.6724
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7339 | 14.0727 | 0.77697 | 4 | 10776.1624 | 14386.0106 | 219.6866 | 293.2783 | 97.2539 | 0 | 168.8684 | 2194382.8109 | 75663.0067 | 2872042.1493 | 3016201.2494 | 0 | 301522.2935 | 0 | 3299326.4888 | 8584170.739 | 5858872.9165 | 26202181.6542 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 33491206.2871 | 44710244.0021 | 237137.3706 | 3.1079 | 10776.1624 | 14386.0106 | 219.6866 | 293.2783
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.3512 | 14.911 | 0.83748 | 4 | 10365.613 | 13714.6686 | 211.317 | 279.5921 | 97.2015 | 0 | 160.5385 | 2285017.4349 | 78732.9487 | 3008231.7173 | 3196284.0967 | 0 | 289534.4715 | 0 | 3454542.2609 | 8988010.3389 | 6134501.7415 | 27434855.0104 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 34723879.6434 | 45942917.3583 | 316227.766 | 3.3499 | 10365.613 | 13714.6686 | 211.317 | 279.5921
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.9138 | 15.5888 | 0.88777 | 4 | 10055.0064 | 13214.3404 | 204.9849 | 269.3922 | 97.1522 | 0 | 178.8626 | 2357045.7086 | 81165.6968 | 3117255.4541 | 3342298.3152 | 0 | 277162.0912 | 0 | 3578221.6337 | 9309798.6967 | 6354128.9078 | 28417076.5042 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 35706101.1371 | 46925138.8521 | 421696.5034 | 3.5511 | 10055.0064 | 13214.3404 | 204.9849 | 269.3922
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5413 | 16.1256 | 0.92853 | 4 | 9820.5012 | 12841.1537 | 200.2042 | 261.7843 | 97.109 | 0 | 161.658 | 2413330.4003 | 83062.1548 | 3202946.739 | 3458217.4331 | 0 | 265437.633 | 0 | 3674967.8005 | 9561512.3773 | 6525928.667 | 29185403.205 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 36474427.838 | 47693465.5529 | 562341.3252 | 3.7141 | 9820.5012 | 12841.1537 | 200.2042 | 261.7843
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.3593 | 16.5413 | 0.9608 | 4 | 9643.7214 | 12562.9186 | 196.6003 | 256.1121 | 97.073 | 0 | 172.4235 | 2456469.1884 | 84512.8468 | 3268924.0152 | 3548160.0595 | 0 | 254855.6022 | 0 | 3749039.4677 | 9754231.6612 | 6657463.5382 | 29773656.3792 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 37062681.0122 | 48281718.7271 | 749894.2093 | 3.8432 | 9643.7214 | 12562.9186 | 196.6003 | 256.1121
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.5519 | 16.864 | 0.98615 | 4 | 9510.6101 | 12354.7529 | 193.8867 | 251.8683 | 97.0435 | 0 | 164.4323 | 2489686.6295 | 85628.1695 | 3319907.1816 | 3618074.4643 | 0 | 245877.0767 | 0 | 3806077.6734 | 9902633.3723 | 6758750.7553 | 30226635.3225 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 37515659.9554 | 48734697.6704 | 1000000 | 3.9446 | 9510.6101 | 12354.7529 | 193.8867 | 251.8683
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2233 | 17.1094 | 1.0057 | 4 | 9410.4686 | 12199.2504 | 191.8451 | 248.6982 | 97.0202 | 0 | 182.6904 | 2514806.0786 | 86470.5645 | 3358566.3152 | 3671328.4719 | 0 | 238381.924 | 0 | 3849125.8081 | 10014635.7884 | 6835194.7057 | 30568509.6562 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 37857534.2892 | 49076572.0041 | 1333521.4322 | 4.0229 | 9410.4686 | 12199.2504 | 191.8451 | 248.6982
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.4802 | 17.2937 | 1.0207 | 4 | 9335.1844 | 12083.1673 | 190.3104 | 246.3317 | 97.0023 | 0 | 177.8599 | 2533582.4057 | 87099.6518 | 3387522.8181 | 3711352.3905 | 0 | 232232.2777 | 0 | 3881197.922 | 10098080.8499 | 6892147.6749 | 30823215.9905 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38112240.6234 | 49331278.3384 | 1778279.41 | 4.0826 | 9335.1844 | 12083.1673 | 190.3104 | 246.3317
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.4398 | 17.4342 | 1.0321 | 4 | 9278.6185 | 11996.1683 | 189.1572 | 244.5581 | 96.9883 | 0 | 182.7417 | 2547843.2384 | 87577.0181 | 3409554.8266 | 3741838.4256 | 0 | 227380.7931 | 0 | 3905535.7777 | 10161402.9581 | 6935366.3149 | 31016499.3526 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38305523.9856 | 49524561.7005 | 2371373.7057 | 4.1284 | 9278.6185 | 11996.1683 | 189.1572 | 244.5581
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1781 | 17.5421 | 1.0409 | 4 | 9236.1346 | 11930.8036 | 188.2911 | 243.2256 | 96.9774 | 0 | 179.0674 | 2558774.9506 | 87942.7281 | 3426464.5664 | 3765274.3936 | 0 | 223644.1202 | 0 | 3924219.296 | 10210013.6401 | 6968544.1042 | 31164877.7993 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38453902.4322 | 49672940.1472 | 3162277.6602 | 4.1634 | 9236.1346 | 11930.8036 | 188.2911 | 243.2256
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7265 | 17.6223 | 1.0474 | 4 | 9204.238 | 11881.9724 | 187.6408 | 242.2301 | 96.9692 | 0 | 160.3738 | 2566873.9635 | 88213.5573 | 3439003.9531 | 3782678.2102 | 0 | 220702.5247 | 0 | 3938014.1614 | 10245905.0503 | 6993040.7291 | 31274432.1497 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38563456.7826 | 49782494.4976 | 4216965.0343 | 4.1898 | 9204.238 | 11881.9724 | 187.6408 | 242.2301
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.1324 | 17.6816 | 1.0524 | 4 | 9180.2971 | 11845.4944 | 187.1528 | 241.4864 | 96.9631 | 0 | 200.1236 | 2572856.419 | 88413.5455 | 3448272.6197 | 3795556.1382 | 0 | 218404.1319 | 0 | 3948166.1131 | 10272318.3461 | 7011068.3463 | 31355055.6597 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38644080.2926 | 49863118.0076 | 5623413.2519 | 4.2095 | 9180.2971 | 11845.4944 | 187.1528 | 241.4864
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.4419 | 17.7268 | 1.0561 | 4 | 9162.3313 | 11818.0878 | 186.7865 | 240.9277 | 96.9584 | 0 | 199.7831 | 2577411.2105 | 88565.772 | 3455332.9532 | 3805373.5646 | 0 | 216668.7836 | 0 | 3955907.3907 | 10292459.5623 | 7024815.1402 | 31416534.3769 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38705559.0099 | 49924596.7248 | 7498942.0933 | 4.2244 | 9162.3313 | 11818.0878 | 186.7865 | 240.9277
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.6855 | 17.7623 | 1.059 | 4 | 9148.8516 | 11797.3709 | 186.5117 | 240.5054 | 96.9547 | 0 | 201.9913 | 2580991.6789 | 88685.4138 | 3460885.1427 | 3813098.6078 | 0 | 215403.801 | 0 | 3962035.2112 | 10308402.8944 | 7035696.792 | 31465199.5418 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38754224.1747 | 49973261.8897 | 10000000 | 4.236 | 9148.8516 | 11797.3709 | 186.5117 | 240.5054
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0727 | [19 empty] | 100 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5809 | [19 empty] | 133.3521 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9 | [19 empty] | 177.8279 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.953 | [19 empty] | 237.1374 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.205 | [19 empty] | 316.2278 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1553 | [19 empty] | 421.6965 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.10365 | 0.0010403 | 4 | 1990248.1749 | 4797196.8248 | 40573.9011 | 97797.346 | 82.4708 | 0 | 57.7978 | 63274.3038 | 1942.2284 | 57149.1191 | 50144.9526 | 0 | 41660.7634 | 0 | 83526.8332 | 217319.6864 | 148325.1514 | 663343.0384 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8281554.0897 | 19961452.7905 | 562.3413 | 0.0041611 | 1990248.1749 | 4797196.8248 | 40573.9011 | 97797.346
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3402 | 0.16936 | 0.0027986 | 4 | 762717.5464 | 1806078.0418 | 15549.0288 | 36819.3438 | 87.8018 | 0 | 220.8951 | 93080.757 | 2981.4119 | 84283.2304 | 63959.0274 | 0 | 52742.6912 | 0 | 115848.376 | 301413.7106 | 205721.0509 | 920030.2554 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8538241.3068 | 20218140.0075 | 749.8942 | 0.011194 | 762717.5464 | 1806078.0418 | 15549.0288 | 36819.3438
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.24999 | 0.0054216 | 4 | 406740.3537 | 945327.0004 | 8291.9523 | 19271.7696 | 91.2591 | 0 | 317.4141 | 125345.528 | 4127.155 | 114774.5663 | 80678.5506 | 0 | 63302.7697 | 0 | 151409.1421 | 393935.5295 | 268869.0934 | 1202442.3345 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8820653.3858 | 20500552.0865 | 1000 | 0.021686 | 406740.3537 | 945327.0004 | 8291.9523 | 19271.7696
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4682 | 0.35046 | 0.0091197 | 4 | 250639.6048 | 570823.8816 | 5109.6274 | 11637.0169 | 93.6953 | 0 | 399.9326 | 161443.0765 | 5420.5505 | 150102.7768 | 101400.6159 | 0 | 73936.8873 | 0 | 191998.5237 | 499540.7744 | 340946.843 | 1524790.048 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9143001.0994 | 20822899.8001 | 1333.5214 | 0.036479 | 250639.6048 | 570823.8816 | 5109.6274 | 11637.0169
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3077 | 0.48684 | 0.014209 | 4 | 168051.8481 | 373554.0419 | 3425.9642 | 7615.4044 | 95.5989 | 0 | 77.4349 | 205738.4021 | 7014.4139 | 194960.5621 | 129398.7796 | 0 | 87042.1488 | 0 | 243420.1796 | 633329.3748 | 432260.3119 | 1933164.1729 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9551375.2242 | 21231273.925 | 1778.2794 | 0.056836 | 168051.8481 | 373554.0419 | 3425.9642 | 7615.4044
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 0.65846 | 0.021058 | 4 | 119072.9942 | 257737.1009 | 2427.464 | 5254.3194 | 96.9872 | 0 | 100.7068 | 256368.4343 | 8838.4314 | 247972.0709 | 164493.2244 | 0 | 100919.8851 | 0 | 303650.898 | 790037.3492 | 539216.7244 | 2411497.0177 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10029708.069 | 21709606.7697 | 2371.3737 | 0.084232 | 119072.9942 | 257737.1009 | 2427.464 | 5254.3194
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6628 | 0.87108 | 0.030109 | 4 | 87883.5584 | 184863.7321 | 1791.6252 | 3768.6972 | 98.005 | 0 | 127.8725 | 313743.3178 | 10904.1328 | 309948.7426 | 207756.7553 | 0 | 115311.0324 | 0 | 373488.9525 | 971741.6413 | 663233.6375 | 2966128.2121 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10584339.2635 | 22264237.9642 | 3162.2777 | 0.12044 | 87883.5584 | 184863.7321 | 1791.6252 | 3768.6972
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2855 | 1.1356 | 0.041921 | 4 | 67007.5153 | 136662.4526 | 1366.0388 | 2786.0489 | 98.7352 | 0 | 87.6726 | 379400.3603 | 13263.8493 | 382987.9009 | 261815.242 | 0 | 130587.4348 | 0 | 455541.367 | 1185225.1926 | 808940.5479 | 3617761.8949 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 11235972.9462 | 22915871.647 | 4216.965 | 0.16768 | 67007.5153 | 136662.4526 | 1366.0388 | 2786.0489
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5487 | 1.5071 | 0.0581 | 4 | 52104.4181 | 102362.0063 | 1062.219 | 2086.788 | 99.434 | 0 | 108.5757 | 464520.1015 | 16327.3058 | 480047.7871 | 337333.2277 | 0 | 151731.0514 | 0 | 565484.1947 | 1471273.8778 | 1004174.6532 | 4490892.1992 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 12109103.2505 | 23789001.9512 | 5623.4133 | 0.2324 | 52104.4181 | 102362.0063 | 1062.219 | 2086.788
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2166 | 1.944 | 0.07869 | 4 | 41543.5261 | 78650.8897 | 846.921 | 1603.4048 | 99.8944 | 0 | 113.6861 | 556727.7855 | 19635.5489 | 588266.0333 | 426201.109 | 0 | 171379.8846 | 0 | 687262.0409 | 1788114.8536 | 1220425.1297 | 5458012.3856 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 13076223.4369 | 24756122.1376 | 7498.9421 | 0.31476 | 41543.5261 | 78650.8897 | 846.921 | 1603.4048
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5922 | 2.497 | 0.10544 | 4 | 33771.092 | 61463.693 | 688.4694 | 1253.0205 | 100.2531 | 0 | 125.6702 | 664974.1098 | 23512.786 | 718512.2335 | 538769.6323 | 0 | 193355.6204 | 0 | 834258.509 | 2170569.5105 | 1481458.2917 | 6625410.6932 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 14243621.7446 | 25923520.4453 | 10000 | 0.42177 | 33771.092 | 61463.693 | 688.4694 | 1253.0205
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.7682 | 3.1812 | 0.13975 | 4 | 27945.4089 | 48839.142 | 569.705 | 995.652 | 100.5292 | 0 | 113.7462 | 789462.9741 | 27963.5321 | 871943.4927 | 678080.6393 | 0 | 216669.7956 | 0 | 1007806.9692 | 2622107.0042 | 1789641.9093 | 8003676.3165 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 15621887.3679 | 27301786.0686 | 13335.2143 | 0.55901 | 27945.4089 | 48839.142 | 569.705 | 995.652
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8929 | 4.0211 | 0.18331 | 4 | 23512.3649 | 39441.5506 | 479.3314 | 804.0694 | 100.7429 | 0 | 141.6677 | 931857.9763 | 33044.4481 | 1051518.6401 | 849054.9359 | 0 | 241137.4542 | 0 | 1211579.2473 | 3152280.6723 | 2151496.3317 | 9621969.7058 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 17240180.7571 | 28920079.4579 | 17782.7941 | 0.73324 | 23512.3649 | 39441.5506 | 479.3314 | 804.0694
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.0808 | 5.0353 | 0.23777 | 4 | 20096.7848 | 32377.3276 | 409.7001 | 660.0556 | 100.9083 | 0 | 128.3025 | 1092575.2369 | 38767.696 | 1258668.0554 | 1055515.2521 | 0 | 266031.4812 | 0 | 1447507.5114 | 3766117.6201 | 2570452.6617 | 11495635.5148 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19113846.5662 | 30793745.2669 | 23713.7371 | 0.95109 | 20096.7848 | 32377.3276 | 409.7001 | 660.0556
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4427 | 6.2421 | 0.30471 | 4 | 17440.2109 | 27022.9646 | 355.5423 | 550.8997 | 101.0369 | 0 | 131.841 | 1271848.642 | 45138.6691 | 1494558.3192 | 1301117.6303 | 0 | 290823.8186 | 0 | 1717359.9609 | 4468218.3392 | 3049650.8292 | 13638716.2085 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21256927.2599 | 32936825.9606 | 31622.7766 | 1.2188 | 17440.2109 | 27022.9646 | 355.5423 | 550.8997
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.8903 | 7.6266 | 0.38446 | 4 | 15362.1528 | 22957.1558 | 313.1783 | 468.0127 | 101.133 | 0 | 164.5589 | 1465378.5223 | 52001.2616 | 1754211.0021 | 1582828.0734 | 0 | 313488.8626 | 0 | 2015484.0116 | 5243875.9655 | 3579053.0973 | 16006320.7963 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 23624531.8476 | 35304430.5483 | 42169.6503 | 1.5378 | 15362.1528 | 22957.1558 | 313.1783 | 468.0127
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.1593 | 9.1442 | 0.47561 | 4 | 13735.0322 | 19874.4991 | 280.0072 | 405.1685 | 101.1957 | 0 | 140.7958 | 1665931.4427 | 59095.3177 | 2028213.4666 | 1891801.5212 | 0 | 331772.7164 | 0 | 2330957.6412 | 6064673.6372 | 4139264.374 | 18511710.1169 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 26129921.1682 | 37809819.8689 | 56234.1325 | 1.9024 | 13735.0322 | 19874.4991 | 280.0072 | 405.1685
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.765 | 10.7131 | 0.5743 | 4 | 12465.9546 | 17550.3865 | 254.1353 | 357.7884 | 101.2214 | 0 | 176.8464 | 1863015.923 | 66045.244 | 2302076.6906 | 2211670.6535 | 0 | 343344.6424 | 0 | 2646599.7298 | 6885909.6048 | 4699774.7966 | 21018437.2846 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 28636648.336 | 40316547.0367 | 74989.4209 | 2.2972 | 12465.9546 | 17550.3865 | 254.1353 | 357.7884
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.1239 | 12.2354 | 0.67488 | 4 | 11482.5841 | 15809.2368 | 234.088 | 322.2927 | 101.2109 | 0 | 181.6859 | 2045952.5537 | 72472.3533 | 2560272.4347 | 2522794.6076 | 0 | 346901.7853 | 0 | 2943873.5565 | 7659355.1225 | 5227667.2551 | 23379289.6688 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 30997500.7201 | 42677399.4208 | 100000 | 2.6995 | 11482.5841 | 15809.2368 | 234.088 | 322.2927
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.6574 | 13.6162 | 0.77188 | 4 | 10713.0882 | 14496.0238 | 218.4008 | 295.5211 | 101.1726 | 0 | 172.0112 | 2205766.1309 | 78064.2038 | 2788987.3312 | 2805854.7814 | 0 | 341090.2867 | 0 | 3205707.4662 | 8340593.2462 | 5692626.2726 | 25458689.7189 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 33076900.7703 | 44756799.471 | 133352.1432 | 3.0875 | 10713.0882 | 14496.0238 | 218.4008 | 295.5211
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.7157 | 14.9122 | 0.86311 | 4 | 10137.9587 | 13521.0303 | 206.676 | 275.6445 | 101.113 | 0 | 163.9375 | 2351075.7297 | 83126.9578 | 2999541.237 | 3072491.8035 | 0 | 334701.2879 | 0 | 3447965.4362 | 8970898.7901 | 6122822.7578 | 27382624.0001 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 35000835.0515 | 46680733.7522 | 177827.941 | 3.4525 | 10137.9587 | 13521.0303 | 206.676 | 275.6445
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.2003 | 15.9488 | 0.94072 | 4 | 9700.241 | 12804.2044 | 197.7525 | 261.031 | 101.0495 | 0 | 157.0607 | 2464307.7599 | 87056.025 | 3165368.0205 | 3286519.3874 | 0 | 322045.7778 | 0 | 3636865.8185 | 9462378.836 | 6458267.988 | 28882809.6132 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 36501020.6645 | 48180919.3652 | 237137.3706 | 3.7629 | 9700.241 | 12804.2044 | 197.7525 | 261.031
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.5056 | 16.7922 | 1.0061 | 4 | 9368.2287 | 12270.5848 | 190.984 | 250.1525 | 100.9879 | 0 | 172.1877 | 2554612.3789 | 90178.3622 | 3298750.6782 | 3461199.9636 | 0 | 307792.5439 | 0 | 3787888.2314 | 9855308.1755 | 6726450.3361 | 30082180.6698 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 37700391.7212 | 49380290.4219 | 316227.766 | 4.0243 | 9368.2287 | 12270.5848 | 190.984 | 250.1525
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7982 | 17.4714 | 1.0599 | 4 | 9117.0703 | 11872.022 | 185.8638 | 242.0272 | 100.932 | 0 | 161.5314 | 2626180.0251 | 92644.9205 | 3405207.6418 | 3602121.2718 | 0 | 293864.144 | 0 | 3907807.0212 | 10167312.2678 | 6939399.5401 | 31034536.8322 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 38652747.8836 | 50332646.5843 | 421696.5034 | 4.2396 | 9117.0703 | 11872.022 | 185.8638 | 242.0272
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.1692 | 18.0027 | 1.103 | 4 | 8927.4247 | 11574.7025 | 181.9976 | 235.966 | 100.8844 | 0 | 173.4831 | 2681480.1212 | 94545.9913 | 3487918.6426 | 3712589.2962 | 0 | 280925.8357 | 0 | 4000409.3559 | 10408244.5473 | 7103840.7716 | 31769954.5619 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 39388165.6132 | 51068064.3139 | 562341.3252 | 4.412 | 8927.4247 | 11574.7025 | 181.9976 | 235.966
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.8003 | 18.416 | 1.1371 | 4 | 8784.4373 | 11352.3808 | 179.0826 | 231.4336 | 100.8451 | 0 | 193.1667 | 2724099.6883 | 96008.1457 | 3551937.1763 | 3798679.9966 | 0 | 269640.354 | 0 | 4071742.4908 | 10593838.7317 | 7230512.616 | 32336459.1994 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 39954670.2507 | 51634568.9514 | 749894.2093 | 4.5483 | 8784.4373 | 11352.3808 | 179.0826 | 231.4336
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.8102 | 18.7309 | 1.1635 | 4 | 8676.7515 | 11186.3636 | 176.8873 | 228.0492 | 100.8139 | 0 | 167.4811 | 2756345.0436 | 97112.6029 | 3600533.1681 | 3864373.6192 | 0 | 260025.705 | 0 | 4125572.1541 | 10733892.4739 | 7326102.1728 | 32763956.9397 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 40382167.991 | 52062066.6917 | 1000000 | 4.6541 | 8676.7515 | 11186.3636 | 176.8873 | 228.0492
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3519 | 18.972 | 1.1839 | 4 | 8595.7249 | 11062.0456 | 175.2355 | 225.5148 | 100.7891 | 0 | 175.0456 | 2780894.745 | 97952.4142 | 3637624.9784 | 3914714.7001 | 0 | 252169.5705 | 0 | 4166508.9992 | 10840401.7474 | 7398796.9406 | 33089064.0955 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 40707275.1468 | 52387173.8476 | 1333521.4322 | 4.7358 | 8595.7249 | 11062.0456 | 175.2355 | 225.5148
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.524 | 19.155 | 1.1996 | 4 | 8534.8017 | 10968.9694 | 173.9935 | 223.6173 | 100.7699 | 0 | 204.6688 | 2799453.6525 | 98586.6709 | 3665719.6317 | 3952959.6788 | 0 | 245860.3272 | 0 | 4197406.1848 | 10920789.8865 | 7453663.4973 | 33334439.5296 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 40952650.581 | 52632549.2817 | 1778279.41 | 4.7983 | 8534.8017 | 10968.9694 | 173.9935 | 223.6173
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4176 | 19.2943 | 1.2115 | 4 | 8489.0205 | 10899.1712 | 173.0602 | 222.1943 | 100.7551 | 0 | 185.5463 | 2813544.3293 | 99067.8645 | 3687081.6303 | 3982105.8459 | 0 | 240907.9032 | 0 | 4220855.9536 | 10981801.3745 | 7495305.0916 | 33520669.9929 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41138881.0442 | 52818779.745 | 2371373.7057 | 4.8461 | 8489.0205 | 10899.1712 | 173.0602 | 222.1943
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.0755 | 19.3968 | 1.2205 | 4 | 8454.6339 | 10847.1187 | 172.3591 | 221.1332 | 100.744 | 0 | 193.0412 | 2823883.6905 | 99420.7507 | 3702773.8784 | 4003552.8041 | 0 | 236951.1983 | 0 | 4237967.1056 | 11026321.0821 | 7525690.7068 | 33656561.2164 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41274772.2677 | 52954670.9685 | 3162277.6602 | 4.8819 | 8454.6339 | 10847.1187 | 172.3591 | 221.1332
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.5702 | 19.4739 | 1.2272 | 4 | 8428.8153 | 10808.1266 | 171.8328 | 220.3383 | 100.7356 | 0 | 185.9913 | 2831640.0947 | 99685.3676 | 3714555.6006 | 4019675.4958 | 0 | 233888.4602 | 0 | 4250783.5573 | 11059666.8606 | 7548449.8858 | 33758345.3225 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41376556.3739 | 53056455.0746 | 4216965.0343 | 4.9089 | 8428.8153 | 10808.1266 | 171.8328 | 220.3383
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9575 | 19.5341 | 1.2324 | 4 | 8409.4354 | 10778.6952 | 171.4377 | 219.7383 | 100.729 | 0 | 200.8038 | 2837701.1696 | 99892.0805 | 3723767.9201 | 4032294.2007 | 0 | 231619.2081 | 0 | 4260857.0858 | 11085876.1152 | 7566338.2406 | 33838346.0204 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41456557.0718 | 53136455.7725 | 5623413.2519 | 4.9298 | 8409.4354 | 10778.6952 | 171.4377 | 219.7383
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2398 | 19.578 | 1.2363 | 4 | 8394.892 | 10756.7569 | 171.1412 | 219.291 | 100.7241 | 0 | 195.2967 | 2842112.8192 | 100042.502 | 3730476.4797 | 4041490.0851 | 0 | 229839.7677 | 0 | 4268145.0449 | 11104837.89 | 7579280.0415 | 33896224.6301 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41514435.6814 | 53194334.3821 | 7498942.0933 | 4.9452 | 8394.892 | 10756.7569 | 171.1412 | 219.291
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.4593 | 19.6122 | 1.2393 | 4 | 8383.9798 | 10740.2093 | 170.9188 | 218.9537 | 100.7203 | 0 | 172.6468 | 2845539.4765 | 100159.3175 | 3735689.0572 | 4048639.2094 | 0 | 228527.371 | 0 | 4273836.2283 | 11119645.1818 | 7589386.3224 | 33941422.1641 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41559633.2155 | 53239531.9162 | 10000000 | 4.957 | 8383.9798 | 10740.2093 | 170.9188 | 218.9537
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7093 | [19 empty] | 100 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.364 | [19 empty] | 133.3521 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8592 | [19 empty] | 177.8279 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7286 | [19 empty] | 237.1374 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.1225 | [19 empty] | 316.2278 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75252 | 0.08244 | 0.00043727 | 4 | 4877693.1243 | 11823648.5387 | 99438.3719 | 241041.0681 | 81.0864 | 0 | 73.4664 | 53385.6687 | 1618.5178 | 47637.1733 | 45265.3137 | 0 | 38765.2411 | 0 | 72802.0467 | 189415.9918 | 129280.3065 | 578170.2596 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8531427.8202 | 20680391.6339 | 421.6965 | 0.0017491 | 4877693.1243 | 11823648.5387 | 99438.3719 | 241041.0681
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.14303 | 0.0019631 | 4 | 1118244.3327 | 2665392.0279 | 22796.9233 | 54337.6217 | 88.0459 | 0 | 198.9289 | 83033.2108 | 2658.8795 | 73614.9796 | 57661.8526 | 0 | 50282.7912 | 0 | 104228.1683 | 271180.3138 | 185086.1364 | 827746.332 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8781003.8927 | 20929967.7064 | 562.3413 | 0.0078525 | 1118244.3327 | 2665392.0279 | 22796.9233 | 54337.6217
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5736 | 0.21829 | 0.0044192 | 4 | 512292.2404 | 1199574.7493 | 10443.7702 | 24454.9538 | 92.4932 | 0 | 269.6464 | 115284.6716 | 3822.9714 | 102876.6258 | 72834.7185 | 0 | 61120.9161 | 0 | 138816.5623 | 361172.2199 | 246507.4614 | 1102436.1469 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9055693.7075 | 21204657.5213 | 749.8942 | 0.017677 | 512292.2404 | 1199574.7493 | 10443.7702 | 24454.9538
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 0.3183 | 0.0079436 | 4 | 295505.2555 | 677856.1263 | 6024.2743 | 13819.014 | 95.7365 | 0 | 346.5129 | 153437.8019 | 5219.8242 | 138757.9871 | 92834.1906 | 0 | 73464.3164 | 0 | 180848.5069 | 470530.7177 | 321146.8833 | 1436240.2281 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9389497.7887 | 21538461.6024 | 1000 | 0.031774 | 295505.2555 | 677856.1263 | 6024.2743 | 13819.014
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.44434 | 0.012852 | 4 | 190157.6572 | 426487.1159 | 3876.621 | 8694.5167 | 98.0525 | 0 | 80.4993 | 196642.8535 | 6811.5148 | 180884.5552 | 117728.7233 | 0 | 86246.2305 | 0 | 229442.4122 | 596962.0914 | 407438.8937 | 1822157.2748 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9775414.8354 | 21924378.6491 | 1333.5214 | 0.051407 | 190157.6572 | 426487.1159 | 3876.621 | 8694.5167
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 0.6078 | 0.01954 | 4 | 131031.9883 | 286468.3185 | 2671.2643 | 5840.0441 | 99.7928 | 0 | 104.1149 | 247457.8722 | 8689.3621 | 232093.3692 | 149937.5372 | 0 | 100622.6599 | 0 | 288132.3123 | 749661.1725 | 511659.1543 | 2288253.4399 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10241511.0005 | 22390474.8142 | 1778.2794 | 0.07816 | 131031.9883 | 286468.3185 | 2671.2643 | 5840.0441
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0056 | 0.81339 | 0.028489 | 4 | 94681.0578 | 201292.6657 | 1930.2014 | 4103.6233 | 101.0796 | 0 | 85.5634 | 305775.0502 | 10846.1422 | 292732.5338 | 190410.4257 | 0 | 115936.187 | 0 | 357123.1322 | 929161.1339 | 634171.5663 | 2836156.1713 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10789413.732 | 22938377.5457 | 2371.3737 | 0.11396 | 94681.0578 | 201292.6657 | 1930.2014 | 4103.6233
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4935 | 1.0729 | 0.04028 | 4 | 70999.4924 | 146401.9551 | 1447.4207 | 2984.6019 | 102.0342 | 0 | 98.3182 | 373229.0713 | 13336.7937 | 365065.6315 | 241363.4815 | 0 | 132612.7984 | 0 | 438987.0328 | 1142154.2107 | 779543.7177 | 3486292.7375 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11439550.2981 | 23588514.1118 | 3162.2777 | 0.16112 | 70999.4924 | 146401.9551 | 1447.4207 | 2984.6019
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2257 | 1.3734 | 0.055221 | 4 | 54994.2033 | 109996.0414 | 1121.1312 | 2242.4181 | 102.6361 | 0 | 84.6721 | 445222.3251 | 15985.3119 | 444598.176 | 300732.9152 | 0 | 147570.5618 | 0 | 528102.623 | 1374014.6964 | 937793.2635 | 4194019.8728 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 12147277.4334 | 24296241.2471 | 4216.965 | 0.22088 | 54994.2033 | 109996.0414 | 1121.1312 | 2242.4181
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8787 | 1.8407 | 0.07668 | 4 | 43062.7923 | 82672.1838 | 877.8933 | 1685.3843 | 103.4038 | 0 | 90.8686 | 549124.3198 | 19827.4259 | 561644.5276 | 392253.874 | 0 | 173791.9456 | 0 | 661690.4162 | 1721582.7316 | 1175015.5893 | 5254930.8301 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 13208188.3907 | 25357152.2044 | 5623.4133 | 0.30672 | 43062.7923 | 82672.1838 | 877.8933 | 1685.3843
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9191 | 2.3731 | 0.10339 | 4 | 34681.4087 | 64057.1411 | 707.0274 | 1305.8915 | 103.8455 | 0 | 107.3541 | 657855.3265 | 23826.8661 | 688000.9465 | 496780.2812 | 0 | 196649.0236 | 0 | 804613.8531 | 2093440.1969 | 1428815.9503 | 6389982.4442 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 14343240.0048 | 26492203.8185 | 7498.9421 | 0.41357 | 34681.4087 | 64057.1411 | 707.0274 | 1305.8915
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6922 | 3.0339 | 0.13779 | 4 | 28458.1391 | 50501.1016 | 580.1577 | 1029.5333 | 104.1849 | 0 | 115.5178 | 783134.7417 | 28426.0727 | 837193.9734 | 626464.1565 | 0 | 221001.0782 | 0 | 973525.8088 | 2532914.4569 | 1728766.163 | 7731426.4511 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 15684684.0118 | 27833647.8255 | 10000 | 0.55115 | 28458.1391 | 50501.1016 | 580.1577 | 1029.5333
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.3481 | 3.8493 | 0.18169 | 4 | 23756.1591 | 40472.3532 | 484.3014 | 825.0837 | 104.4474 | 0 | 91.1657 | 927043.0948 | 33698.4747 | 1012619.7182 | 786455.839 | 0 | 246781.5733 | 0 | 1172573.493 | 3050795.7009 | 2082230.7534 | 9312198.6473 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 17265456.2079 | 29414420.0216 | 13335.2143 | 0.72678 | 23756.1591 | 40472.3532 | 484.3014 | 825.0837
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0601 | 4.8499 | 0.23723 | 4 | 20152.4577 | 32955.5092 | 410.8351 | 671.8426 | 104.6519 | 0 | 131.5746 | 1091822.0205 | 39722.7868 | 1218028.3535 | 982755.9585 | 0 | 273976.4631 | 0 | 1406459.1771 | 3659318.2745 | 2497559.9138 | 11169642.9478 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 19122900.5085 | 31271864.3222 | 17782.7941 | 0.94891 | 20152.4577 | 32955.5092 | 410.8351 | 671.8426
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.9077 | 6.0495 | 0.30617 | 4 | 17358.9939 | 27279.2412 | 353.8866 | 556.1242 | 104.8104 | 0 | 120.2756 | 1276702.1574 | 46467.6276 | 1453444.0817 | 1218095.9114 | 0 | 301246.8332 | 0 | 1675423.0784 | 4359107.1734 | 2975180.2166 | 13305667.0796 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21258924.6403 | 33407888.454 | 23713.7371 | 1.2247 | 17358.9939 | 27279.2412 | 353.8866 | 556.1242
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.9586 | 7.46 | 0.38999 | 4 | 15176.0286 | 22963.9626 | 309.3839 | 468.1514 | 104.9321 | 0 | 134.5189 | 1480799.8499 | 53897.355 | 1718595.5333 | 1494795.0716 | 0 | 327677.2718 | 0 | 1979548.3818 | 5150378.8283 | 3515239.38 | 15720931.6717 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 23674189.2324 | 35823153.0461 | 31622.7766 | 1.56 | 15176.0286 | 22963.9626 | 309.3839 | 468.1514
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0501 | 9.0519 | 0.48835 | 4 | 13463.9217 | 19683.261 | 274.4803 | 401.2699 | 105.0184 | 0 | 151.7585 | 1697938.9158 | 61782.5495 | 2006073.0835 | 1807167.4022 | 0 | 350801.4348 | 0 | 2310267.7205 | 6010842.7076 | 4102523.6584 | 18347397.4723 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 26300655.0329 | 38449618.8466 | 42169.6503 | 1.9534 | 13463.9217 | 19683.261 | 274.4803 | 401.2699
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.7749 | 10.7515 | 0.5982 | 4 | 12123.1603 | 17200.4565 | 247.147 | 350.6546 | 105.0651 | 0 | 138.2356 | 1917564.4051 | 69733.9209 | 2302059.0525 | 2140999.692 | 0 | 367621.251 | 0 | 2651211.5453 | 6897908.6027 | 4707964.3592 | 21055062.8286 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 29008320.3893 | 41157284.203 | 56234.1325 | 2.3928 | 12123.1603 | 17200.4565 | 247.147 | 350.6546
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.6085 | 12.4639 | 0.71421 | 4 | 11078.8494 | 15331.4354 | 225.8573 | 312.552 | 105.0696 | 0 | 193.4605 | 2128419.3935 | 77339.1347 | 2590974.3272 | 2478056.6263 | 0 | 376265.7908 | 0 | 2983911.5563 | 7763525.785 | 5298765.8728 | 23697258.4866 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 31650516.0473 | 43799479.861 | 74989.4209 | 2.8568 | 11078.8494 | 15331.4354 | 225.8573 | 312.552
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.9823 | 14.0876 | 0.82963 | 4 | 10271.0601 | 13932.0329 | 209.3895 | 284.0233 | 105.0366 | 0 | 200.2057 | 2320166.8273 | 84224.8003 | 2857731.2398 | 2798651.6015 | 0 | 376160.674 | 0 | 3290404.7057 | 8560958.0894 | 5843029.8061 | 26131327.744 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 34084585.3046 | 46233549.1183 | 100000 | 3.3185 | 10271.0601 | 13932.0329 | 209.3895 | 284.0233
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.487 | 15.5516 | 0.93842 | 4 | 9650.3319 | 12886.8875 | 196.7351 | 262.7166 | 104.9773 | 0 | 199.8435 | 2487054.3008 | 90189.4817 | 3093074.3305 | 3088742.8248 | 0 | 368673.9955 | 0 | 3559816.624 | 9261912.6367 | 6321445.6878 | 28270909.8817 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 36224167.4423 | 48373131.2561 | 133352.1432 | 3.7537 | 9650.3319 | 12886.8875 | 196.7351 | 262.7166
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.1649 | 16.8645 | 1.0391 | 4 | 9167.5865 | 12090.5465 | 186.8937 | 246.4821 | 104.9015 | 0 | 189.2172 | 2632350.0785 | 95357.6195 | 3300441.283 | 3349834.9463 | 0 | 356709.1192 | 0 | 3796530.2882 | 9877793.0344 | 6741796.7143 | 30150813.0834 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 38104070.6441 | 50253034.4578 | 177827.941 | 4.1564 | 9167.5865 | 12090.5465 | 186.8937 | 246.4821
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.3593 | 17.9168 | 1.1232 | 4 | 8809.2499 | 11513.2459 | 179.5885 | 234.7131 | 104.8259 | 0 | 187.8464 | 2746071.3325 | 99384.8078 | 3464391.2151 | 3559889.6024 | 0 | 341376.5261 | 0 | 3982334.2587 | 10361216.8521 | 7071743.4033 | 31626407.998 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 39579665.5586 | 51728629.3723 | 237137.3706 | 4.493 | 8809.2499 | 11513.2459 | 179.5885 | 234.7131
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.3977 | 18.768 | 1.1934 | 4 | 8537.4964 | 11082.5959 | 174.0484 | 225.9337 | 104.7555 | 0 | 175.4625 | 2836368.6041 | 102570.3749 | 3595628.4254 | 3730331.2522 | 0 | 325209.6225 | 0 | 4130142.2289 | 10745782.8708 | 7334217.6131 | 32800250.9919 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 40753508.5526 | 52902472.3663 | 316227.766 | 4.7735 | 8537.4964 | 11082.5959 | 174.0484 | 225.9337
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.4191 | 19.444 | 1.2504 | 4 | 8331.906 | 10760.9112 | 169.8572 | 219.3757 | 104.6938 | 0 | 184.2135 | 2907064.9976 | 105056.4781 | 3699047.119 | 3866083.1871 | 0 | 309741.3541 | 0 | 4245927.323 | 11047031.935 | 7539826.2895 | 33719778.6835 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 41673036.2441 | 53822000.0578 | 421696.5034 | 5.0016 | 8331.906 | 10760.9112 | 169.8572 | 219.3757
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5667 | 19.9711 | 1.2958 | 4 | 8176.6575 | 10520.5696 | 166.6922 | 214.476 | 104.6423 | 0 | 157.6445 | 2961570.8776 | 106968.2075 | 3779191.2209 | 3972157.042 | 0 | 295763.2678 | 0 | 4335103.7402 | 11279050.6799 | 7698183.8503 | 34427988.8862 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 42381246.4468 | 54530210.2605 | 562341.3252 | 5.1832 | 8176.6575 | 10520.5696 | 166.6922 | 214.476
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3299 | 20.2655 | 1.3272 | 4 | 8051.4656 | 10339.864 | 164.14 | 210.7921 | 104.6121 | 0 | 186.8672 | 2991788.2969 | 108026.0726 | 3823779.5217 | 4031503.1388 | 0 | 277909.2599 | 0 | 4380872.4531 | 11398131.4824 | 7779458.9449 | 34791469.1702 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 42744726.7309 | 54893690.5446 | 749894.2093 | 5.3089 | 8051.4656 | 10339.864 | 164.14 | 210.7921
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8586 | 20.6867 | 1.3589 | 4 | 7971.4184 | 10206.5024 | 162.5081 | 208.0734 | 104.5674 | 0 | 182.564 | 3034744.1026 | 109527.4828 | 3887356.3698 | 4116529.3741 | 0 | 273566.354 | 0 | 4454472.2365 | 11589623.0214 | 7910155.8551 | 35375974.7963 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 43329232.3569 | 55478196.1706 | 1000000 | 5.4356 | 7971.4184 | 10206.5024 | 162.5081 | 208.0734
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2935 | 20.9251 | 1.3802 | 4 | 7905.0669 | 10105.6651 | 161.1555 | 206.0177 | 104.5413 | 0 | 174.9048 | 3058916.3301 | 110371.0476 | 3923234.689 | 4164725.6641 | 0 | 265438.7438 | 0 | 4493847.725 | 11692069.9657 | 7980077.9996 | 35688682.1648 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 43641939.7254 | 55790903.5391 | 1333521.4322 | 5.5208 | 7905.0669 | 10105.6651 | 161.1555 | 206.0177
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.3607 | 21.1022 | 1.3963 | 4 | 7855.1736 | 10030.4101 | 160.1383 | 204.4835 | 104.5215 | 0 | 175.2768 | 3076801.2275 | 110994.58 | 3949828.51 | 4200549.1955 | 0 | 258827.7647 | 0 | 4522830.4983 | 11767477.1965 | 8031544.9841 | 35918853.9567 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 43872111.5173 | 56021075.331 | 1778279.41 | 5.5851 | 7855.1736 | 10030.4101 | 160.1383 | 204.4835
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.1696 | 21.2362 | 1.4085 | 4 | 7817.6785 | 9974.0028 | 159.3739 | 203.3335 | 104.5062 | 0 | 187.9505 | 3090303.2205 | 111464.9578 | 3969932.1882 | 4227686.2649 | 0 | 253642.0096 | 0 | 4544681.17 | 11824328.162 | 8070346.9362 | 36092384.9093 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44045642.4699 | 56194606.2836 | 2371373.7057 | 5.6341 | 7817.6785 | 9974.0028 | 159.3739 | 203.3335
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.7903 | 21.339 | 1.4179 | 4 | 7789.5141 | 9931.6022 | 158.7998 | 202.4691 | 104.4944 | 0 | 209.1715 | 3100634.8822 | 111824.6836 | 3985331.157 | 4248505.359 | 0 | 249670.8735 | 0 | 4561427.1126 | 11867897.6696 | 8100084.0204 | 36225375.7578 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44178633.3185 | 56327597.1322 | 3162277.6602 | 5.6716 | 7789.5141 | 9931.6022 | 158.7998 | 202.4691
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.2554 | 21.416 | 1.4249 | 4 | 7768.3666 | 9899.8528 | 158.3687 | 201.8219 | 104.4855 | 0 | 215.4537 | 3108357.9782 | 112093.4674 | 3996851.1249 | 4264098.7195 | 0 | 246595.8065 | 0 | 4573918.8676 | 11900398.6538 | 8122266.61 | 36324581.2279 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44277838.7885 | 56426802.6023 | 4216965.0343 | 5.6998 | 7768.3666 | 9899.8528 | 158.3687 | 201.8219
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6038 | 21.4736 | 1.4302 | 4 | 7752.4925 | 9876.0711 | 158.045 | 201.3371 | 104.4788 | 0 | 221.8656 | 3114133.556 | 112294.4063 | 4005471.1569 | 4275777.1626 | 0 | 244233.0756 | 0 | 4583244.6494 | 11924662.425 | 8138827.1323 | 36398643.5641 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44351901.1247 | 56500864.9384 | 5623413.2519 | 5.721 | 7752.4925 | 9876.0711 | 158.045 | 201.3371
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8498 | 21.5142 | 1.4341 | 4 | 7740.5796 | 9858.4323 | 157.8022 | 200.9775 | 104.4741 | 0 | 186.9394 | 3118206.4576 | 112436.0718 | 4011552.5997 | 4284021.7439 | 0 | 242344.1695 | 0 | 4589738.8066 | 11941558.8898 | 8150359.3168 | 36450218.0556 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44403475.6163 | 56552439.43 | 7498942.0933 | 5.7365 | 7740.5796 | 9858.4323 | 157.8022 | 200.9775
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0472 | 21.5469 | 1.4371 | 4 | 7731.641 | 9845.0562 | 157.62 | 200.7048 | 104.4702 | 0 | 185.8033 | 3121472.4781 | 112549.6527 | 4016430.7533 | 4290638.1903 | 0 | 240982.6601 | 0 | 4595008.7564 | 11955270.2183 | 8159717.5802 | 36492070.2893 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44445327.8499 | 56594291.6636 | 10000000 | 5.7485 | 7731.641 | 9845.0562 | 157.62 | 200.7048
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4769 | [19 empty] | 100 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8231 | [19 empty] | 133.3521 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1802 | [19 empty] | 177.8279 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6135 | [19 empty] | 237.1374 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9725 | [19 empty] | 316.2278 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.11409 | 0.001095 | 4 | 2057585.2776 | 4940302.0111 | 41946.659 | 100714.7387 | 86.9765 | 0 | 55.0366 | 70424.5928 | 2232.5574 | 61488.0864 | 51216.657 | 0 | 46460.2848 | 0 | 90410.6496 | 235229.9644 | 160549.2842 | 718012.0766 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9012176.2373 | 21638409.2912 | 421.6965 | 0.00438 | 2057585.2776 | 4940302.0111 | 41946.659 | 100714.7387
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3208 | 0.1848 | 0.0032617 | 4 | 711676.5522 | 1679451.5499 | 14508.4891 | 34237.8915 | 92.9413 | 0 | 212.0799 | 103134.8364 | 3424.6635 | 90011.4478 | 65145.6488 | 0 | 58192.3373 | 0 | 124764.4842 | 324611.5951 | 221554.0837 | 990839.0967 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9285003.2574 | 21911236.3113 | 562.3413 | 0.013047 | 711676.5522 | 1679451.5499 | 14508.4891 | 34237.8915
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.27976 | 0.0065401 | 4 | 367567.8263 | 850217.42 | 7493.3673 | 17332.8321 | 97.1825 | 0 | 295.563 | 141853.3548 | 4867.8336 | 125008.4744 | 83606.3142 | 0 | 71332.7725 | 0 | 166400.8123 | 432940.7801 | 295490.9785 | 1321501.3203 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9615665.4811 | 22241898.535 | 749.8942 | 0.02616 | 367567.8263 | 850217.42 | 7493.3673 | 17332.8321
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.40091 | 0.011202 | 4 | 223178.2393 | 504975.8053 | 4549.7903 | 10294.6148 | 100.1712 | 0 | 441.5721 | 185906.9031 | 6527.6268 | 166329.8587 | 106781.0052 | 0 | 85126.0104 | 0 | 214761.8477 | 558766.274 | 381369.4635 | 1705568.9895 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9999733.1502 | 22625966.2041 | 1000 | 0.044806 | 223178.2393 | 504975.8053 | 4549.7903 | 10294.6148
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.55241 | 0.017612 | 4 | 148229.1959 | 327452.146 | 3021.8527 | 6675.5549 | 102.3132 | 0 | 84.7586 | 235663.6421 | 8412.2877 | 214605.5704 | 135673.3419 | 0 | 99344.579 | 0 | 270542.7743 | 703896.8027 | 480424.0315 | 2148563.0296 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10442727.1903 | 23068960.2442 | 1333.5214 | 0.07045 | 148229.1959 | 327452.146 | 3021.8527 | 6675.5549
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3944 | 0.75056 | 0.026308 | 4 | 104383.1248 | 224367.742 | 2127.9912 | 4574.0399 | 103.9502 | 0 | 85.3889 | 294858.59 | 10659.0746 | 273910.1535 | 173434.9515 | 0 | 115742.599 | 0 | 338756.0938 | 881373.8675 | 601555.775 | 2690291.1049 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10984455.2656 | 23610688.3195 | 1778.2794 | 0.10523 | 104383.1248 | 224367.742 | 2127.9912 | 4574.0399
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7218 | 0.9973 | 0.037835 | 4 | 76747.0891 | 160175.6228 | 1564.5932 | 3265.3967 | 105.1525 | 0 | 103.6048 | 362239.6907 | 13215.8045 | 343538.2507 | 220273.3626 | 0 | 132936.4572 | 0 | 418159.3906 | 1087964.9581 | 742558.4394 | 3320886.3539 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 11615050.5146 | 24241283.5685 | 2371.3737 | 0.15134 | 76747.0891 | 160175.6228 | 1564.5932 | 3265.3967
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3218 | 1.2942 | 0.052738 | 4 | 58435.1273 | 118288.4617 | 1191.2791 | 2411.4703 | 105.9905 | 0 | 117.6289 | 436764.4532 | 16035.4056 | 422909.2567 | 276608.6718 | 0 | 149769.3398 | 0 | 507813.9796 | 1321227.8078 | 901765.1274 | 4032894.0418 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 12327058.2025 | 24953291.2564 | 3162.2777 | 0.21095 | 58435.1273 | 118288.4617 | 1191.2791 | 2411.4703
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.607 | 1.7218 | 0.073341 | 4 | 45366.9308 | 88406.571 | 924.8662 | 1802.2875 | 106.8151 | 0 | 109.7472 | 535980.6336 | 19797.6984 | 531093.1683 | 357654.7081 | 0 | 174588.7334 | 0 | 631454.8273 | 1642915.9314 | 1121323.8818 | 5014809.5823 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 13308973.7431 | 25935206.797 | 4216.965 | 0.29336 | 45366.9308 | 88406.571 | 924.8662 | 1802.2875
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 2.2271 | 0.099592 | 4 | 36148.4466 | 67843.4555 | 736.935 | 1383.0806 | 107.3598 | 0 | 102.7697 | 643908.7456 | 23876.1075 | 652225.249 | 453535.4218 | 0 | 197933.2701 | 0 | 768876.7297 | 2000459.5323 | 1365354.7361 | 6106169.792 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 14400333.9528 | 27026567.0066 | 5623.4133 | 0.39837 | 36148.4466 | 67843.4555 | 736.935 | 1383.0806
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7165 | 2.8625 | 0.13364 | 4 | 29381.6438 | 53001.987 | 598.9845 | 1080.5172 | 107.7814 | 0 | 121.8243 | 769721.2555 | 28620.4431 | 797018.3124 | 574086.1925 | 0 | 223566.3872 | 0 | 933274.9104 | 2428189.8757 | 1657289.4845 | 7411766.8613 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 15705931.0221 | 28332164.0759 | 7498.9421 | 0.53455 | 29381.6438 | 53001.987 | 598.9845 | 1080.5172
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9313 | 3.6496 | 0.17732 | 4 | 24316.0764 | 42117.5694 | 495.7161 | 858.6236 | 108.1061 | 0 | 115.8911 | 914555.4055 | 34069.9674 | 967759.3513 | 723332.7434 | 0 | 250820.4354 | 0 | 1127309.7822 | 2933028.8102 | 2001852.4307 | 8952728.926 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 17246893.0868 | 29873126.1407 | 10000 | 0.70928 | 24316.0764 | 42117.5694 | 495.7161 | 858.6236
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1124 | 4.6171 | 0.23282 | 4 | 20461.9857 | 34019.7144 | 417.1453 | 693.5379 | 108.3576 | 0 | 107.7297 | 1080432.9801 | 40297.0128 | 1167848.0493 | 906621.7075 | 0 | 279479.5279 | 0 | 1355124.9183 | 3525757.063 | 2406401.6425 | 10761962.9014 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 19056127.0622 | 31682360.116 | 13335.2143 | 0.93129 | 20461.9857 | 34019.7144 | 417.1453 | 693.5379
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4124 | 5.7937 | 0.30252 | 4 | 17489.2311 | 27923.3228 | 356.5416 | 569.2547 | 108.5532 | 0 | 96.2132 | 1268919.7047 | 47357.0018 | 1400220.0278 | 1129512.4926 | 0 | 309107.8912 | 0 | 1620495.676 | 4216197.3397 | 2877641.3185 | 12869451.4523 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 21163615.6131 | 33789848.667 | 17782.7941 | 1.2101 | 17489.2311 | 27923.3228 | 356.5416 | 569.2547
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.9297 | 7.1979 | 0.38849 | 4 | 15172.7288 | 23297.9537 | 309.3166 | 474.9603 | 108.7049 | 0 | 111.4709 | 1479696.5543 | 55234.1082 | 1665504.3051 | 1395485.0409 | 0 | 338636.2902 | 0 | 1924476.9565 | 5007094.2763 | 3417444.7291 | 15283572.2605 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23577736.4213 | 36203969.4752 | 23713.7371 | 1.554 | 15172.7288 | 23297.9537 | 309.3166 | 474.9603
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.6332 | 8.8233 | 0.49165 | 4 | 13355.9528 | 19776.3175 | 272.2792 | 403.167 | 108.8183 | 0 | 150.738 | 1709132.8817 | 63788.0569 | 1959972.3839 | 1703399.8603 | 0 | 366116.9643 | 0 | 2262939.9574 | 5887705.5762 | 4018480.036 | 17971535.7167 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 26265699.8775 | 38891932.9314 | 31622.7766 | 1.9666 | 13355.9528 | 19776.3175 | 272.2792 | 403.167
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.2823 | 10.6231 | 0.61058 | 4 | 11929.1194 | 17098.8588 | 243.1912 | 348.5834 | 108.8909 | 0 | 174.991 | 1949060.8 | 72707.6601 | 2273647.2548 | 2044587.9532 | 0 | 388775.7574 | 0 | 2624223.976 | 6827692.4831 | 4660040.4148 | 20840736.2995 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 29134900.4602 | 41761133.5141 | 42169.6503 | 2.4423 | 11929.1194 | 17098.8588 | 243.1912 | 348.5834
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.3554 | 12.4965 | 0.74035 | 4 | 10812.509 | 15076.1339 | 220.4276 | 307.3474 | 108.9173 | 0 | 169.4539 | 2186158.0682 | 81489.8508 | 2589074.4963 | 2400327.9222 | 0 | 403230.8376 | 0 | 2987509.6582 | 7772887.3083 | 5305155.3048 | 23725833.4463 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 32019997.607 | 44646230.6609 | 56234.1325 | 2.9614 | 10812.509 | 15076.1339 | 220.4276 | 307.3474
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.3165 | 14.34 | 0.87417 | 4 | 9944.2411 | 13555.1419 | 202.7268 | 276.3399 | 108.8976 | 0 | 165.2468 | 2409009.7407 | 89707.1429 | 2890415.683 | 2751380.0217 | 0 | 408304.3037 | 0 | 3334038.5879 | 8674484.5003 | 5920513.9143 | 26477853.8944 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 34772018.0552 | 47398251.1091 | 74989.4209 | 3.4967 | 9944.2411 | 13555.1419 | 202.7268 | 276.3399
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6339 | 16.0535 | 1.0044 | 4 | 9273.7271 | 12416.3502 | 189.0575 | 253.1241 | 108.841 | 0 | 170.5338 | 2608119.5109 | 97011.5053 | 3163682.3332 | 3078856.9221 | 0 | 404237.9947 | 0 | 3647244.2238 | 9489381.3178 | 6476697.7367 | 28965231.5446 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 37259395.7053 | 49885628.7592 | 100000 | 4.0177 | 9273.7271 | 12416.3502 | 189.0575 | 253.1241
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.9406 | 17.5702 | 1.1248 | 4 | 8759.1002 | 11565.5103 | 178.5661 | 235.7786 | 108.7618 | 0 | 197.5518 | 2778651.5964 | 103234.4744 | 3400822.7099 | 3369934.5031 | 0 | 392912.4489 | 0 | 3917766.7358 | 10193225.402 | 6957085.7867 | 31113633.6572 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 39407797.8179 | 52034030.8718 | 133352.1432 | 4.4991 | 8759.1002 | 11565.5103 | 178.5661 | 235.7786
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.646 | 18.6052 | 1.2202 | 4 | 8359.2226 | 10946.1253 | 170.4141 | 223.1516 | 108.6925 | 0 | 383.7413 | 2892196.7735 | 107358.8372 | 3560347.7002 | 3569313.263 | 0 | 365817.4749 | 0 | 4093063.279 | 10649311.0493 | 7268373.6126 | 32505781.9896 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 40799946.1504 | 53426179.2043 | 177827.941 | 4.8808 | 8359.2226 | 10946.1253 | 170.4141 | 223.1516
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.2586 | 19.977 | 1.3248 | 4 | 8061.6697 | 10444.2624 | 164.348 | 212.9204 | 108.5831 | 0 | 165.1018 | 3039406.893 | 112681.3068 | 3769158.2033 | 3834599.4279 | 0 | 359673.8415 | 0 | 4335052.6723 | 11278917.8117 | 7698093.1651 | 34427583.3215 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 42721747.4823 | 55347980.5362 | 237137.3706 | 5.2994 | 8061.6697 | 10444.2624 | 164.348 | 212.9204
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.0233 | 20.8299 | 1.3993 | 4 | 7836.748 | 10092.541 | 159.7627 | 205.7501 | 108.5049 | 0 | 196.7248 | 3129128.8958 | 115910.2843 | 3897565.19 | 4000169.461 | 0 | 341613.4987 | 0 | 4478911.0586 | 11653207.8236 | 7953553.7891 | 35570060.0012 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 43864224.162 | 56490457.2159 | 316227.766 | 5.5972 | 7836.748 | 10092.541 | 159.7627 | 205.7501
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.777 | 21.4985 | 1.4592 | 4 | 7666.589 | 9829.8581 | 156.2938 | 200.395 | 108.4383 | 0 | 200.9875 | 3198549.5779 | 118400.3724 | 3997526.0213 | 4130345.106 | 0 | 324635.5318 | 0 | 4590088.0777 | 11942467.6216 | 8150979.5449 | 36452991.8535 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 44747156.0143 | 57373389.0682 | 421696.5034 | 5.8366 | 7666.589 | 9829.8581 | 156.2938 | 200.395
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.7271 | 22.0219 | 1.5067 | 4 | 7538.0881 | 9633.0779 | 153.6741 | 196.3833 | 108.383 | 0 | 177.8458 | 3252343.5401 | 120324.7475 | 4075358.3774 | 4232484.5886 | 0 | 309762.3491 | 0 | 4676206.7051 | 12166530.6247 | 8303907.1486 | 37136918.0811 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 45431082.2419 | 58057315.2957 | 562341.3252 | 6.0269 | 7538.0881 | 9633.0779 | 153.6741 | 196.3833
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.9929 | 22.4226 | 1.5437 | 4 | 7441.183 | 9485.9212 | 151.6986 | 193.3833 | 108.3389 | 0 | 160.3835 | 3293207.4177 | 121783.4352 | 4134704.3204 | 4310825.4 | 0 | 297040.0373 | 0 | 4741448.6381 | 12336276.7514 | 8419762.368 | 37655048.368 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 45949212.5288 | 58575445.5827 | 749894.2093 | 6.175 | 7441.183 | 9485.9212 | 151.6986 | 193.3833
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.9 | 23.1109 | 1.5921 | 4 | 7366.1434 | 9348.8042 | 150.1688 | 190.588 | 108.2595 | 0 | 184.5013 | 3362783.4654 | 124260.8264 | 4236187.2467 | 4445707.3862 | 0 | 298832.4668 | 0 | 4862430.8427 | 12651047.631 | 8634599.9612 | 38615849.8266 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 46910013.9874 | 59536247.0412 | 1000000 | 6.3683 | 7366.1434 | 9348.8042 | 150.1688 | 190.588
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.0324 | 22.9583 | 1.5942 | 4 | 7313.2539 | 9293.3357 | 149.0906 | 189.4572 | 108.2773 | 0 | 194.4748 | 3347419.2352 | 123714.276 | 4213735.6826 | 4415774.0041 | 0 | 277965.3705 | 0 | 4827657.3417 | 12560574.1144 | 8572849.9271 | 38339689.9516 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 46633854.1124 | 59260087.1662 | 1333521.4322 | 6.3766 | 7313.2539 | 9293.3357 | 149.0906 | 189.4572
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.0265 | 23.133 | 1.6108 | 4 | 7271.9434 | 9231.5439 | 148.2484 | 188.1975 | 108.2565 | 0 | 202.8376 | 3364999.5866 | 124339.3451 | 4239439.3265 | 4450060.3104 | 0 | 271199.0416 | 0 | 4855514.668 | 12633053.1631 | 8622318.3671 | 38560923.8084 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 46855087.9692 | 59481321.0231 | 1778279.41 | 6.4433 | 7271.9434 | 9231.5439 | 148.2484 | 188.1975
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.7723 | 23.264 | 1.6234 | 4 | 7240.8968 | 9185.2885 | 147.6155 | 187.2545 | 108.2408 | 0 | 203.2975 | 3378142.4821 | 124806.2871 | 4258679.2433 | 4475774.0579 | 0 | 265871.5105 | 0 | 4876276.6965 | 12687071.7025 | 8659187.1302 | 38725809.1102 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47019973.271 | 59646206.3249 | 2371373.7057 | 6.4937 | 7240.8968 | 9185.2885 | 147.6155 | 187.2545
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.3371 | 23.3631 | 1.633 | 4 | 7217.5753 | 9150.59 | 147.14 | 186.5472 | 108.2288 | 0 | 186.9607 | 3388066.6556 | 125158.6723 | 4273220.9925 | 4495236.9145 | 0 | 261758.5246 | 0 | 4891942.2862 | 12727830.3534 | 8687005.747 | 38850220.1461 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47144384.3068 | 59770617.3607 | 3162277.6602 | 6.5319 | 7217.5753 | 9150.59 | 147.14 | 186.5472
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7586 | 23.437 | 1.6402 | 4 | 7200.0636 | 9124.6159 | 146.783 | 186.0176 | 108.2198 | 0 | 188.8598 | 3395459.1888 | 125421.0506 | 4284060.8939 | 4509760.9575 | 0 | 258575.4868 | 0 | 4903578.2553 | 12758104.758 | 8707668.6502 | 38942629.2411 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47236793.4019 | 59863026.4558 | 4216965.0343 | 6.5606 | 7200.0636 | 9124.6159 | 146.783 | 186.0176
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.083 | 23.4938 | 1.6456 | 4 | 7186.9184 | 9105.0651 | 146.5151 | 185.6191 | 108.2128 | 0 | 187.8728 | 3401137.647 | 125622.527 | 4292391.8465 | 4520932.4638 | 0 | 256186.6517 | 0 | 4912545.743 | 12781436.3216 | 8723592.9218 | 39013846.1224 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47308010.2831 | 59934243.337 | 5623413.2519 | 6.5825 | 7186.9184 | 9105.0651 | 146.5151 | 185.6191
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3071 | 23.5331 | 1.6496 | 4 | 7177.0533 | 9090.613 | 146.3139 | 185.3244 | 108.208 | 0 | 169.7887 | 3405057.1134 | 125761.557 | 4298144.5199 | 4528651.3346 | 0 | 254253.7862 | 0 | 4918628.6413 | 12797262.7753 | 8734394.8016 | 39062154.5294 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47356318.6901 | 59982551.744 | 7498942.0933 | 6.5983 | 7177.0533 | 9090.613 | 146.3139 | 185.3244
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.4897 | 23.5651 | 1.6527 | 4 | 7169.6511 | 9079.6261 | 146.163 | 185.1005 | 108.204 | 0 | 188.383 | 3408248.2339 | 125874.7327 | 4302829.4949 | 4534940.3133 | 0 | 252873.8049 | 0 | 4923658.9661 | 12810350.6485 | 8743327.544 | 39102103.7382 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47396267.899 | 60022500.9529 | 10000000 | 6.6107 | 7169.6511 | 9079.6261 | 146.163 | 185.1005
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.452 | [19 empty] | 100 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6773 | [19 empty] | 133.3521 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4228 | [19 empty] | 177.8279 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7811 | [19 empty] | 237.1374 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.71826 | 0.083731 | 0.00029328 | 4 | 7870684.8781 | 19047556.643 | 160454.5571 | 388310.2059 | 83.9183 | 0 | 82.8858 | 55425.6741 | 1713.8847 | 48122.2809 | 44820.6409 | 0 | 41136.2114 | 0 | 74575.2899 | 194029.6067 | 132429.1935 | 592252.7821 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9233183.6339 | 22344890.0552 | 316.2278 | 0.0011731 | 7870684.8781 | 19047556.643 | 160454.5571 | 388310.2059
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.15394 | 0.0020782 | 4 | 1145747.049 | 2723036.9124 | 23357.6033 | 55512.7906 | 92.6276 | 0 | 187.4178 | 90709.1333 | 2999.7036 | 77789.9828 | 58408.9335 | 0 | 55326.6832 | 0 | 111241.4302 | 289427.3826 | 197540.1358 | 883443.385 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9524374.2368 | 22636080.658 | 421.6965 | 0.0083128 | 1145747.049 | 2723036.9124 | 23357.6033 | 55512.7906
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5542 | 0.2386 | 0.0049929 | 4 | 492317.9072 | 1148838.3606 | 10036.5664 | 23420.6239 | 97.8953 | 0 | 253.7157 | 127735.0767 | 4398.0251 | 110005.2409 | 74449.3852 | 0 | 68076.4051 | 0 | 150019.0119 | 390318.6957 | 266400.5301 | 1191402.3706 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9832333.2223 | 22944039.6436 | 562.3413 | 0.019972 | 492317.9072 | 1148838.3606 | 10036.5664 | 23420.6239
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.35135 | 0.0093039 | 4 | 274200.7354 | 626518.7931 | 5589.9529 | 12772.433 | 101.7337 | 0 | 368.9731 | 171514.8172 | 6080.1731 | 149489.1752 | 95447.1827 | 0 | 82302.1323 | 0 | 196885.0574 | 512254.5327 | 349624.2443 | 1563597.3149 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10204528.1666 | 23316234.5879 | 749.8942 | 0.037216 | 274200.7354 | 626518.7931 | 5589.9529 | 12772.433
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8667 | 0.49397 | 0.015352 | 4 | 173203.5417 | 386717.7637 | 3530.9885 | 7883.7647 | 104.4721 | 0 | 73.5969 | 221260.4542 | 8009.0098 | 195927.4761 | 121888.5126 | 0 | 97141.6856 | 0 | 251248.584 | 653697.2773 | 446161.8239 | 1995334.8235 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10636265.6753 | 23747972.0966 | 1000 | 0.061409 | 173203.5417 | 386717.7637 | 3530.9885 | 7883.7647
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 0.67904 | 0.02361 | 4 | 118131.8023 | 256970.2584 | 2408.2766 | 5238.6863 | 106.5282 | 0 | 94.8513 | 279692.4578 | 10282.6115 | 252341.923 | 155957.3619 | 0 | 113822.0836 | 0 | 316717.6107 | 824034.2554 | 562420.3115 | 2515268.6154 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11156199.4672 | 24267905.8885 | 1333.5214 | 0.094439 | 118131.8023 | 256970.2584 | 2408.2766 | 5238.6863
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9861 | 0.91214 | 0.034704 | 4 | 84768.5562 | 179221.4675 | 1728.1217 | 3653.672 | 108.0477 | 0 | 75.6916 | 346806.0963 | 12897.7397 | 319181.8765 | 198936.5867 | 0 | 131594.1352 | 0 | 393672.4094 | 1024254.856 | 699074.9855 | 3126418.6853 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11767349.5371 | 24879055.9584 | 1778.2794 | 0.13882 | 84768.5562 | 179221.4675 | 1728.1217 | 3653.672
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4601 | 1.2034 | 0.049299 | 4 | 63303.1974 | 129794.3542 | 1290.5213 | 2646.0335 | 109.1682 | 0 | 96.7004 | 423637.2635 | 15886.8662 | 398076.8483 | 252373.4503 | 0 | 150520.289 | 0 | 483792.9397 | 1258729.9895 | 859109.0822 | 3842126.7286 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 12483057.5804 | 25594764.0017 | 2371.3737 | 0.19719 | 63303.1974 | 129794.3542 | 1290.5213 | 2646.0335
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.172 | 1.54 | 0.067753 | 4 | 48921.1883 | 97301.766 | 997.3246 | 1983.6281 | 109.8843 | 0 | 92.277 | 505416.1531 | 19053.2601 | 484644.5186 | 314274.367 | 0 | 167379.9773 | 0 | 581399.6277 | 1512682.5698 | 1032436.9364 | 4617287.41 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 13258218.2618 | 26369924.6831 | 3162.2777 | 0.27101 | 48921.1883 | 97301.766 | 997.3246 | 1983.6281
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8445 | 2.0736 | 0.094448 | 4 | 38237.5349 | 72943.8297 | 779.5239 | 1487.0586 | 110.7859 | 0 | 99.8388 | 625734.25 | 23739.9867 | 614471.2576 | 411918.9048 | 0 | 198326.431 | 0 | 730934.4237 | 1901741.4353 | 1297977.6065 | 5804844.2956 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 14445775.1473 | 27557481.5686 | 4216.965 | 0.37779 | 38237.5349 | 72943.8297 | 779.5239 | 1487.0586
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8607 | 2.6725 | 0.12757 | 4 | 30754.7035 | 56450.2169 | 626.9762 | 1150.814 | 111.3045 | 0 | 92.3436 | 749763.1414 | 28544.5237 | 752488.5766 | 521840.4924 | 0 | 224328.7905 | 0 | 888016.5546 | 2310436.9179 | 1576920.6712 | 7052339.6686 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 15693270.5203 | 28804976.9416 | 5623.4133 | 0.51027 | 30754.7035 | 56450.2169 | 626.9762 | 1150.814
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.6339 | 3.422 | 0.17034 | 4 | 25212.2153 | 44455.1238 | 513.9851 | 906.2778 | 111.7063 | 0 | 98.4708 | 893825.2368 | 34112.3385 | 916776.4798 | 659354.2233 | 0 | 252610.5852 | 0 | 1075104.7568 | 2797202.043 | 1909147.8711 | 8538133.5345 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 17179064.3863 | 30290770.8076 | 7498.9421 | 0.68138 | 25212.2153 | 44455.1238 | 513.9851 | 906.2778
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2944 | 4.348 | 0.22503 | 4 | 21030.4035 | 35597.3216 | 428.7332 | 725.6996 | 112.0169 | 0 | 99.9945 | 1059441.5207 | 40498.2969 | 1110120.1305 | 829213.1211 | 0 | 282563.1466 | 0 | 1295516.1241 | 3370667.2081 | 2300549.6298 | 10288569.1777 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 18929500.0295 | 32041206.4508 | 10000 | 0.9001 | 21030.4035 | 35597.3216 | 428.7332 | 725.6996
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0212 | 5.4858 | 0.29429 | 4 | 17827.6985 | 28966.2216 | 363.4417 | 590.5156 | 112.2589 | 0 | 119.4386 | 1249272.1025 | 47800.1658 | 1336763.1243 | 1037756.1975 | 0 | 314176.5473 | 0 | 1554449.5736 | 4044358.9289 | 2760358.0723 | 12344934.7121 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 20985865.5639 | 34097571.9852 | 13335.2143 | 1.1771 | 17827.6985 | 28966.2216 | 363.4417 | 590.5156
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.9271 | 6.858 | 0.38065 | 4 | 15343.5346 | 23954.9934 | 312.7987 | 488.3549 | 112.4467 | 0 | 118.8772 | 1463432.9201 | 56018.5266 | 1597958.7083 | 1289254.3933 | 0 | 346241.4563 | 0 | 1853633.3418 | 4822773.7229 | 3291642.164 | 14720955.2333 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 23361886.085 | 36473592.5063 | 17782.7941 | 1.5226 | 15343.5346 | 23954.9934 | 312.7987 | 488.3549
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.1218 | 8.4864 | 0.48641 | 4 | 13399.3194 | 20138.3617 | 273.1632 | 410.5477 | 112.5914 | 0 | 146.463 | 1701868.0927 | 65146.3738 | 1894696.3608 | 1587687.2893 | 0 | 377920.7097 | 0 | 2194654.3423 | 5710040.4131 | 3897219.9115 | 17429233.4931 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26070164.3449 | 39181870.7662 | 23713.7371 | 1.9456 | 13399.3194 | 20138.3617 | 273.1632 | 410.5477
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.4445 | 10.3377 | 0.61142 | 4 | 11870.7876 | 17231.965 | 242.0021 | 351.2969 | 112.6938 | 0 | 137.8312 | 1957157.8087 | 74892.9738 | 2218551.5829 | 1927103.0109 | 0 | 405926.4512 | 0 | 2567616.4128 | 6680411.2154 | 4559517.9233 | 20391177.379 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 29032108.2308 | 42143814.6521 | 31622.7766 | 2.4457 | 11870.7876 | 17231.965 | 242.0021 | 351.2969
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.5512 | 12.3405 | 0.75261 | 4 | 10670.0819 | 15025.4758 | 217.5241 | 306.3146 | 112.7483 | 0 | 156.3086 | 2218458.8937 | 84834.8968 | 2556108.6818 | 2294714.7841 | 0 | 427064.9001 | 0 | 2956661.041 | 7692625.5341 | 5250374.9947 | 23480843.7263 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 32121774.5781 | 45233480.9993 | 42169.6503 | 3.0105 | 10670.0819 | 15025.4758 | 217.5241 | 306.3146
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.8996 | 14.3826 | 0.90343 | 4 | 9731.6605 | 13359.9656 | 198.3931 | 272.361 | 112.7502 | 0 | 167.1451 | 2471920.9128 | 94435.8898 | 2889221.7495 | 2670402.2733 | 0 | 438587.4235 | 0 | 3340181.6171 | 8690467.4022 | 5931422.5732 | 26526639.8414 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 35167570.6932 | 48279277.1145 | 56234.1325 | 3.6137 | 9731.6605 | 13359.9656 | 198.3931 | 272.361
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.8802 | 16.3399 | 1.0551 | 4 | 9003.1917 | 12109.8164 | 183.5422 | 246.875 | 112.7044 | 0 | 165.462 | 2704496.3411 | 103198.9499 | 3199815.3258 | 3031732.914 | 0 | 439350.7891 | 0 | 3696651.7848 | 9617929.6564 | 6564434.6192 | 29357610.3802 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 37998541.232 | 51110247.6532 | 74989.4209 | 4.2206 | 9003.1917 | 12109.8164 | 183.5422 | 246.875
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.0714 | 18.129 | 1.2 | 4 | 8441.4394 | 11173.1262 | 172.0902 | 227.7793 | 112.6239 | 0 | 154.6955 | 2909332.6862 | 110872.1256 | 3477355.6027 | 3363377.3754 | 0 | 431009.8819 | 0 | 4013859.592 | 10443239.3025 | 7127725.4111 | 31876771.9772 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 40517702.829 | 53629409.2503 | 100000 | 4.7999 | 8441.4394 | 11173.1262 | 172.0902 | 227.7793
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1493 | 19.689 | 1.3314 | 4 | 8010.7083 | 10472.672 | 163.3091 | 213.4996 | 112.5253 | 0 | 179.6429 | 3082509.0648 | 117321.5247 | 3715004.0669 | 3653830.4511 | 0 | 415835.5122 | 0 | 4283955.2417 | 11145972.7787 | 7607355.4483 | 34021784.0884 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 42662714.9401 | 55774421.3614 | 133352.1432 | 5.3257 | 8010.7083 | 10472.672 | 163.3091 | 213.4996
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.9823 | 20.9984 | 1.4458 | 4 | 7681.9586 | 9949.1742 | 156.6071 | 202.8274 | 112.423 | 0 | 180.8248 | 3224276.9874 | 122572.3472 | 3911670.6642 | 3898685.2941 | 0 | 396638.8828 | 0 | 4505999.2285 | 11723685.6851 | 8001656.3778 | 35785185.4672 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 44426116.3189 | 57537822.7402 | 177827.941 | 5.7832 | 7681.9586 | 9949.1742 | 156.6071 | 202.8274
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.9092 | 22.1262 | 1.5459 | 4 | 7426.7544 | 9547.1779 | 151.4044 | 194.6321 | 112.3211 | 0 | 180.9572 | 3343903.6361 | 126981.0341 | 4079154.932 | 4110408.0173 | 0 | 376875.9075 | 0 | 4694556.1755 | 12214272.1828 | 8336491.743 | 37282643.6283 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 45923574.4801 | 59035280.9014 | 237137.3706 | 6.1835 | 7426.7544 | 9547.1779 | 151.4044 | 194.6321
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3908 | 22.9737 | 1.6241 | 4 | 7238.7548 | 9257.0206 | 147.5718 | 188.7169 | 112.2363 | 0 | 177.684 | 3432361.3722 | 130226.9975 | 4203934.8692 | 4270068.1891 | 0 | 356901.7422 | 0 | 4833462.3364 | 12575677.5198 | 8583158.3116 | 38385791.3379 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 47026722.1897 | 60138428.611 | 316227.766 | 6.4965 | 7238.7548 | 9257.0206 | 147.5718 | 188.7169
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.9381 | 23.6412 | 1.6869 | 4 | 7096.5251 | 9039.6852 | 144.6723 | 184.2862 | 112.1647 | 0 | 184.4472 | 3501189.3438 | 132743.9514 | 4301588.0023 | 4396166.3728 | 0 | 338803.9136 | 0 | 4941491.7177 | 12856747.8101 | 8774994.5602 | 39243725.6719 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 47884656.5237 | 60996362.945 | 421696.5034 | 6.7476 | 7096.5251 | 9039.6852 | 144.6723 | 184.2862
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.6707 | 24.1533 | 1.7361 | 4 | 6989.1082 | 8877.2281 | 142.4824 | 180.9743 | 112.1068 | 0 | 193.3044 | 3553507.7368 | 134651.8571 | 4376154.6535 | 4493134.7391 | 0 | 322885.5138 | 0 | 5023330.4551 | 13069675.4173 | 8920322.0273 | 39893662.3999 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 48534593.2517 | 61646299.673 | 562341.3252 | 6.9443 | 6989.1082 | 8877.2281 | 142.4824 | 180.9743
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7661 | 24.5448 | 1.7742 | 4 | 6908.097 | 8755.6115 | 140.8309 | 178.495 | 112.061 | 0 | 167.4376 | 3593217.1152 | 136096.7908 | 4432948.0508 | 4567387.4171 | 0 | 309465.8045 | 0 | 5085254.9196 | 13230790.1715 | 9030286.1576 | 40385446.4271 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49026377.2789 | 62138083.7002 | 749894.2093 | 7.0969 | 6908.097 | 8755.6115 | 140.8309 | 178.495
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.3714 | 24.8439 | 1.8037 | 4 | 6847.0695 | 8664.4345 | 139.5868 | 176.6362 | 112.0249 | 0 | 171.4287 | 3623401.3265 | 137193.254 | 4476234.2097 | 4624211.9921 | 0 | 298515.7713 | 0 | 5132227.0559 | 13353002.0349 | 9113698.2656 | 40758483.91 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49399414.7618 | 62511121.1831 | 1000000 | 7.2147 | 6847.0695 | 8664.4345 | 139.5868 | 176.6362
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.6017 | 25.0728 | 1.8263 | 4 | 6801.1385 | 8595.9973 | 138.6504 | 175.241 | 111.9968 | 0 | 185.2927 | 3646395.581 | 138027.4054 | 4509278.3882 | 4667716.44 | 0 | 289800.3622 | 0 | 5167975.089 | 13446011.084 | 9177178.8527 | 41042383.2026 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49683314.0543 | 62795020.4756 | 1333521.4322 | 7.3051 | 6801.1385 | 8595.9973 | 138.6504 | 175.241
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.5297 | 25.245 | 1.8435 | 4 | 6766.5931 | 8544.7404 | 137.9462 | 174.1961 | 111.9753 | 0 | 179.6687 | 3663644.7697 | 138652.3479 | 4534111.4071 | 4700428.3282 | 0 | 282895.4204 | 0 | 5194695.5866 | 13515532.3377 | 9224628.5369 | 41254588.7343 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49895519.5861 | 63007226.0074 | 1778279.41 | 7.3738 | 6766.5931 | 8544.7404 | 137.9462 | 174.1961
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.207 | 25.3706 | 1.8562 | 4 | 6740.6293 | 8506.5364 | 137.4168 | 173.4173 | 111.9594 | 0 | 193.0984 | 3676192.0885 | 139106.5869 | 4552196.6778 | 4724292.2865 | 0 | 277364.3941 | 0 | 5213969.2932 | 13565678.5687 | 9258854.37 | 41407654.2656 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50048585.1174 | 63160291.5387 | 2371373.7057 | 7.4249 | 6740.6293 | 8506.5364 | 137.4168 | 173.4173
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.7398 | 25.4693 | 1.8661 | 4 | 6721.1251 | 8477.6794 | 137.0192 | 172.829 | 111.9468 | 0 | 214.604 | 3686036.4339 | 139462.7677 | 4566398.4394 | 4743055.747 | 0 | 273232.0002 | 0 | 5229192.3014 | 13605285.7135 | 9285887.0601 | 41528550.4634 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50169481.3151 | 63281187.7364 | 3162277.6602 | 7.4644 | 6721.1251 | 8477.6794 | 137.0192 | 172.829
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1297 | 25.5414 | 1.8735 | 4 | 6706.4793 | 8456.1473 | 136.7207 | 172.39 | 111.9376 | 0 | 204.3625 | 3693226.2689 | 139722.787 | 4576777.8005 | 4756782.4517 | 0 | 269992.5549 | 0 | 5240235.7266 | 13634018.4404 | 9305497.7367 | 41616253.7667 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50257184.6185 | 63368891.0398 | 4216965.0343 | 7.4938 | 6706.4793 | 8456.1473 | 136.7207 | 172.39
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.4197 | 25.5951 | 1.879 | 4 | 6695.4852 | 8440.0307 | 136.4965 | 172.0614 | 111.9307 | 0 | 200.0884 | 3698567.1589 | 139915.8751 | 4584491.8606 | 4766991.6312 | 0 | 267502.4085 | 0 | 5248412.8844 | 13655293.7276 | 9320018.5573 | 41681194.1037 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50322124.9554 | 63433831.3767 | 5623413.2519 | 7.5158 | 6695.4852 | 8440.0307 | 136.4965 | 172.0614
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.6413 | 25.6361 | 1.8831 | 4 | 6687.2342 | 8427.9119 | 136.3283 | 171.8144 | 111.9254 | 0 | 223.2303 | 3702641.704 | 140063.145 | 4590379.0789 | 4774787.2572 | 0 | 265633.2568 | 0 | 5254666.7324 | 13671564.9573 | 9331124.0059 | 41730860.1375 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50371790.9893 | 63483497.4106 | 7498942.0933 | 7.5325 | 6687.2342 | 8427.9119 | 136.3283 | 171.8144
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8 | 26.0367 | 1.9064 | 4 | 6681.0117 | 8400.4278 | 136.2015 | 171.2541 | 111.8779 | 0 | 193.26 | 3742466.8135 | 141505.9371 | 4647835.4811 | 4850881.8923 | 0 | 276599.886 | 0 | 5327123.1039 | 13860081.5731 | 9459790.4699 | 42306285.1569 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50947216.0087 | 64058922.4299 | 10000000 | 7.6257 | 6681.0117 | 8400.4278 | 136.2015 | 171.2541
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7575 | [19 empty] | 100 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6119 | [19 empty] | 133.3521 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0897 | [19 empty] | 177.8279 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7807 | [19 empty] | 237.1374 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.86458 | 0.11416 | 0.00092831 | 4 | 2618153.5495 | 6282183.4125 | 53374.6014 | 128070.8061 | 89.9782 | 0 | 62.605 | 72282.0229 | 2339.2136 | 61372.2409 | 50309.8598 | 0 | 48823.5061 | 0 | 91699.4689 | 238583.208 | 162837.9418 | 728247.4621 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9721805.0957 | 23327189.0116 | 316.2278 | 0.0037132 | 2618153.5495 | 6282183.4125 | 53374.6014 | 128070.8061
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.1957 | 0.0034017 | 4 | 737889.7354 | 1737792.0819 | 15042.8803 | 35427.2421 | 97.5837 | 0 | 199.7774 | 111149.7716 | 3811.7196 | 93896.0194 | 65534.1392 | 0 | 63551.6075 | 0 | 131797.8704 | 342911.0232 | 234043.8195 | 1046695.9704 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10040253.604 | 23645637.5199 | 421.6965 | 0.013607 | 737889.7354 | 1737792.0819 | 15042.8803 | 35427.2421
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.30197 | 0.0072689 | 4 | 358009.4708 | 825943.2415 | 7298.5073 | 16837.9701 | 102.6853 | 0 | 306.0826 | 155456.9106 | 5540.1859 | 132335.6834 | 84877.4501 | 0 | 78881.1881 | 0 | 178265.6531 | 463810.662 | 316560.3072 | 1415728.0404 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10409285.674 | 24014669.5899 | 562.3413 | 0.029075 | 358009.4708 | 825943.2415 | 7298.5073 | 16837.9701
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.43421 | 0.012833 | 4 | 210876.814 | 475913.7286 | 4299.0091 | 9702.1451 | 106.1772 | 0 | 434.5187 | 204575.3292 | 7484.1688 | 176499.7785 | 108663.9713 | 0 | 94131.6165 | 0 | 230628.397 | 600047.7807 | 409544.9401 | 1831575.982 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10825133.6157 | 24430517.5316 | 749.8942 | 0.051334 | 210876.814 | 475913.7286 | 4299.0091 | 9702.1451
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2734 | 0.60586 | 0.02057 | 4 | 137620.4989 | 302971.7297 | 2805.58 | 6176.4885 | 108.7685 | 0 | 88.8595 | 262076.1254 | 9776.4203 | 229963.5876 | 139442.7872 | 0 | 111050.7772 | 0 | 293400.7821 | 763368.6502 | 521014.7894 | 2330093.9192 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11323651.5528 | 24929035.4687 | 1000 | 0.082282 | 137620.4989 | 302971.7297 | 2805.58 | 6176.4885
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3212 | 0.82505 | 0.031048 | 4 | 95937.5683 | 205487.1561 | 1955.8171 | 4189.1336 | 110.6952 | 0 | 87.6149 | 328717.2455 | 12439.503 | 293993.8962 | 178507.6902 | 0 | 129531.2431 | 0 | 367843.9354 | 957054.4647 | 653209.3377 | 2921297.3157 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11914854.9493 | 25520238.8652 | 1333.5214 | 0.12419 | 95937.5683 | 205487.1561 | 1955.8171 | 4189.1336
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6318 | 1.1002 | 0.045032 | 4 | 69998.0723 | 145529.6739 | 1427.0054 | 2966.8192 | 112.1223 | 0 | 73.7214 | 405179.533 | 15496.6308 | 369723.2584 | 227614.1276 | 0 | 149175.5664 | 0 | 455203.7553 | 1184346.7962 | 808341.0243 | 3615080.6921 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 12608638.3258 | 26214022.2417 | 1778.2794 | 0.18013 | 69998.0723 | 145529.6739 | 1427.0054 | 2966.8192
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2371 | 1.4365 | 0.063201 | 4 | 53021.63 | 106839.8469 | 1080.9176 | 2178.0748 | 113.1371 | 0 | 80.579 | 491013.6362 | 18918.8036 | 457345.8 | 287530.9201 | 0 | 169177.2535 | 0 | 555354.7012 | 1444919.0137 | 986186.917 | 4410447.0453 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13404004.679 | 27009388.5949 | 2371.3737 | 0.2528 | 53021.63 | 106839.8469 | 1080.9176 | 2178.0748
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5 | 1.9144 | 0.088215 | 4 | 41042.3127 | 79599.5924 | 836.7031 | 1622.7454 | 114.0999 | 0 | 102.9847 | 603562.8994 | 23414.795 | 575068.8198 | 372457.11 | 0 | 197614.443 | 0 | 691126.0462 | 1798168.2029 | 1227286.7471 | 5488699.0636 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 14482256.6972 | 28087640.6131 | 3162.2777 | 0.35286 | 41042.3127 | 79599.5924 | 836.7031 | 1622.7454
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.146 | 2.472 | 0.12 | 4 | 32627.709 | 60971.5004 | 665.16 | 1242.9865 | 114.7375 | 0 | 107.3719 | 724467.9738 | 28225.6975 | 705229.2835 | 471500.09 | 0 | 223504.2441 | 0 | 839641.6427 | 2184575.32 | 1491017.5444 | 6668161.796 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 15661719.4296 | 29267103.3455 | 4216.965 | 0.48001 | 32627.709 | 60971.5004 | 665.16 | 1242.9865
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4996 | 3.1789 | 0.16134 | 4 | 26472.4875 | 47554.0089 | 539.6775 | 969.4528 | 115.2358 | 0 | 111.1583 | 866627.4682 | 33870.2676 | 862107.8945 | 597128.1759 | 0 | 252578.8512 | 0 | 1018801.9364 | 2650713.6535 | 1809166.5352 | 8090994.7826 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 17084552.4162 | 30689936.3321 | 5623.4133 | 0.64537 | 26472.4875 | 47554.0089 | 539.6775 | 969.4528
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6756 | 4.0594 | 0.21455 | 4 | 21874.0101 | 37727.5258 | 445.9313 | 769.1266 | 115.6215 | 0 | 105.7094 | 1031169.2172 | 40388.9597 | 1048063.3934 | 753662.6031 | 0 | 283892.039 | 0 | 1231298.7228 | 3203586.7026 | 2186513.7517 | 9778575.3895 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 18772133.0231 | 32377516.939 | 7498.9421 | 0.85819 | 21874.0101 | 37727.5258 | 445.9313 | 769.1266
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8151 | 5.1433 | 0.28229 | 4 | 18379.9802 | 30428.9525 | 374.7008 | 620.3354 | 115.92 | 0 | 114.2253 | 1219850.4485 | 47845.5705 | 1266246.9784 | 946339.5061 | 0 | 316834.582 | 0 | 1480875.6633 | 3852934.7066 | 2629707.1072 | 11760634.5626 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 20754192.1962 | 34359576.1121 | 10000 | 1.1292 | 18379.9802 | 30428.9525 | 374.7008 | 620.3354
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.1003 | 6.4692 | 0.36772 | 4 | 15686.9682 | 24936.6768 | 319.8001 | 508.3679 | 116.1527 | 0 | 125.101 | 1435393.1171 | 56342.643 | 1521009.8498 | 1182051.3665 | 0 | 351289.5397 | 0 | 1772973.7413 | 4612913.9879 | 3148408.5827 | 14080382.828 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 23073940.4616 | 36679324.3775 | 13335.2143 | 1.4709 | 15686.9682 | 24936.6768 | 319.8001 | 508.3679
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6519 | 8.0624 | 0.4737 | 4 | 13587.9721 | 20768.3874 | 277.0092 | 423.3917 | 116.3335 | 0 | 124.0719 | 1677935.2013 | 65880.3282 | 1813725.636 | 1465308.2429 | 0 | 386073.2279 | 0 | 2109479.8282 | 5488433.7991 | 3745968.8439 | 16752805.1075 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 25746362.7411 | 39351746.657 | 17782.7941 | 1.8948 | 13587.9721 | 20768.3874 | 277.0092 | 423.3917
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4675 | 9.922 | 0.60182 | 4 | 11939.6329 | 17591.3841 | 243.4056 | 358.6242 | 116.469 | 0 | 163.2164 | 1943882.7888 | 76310.8927 | 2141098.9626 | 1795940.7094 | 0 | 418918.2596 | 0 | 2486699.1291 | 6469881.0418 | 4415826.7538 | 19748558.5379 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 28742116.1715 | 42347500.0874 | 23713.7371 | 2.4073 | 11939.6329 | 17591.3841 | 243.4056 | 358.6242
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.3554 | 12.0051 | 0.75108 | 4 | 10642.0526 | 15170.6676 | 216.9526 | 309.2746 | 116.5565 | 0 | 166.4228 | 2224879.4452 | 87296.6514 | 2493569.2109 | 2166538.3394 | 0 | 446713.4793 | 0 | 2893408.8792 | 7528056.3839 | 5138053.1681 | 22978515.5572 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 31972073.1908 | 45577457.1067 | 31622.7766 | 3.0043 | 10642.0526 | 15170.6676 | 216.9526 | 309.2746
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.8307 | 14.2046 | 0.91602 | 4 | 9623.4634 | 13336.6249 | 196.1873 | 271.8851 | 116.588 | 0 | 161.976 | 2506115.5246 | 98245.7059 | 2852740.9382 | 2558473.8801 | 0 | 465403.7953 | 0 | 3307582.1392 | 8605650.2478 | 5873533.1226 | 26267745.3538 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 35261302.9874 | 48866686.9033 | 42169.6503 | 3.6641 | 9623.4634 | 13336.6249 | 196.1873 | 271.8851
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.3272 | 16.3962 | 1.0883 | 4 | 8828.6659 | 11954.1344 | 179.9843 | 243.7012 | 116.5623 | 0 | 169.4908 | 2773267.5148 | 108590.9323 | 3199789.7067 | 2950057.1769 | 0 | 472923.035 | 0 | 3706805.0627 | 9644346.4028 | 6582464.5914 | 29438244.4226 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 38431802.0562 | 52037185.9721 | 56234.1325 | 4.3531 | 8828.6659 | 11954.1344 | 179.9843 | 243.7012
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.2735 | 18.4574 | 1.258 | 4 | 8212.6804 | 10916.4965 | 167.4266 | 222.5475 | 116.4891 | 0 | 160.2121 | 3014320.076 | 117867.6156 | 3517918.4069 | 3319676.2326 | 0 | 469139.0892 | 0 | 4071179.3539 | 10592373.5652 | 7229512.6097 | 32331986.9491 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 41325544.5828 | 54930928.4987 | 74989.4209 | 5.0319 | 8212.6804 | 10916.4965 | 167.4266 | 222.5475
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.2964 | 20.3113 | 1.417 | 4 | 7738.2392 | 10138.5734 | 157.7545 | 206.6885 | 116.385 | 0 | 206.3887 | 3223664.8146 | 125871.1379 | 3798157.4651 | 3653512.0667 | 0 | 456418.6143 | 0 | 4390473.3984 | 11423111.1728 | 7796508.0969 | 34867716.7666 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 43861274.4002 | 57466658.3161 | 100000 | 5.6681 | 7738.2392 | 10138.5734 | 157.7545 | 206.6885
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.1038 | 21.9017 | 1.5589 | 4 | 7374.7305 | 9556.622 | 150.3439 | 194.8247 | 116.2682 | 0 | 217.249 | 3398111.9397 | 132497.5117 | 4034596.2879 | 3941088.78 | 0 | 437269.6848 | 0 | 4657990.0396 | 12119134.5979 | 8271558.3864 | 36992247.228 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 45985804.8617 | 59591188.7776 | 133352.1432 | 6.2356 | 7374.7305 | 9556.622 | 150.3439 | 194.8247
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.6614 | 23.2265 | 1.6809 | 4 | 7097.3984 | 9120.9047 | 144.6901 | 185.942 | 116.1525 | 0 | 208.5021 | 3540076.2844 | 137857.997 | 4229041.3154 | 4181622.5427 | 0 | 415056.8257 | 0 | 4876425.4364 | 12687458.6932 | 8659451.2593 | 38726990.3542 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 47720547.9878 | 61325931.9037 | 177827.941 | 6.7237 | 7097.3984 | 9120.9047 | 144.6901 | 185.942
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.2595 | 24.3492 | 1.7862 | 4 | 6881.6083 | 8785.8057 | 140.2909 | 179.1105 | 116.0416 | 0 | 201.2797 | 3658109.733 | 142291.1261 | 4392146.8527 | 4386190.6818 | 0 | 392478.7516 | 0 | 5058774.6866 | 13161894.0373 | 8983263.1303 | 40175148.9994 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 49168706.633 | 62774090.5489 | 237137.3706 | 7.1449 | 6881.6083 | 8785.8057 | 140.2909 | 179.1105
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.5371 | 25.2018 | 1.8685 | 4 | 6723.11 | 8543.4233 | 137.0597 | 174.1692 | 115.9497 | 0 | 183.0095 | 3746405.8626 | 145592.1708 | 4515046.4623 | 4542078.5097 | 0 | 371163.54 | 0 | 5194911.7527 | 13516094.7575 | 9225012.4 | 41256305.4555 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 50249863.0891 | 63855247.005 | 316227.766 | 7.4742 | 6723.11 | 8543.4233 | 137.0597 | 174.1692
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8498 | 25.8588 | 1.9336 | 4 | 6603.1971 | 8362.3075 | 134.6151 | 170.4769 | 115.8744 | 0 | 181.6601 | 3813686.0695 | 148098.3378 | 4609217.2356 | 4662554.9566 | 0 | 351756.627 | 0 | 5298272.1583 | 13785017.3309 | 9408557.5821 | 42077160.2977 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 51070717.9314 | 64676101.8473 | 421696.5034 | 7.7342 | 6603.1971 | 8362.3075 | 134.6151 | 170.4769
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4102 | 26.3645 | 1.9844 | 4 | 6512.6271 | 8226.6455 | 132.7687 | 167.7113 | 115.8137 | 0 | 179.9616 | 3865035.2468 | 150005.5293 | 4681401.0409 | 4755490.7982 | 0 | 335055.8484 | 0 | 5376925.5008 | 13989657.1941 | 9548228.4937 | 42701799.6523 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 51695357.2859 | 65300741.2018 | 562341.3252 | 7.9377 | 6512.6271 | 8226.6455 | 132.7687 | 167.7113
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3787 | 26.7521 | 2.0239 | 4 | 6444.3146 | 8124.9334 | 131.3761 | 165.6378 | 115.7657 | 0 | 169.4839 | 3904130.4283 | 151454.2662 | 4736542.9737 | 4826830.5699 | 0 | 321178.176 | 0 | 5436653.2015 | 14145056.4194 | 9654291.6581 | 43176137.6932 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 52169695.3269 | 65775079.2428 | 749894.2093 | 8.0955 | 6444.3146 | 8124.9334 | 131.3761 | 165.6378
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8667 | 27.0444 | 2.054 | 4 | 6392.8487 | 8048.7997 | 130.3269 | 164.0857 | 115.7287 | 0 | 191.4118 | 3933462.67 | 152539.2878 | 4778020.8878 | 4880690.2712 | 0 | 309814.3279 | 0 | 5481265.7034 | 14261128.9982 | 9733513.5781 | 43530435.7245 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 52523993.3581 | 66129377.274 | 1000000 | 8.2161 | 6392.8487 | 8048.7997 | 130.3269 | 164.0857
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3125 | 26.739 | 2.0482 | 4 | 6350.5505 | 8011.1968 | 129.4646 | 163.3191 | 115.767 | 0 | 219.4096 | 3902794.5871 | 151404.3716 | 4734670.9862 | 4824417.3507 | 0 | 281405.5232 | 0 | 5418930.1993 | 14098944.8032 | 9622819.5325 | 43035387.3537 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 52028944.9874 | 65634328.9033 | 1333521.4322 | 8.1928 | 6350.5505 | 8011.1968 | 129.4646 | 163.3191
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.8355 | 27.8247 | 2.1181 | 4 | 6319.918 | 7925.7608 | 128.8401 | 161.5774 | 115.6356 | 0 | 205.1846 | 4011401.922 | 155424.5854 | 4888325.9286 | 5024423.6197 | 0 | 304611.3428 | 0 | 5609833.0854 | 14595634.9533 | 9961820.7659 | 44551476.2031 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53545033.8367 | 67150417.7526 | 1778279.41 | 8.4724 | 6319.918 | 7925.7608 | 128.8401 | 161.5774
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.2714 | 27.9105 | 2.1279 | 4 | 6302.235 | 7900.6496 | 128.4796 | 161.0654 | 115.6257 | 0 | 180.6875 | 4019927.1352 | 155740.2514 | 4900404.001 | 5040209.8657 | 0 | 299651.0999 | 0 | 5622213.6177 | 14627846.5588 | 9983805.8485 | 44649798.3782 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53643356.0118 | 67248739.9277 | 2371373.7057 | 8.5118 | 6302.235 | 7900.6496 | 128.4796 | 161.0654
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.7829 | 28.011 | 2.1384 | 4 | 6285.5519 | 7876.1596 | 128.1395 | 160.5662 | 115.6142 | 0 | 201.3087 | 4029921.2819 | 156110.2605 | 4914568.4605 | 5058736.9875 | 0 | 295530.0237 | 0 | 5637398.1355 | 14667353.5592 | 10010770.1882 | 44770388.8971 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53763946.5307 | 67369330.4466 | 3162277.6602 | 8.5536 | 6285.5519 | 7876.1596 | 128.1395 | 160.5662
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1728 | 28.0877 | 2.1463 | 4 | 6273.0239 | 7857.7533 | 127.8841 | 160.1909 | 115.6054 | 0 | 190.6691 | 4037525.5499 | 156391.6868 | 4925351.9546 | 5072854.0426 | 0 | 292406.2339 | 0 | 5648966.4925 | 14697452.051 | 10031313.0273 | 44862261.0386 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53855818.6722 | 67461202.5881 | 4216965.0343 | 8.5853 | 6273.0239 | 7857.7533 | 127.8841 | 160.1909
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4675 | 28.1456 | 2.1523 | 4 | 6263.6192 | 7843.9376 | 127.6924 | 159.9093 | 115.5987 | 0 | 209.4451 | 4043265.4758 | 156604.0561 | 4933495.1882 | 5083521.657 | 0 | 290035.9447 | 0 | 5657699.7055 | 14720174.0799 | 10046821.2788 | 44931617.3859 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53925175.0195 | 67530558.9354 | 5623413.2519 | 8.6093 | 6263.6192 | 7843.9376 | 127.6924 | 159.9093
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.6844 | 28.1882 | 2.1568 | 4 | 6256.561 | 7833.6141 | 127.5485 | 159.6988 | 115.5938 | 0 | 212.2789 | 4047486.0144 | 156760.1766 | 4939484.8372 | 5091371.9621 | 0 | 288207.2754 | 0 | 5664091.0036 | 14736802.9266 | 10058170.8084 | 44982375.0044 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53975932.638 | 67581316.5539 | 7498942.0933 | 8.6271 | 6256.561 | 7833.6141 | 127.5485 | 159.6988
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.8501 | 28.2207 | 2.1602 | 4 | 6251.2648 | 7825.8487 | 127.4405 | 159.5405 | 115.59 | 0 | 201.5944 | 4050709.6358 | 156879.4021 | 4944060.7912 | 5097371.6045 | 0 | 286842.4779 | 0 | 5668986.9254 | 14749541.1109 | 10066864.8809 | 45021256.8286 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 54014814.4623 | 67620198.3782 | 10000000 | 8.6406 | 6251.2648 | 7825.8487 | 127.4405 | 159.5405
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5604 | [19 empty] | 100 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2716 | [19 empty] | 133.3521 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5766 | [19 empty] | 177.8279 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8815 | [19 empty] | 237.1374 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.15229 | 0.0018699 | 4 | 1369173.0783 | 3255258.6504 | 27912.4451 | 66362.8507 | 95.8257 | 0 | 44.4948 | 92299.7296 | 3119.5719 | 76930.7597 | 56942.4729 | 0 | 57702.0359 | 0 | 111927.8823 | 291213.3901 | 198759.1226 | 888894.9649 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10240939.4713 | 24348205.009 | 316.2278 | 0.0074797 | 1369173.0783 | 3255258.6504 | 27912.4451 | 66362.8507
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.24994 | 0.005179 | 4 | 511739.7084 | 1192729.0366 | 10432.5061 | 24315.3947 | 102.6784 | 0 | 245.9538 | 136394.3602 | 4852.8116 | 113756.6406 | 74404.516 | 0 | 73875.7595 | 0 | 157280.7943 | 409212.364 | 279295.8469 | 1249073.093 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10601117.5994 | 24708383.1371 | 421.6965 | 0.020716 | 511739.7084 | 1192729.0366 | 10432.5061 | 24315.3947
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.37595 | 0.010188 | 4 | 270359.7988 | 616531.1081 | 5511.6502 | 12568.8206 | 107.3423 | 0 | 366.6898 | 186523.044 | 6871.272 | 157150.8376 | 96583.7398 | 0 | 90679.8703 | 0 | 209745.4178 | 545714.5525 | 372461.3954 | 1665730.1295 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11017774.6358 | 25125040.1735 | 562.3413 | 0.040752 | 270359.7988 | 616531.1081 | 5511.6502 | 12568.8206
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7989 | 0.53358 | 0.017278 | 4 | 166282.0853 | 370398.8667 | 3389.8852 | 7551.0819 | 110.6021 | 0 | 520.7661 | 242646.7641 | 9157.6937 | 207466.0237 | 124027.6097 | 0 | 107741.6345 | 0 | 269505.493 | 701198.0096 | 478582.0498 | 2140325.2781 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11492369.7844 | 25599635.3221 | 749.8942 | 0.069114 | 166282.0853 | 370398.8667 | 3389.8852 | 7551.0819
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.73273 | 0.027017 | 4 | 111471.2668 | 242012.1153 | 2272.4926 | 4933.7443 | 112.9896 | 0 | 87.1384 | 306844.4524 | 11787.437 | 266928.1102 | 158617.5776 | 0 | 125758.5579 | 0 | 339275.0927 | 882724.1963 | 602477.4022 | 2694412.8263 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12046457.3326 | 26153722.8704 | 1000 | 0.10807 | 111471.2668 | 242012.1153 | 2272.4926 | 4933.7443
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8548 | 0.98906 | 0.040148 | 4 | 79156.4001 | 167000.8587 | 1613.7103 | 3404.5384 | 114.8029 | 0 | 89.0208 | 382139.8134 | 14877.2103 | 338885.1137 | 202996.329 | 0 | 145925.09 | 0 | 423081.187 | 1100770.4627 | 751298.4594 | 3359973.6656 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12712018.172 | 26819283.7097 | 1333.5214 | 0.16059 | 79156.4001 | 167000.8587 | 1613.7103 | 3404.5384
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3091 | 1.3123 | 0.057559 | 4 | 58629.6008 | 119902.3306 | 1195.2437 | 2444.3712 | 116.152 | 0 | 88.1413 | 469110.0546 | 18444.8155 | 424515.0947 | 258987.4471 | 0 | 167765.5611 | 0 | 522140.9595 | 1358503.6707 | 927206.6697 | 4146674.273 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 13498718.7793 | 27605984.317 | 1778.2794 | 0.23024 | 58629.6008 | 119902.3306 | 1195.2437 | 2444.3712
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.005 | 1.6879 | 0.079699 | 4 | 45024.7741 | 89276.6697 | 917.8909 | 1820.0257 | 117.0326 | 0 | 89.112 | 562076.6352 | 22241.1157 | 518859.9368 | 324229.2159 | 0 | 187446.5043 | 0 | 629792.829 | 1638591.7529 | 1118372.5411 | 5001610.5308 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 14353655.0372 | 28460920.5749 | 2371.3737 | 0.31879 | 45024.7741 | 89276.6697 | 917.8909 | 1820.0257
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5887 | 2.2676 | 0.11129 | 4 | 35095.8716 | 66786.2026 | 715.4768 | 1361.5271 | 118.0614 | 0 | 83.1888 | 695015.0853 | 27694.9565 | 656642.4411 | 423964.3057 | 0 | 221454.8607 | 0 | 789660.9432 | 2054535.7925 | 1402262.8949 | 6271231.2798 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 15623275.7861 | 29730541.3238 | 3162.2777 | 0.44516 | 35095.8716 | 66786.2026 | 715.4768 | 1361.5271
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.5512 | 2.9295 | 0.15083 | 4 | 28143.791 | 51525.7882 | 573.7492 | 1050.4229 | 118.6797 | 0 | 87.7285 | 834483.8017 | 33387.0228 | 805577.9661 | 538336.4372 | 0 | 251105.0647 | 0 | 960527.2141 | 2499094.7799 | 1705683.5385 | 7628195.825 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 16980240.3314 | 31087505.8691 | 4216.965 | 0.60334 | 28143.791 | 51525.7882 | 573.7492 | 1050.4229
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.2318 | 3.7518 | 0.20182 | 4 | 23017.3322 | 40492.3335 | 469.2395 | 825.491 | 119.1553 | 0 | 94.994 | 995302.2402 | 39933.8426 | 981581.2899 | 680341.4409 | 0 | 282722.7133 | 0 | 1162153.7955 | 3023685.7854 | 2063727.6791 | 9229448.7869 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 18581493.2933 | 32688758.831 | 5623.4133 | 0.80728 | 23017.3322 | 40492.3335 | 469.2395 | 825.491
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.8339 | 4.78 | 0.26733 | 4 | 19161.5025 | 32354.3394 | 390.6331 | 659.587 | 119.5269 | 0 | 92.3974 | 1182324.1316 | 47527.4161 | 1191137.5178 | 857683.771 | 0 | 317283.8996 | 0 | 1402423.1271 | 3648817.3001 | 2490392.783 | 11137589.9462 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 20489634.4526 | 34596899.9903 | 7498.9421 | 1.0693 | 19161.5025 | 32354.3394 | 390.6331 | 659.587
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4681 | 6.039 | 0.35035 | 4 | 16212.1153 | 26278.7201 | 330.5059 | 535.7273 | 119.8144 | 0 | 119.8565 | 1395860.9442 | 56175.1794 | 1435841.9541 | 1074822.6942 | 0 | 353217.6507 | 0 | 1683208.1848 | 4379362.4234 | 2989004.8409 | 13367493.8717 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 22719538.378 | 36826803.9158 | 10000 | 1.4014 | 16212.1153 | 26278.7201 | 330.5059 | 535.7273
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.3204 | 7.5706 | 0.45448 | 4 | 13925.899 | 21686.0869 | 283.8983 | 442.1002 | 120.0385 | 0 | 138.2243 | 1638711.7245 | 65984.9426 | 1720157.5758 | 1338975.3038 | 0 | 390376.3515 | 0 | 2010140.3003 | 5229972.7249 | 3569563.85 | 15963882.7734 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 25315927.2798 | 39423192.8175 | 13335.2143 | 1.8179 | 13925.899 | 21686.0869 | 283.8983 | 442.1002
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.4982 | 9.3988 | 0.58277 | 4 | 12135.6309 | 18187.4398 | 247.4013 | 370.7756 | 120.2116 | 0 | 131.3793 | 1910501.1053 | 76935.5455 | 2044890.7375 | 1654465.7451 | 0 | 427369.4224 | 0 | 2384523.3968 | 6204040.7454 | 4234385.289 | 18937111.9871 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28289156.4934 | 42396422.0312 | 17782.7941 | 2.3311 | 12135.6309 | 18187.4398 | 247.4013 | 370.7756
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9381 | 11.5079 | 0.73617 | 4 | 10726.0055 | 15516.7426 | 218.6641 | 316.3298 | 120.3358 | 0 | 148.6458 | 2205438.9119 | 88783.748 | 2404196.6481 | 2018528.4594 | 0 | 461277.4123 | 0 | 2799507.8201 | 7283745.0899 | 4971305.6899 | 22232783.7797 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 31584828.2861 | 45692093.8238 | 23713.7371 | 2.9447 | 10726.0055 | 15516.7426 | 218.6641 | 316.3298
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.3077 | 13.8195 | 0.91157 | 4 | 9615.8206 | 13484.785 | 196.0315 | 274.9056 | 120.4037 | 0 | 155.9269 | 2510821.2306 | 101004.901 | 2783214.9498 | 2417984.4451 | 0 | 487804.5288 | 0 | 3237323.7215 | 8422852.2571 | 5748769.7377 | 25709775.7716 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 35061820.278 | 49169085.8157 | 31622.7766 | 3.6463 | 9615.8206 | 13484.785 | 196.0315 | 274.9056
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.0823 | 16.2103 | 1.1015 | 4 | 8745.292 | 11947.0884 | 178.2846 | 243.5576 | 120.4081 | 0 | 189.0739 | 2810748.8417 | 112947.0583 | 3162164.5006 | 2832046.7335 | 0 | 503382.6381 | 0 | 3674303.0111 | 9559782.7317 | 6524748.1483 | 29180123.6633 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 38532168.1696 | 52639433.7073 | 42169.6503 | 4.406 | 8745.292 | 11947.0884 | 178.2846 | 243.5576
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.6501 | 18.5389 | 1.2955 | 4 | 8067.1001 | 10789.4576 | 164.4587 | 219.9577 | 120.3523 | 0 | 177.3232 | 3089813.9268 | 123988.9432 | 3520751.6746 | 3236699.6735 | 0 | 506316.6841 | 0 | 4086252.6518 | 10631591.1944 | 7256279.4475 | 32451694.1959 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 41803738.7023 | 55911004.24 | 56234.1325 | 5.182 | 8067.1001 | 10789.4576 | 164.4587 | 219.9577
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.5056 | 20.6917 | 1.483 | 4 | 7542.2182 | 9920.3084 | 153.7583 | 202.2389 | 120.2512 | 0 | 189.2148 | 3337869.0356 | 133734.8672 | 3844478.2674 | 3612396.1982 | 0 | 497700.3546 | 0 | 4456209.7019 | 11594143.5502 | 7913241.2088 | 35389773.1838 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 44741817.6902 | 58849083.2279 | 74989.4209 | 5.9322 | 7542.2182 | 9920.3084 | 153.7583 | 202.2389
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.307 | 22.5964 | 1.6557 | 4 | 7138.3535 | 9268.4614 | 145.525 | 188.9501 | 120.1242 | 0 | 207.9198 | 3550193.1682 | 142016.569 | 4125443.6326 | 3946307.8246 | 0 | 480369.9928 | 0 | 4775289.163 | 12424322.8557 | 8479855.6433 | 37923798.8493 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 47275843.3557 | 61383108.8934 | 100000 | 6.6228 | 7138.3535 | 9268.4614 | 145.525 | 188.9501
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.8586 | 24.2157 | 1.8078 | 4 | 6829.1222 | 8780.0299 | 139.2209 | 178.9928 | 119.99 | 0 | 202.8734 | 3725858.6302 | 148820.8288 | 4360709.0472 | 4231498.3604 | 0 | 457537.252 | 0 | 5040525.4062 | 13114413.1531 | 8950856.4512 | 40030219.129 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 49382263.6353 | 63489529.173 | 133352.1432 | 7.2311 | 6829.1222 | 8780.0299 | 139.2209 | 178.9928
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1339 | 25.5506 | 1.9371 | 4 | 6593.288 | 8413.9986 | 134.4131 | 171.5307 | 119.8618 | 0 | 202.7606 | 3867562.8062 | 154276.1748 | 4552386.9491 | 4467995.0856 | 0 | 432360.7854 | 0 | 5255086.9024 | 13672658.1536 | 9331870.1348 | 41734196.9919 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 51086241.4983 | 65193507.036 | 177827.941 | 7.7482 | 6593.288 | 8413.9986 | 134.4131 | 171.5307
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.1887 | 26.618 | 2.0434 | 4 | 6414.0113 | 8139.9916 | 130.7583 | 165.9447 | 119.7481 | 0 | 192.3332 | 3978932.7864 | 158540.4068 | 4704284.9973 | 4657875.5554 | 0 | 407122.3473 | 0 | 5423634.8764 | 14111185.4078 | 9631173.9967 | 43072750.374 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 52424794.8804 | 66532060.4181 | 237137.3706 | 8.1735 | 6414.0113 | 8139.9916 | 130.7583 | 165.9447
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.4734 | 27.5172 | 2.1333 | 4 | 6274.6825 | 7927.9287 | 127.9179 | 161.6216 | 119.6449 | 0 | 206.4722 | 4071453.3389 | 162066.4103 | 4831337.8271 | 4818380.3803 | 0 | 384324.6453 | 0 | 5564349.4147 | 14477295.7721 | 9881051.8431 | 44190259.6318 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 53542304.1381 | 67649569.6758 | 316227.766 | 8.5331 | 6274.6825 | 7927.9287 | 127.9179 | 161.6216
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5823 | 28.1662 | 2.2005 | 4 | 6172.7859 | 7775.5022 | 125.8406 | 158.5141 | 119.566 | 0 | 188.5556 | 4137514.5798 | 164574.2566 | 4922553.7279 | 4934568.7123 | 0 | 363790.3863 | 0 | 5663970.6486 | 14736489.7874 | 10057957.0845 | 44981419.1834 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 54333463.6897 | 68440729.2274 | 421696.5034 | 8.8021 | 6172.7859 | 7775.5022 | 125.8406 | 158.5141
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9787 | 28.6645 | 2.2529 | 4 | 6095.8221 | 7661.2497 | 124.2716 | 156.1849 | 119.5031 | 0 | 196.7819 | 4187834.8702 | 166478.9031 | 4992318.5137 | 5023974.5275 | 0 | 346325.7575 | 0 | 5739603.7031 | 14933271.4808 | 10192264.6337 | 45582072.3896 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 54934116.896 | 69041382.4337 | 562341.3252 | 9.0118 | 6095.8221 | 7661.2497 | 124.2716 | 156.1849
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.5844 | 29.4145 | 2.3152 | 4 | 6037.278 | 7560.6144 | 123.0781 | 154.1334 | 119.4132 | 0 | 215.2388 | 4263138.7277 | 169330.1978 | 5096867.4362 | 5158516.4372 | 0 | 344105.8056 | 0 | 5862463.8558 | 15252928.396 | 10410437.0466 | 46557787.903 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 55909832.4094 | 70017097.9471 | 749894.2093 | 9.2608 | 6037.278 | 7560.6144 | 123.0781 | 154.1334
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.0756 | 29.7248 | 2.3478 | 4 | 5992.8872 | 7495.0497 | 122.1731 | 152.7967 | 119.3777 | 0 | 194.8214 | 4294147.8563 | 170504.7456 | 5139967.1739 | 5214170.8875 | 0 | 333014.6014 | 0 | 5909204.0532 | 15374536.8021 | 10493437.2826 | 46928983.4026 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 56281027.9089 | 70388293.4466 | 1000000 | 9.3913 | 5992.8872 | 7495.0497 | 122.1731 | 152.7967
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.201 | 29.9586 | 2.3726 | 4 | 5959.4693 | 7445.9173 | 121.4918 | 151.7951 | 119.3506 | 0 | 184.0293 | 4317434.9189 | 171385.8045 | 5172387.8884 | 5256144.4758 | 0 | 324157.071 | 0 | 5944188.9618 | 15465560.3579 | 10555562.7298 | 47206822.2081 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 56558866.7144 | 70666132.2521 | 1333521.4322 | 9.4906 | 5959.4693 | 7445.9173 | 121.4918 | 151.7951
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.0487 | 30.1346 | 2.3915 | 4 | 5934.3332 | 7409.0899 | 120.9794 | 151.0443 | 119.33 | 0 | 185.5035 | 4334911.5868 | 172046.4618 | 5196749.8014 | 5287746.2875 | 0 | 317190.4537 | 0 | 5970371.3906 | 15533681.6667 | 10602056.9228 | 47414754.5712 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 56766799.0775 | 70874064.6153 | 1778279.41 | 9.5658 | 5934.3332 | 7409.0899 | 120.9794 | 151.0443
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1472 | 29.9474 | 2.3879 | 4 | 5911.8692 | 7388.8389 | 120.5214 | 150.6315 | 119.3517 | 0 | 173.882 | 4316312.3017 | 171343.1077 | 5170831.4056 | 5254134.8785 | 0 | 299284.6313 | 0 | 5932643.4667 | 15435521.3477 | 10535060.4881 | 47115131.6273 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 56467176.1336 | 70574441.6713 | 2371373.7057 | 9.5515 | 5911.8692 | 7388.8389 | 120.5214 | 150.6315
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1593 | 30.3648 | 2.4163 | 4 | 5901.2456 | 7360.8309 | 120.3049 | 150.0605 | 119.3028 | 0 | 195.4371 | 4357722.6779 | 172908.0328 | 5228587.3739 | 5329125.1359 | 0 | 307555.3885 | 0 | 6004400.4575 | 15622218.3185 | 10662485.0068 | 47685002.3917 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57037046.8981 | 71144312.4358 | 3162277.6602 | 9.6653 | 5901.2456 | 7360.8309 | 120.3049 | 150.0605
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5218 | 30.4399 | 2.4244 | 4 | 5890.5868 | 7345.292 | 120.0876 | 149.7437 | 119.2939 | 0 | 236.0472 | 4365148.9478 | 173188.341 | 5238961.9478 | 5342628.3184 | 0 | 304377.0129 | 0 | 6015478.7815 | 15651041.8451 | 10682157.656 | 47772982.8506 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57125027.3569 | 71232292.8946 | 4216965.0343 | 9.6977 | 5890.5868 | 7345.292 | 120.0876 | 149.7437
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7802 | 30.4934 | 2.4303 | 4 | 5882.5854 | 7333.7426 | 119.9245 | 149.5083 | 119.2875 | 0 | 222.2116 | 4370435.1533 | 173387.8141 | 5246349.8321 | 5352250.071 | 0 | 301861.6977 | 0 | 6023270.9816 | 15671315.5514 | 10695994.8772 | 47834865.9785 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57186910.4848 | 71294176.0225 | 5623413.2519 | 9.7214 | 5882.5854 | 7333.7426 | 119.9245 | 149.5083
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.9971 | 30.5383 | 2.4351 | 4 | 5876.5804 | 7324.913 | 119.802 | 149.3283 | 119.2822 | 0 | 226.0858 | 4374868.6669 | 173555.0809 | 5252547.7344 | 5360325.6305 | 0 | 300110.4446 | 0 | 6029948.9474 | 15688690.2485 | 10707853.4649 | 47887900.2182 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57239944.7246 | 71347210.2623 | 7498942.0933 | 9.7403 | 5876.5804 | 7324.913 | 119.802 | 149.3283
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.146 | 30.5691 | 2.4385 | 4 | 5872.0745 | 7318.3939 | 119.7102 | 149.1954 | 119.2785 | 0 | 234.0753 | 4377910.7568 | 173669.8312 | 5256801.544 | 5365870.2004 | 0 | 298690.709 | 0 | 6034447.7861 | 15700395.3041 | 10715842.4059 | 47923628.5375 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57275673.0438 | 71382938.5815 | 10000000 | 9.7539 | 5872.0745 | 7318.3939 | 119.7102 | 149.1954
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3228 | [19 empty] | 100 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5865 | [19 empty] | 133.3521 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2105 | [19 empty] | 177.8279 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.77197 | 0.10412 | 0.0005271 | 4 | 4937313.4359 | 11870212.891 | 100653.8126 | 241990.3454 | 91.051 | 0 | 56.3014 | 68443.099 | 2228.5521 | 56965.3184 | 47704.8859 | 0 | 48552.8713 | 0 | 87318.9434 | 227185.9792 | 155059.099 | 693458.7484 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10409850.2183 | 25027201.5051 | 237.1374 | 0.0021084 | 4937313.4359 | 11870212.891 | 100653.8126 | 241990.3454
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2083 | 0.19723 | 0.003159 | 4 | 853417.029 | 2010202.8291 | 17398.0605 | 40980.7037 | 101.336 | 0 | 60.1302 | 114757.7146 | 4037.0091 | 94218.1977 | 64304.5079 | 0 | 67355.0324 | 0 | 134422.2601 | 349739.1469 | 238704.1542 | 1067538.0229 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10783929.4929 | 25401280.7796 | 316.2278 | 0.012636 | 853417.029 | 2010202.8291 | 17398.0605 | 40980.7037
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.3141 | 0.0074897 | 4 | 373638.3771 | 861554.9408 | 7617.1237 | 17563.9628 | 107.6204 | 0 | 290.8412 | 164983.4093 | 6081.1937 | 136076.582 | 84512.7041 | 0 | 85327.6086 | 0 | 186022.7841 | 483993.1258 | 330335.2534 | 1477332.6612 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11193724.1311 | 25811075.4179 | 421.6965 | 0.029959 | 373638.3771 | 861554.9408 | 7617.1237 | 17563.9628
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.45697 | 0.013846 | 4 | 210227.9102 | 474147.2837 | 4285.7803 | 9666.1337 | 111.792 | 0 | 413.9269 | 219469.1497 | 8342.7281 | 183112.2825 | 108850.9254 | 0 | 102460.742 | 0 | 242671.9728 | 631382.6943 | 430931.6625 | 1927222.1571 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11643613.627 | 26260964.9138 | 562.3413 | 0.055386 | 210227.9102 | 474147.2837 | 4285.7803 | 9666.1337
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1295 | 0.63776 | 0.02273 | 4 | 133809.1307 | 294578.7904 | 2727.8801 | 6005.3871 | 114.8226 | 0 | 563.7925 | 281587.5687 | 10945.3578 | 238556.8183 | 139426.8491 | 0 | 120403.2594 | 0 | 308458.7428 | 802546.3751 | 547754.3917 | 2449679.3628 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12166070.8328 | 26783422.1195 | 749.8942 | 0.090921 | 133809.1307 | 294578.7904 | 2727.8801 | 6005.3871
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 0.87857 | 0.034932 | 4 | 91713.6387 | 196327.4814 | 1869.7066 | 4002.4013 | 117.1717 | 0 | 67.2803 | 356661.2721 | 14106.1148 | 307723.3124 | 180134.1898 | 0 | 141763.441 | 0 | 390151.4488 | 1015094.0386 | 692822.5395 | 3098456.357 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12814847.8269 | 27432199.1137 | 1000 | 0.13973 | 91713.6387 | 196327.4814 | 1869.7066 | 4002.4013
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4421 | 1.1804 | 0.051245 | 4 | 66208.4808 | 137520.0483 | 1349.7494 | 2803.5322 | 118.8981 | 0 | 70.5361 | 442391.6174 | 17717.706 | 389243.0348 | 230956.3997 | 0 | 164321.5822 | 0 | 485405.8326 | 1262926.4061 | 861973.2227 | 3854935.8015 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 13571327.2714 | 28188678.5582 | 1333.5214 | 0.20498 | 66208.4808 | 137520.0483 | 1349.7494 | 2803.5322
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0059 | 1.5475 | 0.072522 | 4 | 49749.4389 | 100138.7039 | 1014.2096 | 2041.4629 | 120.1286 | 0 | 90.6341 | 538079.0007 | 21740.7077 | 482991.4585 | 292677.6874 | 0 | 186941.7156 | 0 | 593747.9223 | 1544810.2993 | 1054364.7719 | 4715353.5633 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 14431745.0333 | 29049096.32 | 1778.2794 | 0.29009 | 49749.4389 | 100138.7039 | 1014.2096 | 2041.4629
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3495 | 2.1017 | 0.10223 | 4 | 38334.4964 | 74081.7986 | 781.5006 | 1510.2577 | 121.3041 | 0 | 100.7143 | 670794.3087 | 27326.4763 | 616500.9647 | 385832.5864 | 0 | 223470.7075 | 0 | 750330.767 | 1952206.7417 | 1332421.215 | 5958883.7673 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 15675275.2372 | 30292626.5239 | 2371.3737 | 0.40891 | 38334.4964 | 74081.7986 | 781.5006 | 1510.2577
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7607 | 2.6716 | 0.13898 | 4 | 30319.2437 | 56612.4707 | 618.0988 | 1154.1218 | 122.0117 | 0 | 83.6956 | 796595.4104 | 32605.7232 | 746593.7359 | 481709.3857 | 0 | 247495.043 | 0 | 898949.7262 | 2338882.7877 | 1596335.5619 | 7139167.3739 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 16855558.8439 | 31472910.1306 | 3162.2777 | 0.55594 | 30319.2437 | 56612.4707 | 618.0988 | 1154.1218
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0056 | 3.438 | 0.18734 | 4 | 24521.7389 | 44028.009 | 499.9088 | 897.5705 | 122.6042 | 0 | 80.6435 | 953671.399 | 39176.224 | 913122.6027 | 610091.6888 | 0 | 279765.193 | 0 | 1090372.5719 | 2836925.7659 | 1936260.1282 | 8659385.5734 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 18375777.0433 | 32993128.33 | 4216.965 | 0.74937 | 24521.7389 | 44028.009 | 499.9088 | 897.5705
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0929 | 4.4037 | 0.2499 | 4 | 20207.2542 | 34830.2843 | 411.9522 | 710.0625 | 123.0672 | 0 | 106.9629 | 1137515.8342 | 46846.9438 | 1112769.1214 | 771929.5382 | 0 | 315554.9498 | 0 | 1320000.3911 | 3434370.2483 | 2344028.2637 | 10483015.2904 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 20199406.7604 | 34816758.0471 | 5623.4133 | 0.99961 | 20207.2542 | 34830.2843 | 411.9522 | 710.0625
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.1159 | 5.5912 | 0.32973 | 4 | 16935.1289 | 28017.8147 | 345.2455 | 571.181 | 123.4237 | 0 | 135.5357 | 1348040.3026 | 55611.5969 | 1346628.5761 | 971361.6004 | 0 | 352921.5254 | 0 | 1589079.8046 | 4134459.6864 | 2821853.6906 | 12619956.7829 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 22336348.2528 | 36953699.5396 | 7498.9421 | 1.3189 | 16935.1289 | 28017.8147 | 345.2455 | 571.181
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.2649 | 7.0453 | 0.43062 | 4 | 14418.486 | 22904.6176 | 293.9403 | 466.9416 | 123.701 | 0 | 128.5563 | 1588649.3685 | 65601.7176 | 1619855.757 | 1215532.8535 | 0 | 391921.4732 | 0 | 1903808.8563 | 4953320.1191 | 3380742.7618 | 15119432.9071 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 24835824.377 | 39453175.6638 | 10000 | 1.7225 | 14418.486 | 22904.6176 | 293.9403 | 466.9416
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.7071 | 8.8054 | 0.5565 | 4 | 12458.6519 | 19025.2732 | 253.9865 | 387.8559 | 123.9172 | 0 | 97.6337 | 1861210.9763 | 76888.0233 | 1935934.2788 | 1511078.6443 | 0 | 431869.6008 | 0 | 2268622.7942 | 5902491.1519 | 4028571.4953 | 18016666.9649 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 27733058.4348 | 42350409.7215 | 13335.2143 | 2.226 | 12458.6519 | 19025.2732 | 253.9865 | 387.8559
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.5077 | 10.8862 | 0.71018 | 4 | 10919.1831 | 16064.8398 | 222.6023 | 327.5035 | 124.0812 | 0 | 137.3057 | 2163593.0582 | 89371.5375 | 2293737.3455 | 1860227.2408 | 0 | 470748.0024 | 0 | 2682294.1019 | 6978779.039 | 4763160.0937 | 21301910.4189 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31018301.8888 | 45635653.1755 | 17782.7941 | 2.8407 | 10919.1831 | 16064.8398 | 222.6023 | 327.5035
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.5077 | 13.2475 | 0.8913 | 4 | 9705.0426 | 13805.0676 | 197.8504 | 281.435 | 124.1899 | 0 | 139.6797 | 2486778.5474 | 102666.8469 | 2683592.8897 | 2256462.2852 | 0 | 504678.4059 | 0 | 3133329.8003 | 8152281.406 | 5564099.5722 | 24883889.7535 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 34600281.2235 | 49217632.5102 | 23713.7371 | 3.5652 | 9705.0426 | 13805.0676 | 197.8504 | 281.435
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.2776 | 15.7821 | 1.0945 | 4 | 8748.9357 | 12087.7433 | 178.3589 | 246.425 | 124.2333 | 0 | 150.8818 | 2815057.5479 | 116110.7017 | 3086947.0348 | 2682617.7903 | 0 | 528922.6913 | 0 | 3599565.7487 | 9365331.7057 | 6392031.3274 | 28586584.5477 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 38302976.0177 | 52920327.3044 | 31622.7766 | 4.378 | 8748.9357 | 12087.7433 | 178.3589 | 246.425
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.2586 | 18.3511 | 1.3102 | 4 | 8000.1674 | 10789.2679 | 163.0942 | 219.9538 | 124.2068 | 0 | 173.2324 | 3131641.0454 | 128998.8774 | 3482851.055 | 3116059.5253 | 0 | 540487.5676 | 0 | 4056014.8476 | 10552918.6303 | 7202583.806 | 32211555.3545 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 41927946.8245 | 56545298.1112 | 42169.6503 | 5.2409 | 8000.1674 | 10789.2679 | 163.0942 | 219.9538
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.8387 | 20.8062 | 1.5262 | 4 | 7417.6838 | 9812.0277 | 151.2195 | 200.0315 | 124.1193 | 0 | 192.4136 | 3421264.3863 | 140706.0678 | 3851090.4065 | 3532269.7661 | 0 | 538456.8507 | 0 | 4478677.1162 | 11652599.1533 | 7953138.3591 | 35568202.1058 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 45284593.5758 | 59901944.8625 | 56234.1325 | 6.105 | 7417.6838 | 9812.0277 | 151.2195 | 200.0315
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.5487 | 23.0378 | 1.7313 | 4 | 6967.4287 | 9078.1453 | 142.0405 | 185.0703 | 123.9905 | 0 | 176.5371 | 3674910.9484 | 150879.8418 | 4178507.3916 | 3912683.3464 | 0 | 524737.9619 | 0 | 4852270.6012 | 12624612.7667 | 8616557.6231 | 38535160.4813 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 48251551.9512 | 62868903.238 | 74989.4209 | 6.9253 | 6967.4287 | 9078.1453 | 142.0405 | 185.0703
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.1138 | 24.9859 | 1.9171 | 4 | 6621.3755 | 8527.5445 | 134.9857 | 173.8455 | 123.8416 | 0 | 186.906 | 3889428.4464 | 159411.0395 | 4459327.2038 | 4245623.4708 | 0 | 502876.9681 | 0 | 5170100.1801 | 13451540.1354 | 9180952.5439 | 41059259.988 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 50775651.4579 | 65393002.7447 | 100000 | 7.6684 | 6621.3755 | 8527.5445 | 134.9857 | 173.8455
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.383 | 26.6232 | 2.0786 | 4 | 6356.5379 | 8114.6188 | 129.5866 | 165.4275 | 123.6913 | 0 | 195.2231 | 4065168.9511 | 166347.2666 | 4692103.1714 | 4526704.901 | 0 | 476295.7535 | 0 | 5431381.817 | 14131341.3582 | 9644930.847 | 43134274.0659 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 52850665.5358 | 67468016.8225 | 133352.1432 | 8.3144 | 6356.5379 | 8114.6188 | 129.5866 | 165.4275
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3682 | 27.9596 | 2.2143 | 4 | 6154.6096 | 7804.9785 | 125.47 | 159.115 | 123.5521 | 0 | 195.8575 | 4205687.0035 | 171855.7333 | 4880067.0074 | 4757048.966 | 0 | 448190.5217 | 0 | 5640511.2004 | 14675453.1155 | 10016298.3017 | 44795111.8494 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 54511503.3193 | 69128854.6061 | 177827.941 | 8.857 | 6154.6096 | 7804.9785 | 125.47 | 159.115
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.1593 | 29.0212 | 2.3249 | 4 | 6001.1113 | 7572.9431 | 122.3408 | 154.3847 | 123.4311 | 0 | 196.0602 | 4315529.4576 | 176136.6232 | 5028184.3572 | 4940692.9444 | 0 | 420811.9737 | 0 | 5803728.5888 | 15100111.2798 | 10306136.2247 | 46091331.4493 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 55807722.9193 | 70425074.206 | 237137.3706 | 9.2996 | 6001.1113 | 7572.9431 | 122.3408 | 154.3847
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2324 | 29.918 | 2.4184 | 4 | 5881.4518 | 7392.5292 | 119.9014 | 150.7067 | 123.3218 | 0 | 191.5436 | 4407112.9332 | 179688.2054 | 5152501.0392 | 5096280.6413 | 0 | 396496.8586 | 0 | 5940511.0743 | 15455991.249 | 10549031.6163 | 47177613.6173 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 56894005.0872 | 71511356.3739 | 316227.766 | 9.6735 | 5881.4518 | 7392.5292 | 119.9014 | 150.7067
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8 | 30.9193 | 2.5093 | 4 | 5794.0614 | 7250.377 | 118.1198 | 147.8087 | 123.1976 | 0 | 201.6386 | 4508234.1439 | 183596.7834 | 5290468.0193 | 5270357.6423 | 0 | 386954.856 | 0 | 6099448.4635 | 15869513.7332 | 10831269.2088 | 48439842.8504 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 58156234.3203 | 72773585.6071 | 421696.5034 | 10.0372 | 5794.0614 | 7250.377 | 118.1198 | 147.8087
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3554 | 31.4804 | 2.5679 | 4 | 5727.1418 | 7150.2094 | 116.7555 | 145.7667 | 123.1335 | 0 | 211.125 | 4564546.2298 | 185776.1799 | 5367373.2777 | 5367828.018 | 0 | 370847.7553 | 0 | 6183984.8696 | 16089460.1211 | 10981387.138 | 49111203.5893 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 58827595.0593 | 73444946.346 | 562341.3252 | 10.2717 | 5727.1418 | 7150.2094 | 116.7555 | 145.7667
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.1802 | 31.88 | 2.6114 | 4 | 5676.6461 | 7076.0217 | 115.7261 | 144.2543 | 123.0868 | 0 | 189.2317 | 4604419.4972 | 187316.1615 | 5421983.77 | 5437330.2951 | 0 | 356590.1753 | 0 | 6242979.5606 | 16242952.2056 | 11086148.6396 | 49579720.3049 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59296111.7748 | 73913463.0616 | 749894.2093 | 10.4456 | 5676.6461 | 7076.0217 | 115.7261 | 144.2543
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5755 | 32.1849 | 2.6448 | 4 | 5638.5914 | 7020.3055 | 114.9503 | 143.1184 | 123.0506 | 0 | 217.2824 | 4634721.762 | 188484.7072 | 5463572.472 | 5490420.2105 | 0 | 345172.7051 | 0 | 6287725.0241 | 16359370.7231 | 11165606.6699 | 49935074.2739 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59651465.7439 | 74268817.0306 | 1000000 | 10.5791 | 5638.5914 | 7020.3055 | 114.9503 | 143.1184
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.6233 | 32.4135 | 2.6701 | 4 | 5609.943 | 6978.5695 | 114.3663 | 142.2676 | 123.0232 | 0 | 211.1756 | 4657369.9775 | 189357.0668 | 5494705.6276 | 5530254.0006 | 0 | 336067.2306 | 0 | 6321024.0222 | 16446007.8855 | 11224738.3135 | 50199524.1245 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59915915.5944 | 74533266.8811 | 1333521.4322 | 10.6803 | 5609.943 | 6978.5695 | 114.3663 | 142.2676
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4197 | 32.5871 | 2.6893 | 4 | 5588.3943 | 6947.2255 | 113.927 | 141.6286 | 123.0022 | 0 | 195.4215 | 4674525.2329 | 190017.2641 | 5518316.1218 | 5560514.643 | 0 | 328987.0491 | 0 | 6346220.5213 | 16511564.0075 | 11269481.7138 | 50399626.5536 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60116018.0235 | 74733369.3103 | 1778279.41 | 10.7573 | 5588.3943 | 6947.2255 | 113.927 | 141.6286
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9922 | 32.7119 | 2.7035 | 4 | 5572.1987 | 6923.8925 | 113.5968 | 141.1529 | 122.987 | 0 | 208.9336 | 4686846.4858 | 190491.7952 | 5535269.4104 | 5582385.6852 | 0 | 323308.292 | 0 | 6364137.6508 | 16558180.7032 | 11301298.5665 | 50541918.5891 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60258310.059 | 74875661.3457 | 2371373.7057 | 10.8141 | 5572.1987 | 6923.8925 | 113.5968 | 141.1529
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.4518 | 31.9391 | 2.661 | 4 | 5558.3073 | 6931.6096 | 113.3136 | 141.3102 | 123.0791 | 0 | 224.6772 | 4610283.3445 | 187541.4822 | 5430052.1183 | 5447640.5757 | 0 | 288920.6905 | 0 | 6226130.9024 | 16199115.4529 | 11056229.1551 | 49445913.7215 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59162305.1915 | 73779656.4782 | 3162277.6602 | 10.6439 | 5558.3073 | 6931.6096 | 113.3136 | 141.3102
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7519 | 32.4414 | 2.6964 | 4 | 5547.9909 | 6903.2621 | 113.1033 | 140.7323 | 123.0195 | 0 | 221.8162 | 4660119.0493 | 189462.4362 | 5498500.5461 | 5535125.4775 | 0 | 299440.9098 | 0 | 6311232.8833 | 16420533.3506 | 11207351.42 | 50121766.0727 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59838157.5426 | 74455508.8294 | 4216965.0343 | 10.7856 | 5547.9909 | 6903.2621 | 113.1033 | 140.7323
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.1458 | 33.1806 | 2.744 | 4 | 5544.1616 | 6875.9238 | 113.0252 | 140.175 | 122.9295 | 0 | 179.0112 | 4732987.2823 | 192267.306 | 5598844.7644 | 5664688.4026 | 0 | 321332.3809 | 0 | 6438946.8531 | 16752818.9022 | 11434143.1368 | 51136029.0284 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60852420.4984 | 75469771.7851 | 5623413.2519 | 10.9759 | 5544.1616 | 6875.9238 | 113.0252 | 140.175
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.2102 | 32.9771 | 2.7335 | 4 | 5538.8902 | 6875.7826 | 112.9178 | 140.1721 | 122.9545 | 0 | 198.0918 | 4712980.0181 | 191497.6944 | 5571261.108 | 5628941.5188 | 0 | 311438.8437 | 0 | 6402286.4814 | 16657436.135 | 11369042.4382 | 50844884.2377 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60561275.7076 | 75178626.9944 | 7498942.0933 | 10.9338 | 5538.8902 | 6875.7826 | 112.9178 | 140.1721
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3493 | 33.0073 | 2.7369 | 4 | 5535.0281 | 6870.232 | 112.839 | 140.059 | 122.9508 | 0 | 208.2149 | 4715956.7238 | 191612.1963 | 5575364.2475 | 5634256.1685 | 0 | 310004.2714 | 0 | 6406605.5069 | 16668673.3535 | 11376712.0707 | 50879184.5385 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60595576.0084 | 75212927.2952 | 10000000 | 10.9477 | 5535.0281 | 6870.232 | 112.839 | 140.059
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3318 | [19 empty] | 100 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4507 | [19 empty] | 133.3521 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8644 | [19 empty] | 177.8279 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | 0.14387 | 0.0013547 | 4 | 2021320.3609 | 4814483.5527 | 41207.3496 | 98149.7593 | 97.859 | 0 | 51.3333 | 90086.7173 | 3084.9616 | 73394.8708 | 54462.5294 | 0 | 58756.6368 | 0 | 109116.4292 | 283898.5659 | 193766.6048 | 866567.3158 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 10953165.8402 | 26088807.0032 | 237.1374 | 0.0054188 | 2021320.3609 | 4814483.5527 | 41207.3496 | 98149.7593
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3936 | 0.24851 | 0.0048726 | 4 | 582221.7567 | 1358797.0463 | 11869.378 | 27700.9157 | 106.5169 | 0 | 50.9099 | 139320.2812 | 5086.9636 | 112916.875 | 72347.3037 | 0 | 77478.0073 | 0 | 158788.278 | 413134.5275 | 281972.8041 | 1261045.0405 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11347643.5649 | 26483284.7278 | 316.2278 | 0.01949 | 582221.7567 | 1358797.0463 | 11869.378 | 27700.9157
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.35156 | 0.01023 | 4 | 285558.5713 | 655435.8558 | 5821.4977 | 13361.9465 | 111.1974 | 0 | 313.3166 | 182329.6328 | 6890.9103 | 148522.3249 | 89612.4544 | 0 | 88799.0588 | 0 | 201300.2086 | 523741.8505 | 357464.5748 | 1598661.015 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11685259.5394 | 26820900.7024 | 421.6965 | 0.040921 | 285558.5713 | 655435.8558 | 5821.4977 | 13361.9465
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4293 | 0.49776 | 0.017941 | 4 | 169042.1117 | 379950.1697 | 3446.1521 | 7745.7981 | 115.1727 | 0 | 428.7186 | 237521.7447 | 9242.5517 | 195603.3021 | 113851.0245 | 0 | 103904.2233 | 0 | 257447.9101 | 669826.6521 | 457170.4536 | 2044567.8621 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12131166.3865 | 27266807.5495 | 562.3413 | 0.071764 | 169042.1117 | 379950.1697 | 3446.1521 | 7745.7981
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2073 | 0.68868 | 0.028617 | 4 | 110688.6343 | 242913.6211 | 2256.5375 | 4952.1227 | 118.2356 | 0 | 581.091 | 302819.9459 | 12051.72 | 253062.6326 | 145366.4062 | 0 | 120922.6542 | 0 | 325347.11 | 846486.4422 | 577744.3904 | 2583801.3014 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12670399.8258 | 27806040.9888 | 749.8942 | 0.11447 | 110688.6343 | 242913.6211 | 2256.5375 | 4952.1227
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.95067 | 0.043304 | 4 | 77144.8387 | 164525.5612 | 1572.7019 | 3354.0761 | 120.698 | 0 | 85.7262 | 384155.2609 | 15566.1987 | 326955.3116 | 188410.5722 | 0 | 142635.3025 | 0 | 412511.8319 | 1073271.1689 | 732529.6263 | 3276035.273 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 13362633.7974 | 28498274.9604 | 1000 | 0.17321 | 77144.8387 | 164525.5612 | 1572.7019 | 3354.0761
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6636 | 1.2971 | 0.063103 | 4 | 56328.9517 | 116292.6403 | 1148.3419 | 2370.7828 | 122.5766 | 0 | 92.8288 | 481925.1552 | 19794.7531 | 418671.8438 | 245222.4188 | 0 | 168337.3629 | 0 | 520241.0982 | 1353560.6213 | 923832.9369 | 4131586.1902 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 14218184.7146 | 29353825.8775 | 1333.5214 | 0.25241 | 56328.9517 | 116292.6403 | 1148.3419 | 2370.7828
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5468 | 1.7635 | 0.089522 | 4 | 42731.3766 | 84999.4583 | 871.1369 | 1732.8289 | 123.9637 | 0 | 91.5694 | 601694.5611 | 24960.1563 | 534787.7962 | 321798.6661 | 0 | 200489.9957 | 0 | 656655.1584 | 1708482.0237 | 1166074.087 | 5214942.4445 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 15301540.9689 | 30437182.1318 | 1778.2794 | 0.35809 | 42731.3766 | 84999.4583 | 871.1369 | 1732.8289
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.048 | 2.3888 | 0.12565 | 4 | 33156.5089 | 63271.6033 | 675.9403 | 1289.8772 | 125.1737 | 0 | 91.3885 | 748660.6081 | 31308.6756 | 681194.6679 | 423416.4653 | 0 | 239119.3679 | 0 | 828242.9161 | 2154918.1717 | 1470775.9313 | 6577636.804 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 16664235.3284 | 31799876.4914 | 2371.3737 | 0.50259 | 33156.5089 | 63271.6033 | 675.9403 | 1289.8772
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0106 | 3.1275 | 0.17163 | 4 | 26467.7646 | 48514.3996 | 539.5812 | 989.0317 | 125.9506 | 0 | 101.8538 | 907899.6935 | 38158.158 | 844599.9451 | 543925.7907 | 0 | 275559.0627 | 0 | 1017955.6335 | 2648511.7469 | 1807663.6887 | 8084273.7189 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 18170872.2433 | 33306513.4063 | 3162.2777 | 0.68653 | 26467.7646 | 48514.3996 | 539.5812 | 989.0317
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5844 | 4.0193 | 0.2306 | 4 | 21561.4194 | 37970.2379 | 439.5587 | 774.0747 | 126.5232 | 0 | 106.2061 | 1085943.6618 | 45798.5008 | 1031910.7454 | 689644.5821 | 0 | 311392.6747 | 0 | 1234229.1642 | 3211211.1101 | 2191717.5665 | 9801848.0055 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 19888446.5299 | 35024087.6929 | 4216.965 | 0.92241 | 21561.4194 | 37970.2379 | 439.5587 | 774.0747
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.0297 | 5.1291 | 0.30639 | 4 | 17887.2467 | 30237.3751 | 364.6557 | 616.4298 | 126.9669 | 0 | 91.786 | 1291894.4419 | 54611.9768 | 1253766.763 | 870970.6274 | 0 | 349893.6381 | 0 | 1490243.6044 | 3877308.1677 | 2646342.4951 | 11835031.7144 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 21921630.2388 | 37057271.4017 | 5623.4133 | 1.2255 | 17887.2467 | 30237.3751 | 364.6557 | 616.4298
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.513 | 6.4987 | 0.40297 | 4 | 15085.2985 | 24475.3713 | 307.5342 | 498.9635 | 127.3116 | 0 | 105.6188 | 1528818.5459 | 64726.6053 | 1514743.32 | 1095149.9717 | 0 | 390646.2211 | 0 | 1791693.0189 | 4661617.7085 | 3181649.8727 | 14229045.264 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 24315643.7884 | 39451284.9513 | 7498.9421 | 1.6119 | 15085.2985 | 24475.3713 | 307.5342 | 498.9635
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.2144 | 8.1729 | 0.52467 | 4 | 12919.1573 | 20131.1972 | 263.3745 | 410.4017 | 127.5805 | 0 | 128.5195 | 1799370.7752 | 76244.7516 | 1819277.7307 | 1369223.1193 | 0 | 433127.5151 | 0 | 2143925.1178 | 5578053.377 | 3807136.0474 | 17026358.4341 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 27112956.9585 | 42248598.1214 | 10000 | 2.0987 | 12919.1573 | 20131.1972 | 263.3745 | 410.4017
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.2607 | 10.1833 | 0.67548 | 4 | 11225.2311 | 16827.0117 | 228.8415 | 343.0414 | 127.7885 | 0 | 125.7237 | 2103659.0851 | 89162.3238 | 2168931.2773 | 1698318.8719 | 0 | 475794.5764 | 0 | 2548987.7924 | 6631943.3666 | 4526437.6205 | 20243234.914 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 30329833.4384 | 45465474.6014 | 13335.2143 | 2.7019 | 11225.2311 | 16827.0117 | 228.8415 | 343.0414
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6734 | 12.5339 | 0.85785 | 4 | 9890.808 | 14301.7371 | 201.6375 | 291.5603 | 127.9408 | 0 | 149.9828 | 2437926.0657 | 103307.7301 | 2560688.284 | 2083170.2766 | 0 | 516141.0167 | 0 | 3003481.0155 | 7814441.5038 | 5333516.897 | 23852672.7895 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 33939271.3139 | 49074912.4769 | 17782.7941 | 3.4314 | 9890.808 | 14301.7371 | 201.6375 | 291.5603
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.1487 | 15.144 | 1.069 | 4 | 8837.8263 | 12377.5736 | 180.171 | 252.3336 | 128.0291 | 0 | 147.1296 | 2788010.3765 | 118060.7947 | 2978881.2257 | 2510695.7175 | 0 | 548776.8765 | 0 | 3488325.7465 | 9075908.0383 | 6194493.7274 | 27703152.5031 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 37789751.0275 | 52925392.1905 | 23713.7371 | 4.2759 | 8837.8263 | 12377.5736 | 180.171 | 252.3336
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.2493 | 17.8967 | 1.3016 | 4 | 8009.6211 | 10916.6836 | 163.287 | 222.5514 | 128.0431 | 0 | 176.2689 | 3137935.7287 | 132724.1761 | 3404666.6187 | 2962390.2163 | 0 | 569890.707 | 0 | 3980966.9043 | 10357659.2763 | 7069315.2847 | 31615548.9121 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 41702147.4365 | 56837788.5994 | 31622.7766 | 5.2065 | 8009.6211 | 10916.6836 | 163.287 | 222.5514
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.3212 | 20.6218 | 1.5432 | 4 | 7362.0633 | 9814.1042 | 150.0856 | 200.0738 | 127.983 | 0 | 171.0202 | 3468130.9936 | 146462.1529 | 3813600.8056 | 3411126.5757 | 0 | 576274.9176 | 0 | 4452082.2237 | 11583404.6984 | 7905911.7218 | 35356994.0891 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 45443592.6135 | 60579233.7765 | 42169.6503 | 6.1727 | 7362.0633 | 9814.1042 | 150.0856 | 200.0738
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.854 | 23.1886 | 1.7808 | 4 | 6859.1066 | 8983.942 | 139.8322 | 183.1498 | 127.8633 | 0 | 193.0203 | 3766353.8445 | 158763.4118 | 4189193.2409 | 3835049.5785 | 0 | 568902.133 | 0 | 4882122.2614 | 12702280.6631 | 8669567.5583 | 38772232.6915 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 48858831.2159 | 63994472.3788 | 56234.1325 | 7.1232 | 6859.1066 | 8983.942 | 139.8322 | 183.1498
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4083 | 25.4917 | 2.0028 | 4 | 6470.6985 | 8359.9839 | 131.9139 | 170.4296 | 127.707 | 0 | 188.235 | 4024546.5699 | 169317.5777 | 4519366.3309 | 4216917.5706 | 0 | 550226.8458 | 0 | 5257346.209 | 13678536.4059 | 9335882.1629 | 41752139.6728 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 51838738.1972 | 66974379.3602 | 74989.4209 | 8.0113 | 6470.6985 | 8359.9839 | 131.9139 | 170.4296
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7151 | 27.4721 | 2.2009 | 4 | 6172.2673 | 7891.5329 | 125.83 | 160.8796 | 127.5374 | 0 | 196.7525 | 4240068.0238 | 178049.2379 | 4798709.1165 | 4546603.2116 | 0 | 523830.6359 | 0 | 5572031.488 | 14497282.951 | 9894693.5035 | 44251268.1683 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 54337866.6927 | 69473507.8556 | 100000 | 8.8036 | 6172.2673 | 7891.5329 | 125.83 | 160.8796
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.6944 | 29.119 | 2.3709 | 4 | 5943.9455 | 7539.9108 | 121.1754 | 153.7113 | 127.3724 | 0 | 205.4253 | 4415006.9404 | 185078.2806 | 5028083.714 | 4821800.4432 | 0 | 493573.2933 | 0 | 5827981.6419 | 15163212.7487 | 10349204.2739 | 46283941.3359 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 56370539.8602 | 71506181.0232 | 133352.1432 | 9.4837 | 5943.9455 | 7539.9108 | 121.1754 | 153.7113
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.4017 | 30.4534 | 2.5124 | 4 | 5769.8773 | 7275.9476 | 117.6268 | 148.33 | 127.2231 | 0 | 221.3726 | 4554043.0523 | 190623.9167 | 5212148.4053 | 5045550.956 | 0 | 462711.7091 | 0 | 6031380.4354 | 15692414.6866 | 10710395.4705 | 47899268.6319 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 57985867.1563 | 73121508.3193 | 177827.941 | 10.0498 | 5769.8773 | 7275.9476 | 117.6268 | 148.33
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.965 | 31.5121 | 2.6273 | 4 | 5637.5555 | 7077.8016 | 114.9292 | 144.2906 | 127.0949 | 0 | 224.1757 | 4662668.1597 | 194929.5023 | 5357089.2696 | 5223569.6982 | 0 | 433496.5788 | 0 | 6189983.7513 | 16105067.9807 | 10992039.8229 | 49158844.7636 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 59245443.288 | 74381084.4509 | 237137.3706 | 10.5091 | 5637.5555 | 7077.8016 | 114.9292 | 144.2906
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.3823 | 32.7631 | 2.7451 | 4 | 5536.892 | 6915.3263 | 112.877 | 140.9783 | 126.9406 | 0 | 219.1927 | 4789432.2469 | 199937.1709 | 5527156.6941 | 5434719.9895 | 0 | 421392.8728 | 0 | 6385329.1999 | 16613316.767 | 11338930.063 | 50710215.004 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 60796813.5284 | 75932454.6914 | 316227.766 | 10.9803 | 5536.892 | 6915.3263 | 112.877 | 140.9783
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.666 | 33.5218 | 2.8263 | 4 | 5457.224 | 6796.0636 | 111.2529 | 138.5469 | 126.8532 | 0 | 204.6258 | 4865712.9907 | 202953.7998 | 5629660.8292 | 5563150.2768 | 0 | 400884.9966 | 0 | 6498321.5283 | 16907299.6276 | 11539579.4061 | 51607563.455 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 61694161.9794 | 76829803.1424 | 421696.5034 | 11.305 | 5457.224 | 6796.0636 | 111.2529 | 138.5469
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.9239 | 34.0416 | 2.8843 | 4 | 5399.4801 | 6711.3665 | 110.0757 | 136.8203 | 126.7915 | 0 | 230.0872 | 4917597.8636 | 204999.8801 | 5699637.3071 | 5651290.7901 | 0 | 382982.3296 | 0 | 6574038.1865 | 17104298.8407 | 11674035.4169 | 52208880.6147 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 62295479.1391 | 77431120.302 | 562341.3252 | 11.5373 | 5399.4801 | 6711.3665 | 110.0757 | 136.8203
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6561 | 34.4394 | 2.9291 | 4 | 5355.9087 | 6647.7393 | 109.1874 | 135.5232 | 126.7435 | 0 | 214.0063 | 4957096.8853 | 206554.3931 | 5753047.3916 | 5718817.338 | 0 | 368426.5588 | 0 | 6631537.601 | 17253900.5224 | 11776141.6387 | 52665522.3288 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 62752120.8532 | 77887762.0162 | 749894.2093 | 11.7164 | 5355.9087 | 6647.7393 | 109.1874 | 135.5232
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.9519 | 34.7364 | 2.963 | 4 | 5323.0736 | 6600.115 | 108.5181 | 134.5523 | 126.7071 | 0 | 212.9361 | 4986473.1025 | 207708.7246 | 5792848.0035 | 5769279.9155 | 0 | 356619.1928 | 0 | 6674042.2862 | 17364488.9944 | 11851620.5432 | 53003080.7628 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63089679.2872 | 78225320.4502 | 1000000 | 11.8521 | 5323.0736 | 6600.115 | 108.5181 | 134.5523
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.9218 | 34.9584 | 2.9887 | 4 | 5298.3553 | 6564.4434 | 108.0141 | 133.8251 | 126.6796 | 0 | 193.7502 | 5008367.1522 | 208568.0401 | 5822555.1992 | 5807024.6164 | 0 | 347231.0013 | 0 | 6705560.9436 | 17446494.0755 | 11907590.6961 | 53253391.7244 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63339990.2488 | 78475631.4117 | 1333521.4322 | 11.9547 | 5298.3553 | 6564.4434 | 108.0141 | 133.8251
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.6723 | 35.1299 | 3.0084 | 4 | 5279.7632 | 6537.565 | 107.6351 | 133.2771 | 126.6582 | 0 | 217.2769 | 5025251.391 | 209230.1427 | 5845490.2907 | 5836211.2581 | 0 | 340053.6069 | 0 | 6729932.3088 | 17509903.3687 | 11950868.8417 | 53446941.2086 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63533539.733 | 78669180.8959 | 1778279.41 | 12.0334 | 5279.7632 | 6537.565 | 107.6351 | 133.2771
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.2176 | 35.2545 | 3.0229 | 4 | 5265.7883 | 6517.5237 | 107.3502 | 132.8685 | 126.6426 | 0 | 189.2269 | 5037488.4174 | 209709.6785 | 5862126.9432 | 5857408.1296 | 0 | 334360.2585 | 0 | 6747426.4366 | 17555419.5006 | 11981934.537 | 53585873.9014 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63672472.4258 | 78808113.5887 | 2371373.7057 | 12.0917 | 5265.7883 | 6517.5237 | 107.3502 | 132.8685
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6392 | 35.3507 | 3.0341 | 4 | 5255.2898 | 6502.4209 | 107.1362 | 132.5606 | 126.6305 | 0 | 193.9088 | 5046931.0595 | 210079.5267 | 5874972.5344 | 5873789.2859 | 0 | 330079.2384 | 0 | 6760982.1415 | 17590688.6641 | 12006006.4657 | 53693528.9162 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63780127.4406 | 78915768.6035 | 3162277.6602 | 12.1364 | 5255.2898 | 6502.4209 | 107.1362 | 132.5606
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.9487 | 35.4213 | 3.0424 | 4 | 5247.4061 | 6491.1371 | 106.9755 | 132.3306 | 126.6215 | 0 | 195.4305 | 5053853.7873 | 210350.5691 | 5884394.6341 | 5885812.8151 | 0 | 326759.1058 | 0 | 6770856.6554 | 17616380.1237 | 12023541.4148 | 53771949.1053 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63858547.6297 | 78994188.7926 | 4216965.0343 | 12.1695 | 5247.4061 | 6491.1371 | 106.9755 | 132.3306
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.1922 | 35.4769 | 3.0488 | 4 | 5241.488 | 6482.6071 | 106.8548 | 132.1567 | 126.6145 | 0 | 197.9113 | 5059296.2116 | 210563.5959 | 5891804.554 | 5895273.3248 | 0 | 324319.4996 | 0 | 6778690.3025 | 17636761.6666 | 12037452.2366 | 53834161.3917 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63920759.9161 | 79056401.079 | 5623413.2519 | 12.1952 | 5241.488 | 6482.6071 | 106.8548 | 132.1567
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.3554 | 35.5141 | 3.0533 | 4 | 5237.0464 | 6476.3279 | 106.7643 | 132.0287 | 126.6098 | 0 | 211.0191 | 5062939.0662 | 210706.1471 | 5896765.8299 | 5901610.0719 | 0 | 322325.9866 | 0 | 6783795.3697 | 17650044.0041 | 12046517.705 | 53874704.1805 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63961302.7049 | 79096943.8679 | 7498942.0933 | 12.2132 | 5237.0464 | 6476.3279 | 106.7643 | 132.0287
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.0223 | 34.7522 | 3.0062 | 4 | 5231.9456 | 6490.6344 | 106.6603 | 132.3204 | 126.7044 | 0 | 203.9139 | 4988013.5447 | 207768.1562 | 5794964.5575 | 5771989.7073 | 0 | 293396.8317 | 0 | 6651891.791 | 17306857.9496 | 11812286.1709 | 52827168.7089 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 62913767.2333 | 78049408.3963 | 10000000 | 12.0249 | 5231.9456 | 6490.6344 | 106.6603 | 132.3204
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8748 | [19 empty] | 100 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9253 | [19 empty] | 133.3521 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4933 | [19 empty] | 177.8279 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0887 | 0.18462 | 0.0025102 | 4 | 1144836.6851 | 2704655.5005 | 23339.0443 | 55138.0607 | 103.5338 | 0 | 56.6651 | 111289.6949 | 3971.306 | 89219.7841 | 60960.0362 | 0 | 67962.7483 | 0 | 130027.3921 | 338304.6019 | 230899.8423 | 1032635.4057 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11495301.0754 | 27157436.2418 | 237.1374 | 0.010041 | 1144836.6851 | 2704655.5005 | 23339.0443 | 55138.0607
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.26468 | 0.0068127 | 4 | 432071.5524 | 1006812.8368 | 8808.363 | 20525.2415 | 109.3072 | 0 | 58.427 | 148091.7114 | 5513.4151 | 118512.7562 | 74222.8672 | 0 | 77134.8344 | 0 | 165155.4779 | 429700.6754 | 293279.5404 | 1311611.2779 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11774276.9476 | 27436412.114 | 316.2278 | 0.027251 | 432071.5524 | 1006812.8368 | 8808.363 | 20525.2415
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.3818 | 0.013261 | 4 | 229115.665 | 524373.1523 | 4670.8327 | 10690.056 | 114.4352 | 0 | 323.1657 | 196771.5332 | 7606.19 | 158291.6269 | 93359.0122 | 0 | 89917.0311 | 0 | 212918.7034 | 553970.7906 | 378096.4476 | 1690931.335 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12153597.0047 | 27815732.1711 | 421.6965 | 0.053046 | 229115.665 | 524373.1523 | 4670.8327 | 10690.056
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4877 | 0.53591 | 0.022387 | 4 | 140855.2126 | 315756.2133 | 2871.524 | 6437.1175 | 118.4506 | 0 | 437.3213 | 254671.348 | 10138.1994 | 207025.3865 | 118312.8451 | 0 | 104247.3231 | 0 | 270814.0898 | 704602.7099 | 480905.8277 | 2150717.7293 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12613383.399 | 28275518.5654 | 562.3413 | 0.089549 | 140855.2126 | 315756.2133 | 2871.524 | 6437.1175
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 0.74219 | 0.035022 | 4 | 94123.0575 | 205925.1787 | 1918.8258 | 4198.0633 | 121.6438 | 0 | 597.1719 | 324957.7683 | 13242.1129 | 268032.6734 | 151530.6495 | 0 | 121352.6945 | 0 | 342855.2005 | 892038.9024 | 608834.8804 | 2722844.8819 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 13185510.5516 | 28847645.718 | 749.8942 | 0.14009 | 94123.0575 | 205925.1787 | 1918.8258 | 4198.0633
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 1.0222 | 0.052333 | 4 | 66453.3194 | 141272.6502 | 1354.7408 | 2880.0341 | 124.1893 | 0 | 83.841 | 411571.267 | 17084.2425 | 345639.8737 | 196325.4364 | 0 | 142684.679 | 0 | 434189.1444 | 1129671.0893 | 771023.7309 | 3448189.4631 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 13910855.1328 | 29572990.2992 | 1000 | 0.20933 | 66453.3194 | 141272.6502 | 1354.7408 | 2880.0341
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8022 | 1.399 | 0.075742 | 4 | 48930.75 | 100626.7582 | 997.5195 | 2051.4126 | 126.1654 | 0 | 79.5509 | 517501.0596 | 21784.6106 | 443699.7973 | 256285.8598 | 0 | 168973.107 | 0 | 549215.3294 | 1428945.6275 | 975284.7527 | 4361690.1439 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 14824355.8136 | 30486490.98 | 1333.5214 | 0.30297 | 48930.75 | 100626.7582 | 997.5195 | 2051.4126
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7099 | 1.8973 | 0.10686 | 4 | 37340.3715 | 73983.7394 | 761.234 | 1508.2586 | 127.5847 | 0 | 102.1467 | 645028.803 | 27432.0249 | 565584.9373 | 336332.5439 | 0 | 200543.5949 | 0 | 692219.5426 | 1801013.256 | 1229228.5544 | 5497383.257 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 15960048.9267 | 31622184.0931 | 1778.2794 | 0.42742 | 37340.3715 | 73983.7394 | 761.234 | 1508.2586
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2721 | 2.5739 | 0.14974 | 4 | 29067.4379 | 55216.2654 | 592.579 | 1125.6583 | 128.8663 | 0 | 96.6732 | 803786.2723 | 34485.7389 | 721256.7255 | 444231.7725 | 0 | 239389.4052 | 0 | 874828.4666 | 2276124.2181 | 1553501.5485 | 6947604.1476 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 17410269.8173 | 33072404.9837 | 2371.3737 | 0.59896 | 29067.4379 | 55216.2654 | 592.579 | 1125.6583
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6562 | 3.4642 | 0.20612 | 4 | 23297.2287 | 42293.1901 | 474.9455 | 862.2039 | 129.7496 | 0 | 98.1291 | 994364.0352 | 42906.6623 | 914180.4859 | 586324.8691 | 0 | 285969.5956 | 0 | 1101260.8028 | 2865254.7092 | 1955595.2141 | 8745856.3741 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 19208522.0438 | 34870657.2102 | 3162.2777 | 0.8245 | 23297.2287 | 42293.1901 | 474.9455 | 862.2039
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1728 | 4.6534 | 0.28137 | 4 | 19085.479 | 33001.5819 | 389.0833 | 672.7819 | 130.4225 | 0 | 73.0493 | 1227563.9103 | 53178.0145 | 1157088.9848 | 776233.5688 | 0 | 343099.6729 | 0 | 1387294.019 | 3609454.4644 | 2463526.8388 | 11017439.4736 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 21480105.1433 | 37142240.3097 | 4216.965 | 1.1255 | 19085.479 | 33001.5819 | 389.0833 | 672.7819
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0714 | 5.9438 | 0.37306 | 4 | 15937.3359 | 26432.9624 | 324.9041 | 538.8717 | 130.8577 | 0 | 77.0307 | 1461379.6558 | 63443.7243 | 1406931.4453 | 982328.1019 | 0 | 386462.3231 | 0 | 1677212.6477 | 4363763.2656 | 2978358.0951 | 13319879.2588 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 23782544.9285 | 39444680.0949 | 5623.4133 | 1.4923 | 15937.3359 | 26432.9624 | 324.9041 | 538.8717
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.0151 | 7.5094 | 0.48875 | 4 | 13525.0596 | 21536.3036 | 275.7266 | 439.0467 | 131.1908 | 0 | 99.1062 | 1725823.5398 | 75017.8929 | 1695935.8648 | 1232046.4399 | 0 | 430290.2852 | 0 | 2012054.4688 | 5234952.9988 | 3572962.9892 | 15979084.4795 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 26441750.1492 | 42103885.3156 | 7498.9421 | 1.955 | 13525.0596 | 21536.3036 | 275.7266 | 439.0467
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.265 | 9.4191 | 0.63396 | 4 | 11650.2239 | 17826.505 | 237.5056 | 363.4174 | 131.4512 | 0 | 123.3532 | 2027396.4326 | 88177.395 | 2032618.2917 | 1536390.4943 | 0 | 475900.4905 | 0 | 2402588.4106 | 6251042.2057 | 4266464.7515 | 19080578.4719 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 29543244.1416 | 45205379.308 | 10000 | 2.5359 | 11650.2239 | 17826.505 | 237.5056 | 363.4174
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.9077 | 11.6955 | 0.81269 | 4 | 10177.5761 | 14995.5406 | 207.4837 | 305.7044 | 131.6502 | 0 | 114.9443 | 2364438.7961 | 102840.585 | 2416606.3144 | 1899198.8296 | 0 | 520928.1317 | 0 | 2848564.9361 | 7411381.6428 | 5058420.2599 | 22622379.4956 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33085045.1653 | 48747180.3317 | 13335.2143 | 3.2508 | 10177.5761 | 14995.5406 | 207.4837 | 305.7044
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8876 | 14.3214 | 1.0263 | 4 | 9014.5642 | 12829.769 | 183.7741 | 261.5522 | 131.7876 | 0 | 151.9631 | 2730144.3477 | 118694.288 | 2841437.5567 | 2317933.5202 | 0 | 561905.572 | 0 | 3342344.961 | 8696095.9792 | 5935264.1927 | 26543820.4174 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 37006486.0871 | 52668621.2535 | 17782.7941 | 4.1052 | 9014.5642 | 12829.769 | 183.7741 | 261.5522
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.8233 | 17.1895 | 1.2698 | 4 | 8096.4241 | 11179.9431 | 165.0566 | 227.9183 | 131.8509 | 0 | 158.4525 | 3107444.9757 | 134971.7435 | 3288086.5484 | 2776078.0653 | 0 | 593010.5456 | 0 | 3860840.8326 | 10045115.8792 | 6855997.994 | 30661546.5845 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 41124212.2542 | 56786347.4206 | 23713.7371 | 5.0793 | 8096.4241 | 11179.9431 | 165.0566 | 227.9183
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.1797 | 20.1498 | 1.5329 | 4 | 7375.0009 | 9929.2902 | 150.3494 | 202.422 | 131.8313 | 0 | 200.0364 | 3477154.3219 | 150817.0952 | 3733838.0134 | 3250472.6008 | 0 | 610119.7443 | 0 | 4376736.6925 | 11387371.0817 | 7772114.7503 | 34758624.3001 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 45221289.9698 | 60883425.1362 | 31622.7766 | 6.1317 | 7375.0009 | 9929.2902 | 150.3494 | 202.422
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.3272 | 23.0301 | 1.8011 | 4 | 6811.75 | 8985.6646 | 138.8667 | 183.1849 | 131.7353 | 0 | 173.5783 | 3820651.3185 | 165418.9735 | 4155299.6821 | 3714197.0261 | 0 | 611319.8235 | 0 | 4862085.8612 | 12650150.06 | 8633987.3505 | 38613110.0955 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 49075775.7652 | 64737910.9315 | 42169.6503 | 7.2046 | 6811.75 | 8985.6646 | 138.8667 | 183.1849
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7534 | 25.6953 | 2.0604 | 4 | 6374.7591 | 8275.1651 | 129.9581 | 168.7004 | 131.5831 | 0 | 177.2688 | 4126085.9241 | 178283.8482 | 4536211.2455 | 4145752.4558 | 0 | 598187.5697 | 0 | 5297963.2069 | 13784213.5027 | 9408008.9528 | 42074706.7058 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 52537372.3755 | 68199507.5419 | 56234.1325 | 8.2415 | 6374.7591 | 8275.1651 | 129.9581 | 168.7004
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.105 | 28.0587 | 2.2992 | 4 | 6037.6324 | 7740.6183 | 123.0853 | 157.803 | 131.4002 | 0 | 218.6613 | 4387946.8371 | 189208.8005 | 4867620.4042 | 4530780.141 | 0 | 574314.4649 | 0 | 5674449.5526 | 14763753.7463 | 10076565.2966 | 45064639.2433 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 55527304.913 | 71189440.0794 | 74989.4209 | 9.1969 | 6037.6324 | 7740.6183 | 123.0853 | 157.803
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.1339 | 30.0651 | 2.5094 | 4 | 5778.8055 | 7339.1391 | 117.8088 | 149.6183 | 131.2111 | 0 | 204.2804 | 4604149.1239 | 198146.159 | 5144790.656 | 4859644.4212 | 0 | 543370.0892 | 0 | 5986539.1752 | 15575746.9258 | 10630767.3265 | 47543153.8767 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 58005819.5464 | 73667954.7128 | 100000 | 10.0377 | 5778.8055 | 7339.1391 | 117.8088 | 149.6183
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.8398 | 31.7237 | 2.6883 | 4 | 5580.8901 | 7037.3845 | 113.774 | 143.4666 | 131.032 | 0 | 234.4243 | 4778885.5073 | 205308.9033 | 5371266.092 | 5133030.8586 | 0 | 509674.2787 | 0 | 6239284.5996 | 16233338.6749 | 11079587.2074 | 49550376.1218 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 60013041.7915 | 75675176.9579 | 133352.1432 | 10.7533 | 5580.8901 | 7037.3845 | 113.774 | 143.4666
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2728 | 33.0539 | 2.8356 | 4 | 5430.0457 | 6810.8936 | 110.6988 | 138.8493 | 130.8736 | 0 | 211.7567 | 4916453.907 | 210902.2179 | 5551297.9283 | 5352471.5755 | 0 | 476114.3591 | 0 | 6437823.5953 | 16749896.4158 | 11432148.4797 | 51127108.4788 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 61589774.1485 | 77251909.3149 | 177827.941 | 11.3424 | 5430.0457 | 6810.8936 | 110.6988 | 138.8493
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.4944 | 34.5667 | 2.984 | 4 | 5315.0813 | 6627.2576 | 108.3551 | 135.1056 | 130.6867 | 0 | 222.7289 | 5070483.7322 | 217130.1667 | 5754371.6217 | 5602513.004 | 0 | 460378.0748 | 0 | 6670901.8737 | 17356318.2854 | 11846043.8664 | 52978140.6249 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 63440806.2946 | 79102941.461 | 237137.3706 | 11.936 | 5315.0813 | 6627.2576 | 108.3551 | 135.1056
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.1265 | 35.4495 | 3.0834 | 4 | 5226.6533 | 6496.5259 | 106.5524 | 132.4405 | 130.5844 | 0 | 228.4206 | 5159480.9757 | 220727.909 | 5872047.544 | 5748452.1822 | 0 | 434390.5298 | 0 | 6799688.6648 | 17691395.0979 | 12074740.6762 | 54000923.5795 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 64463589.2492 | 80125724.4156 | 316227.766 | 12.3336 | 5226.6533 | 6496.5259 | 106.5524 | 132.4405
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2493 | 36.2052 | 3.1673 | 4 | 5157.2622 | 6393.4944 | 105.1378 | 130.34 | 130.4941 | 0 | 225.7316 | 5235005.0306 | 223770.2496 | 5972346.9909 | 5873626.0658 | 0 | 412875.7196 | 0 | 6909873.382 | 17978073.1302 | 12270404.3238 | 54875974.8926 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 65338640.5623 | 81000775.7287 | 421696.5034 | 12.6692 | 5157.2622 | 6393.4944 | 105.1378 | 130.34
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.3734 | 36.7173 | 3.2267 | 4 | 5107.1837 | 6320.6519 | 104.1168 | 128.855 | 130.4313 | 0 | 223.226 | 5285842.8048 | 225812.1538 | 6040099.2352 | 5958595.434 | 0 | 394330.6656 | 0 | 6982825.3144 | 18167879.0938 | 12399950.7941 | 55455335.4958 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 65918001.1655 | 81580136.3319 | 562341.3252 | 12.9069 | 5107.1837 | 6320.6519 | 104.1168 | 128.855
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9935 | 37.107 | 3.2723 | 4 | 5069.3971 | 6265.9523 | 103.3465 | 127.7399 | 130.3827 | 0 | 205.4108 | 5324336.5166 | 227355.0749 | 6091526.8501 | 6023313.4639 | 0 | 379285.4889 | 0 | 7037868.7838 | 18311090.9101 | 12497695.8015 | 55892472.8899 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 66355138.5596 | 82017273.726 | 749894.2093 | 13.0894 | 5069.3971 | 6265.9523 | 103.3465 | 127.7399
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2117 | 37.3994 | 3.307 | 4 | 5040.9218 | 6224.953 | 102.766 | 126.9041 | 130.3457 | 0 | 207.248 | 5353120.6315 | 228506.9871 | 6130054.4969 | 6071923.3921 | 0 | 367206.1721 | 0 | 7078816.5551 | 18417628.6114 | 12570409.9717 | 56217666.8179 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 66680332.4876 | 82342467.654 | 1000000 | 13.2278 | 5040.9218 | 6224.953 | 102.766 | 126.9041
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.1271 | 37.6188 | 3.3331 | 4 | 5019.4856 | 6194.2128 | 102.329 | 126.2774 | 130.3177 | 0 | 224.5363 | 5374661.5206 | 229367.997 | 6158927.7548 | 6108423.1173 | 0 | 357669.8998 | 0 | 7109329.6129 | 18497017.3288 | 12624594.4026 | 56459991.6337 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 66922657.3034 | 82584792.4698 | 1333521.4322 | 13.3326 | 5019.4856 | 6194.2128 | 102.329 | 126.2774
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8117 | 37.7827 | 3.3529 | 4 | 5003.3621 | 6171.1775 | 102.0003 | 125.8078 | 130.2967 | 0 | 230.1005 | 5390719.2568 | 230009.2497 | 6180474.4399 | 6135700.6869 | 0 | 350211.7259 | 0 | 7131974.9901 | 18555935.955 | 12664807.5756 | 56639833.88 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67102499.5497 | 82764634.7161 | 1778279.41 | 13.4115 | 5003.3621 | 6171.1775 | 102.0003 | 125.8078
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3186 | 37.904 | 3.3676 | 4 | 4991.2428 | 6153.9409 | 101.7532 | 125.4564 | 130.281 | 0 | 235.8059 | 5402582.5182 | 230482.6753 | 6196405.5012 | 6155890.7737 | 0 | 344398.5187 | 0 | 7148606.3949 | 18599207.4588 | 12694341.2661 | 56771915.1069 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67234580.7766 | 82896715.943 | 2371373.7057 | 13.4705 | 4991.2428 | 6153.9409 | 101.7532 | 125.4564
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.713 | 37.9982 | 3.379 | 4 | 4982.1382 | 6140.9373 | 101.5676 | 125.1913 | 130.2688 | 0 | 220.0051 | 5411795.1199 | 230850.1384 | 6208784.2551 | 6171591.5059 | 0 | 340049.2989 | 0 | 7161597.4241 | 18633007.452 | 12717410.456 | 56875085.6503 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67337751.32 | 82999886.4864 | 3162277.6602 | 13.5158 | 4982.1382 | 6140.9373 | 101.5676 | 125.1913
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.0102 | 38.0693 | 3.3875 | 4 | 4975.3013 | 6131.1778 | 101.4282 | 124.9924 | 130.2595 | 0 | 216.8817 | 5418730.7751 | 231126.6726 | 6218107.7742 | 6183424.4371 | 0 | 336742.6182 | 0 | 7171371.5881 | 18658437.8217 | 12734767.2059 | 56952708.893 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67415374.5627 | 83077509.7291 | 4216965.0343 | 13.55 | 4975.3013 | 6131.1778 | 101.4282 | 124.9924
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.2271 | 38.1211 | 3.3938 | 4 | 4970.169 | 6123.8923 | 101.3236 | 124.8438 | 130.2528 | 0 | 217.2506 | 5423785.593 | 231328.1529 | 6224905.2911 | 6192055.5376 | 0 | 334183.6403 | 0 | 7178440.7038 | 18676830.2106 | 12747320.3892 | 57008849.5186 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67471515.1883 | 83133650.3547 | 5623413.2519 | 13.5753 | 4970.169 | 6123.8923 | 101.3236 | 124.8438
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3929 | 38.1607 | 3.3986 | 4 | 4966.3173 | 6118.4118 | 101.2451 | 124.7321 | 130.2476 | 0 | 208.3517 | 5427646.3518 | 231482.0067 | 6230098.368 | 6198651.6518 | 0 | 332270.0489 | 0 | 7183857.8866 | 18690924.6092 | 12756940.1059 | 57051871.029 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67514536.6987 | 83176671.8651 | 7498942.0933 | 13.5945 | 4966.3173 | 6118.4118 | 101.2451 | 124.7321
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5024 | 38.1868 | 3.402 | 4 | 4963.4271 | 6114.3828 | 101.1862 | 124.65 | 130.2442 | 0 | 231.2576 | 5430193.874 | 231583.5044 | 6233525.8074 | 6203006.2989 | 0 | 330710.1686 | 0 | 7187317.6648 | 18699926.2423 | 12763083.9055 | 57079347.4661 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67542013.1358 | 83204148.3022 | 10000000 | 13.6079 | 4963.4271 | 6114.3828 | 101.1862 | 124.65
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.488 | [19 empty] | 100 | 0
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5518 | [19 empty] | 133.3521 | 0
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79402 | 0.11988 | 0.00058104 | 4 | 4999126.7645 | 11967987.2076 | 101913.9609 | 243983.6071 | 96.9709 | 0 | 38.2536 | 78948.4846 | 2681.7505 | 63470.5874 | 49644.9105 | 0 | 55230.4668 | 0 | 97490.7179 | 253650.8499 | 173121.917 | 774239.6845 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11618832.5904 | 27815665.8874 | 177.8279 | 0.0023242 | 4999126.7645 | 11967987.2076 | 101913.9609 | 243983.6071
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.19619 | 0.0038432 | 4 | 775105.0951 | 1828695.6778 | 15801.5658 | 37280.4349 | 106.0867 | 0 | 60.5424 | 118001.4193 | 4286.578 | 93489.0862 | 62326.8488 | 0 | 67714.3383 | 0 | 134869.1255 | 350901.7991 | 239497.6882 | 1071086.8834 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11915679.7893 | 28112513.0863 | 237.1374 | 0.015373 | 775105.0951 | 1828695.6778 | 15801.5658 | 37280.4349
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.28533 | 0.0089505 | 4 | 341397.5978 | 793800.0403 | 6959.8518 | 16182.6875 | 112.2997 | 0 | 66.3773 | 158836.4763 | 6038.5513 | 125583.5513 | 76782.9923 | 0 | 77689.4851 | 0 | 173523.1119 | 451471.5427 | 308138.6047 | 1378064.3154 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12222657.2213 | 28419490.5183 | 316.2278 | 0.035802 | 341397.5978 | 793800.0403 | 6959.8518 | 16182.6875
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.40851 | 0.01649 | 4 | 191225.3925 | 436774.4976 | 3898.3883 | 8904.2389 | 117.5028 | 0 | 326.3294 | 209834.1841 | 8286.4318 | 166724.2792 | 96441.412 | 0 | 89850.8603 | 0 | 222743.4953 | 579532.8839 | 395543.1015 | 1768956.6483 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12613549.5542 | 28810382.8512 | 421.6965 | 0.065962 | 191225.3925 | 436774.4976 | 3898.3883 | 8904.2389
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.57591 | 0.027206 | 4 | 120424.2637 | 269258.9611 | 2455.0115 | 5489.2081 | 121.724 | 0 | 447.4545 | 272512.394 | 11098.6334 | 218792.7011 | 122921.3122 | 0 | 104513.3384 | 0 | 284636.9679 | 740567.0034 | 505452.1969 | 2260494.5473 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13105087.4532 | 29301920.7502 | 562.3413 | 0.10882 | 120424.2637 | 269258.9611 | 2455.0115 | 5489.2081
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3628 | 0.79805 | 0.041919 | 4 | 81763.6399 | 178360.4155 | 1666.8624 | 3636.1183 | 125.0474 | 0 | 602.1298 | 347852.3949 | 14511.1411 | 283390.2169 | 157611.3313 | 0 | 121679.9709 | 0 | 360767.5715 | 938643.2175 | 640643.2831 | 2865099.1272 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13709692.0331 | 29906525.3301 | 749.8942 | 0.16767 | 81763.6399 | 178360.4155 | 1666.8624 | 3636.1183
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4721 | 1.1025 | 0.062254 | 4 | 58172.232 | 123215.0594 | 1185.9196 | 2511.9056 | 127.7108 | 0 | 89.559 | 441699.2956 | 18789.2999 | 366322.2941 | 205412.905 | 0 | 143443.1274 | 0 | 458510.0996 | 1192949.2257 | 814212.3592 | 3641338.6065 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 14485931.5124 | 30682764.8094 | 1000 | 0.24902 | 58172.232 | 123215.0594 | 1185.9196 | 2511.9056
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9459 | 1.5084 | 0.089645 | 4 | 43096.1092 | 88265.6619 | 878.5725 | 1799.4149 | 129.754 | 0 | 86.7488 | 555385.8452 | 23976.5766 | 470069.4206 | 268887.5089 | 0 | 169691.844 | 0 | 580324.3662 | 1509884.9599 | 1030527.5102 | 4608748.0316 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 15453340.9375 | 31650174.2345 | 1333.5214 | 0.35858 | 43096.1092 | 88265.6619 | 878.5725 | 1799.4149
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8951 | 2.0438 | 0.12582 | 4 | 33085.4158 | 65267.862 | 674.491 | 1330.5736 | 131.2083 | 0 | 98.9803 | 691786.7977 | 30174.5455 | 598792.2157 | 352808.1215 | 0 | 201224.5612 | 0 | 731166.6342 | 1902345.5993 | 1298389.9608 | 5806688.4359 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 16651281.3418 | 32848114.6388 | 1778.2794 | 0.50328 | 33085.4158 | 65267.862 | 674.491 | 1330.5736
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.489 | 2.7655 | 0.17562 | 4 | 25863.3852 | 48920.3773 | 527.2601 | 997.3081 | 132.551 | 0 | 96.5318 | 860559.4945 | 37879.6211 | 761980.1992 | 464904.6443 | 0 | 239237.3156 | 0 | 922178.8971 | 2399320.3254 | 1637585.4232 | 7323645.9205 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 18168238.8264 | 34365072.1234 | 2371.3737 | 0.70247 | 25863.3852 | 48920.3773 | 527.2601 | 997.3081
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.958 | 3.727 | 0.24146 | 4 | 20787.1149 | 37556.5297 | 423.7735 | 765.6407 | 133.475 | 0 | 95.5451 | 1065773.2235 | 47194.5204 | 966801.0017 | 615007.3431 | 0 | 286174.0472 | 0 | 1162570.553 | 3024770.103 | 2064467.7481 | 9232758.5401 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 20077351.446 | 36274184.743 | 3162.2777 | 0.96586 | 20787.1149 | 37556.5297 | 423.7735 | 765.6407
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5601 | 5.0034 | 0.32904 | 4 | 17073.7311 | 29379.8315 | 348.0711 | 598.9476 | 134.1745 | 0 | 86.2685 | 1315302.2326 | 58481.3565 | 1223083.3763 | 814174.9188 | 0 | 342999.8675 | 0 | 1464076.2832 | 3809226.1654 | 2599875.1297 | 11627219.33 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 22471812.2359 | 38668645.5329 | 4216.965 | 1.3162 | 17073.7311 | 29379.8315 | 348.0711 | 598.9476
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6574 | 6.6946 | 0.44514 | 4 | 14307.1538 | 23403.5705 | 291.6707 | 477.1134 | 134.7038 | 0 | 95.1756 | 1618587.461 | 72147.6207 | 1543375.4983 | 1077684.0642 | 0 | 411854.0119 | 0 | 1842222.9759 | 4793086.2914 | 3271379.882 | 14630337.8055 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 25474930.7114 | 41671764.0084 | 5623.4133 | 1.7806 | 14307.1538 | 23403.5705 | 291.6707 | 477.1134
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.6487 | 8.6341 | 0.58807 | 4 | 12207.3446 | 19092.9569 | 248.8632 | 389.2358 | 135.0627 | 0 | 96.964 | 1939813.1843 | 86570.9432 | 1891315.0123 | 1379713.3053 | 0 | 472345.2336 | 0 | 2250205.4947 | 5854573.1166 | 3995866.4515 | 17870402.7416 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 28714995.6474 | 44911828.9445 | 7498.9421 | 2.3523 | 12207.3446 | 19092.9569 | 248.8632 | 389.2358
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.4561 | 10.7994 | 0.76003 | 4 | 10571.1263 | 15898.8042 | 215.5067 | 324.1186 | 135.3144 | 0 | 108.641 | 2274314.5461 | 101538.8635 | 2261717.0498 | 1716298.7872 | 0 | 520932.6495 | 0 | 2681172.7395 | 6975861.484 | 4761168.8025 | 21293004.9221 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 32137597.828 | 48334431.125 | 10000 | 3.0401 | 10571.1263 | 15898.8042 | 215.5067 | 324.1186
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.7056 | 13.3638 | 0.97027 | 4 | 9281.5409 | 13454.8047 | 189.2168 | 274.2944 | 135.5027 | 0 | 113.4152 | 2646081.4548 | 118120.3046 | 2681693.4679 | 2115010.4598 | 0 | 568215.2813 | 0 | 3170357.1777 | 8248619.0466 | 5629851.9915 | 25177949.184 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 36022542.0899 | 52219375.3869 | 13335.2143 | 3.8811 | 9281.5409 | 13454.8047 | 189.2168 | 274.2944
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.1996 | 16.2681 | 1.2178 | 4 | 8261.6975 | 11586.6463 | 168.4259 | 236.2095 | 135.6203 | 0 | 144.7949 | 3042587.915 | 135732.2314 | 3138341.9101 | 2567054.487 | 0 | 608770.4117 | 0 | 3702069.9125 | 9632026.5134 | 6574056.0138 | 29400639.3948 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 40245232.3007 | 56442065.5978 | 17782.7941 | 4.8713 | 8261.6975 | 11586.6463 | 168.4259 | 236.2095
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5218 | 19.3877 | 1.4955 | 4 | 7456.9524 | 10164.4778 | 152.0201 | 207.2166 | 135.6532 | 0 | 182.5517 | 3445465.54 | 153524.242 | 3611131.5668 | 3053921.3028 | 0 | 637241.9481 | 0 | 4251500.9939 | 11061533.4834 | 7549723.8942 | 33764042.9713 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 44608635.8771 | 60805469.1742 | 23713.7371 | 5.9822 | 7456.9524 | 10164.4778 | 152.0201 | 207.2166
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.0519 | 22.5409 | 1.7897 | 4 | 6825.4713 | 9087.9499 | 139.1465 | 185.2702 | 135.5966 | 0 | 150.4929 | 3832714.7476 | 170495.146 | 4073946.8828 | 3548266.4304 | 0 | 649386.4098 | 0 | 4787175.7505 | 12455249.318 | 8500963.5893 | 38018198.2745 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 48862791.1804 | 65059624.4774 | 31622.7766 | 7.1589 | 6825.4713 | 9087.9499 | 139.1465 | 185.2702
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.189 | 25.5562 | 2.0843 | 4 | 6333.1344 | 8275.8583 | 129.1095 | 168.7146 | 135.4637 | 0 | 215.382 | 4187003.569 | 185878.7662 | 4504769.3786 | 4023888.8036 | 0 | 644611.8273 | 0 | 5282999.4144 | 13745280.7842 | 9381436.5725 | 41955869.1158 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 52800462.0217 | 68997295.3187 | 42169.6503 | 8.3372 | 6333.1344 | 8275.8583 | 129.1095 | 168.7146
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.4861 | 28.312 | 2.3648 | 4 | 5951.6082 | 7663.879 | 121.3316 | 156.2385 | 135.2792 | 0 | 190.5568 | 4498722.3168 | 199277.8101 | 4889943.1315 | 4461672.8698 | 0 | 625734.2097 | 0 | 5723386.6318 | 14891077.9878 | 10163466.7077 | 45453281.6652 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 56297874.5711 | 72494707.8681 | 56234.1325 | 9.4593 | 5951.6082 | 7663.879 | 121.3316 | 156.2385
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5971 | 30.7213 | 2.6195 | 4 | 5657.5245 | 7203.3422 | 115.3363 | 146.8499 | 135.0713 | 0 | 208.7548 | 4762667.7318 | 210507.7621 | 5220804.0269 | 4847257.3632 | 0 | 596504.2127 | 0 | 6098719.0277 | 15867615.8908 | 10829973.8924 | 48434049.9077 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 59278642.8135 | 75475476.1106 | 74989.4209 | 10.4778 | 5657.5245 | 7203.3422 | 115.3363 | 146.8499
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3534 | 32.747 | 2.8408 | 4 | 5431.8703 | 6857.2239 | 110.736 | 139.7938 | 134.8639 | 0 | 211.6996 | 4978741.5769 | 219605.7379 | 5495190.1536 | 5172633.8172 | 0 | 561223.1854 | 0 | 6406683.8437 | 16668877.1697 | 11376851.1795 | 50879806.6639 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 61724399.5697 | 77921232.8668 | 100000 | 11.3634 | 5431.8703 | 6857.2239 | 110.736 | 139.7938
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.7723 | 34.4048 | 3.0271 | 4 | 5259.3686 | 6597.0027 | 107.2193 | 134.4888 | 134.6724 | 0 | 247.6796 | 5151791.2645 | 226823.9662 | 5717366.2663 | 5439836.1593 | 0 | 524079.7078 | 0 | 6653359.972 | 17310677.8553 | 11814893.3351 | 52838828.5263 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 63683421.4322 | 79880254.7292 | 133352.1432 | 12.1086 | 5259.3686 | 6597.0027 | 107.2193 | 134.4888
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8 | 36.2027 | 3.2107 | 4 | 5127.9159 | 6389.091 | 104.5395 | 130.2503 | 134.4485 | 0 | 219.2306 | 5335954.8065 | 234445.0188 | 5956057.6997 | 5730970.6789 | 0 | 503936.3042 | 0 | 6926932.1581 | 18022456.5663 | 12300696.9309 | 55011450.1633 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 65856043.0691 | 82052876.3662 | 177827.941 | 12.8427 | 5127.9159 | 6389.091 | 104.5395 | 130.2503
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2534 | 37.3415 | 3.3409 | 4 | 5026.2545 | 6238.2605 | 102.467 | 127.1754 | 134.3168 | 0 | 209.1701 | 5451252.4785 | 239215.1679 | 6106002.3954 | 5915415.3928 | 0 | 473434.8017 | 0 | 7092274.8921 | 18452644.4437 | 12594308.9968 | 56324548.5689 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 67169141.4747 | 83365974.7718 | 237137.3706 | 13.3637 | 5026.2545 | 6238.2605 | 102.467 | 127.1754
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6755 | 38.212 | 3.4429 | 4 | 4949.0989 | 6125.2096 | 100.8941 | 124.8707 | 134.2123 | 0 | 241.9094 | 5538494.1321 | 242808.7425 | 6220048.4022 | 6056778.2234 | 0 | 446016.4707 | 0 | 7216616.9287 | 18776156.9167 | 12815112.9071 | 57312032.7234 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 68156625.6293 | 84353458.9263 | 316227.766 | 13.7715 | 4949.0989 | 6125.2096 | 100.8941 | 124.8707
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.499 | 37.9127 | 3.457 | 4 | 4889.7636 | 6061.0754 | 99.6844 | 123.5632 | 134.2477 | 0 | 221.0895 | 5508563.6121 | 241575.8001 | 6180900.0044 | 6008178.8269 | 0 | 390175.4568 | 0 | 7148463.5431 | 18598835.7876 | 12694087.5929 | 56770780.6238 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 67615373.5297 | 83812206.8267 | 421696.5034 | 13.8279 | 4889.7636 | 6061.0754 | 99.6844 | 123.5632
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6332 | 39.466 | 3.5899 | 4 | 4844.6578 | 5972.6078 | 98.7649 | 121.7597 | 134.0561 | 0 | 215.9483 | 5662838.6227 | 247906.3374 | 6383489.3279 | 6260991.411 | 0 | 404286.8721 | 0 | 7394209.9027 | 19238217.4059 | 13130478.6854 | 58722418.5652 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 69567011.4711 | 85763844.7681 | 562341.3252 | 14.3595 | 4844.6578 | 5972.6078 | 98.7649 | 121.7597
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.1601 | 39.8504 | 3.6364 | 4 | 4811.7111 | 5925.2191 | 98.0932 | 120.7936 | 134.0067 | 0 | 249.3139 | 5700646.2201 | 249450.2855 | 6433400.2377 | 6323739.2586 | 0 | 388863.4763 | 0 | 7447478.7965 | 19376812.1405 | 13225072.4396 | 59145462.8549 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 69990055.7607 | 86186889.0578 | 749894.2093 | 14.5458 | 4811.7111 | 5925.2191 | 98.0932 | 120.7936
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.3586 | 40.1513 | 3.6726 | 4 | 4786.8758 | 5889.4279 | 97.5869 | 120.064 | 133.9676 | 0 | 234.0545 | 5730125.1928 | 250651.3744 | 6472403.9571 | 6372725.3851 | 0 | 376945.6096 | 0 | 7489112.0924 | 19485133.4364 | 13299003.9498 | 59476100.9977 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70320693.9036 | 86517527.2006 | 1000000 | 14.6903 | 4786.8758 | 5889.4279 | 97.5869 | 120.064
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.2017 | 40.3626 | 3.6989 | 4 | 4768.1788 | 5862.886 | 97.2058 | 119.5229 | 133.9399 | 0 | 228.1762 | 5750770.9093 | 251491.364 | 6499761.0099 | 6407121.8533 | 0 | 367093.8367 | 0 | 7517733.1995 | 19559599.6861 | 13349828.6953 | 59703400.5541 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70547993.46 | 86744826.7571 | 1333521.4322 | 14.7956 | 4768.1788 | 5862.886 | 97.2058 | 119.5229
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8519 | 40.5254 | 3.719 | 4 | 4754.1158 | 5842.8908 | 96.9191 | 119.1152 | 133.9184 | 0 | 229.0689 | 5766644.5651 | 252136.6138 | 6520815.6022 | 6433629.0907 | 0 | 359572.733 | 0 | 7539791.4559 | 19616990.7443 | 13388999.2718 | 59878580.0768 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70723172.9826 | 86920006.2797 | 1778279.41 | 14.8762 | 4754.1158 | 5842.8908 | 96.9191 | 119.1152
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3271 | 40.6443 | 3.734 | 4 | 4743.5455 | 5827.9579 | 96.7036 | 118.8108 | 133.9026 | 0 | 219.4342 | 5778222.7721 | 252606.9226 | 6536184.5392 | 6452997.637 | 0 | 353672.8951 | 0 | 7555737.0587 | 19658477.932 | 13417315.13 | 60005214.8867 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70849807.7926 | 87046641.0896 | 2371373.7057 | 14.936 | 4743.5455 | 5827.9579 | 96.7036 | 118.8108
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.695 | 40.7362 | 3.7455 | 4 | 4735.6046 | 5816.7011 | 96.5417 | 118.5813 | 133.8904 | 0 | 227.9544 | 5787169.2556 | 252970.1466 | 6548066.7047 | 6467983.0787 | 0 | 349246.0996 | 0 | 7568119.7612 | 19690695.1838 | 13439304.0663 | 60103554.2964 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70948147.2023 | 87144980.4994 | 3162277.6602 | 14.9819 | 4735.6046 | 5816.7011 | 96.5417 | 118.5813
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.9682 | 40.8045 | 3.754 | 4 | 4729.6416 | 5808.2724 | 96.4201 | 118.4095 | 133.8813 | 0 | 215.7595 | 5793805.4924 | 253239.4663 | 6556884.3773 | 6479109.9957 | 0 | 345851.269 | 0 | 7577267.3343 | 19714495.2925 | 13455548.1295 | 60176201.357 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 71020794.2629 | 87217627.5599 | 4216965.0343 | 15.0161 | 4729.6416 | 5808.2724 | 96.4201 | 118.4095
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.1749 | 40.8561 | 3.7605 | 4 | 4725.1653 | 5801.9421 | 96.3289 | 118.2804 | 133.8744 | 0 | 230.4775 | 5798821.628 | 253442.9776 | 6563551.5166 | 6487526.7217 | 0 | 343289.0899 | 0 | 7584186.4541 | 19732497.4231 | 13467834.9536 | 60231150.7645 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 71075743.6704 | 87272576.9674 | 5623413.2519 | 15.042 | 4725.1653 | 5801.9421 | 96.3289 | 118.2804
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3212 | 40.8927 | 3.7652 | 4 | 4721.8058 | 5797.2379 | 96.2604 | 118.1845 | 133.8695 | 0 | 220.4088 | 5802369.9176 | 253586.899 | 6568268.9311 | 6493484.0241 | 0 | 341280.7555 | 0 | 7589006.3057 | 19745037.6881 | 13476393.9421 | 60269428.4631 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 71114021.369 | 87310854.666 | 7498942.0933 | 15.0608 | 4721.8058 | 5797.2379 | 96.2604 | 118.1845
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.4332 | 40.9206 | 3.7688 | 4 | 4719.2851 | 5793.6984 | 96.209 | 118.1124 | 133.8657 | 0 | 220.2194 | 5805085.9639 | 253697.0479 | 6571880.4773 | 6498045.8121 | 0 | 339783.2786 | 0 | 7592712.1061 | 19754679.4207 | 13482974.6227 | 60298858.7292 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 71143451.6351 | 87340284.9322 | 10000000 | 15.075 | 4719.2851 | 5793.6984 | 96.209 | 118.1124
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9555 | [19 empty] | 100 | 0
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6357 | [19 empty] | 133.3521 | 0
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.14567 | 0.0014635 | 4 | 2069596.5331 | 4929063.1911 | 42191.5247 | 100485.6202 | 101.8792 | 0 | 54.9061 | 93460.6049 | 3289.3608 | 73904.7635 | 53623.9426 | 0 | 60922.4556 | 0 | 111228.4397 | 289393.5841 | 197517.0676 | 883340.2188 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12115720.4517 | 28855456.0066 | 177.8279 | 0.0058541 | 2069596.5331 | 4929063.1911 | 42191.5247 | 100485.6202
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.21212 | 0.0053328 | 4 | 579374.5326 | 1364124.7936 | 11811.3335 | 27809.529 | 108.9661 | 0 | 47.1461 | 126818.6552 | 4701.4417 | 99303.1157 | 64394.0091 | 0 | 68468.2249 | 0 | 141837.3242 | 369031.6227 | 251871.6653 | 1126426.0588 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12358806.2917 | 29098541.8466 | 237.1374 | 0.021331 | 579374.5326 | 1364124.7936 | 11811.3335 | 27809.529
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.31101 | 0.011378 | 4 | 278896.3028 | 646690.5985 | 5685.6784 | 13183.6626 | 115.5 | 0 | 57.4558 | 171750.1855 | 6677.4911 | 134237.2958 | 80026.3711 | 0 | 79102.4847 | 0 | 183999.593 | 478729.1975 | 326742.5142 | 1461265.133 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12693645.3659 | 29433380.9208 | 316.2278 | 0.045514 | 278896.3028 | 646690.5985 | 5685.6784 | 13183.6626
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.44179 | 0.020118 | 4 | 162790.3626 | 370813.7627 | 3318.7017 | 7559.5401 | 120.7362 | 0 | 334.978 | 225486.6874 | 9107.841 | 177103.0314 | 100424.3443 | 0 | 90809.8917 | 0 | 235143.4004 | 611794.8932 | 417562.5858 | 1867432.6752 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13099812.9081 | 29839548.463 | 421.6965 | 0.08047 | 162790.3626 | 370813.7627 | 3318.7017 | 7559.5401
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.61758 | 0.032378 | 4 | 105047.9315 | 234299.8311 | 2141.5442 | 4776.519 | 124.9929 | 0 | 452.9547 | 290929.6481 | 12119.4151 | 230849.1684 | 127455.3816 | 0 | 104692.5076 | 0 | 298757.9871 | 777306.9988 | 530527.9987 | 2372639.1054 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13605019.3383 | 30344754.8932 | 562.3413 | 0.12951 | 105047.9315 | 234299.8311 | 2141.5442 | 4776.519
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4601 | 0.86268 | 0.049661 | 4 | 71804.3848 | 156074.3591 | 1463.8295 | 3181.7869 | 128.5081 | 0 | 610.0146 | 373739.638 | 15976.6518 | 300883.0978 | 165249.9614 | 0 | 122804.5028 | 0 | 381675.0022 | 993040.0634 | 677770.2482 | 3031139.1655 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 14263519.3984 | 31003254.9533 | 749.8942 | 0.19864 | 71804.3848 | 156074.3591 | 1463.8295 | 3181.7869
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5842 | 1.187 | 0.073045 | 4 | 51593.9504 | 108886.608 | 1051.8125 | 2219.8008 | 131.2278 | 0 | 87.8326 | 473177.5212 | 20632.5266 | 387691.0398 | 214973.8101 | 0 | 144079.0976 | 0 | 483816.0581 | 1258790.139 | 859150.1354 | 3842310.3277 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 15074690.5607 | 31814426.1155 | 1000 | 0.29218 | 51593.9504 | 108886.608 | 1051.8125 | 2219.8008
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0728 | 1.6181 | 0.10445 | 4 | 38493.5456 | 78558.3446 | 784.743 | 1601.5181 | 133.3193 | 0 | 69.5616 | 593414.2747 | 26268.4588 | 496014.0952 | 280853.5953 | 0 | 169630.5577 | 0 | 610810.5829 | 1589203.8422 | 1084664.2772 | 4850859.6839 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 16083239.9168 | 32822975.4717 | 1333.5214 | 0.41782 | 38493.5456 | 78558.3446 | 784.743 | 1601.5181
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0756 | 2.196 | 0.14623 | 4 | 29671.7319 | 58291.4458 | 604.8984 | 1188.35 | 134.8205 | 0 | 65.0481 | 740048.802 | 33109.0685 | 632650.622 | 369431.8713 | 0 | 201570.0163 | 0 | 770956.0482 | 2005869.4926 | 1369047.1452 | 6122683.066 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 17355063.2989 | 34094798.8538 | 1778.2794 | 0.5849 | 29671.7319 | 58291.4458 | 604.8984 | 1188.35
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7326 | 2.9735 | 0.2037 | 4 | 23269.5553 | 43814.65 | 474.3814 | 893.2209 | 136.2396 | 0 | 102.8327 | 921154.7475 | 41602.5961 | 805503.1196 | 486885.234 | 0 | 239707.0693 | 0 | 972992.5789 | 2531527.102 | 1727819.2648 | 7727191.7121 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 18959571.945 | 35699307.4999 | 2371.3737 | 0.81478 | 23269.5553 | 43814.65 | 474.3814 | 893.2209
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.2675 | 4.0038 | 0.27948 | 4 | 18757.0539 | 33730.9366 | 382.3879 | 687.6508 | 137.1964 | 0 | 91.0929 | 1140234.6954 | 51816.297 | 1021304.2835 | 643951.6927 | 0 | 286339.922 | 0 | 1226022.2874 | 3189858.5 | 2177143.9713 | 9736671.6494 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 20969051.8823 | 37708787.4372 | 3162.2777 | 1.1179 | 18757.0539 | 33730.9366 | 382.3879 | 687.6508
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.9622 | 5.3729 | 0.38029 | 4 | 15443.4715 | 26448.1466 | 314.8361 | 539.1812 | 137.9227 | 0 | 85.3413 | 1406938.2023 | 64204.5231 | 1291612.8752 | 852429.3775 | 0 | 342973.2806 | 0 | 1543681.7209 | 4016343.1851 | 2741236.7514 | 12259419.9161 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 23491800.149 | 40231535.7039 | 4216.965 | 1.5211 | 15443.4715 | 26448.1466 | 314.8361 | 539.1812
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1884 | 7.1887 | 0.51398 | 4 | 12966.9954 | 21109.149 | 264.3497 | 430.3386 | 138.4731 | 0 | 120.6678 | 1731485.9656 | 79222.3234 | 1629765.7369 | 1128575.3705 | 0 | 411787.4431 | 0 | 1942526.3674 | 5054055.1411 | 3449496.4842 | 15426914.8322 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 26659295.0651 | 43399030.62 | 5623.4133 | 2.0559 | 12966.9954 | 21109.149 | 264.3497 | 430.3386
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4005 | 9.5843 | 0.69041 | 4 | 11089.0623 | 17150.578 | 226.0655 | 349.6377 | 138.8893 | 0 | 106.6104 | 2124938.6138 | 97358.7619 | 2050851.2525 | 1492814.3938 | 0 | 494950.961 | 0 | 2441756.4534 | 6352949.4187 | 4336018.5183 | 19391638.3735 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 30624018.6064 | 47363754.1613 | 7498.9421 | 2.7616 | 11089.0623 | 17150.578 | 226.0655 | 349.6377
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.813 | 12.3307 | 0.905 | 4 | 9645.1769 | 14269.4001 | 196.63 | 290.901 | 139.1702 | 0 | 108.725 | 2542143.6701 | 116521.9946 | 2508394.6692 | 1910754.2839 | 0 | 568720.7124 | 0 | 2982148.7788 | 7758939.3996 | 5295635.5705 | 23683259.079 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 34915639.3119 | 51655374.8668 | 10000 | 3.62 | 9645.1769 | 14269.4001 | 196.63 | 290.901
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.6233 | 15.1912 | 1.1501 | 4 | 8508.4577 | 12147.2963 | 173.4564 | 247.6391 | 139.3439 | 0 | 123.9013 | 2948611.2276 | 135121.1215 | 2963645.9482 | 2346369.0595 | 0 | 617153.6376 | 0 | 3514251.3878 | 9143361.2389 | 6240531.9229 | 27909045.5439 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 39141425.7768 | 55881161.3317 | 13335.2143 | 4.6003 | 8508.4577 | 12147.2963 | 173.4564 | 247.6391
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.5971 | 18.3816 | 1.4346 | 4 | 7609.5162 | 10526.7047 | 155.1303 | 214.6011 | 139.4366 | 0 | 145.6125 | 3376030.5052 | 154580.2353 | 3451697.2258 | 2832776.4886 | 0 | 656577.3257 | 0 | 4083948.0945 | 10625595.2088 | 7252187.0642 | 32433392.1481 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 43665772.3811 | 60405507.9359 | 17782.7941 | 5.7383 | 7609.5162 | 10526.7047 | 155.1303 | 214.6011
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.1971 | 21.7336 | 1.7474 | 4 | 6901.1256 | 9296.0074 | 140.6888 | 189.5117 | 139.4341 | 0 | 170.873 | 3801376.5113 | 173806.4534 | 3946690.3714 | 3345011.1228 | 0 | 680823.5909 | 0 | 4659606.1395 | 12123339.3582 | 8274428.2217 | 37005081.7692 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 48237462.0021 | 64977197.557 | 23713.7371 | 6.9898 | 6901.1256 | 9296.0074 | 140.6888 | 189.5117
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.8165 | 25.06 | 2.0727 | 4 | 6346.1539 | 8365.2688 | 129.3749 | 170.5373 | 139.3381 | 0 | 202.1193 | 4203378.3357 | 191808.2225 | 4423243.7441 | 3855151.755 | 0 | 687040.7123 | 0 | 5210642.8802 | 13557023.9245 | 9252947.3974 | 41381236.9719 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 52613617.2048 | 69353352.7597 | 31622.7766 | 8.2906 | 6346.1539 | 8365.2688 | 129.3749 | 170.5373
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.9102 | 28.1987 | 2.3931 | 4 | 5914.021 | 7662.7853 | 120.5653 | 156.2162 | 139.1679 | 0 | 185.7888 | 4566797.2094 | 207904.5016 | 4861701.1337 | 4338694.5259 | 0 | 676119.7214 | 0 | 5713974.6659 | 14866589.9833 | 10146753.1415 | 45378534.8827 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 56610915.1156 | 73350650.6705 | 42169.6503 | 9.5723 | 5914.021 | 7662.7853 | 120.5653 | 156.2162
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0487 | 31.03 | 2.6936 | 4 | 5579.4201 | 7133.0741 | 113.744 | 145.4174 | 138.952 | 0 | 221.2359 | 4882840.8849 | 221740.5829 | 5249211.0929 | 4777392.6085 | 0 | 651407.4137 | 0 | 6155211.1073 | 16014596.6938 | 10930291.3106 | 48882691.6946 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 60115071.9275 | 76854807.4824 | 56234.1325 | 10.7744 | 5579.4201 | 7133.0741 | 113.744 | 145.4174
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.9085 | 33.4731 | 2.9626 | 4 | 5321.6063 | 6734.1736 | 108.4881 | 137.2852 | 138.7203 | 0 | 250.1225 | 5147397.6607 | 233196.6997 | 5578166.6054 | 5159054.9602 | 0 | 616919.9734 | 0 | 6526547.0008 | 16980736.5171 | 11589701.5922 | 51831721.0094 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 63064101.2423 | 79803836.7972 | 74989.4209 | 11.8506 | 5321.6063 | 6734.1736 | 108.4881 | 137.2852
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.3823 | 35.509 | 3.1942 | 4 | 5123.8484 | 6434.0346 | 104.4566 | 131.1665 | 138.4961 | 0 | 233.1727 | 5362391.5525 | 242407.1256 | 5848838.0508 | 5479031.0075 | 0 | 577369.7894 | 0 | 6828914.6351 | 17767435.0775 | 12126639.5247 | 54233026.7631 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 65465406.996 | 82205142.5509 | 100000 | 12.7766 | 5123.8484 | 6434.0346 | 104.4566 | 131.1665
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.5159 | 37.1617 | 3.3872 | 4 | 4972.7101 | 6208.2088 | 101.3754 | 126.5627 | 138.2937 | 0 | 271.2446 | 5533429.3223 | 249664.4009 | 6066436.7214 | 5740202.1708 | 0 | 536883.5505 | 0 | 7069380.3047 | 18393077.4236 | 12553653.2815 | 56142727.1757 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 67375107.4086 | 84114842.9635 | 133352.1432 | 13.549 | 4972.7101 | 6208.2088 | 101.3754 | 126.5627
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.666 | 39.0803 | 3.5864 | 4 | 4856.0972 | 6022.9839 | 98.9981 | 122.7867 | 138.0641 | 0 | 231.3367 | 5728935.2023 | 257930.9011 | 6316691.7081 | 6044040.8213 | 0 | 517965.419 | 0 | 7357569.9802 | 19142887.8435 | 13065414.3002 | 58431436.1757 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 69663816.4087 | 86403551.9635 | 177827.941 | 14.3456 | 4856.0972 | 6022.9839 | 98.9981 | 122.7867
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.8996 | 40.2102 | 3.7204 | 4 | 4766.8939 | 5891.7642 | 97.1796 | 120.1116 | 137.9285 | 0 | 252.3944 | 5842538.8449 | 262714.3341 | 6462966.3093 | 6223154.2331 | 0 | 485722.7944 | 0 | 7518067.6411 | 19560469.8346 | 13350422.5895 | 59706056.581 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 70938436.8139 | 87678172.3688 | 237137.3706 | 14.8815 | 4766.8939 | 5891.7642 | 97.1796 | 120.1116
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.1593 | 41.0752 | 3.825 | 4 | 4699.1898 | 5793.2767 | 95.7993 | 118.1038 | 137.8211 | 0 | 216.7068 | 5928660.8169 | 266323.6049 | 6574419.6498 | 6360416.2238 | 0 | 457245.2005 | 0 | 7638955.5434 | 19874995.3587 | 13565092.7226 | 60666109.1205 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 71898489.3534 | 88638224.9083 | 316227.766 | 15.3002 | 4699.1898 | 5793.2767 | 95.7993 | 118.1038
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.6413 | 41.7311 | 3.9058 | 4 | 4647.9252 | 5719.3781 | 94.7542 | 116.5973 | 137.7374 | 0 | 251.9217 | 5993492.5 | 269030.8529 | 6658643.7767 | 6464697.9969 | 0 | 432983.9742 | 0 | 7729351.1492 | 20110186.1824 | 13725615.2925 | 61384001.7247 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 72616381.9576 | 89356117.5125 | 421696.5034 | 15.6234 | 4647.9252 | 5719.3781 | 94.7542 | 116.5973
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8728 | 42.3189 | 3.9756 | 4 | 4607.3479 | 5660.0104 | 93.927 | 115.387 | 137.6611 | 0 | 235.9536 | 6051252.9227 | 271435.948 | 6733911.707 | 6558289.7091 | 0 | 414133.395 | 0 | 7811319.2359 | 20323450.3299 | 13871172.4553 | 62034965.7029 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 73267345.9358 | 90007081.4907 | 562341.3252 | 15.9023 | 4607.3479 | 5660.0104 | 93.927 | 115.387
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2929 | 42.6919 | 4.0225 | 4 | 4578.4497 | 5618.8286 | 93.3379 | 114.5474 | 137.6118 | 0 | 242.5039 | 6087733.9554 | 272951.1348 | 6781572.7998 | 6617756.2324 | 0 | 398182.466 | 0 | 7861696.6695 | 20454522.0782 | 13960631.6168 | 62435046.9528 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 73667427.1857 | 90407162.7406 | 749894.2093 | 16.09 | 4578.4497 | 5618.8286 | 93.3379 | 114.5474
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3601 | 42.9717 | 4.0581 | 4 | 4556.6735 | 5587.9384 | 92.894 | 113.9177 | 137.5744 | 0 | 239.5211 | 6115015.2308 | 274082.3754 | 6817274.7305 | 6662402.3819 | 0 | 385496.8455 | 0 | 7899165.91 | 20552009.3561 | 14027168.6871 | 62732615.5172 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 73964995.7501 | 90704731.305 | 1000000 | 16.2322 | 4556.6735 | 5587.9384 | 92.894 | 113.9177
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.1714 | 43.1841 | 4.0851 | 4 | 4540.2809 | 5564.72 | 92.5598 | 113.4443 | 137.5458 | 0 | 212.6554 | 6135676.5087 | 274938.0559 | 6844347.6037 | 6696315.3557 | 0 | 375629.9672 | 0 | 7927493.9216 | 20625713.0314 | 14077472.9599 | 62957587.4041 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74189967.637 | 90929703.1919 | 1333521.4322 | 16.3404 | 4540.2809 | 5564.72 | 92.5598 | 113.4443
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.7561 | 43.337 | 4.105 | 4 | 4527.9514 | 5547.4162 | 92.3084 | 113.0916 | 137.5251 | 0 | 222.1064 | 6150526.2051 | 275552.4636 | 6863824.2315 | 6720744.0036 | 0 | 367772.2801 | 0 | 7947583.4817 | 20677981.9458 | 14113147.5681 | 63117132.1793 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74349512.4122 | 91089247.9671 | 1778279.41 | 16.4201 | 4527.9514 | 5547.4162 | 92.3084 | 113.0916
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.2165 | 43.4573 | 4.1204 | 4 | 4518.6841 | 5534.3347 | 92.1195 | 112.8249 | 137.5087 | 0 | 227.8489 | 6162196.1652 | 276034.9885 | 6879140.9012 | 6739972.9114 | 0 | 361907.8146 | 0 | 7963508.5845 | 20719415.7967 | 14141427.0227 | 63243604.1847 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74475984.4176 | 91215719.9725 | 2371373.7057 | 16.4818 | 4518.6841 | 5534.3347 | 92.1195 | 112.8249
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.5519 | 43.5449 | 4.1319 | 4 | 4511.7221 | 5524.5691 | 91.9776 | 112.6258 | 137.4968 | 0 | 259.3411 | 6170681.6633 | 276385.6492 | 6890284.1782 | 6753972.6198 | 0 | 357338.6529 | 0 | 7974978.4777 | 20749258.1061 | 14161795.012 | 63334694.3593 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74567074.5922 | 91306810.1471 | 3162277.6602 | 16.5274 | 4511.7221 | 5524.5691 | 91.9776 | 112.6258
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.8102 | 43.6123 | 4.1406 | 4 | 4506.4943 | 5517.2128 | 91.871 | 112.4758 | 137.4875 | 0 | 245.064 | 6177212.1953 | 276655.4189 | 6898863.5246 | 6764756.8623 | 0 | 353918.0033 | 0 | 7983848.3417 | 20772335.6727 | 14177545.9255 | 63405135.9444 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74637516.1773 | 91377251.7322 | 4216965.0343 | 16.5622 | 4506.4943 | 5517.2128 | 91.871 | 112.4758
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.9929 | 43.66 | 4.1469 | 4 | 4502.5699 | 5511.7468 | 91.791 | 112.3644 | 137.481 | 0 | 257.3703 | 6181823.4486 | 276845.8405 | 6904923.4443 | 6772377.3463 | 0 | 351231.347 | 0 | 7990008.5564 | 20788363.2877 | 14188485.102 | 63454058.3727 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74686438.6056 | 91426174.1605 | 5623413.2519 | 16.5875 | 4502.5699 | 5511.7468 | 91.791 | 112.3644
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1346 | 43.6969 | 4.1517 | 4 | 4499.6246 | 5507.6254 | 91.7309 | 112.2804 | 137.4759 | 0 | 239.8693 | 6185399.1516 | 276993.4704 | 6909623.449 | 6778289.3758 | 0 | 349239.1092 | 0 | 7994822.3768 | 20800887.861 | 14197033.3806 | 63492288.1744 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74724668.4073 | 91464403.9622 | 7498942.0933 | 16.6069 | 4499.6246 | 5507.6254 | 91.7309 | 112.2804
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.2318 | 43.7223 | 4.1552 | 4 | 4497.4147 | 5504.5757 | 91.6859 | 112.2182 | 137.4724 | 0 | 233.3745 | 6187851.6142 | 277094.7015 | 6912847.7081 | 6782346.0889 | 0 | 347661.0599 | 0 | 7998042.4573 | 20809265.8499 | 14202751.5302 | 63517861.0101 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74750241.243 | 91489976.7979 | 10000000 | 16.6207 | 4497.4147 | 5504.5757 | 91.6859 | 112.2182
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7271 | [19 empty] | 100 | 0
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3283 | [19 empty] | 133.3521 | 0
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.15523 | 0.002446 | 4 | 1282063.6073 | 3049323.4869 | 26136.6008 | 62164.5838 | 104.3004 | 0 | 58.533 | 99248.612 | 3553.6622 | 77620.0428 | 54864.8366 | 0 | 60995.284 | 0 | 115550.1507 | 300637.7894 | 205191.4688 | 917661.8464 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12543689.4972 | 29834531.4371 | 177.8279 | 0.009784 | 1282063.6073 | 3049323.4869 | 26136.6008 | 62164.5838
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1813 | 0.23013 | 0.007002 | 4 | 457530.0229 | 1074880.0232 | 9327.3684 | 21912.8832 | 111.9483 | 0 | 54.0668 | 136608.4015 | 5171.8075 | 105765.8767 | 66716.1451 | 0 | 69480.8583 | 0 | 149659.8047 | 389384.1124 | 265762.6577 | 1188549.6638 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12814577.3146 | 30105419.2545 | 237.1374 | 0.028008 | 457530.0229 | 1074880.0232 | 9327.3684 | 21912.8832
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.33393 | 0.013952 | 4 | 235777.3993 | 545595.5372 | 4806.6412 | 11122.703 | 118.49 | 0 | 63.6165 | 183460.6855 | 7283.8695 | 141793.6349 | 82778.312 | 0 | 79517.5524 | 0 | 192985.2812 | 502108.115 | 342699.1058 | 1532626.5564 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13158654.2072 | 30449496.1471 | 316.2278 | 0.05581 | 235777.3993 | 545595.5372 | 4806.6412 | 11122.703
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.47682 | 0.02409 | 4 | 141090.4269 | 320529.1228 | 2876.3192 | 6534.4197 | 123.9675 | 0 | 343.3195 | 241827.1893 | 9991.9271 | 187827.5933 | 104572.8674 | 0 | 91681.6875 | 0 | 248001.4932 | 645249.0133 | 440395.7101 | 1969547.4813 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13595575.1321 | 30886417.0721 | 421.6965 | 0.096361 | 141090.4269 | 320529.1228 | 2876.3192 | 6534.4197
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6822 | 0.66736 | 0.038253 | 4 | 92373.7884 | 205375.9774 | 1883.1646 | 4186.8671 | 128.3623 | 0 | 465.9623 | 312339.5113 | 13325.985 | 245048.3391 | 133399.6208 | 0 | 105763.357 | 0 | 315851.9572 | 821782.0024 | 560883.1026 | 2508393.8754 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14134421.5262 | 31425263.4661 | 562.3413 | 0.15301 | 92373.7884 | 205375.9774 | 1883.1646 | 4186.8671
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5379 | 0.92457 | 0.0578 | 4 | 64063.3465 | 138850.7239 | 1306.018 | 2830.6598 | 131.9035 | 0 | 616.5637 | 398736.9414 | 17457.3865 | 317298.158 | 172042.1186 | 0 | 122930.8416 | 0 | 401101.524 | 1043583.8882 | 712267.4472 | 3185418.3054 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14811445.9563 | 32102287.8962 | 749.8942 | 0.2312 | 64063.3465 | 138850.7239 | 1306.018 | 2830.6598
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.689 | 1.2735 | 0.084611 | 4 | 46301.5157 | 97391.0261 | 943.919 | 1985.4478 | 134.7269 | 0 | 84.4667 | 505290.6205 | 22585.4367 | 409149.2916 | 224471.7516 | 0 | 144290.4607 | 0 | 509257.1488 | 1324982.6382 | 904327.8763 | 4044355.2244 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 15670382.8752 | 32961224.8151 | 1000 | 0.33844 | 46301.5157 | 97391.0261 | 943.919 | 1985.4478
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2238 | 1.7398 | 0.12063 | 4 | 34698.2957 | 70532.1475 | 707.3717 | 1437.8932 | 136.9042 | 0 | 78.4051 | 634689.856 | 28812.7942 | 524385.1037 | 293876.0378 | 0 | 170305.1743 | 0 | 644306.8967 | 1676354.3798 | 1144146.3098 | 5116876.5523 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 16742904.2031 | 34033746.143 | 1333.5214 | 0.48253 | 34698.2957 | 70532.1475 | 707.3717 | 1437.8932
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2506 | 2.3531 | 0.16801 | 4 | 26886.1821 | 52614.9921 | 548.1112 | 1072.6278 | 138.4212 | 0 | 83.0298 | 789581.2875 | 36230.9157 | 667010.1627 | 385734.4986 | 0 | 201549.5158 | 0 | 811241.4883 | 2110683.9442 | 1440585.1621 | 6442616.975 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 18068644.6258 | 35359486.5658 | 1778.2794 | 0.67204 | 26886.1821 | 52614.9921 | 548.1112 | 1072.6278
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9689 | 3.1908 | 0.2341 | 4 | 21115.7644 | 39581.1778 | 430.4734 | 806.9158 | 139.9205 | 0 | 107.2233 | 984254.3525 | 45634.6747 | 850157.3576 | 510438.0216 | 0 | 239774.3869 | 0 | 1025800.9294 | 2668923.5976 | 1821595.1962 | 8146578.5165 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 19772606.1673 | 37063448.1073 | 2371.3737 | 0.93639 | 21115.7644 | 39581.1778 | 430.4734 | 806.9158
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5648 | 4.2928 | 0.32073 | 4 | 17061.9611 | 30539.5078 | 347.8312 | 622.5892 | 140.9098 | 0 | 91.811 | 1217936.087 | 56846.3729 | 1077161.1074 | 675789.0289 | 0 | 285974.6651 | 0 | 1292345.8319 | 3362418.7581 | 2294919.8932 | 10263391.7446 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 21889419.3954 | 39180261.3353 | 3162.2777 | 1.2829 | 17061.9611 | 30539.5078 | 347.8312 | 622.5892
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3689 | 5.7654 | 0.43623 | 4 | 14075.4913 | 23984.6612 | 286.9479 | 488.9598 | 141.6658 | 0 | 103.7346 | 1503889.2507 | 70503.5832 | 1363108.0595 | 895860.1204 | 0 | 342844.6035 | 0 | 1628720.1907 | 4237595.8398 | 2892246.2346 | 12934767.8824 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 24560795.5332 | 41851637.4731 | 4216.965 | 1.7449 | 14075.4913 | 23984.6612 | 286.9479 | 488.9598
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7322 | 7.7164 | 0.58934 | 4 | 11840.1119 | 19174.9048 | 241.3767 | 390.9064 | 142.2377 | 0 | 95.6104 | 1851507.0007 | 87041.357 | 1720434.2523 | 1187297.3874 | 0 | 411775.5293 | 0 | 2050641.6554 | 5335348.9429 | 3641485.284 | 16285531.409 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 27911559.0598 | 45202400.9998 | 5623.4133 | 2.3574 | 11840.1119 | 19174.9048 | 241.3767 | 390.9064
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.1043 | 10.2841 | 0.79104 | 4 | 10143.1982 | 15607.7751 | 206.7828 | 318.1856 | 142.6691 | 0 | 94.1463 | 2271937.1361 | 106966.1766 | 2164274.7374 | 1570805.6272 | 0 | 494697.0463 | 0 | 2577385.4822 | 6705828.3303 | 4576865.6264 | 20468760.1625 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 32094787.8133 | 49385629.7533 | 7498.9421 | 3.1642 | 10143.1982 | 15607.7751 | 206.7828 | 318.1856
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0789 | 13.65 | 1.0551 | 4 | 8840.7276 | 12937.881 | 180.2302 | 263.7562 | 142.9911 | 0 | 104.4716 | 2779206.2249 | 130906.3416 | 2713903.8803 | 2073560.2842 | 0 | 594830.2593 | 0 | 3234038.7262 | 8414305.3731 | 5742936.3138 | 25683687.4035 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 37309715.0543 | 54600556.9943 | 10000 | 4.2202 | 8840.7276 | 12937.881 | 180.2302 | 263.7562
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.6381 | 17.1902 | 1.3558 | 4 | 7833.5405 | 11021.9424 | 159.6973 | 224.6972 | 143.1718 | 0 | 116.9813 | 3274453.8902 | 154168.6767 | 3263313.9502 | 2602825.3061 | 0 | 667484.5035 | 0 | 3885276.0674 | 10108691.3477 | 6899389.5577 | 30855603.2996 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 42481630.9504 | 59772472.8903 | 13335.2143 | 5.423 | 7833.5405 | 11021.9424 | 159.6973 | 224.6972
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.0017 | 20.6557 | 1.6792 | 4 | 7039.1015 | 9613.3905 | 143.5016 | 195.982 | 143.2339 | 0 | 131.0981 | 3730399.2183 | 175447.683 | 3779617.0565 | 3121764.1739 | 0 | 704202.2828 | 0 | 4489457.8616 | 11680648.4415 | 7972282.5747 | 35653819.2923 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 47279846.9431 | 64570688.8831 | 17782.7941 | 6.7167 | 7039.1015 | 9613.3905 | 143.5016 | 195.982
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.8381 | 24.2379 | 2.029 | 4 | 6413.8002 | 8544.3135 | 130.754 | 174.1874 | 143.192 | 0 | 167.5715 | 4177450.3264 | 196132.751 | 4295605.6184 | 3659717.647 | 0 | 723676.4052 | 0 | 5090507.2717 | 13244455.7144 | 9039613.1714 | 40427158.9055 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 52053186.5563 | 69344028.4963 | 23713.7371 | 8.1158 | 6413.8002 | 8544.3135 | 130.754 | 174.1874
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.5159 | 27.734 | 2.3862 | 4 | 5924.5723 | 7736.091 | 120.7804 | 157.7107 | 143.0545 | 0 | 213.3546 | 4593620.486 | 215180.1163 | 4784959.3833 | 4186891.4021 | 0 | 723706.1635 | 0 | 5656699.445 | 14717571.6072 | 10045045.0378 | 44923673.6411 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 56549701.292 | 73840543.2319 | 31622.7766 | 9.5449 | 5924.5723 | 7736.091 | 120.7804 | 157.7107
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.5239 | 30.9868 | 2.7328 | 4 | 5544.0146 | 7125.7749 | 113.0222 | 145.2686 | 142.8466 | 0 | 227.7044 | 4965245.045 | 231982.978 | 5229613.3996 | 4680120.1296 | 0 | 706328.307 | 0 | 6167183.0451 | 16045745.2202 | 10951550.8199 | 48977768.9445 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 60603796.5953 | 77894638.5353 | 42169.6503 | 10.9314 | 5544.0146 | 7125.7749 | 113.0222 | 145.2686
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.4534 | 33.88 | 3.0531 | 4 | 5249.5742 | 6665.4235 | 107.0197 | 135.8837 | 142.6003 | 0 | 208.8826 | 5284405.6905 | 246230.443 | 5617652.1701 | 5121498.6579 | 0 | 675417.0941 | 0 | 6608629.5817 | 17194298.5553 | 11735462.0715 | 52483594.2642 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 64109621.915 | 81400463.855 | 56234.1325 | 12.2123 | 5249.5742 | 6665.4235 | 107.0197 | 135.8837
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0501 | 36.3508 | 3.3361 | 4 | 5022.845 | 6318.5656 | 102.3975 | 128.8125 | 142.3462 | 0 | 233.7384 | 5549072.8225 | 257896.9696 | 5944068.773 | 5500625.3565 | 0 | 635702.0087 | 0 | 6976072.7128 | 18150310.2095 | 12387959.6696 | 55401708.5222 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 67027736.173 | 84318578.1129 | 74989.4209 | 13.3446 | 5022.845 | 6318.5656 | 102.3975 | 128.8125
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2534 | 38.3948 | 3.5774 | 4 | 4848.9664 | 6057.2992 | 98.8527 | 123.4862 | 142.1061 | 0 | 224.4037 | 5762843.477 | 267210.1945 | 6210985.5818 | 5816005.5522 | 0 | 592081.9766 | 0 | 7273159.445 | 18923268.9458 | 12915519.8898 | 57761075.0628 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 69387102.7136 | 86677944.6535 | 100000 | 14.3097 | 4848.9664 | 6057.2992 | 98.8527 | 123.4862
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.3313 | 40.6663 | 3.821 | 4 | 4715.2168 | 5846.5271 | 96.1261 | 119.1894 | 141.8283 | 0 | 259.6856 | 5995722.3954 | 277279.8444 | 6504448.4427 | 6167848.0552 | 0 | 569056.9879 | 0 | 7610598.733 | 19801216.7548 | 13514737.3095 | 60440908.523 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 72066936.1738 | 89357778.1137 | 133352.1432 | 15.2839 | 4715.2168 | 5846.5271 | 96.1261 | 119.1894
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.4003 | 42.0857 | 3.9927 | 4 | 4611.9669 | 5694.6133 | 94.0212 | 116.0924 | 141.6593 | 0 | 233.3859 | 6139128.2353 | 283461.1383 | 6686185.1194 | 6388098.5908 | 0 | 530952.3563 | 0 | 7810851.9216 | 20322234.474 | 13870342.6087 | 62031254.4445 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 73657282.0953 | 90948124.0352 | 177827.941 | 15.9709 | 4611.9669 | 5694.6133 | 94.0212 | 116.0924
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.4003 | 43.1984 | 4.1296 | 4 | 4533.4137 | 5580.1646 | 92.4198 | 113.7592 | 141.521 | 0 | 250.7142 | 6250243.4484 | 288222.2983 | 6827865.0586 | 6561267.9647 | 0 | 496802.0687 | 0 | 7965516.327 | 20724639.5309 | 14144992.3286 | 63259549.025 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 74885576.6759 | 92176418.6158 | 237137.3706 | 16.5186 | 4533.4137 | 5580.1646 | 92.4198 | 113.7592
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.4696 | 44.0478 | 4.2362 | 4 | 4473.8062 | 5494.2167 | 91.2046 | 112.007 | 141.4121 | 0 | 271.8254 | 6334302.1682 | 291807.0336 | 6935561.3773 | 6693762.9489 | 0 | 466978.1263 | 0 | 8081740.5452 | 21027031.1057 | 14351380.7919 | 64182564.0971 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 75808591.7479 | 93099433.6878 | 316227.766 | 16.945 | 4473.8062 | 5494.2167 | 91.2046 | 112.007
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8324 | 44.6991 | 4.3189 | 4 | 4428.6736 | 5429.5526 | 90.2845 | 110.6888 | 141.3266 | 0 | 256.3528 | 6398314.4976 | 294526.8431 | 7017875.7143 | 6795533.6915 | 0 | 442055.6979 | 0 | 8169839.5133 | 21256246.5491 | 14507825.042 | 64882217.5488 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 76508245.1997 | 93799087.1396 | 421696.5034 | 17.2757 | 4428.6736 | 5429.5526 | 90.2845 | 110.6888
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.6159 | 45.1891 | 4.382 | 4 | 4394.5642 | 5381.03 | 89.5891 | 109.6996 | 141.2612 | 0 | 265.6139 | 6446230.4277 | 296556.8795 | 7079665.7506 | 6872216.4414 | 0 | 421523.0916 | 0 | 8235315.1104 | 21426600.6218 | 14624095.197 | 65402203.52 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 77028231.1708 | 94319073.1107 | 562341.3252 | 17.5281 | 4394.5642 | 5381.03 | 89.5891 | 109.6996
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.287 | 45.6472 | 4.4378 | 4 | 4367.3505 | 5341.4199 | 89.0343 | 108.8921 | 141.1994 | 0 | 280.4073 | 6490834.4858 | 298442.4395 | 7137312.8727 | 6943974.7448 | 0 | 406164.5946 | 0 | 8297924.3636 | 21589497.0559 | 14735275.3604 | 65899425.9175 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 77525453.5683 | 94816295.5083 | 749894.2093 | 17.7511 | 4367.3505 | 5341.4199 | 89.0343 | 108.8921
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.2829 | 45.9195 | 4.4736 | 4 | 4348.1881 | 5314.4527 | 88.6437 | 108.3423 | 141.1621 | 0 | 270.6726 | 6517262.9409 | 299557.2247 | 7171537.8933 | 6986684.1139 | 0 | 393152.6282 | 0 | 8333595.9724 | 21682307.2646 | 14798620.2349 | 66182718.2729 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 77808745.9238 | 95099587.8637 | 1000000 | 17.8945 | 4348.1881 | 5314.4527 | 88.6437 | 108.3423
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.0406 | 46.1265 | 4.5009 | 4 | 4333.7634 | 5294.1753 | 88.3496 | 107.9289 | 141.1335 | 0 | 272.7884 | 6537300.0908 | 300401.3557 | 7197517.3609 | 7019154.745 | 0 | 383063.8215 | 0 | 8360600.5758 | 21752567.7033 | 14846574.4281 | 66397180.0811 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78023207.7319 | 95314049.6718 | 1333521.4322 | 18.0036 | 4333.7634 | 5294.1753 | 88.3496 | 107.9289
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5935 | 46.2773 | 4.5211 | 4 | 4322.9139 | 5279.0295 | 88.1284 | 107.6202 | 141.1126 | 0 | 253.7819 | 6551881.336 | 301015.0396 | 7216440.291 | 7042833.6693 | 0 | 375116.2336 | 0 | 8380041.7621 | 21803149.6822 | 14881097.668 | 66551575.6819 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78177603.3327 | 95468445.2727 | 1778279.41 | 18.0845 | 4322.9139 | 5279.0295 | 88.1284 | 107.6202
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.0151 | 46.3922 | 4.5365 | 4 | 4314.7591 | 5267.6376 | 87.9622 | 107.3879 | 141.0966 | 0 | 249.1513 | 6562977.3662 | 301481.715 | 7230849.8444 | 7060880.4637 | 0 | 369069.1662 | 0 | 8394850.8366 | 21841679.8561 | 14907395.3035 | 66669184.5516 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78295212.2024 | 95586054.1423 | 2371373.7057 | 18.1459 | 4314.7591 | 5267.6376 | 87.9622 | 107.3879
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3272 | 46.4773 | 4.5479 | 4 | 4308.633 | 5259.1092 | 87.8373 | 107.2141 | 141.0847 | 0 | 241.6952 | 6571180.0173 | 301826.5118 | 7241507.4769 | 7074237.082 | 0 | 364415.0326 | 0 | 8405734.787 | 21869997.6625 | 14926722.7882 | 66755621.3583 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78381649.0091 | 95672490.949 | 3162277.6602 | 18.1918 | 4308.633 | 5259.1092 | 87.8373 | 107.2141
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5681 | 46.5429 | 4.5567 | 4 | 4304.0327 | 5252.6828 | 87.7435 | 107.083 | 141.0755 | 0 | 247.8906 | 6577506.2876 | 302092.334 | 7249730.1701 | 7084547.1167 | 0 | 360935.1659 | 0 | 8414176.3189 | 21891960.797 | 14941713.0787 | 66822661.2688 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78448688.9196 | 95739530.8596 | 4216965.0343 | 18.2268 | 4304.0327 | 5252.6828 | 87.7435 | 107.083
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7339 | 46.588 | 4.563 | 4 | 4300.5794 | 5247.9256 | 87.6731 | 106.9861 | 141.0692 | 0 | 236.9216 | 6581854.4112 | 302274.9682 | 7255383.5878 | 7091638.4334 | 0 | 358169.9059 | 0 | 8419835.3096 | 21906684.3298 | 14951762.1924 | 66867603.1384 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78493630.7892 | 95784472.7291 | 5623413.2519 | 18.2519 | 4300.5794 | 5247.9256 | 87.6731 | 106.9861
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.8628 | 46.6231 | 4.5678 | 4 | 4297.9878 | 5244.3382 | 87.6203 | 106.9129 | 141.0642 | 0 | 263.1848 | 6585233.674 | 302416.8813 | 7259778.1055 | 7097152.0403 | 0 | 356119.5352 | 0 | 8424273.0921 | 21918230.5296 | 14959642.7111 | 66902846.5689 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78528874.2197 | 95819716.1597 | 7498942.0933 | 18.2711 | 4297.9878 | 5244.3382 | 87.6203 | 106.9129
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.9749 | 46.6536 | 4.5717 | 4 | 4296.0432 | 5241.5828 | 87.5807 | 106.8568 | 141.06 | 0 | 263.4773 | 6588170.4368 | 302540.2048 | 7263597.5297 | 7101944.9133 | 0 | 354704.5872 | 0 | 8428273.492 | 21928638.7496 | 14966746.5351 | 66934616.4485 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78560644.0993 | 95851486.0392 | 10000000 | 18.2867 | 4296.0432 | 5241.5828 | 87.5807 | 106.8568
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8573 | [19 empty] | 100 | 0
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.1975 | [19 empty] | 133.3521 | 0
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.16514 | 0.0034985 | 4 | 927398.7748 | 2202940.419 | 18906.2784 | 44909.9201 | 106.7186 | 0 | 63.7207 | 105202.8777 | 3831.5453 | 81414.522 | 56097.9214 | 0 | 61030.5304 | 0 | 119955.1847 | 312098.7845 | 213013.8334 | 952645.1995 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 12978180.359 | 30828332.8113 | 177.8279 | 0.013994 | 927398.7748 | 2202940.419 | 18906.2784 | 44909.9201
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2202 | 0.24908 | 0.0088455 | 4 | 375278.79 | 879775.7 | 7650.5657 | 17935.4176 | 114.9296 | 0 | 62.5268 | 146804.732 | 5675.2341 | 112435.669 | 69086.87 | 0 | 70423.794 | 0 | 157726.2567 | 410371.3657 | 280086.8894 | 1252610.811 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13278145.9705 | 31128298.4228 | 237.1374 | 0.035382 | 375278.79 | 879775.7 | 7650.5657 | 17935.4176
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5834 | 0.35651 | 0.016689 | 4 | 204132.2019 | 471529.8502 | 4161.511 | 9612.7738 | 121.4119 | 0 | 52.2559 | 195022.7739 | 7903.3221 | 149108.4554 | 85396.1838 | 0 | 79584.439 | 0 | 201635.9179 | 524615.2972 | 358060.7201 | 1601327.1094 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13626862.269 | 31477014.7212 | 316.2278 | 0.066755 | 204132.2019 | 471529.8502 | 4161.511 | 9612.7738
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.50755 | 0.028144 | 4 | 125076.3789 | 283634.981 | 2549.8512 | 5782.2827 | 127.0251 | 0 | 361.8167 | 256459.3995 | 10824.4024 | 197038.7599 | 107853.1302 | 0 | 91401.8061 | 0 | 258795.2242 | 673332.0873 | 459562.9852 | 2055267.7948 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14080802.9543 | 31930955.4065 | 421.6965 | 0.11258 | 125076.3789 | 283634.981 | 2549.8512 | 5782.2827
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7405 | 0.71347 | 0.044342 | 4 | 82627.4047 | 183266.1719 | 1684.4714 | 3736.1288 | 131.6245 | 0 | 479.9299 | 332429.3242 | 14513.9694 | 257928.8817 | 138488.099 | 0 | 105768.7694 | 0 | 331160.327 | 861611.2406 | 588067.376 | 2629967.9873 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14655503.1469 | 32505655.5991 | 562.3413 | 0.17737 | 82627.4047 | 183266.1719 | 1684.4714 | 3736.1288
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 0.99552 | 0.066869 | 4 | 57528.9586 | 124264.1374 | 1172.8056 | 2533.2925 | 135.3574 | 0 | 644.2683 | 426704.5036 | 19146.8123 | 335849.4051 | 180016.9849 | 0 | 123812.1929 | 0 | 423356.6605 | 1101487.1883 | 751787.6393 | 3362161.387 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 15387696.5465 | 33237848.9988 | 749.8942 | 0.26748 | 57528.9586 | 124264.1374 | 1172.8056 | 2533.2925
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8011 | 1.366 | 0.097112 | 4 | 41917.6829 | 87870.205 | 854.5487 | 1791.353 | 138.2351 | 0 | 88.885 | 539171.2341 | 24706.0059 | 431743.6136 | 234264.3246 | 0 | 144652.9539 | 0 | 536069.8715 | 1394743.8427 | 951941.3318 | 4257293.1781 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 16282828.3377 | 34132980.7899 | 1000 | 0.38845 | 41917.6829 | 87870.205 | 854.5487 | 1791.353
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3675 | 1.8659 | 0.13814 | 4 | 31521.0577 | 63826.1282 | 642.5994 | 1301.182 | 140.4756 | 0 | 84.1227 | 677456.1001 | 31558.9699 | 553270.1753 | 307844.3711 | 0 | 170577.4886 | 0 | 678875.7709 | 1766295.4994 | 1205532.9721 | 5391411.3473 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 17416946.5068 | 35267098.9591 | 1333.5214 | 0.55255 | 31521.0577 | 63826.1282 | 642.5994 | 1301.182
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4358 | 2.5226 | 0.19191 | 4 | 24511.1232 | 47764.4747 | 499.6924 | 973.7434 | 142.0198 | 0 | 82.6673 | 842612.087 | 39693.1023 | 703470.0292 | 404791.3729 | 0 | 201740.2818 | 0 | 854999.6805 | 2224533.7842 | 1518290.0173 | 6790130.3553 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 18815665.5149 | 36665817.9671 | 1778.2794 | 0.76764 | 24511.1232 | 47764.4747 | 499.6924 | 973.7434
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2079 | 3.4204 | 0.26709 | 4 | 19295.0433 | 36002.7657 | 393.3556 | 733.9651 | 143.5969 | 0 | 96.671 | 1050611.9031 | 50042.9831 | 896540.0484 | 536128.8604 | 0 | 239730.5204 | 0 | 1081491.183 | 2813818.2139 | 1920488.7492 | 8588852.4616 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 20614387.6212 | 38464540.0734 | 2371.3737 | 1.0684 | 19295.0433 | 36002.7657 | 393.3556 | 733.9651
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.8937 | 4.6055 | 0.36556 | 4 | 15629.2177 | 27836.6444 | 318.6227 | 567.4876 | 144.6244 | 0 | 96.2949 | 1300785.7647 | 62378.5752 | 1136660.2928 | 709982.616 | 0 | 286221.3196 | 0 | 1363451.1416 | 3547420.1881 | 2421187.1706 | 10828087.0685 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 22853622.2281 | 40703774.6803 | 3162.2777 | 1.4622 | 15629.2177 | 27836.6444 | 318.6227 | 567.4876
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.7905 | 6.1795 | 0.49631 | 4 | 12925.5965 | 21916.9521 | 263.5058 | 446.8067 | 145.4051 | 0 | 104.9611 | 1605144.4827 | 77314.6653 | 1437344.866 | 939771.7732 | 0 | 342742.812 | 0 | 1716904.2537 | 4467032.6826 | 3048841.5942 | 13635097.1298 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 25660632.2893 | 43510784.7415 | 4216.965 | 1.9853 | 12925.5965 | 21916.9521 | 263.5058 | 446.8067
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2775 | 8.2646 | 0.66945 | 4 | 10896.3586 | 17562.3483 | 222.137 | 358.0322 | 145.9967 | 0 | 82.5873 | 1975034.9565 | 95383.1053 | 1813067.5623 | 1243214.2783 | 0 | 411328.1403 | 0 | 2159830.9366 | 5619437.0549 | 3835381.2578 | 17152677.292 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 29178212.4516 | 47028364.9038 | 5623.4133 | 2.6778 | 10896.3586 | 17562.3483 | 222.137 | 358.0322
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8205 | 11.0139 | 0.89814 | 4 | 9348.9435 | 14317.5834 | 190.5909 | 291.8833 | 146.4436 | 0 | 110.9729 | 2423747.4666 | 117246.9008 | 2280645.407 | 1645586.9669 | 0 | 494145.1921 | 0 | 2714935.054 | 7063704.1008 | 4821123.1934 | 21561134.2816 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 33586669.4411 | 51436821.8933 | 7498.9421 | 3.5926 | 9348.9435 | 14317.5834 | 190.5909 | 291.8833
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9996 | 14.6115 | 1.197 | 4 | 8160.2419 | 11888.2484 | 166.3576 | 242.358 | 146.7757 | 0 | 96.3771 | 2964242.5915 | 143468.3965 | 2858671.9585 | 2172158.7459 | 0 | 593937.9831 | 0 | 3405667.0734 | 8860847.1267 | 6047710.2362 | 27046704.1117 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 39072239.2712 | 56922391.7235 | 10000 | 4.7881 | 8160.2419 | 11888.2484 | 166.3576 | 242.358
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3944 | 19.2343 | 1.5797 | 4 | 7246.8824 | 10071.8339 | 147.7375 | 205.328 | 146.9817 | 0 | 98.3424 | 3604355.6189 | 174337.9051 | 3561304.311 | 2849268.7905 | 0 | 712545.6902 | 0 | 4251706.8031 | 11062068.9568 | 7550089.3658 | 33765677.4415 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 45791212.6011 | 63641365.0533 | 13335.2143 | 6.3187 | 7246.8824 | 10071.8339 | 147.7375 | 205.328
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.4233 | 23.0736 | 1.9491 | 4 | 6541.1965 | 8830.7317 | 133.3511 | 180.0264 | 147.0105 | 0 | 154.2496 | 4101136.6909 | 198092.7686 | 4119389.4516 | 3412763.0589 | 0 | 751477.9017 | 0 | 4907315.3499 | 12767827.9117 | 8714304.9024 | 38972308.0356 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 50997843.1952 | 68847995.6474 | 17782.7941 | 7.7964 | 6541.1965 | 8830.7317 | 133.3511 | 180.0264
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.4271 | 26.8691 | 2.336 | 4 | 5986.5552 | 7896.9243 | 122.044 | 160.9895 | 146.9259 | 0 | 156.1853 | 4567273.6369 | 220153.6256 | 4653360.2197 | 3971634.3931 | 0 | 765230.565 | 0 | 5529284.4517 | 14386063.9312 | 9818784.2371 | 43911785.0602 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 55937320.2198 | 73787472.672 | 23713.7371 | 9.3438 | 5986.5552 | 7896.9243 | 122.044 | 160.9895
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1197 | 30.5202 | 2.7249 | 4 | 5553.1653 | 7190.8761 | 113.2088 | 146.5957 | 146.7458 | 0 | 181.8735 | 4995637.9769 | 240173.6219 | 5153319.3233 | 4511523.8446 | 0 | 758680.2962 | 0 | 6107140.6745 | 15889527.2882 | 10844928.8713 | 48500931.8968 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 60526467.0564 | 78376619.5086 | 31622.7766 | 10.8995 | 5553.1653 | 7190.8761 | 113.2088 | 146.5957
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.0017 | 33.8697 | 3.0963 | 4 | 5216.3932 | 6657.6291 | 106.3432 | 135.7248 | 146.5008 | 0 | 198.7388 | 5373293.3883 | 257578.2254 | 5601937.2816 | 5009286.1331 | 0 | 734593.5015 | 0 | 6620908.5267 | 17226245.8513 | 11757266.7575 | 52581109.6654 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 64606644.825 | 82456797.2772 | 42169.6503 | 12.3853 | 5216.3932 | 6657.6291 | 106.3432 | 135.7248
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7038 | 36.8118 | 3.4347 | 4 | 4956.0096 | 6255.2449 | 101.035 | 127.5216 | 146.2257 | 0 | 254.43 | 5693966.0296 | 272144.713 | 5989063.877 | 5448804.0972 | 0 | 697518.0462 | 0 | 7059583.7376 | 18367588.7654 | 12536256.7486 | 56064926.0146 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 68090461.1741 | 85940613.6264 | 56234.1325 | 13.739 | 4956.0096 | 6255.2449 | 101.035 | 127.5216
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.013 | 39.2963 | 3.7303 | 4 | 4755.6148 | 5951.8938 | 96.9496 | 121.3374 | 145.9511 | 0 | 230.7176 | 5957353.3601 | 283952.0961 | 6311462.5214 | 5822805.4313 | 0 | 652534.081 | 0 | 7420961.921 | 19307820.6699 | 13177984.3433 | 58934874.424 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 70960409.5836 | 88810562.0358 | 74989.4209 | 14.9214 | 4755.6148 | 5951.8938 | 96.9496 | 121.3374
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.8996 | 41.333 | 3.9805 | 4 | 4601.9896 | 5723.0861 | 93.8178 | 116.6729 | 145.698 | 0 | 245.3231 | 6168895.3598 | 293358.9409 | 6572860.7362 | 6135134.9564 | 0 | 604547.0566 | 0 | 7712170.8494 | 20065486.5664 | 13695106.8861 | 61247561.3516 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 73273096.5112 | 91123248.9634 | 100000 | 15.922 | 4601.9896 | 5723.0861 | 93.8178 | 116.6729
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.0313 | 43.7294 | 4.2431 | 4 | 4482.4429 | 5534.1513 | 91.3807 | 112.8212 | 145.4143 | 0 | 253.9071 | 6413710.7909 | 304213.0913 | 6877213.7817 | 6503520.1815 | 0 | 581877.4144 | 0 | 8065408.7514 | 20984539.1283 | 14322379.1442 | 64052862.2837 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 76078397.4433 | 93928549.8955 | 133352.1432 | 16.9725 | 4482.4429 | 5534.1513 | 91.3807 | 112.8212
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8692 | 45.1442 | 4.4204 | 4 | 4391.1726 | 5400.7123 | 89.52 | 110.1008 | 145.2403 | 0 | 221.1604 | 6555936.8498 | 310474.0773 | 7055409.4672 | 6722117.9432 | 0 | 541566.8853 | 0 | 8262347.0369 | 21496932.1496 | 14672097.9099 | 65616882.3192 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 77642417.4788 | 95492569.931 | 177827.941 | 17.6815 | 4391.1726 | 5400.7123 | 89.52 | 110.1008
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6204 | 46.2345 | 4.5599 | 4 | 4321.7632 | 5300.4046 | 88.105 | 108.0559 | 145.101 | 0 | 256.0489 | 6664355.1453 | 315219.4151 | 7192019.5281 | 6891259.6487 | 0 | 505365.0945 | 0 | 8411605.3443 | 21885271.6485 | 14937147.5974 | 66802243.4219 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 78827778.5815 | 96677931.0337 | 237137.3706 | 18.2397 | 4321.7632 | 5300.4046 | 88.105 | 108.0559
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.6903 | 47.1219 | 4.6725 | 4 | 4269.1051 | 5224.1733 | 87.0315 | 106.5018 | 144.9842 | 0 | 256.9736 | 6751833.1519 | 319028.1314 | 7302780.9006 | 7029108.108 | 0 | 475896.0905 | 0 | 8532672.0891 | 22200262.4842 | 15152135.3153 | 67763716.271 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 79789251.4306 | 97639403.8828 | 316227.766 | 18.6899 | 4269.1051 | 5224.1733 | 87.0315 | 106.5018
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.9166 | 47.7609 | 4.7563 | 4 | 4229.1958 | 5167.432 | 86.2179 | 105.3451 | 144.898 | 0 | 276.2247 | 6814271.1514 | 321725.4477 | 7382307.4664 | 7127234.8137 | 0 | 450118.5582 | 0 | 8617306.4006 | 22420463.6017 | 15302427.1026 | 68435854.5424 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 80461389.7019 | 98311542.1541 | 421696.5034 | 19.0252 | 4229.1958 | 5167.432 | 86.2179 | 105.3451
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5802 | 48.2368 | 4.8199 | 4 | 4199.0335 | 5124.899 | 85.603 | 104.478 | 144.8326 | 0 | 264.8973 | 6860560.6812 | 323719.1741 | 7441426.5316 | 7200435.3914 | 0 | 428868.1521 | 0 | 8679453.8728 | 22582158.5763 | 15412787.2453 | 68929409.6249 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 80954944.7844 | 98805097.2367 | 562341.3252 | 19.2794 | 4199.0335 | 5124.899 | 85.603 | 104.478
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.946 | 48.3412 | 4.8501 | 4 | 4174.9181 | 5095.0124 | 85.1114 | 103.8687 | 144.8179 | 0 | 336.5728 | 6870671.7822 | 324153.2412 | 7454371.1825 | 7216501.4832 | 0 | 402203.7969 | 0 | 8684481.5795 | 22595239.6378 | 15421715.3385 | 68969338.0418 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 80994873.2014 | 98845025.6536 | 749894.2093 | 19.4004 | 4174.9181 | 5095.0124 | 85.1114 | 103.8687
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.1212 | 48.9615 | 4.9133 | 4 | 4157.8889 | 5066.1502 | 84.7642 | 103.2803 | 144.7317 | 0 | 251.8915 | 6930677.4542 | 326729.8657 | 7531230.9639 | 7312039.4525 | 0 | 399863.4578 | 0 | 8775211.0657 | 22831299.1496 | 15582830.8059 | 69689882.2153 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 81715417.3749 | 99565569.8271 | 1000000 | 19.6531 | 4157.8889 | 5066.1502 | 84.7642 | 103.2803
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.825 | 49.1617 | 4.9406 | 4 | 4145.1377 | 5048.3749 | 84.5042 | 102.918 | 144.7034 | 0 | 242.3363 | 6949964.2473 | 327555.6966 | 7555993.0061 | 7342903.3466 | 0 | 389515.4205 | 0 | 8800713.3697 | 22897650.9133 | 15628117.248 | 69892413.2481 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 81917948.4077 | 99768100.8599 | 1333521.4322 | 19.7624 | 4145.1377 | 5048.3749 | 84.5042 | 102.918
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.3586 | 49.3133 | 4.9613 | 4 | 4135.5468 | 5035.0146 | 84.3087 | 102.6456 | 144.6818 | 0 | 241.4783 | 6964549.5596 | 328179.6069 | 7574735.1623 | 7366289.4158 | 0 | 381566.2473 | 0 | 8819974.7968 | 22947765.1957 | 15662321.2755 | 70045381.2598 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82070916.4194 | 99921068.8716 | 1778279.41 | 19.8452 | 4135.5468 | 5035.0146 | 84.3087 | 102.6456
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.7413 | 49.4219 | 4.9765 | 4 | 4128.338 | 5025.0596 | 84.1618 | 102.4426 | 144.6663 | 0 | 232.414 | 6974988.4384 | 328625.7976 | 7588158.2154 | 7383052.2343 | 0 | 375310.0476 | 0 | 8833552.546 | 22983091.714 | 15686432.3501 | 70153211.3434 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82178746.503 | 100028898.9552 | 2371373.7057 | 19.906 | 4128.338 | 5025.0596 | 84.1618 | 102.4426
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.036 | 49.5055 | 4.9881 | 4 | 4122.9224 | 5017.5607 | 84.0513 | 102.2898 | 144.6543 | 0 | 249.0246 | 6983016.3815 | 328968.7598 | 7598485.9091 | 7395957.1309 | 0 | 370605.255 | 0 | 8844043.0402 | 23010385.8278 | 15705061.1436 | 70236523.4479 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82262058.6075 | 100112211.0597 | 3162277.6602 | 19.9524 | 4122.9224 | 5017.5607 | 84.0513 | 102.2898
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.2601 | 49.5691 | 4.9969 | 4 | 4118.8556 | 5011.9231 | 83.9684 | 102.1748 | 144.6452 | 0 | 249.3517 | 6989115.668 | 329229.2226 | 7606335.2698 | 7405769.6822 | 0 | 367057.9533 | 0 | 8852028.0404 | 23031161.1604 | 15719240.735 | 70299937.7315 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82325472.8911 | 100175625.3433 | 4216965.0343 | 19.9875 | 4118.8556 | 5011.9231 | 83.9684 | 102.1748
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4233 | 49.6153 | 5.0033 | 4 | 4115.8028 | 5007.7134 | 83.9062 | 102.089 | 144.6386 | 0 | 261.5195 | 6993552.581 | 329418.6304 | 7612046.9447 | 7412912.4059 | 0 | 364327.7249 | 0 | 8857780.7319 | 23046128.4836 | 15729456.2407 | 70345623.743 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82371158.9026 | 100221311.3548 | 5623413.2519 | 20.0134 | 4115.8028 | 5007.7134 | 83.9062 | 102.089
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.5501 | 49.6513 | 5.0083 | 4 | 4113.5117 | 5004.5383 | 83.8595 | 102.0243 | 144.6334 | 0 | 243.3228 | 6997000.7166 | 329565.7993 | 7616486.5747 | 7418465.7241 | 0 | 362304.9162 | 0 | 8862291.255 | 23057863.9396 | 15737465.9305 | 70381444.856 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82406980.0155 | 100257132.4677 | 7498942.0933 | 20.0332 | 4113.5117 | 5004.5383 | 83.8595 | 102.0243
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6427 | 49.6775 | 5.012 | 4 | 4111.7926 | 5002.1668 | 83.8245 | 101.9759 | 144.6296 | 0 | 237.9228 | 6999516.3655 | 329673.1468 | 7619726.1445 | 7422518.7667 | 0 | 360756.9186 | 0 | 8865554.6234 | 23066354.5548 | 15743260.9498 | 70407361.47 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82432896.6296 | 100283049.0818 | 10000000 | 20.0479 | 4111.7926 | 5002.1668 | 83.8245 | 101.9759
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4729 | [19 empty] | 100 | 0
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.74031 | 0.11962 | 0.00097493 | 4 | 3386910.1146 | 8109721.1153 | 69046.7438 | 165327.6341 | 100.7607 | 0 | 46.2252 | 80986.228 | 2822.521 | 63181.5226 | 48615.2099 | 0 | 55299.8404 | 0 | 97853.0756 | 254593.6302 | 173765.384 | 777117.4116 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13208020.1708 | 31625687.2625 | 133.3521 | 0.0038997 | 3386910.1146 | 8109721.1153 | 69046.7438 | 165327.6341
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.17968 | 0.0047327 | 4 | 709799.7997 | 1682696.2111 | 14470.229 | 34304.0383 | 109.6424 | 0 | 49.2199 | 113552.3609 | 4222.0304 | 86912.8578 | 58012.463 | 0 | 62151.2763 | 0 | 126691.8855 | 329626.298 | 224976.7215 | 1006145.8935 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13437048.6527 | 31854715.7444 | 177.8279 | 0.018931 | 709799.7997 | 1682696.2111 | 14470.229 | 34304.0383
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2545 | 0.26763 | 0.010833 | 4 | 317204.5066 | 742253.0763 | 6466.6429 | 15131.8329 | 117.8078 | 0 | 47.6057 | 156803.9213 | 6186.0933 | 118841.4139 | 71366.8065 | 0 | 70984.5873 | 0 | 165431.3007 | 430418.3098 | 293769.3407 | 1313801.7736 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13744704.5328 | 32162371.6245 | 237.1374 | 0.043331 | 317204.5066 | 742253.0763 | 6466.6429 | 15131.8329
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.38448 | 0.01981 | 4 | 178165.0418 | 410590.8937 | 3632.1354 | 8370.4507 | 124.5364 | 0 | 268.8185 | 208865.7377 | 8651.8202 | 158056.4368 | 88681.2733 | 0 | 80447.0167 | 0 | 212433.891 | 552709.4082 | 377235.5282 | 1687081.112 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14117983.8712 | 32535650.9629 | 316.2278 | 0.079241 | 178165.0418 | 410590.8937 | 3632.1354 | 8370.4507
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.54607 | 0.032828 | 4 | 111155.2995 | 251414.7053 | 2266.0511 | 5125.4288 | 130.2525 | 0 | 365.1546 | 274195.1116 | 11843.5851 | 208447.6089 | 112430.5257 | 0 | 92109.4614 | 0 | 272620.2542 | 709301.9793 | 484113.1755 | 2165061.7017 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14595964.4609 | 33013631.5526 | 421.6965 | 0.13131 | 111155.2995 | 251414.7053 | 2266.0511 | 5125.4288
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8183 | 0.76812 | 0.051228 | 4 | 74205.5866 | 164087.0357 | 1512.7813 | 3345.1362 | 134.9887 | 0 | 489.7965 | 355558.2558 | 15902.1092 | 272994.048 | 144747.6176 | 0 | 106628.067 | 0 | 349373.7381 | 908998.8 | 620410.3591 | 2774612.9947 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 15205515.7539 | 33623182.8455 | 562.3413 | 0.20491 | 74205.5866 | 164087.0357 | 1512.7813 | 3345.1362
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.717 | 1.0648 | 0.076381 | 4 | 52242.8808 | 112524.9507 | 1065.0418 | 2293.9733 | 138.7584 | 0 | 62.9828 | 454141.2755 | 20878.9614 | 353616.3515 | 187382.1968 | 0 | 123891.9697 | 0 | 444565.1944 | 1156667.443 | 789449.297 | 3530592.6894 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 15961495.4486 | 34379162.5403 | 749.8942 | 0.30552 | 52242.8808 | 112524.9507 | 1065.0418 | 2293.9733
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9131 | 1.4638 | 0.11076 | 4 | 38177.0502 | 79748.2435 | 778.2908 | 1625.7758 | 141.7389 | 0 | 90.5396 | 574905.5914 | 27030.07 | 455242.4787 | 245337.3101 | 0 | 144904.2755 | 0 | 564493.6931 | 1468696.7958 | 1002415.7418 | 4483025.9564 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 16913928.7156 | 35331595.8073 | 1000 | 0.44304 | 38177.0502 | 79748.2435 | 778.2908 | 1625.7758
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5138 | 1.9993 | 0.15708 | 4 | 28822.6287 | 58134.2853 | 587.5883 | 1185.146 | 144.0439 | 0 | 76.5268 | 722333.8791 | 34546.9656 | 583297.7985 | 322747.3131 | 0 | 170791.771 | 0 | 715149.9137 | 1860673.3779 | 1269947.8135 | 5679488.8324 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 18110391.5916 | 36528058.6833 | 1333.5214 | 0.62834 | 28822.6287 | 58134.2853 | 587.5883 | 1185.146
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 2.703 | 0.21764 | 4 | 22495.6869 | 43651.6667 | 458.605 | 889.8983 | 145.6273 | 0 | 78.7313 | 898322.9546 | 43446.0675 | 741682.2061 | 423935.9771 | 0 | 202099.8648 | 0 | 900699.9574 | 2343436.5301 | 1599443.5846 | 7153067.1422 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 19583969.9014 | 38001636.9931 | 1778.2794 | 0.87057 | 22495.6869 | 43651.6667 | 458.605 | 889.8983
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4636 | 3.6644 | 0.30248 | 4 | 17752.4834 | 32974.5054 | 361.9084 | 672.2299 | 147.2742 | 0 | 105.511 | 1120116.6377 | 54806.9193 | 945073.5897 | 561540.2481 | 0 | 239908.8144 | 0 | 1139364.0216 | 2964391.4684 | 2023258.0894 | 9048459.7885 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 21479362.5477 | 39897029.6394 | 2371.3737 | 1.2099 | 17752.4834 | 32974.5054 | 361.9084 | 672.2299
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2226 | 4.9311 | 0.41342 | 4 | 14413.6371 | 25551.1336 | 293.8415 | 520.8944 | 148.3334 | 0 | 98.7482 | 1386412.0693 | 68314.1007 | 1197619.8345 | 743608.3913 | 0 | 286145.4584 | 0 | 1436018.9432 | 3736226.7221 | 2550051.5096 | 11404397.0291 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 23835299.7883 | 42252966.88 | 3162.2777 | 1.6537 | 14413.6371 | 25551.1336 | 293.8415 | 520.8944
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2138 | 6.6141 | 0.56095 | 4 | 11941.1475 | 20149.3873 | 243.4364 | 410.7725 | 149.139 | 0 | 90.7863 | 1710764.3354 | 84706.2298 | 1513930.4773 | 985469.5694 | 0 | 342357.2614 | 0 | 1808518.8706 | 4705395.123 | 3211528.8577 | 14362670.7246 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 26793573.4838 | 45211240.5754 | 4216.965 | 2.2438 | 11941.1475 | 20149.3873 | 243.4364 | 410.7725
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8474 | 8.8516 | 0.75695 | 4 | 10079.4268 | 16162.274 | 205.4827 | 329.4898 | 149.7516 | 0 | 111.2678 | 2106587.4663 | 104630.5333 | 1910600.4103 | 1306942.5444 | 0 | 411129.9622 | 0 | 2277557.4575 | 5925737.313 | 4044437.4779 | 18087623.1649 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 30518525.9241 | 48936193.0158 | 5623.4133 | 3.0278 | 10079.4268 | 16162.274 | 205.4827 | 329.4898
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5588 | 11.7899 | 1.0144 | 4 | 8663.6982 | 13202.5636 | 176.6212 | 269.1521 | 150.2131 | 0 | 113.9166 | 2584248.2188 | 128559.4461 | 2402326.4105 | 1728152.1316 | 0 | 493659.9748 | 0 | 2861409.0109 | 7444799.2906 | 5081228.4912 | 22724382.9744 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 35155285.7336 | 53572952.8253 | 7498.9421 | 4.0578 | 8663.6982 | 13202.5636 | 176.6212 | 269.1521
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.94 | 15.627 | 1.3502 | 4 | 7574.8207 | 10985.0288 | 154.423 | 223.9447 | 150.5546 | 0 | 118.2842 | 3158454.4572 | 157182.1161 | 3009080.4395 | 2277205.3225 | 0 | 592926.3601 | 0 | 3585990.9912 | 9330012.9711 | 6367925.5654 | 28478778.223 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 40909680.9822 | 59327348.0739 | 10000 | 5.4007 | 7574.8207 | 10985.0288 | 154.423 | 223.9447
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.5757 | 20.5498 | 1.7793 | 4 | 6737.2811 | 9325.1195 | 137.3486 | 190.1052 | 150.7601 | 0 | 127.3167 | 3837653.3757 | 190828.3919 | 3745632.5504 | 2982628.0658 | 0 | 710959.5323 | 0 | 4472403.7473 | 11636277.1342 | 7941998.2457 | 35518381.0433 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 47949283.8025 | 66366950.8941 | 13335.2143 | 7.117 | 6737.2811 | 9325.1195 | 137.3486 | 190.1052
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.8427 | 25.6463 | 2.2477 | 4 | 6101.9831 | 8150.4404 | 124.3972 | 166.1578 | 150.7646 | 0 | 121.2717 | 4490604.8026 | 222851.9742 | 4471955.8939 | 3716249.5854 | 0 | 798213.9973 | 0 | 5342951.7388 | 13901264.4343 | 9487898.6188 | 42431991.0454 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 54862893.8046 | 73280560.8963 | 17782.7941 | 8.991 | 6101.9831 | 8150.4404 | 124.3972 | 166.1578
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.9755 | 29.6495 | 2.6729 | 4 | 5608.3114 | 7330.9388 | 114.333 | 149.4511 | 150.6343 | 0 | 158.0168 | 4974972.1712 | 246311.435 | 5022561.9351 | 4296542.6119 | 0 | 805787.4349 | 0 | 5985008.4793 | 15571764.3691 | 10628049.1497 | 47530997.5861 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 59961900.3453 | 78379567.437 | 23713.7371 | 10.6916 | 5608.3114 | 7330.9388 | 114.333 | 149.4511
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6339 | 33.445 | 3.094 | 4 | 5223.0445 | 6711.2204 | 106.4788 | 136.8173 | 150.4108 | 0 | 204.3685 | 5414537.9917 | 267319.4267 | 5531418.3877 | 4851224.5632 | 0 | 792208.1484 | 0 | 6574116.3219 | 17104502.133 | 11674174.1681 | 52209501.1409 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 64640403.9001 | 83058070.9917 | 31622.7766 | 12.376 | 5223.0445 | 6711.2204 | 106.4788 | 136.8173
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3667 | 36.8877 | 3.4912 | 4 | 4924.0195 | 6242.8884 | 100.3828 | 127.2697 | 150.129 | 0 | 200.0655 | 5798447.4485 | 285403.891 | 5983461.4372 | 5358968.039 | 0 | 761370.916 | 0 | 7093184.1753 | 18455010.2121 | 12595923.6823 | 56331769.8014 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 68762672.5605 | 87180339.6522 | 42169.6503 | 13.9647 | 4924.0195 | 6242.8884 | 100.3828 | 127.2697
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7944 | 39.8634 | 3.8473 | 4 | 4693.0381 | 5889.8152 | 95.6739 | 120.0718 | 149.8273 | 0 | 215.5437 | 6119574.0169 | 300285.9272 | 6367814.1705 | 5799426.8439 | 0 | 717769.6551 | 0 | 7528899.5393 | 19588652.2116 | 13369657.6409 | 59792080.0053 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 72222982.7645 | 90640649.8562 | 56234.1325 | 15.3894 | 4693.0381 | 5889.8152 | 95.6739 | 120.0718
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8445 | 42.3649 | 4.1556 | 4 | 4515.3608 | 5623.3596 | 92.0517 | 114.6398 | 149.5327 | 0 | 253.0235 | 6382224.9005 | 312263.3962 | 6686841.2602 | 6170437.1154 | 0 | 667924.1259 | 0 | 7885679.4113 | 20516920.253 | 14003219.6532 | 62625510.1159 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 75056412.8751 | 93474079.9668 | 74989.4209 | 16.6225 | 4515.3608 | 5623.3596 | 92.0517 | 114.6398
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.9024 | 45.153 | 4.4698 | 4 | 4377.8599 | 5407.9705 | 89.2486 | 110.2488 | 149.1933 | 0 | 244.1953 | 6668521.2595 | 325196.8208 | 7038216.3516 | 6585573.6069 | 0 | 640750.3457 | 0 | 8290720.77 | 21570754.7828 | 14722483.3739 | 65842217.3112 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 78273120.0704 | 96690787.1621 | 100000 | 17.8793 | 4377.8599 | 5407.9705 | 89.2486 | 110.2488
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.7903 | 46.9534 | 4.6967 | 4 | 4271.5724 | 5251.9288 | 87.0818 | 107.0677 | 148.9746 | 0 | 249.0593 | 6850197.7645 | 333353.2476 | 7262909.5668 | 6854387.2607 | 0 | 595283.379 | 0 | 8539491.1753 | 22218004.3476 | 15164244.5016 | 67817871.2431 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 80248774.0023 | 98666441.094 | 133352.1432 | 18.7867 | 4271.5724 | 5251.9288 | 87.0818 | 107.0677
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.4307 | 48.3601 | 4.878 | 4 | 4190.4686 | 5134.3926 | 85.4284 | 104.6715 | 148.7952 | 0 | 268.7281 | 6990238.9854 | 339592.911 | 7437339.0689 | 7065001.12 | 0 | 553054.5813 | 0 | 8730238.3999 | 22714289.4985 | 15502969.3147 | 69332723.8797 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 81763626.6389 | 100181293.7305 | 177827.941 | 19.5118 | 4190.4686 | 5134.3926 | 85.4284 | 104.6715
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.0239 | 49.4422 | 5.0202 | 4 | 4128.7788 | 5045.9558 | 84.1707 | 102.8686 | 148.6521 | 0 | 263.6576 | 7096851.2577 | 344312.1107 | 7570902.8044 | 7227469.6527 | 0 | 515582.3965 | 0 | 8874496.1066 | 23089618.4598 | 15759139.043 | 70478371.8313 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 82909274.5905 | 101326941.6822 | 237137.3706 | 20.0808 | 4128.7788 | 5045.9558 | 84.1707 | 102.8686
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7908 | 50.2713 | 5.1308 | 4 | 4081.9732 | 4979.3866 | 83.2165 | 101.5115 | 148.5394 | 0 | 259.3494 | 7177874.319 | 347880.0256 | 7672866.8445 | 7352202.9556 | 0 | 483670.197 | 0 | 8983452.7932 | 23373101.4085 | 15952621.9805 | 71343670.5239 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 83774573.283 | 102192240.3747 | 316227.766 | 20.5231 | 4081.9732 | 4979.3866 | 83.2165 | 101.5115
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.8862 | 50.8967 | 5.2155 | 4 | 4046.5354 | 4929.3769 | 82.4941 | 100.492 | 148.4527 | 0 | 254.1783 | 7238619.2745 | 350544.1515 | 7749577.2028 | 7446446.4872 | 0 | 457060.4955 | 0 | 9064476.5685 | 23583908.6514 | 16096502.2555 | 71987135.0869 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 84418037.8461 | 102835704.9378 | 421696.5034 | 20.8618 | 4046.5354 | 4929.3769 | 82.4941 | 100.492
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.465 | 51.3664 | 5.2799 | 4 | 4019.7526 | 4891.8195 | 81.9481 | 99.7264 | 148.3867 | 0 | 289.5389 | 7284043.1222 | 352530.1919 | 7807089.9529 | 7517331.9826 | 0 | 435378.0192 | 0 | 9124585.5748 | 23740299.9559 | 16203242.5343 | 72464501.3338 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 84895404.093 | 103313071.1847 | 562341.3252 | 21.1196 | 4019.7526 | 4891.8195 | 81.9481 | 99.7264
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6487 | 51.7179 | 5.3286 | 4 | 3999.5418 | 4863.6299 | 81.5361 | 99.1517 | 148.3367 | 0 | 259.1526 | 7317906.0554 | 354007.2431 | 7850050.4903 | 7570409.6671 | 0 | 418008.9046 | 0 | 9169049.1206 | 23855984.9811 | 16282199.9411 | 72817616.4032 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 85248519.1624 | 103666186.2541 | 749894.2093 | 21.3146 | 3999.5418 | 4863.6299 | 81.5361 | 99.1517
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8861 | 52.0847 | 5.3749 | 4 | 3983.1004 | 4839.7537 | 81.2009 | 98.6649 | 148.2843 | 0 | 232.3829 | 7353152.0817 | 355542.1638 | 7894831.6733 | 7625845.414 | 0 | 405760.3174 | 0 | 9217701.3436 | 23982568.0854 | 16368595.5108 | 73203996.5898 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 85634899.349 | 104052566.4407 | 1000000 | 21.4996 | 3983.1004 | 4839.7537 | 81.2009 | 98.6649
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.5318 | 52.2756 | 5.402 | 4 | 3971.7823 | 4824.1327 | 80.9702 | 98.3465 | 148.2566 | 0 | 231.9867 | 7371456.1731 | 356337.5076 | 7918126.7803 | 7654735.1874 | 0 | 395092.446 | 0 | 9241341.7568 | 24044075.5913 | 16410575.6474 | 73391741.0898 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 85822643.849 | 104240310.9407 | 1333521.4322 | 21.6081 | 3971.7823 | 4824.1327 | 80.9702 | 98.3465
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.0186 | 52.4195 | 5.4225 | 4 | 3963.2694 | 4812.3995 | 80.7966 | 98.1073 | 148.2357 | 0 | 279.4722 | 7385224.8068 | 356935.1832 | 7935664.1238 | 7676505.7493 | 0 | 386885.7127 | 0 | 9259074.0746 | 24090211.4448 | 16442064.3154 | 73532565.4105 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 85963468.1697 | 104381135.2614 | 1778279.41 | 21.69 | 3963.2694 | 4812.3995 | 80.7966 | 98.1073
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3935 | 52.5302 | 5.4381 | 4 | 3956.8706 | 4803.5593 | 80.6662 | 97.9271 | 148.2196 | 0 | 271.2362 | 7395809.2391 | 357394.3016 | 7949153.9184 | 7693264.114 | 0 | 380685.9881 | 0 | 9272759.9488 | 24125819.2823 | 16466367.3962 | 73641254.1884 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86072156.9476 | 104489824.0392 | 2371373.7057 | 21.7526 | 3956.8706 | 4803.5593 | 80.6662 | 97.9271
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6714 | 52.6122 | 5.4498 | 4 | 3952.0636 | 4796.9388 | 80.5682 | 97.7921 | 148.2076 | 0 | 257.8157 | 7403642.3708 | 357733.875 | 7959142.0343 | 7705679.4235 | 0 | 375928.4482 | 0 | 9282829.1992 | 24152017.4062 | 16484248.1541 | 73721220.9112 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86152123.6704 | 104569790.7621 | 3162277.6602 | 21.7993 | 3952.0636 | 4796.9388 | 80.5682 | 97.7921
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.8734 | 52.6718 | 5.4584 | 4 | 3948.4538 | 4791.9947 | 80.4946 | 97.6913 | 148.1988 | 0 | 298.4683 | 7409333.4082 | 357980.4712 | 7966401.4437 | 7714706.7874 | 0 | 372258.464 | 0 | 9290065.4241 | 24170844.579 | 16497098.0863 | 73778688.6639 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86209591.423 | 104627258.5147 | 4216965.0343 | 21.8338 | 3948.4538 | 4791.9947 | 80.4946 | 97.6913
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0197 | 52.715 | 5.4648 | 4 | 3945.7441 | 4788.3046 | 80.4393 | 97.6161 | 148.1925 | 0 | 276.1799 | 7413451.2424 | 358158.8354 | 7971655.571 | 7721242.5664 | 0 | 369433.0421 | 0 | 9295237.0903 | 24184300.1937 | 16506281.8199 | 73819760.3612 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86250663.1204 | 104668330.2121 | 5623413.2519 | 21.8592 | 3945.7441 | 4788.3046 | 80.4393 | 97.6161
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.1318 | 52.748 | 5.4696 | 4 | 3943.7104 | 4785.5282 | 80.3979 | 97.5595 | 148.1876 | 0 | 270.2945 | 7416603.1935 | 358295.3347 | 7975677.9827 | 7726247.2527 | 0 | 367320.7804 | 0 | 9299216.3721 | 24194653.4688 | 16513348.1428 | 73851362.5277 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86282265.2869 | 104699932.3786 | 7498942.0933 | 21.8784 | 3943.7104 | 4785.5282 | 80.3979 | 97.5595
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2218 | 52.7745 | 5.4734 | 4 | 3942.1845 | 4783.4243 | 80.3668 | 97.5166 | 148.1837 | 0 | 284.6099 | 7419134.1656 | 358404.9317 | 7978908.2408 | 7730266.9387 | 0 | 365782.9618 | 0 | 9302473.9231 | 24203128.948 | 16519132.8316 | 73877232.9413 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86308135.7005 | 104725802.7922 | 10000000 | 21.8935 | 3942.1845 | 4783.4243 | 80.3668 | 97.5166
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4963 | [19 empty] | 100 | 0
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75975 | 0.12792 | 0.0017282 | 4 | 1974754.0516 | 4722332.0986 | 40258.0324 | 96271.1273 | 103.118 | 0 | 51.8337 | 86184.2077 | 3054.685 | 66544.7522 | 49732.5306 | 0 | 55649.9916 | 0 | 101854.8052 | 265005.3099 | 180871.5693 | 808897.8515 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13651028.3012 | 32644414.1596 | 133.3521 | 0.0069128 | 1974754.0516 | 4722332.0986 | 40258.0324 | 96271.1273
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.1906 | 0.0059796 | 4 | 580543.9108 | 1374628.8359 | 11835.1729 | 28023.6681 | 112.0613 | 0 | 53.3999 | 120012.9409 | 4539.1124 | 90955.8967 | 59358.2938 | 0 | 62095.8384 | 0 | 131415.2121 | 341915.4248 | 233364.3031 | 1043657.0222 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13885787.4719 | 32879173.3302 | 177.8279 | 0.023919 | 580543.9108 | 1374628.8359 | 11835.1729 | 28023.6681
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.28234 | 0.012797 | 4 | 277445.1744 | 648503.4883 | 5656.0952 | 13220.6208 | 120.3539 | 0 | 52.475 | 164988.2132 | 6626.2959 | 123817.7026 | 73003.0212 | 0 | 70493.4998 | 0 | 171182.2057 | 445380.985 | 303981.6739 | 1359473.5973 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14201604.047 | 33194989.9054 | 237.1374 | 0.051187 | 277445.1744 | 648503.4883 | 5656.0952 | 13220.6208
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.41079 | 0.023073 | 4 | 158278.7152 | 364076.7807 | 3226.7257 | 7422.1976 | 127.5216 | 0 | 277.0627 | 221998.8114 | 9392.1794 | 166307.9307 | 91708.0811 | 0 | 80655.8931 | 0 | 222324.5293 | 578442.8202 | 394799.1106 | 1765629.3558 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14607759.8054 | 33601145.6638 | 316.2278 | 0.092291 | 158278.7152 | 364076.7807 | 3226.7257 | 7422.1976
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.58638 | 0.037883 | 4 | 99780.9951 | 225122.9389 | 2034.1705 | 4589.4356 | 133.4781 | 0 | 374.9508 | 292581.3687 | 12932.4987 | 220187.4962 | 117048.392 | 0 | 92720.9695 | 0 | 286833.5827 | 746282.1447 | 509352.8983 | 2277939.3507 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15120069.8004 | 34113455.6587 | 421.6965 | 0.15153 | 99780.9951 | 225122.9389 | 2034.1705 | 4589.4356
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8961 | 0.82521 | 0.058638 | 4 | 67213.4203 | 148191.3636 | 1370.2365 | 3021.0814 | 138.3503 | 0 | 498.8673 | 379490.7445 | 17384.8384 | 288465.0955 | 150963.898 | 0 | 107365.3131 | 0 | 368031.2569 | 957541.8369 | 653541.9792 | 2922784.9627 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15764915.4123 | 34758301.2707 | 562.3413 | 0.23455 | 67213.4203 | 148191.3636 | 1370.2365 | 3021.0814
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 1.1408 | 0.086904 | 4 | 47634.6919 | 102273.9478 | 971.0976 | 2084.9928 | 142.182 | 0 | 76.1765 | 483930.0244 | 22819.1679 | 372814.1304 | 196101.0538 | 0 | 124227.3366 | 0 | 467957.7681 | 1217530.1212 | 830989.3255 | 3716368.9279 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16558499.3775 | 35551885.2359 | 749.8942 | 0.34761 | 47634.6919 | 102273.9478 | 971.0976 | 2084.9928
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.04 | 1.5711 | 0.12568 | 4 | 34948.7945 | 72730.176 | 712.4784 | 1482.703 | 145.2667 | 0 | 74.8465 | 613359.2501 | 29598.4357 | 480608.9477 | 257130.4365 | 0 | 145578.5072 | 0 | 595247.4751 | 1548711.8281 | 1057027.6456 | 4727262.526 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 17569392.9756 | 36562778.834 | 1000 | 0.50272 | 34948.7945 | 72730.176 | 712.4784 | 1482.703
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6648 | 2.1395 | 0.17733 | 4 | 26529.2066 | 53305.8626 | 540.8338 | 1086.7121 | 147.611 | 0 | 86.2171 | 768937.5943 | 37754.2409 | 614345.1331 | 337356.583 | 0 | 170971.5505 | 0 | 752452.3897 | 1957726.7689 | 1336188.747 | 5975733.0075 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 18817863.4572 | 37811249.3155 | 1333.5214 | 0.70933 | 26529.2066 | 53305.8626 | 540.8338 | 1086.7121
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8185 | 2.8897 | 0.2454 | 4 | 20749.7225 | 40099.4753 | 423.0112 | 817.482 | 149.2569 | 0 | 74.8621 | 955996.4162 | 47510.4148 | 780503.7028 | 443868.6451 | 0 | 201835.1935 | 0 | 947588.6052 | 2465431.1736 | 1682707.4355 | 7525441.5867 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 20367572.0364 | 39360957.8947 | 1778.2794 | 0.98158 | 20749.7225 | 40099.4753 | 423.0112 | 817.482
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7265 | 3.9224 | 0.34064 | 4 | 16418.4784 | 30358.0357 | 334.7129 | 618.8896 | 150.9489 | 0 | 92.8258 | 1192966.322 | 59988.2325 | 995556.3495 | 588016.53 | 0 | 240042.3287 | 0 | 1199862.2075 | 3121795.3382 | 2130689.4648 | 9528916.7732 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 22371047.2228 | 41364433.0812 | 2371.3737 | 1.3626 | 16418.4784 | 30358.0357 | 334.7129 | 618.8896
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.571 | 5.279 | 0.46528 | 4 | 13356.1064 | 23561.4401 | 272.2823 | 480.3318 | 152.0412 | 0 | 103.966 | 1476994.8574 | 74826.9726 | 1261700.1238 | 779502.4061 | 0 | 286293.8457 | 0 | 1512934.1002 | 3936344.1833 | 2686635.7889 | 12015232.2781 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 24857362.7278 | 43850748.5861 | 3162.2777 | 1.8611 | 13356.1064 | 23561.4401 | 272.2823 | 480.3318
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6548 | 7.0797 | 0.63172 | 4 | 11077.5851 | 18594.0698 | 225.8316 | 379.0653 | 152.8694 | 0 | 96.569 | 1823498.2991 | 92944.8871 | 1594589.9294 | 1038185.5059 | 0 | 342144.0702 | 0 | 1907631.4498 | 4963265.7233 | 3387530.841 | 15149790.7058 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 27991921.1555 | 46985307.0138 | 4216.965 | 2.5269 | 11077.5851 | 18594.0698 | 225.8316 | 379.0653
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4152 | 9.4708 | 0.85204 | 4 | 9366.5205 | 14939.4642 | 190.9492 | 304.5612 | 153.5006 | 0 | 100.0103 | 2245235.326 | 114842.645 | 2011676.5916 | 1378075.4818 | 0 | 410564.9142 | 0 | 2402554.0339 | 6250952.7645 | 4266403.706 | 19080305.463 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 31922435.9127 | 50915821.7711 | 5623.4133 | 3.4081 | 9366.5205 | 14939.4642 | 190.9492 | 304.5612
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.2969 | 12.6121 | 1.1415 | 4 | 8063.6383 | 12223.4238 | 164.3882 | 249.191 | 153.9767 | 0 | 91.7129 | 2754462.8545 | 141152.6186 | 2528965.8335 | 1823645.0904 | 0 | 492845.8354 | 0 | 3019018.1706 | 7854865.9942 | 5361107.4424 | 23976063.8396 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 36818194.2893 | 55811580.1476 | 7498.9421 | 4.566 | 8063.6383 | 12223.4238 | 164.3882 | 249.191
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.9022 | 16.7157 | 1.519 | 4 | 7060.414 | 10186.2996 | 143.9361 | 207.6615 | 154.3276 | 0 | 99.5934 | 3367000.0628 | 172650.6165 | 3167459.3627 | 2405604.3485 | 0 | 592040.3057 | 0 | 3784854.3315 | 9847414.5902 | 6721062.802 | 30058086.4198 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 42900216.8695 | 61893602.7279 | 10000 | 6.0762 | 7060.414 | 10186.2996 | 143.9361 | 207.6615
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.7742 | 21.9596 | 1.9997 | 4 | 6289.7419 | 8664.2796 | 128.2249 | 176.6331 | 154.531 | 0 | 113.1405 | 4088639.7784 | 209500.4953 | 3939602.6859 | 3150020.1412 | 0 | 709432.5123 | 0 | 4717906.2891 | 12275024.3885 | 8377956.3717 | 37468082.6624 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 50310213.112 | 69303598.9704 | 13335.2143 | 7.9988 | 6289.7419 | 8664.2796 | 128.2249 | 176.6331
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.2201 | 28.3997 | 2.5842 | 4 | 5709.4817 | 7546.9699 | 116.3955 | 153.8552 | 154.4945 | 0 | 129.5366 | 4906325.0728 | 250712.7084 | 4839654.0853 | 4067389.219 | 0 | 844130.9011 | 0 | 5814202.6747 | 15127362.7027 | 10324735.8808 | 46174513.2448 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 59016643.6945 | 78010029.5528 | 17782.7941 | 10.3366 | 5709.4817 | 7546.9699 | 116.3955 | 153.8552
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.3996 | 32.5881 | 3.0476 | 4 | 5270.1202 | 6828.1811 | 107.4385 | 139.2017 | 154.3171 | 0 | 151.6522 | 5405855.3536 | 275465.3174 | 5403329.7858 | 4667189.7038 | 0 | 844393.0924 | 0 | 6472530.9687 | 16840197.8818 | 11493781.0858 | 51402743.1893 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 64244873.639 | 83238259.4974 | 23713.7371 | 12.1904 | 5270.1202 | 6828.1811 | 107.4385 | 139.2017
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.9802 | 36.5103 | 3.4998 | 4 | 4927.5492 | 6284.3153 | 100.4548 | 128.1143 | 154.0506 | 0 | 177.0254 | 5854010.016 | 297315.062 | 5918668.0638 | 5231951.5508 | 0 | 823369.0813 | 0 | 7068872.3718 | 18391755.8864 | 12552751.3053 | 56138693.3375 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 68980823.7871 | 87974209.6455 | 31622.7766 | 13.999 | 4927.5492 | 6284.3153 | 100.4548 | 128.1143
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5077 | 40.0169 | 3.9195 | 4 | 4661.7691 | 5873.225 | 95.0365 | 119.7336 | 153.7344 | 0 | 212.6079 | 6240114.3719 | 315816.3321 | 6370553.5227 | 5739600.5051 | 0 | 785269.8104 | 0 | 7586028.2714 | 19737289.4538 | 13471105.613 | 60245777.8803 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 73087908.33 | 92081294.1883 | 42169.6503 | 15.6781 | 4661.7691 | 5873.225 | 95.0365 | 119.7336
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.7159 | 43.0339 | 4.2929 | 4 | 4456.5091 | 5562.591 | 90.852 | 113.4009 | 153.4055 | 0 | 262.2638 | 6562093.0164 | 330979.4155 | 6753464.9928 | 6178907.4202 | 0 | 736005.8203 | 0 | 8018965.7594 | 20863703.9899 | 14239906.6794 | 63684027.0938 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 76526157.5435 | 95519543.4019 | 56234.1325 | 17.1718 | 4456.5091 | 5562.591 | 90.852 | 113.4009
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8 | 45.9637 | 4.6441 | 4 | 4298.5682 | 5321.01 | 87.6321 | 108.476 | 153.0407 | 0 | 228.7019 | 6866283.9496 | 345064.0493 | 7120590.2945 | 6607992.6926 | 0 | 695432.0941 | 0 | 8437791.6012 | 21953402.9174 | 14983648.5884 | 67010206.1871 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 79852336.6368 | 98845722.4952 | 74989.4209 | 18.5765 | 4298.5682 | 5321.01 | 87.6321 | 108.476
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.9191 | 48.5574 | 4.9542 | 4 | 4174.6951 | 5133.1444 | 85.1068 | 104.6461 | 152.7342 | 0 | 252.0631 | 7129490.4031 | 357100.0363 | 7441962.1419 | 6978374.372 | 0 | 657229.5895 | 0 | 8800021.0516 | 22895849.6439 | 15626887.8446 | 69886915.0828 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 82729045.5324 | 101722431.3908 | 100000 | 19.8168 | 4174.6951 | 5133.1444 | 85.1068 | 104.6461
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.607 | 50.3521 | 5.1859 | 4 | 4079.8587 | 4995.4778 | 83.1734 | 101.8396 | 152.5073 | 0 | 263.4641 | 7308070.5138 | 365148.1141 | 7662524.7928 | 7233391.5492 | 0 | 609302.3261 | 0 | 9039590.5454 | 23519160.3242 | 16052310.1917 | 71789498.3574 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 84631628.807 | 103625014.6654 | 133352.1432 | 20.7438 | 4079.8587 | 4995.4778 | 83.1734 | 101.8396
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.0628 | 51.7456 | 5.3698 | 4 | 4007.4821 | 4891.746 | 81.6979 | 99.7249 | 152.3226 | 0 | 266.2369 | 7444836.5949 | 371248.7117 | 7832813.1679 | 7431267.4987 | 0 | 565249.7018 | 0 | 9221712.1133 | 23993003.2855 | 16375717.7492 | 73235848.823 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 86077979.2727 | 105071365.131 | 177827.941 | 21.4793 | 4007.4821 | 4891.746 | 81.6979 | 99.7249
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5413 | 52.8258 | 5.5144 | 4 | 3952.4054 | 4813.4893 | 80.5751 | 98.1295 | 152.1743 | 0 | 256.9545 | 7549725.3372 | 375888.4235 | 7964250.3511 | 7584567.533 | 0 | 526887.424 | 0 | 9360514.4368 | 24354138.459 | 16622199.9258 | 74338171.8904 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 87180302.34 | 106173688.1984 | 237137.3706 | 22.0575 | 3952.4054 | 4813.4893 | 80.5751 | 98.1295
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.2092 | 53.6497 | 5.6262 | 4 | 3910.5969 | 4754.5634 | 79.7228 | 96.9282 | 152.0583 | 0 | 261.6416 | 7629075.8789 | 379375.405 | 8064181.5316 | 7701446.2418 | 0 | 494349.1479 | 0 | 9464687.0001 | 24625174.0999 | 16807187.3199 | 75165476.6251 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 88007607.0748 | 107000992.9332 | 316227.766 | 22.5049 | 3910.5969 | 4754.5634 | 79.7228 | 96.9282
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.8339 | 54.1499 | 5.7023 | 4 | 3878.9517 | 4711.652 | 79.0777 | 96.0534 | 151.9864 | 0 | 243.7774 | 7677045.8291 | 381479.6729 | 8124714.9207 | 7772967.9422 | 0 | 463618.3749 | 0 | 9523732.4286 | 24778798.193 | 16912038.9201 | 75634396.2816 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 88476526.7312 | 107469912.5896 | 421696.5034 | 22.8094 | 3878.9517 | 4711.652 | 79.0777 | 96.0534
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3077 | 54.6049 | 5.7669 | 4 | 3855.0801 | 4678.4591 | 78.591 | 95.3767 | 151.9208 | 0 | 240.6173 | 7720786.9174 | 383420.1069 | 8179637.2796 | 7840305.639 | 0 | 441277.8447 | 0 | 9580516.8372 | 24926539.5761 | 17012875.4499 | 76085359.6508 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 88927490.1005 | 107920875.9589 | 562341.3252 | 23.0676 | 3855.0801 | 4678.4591 | 78.591 | 95.3767
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.4324 | 54.9513 | 5.8162 | 4 | 3837.0656 | 4653.4659 | 78.2238 | 94.8672 | 151.8703 | 0 | 278.4159 | 7753986.1228 | 384889.2807 | 8221402.7763 | 7891625.2186 | 0 | 423640.9763 | 0 | 9623462.3061 | 25038274.8769 | 17089137.0886 | 76426418.6462 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 89268549.0959 | 108261934.9543 | 749894.2093 | 23.2648 | 3837.0656 | 4653.4659 | 78.2238 | 94.8672
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.969 | 54.4997 | 5.7968 | 4 | 3822.6459 | 4641.7716 | 77.9298 | 94.6288 | 151.9348 | 0 | 638.9652 | 7710651.0933 | 382967.2373 | 8166954.3231 | 7824772.9426 | 0 | 386347.577 | 0 | 9543960.3376 | 24831427.063 | 16947959.2053 | 75795039.7791 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 88637170.2288 | 107630556.0872 | 1000000 | 23.1874 | 3822.6459 | 4641.7716 | 77.9298 | 94.6288
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.2307 | 55.504 | 5.8907 | 4 | 3812.2228 | 4618.297 | 77.7173 | 94.1502 | 151.7891 | 0 | 268.5662 | 7806764.5173 | 387219.2533 | 8287930.332 | 7973565.8647 | 0 | 400289.2997 | 0 | 9693750.0141 | 25221149.0751 | 17213952.4866 | 76984620.8427 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 89826751.2924 | 108820137.1508 | 1333521.4322 | 23.5628 | 3812.2228 | 4618.297 | 77.7173 | 94.1502
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.6936 | 55.6459 | 5.9114 | 4 | 3804.6375 | 4607.8904 | 77.5627 | 93.9381 | 151.768 | 0 | 249.9326 | 7820276.2984 | 387814.1537 | 8304995.028 | 7994626.8266 | 0 | 392011.6797 | 0 | 9710892.3547 | 25265749.929 | 17244393.4858 | 77120759.756 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 89962890.2057 | 108956276.064 | 1778279.41 | 23.6456 | 3804.6375 | 4607.8904 | 77.5627 | 93.9381
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.0271 | 55.7481 | 5.9266 | 4 | 3798.9359 | 4600.1262 | 77.4464 | 93.7798 | 151.7527 | 0 | 254.4066 | 7829996.2955 | 388241.7469 | 8317278.6251 | 8009797.4711 | 0 | 385547.0352 | 0 | 9723035.8578 | 25297344.833 | 17265957.657 | 77217199.5215 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90059329.9712 | 109052715.8295 | 2371373.7057 | 23.7065 | 3798.9359 | 4600.1262 | 77.4464 | 93.7798
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.2829 | 55.8264 | 5.9382 | 4 | 3794.6526 | 4594.2811 | 77.3591 | 93.6606 | 151.741 | 0 | 265.5207 | 7837440.4691 | 388569.0459 | 8326690.1522 | 8021426.6934 | 0 | 380676.6358 | 0 | 9732373.1686 | 25321638.6004 | 17282538.6524 | 77291353.4179 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90133483.8675 | 109126869.7259 | 3162277.6602 | 23.7528 | 3794.6526 | 4594.2811 | 77.3591 | 93.6606
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.483 | 55.8877 | 5.9471 | 4 | 3791.4361 | 4589.8681 | 77.2936 | 93.5707 | 151.7318 | 0 | 258.7553 | 7843257.1575 | 388824.6909 | 8334046.3494 | 8030519.6212 | 0 | 377058.237 | 0 | 9739745.3618 | 25340819.535 | 17295630.0344 | 77349900.9873 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90192031.437 | 109185417.2953 | 4216965.0343 | 23.7884 | 3791.4361 | 4589.8681 | 77.2936 | 93.5707
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.6191 | 55.9293 | 5.9534 | 4 | 3789.0214 | 4586.604 | 77.2443 | 93.5041 | 151.7255 | 0 | 266.8519 | 7847212.1069 | 388998.4269 | 8339049.7287 | 8036706.2467 | 0 | 374189.5125 | 0 | 9744600.8485 | 25353452.5154 | 17304252.3031 | 77388461.6888 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90230592.1385 | 109223977.9969 | 5623413.2519 | 23.8137 | 3789.0214 | 4586.604 | 77.2443 | 93.5041
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.7265 | 55.9622 | 5.9583 | 4 | 3787.2093 | 4584.1377 | 77.2074 | 93.4538 | 151.7206 | 0 | 244.1536 | 7850331.7329 | 389135.4468 | 8342996.8975 | 8041587.7787 | 0 | 372074.2674 | 0 | 9748489.188 | 25363569.1772 | 17311157.1327 | 77419341.6211 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90261472.0708 | 109254857.9291 | 7498942.0933 | 23.8332 | 3787.2093 | 4584.1377 | 77.2074 | 93.4538
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.7971 | 55.9838 | 5.9617 | 4 | 3785.8495 | 4582.3211 | 77.1797 | 93.4168 | 151.7173 | 0 | 260.1138 | 7852379.3691 | 389225.3462 | 8345588.3647 | 8044793.3552 | 0 | 370385.8903 | 0 | 9750925.2069 | 25369907.1987 | 17315482.9626 | 77438687.6937 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 90280818.1434 | 109274204.0017 | 10000000 | 23.8469 | 3785.8495 | 4582.3211 | 77.1797 | 93.4168
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4299 | [19 empty] | 100 | 0
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.78939 | 0.1395 | 0.0026093 | 4 | 1352228.0288 | 3227932.3542 | 27566.9974 | 65805.7671 | 105.9753 | 0 | 37.7276 | 93203.4712 | 3371.2278 | 71170.917 | 51300.4824 | 0 | 56813.066 | 0 | 107585.0741 | 279914.2941 | 191047.2574 | 854405.79 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14113624.021 | 33690932.7732 | 133.3521 | 0.010437 | 1352228.0288 | 3227932.3542 | 27566.9974 | 65805.7671
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.20798 | 0.0075267 | 4 | 477143.8452 | 1127402.9971 | 9727.2227 | 22983.635 | 115.1422 | 0 | 61.826 | 129759.4489 | 5015.6433 | 97316.9059 | 61596.5229 | 0 | 63440.6376 | 0 | 139280.3718 | 362378.9572 | 247331.0844 | 1106119.5719 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14365337.803 | 33942646.5552 | 177.8279 | 0.030107 | 477143.8452 | 1127402.9971 | 9727.2227 | 22983.635
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.30803 | 0.015363 | 4 | 239267.3296 | 557845.8771 | 4877.7881 | 11372.4427 | 123.6082 | 0 | 59.6517 | 178271.8572 | 7326.7356 | 132453.5242 | 76201.5493 | 0 | 72047.3879 | 0 | 181857.4112 | 473155.6798 | 322938.4738 | 1444252.619 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14703470.85 | 34280779.6022 | 237.1374 | 0.061452 | 239267.3296 | 557845.8771 | 4877.7881 | 11372.4427
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.44503 | 0.026959 | 4 | 140289.7963 | 321834.9621 | 2859.9973 | 6561.041 | 130.7839 | 0 | 288.4014 | 238479.1853 | 10328.4356 | 176910.9843 | 95855.5414 | 0 | 81937.9726 | 0 | 235369.7265 | 612383.7474 | 417964.4908 | 1869230.0839 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15128448.315 | 34705757.0672 | 316.2278 | 0.10784 | 140289.7963 | 321834.9621 | 2859.9973 | 6561.041
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.62845 | 0.043314 | 4 | 90345.523 | 203342.9471 | 1841.8157 | 4145.421 | 136.702 | 0 | 390.2184 | 311589.8323 | 14092.7732 | 232238.6471 | 121643.6533 | 0 | 93231.8062 | 0 | 301390.7177 | 784156.8238 | 535203.145 | 2393547.3986 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15652765.6296 | 35230074.3819 | 421.6965 | 0.17325 | 90345.523 | 203342.9471 | 1841.8157 | 4145.421
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9544 | 0.8787 | 0.066312 | 4 | 61523.9422 | 135331.3175 | 1254.2488 | 2758.912 | 141.6035 | 0 | 510.8888 | 402326.9358 | 18880.2492 | 302664.5733 | 156991.4419 | 0 | 107085.0106 | 0 | 385299.8022 | 1002471.0495 | 684207.09 | 3059926.1527 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16319144.3837 | 35896453.1359 | 562.3413 | 0.26525 | 61523.9422 | 135331.3175 | 1254.2488 | 2758.912
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 1.2207 | 0.098167 | 4 | 43718.655 | 93575.8264 | 891.2639 | 1907.6698 | 145.6106 | 0 | 76.7339 | 514882.4329 | 24900.2697 | 392673.6038 | 204679.6109 | 0 | 124527.7665 | 0 | 492048.8367 | 1280210.14 | 873769.7262 | 3907692.3867 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 17166910.6177 | 36744219.37 | 749.8942 | 0.39267 | 43718.655 | 93575.8264 | 891.2639 | 1907.6698
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1495 | 1.6769 | 0.14129 | 4 | 32244.7947 | 66886.0275 | 657.3538 | 1363.5621 | 148.7568 | 0 | 94.5726 | 651484.3752 | 32268.8523 | 505188.4552 | 268273.8683 | 0 | 145415.9814 | 0 | 625026.2976 | 1626190.2159 | 1109908.2372 | 4963756.2832 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 18222974.5142 | 37800283.2664 | 1000 | 0.56514 | 32244.7947 | 66886.0275 | 657.3538 | 1363.5621
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8085 | 2.2834 | 0.19886 | 4 | 24558.8537 | 49170.7724 | 500.6655 | 1002.4127 | 151.1641 | 0 | 94.1928 | 816674.9765 | 41179.7368 | 645691.5266 | 352008.2266 | 0 | 170718.2439 | 0 | 790246.357 | 2056058.9192 | 1403302.4602 | 6275880.4468 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 19535098.6778 | 39112407.4301 | 1333.5214 | 0.79544 | 24558.8537 | 49170.7724 | 500.6655 | 1002.4127
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.04 | 3.1047 | 0.27737 | 4 | 19124.2431 | 36769.4953 | 389.8736 | 749.5959 | 153.0206 | 0 | 99.5026 | 1021614.408 | 52301.8853 | 824529.2904 | 468837.6763 | 0 | 202419.9705 | 0 | 1002184.2599 | 2607477.868 | 1779657.2232 | 7959022.5816 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 21218240.8126 | 40795549.5649 | 1778.2794 | 1.1095 | 19124.2431 | 36769.4953 | 389.8736 | 749.5959
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9849 | 4.1969 | 0.38286 | 4 | 15223.539 | 28007.125 | 310.3524 | 570.9631 | 154.6166 | 0 | 85.9031 | 1271014.8215 | 65848.6082 | 1048264.535 | 621288.331 | 0 | 239922.6433 | 0 | 1266072.1862 | 3294060.1214 | 2248263.719 | 10054734.9656 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 23313953.1966 | 42891261.9489 | 2371.3737 | 1.5314 | 15223.539 | 28007.125 | 310.3524 | 570.9631
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.907 | 5.6448 | 0.52201 | 4 | 12417.7335 | 21793.6216 | 253.1523 | 444.2925 | 155.7407 | 0 | 87.5704 | 1572760.9862 | 82091.2269 | 1327824.001 | 821991.0124 | 0 | 285928.0856 | 0 | 1595332.1717 | 4150727.0632 | 2832956.5095 | 12669611.0565 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 25928829.2876 | 45506138.0398 | 3162.2777 | 2.088 | 12417.7335 | 21793.6216 | 253.1523 | 444.2925
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1152 | 7.5697 | 0.70728 | 4 | 10327.443 | 17247.382 | 210.5389 | 351.6112 | 156.5964 | 0 | 105.1356 | 1940810.6766 | 101845.0844 | 1678188.6491 | 1089617.3334 | 0 | 341946.0727 | 0 | 2009439.0483 | 5228148.2111 | 3568318.5818 | 15958313.6575 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 29217531.8885 | 48794840.6408 | 4216.965 | 2.8291 | 10327.443 | 17247.382 | 210.5389 | 351.6112
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.007 | 10.1193 | 0.95291 | 4 | 8748.5579 | 13884.762 | 178.3512 | 283.0597 | 157.2453 | 0 | 90.1652 | 2388629.4276 | 125797.5464 | 2115961.9729 | 1445097.9893 | 0 | 409950.8344 | 0 | 2529320.7306 | 6580773.7059 | 4491513.2757 | 20087045.4828 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 33346263.7138 | 52923572.4661 | 5623.4133 | 3.8116 | 8748.5579 | 13884.762 | 178.3512 | 283.0597
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0669 | 13.4726 | 1.2761 | 4 | 7542.6746 | 11378.0846 | 153.7676 | 231.9576 | 157.7354 | 0 | 98.6866 | 2930328.6544 | 154652.0522 | 2659519.8116 | 1913091.9796 | 0 | 491981.9399 | 0 | 3178334.0306 | 8269373.1818 | 5644017.1152 | 25241298.7651 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 38500516.9961 | 58077825.7484 | 7498.9421 | 5.1044 | 7542.6746 | 11378.0846 | 153.7676 | 231.9576
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.889 | 17.8469 | 1.6971 | 4 | 6613.6467 | 9497.6636 | 134.8281 | 193.6227 | 158.0945 | 0 | 105.6964 | 3581084.8528 | 189141.4662 | 3329564.5288 | 2523511.3183 | 0 | 590778.2754 | 0 | 3983491.3722 | 10364227.4241 | 7073798.1805 | 31635597.4184 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 44894815.6494 | 64472124.4017 | 10000 | 6.7882 | 6613.6467 | 9497.6636 | 134.8281 | 193.6227
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.0117 | 23.4232 | 2.2315 | 4 | 5900.3446 | 8093.6751 | 120.2865 | 165.0005 | 158.2943 | 0 | 108.2967 | 4345918.003 | 229364.846 | 4138046.1353 | 3302037.1731 | 0 | 707612.0273 | 0 | 4961961.492 | 12910005.964 | 8811344.3445 | 39406289.9853 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 52665508.2163 | 72242816.9685 | 13335.2143 | 8.9258 | 5900.3446 | 8093.6751 | 120.2865 | 165.0005
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.8474 | 30.2933 | 2.8815 | 4 | 5364.2019 | 7062.7367 | 109.3565 | 143.9834 | 158.2327 | 0 | 117.4524 | 5214990.3959 | 274399.7262 | 5083626.433 | 4264436.9683 | 0 | 843717.4528 | 0 | 6115656.6807 | 15911684.1895 | 10860051.4118 | 48568563.2581 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 61827781.4892 | 81405090.2414 | 17782.7941 | 11.526 | 5364.2019 | 7062.7367 | 109.3565 | 143.9834
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.7823 | 35.6435 | 3.4477 | 4 | 4969.1593 | 6388.7523 | 101.303 | 130.2434 | 157.9732 | 0 | 170.284 | 5847494.6523 | 306493.2739 | 5791048.7386 | 5018068.6069 | 0 | 881546.1117 | 0 | 6959414.0395 | 18106967.7587 | 12358377.5563 | 55269410.7378 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 68528628.9689 | 88105937.7211 | 23713.7371 | 13.7908 | 4969.1593 | 6388.7523 | 101.303 | 130.2434
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2332 | 39.6685 | 3.9291 | 4 | 4662.9799 | 5908.6475 | 95.0612 | 120.4558 | 157.6646 | 0 | 189.6415 | 6301484.1037 | 329053.8947 | 6309873.3667 | 5587297.4863 | 0 | 852576.1988 | 0 | 7558311.1696 | 19665175.2405 | 13421886.1806 | 60025657.6408 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 73284875.8718 | 92862184.6241 | 31622.7766 | 15.7163 | 4662.9799 | 5908.6475 | 95.0612 | 120.4558
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.5614 | 43.2353 | 4.3709 | 4 | 4425.5846 | 5545.3472 | 90.2215 | 113.0494 | 157.3147 | 0 | 227.5448 | 6689581.8388 | 347963.1166 | 6761425.9396 | 6094153.2926 | 0 | 807554.2123 | 0 | 8073264.576 | 21004978.3724 | 14336329.3483 | 64115250.6965 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 77374468.9275 | 96951777.6797 | 42169.6503 | 17.4834 | 4425.5846 | 5545.3472 | 90.2215 | 113.0494
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.5233 | 46.2776 | 4.7597 | 4 | 4242.3135 | 5270.5989 | 86.4853 | 107.4483 | 156.9608 | 0 | 253.1157 | 7010731.1521 | 363310.9712 | 7141160.5663 | 6528781.7158 | 0 | 752516.1846 | 0 | 8500635.2301 | 22116909.1487 | 15095244.951 | 67509289.9199 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 80768508.1509 | 100345816.9032 | 56234.1325 | 19.0388 | 4242.3135 | 5270.5989 | 86.4853 | 107.4483
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.5887 | 49.6546 | 5.1582 | 4 | 4099.9628 | 5048.8008 | 83.5833 | 102.9266 | 156.548 | 0 | 243.0894 | 7358576.2984 | 379750.9995 | 7557153.1535 | 7014988.8747 | 0 | 721237.5092 | 0 | 8982365.6658 | 23370272.9258 | 15950691.4829 | 71335036.9097 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 84594255.1408 | 104171563.893 | 74989.4209 | 20.6329 | 4099.9628 | 5048.8008 | 83.5833 | 102.9266
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.2908 | 51.8846 | 5.4516 | 4 | 3989.4675 | 4887.2519 | 81.3307 | 99.6332 | 156.2737 | 0 | 224.9226 | 7583716.94 | 390297.0672 | 7828904.9176 | 7337086.2681 | 0 | 666921.2571 | 0 | 9284701.3155 | 24156888.2688 | 16487572.6179 | 73736088.6522 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 86995306.8832 | 106572615.6355 | 100000 | 21.8062 | 3989.4675 | 4887.2519 | 81.3307 | 99.6332
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.6692 | 53.6567 | 5.6894 | 4 | 3904.9178 | 4765.1674 | 79.607 | 97.1444 | 156.0432 | 0 | 235.3994 | 7759806.4319 | 398453.6348 | 8043345.7147 | 7594000.6077 | 0 | 615622.6036 | 0 | 9520379.3072 | 24770074.0589 | 16906084.5193 | 75607766.8782 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 88866985.1092 | 108444293.8615 | 133352.1432 | 22.7577 | 3904.9178 | 4765.1674 | 79.607 | 97.1444
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.7519 | 54.9938 | 5.8752 | 4 | 3840.4756 | 4673.5182 | 78.2933 | 95.276 | 155.8622 | 0 | 244.7145 | 7891417.3571 | 404534.4159 | 8204222.7781 | 7791214.6487 | 0 | 567951.6324 | 0 | 9695142.9246 | 25224773.1425 | 17216425.987 | 76995682.8863 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 90254901.1173 | 109832209.8695 | 177827.941 | 23.501 | 3840.4756 | 4673.5182 | 78.2933 | 95.276
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.9749 | 56.0435 | 6.0223 | 4 | 3791.4877 | 4604.1845 | 77.2946 | 93.8625 | 155.7159 | 0 | 279.5969 | 7993904.2718 | 409248.0592 | 8330018.3046 | 7947311.9211 | 0 | 527373.6374 | 0 | 9831063.9157 | 25578411.6801 | 17457791.5555 | 78075123.3453 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 91334341.5763 | 110911650.3286 | 237137.3706 | 24.0893 | 3791.4877 | 4604.1845 | 77.2946 | 93.8625
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4233 | 56.8371 | 6.1354 | 4 | 3754.3274 | 4552.0435 | 76.537 | 92.7996 | 155.6026 | 0 | 283.0284 | 8070847.9204 | 412768.2994 | 8424843.464 | 8065688.7955 | 0 | 493045.3013 | 0 | 9932205.5744 | 25841561.5291 | 17637396.7346 | 78878357.6187 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 92137575.8497 | 111714884.602 | 316227.766 | 24.5417 | 3754.3274 | 4552.0435 | 76.537 | 92.7996
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.2692 | 57.4333 | 6.2216 | 4 | 3726.1949 | 4512.8562 | 75.9635 | 92.0007 | 155.5161 | 0 | 270.9063 | 8128346.5016 | 415388.322 | 8495921.7479 | 8154823.967 | 0 | 464712.0252 | 0 | 10007085.0998 | 26036382.6943 | 17770366.183 | 79473026.5408 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 92732244.7718 | 112309553.524 | 421696.5034 | 24.8866 | 3726.1949 | 4512.8562 | 75.9635 | 92.0007
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6628 | 57.8822 | 6.2872 | 4 | 3704.9332 | 4483.3902 | 75.5301 | 91.4 | 155.4503 | 0 | 302.8741 | 8171472.9776 | 417347.7965 | 8549352.047 | 8222051.1563 | 0 | 441874.8023 | 0 | 10062818.5241 | 26181389.6318 | 17869336.3974 | 79915643.333 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 93174861.5641 | 112752170.3163 | 562341.3252 | 25.1489 | 3704.9332 | 4483.3902 | 75.5301 | 91.4
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.6787 | 58.2088 | 6.336 | 4 | 3688.889 | 4461.3545 | 75.203 | 90.9507 | 155.4019 | 0 | 260.3087 | 8202753.7375 | 418765.6741 | 8588174.7702 | 8271024.2543 | 0 | 423427.5078 | 0 | 10102616.9181 | 26284936.8893 | 17940009.5284 | 80231709.2797 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 93490927.5107 | 113068236.263 | 749894.2093 | 25.3439 | 3688.889 | 4461.3545 | 75.203 | 90.9507
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.4487 | 58.4559 | 6.373 | 4 | 3676.7969 | 4444.7777 | 74.9565 | 90.6128 | 155.3651 | 0 | 266.6142 | 8226372.5418 | 419834.4006 | 8617525.9424 | 8308119.1279 | 0 | 409040.1018 | 0 | 10132547.9247 | 26362811.2286 | 17993160.3651 | 80469411.633 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 93728629.864 | 113305938.6162 | 1000000 | 25.4919 | 3676.7969 | 4444.7777 | 74.9565 | 90.6128
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.505 | 58.4738 | 6.3881 | 4 | 3666.7294 | 4432.896 | 74.7512 | 90.3706 | 155.3622 | 0 | 258.9364 | 8228075.8747 | 419910.6355 | 8619654.4386 | 8310823.2221 | 0 | 391026.8896 | 0 | 10128101.5136 | 26351242.5791 | 17985264.5242 | 80434099.6775 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 93693317.9085 | 113270626.6607 | 1333521.4322 | 25.5523 | 3666.7294 | 4432.896 | 74.7512 | 90.3706
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.7787 | 58.8822 | 6.4317 | 4 | 3659.9442 | 4420.9156 | 74.6129 | 90.1263 | 155.3013 | 0 | 244.4829 | 8267024.3769 | 421671.1297 | 8668106.6311 | 8372170.1283 | 0 | 390681.8977 | 0 | 10186665.1239 | 26503613.08 | 18089260.5219 | 80899192.8895 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94158411.1205 | 113735719.8727 | 1778279.41 | 25.7267 | 3659.9442 | 4420.9156 | 74.6129 | 90.1263
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.0929 | 58.9827 | 6.4471 | 4 | 3654.8684 | 4414.0239 | 74.5094 | 89.9858 | 155.2861 | 0 | 282.2798 | 8276583.9489 | 422102.0401 | 8680019.4336 | 8387286.3066 | 0 | 384122.1248 | 0 | 10198544.4031 | 26534520.5276 | 18110355.49 | 80993534.2747 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94252752.5057 | 113830061.258 | 2371373.7057 | 25.7883 | 3654.8684 | 4414.0239 | 74.5094 | 89.9858
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.3272 | 59.0576 | 6.4586 | 4 | 3651.0552 | 4408.856 | 74.4317 | 89.8805 | 155.2748 | 0 | 245.1016 | 8283706.0876 | 422422.9005 | 8688898.3966 | 8398559.4257 | 0 | 379116.8493 | 0 | 10207354.4273 | 26557442.4035 | 18126000.1413 | 81063500.6317 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94322718.8627 | 113900027.615 | 3162277.6602 | 25.8344 | 3651.0552 | 4408.856 | 74.4317 | 89.8805
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.5 | 59.1128 | 6.4672 | 4 | 3648.1917 | 4404.9876 | 74.3733 | 89.8016 | 155.2664 | 0 | 256.6257 | 8288954.9335 | 422659.2631 | 8695444.0288 | 8406873.7352 | 0 | 375292.9831 | 0 | 10213797.7281 | 26574206.5504 | 18137442.016 | 81114671.2382 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94373889.4693 | 113951198.2215 | 4216965.0343 | 25.8687 | 3648.1917 | 4404.9876 | 74.3733 | 89.8016
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6218 | 59.1517 | 6.4734 | 4 | 3646.042 | 4402.1099 | 74.3295 | 89.743 | 155.2604 | 0 | 240.3734 | 8292652.5738 | 422825.7037 | 8700056.4767 | 8412734.6266 | 0 | 372325.9467 | 0 | 10218232.1778 | 26585744.0789 | 18145316.6163 | 81149888.2005 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94409106.4315 | 113986415.1838 | 5623413.2519 | 25.8936 | 3646.042 | 4402.1099 | 74.3295 | 89.743
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7339 | 59.1875 | 6.4786 | 4 | 3644.4287 | 4399.8857 | 74.2966 | 89.6976 | 155.255 | 0 | 241.0515 | 8296053.0345 | 422978.7875 | 8704298.1892 | 8418124.9211 | 0 | 370287.2312 | 0 | 10222579.4437 | 26597054.7732 | 18153036.3975 | 81184412.7779 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94443631.009 | 114020939.7612 | 7498942.0933 | 25.9145 | 3644.4287 | 4399.8857 | 74.2966 | 89.6976
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.7922 | 59.2062 | 6.4819 | 4 | 3643.2181 | 4398.2986 | 74.2719 | 89.6653 | 155.2521 | 0 | 262.5391 | 8297821.3394 | 423058.3235 | 8706505.0077 | 8420930.6748 | 0 | 368501.7947 | 0 | 10224558.6846 | 26602204.352 | 18156551.0909 | 81200131.2676 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 94459349.4987 | 114036658.2509 | 10000000 | 25.9274 | 3643.2181 | 4398.2986 | 74.2719 | 89.6653
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.8969 | [19 empty] | 100 | 0
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79402 | 0.14419 | 0.0033993 | 4 | 1070152.7969 | 2553505.8027 | 21816.5123 | 52056.6697 | 107.6044 | 0 | 44.6177 | 96350.7975 | 3525.3751 | 72993.4386 | 51824.4146 | 0 | 55847.1135 | 0 | 109411.0443 | 284665.094 | 194289.7759 | 868907.0535 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14551073.1568 | 34720508.9301 | 133.3521 | 0.013597 | 1070152.7969 | 2553505.8027 | 21816.5123 | 52056.6697
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0498 | 0.22483 | 0.0091923 | 4 | 403792.6657 | 952332.7746 | 8231.8597 | 19414.5917 | 118.0626 | 0 | 51.4929 | 139194.4564 | 5492.8509 | 103358.5447 | 63723.6473 | 0 | 64372.6154 | 0 | 146695.4247 | 381671.4038 | 260498.5757 | 1165007.519 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14847173.6222 | 35016609.3956 | 177.8279 | 0.036769 | 403792.6657 | 952332.7746 | 8231.8597 | 19414.5917
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3639 | 0.33086 | 0.01797 | 4 | 211449.069 | 492051.4879 | 4310.6753 | 10031.1351 | 126.5879 | 0 | 69.7535 | 190157.3793 | 7980.5978 | 139964.3476 | 78842.0162 | 0 | 72712.8381 | 0 | 190966.2998 | 496855.1394 | 339113.842 | 1516592.4601 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15198758.5633 | 35368194.3367 | 237.1374 | 0.071879 | 211449.069 | 492051.4879 | 4310.6753 | 10031.1351
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.47401 | 0.03078 | 4 | 126993.6298 | 290811.9336 | 2588.9369 | 5928.5946 | 133.7678 | 0 | 306.26 | 252710.2629 | 11181.5515 | 185692.3039 | 99110.0627 | 0 | 81989.5428 | 0 | 245966.6523 | 639954.7745 | 436782.2834 | 1953387.434 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15635553.5372 | 35804989.3105 | 316.2278 | 0.12312 | 126993.6298 | 290811.9336 | 2588.9369 | 5928.5946
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.67276 | 0.049213 | 4 | 82278.2474 | 184738.1303 | 1677.3534 | 3766.1367 | 139.9241 | 0 | 396.7203 | 331494.8638 | 15349.3438 | 244721.011 | 126622.6685 | 0 | 93651.9329 | 0 | 316617.5298 | 823773.8653 | 562242.5899 | 2514473.8049 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16196639.9082 | 36366075.6815 | 421.6965 | 0.19685 | 82278.2474 | 184738.1303 | 1677.3534 | 3766.1367
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 0.94166 | 0.074984 | 4 | 56355.8021 | 123602.0047 | 1148.8893 | 2519.794 | 144.9601 | 0 | 522.3445 | 428429.5808 | 20614.6262 | 319176.6944 | 164078.9288 | 0 | 107610.5456 | 0 | 405565.0466 | 1055197.0585 | 720193.6745 | 3220866.1555 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16903032.2588 | 37072468.0321 | 562.3413 | 0.29993 | 56355.8021 | 123602.0047 | 1148.8893 | 2519.794
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 1.3046 | 0.11032 | 4 | 40312.6897 | 86018.9946 | 821.8287 | 1753.6136 | 149.0358 | 0 | 74.8299 | 547211.658 | 27157.6661 | 413187.8621 | 213805.0352 | 0 | 124701.795 | 0 | 517164.9664 | 1345557.1575 | 918370.4084 | 4107156.5488 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 17789322.652 | 37958758.4254 | 749.8942 | 0.44128 | 40312.6897 | 86018.9946 | 821.8287 | 1753.6136
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.281 | 1.7962 | 0.15867 | 4 | 29798.5466 | 61578.3479 | 607.4837 | 1255.3579 | 152.285 | 0 | 101.279 | 693623.9437 | 35299.9037 | 532489.5977 | 281181.8882 | 0 | 145946.5118 | 0 | 658531.3196 | 1713363.4103 | 1169405.7336 | 5229842.3086 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 18912008.4119 | 39081444.1852 | 1000 | 0.63466 | 29798.5466 | 61578.3479 | 607.4837 | 1255.3579
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9742 | 2.4458 | 0.22333 | 4 | 22731.8103 | 45309.4205 | 463.4187 | 923.6938 | 154.734 | 0 | 83.4498 | 870244.1281 | 45185.777 | 680495.9521 | 371932.595 | 0 | 171140.6047 | 0 | 834209.6322 | 2170442.343 | 1481371.4973 | 6625022.5294 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 20307188.6326 | 40476624.406 | 1333.5214 | 0.89334 | 22731.8103 | 45309.4205 | 463.4187 | 923.6938
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.24 | 3.3182 | 0.31044 | 4 | 17763.4043 | 34005.8566 | 362.131 | 693.2554 | 156.7398 | 0 | 74.4781 | 1086609.0577 | 57277.0482 | 867482.1009 | 490893.224 | 0 | 202052.6971 | 0 | 1054682.5099 | 2744067.5456 | 1872882.4848 | 8375946.6683 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 22058112.7715 | 42227548.5449 | 1778.2794 | 1.2418 | 17763.4043 | 34005.8566 | 362.131 | 693.2554
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2601 | 4.4857 | 0.42757 | 4 | 14190.8254 | 25983.8906 | 289.2992 | 529.7168 | 158.2853 | 0 | 95.3324 | 1351741.862 | 72112.3079 | 1102930.087 | 651854.3458 | 0 | 239909.1788 | 0 | 1333233.6348 | 3468800.4339 | 2367527.5729 | 10588109.4231 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 24270275.5263 | 44439711.2997 | 2371.3737 | 1.7103 | 14190.8254 | 25983.8906 | 289.2992 | 529.7168
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.258 | 6.0293 | 0.58244 | 4 | 11598.7236 | 20256.0521 | 236.4557 | 412.947 | 159.4377 | 0 | 74.0394 | 1672246.9218 | 89935.8068 | 1396270.2771 | 863032.6379 | 0 | 285553.7816 | 0 | 1679745.3758 | 4370352.9047 | 2982855.6592 | 13339993.3649 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 27022159.4682 | 47191595.2415 | 3162.2777 | 2.3298 | 11598.7236 | 20256.0521 | 236.4557 | 412.947
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.5757 | 8.0831 | 0.78849 | 4 | 9664.5925 | 16059.5374 | 197.0258 | 327.3954 | 160.3175 | 0 | 112.7125 | 2063316.0635 | 111586.3329 | 1764316.602 | 1143453.3445 | 0 | 341367.0308 | 0 | 2115375.3557 | 5503772.7525 | 3756437.9948 | 16799625.4767 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 30481791.58 | 50651227.3533 | 4216.965 | 3.154 | 9664.5925 | 16059.5374 | 197.0258 | 327.3954
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.6138 | 10.8066 | 1.0622 | 4 | 8199.0995 | 12946.1272 | 167.1497 | 263.9243 | 160.9851 | 0 | 83.466 | 2540066.8768 | 137926.123 | 2224657.0894 | 1518219.5911 | 0 | 409253.7254 | 0 | 2663748.1282 | 6930526.2197 | 4730226.553 | 21154624.3067 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 34836790.4099 | 55006226.1832 | 5623.4133 | 4.2489 | 8199.0995 | 12946.1272 | 167.1497 | 263.9243
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8562 | 14.3817 | 1.4214 | 4 | 7080.1992 | 10627.5754 | 144.3394 | 216.6575 | 161.4888 | 0 | 107.635 | 3115439.1787 | 169547.0606 | 2795206.1533 | 2008667.1748 | 0 | 490986.518 | 0 | 3346139.9733 | 8705969.8229 | 5942003.2939 | 26573959.1755 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 40256125.2787 | 60425561.0521 | 7498.9421 | 5.6857 | 7080.1992 | 10627.5754 | 144.3394 | 216.6575
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8831 | 19.0324 | 1.8882 | 4 | 6217.7008 | 8888.1777 | 126.7562 | 181.1975 | 161.8549 | 0 | 113.0145 | 3804871.3743 | 207236.6086 | 3496660.1396 | 2646747.786 | 0 | 589020.2182 | 0 | 4190369.0894 | 10902480.8078 | 7441167.1749 | 33278553.1987 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 46960719.302 | 67130155.0753 | 10000 | 7.5527 | 6217.7008 | 8888.1777 | 126.7562 | 181.1975
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2615 | 24.9568 | 2.48 | 4 | 5555.1375 | 7588.3806 | 113.249 | 154.6994 | 162.0495 | 0 | 125.2659 | 4614735.1612 | 251141.0998 | 4342631.9155 | 3460579.7472 | 0 | 705303.8088 | 0 | 5216012.7757 | 13570995.291 | 9262483.1422 | 41423882.9414 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 55106049.0447 | 75275484.818 | 13335.2143 | 9.9198 | 5555.1375 | 7588.3806 | 113.249 | 154.6994
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3601 | 32.2271 | 3.1966 | 4 | 5058.0172 | 6635.4135 | 103.1145 | 135.2719 | 161.9613 | 0 | 120.6252 | 5531348.064 | 300024.2602 | 5328497.8954 | 4463189.1675 | 0 | 840673.3565 | 0 | 6420855.77 | 16705749.6149 | 11402017.381 | 50992355.5093 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 64674521.6125 | 84843957.3859 | 17782.7941 | 12.7865 | 5058.0172 | 6635.4135 | 103.1145 | 135.2719
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0554 | 38.8232 | 3.8801 | 4 | 4698.4746 | 5998.0113 | 95.7848 | 122.2776 | 161.603 | 0 | 150.0727 | 6304995.6342 | 340259.5028 | 6185926.1023 | 5379081.0581 | 0 | 916496.6465 | 0 | 7459435.9881 | 19407922.3004 | 13246305.7629 | 59240422.9953 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 72922589.0985 | 93092024.8718 | 23713.7371 | 15.5205 | 4698.4746 | 5998.0113 | 95.7848 | 122.2776
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.3749 | 42.9525 | 4.3915 | 4 | 4424.2063 | 5572.4272 | 90.1934 | 113.6015 | 161.2524 | 0 | 167.4279 | 6765343.6155 | 363598.7093 | 6708491.9762 | 5956704.2662 | 0 | 879861.3191 | 0 | 8062859.9557 | 20977907.6846 | 14317853.0477 | 64032620.5742 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 77714786.6774 | 97884222.4508 | 31622.7766 | 17.5658 | 4424.2063 | 5572.4272 | 90.1934 | 113.6015
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.5056 | 46.5791 | 4.8555 | 4 | 4211.6635 | 5250.1503 | 85.8605 | 107.0314 | 160.8692 | 0 | 204.0757 | 7155720.0089 | 382954.2514 | 7159780.6337 | 6465956.4909 | 0 | 828152.0337 | 0 | 8577099.7333 | 22315854.101 | 15231028.9689 | 68116546.2218 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 81798712.325 | 101968148.0984 | 42169.6503 | 19.4219 | 4211.6635 | 5250.1503 | 85.8605 | 107.0314
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2091 | 49.6351 | 5.2585 | 4 | 4047.6186 | 5006.5144 | 82.5162 | 102.0646 | 160.492 | 0 | 244.9208 | 7474929.5733 | 398420.3778 | 7535137.8253 | 6894780.1099 | 0 | 767342.9465 | 0 | 8997538.2248 | 23409748.8121 | 15977634.5865 | 71455532.4562 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 85137698.5594 | 105307134.3328 | 56234.1325 | 21.034 | 4047.6186 | 5006.5144 | 82.5162 | 102.0646
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.3406 | 53.1665 | 5.6825 | 4 | 3918.8209 | 4806.1732 | 79.8905 | 97.9803 | 160.0671 | 0 | 250.3891 | 7835683.4076 | 415755.7004 | 7963398.5402 | 7391258.7567 | 0 | 735552.7044 | 0 | 9493243.1526 | 24699471.3511 | 16857896.7205 | 75392260.3335 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 89074426.4367 | 109243862.2101 | 74989.4209 | 22.7299 | 3918.8209 | 4806.1732 | 79.8905 | 97.9803
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6593 | 55.3498 | 5.9813 | 4 | 3819.8683 | 4662.8956 | 77.8732 | 95.0594 | 159.7895 | 0 | 261.9803 | 8054913.4561 | 426244.4707 | 8225393.7275 | 7706520.1485 | 0 | 676322.1926 | 0 | 9784863.6582 | 25458208.0871 | 17375750.1333 | 77708215.8739 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 91390381.9772 | 111559817.7505 | 100000 | 23.925 | 3819.8683 | 4662.8956 | 77.8732 | 95.0594
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.7554 | 57.0964 | 6.2243 | 4 | 3744.2229 | 4554.3378 | 76.331 | 92.8463 | 159.5561 | 0 | 282.2518 | 8228006.5376 | 434466.0688 | 8433594.9657 | 7962134.1616 | 0 | 621895.3422 | 0 | 10015237.8596 | 26057594.5029 | 17784843.6783 | 79537773.1167 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 93219939.22 | 113389374.9933 | 133352.1432 | 24.897 | 3744.2229 | 4554.3378 | 76.331 | 92.8463
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7534 | 58.4566 | 6.4167 | 4 | 3686.5512 | 4472.3725 | 75.1553 | 91.1754 | 159.3677 | 0 | 247.3953 | 8361281.3782 | 440742.558 | 8594927.9566 | 8162213.4353 | 0 | 573478.0649 | 0 | 10191730.9233 | 26516793.2509 | 18098256.2594 | 80939423.8266 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 94621589.9299 | 114791025.7032 | 177827.941 | 25.6667 | 3686.5512 | 4472.3725 | 75.1553 | 91.1754
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.7929 | 59.4846 | 6.5653 | 4 | 3642.7073 | 4410.7425 | 74.2615 | 89.919 | 159.2213 | 0 | 292.2412 | 8461145.2346 | 445413.5264 | 8716421.3941 | 8314064.335 | 0 | 531329.6475 | 0 | 10322665.9137 | 26857459.2375 | 18330767.7952 | 81979267.0839 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 95661433.1872 | 115830868.9605 | 237137.3706 | 26.2611 | 3642.7073 | 4410.7425 | 74.2615 | 89.919
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.0929 | 60.259 | 6.6791 | 4 | 3609.4544 | 4364.3983 | 73.5836 | 88.9742 | 159.1087 | 0 | 261.7158 | 8535875.5872 | 448890.0644 | 8807689.5647 | 8428818.6314 | 0 | 495855.8648 | 0 | 10419680.5879 | 27109871.5192 | 18503044.364 | 82749726.1836 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 96431892.2868 | 116601328.0602 | 316227.766 | 26.7165 | 3609.4544 | 4364.3983 | 73.5836 | 88.9742
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.8102 | 60.8352 | 6.7653 | 4 | 3584.2827 | 4329.6052 | 73.0705 | 88.2649 | 159.0235 | 0 | 260.7298 | 8591205.3867 | 451453.3649 | 8875462.5155 | 8514414.9701 | 0 | 466573.9298 | 0 | 10490652.9651 | 27294527.0864 | 18629075.5829 | 83313365.8014 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 96995531.9046 | 117164967.6779 | 421696.5034 | 27.0614 | 3584.2827 | 4329.6052 | 73.0705 | 88.2649
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6324 | 61.4418 | 6.8453 | 4 | 3565.2087 | 4301.8229 | 72.6816 | 87.6985 | 158.9326 | 0 | 268.1508 | 8648997.6765 | 454097.6714 | 8946721.4562 | 8602608.8693 | 0 | 448290.4673 | 0 | 10569279.2949 | 27499096.668 | 18768698.5258 | 83937790.6293 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 97619956.7325 | 117789392.5059 | 562341.3252 | 27.3813 | 3565.2087 | 4301.8229 | 72.6816 | 87.6985
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.6265 | 61.7711 | 6.895 | 4 | 3550.8056 | 4282.1147 | 72.388 | 87.2967 | 158.8824 | 0 | 276.4637 | 8680213.7921 | 455515.7643 | 8985364.7659 | 8650145.6087 | 0 | 429863.0456 | 0 | 10608430.1609 | 27600959.1904 | 18838221.7904 | 84248714.1183 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 97930880.2215 | 118100315.9949 | 749894.2093 | 27.5799 | 3550.8056 | 4282.1147 | 72.388 | 87.2967
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.3575 | 62.0129 | 6.932 | 4 | 3539.949 | 4267.3519 | 72.1666 | 86.9957 | 158.8453 | 0 | 267.3384 | 8703082.0629 | 456552.4281 | 9013713.5158 | 8685067.3991 | 0 | 415289.2173 | 0 | 10636744.8031 | 27674628.0812 | 18888502.3222 | 84473579.8297 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98155745.9329 | 118325181.7063 | 1000000 | 27.728 | 3539.949 | 4267.3519 | 72.1666 | 86.9957
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.8929 | 62.1898 | 6.9595 | 4 | 3531.7744 | 4256.3016 | 72 | 86.7705 | 158.818 | 0 | 277.6858 | 8719781.701 | 457308.2509 | 9034436.7771 | 8710621.936 | 0 | 403865.8104 | 0 | 10657145.6454 | 27727706.8883 | 18924729.6986 | 84635596.7078 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98317762.8111 | 118487198.5844 | 1333521.4322 | 27.8381 | 3531.7744 | 4256.3016 | 72 | 86.7705
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.869 | 62.1817 | 6.9695 | 4 | 3524.7666 | 4248.2602 | 71.8571 | 86.6065 | 158.819 | 0 | 288.6355 | 8719016.1689 | 457272.771 | 9033497.0022 | 8709467.6071 | 0 | 389036.4777 | 0 | 10650233.1105 | 27709721.8903 | 18912454.568 | 84580699.5958 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98262865.699 | 118432301.4724 | 1778279.41 | 27.8778 | 3524.7666 | 4248.2602 | 71.8571 | 86.6065
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9575 | 62.5412 | 7.0073 | 4 | 3520.1855 | 4239.7745 | 71.7637 | 86.4335 | 158.7638 | 0 | 294.2522 | 8752912.1198 | 458806.4663 | 9075581.7036 | 8761414.6392 | 0 | 390264.5161 | 0 | 10701201.9835 | 27842332.4428 | 19002963.9949 | 84985477.8662 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98667643.9695 | 118837079.7428 | 2371373.7057 | 28.0291 | 3520.1855 | 4239.7745 | 71.7637 | 86.4335
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.1692 | 62.6109 | 7.0185 | 4 | 3516.7623 | 4235.2015 | 71.694 | 86.3403 | 158.7529 | 0 | 269.7199 | 8759472.4598 | 459102.2674 | 9083742.4311 | 8771501.648 | 0 | 385113.0321 | 0 | 10708983.417 | 27862578.1365 | 19016782.0969 | 85047275.4888 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98729441.592 | 118898877.3654 | 3162277.6602 | 28.074 | 3516.7623 | 4235.2015 | 71.694 | 86.3403
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3324 | 62.6646 | 7.027 | 4 | 3514.1915 | 4231.7573 | 71.6415 | 86.2701 | 158.7445 | 0 | 293.2508 | 8764524.451 | 459329.9682 | 9090028.5538 | 8779273.8135 | 0 | 381252.4531 | 0 | 10715019.6034 | 27878283.0554 | 19027501.0267 | 85095212.9251 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98777379.0283 | 118946814.8017 | 4216965.0343 | 28.1081 | 3514.1915 | 4231.7573 | 71.6415 | 86.2701
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.4593 | 62.7064 | 7.0336 | 4 | 3512.2617 | 4229.16 | 71.6022 | 86.2171 | 158.738 | 0 | 267.6082 | 8768450.5679 | 459506.8766 | 9094914.7111 | 8785316.3748 | 0 | 378378.794 | 0 | 10719761.2565 | 27890619.8639 | 19035921.1521 | 85132869.5967 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98815035.7 | 118984471.4733 | 5623413.2519 | 28.1343 | 3512.2617 | 4229.16 | 71.6022 | 86.2171
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.5519 | 62.7369 | 7.0384 | 4 | 3510.8133 | 4227.219 | 71.5727 | 86.1776 | 158.7332 | 0 | 261.6701 | 8771314.7329 | 459635.8901 | 9098479.9821 | 8789726.2662 | 0 | 376185.1365 | 0 | 10723183.383 | 27899523.5353 | 19041998.0907 | 85160047.0167 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98842213.12 | 119011648.8933 | 7498942.0933 | 28.1537 | 3510.8133 | 4227.219 | 71.5727 | 86.1776
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.6102 | 62.756 | 7.0417 | 4 | 3509.7264 | 4225.795 | 71.5505 | 86.1485 | 158.7302 | 0 | 271.3414 | 8773117.5918 | 459717.0434 | 9100724.9208 | 8792503.6063 | 0 | 374421.6939 | 0 | 10725189.0939 | 27904741.9835 | 19045559.7888 | 85175975.7223 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 98858141.8255 | 119027577.5989 | 10000000 | 28.1669 | 3509.7264 | 4225.795 | 71.5505 | 86.1485
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3314 | [19 empty] | 100 | 0
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.83292 | 0.15961 | 0.0045534 | 4 | 825758.1745 | 1966102.4017 | 16834.1973 | 40081.6568 | 110.9216 | 0 | 47.5654 | 105460.0322 | 3950.7717 | 78982.8025 | 53897.9424 | 0 | 57667.7995 | 0 | 116984.1458 | 304368.7507 | 207737.9265 | 929050.1714 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15040024.2378 | 35809791.1594 | 133.3521 | 0.018214 | 825758.1745 | 1966102.4017 | 16834.1973 | 40081.6568
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.23745 | 0.010782 | 4 | 355169.4805 | 836767.7237 | 7240.6103 | 17058.6419 | 120.4876 | 0 | 50.8868 | 146466.2834 | 5879.569 | 107792.0013 | 65185.0415 | 0 | 64161.2728 | 0 | 151898.8255 | 395209.5853 | 269738.6627 | 1206331.2414 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15317305.3077 | 36087072.2294 | 177.8279 | 0.043127 | 355169.4805 | 836767.7237 | 7240.6103 | 17058.6419
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3982 | 0.35328 | 0.020735 | 4 | 189267.7369 | 439691.3508 | 3858.4788 | 8963.7029 | 129.4654 | 0 | 54.7972 | 201877.4884 | 8649.9247 | 147208.2873 | 81519.6792 | 0 | 73009.4839 | 0 | 199783.2968 | 519795.157 | 354770.8754 | 1586614.1928 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15697588.2591 | 36467355.1807 | 237.1374 | 0.082939 | 189267.7369 | 439691.3508 | 3858.4788 | 8963.7029
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.51139 | 0.035318 | 4 | 114485.5024 | 261505.7744 | 2333.9418 | 5331.1489 | 137.0269 | 0 | 301.3754 | 270382.8978 | 12246.1807 | 196892.4921 | 103329.6784 | 0 | 83080.2721 | 0 | 259713.2933 | 675720.7146 | 461193.2724 | 2062558.8014 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16173532.8677 | 36943299.7893 | 316.2278 | 0.14127 | 114485.5024 | 261505.7744 | 2333.9418 | 5331.1489
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.71936 | 0.055609 | 4 | 75310.9104 | 168684.9944 | 1535.3148 | 3438.8718 | 143.1444 | 0 | 396.472 | 352327.3084 | 16711.7663 | 257632.9878 | 132005.2124 | 0 | 93978.4466 | 0 | 332535.7314 | 865189.7606 | 590509.7895 | 2640891.0031 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16751865.0694 | 37521631.991 | 421.6965 | 0.22244 | 75310.9104 | 168684.9944 | 1535.3148 | 3438.8718
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.11 | 1.0072 | 0.084243 | 4 | 51921.8954 | 113558.3785 | 1058.4981 | 2315.0411 | 148.3141 | 0 | 532.4142 | 455364.9784 | 22466.1524 | 336092.819 | 171057.134 | 0 | 108003.0692 | 0 | 426263.8197 | 1109051.0201 | 756950.1099 | 3385249.1026 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 17496223.1689 | 38265990.0906 | 562.3413 | 0.33697 | 51921.8954 | 113558.3785 | 1058.4981 | 2315.0411
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1043 | 1.4003 | 0.12402 | 4 | 37184.126 | 79053.397 | 758.0487 | 1611.6104 | 152.5214 | 0 | 76.1454 | 583386.6607 | 29751.1158 | 436252.9713 | 224577.5219 | 0 | 125551.9507 | 0 | 545812.8859 | 1420093.1676 | 969242.7669 | 4334669.0407 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 18445643.107 | 39215410.0287 | 749.8942 | 0.49606 | 37184.126 | 79053.397 | 758.0487 | 1611.6104
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4079 | 1.9204 | 0.17746 | 4 | 27637.4271 | 56896.7013 | 563.4263 | 1159.9162 | 155.7999 | 0 | 84.8955 | 737577.6702 | 38619.072 | 560419.5025 | 295419.5418 | 0 | 146159.1756 | 0 | 693496.0352 | 1804334.428 | 1231495.3225 | 5507520.7477 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 19618494.814 | 40388261.7356 | 1000 | 0.70985 | 27637.4271 | 56896.7013 | 563.4263 | 1159.9162
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.14 | 2.6128 | 0.24897 | 4 | 21169.7086 | 42025.6601 | 431.5731 | 856.7499 | 158.2969 | 0 | 75.3895 | 924631.2859 | 49403.6062 | 715743.7003 | 389716.6128 | 0 | 171290.2662 | 0 | 877806.3338 | 2283872.0177 | 1558789.581 | 6971253.4039 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 21082227.4702 | 41851994.3918 | 1333.5214 | 0.99587 | 21169.7086 | 42025.6601 | 431.5731 | 856.7499
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4615 | 3.5482 | 0.34622 | 4 | 16561.136 | 31558.5173 | 337.6212 | 643.3631 | 160.3995 | 0 | 95.9902 | 1155743.6056 | 62772.7663 | 913044.7089 | 515340.7821 | 0 | 202211.1556 | 0 | 1111154.0772 | 2890994.9798 | 1973163.4777 | 8824425.5532 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 22935399.6195 | 43705166.5412 | 1778.2794 | 1.3849 | 16561.136 | 31558.5173 | 337.6212 | 643.3631
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5379 | 4.789 | 0.47566 | 4 | 13273.5577 | 24189.8029 | 270.5994 | 493.1419 | 161.9495 | 0 | 88.6444 | 1436176.3758 | 78979.0046 | 1159392.8885 | 683772.5773 | 0 | 239682.1113 | 0 | 1403221.1534 | 3650893.601 | 2491809.901 | 11143927.6129 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 25254901.6792 | 46024668.6008 | 2371.3737 | 1.9026 | 13273.5577 | 24189.8029 | 270.5994 | 493.1419
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6259 | 6.4377 | 0.64774 | 4 | 10867.6067 | 18883.8844 | 221.5509 | 384.9735 | 163.1328 | 0 | 83.7495 | 1777229.5744 | 98597.3024 | 1467834.1648 | 906203.8052 | 0 | 285262.9337 | 0 | 1768699.8344 | 4601794.1589 | 3140819.0708 | 14046440.8446 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 28157414.9109 | 48927181.8326 | 3162.2777 | 2.5909 | 10867.6067 | 18883.8844 | 221.5509 | 384.9735
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.058 | 8.6224 | 0.87511 | 4 | 9077.1389 | 15010.645 | 185.0498 | 306.0123 | 164.0354 | 0 | 80.4804 | 2190867.7563 | 122175.3588 | 1853399.8412 | 1195526.8256 | 0 | 340769.4475 | 0 | 2224068.2994 | 5786569.496 | 3949452.5831 | 17662829.608 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 31773803.6743 | 52543570.5959 | 4216.965 | 3.5004 | 9077.1389 | 15010.645 | 185.0498 | 306.0123
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.24 | 11.5173 | 1.1773 | 4 | 7714.635 | 12125.2101 | 157.2733 | 247.1888 | 164.7201 | 0 | 83.3372 | 2695393.0769 | 150926.5699 | 2335348.4946 | 1583538.557 | 0 | 408209.037 | 0 | 2797632.1368 | 7278864.9468 | 4967974.8919 | 22217887.7111 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 36328861.7774 | 57098628.699 | 5623.4133 | 4.7091 | 7714.635 | 12125.2101 | 157.2733 | 247.1888
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6721 | 15.3235 | 1.5747 | 4 | 6670.5266 | 9967.9363 | 135.9877 | 203.2099 | 165.2369 | 0 | 99.8128 | 3305758.7734 | 185568.0114 | 2933617.891 | 2095162.3436 | 0 | 489625.0163 | 0 | 3513795.4939 | 9142175.0966 | 6239722.3564 | 27905424.9826 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 42016399.0489 | 62786165.9706 | 7498.9421 | 6.2988 | 6670.5266 | 9967.9363 | 135.9877 | 203.2099
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.928 | 20.2697 | 2.0908 | 4 | 5865.1515 | 8348.6397 | 119.569 | 170.1983 | 165.6094 | 0 | 114.142 | 4036673.4829 | 226847.4516 | 3668435.5022 | 2761837.5777 | 0 | 587209.413 | 0 | 4399591.3367 | 11446834.1778 | 7812699.5353 | 34940128.4773 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 49051102.5436 | 69820869.4652 | 10000 | 8.3631 | 5865.1515 | 8348.6397 | 119.569 | 170.1983
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.5527 | 26.5478 | 2.7426 | 4 | 5247.285 | 7140.5486 | 106.973 | 145.5697 | 165.7964 | 0 | 108.269 | 4892109.3507 | 274700.3287 | 4551660.1438 | 3608635.7588 | 0 | 702609.8081 | 0 | 5471589.0021 | 14235952.2063 | 9716329.9004 | 43453586.4989 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 57564560.5652 | 78334327.4869 | 13335.2143 | 10.9704 | 5247.285 | 7140.5486 | 106.973 | 145.5697
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.8948 | 34.2152 | 3.5275 | 4 | 4784.6238 | 6256.6197 | 97.541 | 127.5497 | 165.679 | 0 | 110.0395 | 5855364.4533 | 327569.2399 | 5576445.8574 | 4644848.5699 | 0 | 836774.211 | 0 | 6723990.9093 | 17494445.0658 | 11940318.2323 | 53399756.5389 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 67510730.6052 | 88280497.5269 | 17782.7941 | 14.1099 | 4784.6238 | 6256.6197 | 97.541 | 127.5497
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.2749 | 42.095 | 4.338 | 4 | 4453.7436 | 5650.7094 | 90.7956 | 115.1974 | 165.2059 | 0 | 146.1793 | 6771723.2069 | 376297.4853 | 6584317.0423 | 5713848.9616 | 0 | 949446.501 | 0 | 7954296.9469 | 20695449.0051 | 14125069.195 | 63170448.3441 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 77281422.4104 | 98051189.3321 | 23713.7371 | 17.352 | 4453.7436 | 5650.7094 | 90.7956 | 115.1974
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.3897 | 46.2884 | 4.8751 | 4 | 4207.2269 | 5272.3286 | 85.77 | 107.4835 | 164.8164 | 0 | 170.4173 | 7233613.1823 | 400110.0458 | 7105920.031 | 6288640.722 | 0 | 904396.3065 | 0 | 8553745.3122 | 22255090.6879 | 15189556.6909 | 67931072.9786 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 82042047.0449 | 102811813.9666 | 31622.7766 | 19.5003 | 4207.2269 | 5272.3286 | 85.77 | 107.4835
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1861 | 49.9222 | 5.3568 | 4 | 4016.4043 | 4985.7137 | 81.8798 | 101.6405 | 164.4067 | 0 | 203.8698 | 7621046.6263 | 419661.4477 | 7550842.4593 | 6794043.7027 | 0 | 844687.4752 | 0 | 9059809.8674 | 23571766.8523 | 16088215.2281 | 71950073.659 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 86061047.7253 | 106830814.6469 | 42169.6503 | 21.4274 | 4016.4043 | 4985.7137 | 81.8798 | 101.6405
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.048 | 53.8949 | 5.849 | 4 | 3868.2938 | 4756.0461 | 78.8604 | 96.9584 | 163.9184 | 0 | 255.8144 | 8032829.7407 | 440096.0363 | 8030375.8375 | 7353321.1169 | 0 | 807566.8221 | 0 | 9619033.9259 | 25026753.14 | 17081273.2664 | 76391249.8859 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 90502223.9522 | 111271990.8738 | 56234.1325 | 23.3959 | 3868.2938 | 4756.0461 | 78.8604 | 96.9584
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.5996 | 56.6426 | 6.2266 | 4 | 3752.6594 | 4586.5779 | 76.503 | 93.5036 | 163.5816 | 0 | 260.9764 | 8312843.2284 | 454020.3879 | 8357876.4717 | 7751890.9387 | 0 | 744009.7231 | 0 | 9992049.8924 | 25997264.1689 | 17743666.9856 | 79353621.7967 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 93464595.863 | 114234362.7847 | 74989.4209 | 24.9062 | 3752.6594 | 4586.5779 | 76.503 | 93.5036
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.807 | 58.878 | 6.5391 | 4 | 3663.9608 | 4458.0185 | 74.6948 | 90.8827 | 163.2906 | 0 | 250.6739 | 8536705.9373 | 465015.4121 | 8622160.5768 | 8079489.6693 | 0 | 683037.8144 | 0 | 10290699.6698 | 26774289.6281 | 18274002.8278 | 81725401.5356 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 95836375.6019 | 116606142.5236 | 100000 | 26.1565 | 3663.9608 | 4458.0185 | 74.6948 | 90.8827
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.6083 | 60.5925 | 6.7861 | 4 | 3596.1772 | 4361.3306 | 73.3129 | 88.9116 | 163.0572 | 0 | 254.3125 | 8706073.549 | 473248.6659 | 8823617.809 | 8332903.5088 | 0 | 625381.5801 | 0 | 10514877.794 | 27357555.122 | 18672093.5123 | 83505751.5412 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 97616725.6075 | 118386492.5291 | 133352.1432 | 27.1446 | 3596.1772 | 4361.3306 | 73.3129 | 88.9116
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.0318 | 62.1475 | 6.9989 | 4 | 3544.355 | 4286.2507 | 72.2565 | 87.381 | 162.8362 | 0 | 270.3544 | 8857108.7435 | 480419.5003 | 9005589.214 | 8556100.3735 | 0 | 581623.265 | 0 | 10717528.0276 | 27884809.4605 | 19031955.4323 | 85115134.0167 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 99226108.083 | 119995875.0047 | 177827.941 | 27.9955 | 3544.355 | 4286.2507 | 72.2565 | 87.381
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.9749 | 63.1719 | 7.1495 | 4 | 3504.9062 | 4231.1753 | 71.4523 | 86.2582 | 162.6854 | 0 | 261.8795 | 8955464.3917 | 485021.5805 | 9125069.9499 | 8701644.6883 | 0 | 538712.6438 | 0 | 10844306.1691 | 28214660.1789 | 19257085.3254 | 86121964.9276 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 100232938.9939 | 121002705.9155 | 237137.3706 | 28.5979 | 3504.9062 | 4231.1753 | 71.4523 | 86.2582
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.1844 | 63.9372 | 7.2641 | 4 | 3474.9754 | 4189.7798 | 70.8421 | 85.4143 | 162.5705 | 0 | 286.4173 | 9028461.7657 | 488414.7825 | 9214114.1518 | 8810586.2672 | 0 | 502595.2102 | 0 | 10937227.1492 | 28456421.5084 | 19422092.4005 | 86859913.2354 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 100970887.3017 | 121740654.2233 | 316227.766 | 29.0566 | 3474.9754 | 4189.7798 | 70.8421 | 85.4143
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8387 | 64.5082 | 7.351 | 4 | 3452.3108 | 4158.6662 | 70.38 | 84.78 | 162.4835 | 0 | 277.7223 | 9082657.758 | 490921.6868 | 9280428.1754 | 8891981.2799 | 0 | 472956.5092 | 0 | 11005388.7097 | 28633763.9069 | 19543132.2315 | 87401230.2575 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 101512204.3238 | 122281971.2455 | 421696.5034 | 29.4041 | 3452.3108 | 4158.6662 | 70.38 | 84.78
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.0755 | 64.9339 | 7.4166 | 4 | 3435.1788 | 4135.2866 | 70.0308 | 84.3034 | 162.4179 | 0 | 299.6498 | 9122913.0793 | 492776.6374 | 9329801.0587 | 8952729.9563 | 0 | 449101.6737 | 0 | 11055455.7381 | 28764028.0447 | 19632040.1822 | 87798846.3702 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 101909820.4365 | 122679587.3582 | 562341.3252 | 29.6665 | 3435.1788 | 4135.2866 | 70.0308 | 84.3034
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.977 | 65.2436 | 7.4654 | 4 | 3422.2481 | 4117.7864 | 69.7672 | 83.9466 | 162.3698 | 0 | 319.6758 | 9152111.2223 | 494118.1368 | 9365676.4714 | 8996951.1511 | 0 | 429964.8004 | 0 | 11091140.495 | 28856872.4622 | 19695408.4049 | 88082243.144 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102193217.2103 | 122962984.1319 | 749894.2093 | 29.8614 | 3422.2481 | 4117.7864 | 69.7672 | 83.9466
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.6614 | 65.4783 | 7.5023 | 4 | 3412.5007 | 4104.6115 | 69.5684 | 83.6781 | 162.3331 | 0 | 292.5358 | 9174200.8387 | 495130.902 | 9392852.8662 | 9030494.048 | 0 | 415101.5206 | 0 | 11118034.2685 | 28926844.5442 | 19743165.7886 | 88295824.7769 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102406798.8432 | 123176565.7648 | 1000000 | 30.0093 | 3412.5007 | 4104.6115 | 69.5684 | 83.6781
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1561 | 65.6477 | 7.5296 | 4 | 3405.1609 | 4094.7653 | 69.4188 | 83.4773 | 162.3064 | 0 | 282.5382 | 9190124.5132 | 495859.7275 | 9412463.4098 | 9054723.0478 | 0 | 403407.2412 | 0 | 11137065.3964 | 28976359.6352 | 19776960.8557 | 88446963.8269 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102557937.8932 | 123327704.8148 | 1333521.4322 | 30.1184 | 3405.1609 | 4094.7653 | 69.4188 | 83.4773
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.205 | 64.9772 | 7.4807 | 4 | 3399.0701 | 4093.1852 | 69.2946 | 83.4451 | 162.4093 | 0 | 629.2715 | 9126923.5121 | 492952.4664 | 9334823.0497 | 8958965.966 | 0 | 368888.938 | 0 | 11030196.0335 | 28698307.4749 | 19587184.5429 | 87598241.9834 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 101709216.0497 | 122478982.9713 | 1778279.41 | 29.9227 | 3399.0701 | 4093.1852 | 69.2946 | 83.4451
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.8795 | 65.8954 | 7.5691 | 4 | 3394.7104 | 4080.7176 | 69.2058 | 83.1909 | 162.2675 | 0 | 288.4852 | 9213368.1156 | 496922.7605 | 9441106.9046 | 9090142.9705 | 0 | 386511.1983 | 0 | 11164940.2603 | 29048884.3131 | 19826460.4386 | 88668336.9615 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102779311.0278 | 123549077.9494 | 2371373.7057 | 30.2763 | 3394.7104 | 4080.7176 | 69.2058 | 83.1909
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3741 | 66.0646 | 7.5892 | 4 | 3391.6346 | 4075.8214 | 69.1431 | 83.0911 | 162.241 | 0 | 268.497 | 9229225.4133 | 497647.3207 | 9460661.7032 | 9114345.4828 | 0 | 384313.5588 | 0 | 11187615.4567 | 29107880.523 | 19866726.5641 | 88848416.0226 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102959390.0889 | 123729157.0105 | 3162277.6602 | 30.3569 | 3391.6346 | 4075.8214 | 69.1431 | 83.0911
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.525 | 66.1161 | 7.5977 | 4 | 3389.327 | 4072.7514 | 69.096 | 83.0285 | 162.2328 | 0 | 282.5534 | 9234049.6116 | 497867.1422 | 9466618.6758 | 9121724.687 | 0 | 380379.4765 | 0 | 11193249.4413 | 29122538.995 | 19876731.2724 | 88893159.3017 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 103004133.368 | 123773900.2896 | 4216965.0343 | 30.3907 | 3389.327 | 4072.7514 | 69.096 | 83.0285
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.6325 | 66.1528 | 7.6039 | 4 | 3387.5947 | 4070.4635 | 69.0607 | 82.9819 | 162.2269 | 0 | 248.4926 | 9237480.1871 | 498023.3782 | 9470856.0116 | 9126974.9846 | 0 | 377346.9745 | 0 | 11197165.799 | 29132728.5546 | 19883685.8562 | 88924261.7458 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 103035235.8121 | 123805002.7338 | 5623413.2519 | 30.4155 | 3387.5947 | 4070.4635 | 69.0607 | 82.9819
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.7297 | 66.186 | 7.609 | 4 | 3386.2945 | 4068.7019 | 69.0342 | 82.946 | 162.2216 | 0 | 264.19 | 9240585.8181 | 498164.8574 | 9474691.7078 | 9131727.9624 | 0 | 375230.5435 | 0 | 11200956.3468 | 29142590.7823 | 19890417.0293 | 88954365.0475 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 103065339.1138 | 123835106.0355 | 7498942.0933 | 30.436 | 3386.2945 | 4068.7019 | 69.0342 | 82.946
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.7808 | 66.2034 | 7.6122 | 4 | 3385.3189 | 4067.4396 | 69.0143 | 82.9203 | 162.2188 | 0 | 280.5936 | 9242215.7071 | 498239.0037 | 9476706.0128 | 9134224.8073 | 0 | 373412.4144 | 0 | 11202671.1987 | 29147052.4752 | 19893462.2263 | 88967983.8456 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 103078957.9119 | 123848724.8335 | 10000000 | 30.4488 | 3385.3189 | 4067.4396 | 69.0143 | 82.9203
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.66714 | 0.11148 | 0.0013429 | 4 | 2845942.1753 | 6825879.7415 | 58018.3807 | 139154.7912 | 102.6797 | 0 | 53.6099 | 78166.1983 | 2757.688 | 59628.6577 | 46523.5345 | 0 | 52292.304 | 0 | 93353.6692 | 242887.0977 | 165775.435 | 741384.5844 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15287026.7047 | 36665328.9018 | 100 | 0.0053715 | 2845942.1753 | 6825879.7415 | 58018.3807 | 139154.7912
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85236 | 0.16958 | 0.0056252 | 4 | 689329.7945 | 1639444.7321 | 14052.9202 | 33422.2984 | 113.2841 | 0 | 52.0304 | 111507.7676 | 4247.6769 | 82765.9095 | 55141.0104 | 0 | 57838.7036 | 0 | 121485.4165 | 316080.1337 | 215731.1861 | 964797.8044 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15510439.9247 | 36888742.1218 | 133.3521 | 0.022501 | 689329.7945 | 1639444.7321 | 14052.9202 | 33422.2984
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.25745 | 0.01283 | 4 | 308269.1764 | 724837.3383 | 6284.4841 | 14776.7896 | 123.5631 | 0 | 58.2356 | 157412.1701 | 6458.484 | 114748.2174 | 67653.9993 | 0 | 65301.3934 | 0 | 160513.963 | 417624.4059 | 285037.2383 | 1274749.8714 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15820391.9917 | 37198694.1888 | 177.8279 | 0.05132 | 308269.1764 | 724837.3383 | 6284.4841 | 14776.7896
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.37835 | 0.0238 | 4 | 170271.3805 | 394834.0469 | 3471.2124 | 8049.2261 | 132.4447 | 0 | 66.599 | 214749.7903 | 9400.1841 | 155191.6497 | 84424.5409 | 0 | 73530.8286 | 0 | 209545.8275 | 545195.2594 | 372106.9672 | 1664145.0478 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16209787.168 | 37588089.3652 | 237.1374 | 0.0952 | 170271.3805 | 394834.0469 | 3471.2124 | 8049.2261
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.54325 | 0.039753 | 4 | 105013.6469 | 239458.2495 | 2140.8452 | 4881.6803 | 140.0097 | 0 | 333.2308 | 285783.1501 | 13229.0775 | 206233.651 | 106847.8018 | 0 | 82969.0683 | 0 | 271074.472 | 705280.171 | 481368.2088 | 2152785.6003 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16698427.7206 | 38076729.9177 | 316.2278 | 0.15901 | 105013.6469 | 239458.2495 | 2140.8452 | 4881.6803
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.77547 | 0.062981 | 4 | 68819.5629 | 153680.2986 | 1402.9799 | 3132.9808 | 146.5354 | 0 | 422.1115 | 376617.4869 | 18319.5569 | 272978.8254 | 138199.0297 | 0 | 95178.019 | 0 | 351504.2381 | 914541.924 | 624193.6551 | 2791532.7353 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 17337174.8555 | 38715477.0526 | 421.6965 | 0.25192 | 68819.5629 | 153680.2986 | 1402.9799 | 3132.9808
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2073 | 1.0837 | 0.09481 | 4 | 47784.9452 | 104156.2109 | 974.1607 | 2123.3652 | 151.7711 | 0 | 549.1768 | 486053.252 | 24619.1071 | 355564.3057 | 179300.3383 | 0 | 109155.0966 | 0 | 450329.9189 | 1171666.0735 | 799686.1705 | 3576374.2626 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 18122016.3828 | 39500318.5799 | 562.3413 | 0.37924 | 47784.9452 | 104156.2109 | 974.1607 | 2123.3652
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1969 | 1.4928 | 0.13815 | 4 | 34558.0867 | 73244.5837 | 704.5133 | 1493.1899 | 155.9399 | 0 | 75.7686 | 618672.126 | 32427.7909 | 458106.8794 | 234804.4722 | 0 | 125447.0681 | 0 | 573088.7512 | 1491059.3741 | 1017678.661 | 4551285.1229 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 19096927.2431 | 40475229.4403 | 749.8942 | 0.5526 | 34558.0867 | 73244.5837 | 704.5133 | 1493.1899
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5394 | 2.0515 | 0.19765 | 4 | 25729.7165 | 52770.5639 | 524.5351 | 1075.7993 | 159.3191 | 0 | 93.1508 | 783546.5342 | 42229.498 | 589453.8883 | 309783.4662 | 0 | 146350.7564 | 0 | 729832.0158 | 1898873.1961 | 1296019.9743 | 5796089.3294 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 20341731.4496 | 41720033.6468 | 1000 | 0.79059 | 25729.7165 | 52770.5639 | 524.5351 | 1075.7993
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3226 | 2.7944 | 0.27705 | 4 | 19754.1053 | 39045.4376 | 402.7142 | 795.9941 | 161.8697 | 0 | 88.9101 | 983084.3683 | 54112.842 | 753496.3259 | 409120.1136 | 0 | 171802.4687 | 0 | 924930.2862 | 2406478.8755 | 1642471.2807 | 7345496.5611 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 21891138.6813 | 43269440.8785 | 1333.5214 | 1.1082 | 19754.1053 | 39045.4376 | 402.7142 | 795.9941
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.681 | 3.784 | 0.38381 | 4 | 15514.8885 | 29439.9307 | 316.292 | 600.1728 | 164.0285 | 0 | 79.8172 | 1226226.1813 | 68638.8441 | 959020.7341 | 538191.6269 | 0 | 202013.2998 | 0 | 1167695.3676 | 3038103.8193 | 2073568.2835 | 9273458.1567 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 23819100.2769 | 45197402.4741 | 1778.2794 | 1.5352 | 15514.8885 | 29439.9307 | 316.292 | 600.1728
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8326 | 5.1078 | 0.52691 | 4 | 12458.9117 | 22602.1492 | 253.9918 | 460.7754 | 165.6147 | 0 | 105.6768 | 1524084.337 | 86444.0191 | 1217832.6757 | 713962.236 | 0 | 239501.3104 | 0 | 1474911.5855 | 3837417.3995 | 2619116.2262 | 11713269.7893 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 26258911.9096 | 47637214.1067 | 2371.3737 | 2.1076 | 12458.9117 | 22602.1492 | 253.9918 | 460.7754
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0131 | 6.8683 | 0.71783 | 4 | 10213.0836 | 17658.5357 | 208.2075 | 359.9931 | 166.8263 | 0 | 99.5689 | 1887288.6169 | 108133.5845 | 1542088.7568 | 949267.2386 | 0 | 285006.0167 | 0 | 1860995.8433 | 4841929.4415 | 3304716.3355 | 14779425.8339 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 29325067.9541 | 50703370.1513 | 3162.2777 | 2.8713 | 10213.0836 | 17658.5357 | 208.2075 | 359.9931
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.5574 | 9.2031 | 0.97123 | 4 | 8537.2141 | 14040.107 | 174.0427 | 286.2266 | 167.7494 | 0 | 99.3903 | 2329129.1546 | 134409.5941 | 1947579.3437 | 1260593.7564 | 0 | 340310.2887 | 0 | 2344688.6336 | 6100398.863 | 4163647.5746 | 18620757.2088 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 33166399.3291 | 54544701.5262 | 4216.965 | 3.8849 | 8537.2141 | 14040.107 | 174.0427 | 286.2266
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8831 | 12.2888 | 1.306 | 4 | 7268.1671 | 11360.3645 | 148.1714 | 231.5964 | 168.4502 | 0 | 107.8084 | 2865317.1998 | 166116.5837 | 2453281.6247 | 1670887.2913 | 0 | 407368.5565 | 0 | 2949558.7898 | 7674146.9335 | 5237762.97 | 23424439.9493 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 37970082.0696 | 59348384.2667 | 5623.4133 | 5.2242 | 7268.1671 | 11360.3645 | 148.1714 | 231.5964
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.4958 | 16.339 | 1.7454 | 4 | 6295.3943 | 9357.5187 | 128.3401 | 190.7657 | 168.9788 | 0 | 97.5003 | 3512724.1034 | 204195.874 | 3080118.4298 | 2208883.0425 | 0 | 488237.7231 | 0 | 3702722.0774 | 9633723.3127 | 6575214.1141 | 29405818.677 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 43951460.7973 | 65329762.9944 | 7498.9421 | 6.9815 | 6295.3943 | 9357.5187 | 128.3401 | 190.7657
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9654 | 21.5872 | 2.3152 | 4 | 5543.6831 | 7852.1684 | 113.0155 | 160.0771 | 169.3565 | 0 | 96.5453 | 4286988.9528 | 249640.2729 | 3847812.6083 | 2909843.8188 | 0 | 584952.8416 | 0 | 4632903.0129 | 12053863.3004 | 8227009.3846 | 36793014.1924 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 51338656.3127 | 72716958.5098 | 10000 | 9.2607 | 5543.6831 | 7852.1684 | 113.0155 | 160.0771
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.8562 | 28.2441 | 3.0336 | 4 | 4967.0933 | 6728.8779 | 101.2609 | 137.1773 | 169.5344 | 0 | 118.8779 | 5192316.4405 | 302173.3839 | 4770207.2395 | 3799403.59 | 0 | 699736.463 | 0 | 5757896.4756 | 14980865.5226 | 10224748.5452 | 45727347.6603 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 60272989.7806 | 81651291.9777 | 13335.2143 | 12.1345 | 4967.0933 | 6728.8779 | 101.2609 | 137.1773
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.4541 | 36.3409 | 3.8938 | 4 | 4536.7784 | 5909.3718 | 92.4884 | 120.4705 | 169.3842 | 0 | 127.7072 | 6206435.8682 | 359621.7957 | 5836650.5942 | 4882041.9286 | 0 | 832981.3732 | 0 | 7065915.3084 | 18384062.2139 | 12547500.2157 | 56115209.2978 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 70660851.4181 | 92039153.6152 | 17782.7941 | 15.5751 | 4536.7784 | 5909.3718 | 92.4884 | 120.4705
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.3575 | 45.5517 | 4.8457 | 4 | 4231.1921 | 5334.1383 | 86.2586 | 108.7436 | 168.7811 | 0 | 127.5994 | 7269009.4364 | 417454.7867 | 6995973.132 | 6120053.7114 | 0 | 980405.8819 | 0 | 8495329.8099 | 22103105.5336 | 15085823.7001 | 67467155.992 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 82012798.1122 | 103391100.3093 | 23713.7371 | 19.3829 | 4231.1921 | 5334.1383 | 86.2586 | 108.7436
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2756 | 49.8174 | 5.4109 | 4 | 4009.716 | 4997.4544 | 81.7435 | 101.8799 | 168.3528 | 0 | 159.7108 | 7734237.3401 | 441941.518 | 7517512.9213 | 6702809.6689 | 0 | 927194.1529 | 0 | 9096241.2844 | 23666553.9264 | 16152909.3538 | 72239400.1658 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 86785042.2861 | 108163344.4832 | 31622.7766 | 21.6437 | 4009.716 | 4997.4544 | 81.7435 | 101.8799
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9038 | 53.5059 | 5.9137 | 4 | 3838.3452 | 4742.0996 | 78.2499 | 96.6741 | 167.9109 | 0 | 227.4372 | 8123455.4155 | 461870.3236 | 7961970.6913 | 7209827.8331 | 0 | 861583.6122 | 0 | 9601296.0715 | 24980602.8814 | 17049774.7666 | 76250381.5953 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 90796023.7155 | 112174325.9127 | 42169.6503 | 23.655 | 3838.3452 | 4742.0996 | 78.2499 | 96.6741
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0434 | 57.7195 | 6.4414 | 4 | 3703.8111 | 4533.5395 | 75.5072 | 92.4223 | 167.3978 | 0 | 255.434 | 8555969.9788 | 483620.3497 | 8462786.302 | 7786969.4556 | 0 | 825602.8959 | 0 | 10184830.103 | 26498838.732 | 18086001.9313 | 80884619.7483 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 95430261.8685 | 116808564.0657 | 56234.1325 | 25.7654 | 3703.8111 | 4533.5395 | 75.5072 | 92.4223
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.5024 | 60.5059 | 6.8296 | 4 | 3599.5384 | 4382.0966 | 73.3815 | 89.335 | 167.0425 | 0 | 259.706 | 8835172.6434 | 497409.3019 | 8790275.2534 | 8170169.6817 | 0 | 759416.7655 | 0 | 10550453.0219 | 27450114.5675 | 18735267.2358 | 83788278.4712 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 98333920.5914 | 119712222.7886 | 74989.4209 | 27.3185 | 3599.5384 | 4382.0966 | 73.3815 | 89.335
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.5996 | 62.7519 | 7.1477 | 4 | 3519.4516 | 4267.1831 | 71.7488 | 86.9923 | 166.7378 | 0 | 265.6149 | 9056140.494 | 508133.7765 | 9052303.9508 | 8478813.3105 | 0 | 696515.692 | 0 | 10838843.8173 | 28200448.2601 | 19247385.3988 | 86078584.7 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 100624226.8202 | 122002529.0174 | 100000 | 28.5909 | 3519.4516 | 4267.1831 | 71.7488 | 86.9923
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3844 | 64.4964 | 7.4001 | 4 | 3458.1864 | 4180.4128 | 70.4998 | 85.2234 | 166.4901 | 0 | 271.0098 | 9225289.8314 | 516221.9293 | 9254698.1649 | 8719014.8423 | 0 | 638472.3373 | 0 | 11057941.871 | 28770496.4526 | 19636455.0035 | 87818590.4323 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 102364232.5526 | 123742534.7497 | 133352.1432 | 29.6006 | 3458.1864 | 4180.4128 | 70.4998 | 85.2234
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0332 | 65.8167 | 7.5958 | 4 | 3411.4605 | 4115.0824 | 69.5472 | 83.8915 | 166.2965 | 0 | 275.2972 | 9351888.8949 | 522204.5796 | 9407241.8906 | 8901193.2784 | 0 | 586678.0372 | 0 | 11219990.6055 | 29192114.0191 | 19924217.656 | 89105528.9614 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 103651171.0817 | 125029473.2788 | 177827.941 | 30.3832 | 3411.4605 | 4115.0824 | 69.5472 | 83.8915
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8176 | 66.8181 | 7.7467 | 4 | 3375.9295 | 4065.8486 | 68.8229 | 82.8878 | 166.1459 | 0 | 258.9596 | 9447095.7894 | 526661.0498 | 9522593.4156 | 9039611.728 | 0 | 542447.9746 | 0 | 11340579.8834 | 29505862.5839 | 20138357.4983 | 90063209.9232 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 104608852.0434 | 125987154.2405 | 237137.3706 | 30.9867 | 3375.9295 | 4065.8486 | 68.8229 | 82.8878
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.8982 | 67.5629 | 7.8611 | 4 | 3348.9719 | 4028.848 | 68.2733 | 82.1335 | 166.0318 | 0 | 248.5883 | 9517450.1035 | 529929.7534 | 9608195.561 | 9142700.5609 | 0 | 505360.5345 | 0 | 11428418.2402 | 29734399.97 | 20294338.9603 | 90760793.6837 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 105306435.804 | 126684738.0011 | 316227.766 | 31.4444 | 3348.9719 | 4028.848 | 68.2733 | 82.1335
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.8271 | 68.2481 | 7.9592 | 4 | 3328.5253 | 4000.024 | 67.8565 | 81.5459 | 165.925 | 0 | 289.927 | 9581890.7181 | 532913.0224 | 9686795.8958 | 9237084.3856 | 0 | 478951.8287 | 0 | 11511877.9817 | 29951545.0975 | 20442544.9717 | 91423603.9014 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 105969246.0217 | 127347548.2188 | 421696.5034 | 31.8367 | 3328.5253 | 4000.024 | 67.8565 | 81.5459
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.0038 | 68.6639 | 8.0247 | 4 | 3313.0599 | 3979.0762 | 67.5412 | 81.1189 | 165.8592 | 0 | 317.3023 | 9620835.9055 | 534707.7333 | 9734422.7798 | 9294253.379 | 0 | 454777.5532 | 0 | 11559208.9668 | 30074690.6118 | 20526594.3157 | 91799491.245 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 106345133.3653 | 127723435.5624 | 562341.3252 | 32.0988 | 3313.0599 | 3979.0762 | 67.5412 | 81.1189
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8734 | 68.9705 | 8.0737 | 4 | 3301.3863 | 3963.359 | 67.3032 | 80.7984 | 165.8102 | 0 | 297.0034 | 9649478.6377 | 536023.3261 | 9769514.4888 | 9336432.326 | 0 | 435564.3901 | 0 | 11593535.1358 | 30164000.2622 | 20587549.9872 | 92072098.5537 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 106617740.6739 | 127996042.8711 | 749894.2093 | 32.2948 | 3301.3863 | 3963.359 | 67.3032 | 80.7984
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5191 | 69.1977 | 8.1104 | 4 | 3292.586 | 3951.5617 | 67.1238 | 80.5579 | 165.7737 | 0 | 287.6542 | 9670668.9029 | 536994.221 | 9795511.0149 | 9367710.2045 | 0 | 420509.9221 | 0 | 11618643.7635 | 30229327.7612 | 20632137.3476 | 92271503.1377 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 106817145.2579 | 128195447.4551 | 1000000 | 32.4417 | 3292.586 | 3951.5617 | 67.1238 | 80.5579
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.9944 | 69.3648 | 8.1378 | 4 | 3285.9591 | 3942.7203 | 66.9887 | 80.3777 | 165.7467 | 0 | 279.9481 | 9686224.5934 | 537705.6134 | 9814614.4858 | 9390711.5527 | 0 | 408779.4266 | 0 | 11636833.9121 | 30276654.7963 | 20664439.0215 | 92415963.4019 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 106961605.5221 | 128339907.7192 | 1333521.4322 | 32.5511 | 3285.9591 | 3942.7203 | 66.9887 | 80.3777
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.3427 | 69.4872 | 8.1581 | 4 | 3280.9732 | 3936.0995 | 66.8871 | 80.2427 | 165.7269 | 0 | 275.3486 | 9697604.5353 | 538225.2998 | 9828600.5784 | 9407560.4838 | 0 | 399692.3272 | 0 | 11649956.4575 | 30310796.9677 | 20687741.7551 | 92520178.4047 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107065820.5249 | 128444122.7221 | 1778279.41 | 32.6323 | 3280.9732 | 3936.0995 | 66.8871 | 80.2427
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6056 | 69.5795 | 8.1734 | 4 | 3277.2247 | 3931.1241 | 66.8107 | 80.1413 | 165.7119 | 0 | 263.7931 | 9706177.7646 | 538616.4308 | 9839142.8495 | 9420265.7173 | 0 | 392773.6099 | 0 | 11659820.7851 | 30336461.9247 | 20705258.6156 | 92598517.6974 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107144159.8176 | 128522462.0148 | 2371373.7057 | 32.6936 | 3277.2247 | 3931.1241 | 66.8107 | 80.1413
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.2379 | 69.4501 | 8.1684 | 4 | 3273.7224 | 3928.0243 | 66.7393 | 80.0781 | 165.7324 | 0 | 265.2543 | 9694134.5291 | 538064.5026 | 9824359.9028 | 9402454.5259 | 0 | 379739.4251 | 0 | 11637113.6253 | 30277382.5528 | 20664935.7303 | 92418184.7938 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 106963826.9141 | 128342129.1112 | 3162277.6602 | 32.6735 | 3273.7224 | 3928.0243 | 66.7393 | 80.0781
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3218 | 69.831 | 8.2065 | 4 | 3271.6096 | 3922.8695 | 66.6962 | 79.973 | 165.6714 | 0 | 278.0631 | 9729544.4273 | 539683.7086 | 9867870.7089 | 9454905.3395 | 0 | 385666.025 | 0 | 11691291.3817 | 30418341.9615 | 20761143.4231 | 92848446.9756 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107394089.0959 | 128772391.293 | 4216965.0343 | 32.8261 | 3271.6096 | 3922.8695 | 66.6962 | 79.973
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.4144 | 69.8635 | 8.2124 | 4 | 3270.046 | 3920.8413 | 66.6643 | 79.9317 | 165.6661 | 0 | 271.7259 | 9732549.7957 | 539820.2868 | 9871573.6298 | 9459373.3843 | 0 | 382523.2086 | 0 | 11694477.7191 | 30426632.1578 | 20766801.6525 | 92873751.8347 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107419393.9549 | 128797696.1521 | 5623413.2519 | 32.8495 | 3270.046 | 3920.8413 | 66.6643 | 79.9317
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.505 | 69.8952 | 8.2174 | 4 | 3268.8725 | 3919.267 | 66.6404 | 79.8996 | 165.6609 | 0 | 269.062 | 9735489.1347 | 539953.8779 | 9875195.2283 | 9463743.7424 | 0 | 380374.8318 | 0 | 11697955.1579 | 30435679.7403 | 20772976.8135 | 92901368.5268 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107447010.6471 | 128825312.8442 | 7498942.0933 | 32.8697 | 3268.8725 | 3919.267 | 66.6404 | 79.8996
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5607 | 69.9147 | 8.2208 | 4 | 3267.9919 | 3918.1164 | 66.6224 | 79.8761 | 165.6577 | 0 | 256.4462 | 9737295.94 | 540035.9064 | 9877422.4384 | 9466431.7858 | 0 | 378628.2654 | 0 | 11699927.5911 | 30440811.6068 | 20776479.4178 | 92917032.9516 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107462675.0719 | 128840977.269 | 10000000 | 32.8834 | 3267.9919 | 3918.1164 | 66.6224 | 79.8761
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.68659 | 0.11949 | 0.0020292 | 4 | 1941534.7254 | 4651295.891 | 39580.8115 | 94822.9581 | 105.0594 | 0 | 54.868 | 83288.9421 | 2988.8487 | 62920.915 | 47604.5081 | 0 | 52838.2019 | 0 | 97360.1522 | 253311.1446 | 172890.0612 | 773202.7739 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 15759373.0389 | 37754414.6388 | 100 | 0.008117 | 1941534.7254 | 4651295.891 | 39580.8115 | 94822.9581
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.18413 | 0.0069607 | 4 | 574825 | 1364795.2851 | 11718.5851 | 27823.1979 | 116.2367 | 0 | 54.5596 | 120035.8507 | 4669.6132 | 88210.1723 | 57014.7259 | 0 | 58944.4452 | 0 | 128261.1749 | 333709.267 | 227763.4318 | 1018608.681 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16004778.946 | 37999820.5459 | 133.3521 | 0.027843 | 574825 | 1364795.2851 | 11718.5851 | 27823.1979
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.27671 | 0.014972 | 4 | 272596.4171 | 639874.4332 | 5557.2467 | 13044.7058 | 126.4816 | 0 | 45.9006 | 167922.0981 | 7032.9827 | 121324.088 | 69909.7028 | 0 | 66035.8974 | 0 | 168567.66 | 438578.4732 | 299338.8199 | 1338709.7221 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16324879.9871 | 38319921.587 | 177.8279 | 0.059887 | 272596.4171 | 639874.4332 | 5557.2467 | 13044.7058
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.476 | 0.40456 | 0.027107 | 4 | 154300.7622 | 357157.8137 | 3145.6297 | 7281.1451 | 135.4236 | 0 | 70.0809 | 228107.8563 | 10201.7867 | 163408.8429 | 87415.4246 | 0 | 73975.3071 | 0 | 219612.5949 | 571386.9232 | 389983.3159 | 1744092.0518 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16730262.3168 | 38725303.9167 | 237.1374 | 0.10843 | 154300.7622 | 357157.8137 | 3145.6297 | 7281.1451
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.58457 | 0.045117 | 4 | 95626.5313 | 217503.3314 | 1949.4762 | 4434.0996 | 143.2659 | 0 | 328.102 | 305103.393 | 14473.3167 | 218209.2076 | 111729.4293 | 0 | 83876.073 | 0 | 286022.6536 | 744172.2734 | 507912.8678 | 2271499.2144 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17257669.4795 | 39252711.0794 | 316.2278 | 0.18047 | 95626.5313 | 217503.3314 | 1949.4762 | 4434.0996
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.82661 | 0.070389 | 4 | 63620.5439 | 141740.5426 | 1296.9908 | 2889.5727 | 149.7523 | 0 | 421.3622 | 399126.9622 | 19900.201 | 286676.9414 | 143877.5074 | 0 | 95282.4985 | 0 | 368497.0031 | 958753.6129 | 654369.0412 | 2926483.7677 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17912654.0327 | 39907695.6326 | 421.6965 | 0.28155 | 63620.5439 | 141740.5426 | 1296.9908 | 2889.5727
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 1.1574 | 0.1059 | 4 | 44257.9933 | 96179.9433 | 902.2591 | 1960.7582 | 155.1198 | 0 | 563.2604 | 516231.9495 | 26885.7595 | 373905.7296 | 188368.2244 | 0 | 109325.1174 | 0 | 473739.5443 | 1232573.117 | 841256.4792 | 3762285.9208 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 18748456.1859 | 40743497.7857 | 562.3413 | 0.42362 | 44257.9933 | 96179.9433 | 902.2591 | 1960.7582
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3166 | 1.6009 | 0.15427 | 4 | 32070.5744 | 67715.0506 | 653.802 | 1380.4629 | 159.4432 | 0 | 72.3512 | 658902.6989 | 35549.0063 | 483332.0577 | 246827.644 | 0 | 126289.4621 | 0 | 604851.3389 | 1573699.1118 | 1074081.9801 | 4803533.2997 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 19789703.5648 | 41784745.1646 | 749.8942 | 0.61707 | 32070.5744 | 67715.0506 | 653.802 | 1380.4629
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 2.1938 | 0.21974 | 4 | 23997.1604 | 49020.7496 | 489.2146 | 999.3543 | 162.857 | 0 | 97.5117 | 832861.8722 | 46257.3297 | 620481.7851 | 325236.7496 | 0 | 146802.1757 | 0 | 768939.5658 | 2000623.019 | 1365466.3192 | 6106668.8162 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 21092839.0813 | 43087880.6811 | 1000 | 0.87897 | 23997.1604 | 49020.7496 | 489.2146 | 999.3543
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4884 | 2.9736 | 0.30595 | 4 | 18540.5161 | 36513.0772 | 377.9735 | 744.3685 | 165.417 | 0 | 81.6706 | 1040910.561 | 59034.898 | 790109.957 | 425848.8897 | 0 | 171441.8236 | 0 | 970064.9904 | 2523910.1174 | 1722620.5163 | 7703941.7533 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 22690112.0184 | 44685153.6182 | 1333.5214 | 1.2238 | 18540.5161 | 36513.0772 | 377.9735 | 744.3685
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9025 | 4.0355 | 0.42531 | 4 | 14548.6058 | 27477.2949 | 296.593 | 560.1618 | 167.6501 | 0 | 99.326 | 1302038.8833 | 75372.6166 | 1007156.8076 | 566435.3279 | 0 | 201714.7519 | 0 | 1229560.171 | 3199063.3476 | 2183426.4689 | 9764768.3748 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 24750938.6398 | 46745980.2397 | 1778.2794 | 1.7013 | 14548.6058 | 27477.2949 | 296.593 | 560.1618
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1226 | 5.4463 | 0.58359 | 4 | 11705.2071 | 21127.4326 | 238.6265 | 430.7113 | 169.2725 | 0 | 98.582 | 1618639.1671 | 95075.0172 | 1278693.0458 | 752165.6403 | 0 | 239025.6571 | 0 | 1553603.4258 | 4042157.4259 | 2758855.5012 | 12338214.8805 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 27324385.1455 | 49319426.7454 | 2371.3737 | 2.3344 | 11705.2071 | 21127.4326 | 238.6265 | 430.7113
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3958 | 7.3221 | 0.79486 | 4 | 9611.6717 | 16529.6007 | 195.9469 | 336.9783 | 170.5128 | 0 | 89.6851 | 2004914.3886 | 119132.3613 | 1618807.8407 | 1000928.8619 | 0 | 284356.8554 | 0 | 1960974.7201 | 5102053.9704 | 3482256.6715 | 15573425.67 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 30559595.935 | 52554637.5349 | 3162.2777 | 3.1794 | 9611.6717 | 16529.6007 | 195.9469 | 336.9783
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0495 | 9.8045 | 1.0748 | 4 | 8049.0902 | 13165.1319 | 164.0916 | 268.389 | 171.4563 | 0 | 108.9151 | 2473946.9433 | 148232.4439 | 2043255.7879 | 1329614.2196 | 0 | 339182.6815 | 0 | 2470350.5097 | 6427345.2877 | 4386795.2276 | 19618723.1011 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 34604893.3661 | 56599934.966 | 4216.965 | 4.2992 | 8049.0902 | 13165.1319 | 164.0916 | 268.389
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.5279 | 13.0882 | 1.4456 | 4 | 6862.0047 | 10665.8849 | 139.8912 | 217.4385 | 172.1739 | 0 | 115.5666 | 3044488.6373 | 183542.3416 | 2573006.5239 | 1765212.6353 | 0 | 405895.3213 | 0 | 3109136.7291 | 8089335.9976 | 5521138.0376 | 24691756.2237 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 39677926.4887 | 61672968.0886 | 5623.4133 | 5.7823 | 6862.0047 | 10665.8849 | 139.8912 | 217.4385
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.3453 | 17.4092 | 1.9319 | 4 | 5952.7353 | 8799.0728 | 121.3546 | 179.381 | 172.7152 | 0 | 104.2777 | 3733565.6336 | 225717.1071 | 3231530.422 | 2335738.5843 | 0 | 486682.3653 | 0 | 3905161.3038 | 10160428.6538 | 6934701.3322 | 31013525.4022 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 45999695.6672 | 67994737.2671 | 7498.9421 | 7.7275 | 5952.7353 | 8799.0728 | 121.3546 | 179.381
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0495 | 22.9936 | 2.5599 | 4 | 5251.3071 | 7399.3511 | 107.055 | 150.8458 | 173.0971 | 0 | 120.7857 | 4554418.9786 | 275674.1588 | 4036096.9369 | 3073229.4747 | 0 | 582946.5889 | 0 | 4883722.7938 | 12706444.9201 | 8672409.7493 | 38784943.6011 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 53771113.8661 | 75766155.466 | 10000 | 10.2396 | 5251.3071 | 7399.3511 | 107.055 | 150.8458
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1863 | 30.0416 | 3.3485 | 4 | 4713.2544 | 6355.4278 | 96.0861 | 129.564 | 173.2632 | 0 | 110.3045 | 5510282.1037 | 333229.2817 | 4998085.0447 | 4005313.931 | 0 | 696699.2161 | 0 | 6062007.7351 | 15772100.638 | 10764782.7697 | 48142500.72 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 63128670.985 | 85123712.5849 | 13335.2143 | 13.3939 | 4713.2544 | 6355.4278 | 96.0861 | 129.564
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.04 | 38.5847 | 4.2898 | 4 | 4312.1009 | 5593.9266 | 87.908 | 114.0398 | 173.0767 | 0 | 129.9325 | 6578143.9077 | 395941.789 | 6106816.7931 | 5141157.3214 | 0 | 828953.1084 | 0 | 7429895.0386 | 19331062.8095 | 13193847.5811 | 59005818.3488 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 73991988.6138 | 95987030.2137 | 17782.7941 | 17.1592 | 4312.1009 | 5593.9266 | 87.908 | 114.0398
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3092 | 48.2839 | 5.33 | 4 | 4027.5594 | 5059.216 | 82.1072 | 103.139 | 172.4073 | 0 | 117.996 | 7696856.8012 | 459112.5958 | 7309936.4333 | 6442122.5561 | 0 | 977367.7511 | 0 | 8925304.4936 | 23221811.4607 | 15849363.4824 | 70881875.5742 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 85868045.8393 | 107863087.4391 | 23713.7371 | 21.3201 | 4027.5594 | 5059.216 | 82.1072 | 103.139
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8151 | 53.3301 | 5.9785 | 4 | 3828.0414 | 4747.7935 | 78.0398 | 96.7902 | 171.8751 | 0 | 152.8648 | 8243936.621 | 488529.2897 | 7917868.111 | 7123477.4882 | 0 | 944211.2056 | 0 | 9640028.859 | 25081377.6494 | 17118555.6165 | 76557984.8404 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 91544155.1054 | 113539196.7053 | 31622.7766 | 23.9141 | 3828.0414 | 4747.7935 | 78.0398 | 96.7902
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.8165 | 58.0946 | 6.5839 | 4 | 3674.0609 | 4509.2485 | 74.9007 | 91.9271 | 171.2887 | 0 | 207.5167 | 8737386.1245 | 513582.1082 | 8483009.6183 | 7760641.3388 | 0 | 906796.2165 | 0 | 10296552.0084 | 26789516.2127 | 18284395.2847 | 81771878.9121 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 96758049.1772 | 118753090.777 | 42169.6503 | 26.3355 | 3674.0609 | 4509.2485 | 74.9007 | 91.9271
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.9286 | 61.669 | 7.0744 | 4 | 3552.2782 | 4329.5508 | 72.418 | 88.2637 | 170.8527 | 0 | 260.4521 | 9099234.1073 | 531854.9507 | 8901066.6097 | 8242306.7324 | 0 | 842003.9773 | 0 | 10770421.8872 | 28022428.4331 | 19125883.2089 | 85535199.9066 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 100521370.1717 | 122516411.7715 | 56234.1325 | 28.2977 | 3552.2782 | 4329.5508 | 72.418 | 88.2637
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.1176 | 64.4296 | 7.472 | 4 | 3458.2329 | 4194.1522 | 70.5008 | 85.5035 | 170.4869 | 0 | 235.7099 | 9374511.1071 | 545751.1901 | 9220662.0137 | 8620445.4206 | 0 | 771314.8859 | 0 | 11127747.0009 | 28952115.0815 | 19760413.4496 | 88372960.1494 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 103359130.4145 | 125354172.0143 | 74989.4209 | 29.8878 | 3458.2329 | 4194.1522 | 70.5008 | 85.5035
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.823 | 66.5938 | 7.7915 | 4 | 3386.1042 | 4091.8407 | 69.0303 | 83.4177 | 170.1833 | 0 | 253.4889 | 9586630.7982 | 556266.1487 | 9469525.5479 | 8918227.7309 | 0 | 703450.375 | 0 | 11401299.2342 | 29663841.8794 | 20246181.6137 | 90545423.328 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 105531593.593 | 127526635.1929 | 100000 | 31.1661 | 3386.1042 | 4091.8407 | 69.0303 | 83.4177
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2218 | 68.2477 | 8.0416 | 4 | 3330.9601 | 4014.7473 | 67.9061 | 81.8461 | 169.9414 | 0 | 287.7969 | 9746169.4563 | 563995.6578 | 9658829.8029 | 9145004.7804 | 0 | 641120.5376 | 0 | 11604496.8917 | 30192520.5025 | 20607015.6372 | 92159153.2665 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 107145323.5315 | 129140365.1314 | 133352.1432 | 32.1665 | 3330.9601 | 4014.7473 | 67.9061 | 81.8461
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.6861 | 69.5443 | 8.2378 | 4 | 3288.9329 | 3956.434 | 67.0493 | 80.6573 | 169.7463 | 0 | 253.9528 | 9868883.101 | 569708.2192 | 9806880.4847 | 9319024.1658 | 0 | 587540.684 | 0 | 11759294.2953 | 30595271.5935 | 20881901.5325 | 93388504.0761 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 108374674.3411 | 130369715.941 | 177827.941 | 32.9513 | 3288.9329 | 3956.434 | 67.0493 | 80.6573
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.3534 | 70.5369 | 8.3897 | 4 | 3256.9627 | 3912.3832 | 66.3976 | 79.7592 | 169.5935 | 0 | 284.6244 | 9962008.5971 | 573991.8885 | 9919909.1526 | 9452329.2323 | 0 | 542338.3751 | 0 | 11875725.1258 | 30898200.731 | 21088656.8935 | 94313159.9958 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 109299330.2608 | 131294371.8607 | 237137.3706 | 33.5587 | 3256.9627 | 3912.3832 | 66.3976 | 79.7592
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.3218 | 71.2664 | 8.5039 | 4 | 3232.6951 | 3879.3105 | 65.9029 | 79.085 | 169.4792 | 0 | 276.0732 | 10030004.7063 | 577091.634 | 10002809.0685 | 9550349.3844 | 0 | 504341.9051 | 0 | 11959192.7124 | 31115366.2698 | 21236876.836 | 94976032.5165 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 109962202.7816 | 131957244.3814 | 316227.766 | 34.0156 | 3232.6951 | 3879.3105 | 65.9029 | 79.085
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8003 | 71.8125 | 8.5905 | 4 | 3214.3141 | 3854.4145 | 65.5281 | 78.5775 | 169.3926 | 0 | 301.1454 | 10080655.0595 | 579384.2842 | 10064775.9348 | 9623755.4926 | 0 | 473462.1235 | 0 | 12020592.8289 | 31275116.7781 | 21345909.8405 | 95463652.3421 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 110449822.6071 | 132444864.207 | 421696.5034 | 34.3619 | 3214.3141 | 3854.4145 | 65.5281 | 78.5775
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.8823 | 72.2111 | 8.655 | 4 | 3200.4159 | 3835.7471 | 65.2448 | 78.1969 | 169.3287 | 0 | 277.8728 | 10117496.4647 | 581042.7427 | 10109967.9188 | 9677363.8409 | 0 | 448500.9318 | 0 | 12064405.0406 | 31389107.1658 | 21423710.6223 | 95811594.7276 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 110797764.9927 | 132792806.5925 | 562341.3252 | 34.6198 | 3200.4159 | 3835.7471 | 65.2448 | 78.1969
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.6936 | 72.5095 | 8.7036 | 4 | 3189.923 | 3821.7055 | 65.0309 | 77.9106 | 169.2806 | 0 | 264.7471 | 10144993.5857 | 582275.5795 | 10143763.0635 | 9717493.6252 | 0 | 428837.7336 | 0 | 12096771.7991 | 31473318.8322 | 21481186.815 | 96068641.0338 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111054811.2989 | 133049852.8987 | 749894.2093 | 34.8143 | 3189.923 | 3821.7055 | 65.0309 | 77.9106
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2855 | 72.7269 | 8.7396 | 4 | 3182.0113 | 3811.1873 | 64.8696 | 77.6962 | 169.2453 | 0 | 252.2021 | 10164987.8418 | 583169.1959 | 10168373.5879 | 9746739.0861 | 0 | 413340.3186 | 0 | 12119877.9118 | 31533436.1977 | 21522218.1523 | 96252142.2921 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111238312.5572 | 133233354.1571 | 1000000 | 34.9585 | 3182.0113 | 3811.1873 | 64.8696 | 77.6962
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.7038 | 72.8803 | 8.7659 | 4 | 3176.0525 | 3803.3431 | 64.7481 | 77.5363 | 169.2202 | 0 | 337.7269 | 10179078.808 | 583797.3838 | 10185737.9837 | 9767384.7548 | 0 | 401096.288 | 0 | 12135667.1351 | 31574516.518 | 21550256.315 | 96377535.1864 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111363705.4515 | 133358747.0513 | 1333521.4322 | 35.0636 | 3176.0525 | 3803.3431 | 64.7481 | 77.5363
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0398 | 73.0035 | 8.7864 | 4 | 3171.5686 | 3797.3963 | 64.6567 | 77.4151 | 169.2001 | 0 | 317.1894 | 10190380.0978 | 584300.5734 | 10199673.7012 | 9783960.634 | 0 | 391947.9051 | 0 | 12148602.5355 | 31608171.7763 | 21573226.7203 | 96480263.9437 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111466434.2088 | 133461475.8086 | 1778279.41 | 35.1455 | 3171.5686 | 3797.3963 | 64.6567 | 77.4151
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.2593 | 73.0839 | 8.8007 | 4 | 3168.1971 | 3793.0075 | 64.588 | 77.3256 | 169.1869 | 0 | 295.5247 | 10197748.3448 | 584627.9777 | 10208767.3184 | 9794780.1018 | 0 | 384615.8148 | 0 | 12156510.4274 | 31628746.4889 | 21587269.3844 | 96543065.8581 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111529236.1232 | 133524277.723 | 2371373.7057 | 35.2027 | 3168.1971 | 3793.0075 | 64.588 | 77.3256
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.005 | 72.6228 | 8.7649 | 4 | 3165.1116 | 3792.4705 | 64.5251 | 77.3146 | 169.2606 | 0 | 491.7075 | 10155344.3882 | 582727.3641 | 10156604.0531 | 9732743.6756 | 0 | 361912.5609 | 0 | 12085839.4963 | 31444875.2229 | 21461773.4672 | 95981820.2284 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 110967990.4935 | 132963032.0933 | 3162277.6602 | 35.0597 | 3165.1116 | 3792.4705 | 64.5251 | 77.3146
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6079 | 73.2117 | 8.8228 | 4 | 3163.1363 | 3786.3787 | 64.4848 | 77.1905 | 169.1661 | 0 | 331.4887 | 10209460.9453 | 585149.4947 | 10223214.9216 | 9811975.9193 | 0 | 373672.3171 | 0 | 12169354.7032 | 31662164.6599 | 21610077.9728 | 96645070.9339 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111631241.1989 | 133626282.7988 | 4216965.0343 | 35.2913 | 3163.1363 | 3786.3787 | 64.4848 | 77.1905
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.0487 | 73.3733 | 8.8405 | 4 | 3161.7267 | 3783.7231 | 64.4561 | 77.1363 | 169.1399 | 0 | 298.7819 | 10224263.6474 | 585808.6069 | 10241478.4162 | 9833723.2907 | 0 | 374300.8179 | 0 | 12191234.1639 | 31719090.5284 | 21648931.0478 | 96818830.5191 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111805000.7842 | 133800042.384 | 5623413.2519 | 35.362 | 3161.7267 | 3783.7231 | 64.4561 | 77.1363
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.107 | 73.3946 | 8.8446 | 4 | 3160.6714 | 3782.3768 | 64.4346 | 77.1089 | 169.1364 | 0 | 308.0124 | 10226211.3777 | 585894.662 | 10243888.1874 | 9836593.1567 | 0 | 371826.1846 | 0 | 12193121.2917 | 31724000.4479 | 21652282.1687 | 96833817.4766 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111819987.7417 | 133815029.3415 | 7498942.0933 | 35.3786 | 3160.6714 | 3782.3768 | 64.4346 | 77.1089
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.1607 | 73.4142 | 8.8481 | 4 | 3159.8795 | 3781.3434 | 64.4184 | 77.0878 | 169.1331 | 0 | 300.8456 | 10228005.9303 | 585974.0498 | 10246107.5711 | 9839236.514 | 0 | 370070.5356 | 0 | 12195063.8943 | 31729054.7015 | 21655731.8006 | 96849244.9972 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 111835415.2622 | 133830456.8621 | 10000000 | 35.3923 | 3159.8795 | 3781.3434 | 64.4184 | 77.0878
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.70141 | 0.12637 | 0.0027359 | 4 | 1483212.8412 | 3550160.8947 | 30237.3 | 72374.8318 | 107.131 | 0 | 42.6354 | 87719.3368 | 3194.4734 | 65706.8166 | 48494.2048 | 0 | 52928.1534 | 0 | 100636.7642 | 261836.2169 | 178708.5982 | 799224.5643 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16231783.065 | 38851768.1948 | 100 | 0.010944 | 1483212.8412 | 3550160.8947 | 30237.3 | 72374.8318
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.19508 | 0.0082257 | 4 | 501149.6192 | 1188627.9242 | 10216.6128 | 24231.788 | 118.603 | 0 | 59.0769 | 126569.9905 | 5006.8943 | 92231.0926 | 58342.6234 | 0 | 59017.67 | 0 | 133055.6256 | 346183.4443 | 236277.3141 | 1056684.6548 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16489243.1555 | 39109228.2853 | 133.3521 | 0.032903 | 501149.6192 | 1188627.9242 | 10216.6128 | 24231.788
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1619 | 0.29132 | 0.01697 | 4 | 247754.284 | 580990.9155 | 5050.8062 | 11844.2857 | 128.913 | 0 | 49.7822 | 176145.3501 | 7507.9258 | 126210.6648 | 71615.2506 | 0 | 65663.7235 | 0 | 174385.7368 | 453715.9156 | 309670.4354 | 1384915.0026 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16817473.5033 | 39437458.6331 | 177.8279 | 0.06788 | 247754.284 | 580990.9155 | 5050.8062 | 11844.2857
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.43005 | 0.030525 | 4 | 141300.7656 | 326560.1143 | 2880.6072 | 6657.3696 | 138.3013 | 0 | 58.1227 | 241104.1951 | 11010.1864 | 171267.1477 | 90223.8916 | 0 | 74052.8364 | 0 | 229186.7203 | 596296.8336 | 406984.8416 | 1820126.6528 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17252685.1535 | 39872670.2833 | 237.1374 | 0.1221 | 141300.7656 | 326560.1143 | 2880.6072 | 6657.3696
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.62753 | 0.050847 | 4 | 87638.4943 | 198854.3094 | 1786.6292 | 4053.9141 | 146.5191 | 0 | 335.7783 | 324969.4171 | 15793.5008 | 230456.6233 | 116433.9543 | 0 | 84668.6808 | 0 | 301205.6488 | 783675.3123 | 534874.5036 | 2392077.6409 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17824636.1416 | 40444621.2714 | 316.2278 | 0.20339 | 87638.4943 | 198854.3094 | 1786.6292 | 4053.9141
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.88049 | 0.078423 | 4 | 58979.0563 | 131087.5287 | 1202.3678 | 2672.3966 | 152.9676 | 0 | 430.1227 | 422800.7006 | 21632.5876 | 300875.0272 | 150216.3145 | 0 | 95291.6886 | 0 | 386418.3642 | 1005381.3184 | 686193.4083 | 3068809.4095 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 18501367.9102 | 41121353.04 | 421.6965 | 0.31369 | 58979.0563 | 131087.5287 | 1202.3678 | 2672.3966
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3628 | 1.2331 | 0.11751 | 4 | 41229.5928 | 89352.2325 | 840.521 | 1821.5661 | 158.4659 | 0 | 575.7736 | 546866.0661 | 29267.933 | 392478.2542 | 196528.9095 | 0 | 109329.4771 | 0 | 497043.5495 | 1293205.3582 | 882639.2297 | 3947358.7772 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 19379917.2779 | 41999902.4077 | 562.3413 | 0.47005 | 41229.5928 | 89352.2325 | 840.521 | 1821.5661
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4138 | 1.7041 | 0.17071 | 4 | 29982.6316 | 63108.6869 | 611.2365 | 1286.5559 | 162.8699 | 0 | 74.3882 | 697790.0833 | 38766.567 | 506944.5892 | 257998.4356 | 0 | 126056.1947 | 0 | 634746.7892 | 1651480.941 | 1127169.6768 | 5040953.2767 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 20473511.7774 | 43093496.9072 | 749.8942 | 0.68285 | 29982.6316 | 63108.6869 | 611.2365 | 1286.5559
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.817 | 2.336 | 0.24268 | 4 | 22501.0655 | 45803.6056 | 458.7147 | 933.7685 | 166.3713 | 0 | 62.719 | 882186.4632 | 50511.1316 | 650958.6425 | 339094.8358 | 0 | 146639.6858 | 0 | 807062.396 | 2099810.8031 | 1433164.0199 | 6409427.9779 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 21841986.4786 | 44461971.6083 | 1000 | 0.97071 | 22501.0655 | 45803.6056 | 458.7147 | 933.7685
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.671 | 3.1732 | 0.33868 | 4 | 17382.233 | 34079.2492 | 354.3603 | 694.7516 | 168.9728 | 0 | 95.4109 | 1105311.9276 | 64834.06 | 830209.0027 | 448399.9012 | 0 | 171538.0986 | 0 | 1021914.2661 | 2658811.2971 | 1814693.3434 | 8115711.8967 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 23548270.3974 | 46168255.5272 | 1333.5214 | 1.3547 | 17382.233 | 34079.2492 | 354.3603 | 694.7516
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1406 | 4.3054 | 0.47081 | 4 | 13660.6999 | 25672.0065 | 278.4918 | 523.3586 | 171.2771 | 0 | 90.8926 | 1383412.4733 | 83068.6279 | 1057921.1829 | 597434.8218 | 0 | 201624.6959 | 0 | 1296150.1027 | 3372316.6902 | 2301675.4353 | 10293604.03 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 25726162.5307 | 48346147.6605 | 1778.2794 | 1.8832 | 13660.6999 | 25672.0065 | 278.4918 | 523.3586
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4199 | 5.8055 | 0.64542 | 4 | 11015.6063 | 19777.2719 | 224.568 | 403.1864 | 172.9272 | 0 | 96.9162 | 1719377.2685 | 104935.1981 | 1342145.9591 | 794415.6395 | 0 | 238466.6782 | 0 | 1637742.8899 | 4261071.0523 | 2908268.5495 | 13006423.2351 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 28438981.7358 | 51058966.8656 | 2371.3737 | 2.5817 | 11015.6063 | 19777.2719 | 224.568 | 403.1864
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7831 | 7.8007 | 0.87792 | 4 | 9066.598 | 15507.9778 | 184.8349 | 316.1511 | 174.1943 | 0 | 103.3709 | 2128810.0511 | 131510.77 | 1698395.973 | 1054865.2728 | 0 | 283472.2544 | 0 | 2065851.1853 | 5374921.0199 | 3668494.0397 | 16406320.5663 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 31838879.067 | 54458864.1968 | 3162.2777 | 3.5117 | 9066.598 | 15507.9778 | 184.8349 | 316.1511
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5636 | 10.4475 | 1.1873 | 4 | 7603.9608 | 12366.7916 | 155.017 | 252.1138 | 175.1597 | 0 | 110.7881 | 2628127.1633 | 163948.3462 | 2143935.0302 | 1402939.8635 | 0 | 338168.1279 | 0 | 2604076.2272 | 6775272.1736 | 4624262.4764 | 20680729.4083 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 36113287.9089 | 58733273.0387 | 4216.965 | 4.7493 | 7603.9608 | 12366.7916 | 155.017 | 252.1138
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.2079 | 13.9439 | 1.5956 | 4 | 6494.3413 | 10038.5534 | 132.3959 | 204.6495 | 175.8937 | 0 | 107.0045 | 3233575.9174 | 202992.9597 | 2699445.0482 | 1858971.5318 | 0 | 404661.3318 | 0 | 3275862.2477 | 8523121.5967 | 5817205.6224 | 26015836.2556 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 41448394.7563 | 64068379.8861 | 5623.4133 | 6.3822 | 6494.3413 | 10038.5534 | 132.3959 | 204.6495
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.2079 | 18.517 | 2.1298 | 4 | 5642.6428 | 8297.8593 | 115.0329 | 169.1631 | 176.4452 | 0 | 111.3031 | 3962566.6531 | 249790.0287 | 3385665.7397 | 2455098.141 | 0 | 484451.6308 | 0 | 4109653.1554 | 10692474.5046 | 7297833.5578 | 32637533.4112 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 48070091.9119 | 70690077.0417 | 7498.9421 | 8.5191 | 5642.6428 | 8297.8593 | 115.0329 | 169.1631
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.158 | 24.434 | 2.8198 | 4 | 4984.4299 | 6989.8668 | 101.6143 | 142.4979 | 176.8305 | 0 | 90.6925 | 4831881.8745 | 305199.5537 | 4225302.9468 | 3226816.1927 | 0 | 580037.7805 | 0 | 5136002.9558 | 13362826.1519 | 9120403.4273 | 40788470.8831 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 56221029.3838 | 78841014.5136 | 10000 | 11.2793 | 4984.4299 | 6989.8668 | 101.6143 | 142.4979
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5622 | 31.8859 | 3.6835 | 4 | 4480.4388 | 6015.665 | 91.3398 | 122.6375 | 176.9824 | 0 | 115.4215 | 5841260.3786 | 368616.1233 | 5227467.9241 | 4201032.3403 | 0 | 692903.0689 | 0 | 6369199.1357 | 16571349.6488 | 11310286.6425 | 50582115.2622 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 66014673.7629 | 88634658.8926 | 13335.2143 | 14.734 | 4480.4388 | 6015.665 | 91.3398 | 122.6375
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6502 | 40.8664 | 4.7078 | 4 | 4105.9102 | 5307.1034 | 83.7045 | 108.1925 | 176.7569 | 0 | 116.7182 | 6961851.3045 | 436944.2975 | 6376445.5787 | 5382323.3358 | 0 | 823659.3587 | 0 | 7792677.3113 | 20274947.8661 | 13838068.5271 | 61886917.5797 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 77319476.0804 | 99939461.2102 | 17782.7941 | 18.8313 | 4105.9102 | 5307.1034 | 83.7045 | 108.1925
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.0849 | 51.0441 | 5.8336 | 4 | 3842.3581 | 4811.7394 | 78.3317 | 98.0938 | 176.0234 | 0 | 120.9227 | 8130254.866 | 504501.8464 | 7622209.0911 | 6737561.0051 | 0 | 970828.8093 | 0 | 9346488.691 | 24317646.3455 | 16597293.3085 | 74226783.9629 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 89659342.4636 | 112279327.5934 | 23713.7371 | 23.3345 | 3842.3581 | 4811.7394 | 78.3317 | 98.0938
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.4038 | 57.0524 | 6.5855 | 4 | 3661.8702 | 4520.5789 | 74.6522 | 92.1581 | 175.3644 | 0 | 150.5093 | 8776534.7209 | 539746.1045 | 8335943.6575 | 7547510.7265 | 0 | 961481.7551 | 0 | 10202874.6162 | 26545786.8539 | 18118044.9891 | 81027923.4237 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 96460481.9244 | 119080467.0542 | 31622.7766 | 26.3419 | 3661.8702 | 4520.5789 | 74.6522 | 92.1581
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.705 | 62.1017 | 7.2391 | 4 | 3521.7396 | 4302.9138 | 71.7954 | 87.7207 | 174.744 | 0 | 201.4361 | 9298020.1764 | 567054.7878 | 8925311.8831 | 8226948.9722 | 0 | 924935.086 | 0 | 10897485.6532 | 28353022.2879 | 19351520.3078 | 86544299.1545 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 101976857.6552 | 124596842.785 | 42169.6503 | 28.9564 | 3521.7396 | 4302.9138 | 71.7954 | 87.7207
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1151 | 65.497 | 7.7273 | 4 | 3411.9433 | 4143.7614 | 69.5571 | 84.4762 | 174.3129 | 0 | 233.9743 | 9638603.501 | 584362.3414 | 9316784.678 | 8678018.9742 | 0 | 849342.5884 | 0 | 11336173.7124 | 29494398.6306 | 20130533.1147 | 90028217.5406 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 105460776.0413 | 128080761.1711 | 56234.1325 | 30.9093 | 3411.9433 | 4143.7614 | 69.5571 | 84.4762
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.0166 | 68.2463 | 8.131 | 4 | 3327.3682 | 4022.8582 | 67.8329 | 82.0114 | 173.9393 | 0 | 261.962 | 9908611.9096 | 597753.1772 | 9631180.3629 | 9045579.5749 | 0 | 774426.0946 | 0 | 11683444.9365 | 30397927.1208 | 20747209.8749 | 92786133.0516 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 108218691.5523 | 130838676.6821 | 74989.4209 | 32.5238 | 3327.3682 | 4022.8582 | 67.8329 | 82.0114
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.4682 | 70.3931 | 8.4555 | 4 | 3262.4876 | 3931.2865 | 66.5102 | 80.1446 | 173.6317 | 0 | 269.301 | 10117169.4844 | 608092.517 | 9874949.6175 | 9339876.2457 | 0 | 703401.7436 | 0 | 11950960.9472 | 31093948.9055 | 21222259.0447 | 94910658.5057 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 110343217.0064 | 132963202.1362 | 100000 | 33.8218 | 3262.4876 | 3931.2865 | 66.5102 | 80.1446
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.8749 | 72.1137 | 8.7167 | 4 | 3212.8567 | 3861.6087 | 65.4984 | 78.7241 | 173.3766 | 0 | 281.3701 | 10282135.9784 | 616135.7091 | 10069403.1534 | 9576732.2613 | 0 | 641240.2027 | 0 | 12162402.4489 | 31644076.3202 | 21597732.3093 | 96589858.3833 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 112022416.884 | 134642402.0138 | 133352.1432 | 34.8669 | 3212.8567 | 3861.6087 | 65.4984 | 78.7241
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.1144 | 73.3698 | 8.9143 | 4 | 3175.0233 | 3809.3985 | 64.7271 | 77.6597 | 173.185 | 0 | 300.1717 | 10401343.3392 | 621867.6905 | 10210879.0296 | 9750260.9846 | 0 | 585423.3185 | 0 | 12312212.0013 | 32033850.0456 | 21863760.8859 | 97779597.2952 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 113212155.7959 | 135832140.9257 | 177827.941 | 35.6571 | 3175.0233 | 3809.3985 | 64.7271 | 77.6597
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.5434 | 74.3067 | 9.0647 | 4 | 3146.2615 | 3770.1115 | 64.1408 | 76.8588 | 173.0391 | 0 | 296.8809 | 10489567.5033 | 626063.7139 | 10316132.9806 | 9880034.9167 | 0 | 537956.3936 | 0 | 12421404.6482 | 32317946.9141 | 22057662.8363 | 98646769.9066 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 114079328.4073 | 136699313.5371 | 237137.3706 | 36.2587 | 3146.2615 | 3770.1115 | 64.1408 | 76.8588
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.287 | 75.348 | 9.211 | 4 | 3124.3372 | 3738.2745 | 63.6938 | 76.2098 | 172.8727 | 0 | 291.7183 | 10587509.7226 | 630769.4655 | 10432757.1461 | 10023845.5155 | 0 | 508768.7517 | 0 | 12551623.7345 | 32656750.2652 | 22288903.0851 | 99680927.6862 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 115113486.1869 | 137733471.3167 | 316227.766 | 36.8441 | 3124.3372 | 3738.2745 | 63.6938 | 76.2098
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.6682 | 75.8674 | 9.2974 | 4 | 3107.7232 | 3715.9542 | 63.3551 | 75.7548 | 172.7876 | 0 | 264.1324 | 10636171.9329 | 633100.0377 | 10490827.8362 | 10095627.4829 | 0 | 477119.5646 | 0 | 12609810.2732 | 32808139.7031 | 22392229.4872 | 100143026.3179 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 115575584.8186 | 138195569.9484 | 421696.5034 | 37.1898 | 3107.7232 | 3715.9542 | 63.3551 | 75.7548
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6855 | 76.249 | 9.362 | 4 | 3095.1621 | 3699.1974 | 63.0991 | 75.4131 | 172.7244 | 0 | 315.6262 | 10671805.7307 | 634798.9865 | 10533442.2141 | 10148415.0859 | 0 | 451705.3426 | 0 | 12651665.2703 | 32917037.82 | 22466554.6896 | 100475425.1398 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 115907983.6405 | 138527968.7703 | 562341.3252 | 37.4481 | 3095.1621 | 3699.1974 | 63.0991 | 75.4131
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.3971 | 76.5153 | 9.4089 | 4 | 3085.6791 | 3686.7066 | 62.9057 | 75.1585 | 172.68 | 0 | 311.982 | 10696619.7917 | 635977.8222 | 10563166.5061 | 10185293.0936 | 0 | 431165.1764 | 0 | 12679766.7321 | 32990152.0591 | 22516456.6602 | 100698597.8413 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116131156.342 | 138751141.4718 | 749894.2093 | 37.6355 | 3085.6791 | 3686.7066 | 62.9057 | 75.1585
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.9501 | 76.7218 | 9.4448 | 4 | 3078.5303 | 3677.271 | 62.76 | 74.9661 | 172.6451 | 0 | 316.8345 | 10715824.0392 | 636886.6968 | 10586207.6283 | 10213916.4538 | 0 | 415398.4942 | 0 | 12701610.9917 | 33046986.3418 | 22555247.226 | 100872077.8717 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116304636.3723 | 138924621.5021 | 1000000 | 37.7793 | 3078.5303 | 3677.271 | 62.76 | 74.9661
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.3593 | 76.8745 | 9.4716 | 4 | 3073.1458 | 3670.1904 | 62.6502 | 74.8218 | 172.6193 | 0 | 285.0449 | 10729997.373 | 637556.1792 | 10603227.9375 | 10235078.5568 | 0 | 403172.9195 | 0 | 12717522.8568 | 33088385.7507 | 22583503.1732 | 100998444.7469 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116431003.2476 | 139050988.3774 | 1333521.4322 | 37.8866 | 3073.1458 | 3670.1904 | 62.6502 | 74.8218
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.6493 | 76.9826 | 9.4912 | 4 | 3069.0938 | 3664.9077 | 62.5676 | 74.7141 | 172.6009 | 0 | 301.0844 | 10740024.6606 | 638029.0262 | 10615278.322 | 10250071.2403 | 0 | 393616.8456 | 0 | 12728437.8369 | 33116784.2901 | 22602885.7599 | 101085127.9816 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116517686.4823 | 139137671.6121 | 1778279.41 | 37.9649 | 3069.0938 | 3664.9077 | 62.5676 | 74.7141
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8586 | 77.0605 | 9.5056 | 4 | 3066.0469 | 3660.9579 | 62.5055 | 74.6336 | 172.5876 | 0 | 294.08 | 10747250.1599 | 638369.3407 | 10623966.2482 | 10260885.579 | 0 | 386240.1182 | 0 | 12736117.464 | 33136765.1043 | 22616523.0761 | 101146117.0905 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116578675.5912 | 139198660.721 | 2371373.7057 | 38.0225 | 3066.0469 | 3660.9579 | 62.5055 | 74.6336
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.0218 | 77.1213 | 9.5167 | 4 | 3063.7573 | 3657.9783 | 62.4588 | 74.5728 | 172.5772 | 0 | 310.5624 | 10752879.0907 | 638634.3257 | 10630736.254 | 10269315.1236 | 0 | 380707.1227 | 0 | 12742186.0476 | 33152554.314 | 22627299.5362 | 101194311.8145 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116626870.3152 | 139246855.445 | 3162277.6602 | 38.0666 | 3063.7573 | 3657.9783 | 62.4588 | 74.5728
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.546 | 76.5693 | 9.469 | 4 | 3061.5619 | 3658.7743 | 62.4141 | 74.5891 | 172.6688 | 0 | 511.4107 | 10701562.2137 | 636198.5271 | 10569206.2649 | 10192846.5346 | 0 | 357002.5419 | 0 | 12658158.2721 | 32933931.2786 | 22478084.8223 | 100526990.4552 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 115959548.9559 | 138579534.0857 | 4216965.0343 | 37.8759 | 3061.5619 | 3658.7743 | 62.4141 | 74.5891
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8588 | 77.0603 | 9.519 | 4 | 3060.1907 | 3654.2647 | 62.3861 | 74.4971 | 172.5873 | 0 | 311.9332 | 10747213.5002 | 638365.1637 | 10623942.7437 | 10260866.1479 | 0 | 367358.7079 | 0 | 12728721.0427 | 33117521.1335 | 22603388.6706 | 101087377.1102 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116519935.6109 | 139139920.7407 | 5623413.2519 | 38.076 | 3060.1907 | 3654.2647 | 62.3861 | 74.4971
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.6164 | 77.3429 | 9.5482 | 4 | 3059.2202 | 3651.478 | 62.3663 | 74.4403 | 172.5399 | 0 | 288.0033 | 10773423.623 | 639604.1766 | 10655427.7571 | 10300063.29 | 0 | 372629.3059 | 0 | 12769047.7796 | 33222443.0306 | 22675000.0213 | 101407638.9842 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116840197.4849 | 139460182.6147 | 7498942.0933 | 38.1928 | 3059.2202 | 3651.478 | 62.3663 | 74.4403
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.7406 | 77.3892 | 9.5543 | 4 | 3058.5046 | 3650.3869 | 62.3518 | 74.4181 | 172.5321 | 0 | 294.2629 | 10777707.1007 | 639805.9231 | 10660580.7625 | 10306485.1144 | 0 | 371672.8815 | 0 | 12774938.195 | 33237768.6834 | 22685460.0942 | 101454418.7548 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116886977.2555 | 139506962.3853 | 10000000 | 38.217 | 3058.5046 | 3650.3869 | 62.3518 | 74.4181
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.72086 | 0.13503 | 0.0035466 | 4 | 1178390.9076 | 2817482.952 | 24023.0925 | 57438.2009 | 109.5136 | 0 | 46.219 | 93180.8807 | 3451.2336 | 69164.713 | 49611.4647 | 0 | 53393.1196 | 0 | 104832.5505 | 272752.7923 | 186159.3853 | 832546.1397 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 16717352.9669 | 39970485.7538 | 100 | 0.014187 | 1178390.9076 | 2817482.952 | 24023.0925 | 57438.2009
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.20644 | 0.0095757 | 4 | 443319.7931 | 1050404.6526 | 9037.6736 | 21413.9196 | 120.9706 | 0 | 62.819 | 133302.7436 | 5362.4112 | 96341.8286 | 59692.5392 | 0 | 59047.1083 | 0 | 137961.1861 | 358946.7064 | 244988.5027 | 1095643.0262 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 16980449.8534 | 40233582.6403 | 133.3521 | 0.038303 | 443319.7931 | 1050404.6526 | 9037.6736 | 21413.9196
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2008 | 0.31414 | 0.019587 | 4 | 221372.8051 | 518160.6571 | 4512.9841 | 10563.4059 | 131.9847 | 0 | 56.8112 | 188355.7456 | 8207.6718 | 133781.7323 | 74322.6333 | 0 | 66590.5878 | 0 | 183790.7647 | 478185.869 | 326371.6813 | 1459606.6858 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17344413.513 | 40597546.3 | 177.8279 | 0.078349 | 221372.8051 | 518160.6571 | 4512.9841 | 10563.4059
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5686 | 0.46711 | 0.035012 | 4 | 127229.1945 | 293266.5285 | 2593.7392 | 5978.6349 | 141.6987 | 0 | 68.4505 | 259269.3445 | 12144.8188 | 182554.8595 | 94696.0661 | 0 | 75545.5129 | 0 | 243442.1347 | 633386.4977 | 432299.2994 | 1933338.5336 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17818145.3608 | 41071278.1478 | 237.1374 | 0.14005 | 127229.1945 | 293266.5285 | 2593.7392 | 5978.6349
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.66423 | 0.056366 | 4 | 81509.6906 | 184643.787 | 1661.6853 | 3764.2133 | 149.5011 | 0 | 338.3795 | 342355.6491 | 17024.6508 | 240703.1029 | 120459.4892 | 0 | 84292.2449 | 0 | 313885.7034 | 816666.2134 | 557391.4715 | 2492778.5252 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 18377585.3524 | 41630718.1394 | 316.2278 | 0.22547 | 81509.6906 | 184643.787 | 1661.6853 | 3764.2133
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.94481 | 0.087645 | 4 | 54540.525 | 120868.2741 | 1111.8824 | 2464.0633 | 156.351 | 0 | 440.1387 | 450165.8768 | 23660.3289 | 317631.2629 | 157203.7892 | 0 | 96125.5674 | 0 | 407466.8619 | 1060145.1916 | 723570.8771 | 3235969.7558 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 19120776.583 | 42373909.3699 | 421.6965 | 0.35058 | 54540.525 | 120868.2741 | 1111.8824 | 2464.0633
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4601 | 1.3211 | 0.13076 | 4 | 38326.2815 | 82783.1583 | 781.3331 | 1687.6467 | 161.9134 | 0 | 594.0977 | 581708.2685 | 32047.09 | 413792.499 | 206080.6114 | 0 | 110053.2945 | 0 | 524035.8877 | 1363433.8854 | 930571.6425 | 4161723.1791 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 20046530.0063 | 43299662.7932 | 562.3413 | 0.52305 | 38326.2815 | 82783.1583 | 781.3331 | 1687.6467
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5259 | 1.8169 | 0.18863 | 4 | 28070.6729 | 58888.9191 | 572.2586 | 1200.5303 | 166.3411 | 0 | 77.2144 | 739591.0247 | 42344.9262 | 532405.0731 | 269105.4749 | 0 | 126201.5767 | 0 | 666762.7495 | 1734779.9025 | 1184022.9296 | 5295213.6573 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 21180020.4846 | 44433153.2715 | 749.8942 | 0.75452 | 28070.6729 | 58888.9191 | 572.2586 | 1200.5303
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9459 | 2.4842 | 0.2678 | 4 | 21115.6837 | 42823.1896 | 430.4718 | 873.0086 | 169.8708 | 0 | 85.8448 | 934595.0636 | 55406.1524 | 682067.2803 | 356085.2948 | 0 | 146148.1666 | 0 | 847977.7635 | 2206264.1965 | 1505820.6483 | 6734364.5659 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 22619171.3932 | 45872304.1801 | 1000 | 1.0712 | 21115.6837 | 42823.1896 | 430.4718 | 873.0086
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8562 | 3.3822 | 0.37438 | 4 | 16318.8588 | 31846.6084 | 332.682 | 649.2362 | 172.5216 | 0 | 91.1051 | 1173692.8761 | 71506.9039 | 871355.2498 | 473468.4199 | 0 | 171464.5659 | 0 | 1076980.3261 | 2802081.8895 | 1912478.4666 | 8553028.6977 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 24437835.525 | 47690968.3119 | 1333.5214 | 1.4975 | 16318.8588 | 31846.6084 | 332.682 | 649.2362
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3842 | 4.5914 | 0.5202 | 4 | 12849.9699 | 24024.9653 | 261.964 | 489.7814 | 174.9022 | 0 | 100.2689 | 1469723.6578 | 91824.4963 | 1110814.2823 | 630485.8748 | 0 | 201431.4223 | 0 | 1366669.096 | 3555792.6455 | 2426901.5448 | 10853643.0198 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 26738449.847 | 49991582.6339 | 1778.2794 | 2.0808 | 12849.9699 | 24024.9653 | 261.964 | 489.7814
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7365 | 6.1814 | 0.71181 | 4 | 10389.1636 | 18556.0988 | 211.7972 | 378.2912 | 176.5835 | 0 | 75.1562 | 1825261.2624 | 116147.7842 | 1407383.6246 | 835139.9277 | 0 | 237894.1541 | 0 | 1724512.4337 | 4486827.6062 | 3062352.0364 | 13695518.8292 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 29580325.6565 | 52833458.4434 | 2371.3737 | 2.8472 | 10389.1636 | 18556.0988 | 211.7972 | 378.2912
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1922 | 8.3089 | 0.96753 | 4 | 8568.8506 | 14577.2428 | 174.6876 | 297.1768 | 177.8744 | 0 | 79.6452 | 2259921.2826 | 145579.6019 | 1781568.2864 | 1108620.4628 | 0 | 282664.9957 | 0 | 2175558.3055 | 5660356.4425 | 3863309.5807 | 17277578.9581 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 33162385.7853 | 56415518.5722 | 3162.2777 | 3.8701 | 8568.8506 | 14577.2428 | 174.6876 | 297.1768
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0849 | 11.2203 | 1.308 | 4 | 7213.3023 | 11657.7292 | 147.0529 | 237.6586 | 178.8576 | 0 | 86.9381 | 2792505.8958 | 179161.7094 | 2265817.9522 | 1480085.0932 | 0 | 338685.2541 | 0 | 2751939.8028 | 7159982.8664 | 4886835.4293 | 21855014.0031 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 37739820.8303 | 60992953.6172 | 4216.965 | 5.232 | 7213.3023 | 11657.7292 | 147.0529 | 237.6586
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.8922 | 15.0398 | 1.7564 | 4 | 6180.1356 | 9489.9105 | 125.9904 | 193.4647 | 179.6072 | 0 | 95.639 | 3436699.6883 | 220127.6779 | 2864170.3611 | 1962457.0198 | 0 | 406457.6855 | 0 | 3467065.8487 | 9020594.1453 | 6156740.8588 | 27534313.2854 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 43419120.1126 | 66672252.8995 | 5623.4133 | 7.0256 | 6180.1356 | 9489.9105 | 125.9904 | 193.4647
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.0969 | 20.0231 | 2.3418 | 4 | 5385.1962 | 7867.5549 | 109.7845 | 160.3907 | 180.1695 | 0 | 99.578 | 4210597.0219 | 269227.5564 | 3600895.1629 | 2590149.3983 | 0 | 487478.8295 | 0 | 4351755.7079 | 11322375.6841 | 7727754.056 | 34560233.417 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 50445040.2442 | 73698173.0311 | 7498.9421 | 9.3674 | 5385.1962 | 7867.5549 | 109.7845 | 160.3907
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.281 | 26.4525 | 3.0956 | 4 | 4769.8734 | 6647.7685 | 97.2403 | 135.5238 | 180.5559 | 0 | 126.9964 | 5130588.5937 | 327170.5145 | 4499441.876 | 3399607.9758 | 0 | 584056.7088 | 0 | 5436937.6108 | 14145796.3941 | 9654796.706 | 43178396.3798 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 59063203.207 | 82316335.9939 | 10000 | 12.3826 | 4769.8734 | 6647.7685 | 97.2403 | 135.5238
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9506 | 34.4999 | 4.0371 | 4 | 4296.5518 | 5736.522 | 87.591 | 116.9468 | 180.6884 | 0 | 121.7118 | 6196258.0724 | 394021.2366 | 5564667.0733 | 4420109.5135 | 0 | 697467.0938 | 0 | 6736283.9659 | 17526429.0775 | 11962147.9775 | 53497384.0106 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 69382190.8378 | 92635323.6247 | 13335.2143 | 16.1483 | 4296.5518 | 5736.522 | 87.591 | 116.9468
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.2795 | 44.0589 | 5.1501 | 4 | 3942.0785 | 5070.8482 | 80.3646 | 103.3761 | 180.413 | 0 | 132.4642 | 7373736.0608 | 467595.7811 | 6767241.9718 | 5655179.0587 | 0 | 827084.5586 | 0 | 8225426.5981 | 21400872.7414 | 14606535.39 | 65323672.1606 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 81208478.9878 | 104461611.7748 | 17782.7941 | 20.6004 | 3942.0785 | 5070.8482 | 80.3646 | 103.3761
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.8754 | 54.6423 | 6.3685 | 4 | 3689.1006 | 4601.9232 | 75.2073 | 93.8164 | 179.6042 | 0 | 122.1509 | 8593082.813 | 543089.7396 | 8039479.9437 | 7066753.7594 | 0 | 970545.2752 | 0 | 9833051.0971 | 25583581.9184 | 17461320.3494 | 78090904.8957 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 93975711.7229 | 117228844.5098 | 23713.7371 | 25.4739 | 3689.1006 | 4601.9232 | 75.2073 | 93.8164
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.583 | 64.4446 | 7.5102 | 4 | 3513.6509 | 4287.7032 | 71.6305 | 87.4106 | 178.433 | 0 | 148.3809 | 9668803.2351 | 610419.434 | 9173333.5445 | 8408792.6825 | 0 | 1089460.5954 | 0 | 11290815.7017 | 29376386.3911 | 20049987.3363 | 89667998.9207 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 105552805.7479 | 128805938.5348 | 31622.7766 | 30.0408 | 3513.6509 | 4287.7032 | 71.6305 | 87.4106
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8159 | 67.6161 | 8.0476 | 4 | 3380.7042 | 4103.0637 | 68.9202 | 83.6465 | 178.0009 | 0 | 208.2906 | 10011521.5317 | 632710.7212 | 9531772.7459 | 8845605.3285 | 0 | 986214.1664 | 0 | 11703051.5526 | 30448939.5138 | 20782026.8813 | 92941842.4414 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 108826649.2686 | 132079782.0555 | 42169.6503 | 32.1905 | 3380.7042 | 4103.0637 | 68.9202 | 83.6465
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.0936 | 69.7803 | 8.4455 | 4 | 3280.6167 | 3968.9431 | 66.8798 | 80.9123 | 177.7068 | 0 | 224.1508 | 10228300.7901 | 644213.26 | 9776861.5788 | 9138254.17 | 0 | 865791.966 | 0 | 11954834.4883 | 31104027.0649 | 21229137.5956 | 94941420.9137 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 110826227.741 | 134079360.5279 | 56234.1325 | 33.7821 | 3280.6167 | 3968.9431 | 66.8798 | 80.9123
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5218 | 72.3881 | 8.8497 | 4 | 3204.0266 | 3860.9183 | 65.3184 | 78.71 | 177.3371 | 0 | 270.2343 | 10485551.3385 | 657609.2158 | 10070426.8883 | 9492807.4778 | 0 | 783977.0644 | 0 | 12281245.074 | 31953280.4529 | 21808770.4834 | 97533667.995 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 113418474.8223 | 136671607.6092 | 74989.4209 | 35.3987 | 3204.0266 | 3860.9183 | 65.3184 | 78.71
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.7714 | 74.4915 | 9.1783 | 4 | 3145.3504 | 3778.7229 | 64.1222 | 77.0344 | 177.0229 | 0 | 246.0424 | 10689836.4337 | 668021.9336 | 10305893.3667 | 9780607.7507 | 0 | 710286.4402 | 0 | 12540311.9107 | 32627319.2199 | 22268815.792 | 99591092.8474 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 115475899.6746 | 138729032.4615 | 100000 | 36.7132 | 3145.3504 | 3778.7229 | 64.1222 | 77.0344
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.1157 | 75.8363 | 9.4091 | 4 | 3100.6729 | 3718.5099 | 63.2114 | 75.8069 | 176.8166 | 0 | 290.6526 | 10817811.1584 | 674222.1949 | 10456057.3991 | 9965032.4635 | 0 | 636104.5403 | 0 | 12694198.8249 | 33027701.4043 | 22542084.8598 | 100813212.8453 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 116698019.6725 | 139951152.4594 | 133352.1432 | 37.6364 | 3100.6729 | 3718.5099 | 63.2114 | 75.8069
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.1561 | 77.0544 | 9.6058 | 4 | 3066.6437 | 3671.826 | 62.5177 | 74.8551 | 176.626 | 0 | 279.3181 | 10932576.8474 | 679682.7133 | 10591703.2005 | 10132583.7303 | 0 | 578400.124 | 0 | 12836829.18 | 33398796.3307 | 22795364.7723 | 101945936.8985 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 117830743.7257 | 141083876.5126 | 177827.941 | 38.4234 | 3066.6437 | 3671.826 | 62.5177 | 74.8551
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4996 | 77.9891 | 9.758 | 4 | 3040.7535 | 3636.5005 | 61.9899 | 74.135 | 176.4773 | 0 | 281.8619 | 11019995.5618 | 683792.6308 | 10695558.0882 | 10261544.6954 | 0 | 530308.8712 | 0 | 12944567.9405 | 33679110.4853 | 22986684.9427 | 102801563.216 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 118686370.0432 | 141939502.8302 | 237137.3706 | 39.0319 | 3040.7535 | 3636.5005 | 61.9899 | 74.135
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1728 | 78.654 | 9.8701 | 4 | 3021.1035 | 3610.084 | 61.5893 | 73.5964 | 176.3697 | 0 | 333.858 | 11081813.8948 | 686669.2958 | 10769307.9654 | 10353497.6065 | 0 | 489669.4047 | 0 | 13018573.6852 | 33871658.2523 | 23118102.7502 | 103389292.8549 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 119274099.6821 | 142527232.469 | 316227.766 | 39.4803 | 3021.1035 | 3610.084 | 61.5893 | 73.5964
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4102 | 79.1444 | 9.9542 | 4 | 3006.2163 | 3590.2205 | 61.2858 | 73.1915 | 176.2895 | 0 | 311.0948 | 11127220.2261 | 688766.4556 | 10823643.4442 | 10421445.1711 | 0 | 456644.8366 | 0 | 13071910.8521 | 34010430.6194 | 23212817.7422 | 103812879.3472 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 119697686.1744 | 142950818.9613 | 421696.5034 | 39.8167 | 3006.2163 | 3590.2205 | 61.2858 | 73.1915
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.3265 | 79.5068 | 10.0172 | 4 | 2994.9558 | 3575.286 | 61.0562 | 72.887 | 176.2298 | 0 | 290.5488 | 11160669.5626 | 690302.6435 | 10863761.9472 | 10471724.7467 | 0 | 430244.7918 | 0 | 13110514.4398 | 34110869.236 | 23281369.1618 | 104119456.5293 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120004263.3566 | 143257396.1435 | 562341.3252 | 40.0688 | 2994.9558 | 3575.286 | 61.0562 | 72.887
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.9696 | 79.7607 | 10.063 | 4 | 2986.4507 | 3564.1402 | 60.8828 | 72.6598 | 176.1876 | 0 | 315.6523 | 11184051.9809 | 691371.5488 | 10891856.7374 | 10506993.5971 | 0 | 409011.6337 | 0 | 13136481.3442 | 34178429.7947 | 23327480.6314 | 104325677.2683 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120210484.0955 | 143463616.8824 | 749894.2093 | 40.252 | 2986.4507 | 3564.1402 | 60.8828 | 72.6598
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4519 | 79.9509 | 10.0975 | 4 | 2980.0351 | 3555.7528 | 60.752 | 72.4888 | 176.1559 | 0 | 274.3775 | 11201543.1306 | 692168.7649 | 10912898.0323 | 10533438.2669 | 0 | 392504.4723 | 0 | 13155695.5401 | 34228421.1912 | 23361600.7867 | 104478270.1851 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120363077.0124 | 143616209.7993 | 1000000 | 40.3898 | 2980.0351 | 3555.7528 | 60.752 | 72.4888
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8003 | 80.0883 | 10.1229 | 4 | 2975.2012 | 3549.4741 | 60.6535 | 72.3608 | 176.1329 | 0 | 283.9212 | 11214150.0226 | 692741.9028 | 10928078.5485 | 10552534.1233 | 0 | 379620.4379 | 0 | 13169178.7637 | 34263501.7731 | 23385544.0047 | 104585349.5766 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120470156.4038 | 143723289.1907 | 1333521.4322 | 40.4914 | 2975.2012 | 3549.4741 | 60.6535 | 72.3608
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.0413 | 80.1831 | 10.1412 | 4 | 2971.5624 | 3544.7986 | 60.5793 | 72.2655 | 176.1169 | 0 | 310.7186 | 11222853.5091 | 693136.6544 | 10938567.6441 | 10565737.7288 | 0 | 369515.9383 | 0 | 13178026.4752 | 34286521.7034 | 23401255.5802 | 104655615.2335 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120540422.0607 | 143793554.8476 | 1778279.41 | 40.5647 | 2971.5624 | 3544.7986 | 60.5793 | 72.2655
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.2265 | 80.2561 | 10.1551 | 4 | 2968.8255 | 3541.2758 | 60.5235 | 72.1937 | 176.1046 | 0 | 303.1552 | 11229537.7491 | 693439.546 | 10946626.3683 | 10575886.1659 | 0 | 361862.1551 | 0 | 13184867.2739 | 34304320.0585 | 23413403.3232 | 104709942.6398 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120594749.467 | 143847882.2539 | 2371373.7057 | 40.6204 | 2968.8255 | 3541.2758 | 60.5235 | 72.1937
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.987 | 79.7661 | 10.1134 | 4 | 2966.3228 | 3541.1341 | 60.4725 | 72.1908 | 176.1846 | 0 | 460.9235 | 11184443.6618 | 691370.4468 | 10892467.4336 | 10507834.1004 | 0 | 338615.1976 | 0 | 13109745.0276 | 34108867.3835 | 23280002.8563 | 104113346.1075 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 119998152.9347 | 143251285.7217 | 3162277.6602 | 40.4535 | 2966.3228 | 3541.1341 | 60.4725 | 72.1908
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.5238 | 80.3732 | 10.1767 | 4 | 2964.7191 | 3535.9509 | 60.4398 | 72.0851 | 176.0851 | 0 | 292.1634 | 11240285.5913 | 693928.4681 | 10959572.3144 | 10592187.3438 | 0 | 350455.268 | 0 | 13196207.3044 | 34333824.4917 | 23433540.7051 | 104800001.4868 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120684808.314 | 143937941.1009 | 4216965.0343 | 40.707 | 2964.7191 | 3535.9509 | 60.4398 | 72.0851
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9038 | 80.5231 | 10.1942 | 4 | 2963.5756 | 3533.8275 | 60.4165 | 72.0419 | 176.0603 | 0 | 307.0698 | 11254023.9814 | 694553.8672 | 10976120.7657 | 10613032.9924 | 0 | 350608.4659 | 0 | 13216452.6283 | 34386498.6716 | 23469491.9153 | 104960783.2878 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120845590.115 | 144098722.902 | 5623413.2519 | 40.777 | 2963.5756 | 3533.8275 | 60.4165 | 72.0419
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9575 | 80.5442 | 10.1984 | 4 | 2962.7192 | 3532.7365 | 60.399 | 72.0196 | 176.0567 | 0 | 296.0729 | 11255953.5191 | 694640.8012 | 10978451.9804 | 10615974.0198 | 0 | 348096.4347 | 0 | 13218315.5345 | 34391345.5714 | 23472800.024 | 104975577.8851 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120860384.7123 | 144113517.4992 | 7498942.0933 | 40.7937 | 2962.7192 | 3532.7365 | 60.399 | 72.0196
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.9964 | 80.5595 | 10.2015 | 4 | 2962.0765 | 3531.9209 | 60.3859 | 72.003 | 176.0541 | 0 | 301.9588 | 11257350.1368 | 694703.683 | 10980139.696 | 10618103.5234 | 0 | 346189.1224 | 0 | 13219629.603 | 34394764.5082 | 23475133.5186 | 104986013.7915 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 120870820.6187 | 144123953.4056 | 10000000 | 40.8061 | 2962.0765 | 3531.9209 | 60.3859 | 72.003
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.74031 | 0.1441 | 0.0044334 | 4 | 970469.017 | 2317883.6179 | 19784.3236 | 47253.1927 | 111.8972 | 0 | 50.3909 | 98860.0623 | 3724.2946 | 72730.4476 | 50787.5078 | 0 | 53814.9251 | 0 | 109167.7226 | 284032.0208 | 193857.6904 | 866974.6712 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17209889.9158 | 41104374.487 | 100 | 0.017734 | 970469.017 | 2317883.6179 | 19784.3236 | 47253.1927
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.22394 | 0.011352 | 4 | 385410.9601 | 911628.2069 | 7857.1237 | 18584.7741 | 124.0446 | 0 | 50.5908 | 143297.0261 | 5892.3248 | 102601.1437 | 61859.3496 | 0 | 60176.2763 | 0 | 145792.187 | 379321.3646 | 258894.6256 | 1157834.2979 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17500749.5425 | 41395234.1137 | 133.3521 | 0.045408 | 385410.9601 | 911628.2069 | 7857.1237 | 18584.7741
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.235 | 0.33621 | 0.022307 | 4 | 200311.411 | 468105.2071 | 4083.6191 | 9542.9578 | 134.9026 | 0 | 44.4709 | 200160.0465 | 8909.407 | 140969.5452 | 76924.1832 | 0 | 67121.8278 | 0 | 192693.1538 | 501348.0593 | 342180.3522 | 1530306.575 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17873221.8196 | 41767706.3908 | 177.8279 | 0.089227 | 200311.411 | 468105.2071 | 4083.6191 | 9542.9578
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.49963 | 0.039373 | 4 | 116658.1039 | 268378.7082 | 2378.2332 | 5471.263 | 144.7821 | 0 | 264.0662 | 275345.1461 | 13200.7952 | 192258.7941 | 98428.0227 | 0 | 76049.2722 | 0 | 255559.9918 | 664914.6761 | 453817.9291 | 2029574.6274 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 18372489.872 | 42266974.4432 | 237.1374 | 0.15749 | 116658.1039 | 268378.7082 | 2378.2332 | 5471.263
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.71158 | 0.063075 | 4 | 75177.6723 | 169884.2581 | 1532.5985 | 3463.3204 | 152.7516 | 0 | 344.1197 | 364095.1405 | 18581.1493 | 253780.2757 | 125990.8052 | 0 | 84890.9832 | 0 | 330461.958 | 859794.2276 | 586827.2273 | 2624421.7667 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 18967337.0113 | 42861821.5826 | 316.2278 | 0.2523 | 75177.6723 | 169884.2581 | 1532.5985 | 3463.3204
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7211 | 1.0124 | 0.097634 | 4 | 50580.2992 | 111764.1769 | 1031.1478 | 2278.4639 | 159.7305 | 0 | 464.6916 | 478816.9992 | 25879.0405 | 334947.897 | 164661.5918 | 0 | 96829.3677 | 0 | 429442.6095 | 1117321.579 | 762594.9364 | 3410494.0209 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19753409.2655 | 43647893.8368 | 421.6965 | 0.39054 | 50580.2992 | 111764.1769 | 1031.1478 | 2278.4639
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5379 | 1.4021 | 0.1438 | 4 | 35978.4593 | 77518.217 | 733.4696 | 1580.3137 | 165.254 | 0 | 618.928 | 614144.9317 | 34802.2053 | 433056.6719 | 213580.6157 | 0 | 109725.4988 | 0 | 548070.8701 | 1425967.9792 | 973252.4465 | 4352601.2191 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 20695516.4637 | 44590001.035 | 562.3413 | 0.57522 | 35978.4593 | 77518.217 | 733.4696 | 1580.3137
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6379 | 1.9364 | 0.20846 | 4 | 26281.75 | 54937.7413 | 535.789 | 1119.9802 | 169.8083 | 0 | 80.2594 | 784544.552 | 46492.8721 | 558841.3691 | 282874.2088 | 0 | 126206.6145 | 0 | 701594.2505 | 1825404.3229 | 1245875.9587 | 5571834.1487 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 21914749.3933 | 45809233.9646 | 749.8942 | 0.83384 | 26281.75 | 54937.7413 | 535.789 | 1119.9802
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0922 | 2.6492 | 0.29566 | 4 | 19817.3077 | 40021.7319 | 404.0026 | 815.8971 | 173.398 | 0 | 74.969 | 991960.2581 | 61007.3589 | 716267.8566 | 374979.7882 | 0 | 146120.6915 | 0 | 893231.0218 | 2324003.8919 | 1586180.4097 | 7093751.2767 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 23436666.5213 | 47331151.0926 | 1000 | 1.1826 | 19817.3077 | 40021.7319 | 404.0026 | 815.8971
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0265 | 3.5921 | 0.41146 | 4 | 15388.0578 | 29906.2212 | 313.7064 | 609.6788 | 176.0462 | 0 | 81.7942 | 1242555.291 | 78741.1535 | 911992.5815 | 496468.62 | 0 | 170641.2567 | 0 | 1131155.5721 | 2943034.7666 | 2008681.7015 | 8983270.9429 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 25326186.1875 | 49220670.7587 | 1333.5214 | 1.6458 | 15388.0578 | 29906.2212 | 313.7064 | 609.6788
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6205 | 4.9122 | 0.57244 | 4 | 12134.62 | 22569.9665 | 247.3806 | 460.1193 | 178.5169 | 0 | 105.2734 | 1559505.5261 | 100670.4969 | 1170057.938 | 662854.9542 | 0 | 201314.8542 | 0 | 1440817.4701 | 3748711.5049 | 2558572.6304 | 11442505.3748 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 27785420.6194 | 51679905.1906 | 1778.2794 | 2.2898 | 12134.62 | 22569.9665 | 247.3806 | 460.1193
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0608 | 6.6949 | 0.78305 | 4 | 9850.556 | 17479.2245 | 200.8169 | 356.3376 | 180.2368 | 0 | 73.7947 | 1939950.3529 | 125046.059 | 1498933.8828 | 881425.1484 | 0 | 239748.9913 | 0 | 1827190.7294 | 4753975.4697 | 3244685.9425 | 14510956.576 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 30853871.8206 | 54748356.3919 | 2371.3737 | 3.1322 | 9850.556 | 17479.2245 | 200.8169 | 356.3376
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.6138 | 9.0439 | 1.0606 | 4 | 8167.6132 | 13799.6906 | 166.5078 | 281.3254 | 181.551 | 0 | 79.7536 | 2398830.5137 | 154345.6684 | 1906634.9399 | 1165607.1215 | 0 | 285869.7348 | 0 | 2305402.3115 | 5998183.9116 | 4093883.77 | 18308757.9714 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 34651673.216 | 58546157.7873 | 3162.2777 | 4.2426 | 8167.6132 | 13799.6906 | 166.5078 | 281.3254
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6379 | 12.1525 | 1.4281 | 4 | 6897.3578 | 11080.3917 | 140.612 | 225.8888 | 182.5529 | 0 | 90.5263 | 2956111.9195 | 189807.4562 | 2415002.7573 | 1541518.1286 | 0 | 341713.945 | 0 | 2903220.1406 | 7553583.2735 | 5155475.7948 | 23056433.4157 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 39399348.6603 | 63293833.2316 | 4216.965 | 5.7122 | 6897.3578 | 11080.3917 | 140.612 | 225.8888
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.589 | 16.2562 | 1.913 | 4 | 5924.4194 | 9047.1363 | 120.7773 | 184.4381 | 183.3149 | 0 | 103.1013 | 3632304.5105 | 232680.6598 | 3047894.5482 | 2037506.8021 | 0 | 409424.1029 | 0 | 3650326.1432 | 9497399.8398 | 6482170.5427 | 28989707.1493 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 45332622.3939 | 69227106.9652 | 5623.4133 | 7.6518 | 5924.4194 | 9047.1363 | 120.7773 | 184.4381
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.9984 | 21.6277 | 2.5474 | 4 | 5171.9403 | 7516.8818 | 105.437 | 153.2418 | 183.8871 | 0 | 106.0887 | 4447245.3322 | 284154.4049 | 3829950.854 | 2686530.4518 | 0 | 490945.0972 | 0 | 4578142.1946 | 11911386.8843 | 8129766.3031 | 36358121.5221 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 52701036.7667 | 76595521.338 | 7498.9421 | 10.1898 | 5171.9403 | 7516.8818 | 105.437 | 153.2418
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4406 | 28.5477 | 3.3642 | 4 | 4587.6601 | 6363.3021 | 93.5257 | 129.7245 | 184.2735 | 0 | 100.4112 | 5415998.3929 | 345101.1451 | 4782348.3774 | 3524130.8995 | 0 | 588106.336 | 0 | 5715717.2089 | 14871123.7226 | 10149847.5117 | 45392373.5942 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 61735288.8388 | 85629773.41 | 10000 | 13.4568 | 4587.6601 | 6363.3021 | 93.5257 | 129.7245
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.3662 | 37.1673 | 4.3798 | 4 | 4138.443 | 5502.3593 | 84.3678 | 112.173 | 184.3836 | 0 | 124.9062 | 6533236.2277 | 415106.6178 | 5906272.8123 | 4575689.827 | 0 | 701428.4244 | 0 | 7071376.2246 | 18398270.3977 | 12557197.5931 | 56158578.1246 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 72501493.3692 | 96395977.9405 | 13335.2143 | 17.519 | 4138.443 | 5502.3593 | 84.3678 | 112.173
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.9385 | 47.3639 | 5.5757 | 4 | 3801.989 | 4873.3584 | 77.5087 | 99.35 | 184.0536 | 0 | 120.3111 | 7763367.0714 | 491881.3571 | 7170391.7035 | 5844539.4419 | 0 | 830658.0306 | 0 | 8619326.6658 | 22425719.9173 | 15306014.646 | 68451898.8336 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 84794814.0782 | 108689298.6495 | 17782.7941 | 22.3028 | 3801.989 | 4873.3584 | 77.5087 | 99.35
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7099 | 58.582 | 6.8802 | 4 | 3561.3817 | 4429.6197 | 72.6036 | 90.3038 | 183.1578 | 0 | 144.0582 | 9032508.7273 | 570797.533 | 8499556.8044 | 7292146.8825 | 0 | 973081.4797 | 0 | 10283555.6565 | 26755702.3708 | 18261316.6428 | 81668666.097 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 98011581.3416 | 121906065.9128 | 23713.7371 | 27.5207 | 3561.3817 | 4429.6197 | 72.6036 | 90.3038
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8398 | 68.8164 | 8.0842 | 4 | 3397.6686 | 4136.5961 | 69.2661 | 84.3301 | 181.9234 | 0 | 117.6033 | 10131157.7586 | 638897.8182 | 9668038.2077 | 8675282.845 | 0 | 1083221.2151 | 0 | 11776673.1594 | 30640487.833 | 20912762.5451 | 93526521.3821 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 109869436.6266 | 133763921.1979 | 31622.7766 | 32.3367 | 3397.6686 | 4136.5961 | 69.2661 | 84.3301
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0413 | 73.1661 | 8.7401 | 4 | 3274.7613 | 3958.2313 | 66.7604 | 80.6939 | 181.3533 | 0 | 195.8519 | 10583848.0327 | 666904.6381 | 10153889.9621 | 9279214.9357 | 0 | 1003736.9395 | 0 | 12358161.8582 | 32153402.1474 | 21945357.6519 | 98144516.1655 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 114487431.4101 | 138381915.9814 | 42169.6503 | 34.9605 | 3274.7613 | 3958.2313 | 66.7604 | 80.6939
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.4908 | 76.6699 | 9.2881 | 4 | 3180.0412 | 3823.1917 | 64.8294 | 77.9409 | 180.853 | 0 | 225.5515 | 10943002.679 | 689103.5697 | 10541071.3235 | 9775946.6001 | 0 | 919593.5636 | 0 | 12818799.917 | 33351887.8866 | 22763348.7954 | 101802754.3348 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 118145669.5794 | 142040154.1506 | 56234.1325 | 37.1522 | 3180.0412 | 3823.1917 | 64.8294 | 77.9409
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0944 | 79.3414 | 9.7247 | 4 | 3107.383 | 3721.6584 | 63.3482 | 75.871 | 180.4451 | 0 | 269.8136 | 11213722.4552 | 705824.4543 | 10833889.7228 | 10160976.8985 | 0 | 834871.9527 | 0 | 13162221.3385 | 34245399.9801 | 23373189.159 | 104530095.9611 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 120873011.2057 | 144767495.7769 | 74989.4209 | 38.8987 | 3107.383 | 3721.6584 | 63.3482 | 75.871
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.3413 | 81.4222 | 10.073 | 4 | 3051.8938 | 3644.9239 | 62.217 | 74.3067 | 180.1103 | 0 | 286.7768 | 11422816.1171 | 718732.1195 | 11060610.5065 | 10465688.9058 | 0 | 757679.7881 | 0 | 13425955.7004 | 34931582.6903 | 23841522.9584 | 106624588.786 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 122967504.0306 | 146861988.6018 | 100000 | 40.2922 | 3051.8938 | 3644.9239 | 62.217 | 74.3067
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8567 | 82.8004 | 10.3229 | 4 | 3009.6744 | 3588.3499 | 61.3563 | 73.1534 | 179.8805 | 0 | 293.0776 | 11559538.9823 | 727001.1007 | 11210286.0561 | 10667689.1638 | 0 | 683007.5754 | 0 | 13590533.9225 | 35359781.4646 | 24133777.4204 | 107931615.6859 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 124274530.9305 | 148169015.5017 | 133352.1432 | 41.2917 | 3009.6744 | 3588.3499 | 61.3563 | 73.1534
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 177.8964 | 83.9841 | 10.529 | 4 | 2977.6145 | 3544.9619 | 60.7027 | 72.2688 | 179.6792 | 0 | 342.7071 | 11675658.9519 | 733877.523 | 11338577.225 | 10840701.6211 | 0 | 623911.1316 | 0 | 13732963.3165 | 35730353.5314 | 24386700.4705 | 109062743.7709 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 125405659.0155 | 149300143.5867 | 177827.941 | 42.1161 | 2977.6145 | 3544.9619 | 60.7027 | 72.2688
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.8855 | 85.144 | 10.7142 | 4 | 2953.2075 | 3510.7507 | 60.2051 | 71.5714 | 179.4844 | 0 | 319.4855 | 11788984.8851 | 740583.9349 | 11463948.3874 | 11010783.5444 | 0 | 582686.1325 | 0 | 13878924.8849 | 36110115.5916 | 24645895.8799 | 110221923.2408 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 126564838.4854 | 150459323.0567 | 237137.3706 | 42.8567 | 2953.2075 | 3510.7507 | 60.2051 | 71.5714
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.0018 | 85.5741 | 10.8098 | 4 | 2934.7317 | 3487.3416 | 59.8285 | 71.0942 | 179.4108 | 0 | 305.7868 | 11830874.5163 | 743058.9055 | 11510351.7824 | 11074195.3736 | 0 | 535372.2299 | 0 | 13920602.595 | 36218552.4439 | 24719906.2598 | 110552914.1064 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 126895829.351 | 150790313.9223 | 316227.766 | 43.2393 | 2934.7317 | 3487.3416 | 59.8285 | 71.0942
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.746 | 85.473 | 10.8383 | 4 | 2920.8598 | 3472.0193 | 59.5457 | 70.7818 | 179.4256 | 0 | 550.9676 | 11821012.107 | 742472.6684 | 11499449.7786 | 11059545.9111 | 0 | 485028.8878 | 0 | 13886928.6476 | 36130939.7404 | 24660108.7894 | 110285486.5304 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 126628401.775 | 150522886.3463 | 421696.5034 | 43.3531 | 2920.8598 | 3472.0193 | 59.5457 | 70.7818
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.2749 | 88.5799 | 11.1898 | 4 | 2910.7345 | 3444.5799 | 59.3393 | 70.2224 | 178.824 | 0 | 308.5734 | 12125578.7097 | 761118.272 | 11832761.6527 | 11521053.6521 | 0 | 546654.6537 | 0 | 14346995.1067 | 37327938.2942 | 25477084.8982 | 113939185.2393 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130282100.4839 | 154176585.0551 | 562341.3252 | 44.7592 | 2910.7345 | 3444.5799 | 59.3393 | 70.2224
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.9982 | 88.8237 | 11.2395 | 4 | 2902.5092 | 3433.9958 | 59.1716 | 70.0066 | 178.7744 | 0 | 303.6005 | 12150202.0073 | 762779.8432 | 11858664.4983 | 11556202.4425 | 0 | 526614.5065 | 0 | 14373240.6861 | 37396223.9083 | 25523691.233 | 114147619.1252 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130490534.3698 | 154385018.9411 | 749894.2093 | 44.9578 | 2902.5092 | 3433.9958 | 59.1716 | 70.0066
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.5239 | 89.0002 | 11.2762 | 4 | 2896.317 | 3426.0715 | 59.0453 | 69.8451 | 178.7383 | 0 | 381.6796 | 12168023.9099 | 763983.6103 | 11877408.0519 | 11581687.9798 | 0 | 510929.742 | 0 | 14391792.9846 | 37444493.1833 | 25556636.005 | 114294955.4667 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130637870.7113 | 154532355.2825 | 1000000 | 45.1048 | 2896.317 | 3426.0715 | 59.0453 | 69.8451
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.9332 | 89.1371 | 11.3043 | 4 | 2891.6592 | 3420.0951 | 58.9504 | 69.7233 | 178.71 | 0 | 370.463 | 12181850.5174 | 764918.328 | 11891946.1051 | 11601489.0361 | 0 | 499073.2305 | 0 | 14406318.1147 | 37482284.5923 | 25582429.4182 | 114410309.3424 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130753224.587 | 154647709.1582 | 1333521.4322 | 45.2174 | 2891.6592 | 3420.0951 | 58.9504 | 69.7233
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.2233 | 89.2339 | 11.3249 | 4 | 2888.1577 | 3415.6356 | 58.879 | 69.6324 | 178.6899 | 0 | 365.7293 | 12191623.4197 | 765579.3841 | 11902220.3055 | 11615499.2645 | 0 | 489819.6913 | 0 | 14416249.4054 | 37508123.7734 | 25600065.1902 | 114489180.4341 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130832095.6787 | 154726580.2499 | 1778279.41 | 45.2995 | 2888.1577 | 3415.6356 | 58.879 | 69.6324
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.4519 | 89.3101 | 11.3407 | 4 | 2885.5269 | 3412.2695 | 58.8254 | 69.5637 | 178.6741 | 0 | 368.5783 | 12199315.8759 | 766099.8182 | 11910307.2654 | 11626533.4637 | 0 | 482920.9815 | 0 | 14424219.1878 | 37528859.5125 | 25614217.7582 | 114552473.8631 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130895389.1077 | 154789873.6789 | 2371373.7057 | 45.3627 | 2885.5269 | 3412.2695 | 58.8254 | 69.5637
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.6176 | 89.3653 | 11.3523 | 4 | 2883.5512 | 3409.7526 | 58.7851 | 69.5124 | 178.6626 | 0 | 343.4136 | 12204886.9313 | 766476.8529 | 11916163.5107 | 11634529.3846 | 0 | 477626.308 | 0 | 14429876.3651 | 37543578.3274 | 25624263.6519 | 114597401.3319 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130940316.5765 | 154834801.1478 | 3162277.6602 | 45.4094 | 2883.5512 | 3409.7526 | 58.7851 | 69.5124
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.7251 | 89.401 | 11.3605 | 4 | 2882.068 | 3407.8917 | 58.7549 | 69.4745 | 178.6552 | 0 | 309.7764 | 12208490.1515 | 766720.8492 | 11919950.3631 | 11639704.4707 | 0 | 473421.1224 | 0 | 14433231.9132 | 37552308.7752 | 25630222.3619 | 114624050.0073 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130966965.2519 | 154861449.8231 | 4216965.0343 | 45.442 | 2882.068 | 3407.8917 | 58.7549 | 69.4745
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.8151 | 89.4309 | 11.367 | 4 | 2880.9548 | 3406.4799 | 58.7322 | 69.4457 | 178.6489 | 0 | 353.4121 | 12211510.0045 | 766925.3037 | 11923124.4834 | 11644041.7605 | 0 | 470364.0828 | 0 | 14436226.5976 | 37560100.3297 | 25635540.2579 | 114647832.8201 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130990748.0647 | 154885232.636 | 5623413.2519 | 45.4678 | 2880.9548 | 3406.4799 | 58.7322 | 69.4457
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.8929 | 89.4568 | 11.3722 | 4 | 2880.1194 | 3405.4039 | 58.7151 | 69.4238 | 178.6435 | 0 | 382.897 | 12214121.3255 | 767102.0554 | 11925869.5794 | 11647792.0727 | 0 | 468186.1657 | 0 | 14438997.7675 | 37567310.3453 | 25640461.2417 | 114669840.5531 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 131012755.7977 | 154907240.3689 | 7498942.0933 | 45.4887 | 2880.1194 | 3405.4039 | 58.7151 | 69.4238
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.942 | 89.4731 | 11.3757 | 4 | 2879.4927 | 3404.612 | 58.7024 | 69.4076 | 178.6401 | 0 | 359.8982 | 12215766.2771 | 767213.4541 | 11927598.4314 | 11650155.7262 | 0 | 466435.3536 | 0 | 14440596.0046 | 37571468.6303 | 25643299.3567 | 114682533.234 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 131025448.4786 | 154919933.0498 | 10000000 | 45.503 | 2879.4927 | 3404.612 | 58.7024 | 69.4076
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75975 | 0.15354 | 0.0053922 | 4 | 821051.3375 | 1958994.7378 | 16738.2421 | 39936.7575 | 114.2818 | 0 | 54.5802 | 104721.3965 | 4012.358 | 76384.566 | 51974.2204 | 0 | 54192.7544 | 0 | 113601.2652 | 295567.1892 | 201730.6799 | 902184.4296 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 17709068.1825 | 42253108.6653 | 100 | 0.021569 | 821051.3375 | 1958994.7378 | 16738.2421 | 39936.7575
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.23634 | 0.012915 | 4 | 348539.9031 | 823640.8953 | 7105.4574 | 16791.0337 | 126.4168 | 0 | 54.1958 | 150511.4568 | 6293.0046 | 106948.4968 | 63239.338 | 0 | 60100.5664 | 0 | 150966.2164 | 392783.1276 | 268082.5555 | 1198924.762 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18005808.5149 | 42549848.9977 | 133.3521 | 0.051661 | 348539.9031 | 823640.8953 | 7105.4574 | 16791.0337
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.36118 | 0.025368 | 4 | 181493.4881 | 423377.1295 | 3699.9902 | 8631.1154 | 137.9674 | 0 | 54.4679 | 213278.6315 | 9706.1924 | 148979.9165 | 79746.1328 | 0 | 67891.7406 | 0 | 202645.0194 | 527240.7722 | 359852.6608 | 1609341.0662 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18416224.819 | 42960265.3018 | 177.8279 | 0.10147 | 181493.4881 | 423377.1295 | 3699.9902 | 8631.1154
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.53111 | 0.04382 | 4 | 107981.8148 | 248008.1905 | 2201.3554 | 5055.9824 | 147.7585 | 0 | 280.1649 | 290880.7587 | 14260.3822 | 201499.0095 | 101790.578 | 0 | 76155.2445 | 0 | 266988.5295 | 694649.3868 | 474112.4801 | 2120336.3692 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18927220.1221 | 43471260.6049 | 237.1374 | 0.17528 | 107981.8148 | 248008.1905 | 2201.3554 | 5055.9824
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.76085 | 0.070228 | 4 | 69650.4934 | 157022.8997 | 1419.9195 | 3201.1242 | 155.9994 | 0 | 382.3579 | 386511.6917 | 20245.0416 | 267172.1385 | 131438.2733 | 0 | 85370.9873 | 0 | 347387.8717 | 903831.983 | 616883.9003 | 2758841.8875 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19565725.6404 | 44109766.1232 | 316.2278 | 0.28091 | 69650.4934 | 157022.8997 | 1419.9195 | 3201.1242
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7794 | 1.074 | 0.10751 | 4 | 47376.1369 | 104448.302 | 965.8266 | 2129.3199 | 162.9405 | 0 | 481.3228 | 505384.702 | 28086.2533 | 350379.0197 | 171462.0498 | 0 | 96467.5074 | 0 | 449194.0176 | 1168710.6913 | 797669.0614 | 3567353.3025 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 20374237.0554 | 44918277.5382 | 421.6965 | 0.43005 | 47376.1369 | 104448.302 | 965.8266 | 2129.3199
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 1.499 | 0.1593 | 4 | 33576.3044 | 72094.2633 | 684.4984 | 1469.7391 | 168.6946 | 0 | 633.724 | 652556.6327 | 38213.6 | 455729.5368 | 224750.8081 | 0 | 110153.3153 | 0 | 577747.5183 | 1503180.5302 | 1025951.5991 | 4588283.5406 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 21395167.2934 | 45939207.7762 | 562.3413 | 0.63721 | 33576.3044 | 72094.2633 | 684.4984 | 1469.7391
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7622 | 2.0689 | 0.23049 | 4 | 24604.1436 | 51226.1781 | 501.5887 | 1044.3149 | 173.3103 | 0 | 81.2438 | 833675.94 | 51245.0105 | 587754.1416 | 298201.6329 | 0 | 126537.5216 | 0 | 739991.5562 | 1925306.236 | 1314061.0672 | 5876773.1059 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 22683656.8587 | 47227697.3415 | 749.8942 | 0.92194 | 24604.1436 | 51226.1781 | 501.5887 | 1044.3149
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.258 | 2.8271 | 0.32637 | 4 | 18603.9243 | 37404.7414 | 379.2662 | 762.5462 | 176.9554 | 0 | 67.6488 | 1054125.84 | 67577.6713 | 752476.6676 | 394457.3021 | 0 | 146443.2994 | 0 | 941881.5044 | 2450582.4679 | 1672572.8888 | 7480117.6415 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 24287001.3944 | 48831041.8772 | 1000 | 1.3055 | 18603.9243 | 37404.7414 | 379.2662 | 762.5462
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2311 | 3.8807 | 0.45297 | 4 | 14526.0737 | 28072.2067 | 296.1337 | 572.2899 | 179.5915 | 0 | 79.964 | 1320745.0171 | 85276.0563 | 969029.5097 | 524315.1025 | 0 | 171967.2552 | 0 | 1197819.8469 | 3116481.535 | 2127062.685 | 9512697.0077 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 26319580.7605 | 50863621.2434 | 1333.5214 | 1.8119 | 14526.0737 | 28072.2067 | 296.1337 | 572.2899
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8789 | 5.333 | 0.62605 | 4 | 11541.3408 | 21342.5327 | 235.2858 | 435.0964 | 182.1404 | 0 | 92.3557 | 1652508.802 | 106641.2934 | 1249568.5066 | 692938.3054 | 0 | 203357.229 | 0 | 1522955.5132 | 3962417.8442 | 2704431.5982 | 12094819.0921 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 28901702.8449 | 53445743.3277 | 1778.2794 | 2.5042 | 11541.3408 | 21342.5327 | 235.2858 | 435.0964
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.3795 | 7.2322 | 0.8519 | 4 | 9413.9071 | 16616.6644 | 191.9152 | 338.7532 | 183.8819 | 0 | 95.6526 | 2048545.0851 | 131988.6459 | 1594415.133 | 914437.7996 | 0 | 241384.1475 | 0 | 1923000.6163 | 5003253.1419 | 3414823.0759 | 15271847.6451 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 32078731.3979 | 56622771.8807 | 2371.3737 | 3.4076 | 9413.9071 | 16616.6644 | 191.9152 | 338.7532
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.04 | 9.7616 | 1.1525 | 4 | 7823.4145 | 13147.2884 | 159.4909 | 268.0253 | 185.2221 | 0 | 98.3184 | 2531844.1156 | 162821.219 | 2026752.6728 | 1209171.8913 | 0 | 287983.5658 | 0 | 2425243.6512 | 6309986.4944 | 4306695.4397 | 19260499.0498 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 36067382.8026 | 60611423.2854 | 3162.2777 | 4.6102 | 7823.4145 | 13147.2884 | 159.4909 | 268.0253
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1986 | 13.1044 | 1.55 | 4 | 6620.387 | 10579.1292 | 134.9655 | 215.6699 | 186.2425 | 0 | 86.6556 | 3118161.1669 | 200096.6936 | 2565189.8295 | 1598370.7244 | 0 | 344226.7116 | 0 | 3052157.5992 | 7941087.9894 | 5419955.7258 | 24239246.4405 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 41046130.1933 | 65590170.6761 | 4216.965 | 6.2 | 6620.387 | 10579.1292 | 134.9655 | 215.6699
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.3079 | 17.5068 | 2.0734 | 4 | 5697.4527 | 8656.8051 | 116.1503 | 176.4807 | 187.0172 | 0 | 96.196 | 3828174.4721 | 245070.8536 | 3234074.9613 | 2110678.6287 | 0 | 412062.7132 | 0 | 3833724.0353 | 9974563.5348 | 6807844.5693 | 30446193.7683 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 47253077.5211 | 71797118.0039 | 5623.4133 | 8.2937 | 5697.4527 | 8656.8051 | 116.1503 | 176.4807
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.9385 | 23.2772 | 2.7591 | 4 | 4981.0636 | 7204.964 | 101.5457 | 146.8829 | 187.5987 | 0 | 98.0681 | 4685339.8611 | 299156.557 | 4061901.1821 | 2782186.126 | 0 | 494121.542 | 0 | 4805855.0546 | 12503849.0355 | 8534133.8952 | 38166543.2533 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 54973427.0062 | 79517467.489 | 7498.9421 | 11.0365 | 4981.0636 | 7204.964 | 101.5457 | 146.8829
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.6005 | 30.6732 | 3.6378 | 4 | 4425.1438 | 6111.8929 | 90.2125 | 124.5992 | 187.9824 | 0 | 97.8538 | 5699510.4037 | 362892.9055 | 5065148.1865 | 3644719.3294 | 0 | 590949.7796 | 0 | 5991656.0359 | 15589059.9477 | 10639853.7374 | 47583790.3257 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64390674.0786 | 88934714.5614 | 10000 | 14.5511 | 4425.1438 | 6111.8929 | 90.2125 | 124.5992
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.8011 | 39.878 | 4.7291 | 4 | 3996.9484 | 5294.4563 | 81.4832 | 107.9347 | 188.0674 | 0 | 111.229 | 6868713.2198 | 436074.2427 | 6248439.0155 | 4727201.7914 | 0 | 704316.4837 | 0 | 7404050.4538 | 19263820.5011 | 13147953.3239 | 58800569.0321 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 75607452.7849 | 100151493.2677 | 13335.2143 | 18.9163 | 3996.9484 | 5294.4563 | 81.4832 | 107.9347
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.6294 | 50.7163 | 6.0085 | 4 | 3676.4838 | 4697.7093 | 74.9501 | 95.7692 | 187.679 | 0 | 136.5593 | 8150775.7487 | 516000.6128 | 7573606.1189 | 6028623.4397 | 0 | 833201.1716 | 0 | 9009860.7657 | 23441809.5359 | 15999516.6892 | 71553394.0824 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 88360277.8353 | 112904318.3181 | 17782.7941 | 24.0339 | 3676.4838 | 4697.7093 | 74.9501 | 95.7692
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.5541 | 62.5607 | 7.3955 | 4 | 3447.512 | 4277.2064 | 70.2822 | 87.1966 | 186.6937 | 0 | 127.0036 | 9465600.7555 | 597665.5463 | 8958311.2459 | 7505037.5533 | 0 | 974364.6692 | 0 | 10725382.1104 | 27905244.1729 | 19045902.5434 | 85177508.597 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 101984392.3498 | 126528432.8326 | 23713.7371 | 29.582 | 3447.512 | 4277.2064 | 70.2822 | 87.1966
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4649 | 74.1249 | 8.7439 | 4 | 3291.4565 | 3993.2038 | 67.1008 | 81.4069 | 185.2791 | 0 | 144.6699 | 10682606.2051 | 673010.5984 | 10260205.7654 | 9017800.7743 | 0 | 1108637.5517 | 0 | 12379481.749 | 32208872.1301 | 21983217.0549 | 98313831.8289 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 115120715.5818 | 139664756.0646 | 31622.7766 | 34.9756 | 3291.4565 | 3993.2038 | 67.1008 | 81.4069
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.6512 | 78.662 | 9.4304 | 4 | 3176.489 | 3827.1533 | 64.757 | 78.0217 | 184.6642 | 0 | 164.6691 | 11145121.1458 | 701588.2869 | 10759610.6923 | 9629220.4241 | 0 | 1024599.949 | 0 | 12971454.7943 | 33749064.5634 | 23034430.0385 | 103015089.8943 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 119821973.6472 | 144366014.13 | 42169.6503 | 37.7215 | 3176.489 | 3827.1533 | 64.757 | 78.0217
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.9797 | 82.2682 | 9.9979 | 4 | 3087.9293 | 3701.6601 | 62.9516 | 75.4633 | 184.1327 | 0 | 228.7885 | 11507394.4134 | 723951.5768 | 11152455.2055 | 10125427.4033 | 0 | 935535.5877 | 0 | 13433458.0328 | 34951102.2202 | 23854845.4386 | 106684169.8782 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 123491053.631 | 148035094.1138 | 56234.1325 | 39.9915 | 3087.9293 | 3701.6601 | 62.9516 | 75.4633
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.6339 | 85.0813 | 10.4556 | 4 | 3020.0165 | 3606.8787 | 61.5671 | 73.5311 | 183.6906 | 0 | 271.2109 | 11786884.2898 | 741192.5084 | 11456506.4746 | 10519683.0751 | 0 | 848903.2292 | 0 | 13787736.135 | 35872861.1698 | 24483964.862 | 109497731.7439 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 126304615.4967 | 150848655.9796 | 74989.4209 | 41.8225 | 3020.0165 | 3606.8787 | 61.5671 | 73.5311
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.8251 | 87.2334 | 10.8166 | 4 | 2968.1199 | 3535.3982 | 60.5091 | 72.0739 | 183.3357 | 0 | 263.4286 | 11998943.5001 | 754266.9413 | 11687755.6106 | 10826054.0096 | 0 | 769012.477 | 0 | 14054052.6901 | 36565762.217 | 24956884.0644 | 111612731.5101 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 128419615.2629 | 152963655.7457 | 100000 | 43.2663 | 2968.1199 | 3535.3982 | 60.5091 | 72.0739
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.766 | 88.8423 | 11.0949 | 4 | 2928.575 | 3481.6231 | 59.703 | 70.9776 | 183.0606 | 0 | 342.5121 | 12156507.2794 | 763977.684 | 11859882.2853 | 11058056.5874 | 0 | 697828.8583 | 0 | 14249138.5509 | 37073335.6092 | 25303313.3341 | 113162040.1887 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 129968923.9416 | 154512964.4244 | 133352.1432 | 44.3796 | 2928.575 | 3481.6231 | 59.703 | 70.9776
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.9332 | 90.1168 | 11.3153 | 4 | 2898.4893 | 3440.7648 | 59.0896 | 70.1446 | 182.8362 | 0 | 359.265 | 12280758.2976 | 771633.087 | 11995797.964 | 11242976.948 | 0 | 639043.9377 | 0 | 14402781.9914 | 37473084.3247 | 25576150.0465 | 114382226.5969 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 131189110.3498 | 155733150.8326 | 177827.941 | 45.2612 | 2898.4893 | 3440.7648 | 59.0896 | 70.1446
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.1445 | 90.9969 | 11.4756 | 4 | 2875.6551 | 3410.3549 | 58.6241 | 69.5247 | 182.6775 | 0 | 398.4402 | 12366276.8727 | 776900.9451 | 12089436.7189 | 11371537.378 | 0 | 587756.4107 | 0 | 14504844.2469 | 37738629.3778 | 25757390.0016 | 115192771.9518 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 131999655.7047 | 156543696.1875 | 237137.3706 | 45.9025 | 2875.6551 | 3410.3549 | 58.6241 | 69.5247
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.777 | 91.6421 | 11.5959 | 4 | 2858.3585 | 3387.5137 | 58.2715 | 69.059 | 182.5593 | 0 | 394.2691 | 12428816.1226 | 780752.7119 | 12157961.2226 | 11466328.7548 | 0 | 545585.7097 | 0 | 14577983.3634 | 37928922.356 | 25887268.8694 | 115773619.1103 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 132580502.8632 | 157124543.346 | 316227.766 | 46.3834 | 2858.3585 | 3387.5137 | 58.2715 | 69.059
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.9755 | 92.1133 | 11.6856 | 4 | 2845.2762 | 3370.3682 | 58.0048 | 68.7095 | 182.472 | 0 | 375.2249 | 12474410.7306 | 783560.5533 | 12207944.3251 | 11535858.6673 | 0 | 511474.5093 | 0 | 14630167.0264 | 38064693.5428 | 25979935.4942 | 116188044.849 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 132994928.6019 | 157538969.0847 | 421696.5034 | 46.7424 | 2845.2762 | 3370.3682 | 58.0048 | 68.7095
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.8186 | 92.4433 | 11.7509 | 4 | 2835.3952 | 3357.5681 | 57.8034 | 68.4486 | 182.4102 | 0 | 377.5481 | 12506310.0594 | 785524.8459 | 12242926.4196 | 11584731.9867 | 0 | 483851.6295 | 0 | 14665304.527 | 38156114.1117 | 26042331.911 | 116467095.4907 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133273979.2436 | 157818019.7264 | 562341.3252 | 47.0037 | 2835.3952 | 3357.5681 | 57.8034 | 68.4486
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.4519 | 92.6906 | 11.8001 | 4 | 2827.9414 | 3347.936 | 57.6514 | 68.2522 | 182.3637 | 0 | 345.1411 | 12530182.7672 | 786994.7926 | 12269112.8832 | 11621424.7374 | 0 | 462289.7347 | 0 | 14691301.9169 | 38223753.9873 | 26088497.5159 | 116673558.3352 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133480442.0881 | 158024482.5709 | 749894.2093 | 47.2006 | 2827.9414 | 3347.936 | 57.6514 | 68.2522
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.9124 | 92.8699 | 11.8366 | 4 | 2822.3246 | 3340.7191 | 57.5369 | 68.1051 | 182.3298 | 0 | 353.3201 | 12547489.7121 | 788060.4119 | 12288100.7992 | 11648093.0339 | 0 | 445420.9311 | 0 | 14709694.3064 | 38271607.2121 | 26121158.3251 | 116819624.7318 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133626508.4847 | 158170548.9675 | 1000000 | 47.3463 | 2822.3246 | 3340.7191 | 57.5369 | 68.1051
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.2413 | 92.9978 | 11.8633 | 4 | 2818.0961 | 3335.3241 | 57.4507 | 67.9951 | 182.3054 | 0 | 356.4695 | 12559825.482 | 788819.9241 | 12301636.5356 | 11667138.5443 | 0 | 432256.0016 | 0 | 14722373.8302 | 38304596.7321 | 26143674.3504 | 116920321.4003 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133727205.1532 | 158271245.636 | 1333521.4322 | 47.453 | 2818.0961 | 3335.3241 | 57.4507 | 67.9951
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.4628 | 93.0838 | 11.8823 | 4 | 2814.9153 | 3331.3162 | 57.3859 | 67.9134 | 182.289 | 0 | 372.1634 | 12568114.1712 | 789330.2473 | 12310732.365 | 11679959.2877 | 0 | 421888.723 | 0 | 14730309.6697 | 38325244.1586 | 26157766.6432 | 116983345.2656 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133790229.0185 | 158334269.5013 | 1778279.41 | 47.529 | 2814.9153 | 3331.3162 | 57.3859 | 67.9134
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.646 | 93.1549 | 11.8972 | 4 | 2812.5241 | 3328.2748 | 57.3371 | 67.8514 | 182.2754 | 0 | 366.5463 | 12574967.2713 | 789752.1767 | 12318253.3284 | 11690562.5874 | 0 | 414208.8546 | 0 | 14737220.2452 | 38343224.0585 | 26170038.2944 | 117038226.8166 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133845110.5694 | 158389151.0522 | 2371373.7057 | 47.589 | 2812.5241 | 3328.2748 | 57.3371 | 67.8514
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.7749 | 93.2048 | 11.9081 | 4 | 2810.7276 | 3326.0066 | 57.3005 | 67.8051 | 182.2659 | 0 | 348.1543 | 12579783.6231 | 790048.7048 | 12323539.3346 | 11698022.185 | 0 | 408281.5248 | 0 | 14741873.3952 | 38355330.6003 | 26178301.2579 | 117075180.6257 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133882064.3786 | 158426104.8614 | 3162277.6602 | 47.6325 | 2810.7276 | 3326.0066 | 57.3005 | 67.8051
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.8649 | 93.2397 | 11.916 | 4 | 2809.3785 | 3324.316 | 57.273 | 67.7707 | 182.2592 | 0 | 372.3678 | 12583143.038 | 790255.5319 | 12327226.4715 | 11703229.8782 | 0 | 403717.5554 | 0 | 14744953.2652 | 38363343.7904 | 26183770.4248 | 117099639.9554 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133906523.7083 | 158450564.1911 | 4216965.0343 | 47.6641 | 2809.3785 | 3324.316 | 57.273 | 67.7707
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.105 | 92.1575 | 11.804 | 4 | 2808.1529 | 3327.9792 | 57.248 | 67.8454 | 182.4577 | 0 | 801.6064 | 12478682.5166 | 783823.6082 | 12212628.345 | 11543131.7323 | 0 | 364033.7039 | 0 | 14579096.9633 | 37931819.7146 | 25889246.3762 | 115782462.96 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 132589346.7129 | 157133387.1957 | 5623413.2519 | 47.2159 | 2808.1529 | 3327.9792 | 57.248 | 67.8454
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.987 | 92.5044 | 11.8437 | 4 | 2807.2922 | 3325.373 | 57.2304 | 67.7922 | 182.3944 | 0 | 647.9671 | 12512204.0684 | 785887.7724 | 12249391.1476 | 11594319.94 | 0 | 371551.725 | 0 | 14630208.3148 | 38064800.9668 | 25980008.8133 | 116188372.7483 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 132995256.5012 | 157539296.984 | 7498942.0933 | 47.3749 | 2807.2922 | 3325.373 | 57.2304 | 67.7922
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.428 | 92.6774 | 11.8641 | 4 | 2806.6885 | 3323.8798 | 57.2181 | 67.7618 | 182.3626 | 0 | 578.536 | 12528907.8162 | 786916.2901 | 12267714.2188 | 11619902.277 | 0 | 374515.6707 | 0 | 14655402.9464 | 38130352.23 | 26024748.8974 | 116388460.3465 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 133195344.0994 | 157739384.5822 | 10000000 | 47.4564 | 2806.6885 | 3323.8798 | 57.2181 | 67.7618
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.78939 | 0.1672 | 0.0066274 | 4 | 687717.0437 | 1638382.8047 | 14020.0421 | 33400.6495 | 117.3313 | 0 | 37.7019 | 112994.4458 | 4424.6234 | 81597.2498 | 53736.7882 | 0 | 55395.4256 | 0 | 120177.9278 | 312678.3162 | 213409.3757 | 954414.1526 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18231126.5045 | 43432927.0261 | 100 | 0.02651 | 687717.0437 | 1638382.8047 | 14020.0421 | 33400.6495
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.25743 | 0.015152 | 4 | 306043.4518 | 721848.4113 | 6239.1097 | 14715.8562 | 129.698 | 0 | 60.9685 | 162311.5993 | 6950.1336 | 114258.5808 | 65871.8571 | 0 | 61449.111 | 0 | 160228.0999 | 416880.6487 | 284529.6088 | 1272479.6392 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18549191.9911 | 43750992.5127 | 133.3521 | 0.06061 | 306043.4518 | 721848.4113 | 6239.1097 | 14715.8562
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3128 | 0.38754 | 0.028723 | 4 | 165103.8086 | 384456.4103 | 3365.8645 | 7837.6639 | 141.0281 | 0 | 61.2392 | 227071.8254 | 10573.6766 | 157292.8417 | 82881.9208 | 0 | 68583.2723 | 0 | 213097.3794 | 554435.6688 | 378413.7365 | 1692350.3214 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18969062.6733 | 44170863.1949 | 177.8279 | 0.11489 | 165103.8086 | 384456.4103 | 3365.8645 | 7837.6639
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.56394 | 0.048576 | 4 | 100310.0387 | 230012.1608 | 2044.9558 | 4689.109 | 150.7349 | 0 | 276.2056 | 306993.3043 | 15396.4319 | 210995.211 | 105282.1387 | 0 | 76176.7645 | 0 | 278789.1017 | 725352.0551 | 495067.6821 | 2214052.6894 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19490765.0414 | 44692565.5629 | 237.1374 | 0.19431 | 100310.0387 | 230012.1608 | 2044.9558 | 4689.109
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.8126 | 0.077965 | 4 | 64695.5758 | 145506.5432 | 1318.9068 | 2966.3477 | 159.2445 | 0 | 362.1921 | 409982.9712 | 22065.1745 | 281001.6359 | 137304.645 | 0 | 85740.6188 | 0 | 365077.0677 | 949855.6425 | 648295.9936 | 2899323.7492 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 20176036.1011 | 45377836.6227 | 316.2278 | 0.31186 | 64695.5758 | 145506.5432 | 1318.9068 | 2966.3477
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8572 | 1.1467 | 0.11881 | 4 | 44241.8966 | 97269.8263 | 901.9309 | 1982.977 | 166.3143 | 0 | 480.8228 | 535898.2796 | 30670.0893 | 368412.5873 | 178727.0644 | 0 | 96874.168 | 0 | 472127.0536 | 1228377.7468 | 838393.0528 | 3749480.0418 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 21026192.3938 | 46227992.9153 | 421.6965 | 0.47526 | 44241.8966 | 97269.8263 | 901.9309 | 1982.977
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7365 | 1.6015 | 0.17636 | 4 | 31351.6765 | 67075.6708 | 639.1463 | 1367.4283 | 172.1525 | 0 | 67.6267 | 693732.3822 | 42166.8956 | 479258.8249 | 237145.5441 | 0 | 110564.4317 | 0 | 609518.5506 | 1585842.2393 | 1082369.9141 | 4840598.7827 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 22117311.1347 | 47319111.6562 | 562.3413 | 0.70546 | 31351.6765 | 67075.6708 | 639.1463 | 1367.4283
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8742 | 2.1977 | 0.25325 | 4 | 23147.6579 | 48026.0486 | 471.8963 | 979.076 | 176.7691 | 0 | 84.0128 | 882626.3087 | 56484.3216 | 615248.0339 | 312211.7034 | 0 | 126116.4571 | 0 | 777147.8617 | 2021979.3211 | 1380042.4342 | 6171856.4417 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 23448568.7936 | 48650369.3152 | 749.8942 | 1.013 | 23147.6579 | 48026.0486 | 471.8963 | 979.076
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4064 | 3.0616 | 0.35811 | 4 | 17584.8559 | 35178.5873 | 358.4911 | 717.1631 | 180.4737 | 0 | 94.8034 | 1118251.7167 | 72312.2098 | 801575.3131 | 415114.2198 | 0 | 147388.69 | 0 | 996310.4383 | 2592195.3891 | 1769226.6173 | 7912374.5941 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 25189086.9461 | 50390887.4676 | 1000 | 1.4324 | 17584.8559 | 35178.5873 | 358.4911 | 717.1631
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4164 | 4.1857 | 0.49235 | 4 | 13851.1744 | 26647.8101 | 282.3749 | 543.2517 | 183.1087 | 0 | 76.8715 | 1393327.3789 | 90008.2544 | 1029429.4024 | 543654.5017 | 0 | 172862.5867 | 0 | 1259420.0284 | 3276752.5713 | 2236450.9604 | 10001905.6841 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 27278618.0361 | 52480418.5576 | 1333.5214 | 1.9694 | 13851.1744 | 26647.8101 | 282.3749 | 543.2517
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1347 | 5.7516 | 0.6797 | 4 | 11032.0216 | 20301.416 | 224.9027 | 413.8718 | 185.7562 | 0 | 99.5449 | 1742910.0254 | 112434.2155 | 1327440.4003 | 718504.7183 | 0 | 204719.7137 | 0 | 1601343.5385 | 4166367.4064 | 2843631.3652 | 12717351.3831 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 29994063.7351 | 55195864.2566 | 1778.2794 | 2.7188 | 11032.0216 | 20301.416 | 224.9027 | 413.8718
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.7085 | 7.7842 | 0.9228 | 4 | 9025.0524 | 15852.6097 | 183.9879 | 323.1769 | 187.5244 | 0 | 96.1313 | 2157720.5684 | 138962.744 | 1691055.104 | 947116.2575 | 0 | 242782.8382 | 0 | 2019278.6297 | 5253748.7836 | 3585791.4986 | 16036456.4241 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 33313168.776 | 58514969.2976 | 2371.3737 | 3.6912 | 9025.0524 | 15852.6097 | 183.9879 | 323.1769
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4615 | 10.4884 | 1.2461 | 4 | 7518.7186 | 12574.8349 | 153.2792 | 256.355 | 188.8855 | 0 | 98.7267 | 2663702.693 | 171215.9328 | 2146609.0391 | 1250953.4558 | 0 | 289338.518 | 0 | 2543509.6591 | 6617690.3874 | 4516709.6693 | 20199729.3546 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 37476441.7065 | 62678242.2281 | 3162.2777 | 4.9844 | 7518.7186 | 12574.8349 | 153.2792 | 256.355
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7562 | 14.0706 | 1.6744 | 4 | 6373.6302 | 10136.5522 | 129.9351 | 206.6473 | 189.9247 | 0 | 101.1067 | 3279211.8439 | 210313.1237 | 2715410.3258 | 1653238.7408 | 0 | 345884.3736 | 0 | 3199582.779 | 8324658.0663 | 5681750.1849 | 25410049.438 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 42686761.79 | 67888562.3115 | 4216.965 | 6.6974 | 6373.6302 | 10136.5522 | 129.9351 | 206.6473
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0608 | 18.7975 | 2.2393 | 4 | 5492.3026 | 8305.8831 | 111.968 | 169.3267 | 190.7146 | 0 | 80.6044 | 4026168.4437 | 257583.1802 | 3423460.5256 | 2183901.9982 | 0 | 414447.122 | 0 | 4019168.8951 | 10457053.0203 | 7137153.5573 | 31918936.7423 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 49195649.0943 | 74397449.6158 | 5623.4133 | 8.9572 | 5492.3026 | 8305.8831 | 111.968 | 169.3267
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8742 | 24.9511 | 2.975 | 4 | 4809.6381 | 6927.4619 | 98.051 | 141.2257 | 191.3025 | 0 | 101.7101 | 4922079.3537 | 314058.0877 | 4293947.5146 | 2874736.6944 | 0 | 496057.3431 | 0 | 5031342.8075 | 13090521.9147 | 8934550.1901 | 39957293.9057 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 57234006.2577 | 82435806.7792 | 7498.9421 | 11.8999 | 4809.6381 | 6927.4619 | 98.051 | 141.2257
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.8185 | 32.8617 | 3.9198 | 4 | 4277.6627 | 5884.9855 | 87.2059 | 119.9734 | 191.6832 | 0 | 92.2526 | 5985627.3165 | 380829.0398 | 5352255.2671 | 3764795.6399 | 0 | 593420.6014 | 0 | 6270001.8672 | 16313258.7043 | 11134134.2697 | 49794322.7059 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 67071035.0579 | 92272835.5795 | 10000 | 15.6794 | 4277.6627 | 5884.9855 | 87.2059 | 119.9734
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.2775 | 42.6461 | 5.0867 | 4 | 3868.7686 | 5107.3806 | 78.8701 | 104.1209 | 191.7393 | 0 | 96.4899 | 7204661.9637 | 457048.4353 | 6593072.7555 | 4875971.2508 | 0 | 706296.1586 | 0 | 7736449.7199 | 20128655.2072 | 13738220.7814 | 61440376.2725 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 78717088.6245 | 103918889.146 | 13335.2143 | 20.3468 | 3868.7686 | 5107.3806 | 78.8701 | 104.1209
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.3421 | 54.1152 | 6.4487 | 4 | 3562.9298 | 4539.9371 | 72.6351 | 92.5528 | 191.289 | 0 | 124.8787 | 8536219.9949 | 539971.0904 | 7977010.9974 | 6207537.0357 | 0 | 834377.1915 | 0 | 9397095.3609 | 24449314.5196 | 16687159.5428 | 74628685.7332 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 91905398.0851 | 117107198.6067 | 17782.7941 | 25.7949 | 3562.9298 | 4539.9371 | 72.6351 | 92.5528
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.4099 | 66.5727 | 7.9169 | 4 | 3344.5901 | 4140.4123 | 68.184 | 84.4079 | 190.2119 | 0 | 152.7396 | 9894493.5994 | 624243.8803 | 9415028.9358 | 7710572.8084 | 0 | 974083.5776 | 0 | 11161184.8926 | 29039113.6166 | 19819791.7375 | 88638513.0482 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 105915225.4001 | 131117025.9217 | 23713.7371 | 31.6676 | 3344.5901 | 4140.4123 | 68.184 | 84.4079
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.2495 | 79.1182 | 9.3791 | 4 | 3195.2169 | 3866.9706 | 65.1388 | 78.8334 | 188.657 | 0 | 143.9691 | 11191207.1165 | 704434.1917 | 10809505.1381 | 9299875.2158 | 0 | 1119944.7131 | 0 | 12918736.8863 | 33611903.3809 | 22940814.713 | 102596421.3553 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 119873133.7073 | 145074934.2288 | 31622.7766 | 37.5164 | 3195.2169 | 3866.9706 | 65.1388 | 78.8334
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.201 | 84.2069 | 10.1289 | 4 | 3087.4289 | 3709.456 | 62.9414 | 75.6223 | 187.9491 | 0 | 166.8567 | 11700286.3707 | 735851.6426 | 11362208.8528 | 9967057.6342 | 0 | 1043600.983 | 0 | 13575512.1385 | 35320697.864 | 24107102.06 | 107812317.5459 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 125089029.8979 | 150290830.4194 | 42169.6503 | 40.5156 | 3087.4289 | 3709.456 | 62.9414 | 75.6223
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.4339 | 87.9173 | 10.7155 | 4 | 3004.4162 | 3592.3894 | 61.2491 | 73.2357 | 187.3857 | 0 | 220.5184 | 12066020.2791 | 758401.3132 | 11761000.49 | 10463677.856 | 0 | 950228.2124 | 0 | 14039737.9788 | 36528518.2745 | 24931464.3083 | 111499048.7123 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 128775761.0642 | 153977561.5858 | 56234.1325 | 42.8622 | 3004.4162 | 3592.3894 | 61.2491 | 73.2357
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.025 | 90.8185 | 11.1886 | 4 | 2940.7728 | 3503.8847 | 59.9516 | 71.4314 | 186.917 | 0 | 235.4793 | 12348962.257 | 775834.4574 | 12070472.0339 | 10859525.2956 | 0 | 860531.933 | 0 | 14396977.131 | 37457981.2687 | 25565841.9004 | 114336126.2768 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 131612838.6288 | 156814639.1503 | 74989.4209 | 44.7545 | 2940.7728 | 3503.8847 | 59.9516 | 71.4314
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1157 | 93.0144 | 11.5588 | 4 | 2892.1379 | 3437.2179 | 58.9601 | 70.0723 | 186.5446 | 0 | 306.9715 | 12561428.5294 | 788918.6222 | 12303395.6318 | 11163613.5698 | 0 | 777696.0849 | 0 | 14662070.4509 | 38147699.709 | 26036588.9082 | 116441411.5062 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 133718123.8581 | 158919924.3797 | 100000 | 46.235 | 2892.1379 | 3437.2179 | 58.9601 | 70.0723
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.0233 | 94.6743 | 11.8457 | 4 | 2855.0781 | 3386.9544 | 58.2046 | 69.0476 | 186.2529 | 0 | 340.3229 | 12721089.9831 | 798747.2166 | 12478727.5856 | 11396485.1638 | 0 | 704816.2024 | 0 | 14858947.7991 | 38659934.184 | 26386199.4628 | 118004947.5974 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 135281659.9494 | 160483460.4709 | 133352.1432 | 47.3828 | 2855.0781 | 3386.9544 | 58.2046 | 69.0476
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.9144 | 95.8877 | 12.0624 | 4 | 2826.9029 | 3349.2245 | 57.6302 | 68.2785 | 186.0338 | 0 | 392.5211 | 12837309.4381 | 805899.5761 | 12606512.389 | 11568491.6493 | 0 | 641722.0049 | 0 | 14999374.6724 | 39025296.1027 | 26635566.4798 | 119120172.3122 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 136396884.6642 | 161598685.1857 | 177827.941 | 48.2496 | 2826.9029 | 3349.2245 | 57.6302 | 68.2785
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.2339 | 96.8505 | 12.2331 | 4 | 2805.5071 | 3320.5417 | 57.1941 | 67.6937 | 185.8562 | 0 | 356.9636 | 12929230.2008 | 811555.371 | 12707674.2583 | 11705553.8162 | 0 | 590972.7465 | 0 | 15110544.6932 | 39314537.6928 | 26832979.8083 | 120003048.5872 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 137279760.9391 | 162481561.4607 | 237137.3706 | 48.9322 | 2805.5071 | 3320.5417 | 57.1941 | 67.6937
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.8197 | 97.5034 | 12.3554 | 4 | 2789.2955 | 3299.23 | 56.8636 | 67.2593 | 185.7336 | 0 | 356.8546 | 12991418.0122 | 815381.1397 | 12776160.6968 | 11799024.6587 | 0 | 547618.6964 | 0 | 15182545.2495 | 39501868.3709 | 26960836.8453 | 120574853.6695 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 137851566.0214 | 163053366.543 | 316227.766 | 49.4216 | 2789.2955 | 3299.23 | 56.8636 | 67.2593
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.9723 | 97.9754 | 12.4462 | 4 | 2777.0322 | 3283.2483 | 56.6136 | 66.9335 | 185.6439 | 0 | 377.823 | 13036303.0544 | 818142.156 | 12825615.1674 | 11866903.5341 | 0 | 512453.8712 | 0 | 15233172.9354 | 39633591.2246 | 27050740.3996 | 120976922.3428 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138253634.6947 | 163455435.2163 | 421696.5034 | 49.7847 | 2777.0322 | 3283.2483 | 56.6136 | 66.9335
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.8077 | 98.3161 | 12.5133 | 4 | 2767.7682 | 3271.2683 | 56.4247 | 66.6892 | 185.5786 | 0 | 348.2351 | 13068666.2538 | 820132.7635 | 12861285.1119 | 11916068.5513 | 0 | 484330.0387 | 0 | 15268688.2605 | 39725994.8152 | 27113807.7489 | 121258973.5438 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138535685.8958 | 163737486.4173 | 562341.3252 | 50.0532 | 2767.7682 | 3271.2683 | 56.4247 | 66.6892
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.4191 | 98.5647 | 12.5632 | 4 | 2760.7785 | 3262.2796 | 56.2822 | 66.506 | 185.5306 | 0 | 365.7365 | 13092265.1301 | 821584.2117 | 12887301.5932 | 11952037.5622 | 0 | 462181.9747 | 0 | 15293994.484 | 39791836.4178 | 27158745.9957 | 121459947.3695 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138736659.7214 | 163938460.243 | 749894.2093 | 50.2527 | 2760.7785 | 3262.2796 | 56.2822 | 66.506
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.8398 | 98.7355 | 12.5991 | 4 | 2755.5105 | 3255.5838 | 56.1748 | 66.3695 | 185.4974 | 0 | 470.3812 | 13108456.5012 | 822580.0225 | 12905154.8011 | 11976779.6654 | 0 | 444573.251 | 0 | 15310442.2541 | 39834630.1416 | 27187953.5914 | 121590570.2283 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138867282.5802 | 164069083.1018 | 1000000 | 50.3962 | 2755.5105 | 3255.5838 | 56.1748 | 66.3695
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.1519 | 98.8619 | 12.6259 | 4 | 2751.544 | 3250.5556 | 56.0939 | 66.267 | 185.4728 | 0 | 438.4318 | 13120444.3882 | 823317.2878 | 12918374.7142 | 11995129.5195 | 0 | 430999.2829 | 0 | 15322423.4251 | 39865802.6909 | 27209229.4968 | 121685720.8053 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138962433.1573 | 164164233.6788 | 1333521.4322 | 50.5034 | 2751.544 | 3250.5556 | 56.0939 | 66.267
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.3929 | 98.9594 | 12.6463 | 4 | 2748.56 | 3246.7652 | 56.0331 | 66.1897 | 185.4538 | 0 | 443.965 | 13129688.2692 | 823885.7825 | 12928569.555 | 12009295.2531 | 0 | 420710.2979 | 0 | 15331738.1715 | 39890037.7503 | 27225770.4229 | 121759695.5025 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 139036407.8544 | 164238208.376 | 1778279.41 | 50.5852 | 2748.56 | 3246.7652 | 56.0331 | 66.1897
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.5586 | 99.0264 | 12.661 | 4 | 2746.3166 | 3243.9437 | 55.9874 | 66.1322 | 185.4406 | 0 | 425.0865 | 13136037.7365 | 824276.2661 | 12935572.6956 | 12019038.4185 | 0 | 412694.7697 | 0 | 15337771.7557 | 39905735.8988 | 27236484.7318 | 121807612.2727 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 139084324.6246 | 164286125.1462 | 2371373.7057 | 50.644 | 2746.3166 | 3243.9437 | 55.9874 | 66.1322
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.6707 | 99.0717 | 12.6715 | 4 | 2744.631 | 3241.846 | 55.953 | 66.0894 | 185.4317 | 0 | 424.7535 | 13140323.1997 | 824539.8134 | 12940299.5628 | 12025622.8488 | 0 | 406463.6984 | 0 | 15341527.158 | 39915506.6852 | 27243153.4943 | 121837436.4607 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 139114148.8126 | 164315949.3342 | 3162277.6602 | 50.6859 | 2744.631 | 3241.846 | 55.953 | 66.0894
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.4588 | 98.1678 | 12.5794 | 4 | 2743.1109 | 3243.9637 | 55.922 | 66.1326 | 185.6014 | 0 | 436.5821 | 13054585.1962 | 819266.6763 | 12845764.0652 | 11895340.5862 | 0 | 371368.2892 | 0 | 15204666.6771 | 39559423.7879 | 27000119.6001 | 120750534.8783 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138027247.2303 | 163229047.7518 | 4216965.0343 | 50.3178 | 2743.1109 | 3243.9637 | 55.922 | 66.1326
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.246 | 98.49 | 12.6174 | 4 | 2742.0994 | 3241.4448 | 55.9014 | 66.0812 | 185.541 | 0 | 622.4735 | 13085177.0742 | 821148.2681 | 12879486.8326 | 11941715.5414 | 0 | 376839.449 | 0 | 15250703.1945 | 39679201.3627 | 27081870.2561 | 121116141.9786 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138392854.3306 | 163594654.8521 | 5623413.2519 | 50.4697 | 2742.0994 | 3241.4448 | 55.9014 | 66.0812
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.04 | 98.8143 | 12.6548 | 4 | 2741.3431 | 3239.2142 | 55.886 | 66.0358 | 185.48 | 0 | 432.0515 | 13115930.1824 | 823039.6623 | 12913396.4099 | 11988477.665 | 0 | 383482.7216 | 0 | 15297487.3901 | 39800924.2429 | 27164948.623 | 121487686.8971 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138764399.2491 | 163966199.7706 | 7498942.0933 | 50.6191 | 2741.3431 | 3239.2142 | 55.886 | 66.0358
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.5394 | 99.0177 | 12.6785 | 4 | 2740.7956 | 3237.7363 | 55.8748 | 66.0056 | 185.4415 | 0 | 445.3502 | 13135208.3856 | 824225.2624 | 12934657.9416 | 12017874.8285 | 0 | 387273.0276 | 0 | 15326703.3838 | 39876938.2655 | 27216829.7553 | 121719710.8503 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138996423.2022 | 164198223.7238 | 10000000 | 50.7139 | 2740.7956 | 3237.7363 | 55.8748 | 66.0056
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81347 | 0.17937 | 0.0078707 | 4 | 595614.7678 | 1417262.8243 | 12142.4127 | 28892.8197 | 120.0128 | 0 | 45.9819 | 120352.055 | 4803.331 | 86153.5643 | 55236.852 | 0 | 56064.9885 | 0 | 125818.2084 | 327353.1693 | 223425.2645 | 999207.433 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 18751608.4749 | 44619373.1624 | 100 | 0.031483 | 595614.7678 | 1417262.8243 | 12142.4127 | 28892.8197
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0498 | 0.27755 | 0.017452 | 4 | 273512.312 | 644074.8283 | 5575.9184 | 13130.3365 | 132.7528 | 0 | 48.5434 | 173505.2888 | 7595.3727 | 121098.7713 | 68266.5979 | 0 | 62370.453 | 0 | 168806.2287 | 439199.1801 | 299762.4651 | 1340604.3576 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19093005.3995 | 44960770.0871 | 133.3521 | 0.069807 | 273512.312 | 644074.8283 | 5575.9184 | 13130.3365
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.4117 | 0.032043 | 4 | 152283.2453 | 354101.5782 | 3104.4999 | 7218.8396 | 143.8602 | 0 | 64.5214 | 239746.4017 | 11403.8618 | 164777.3372 | 85633.4201 | 0 | 68711.123 | 0 | 222406.1361 | 578655.1443 | 394944.0262 | 1766277.4503 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19518678.4922 | 45386443.1797 | 177.8279 | 0.12817 | 152283.2453 | 354101.5782 | 3104.4999 | 7218.8396
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.60862 | 0.054741 | 4 | 91785.8934 | 209923.162 | 1871.1796 | 4279.5676 | 154.1136 | 0 | 288.9623 | 328421.8272 | 16939.4098 | 223742.5714 | 110867.4643 | 0 | 77270.8764 | 0 | 295324.4382 | 768373.6087 | 524430.7765 | 2345370.9725 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 20097772.0144 | 45965536.7019 | 237.1374 | 0.21896 | 91785.8934 | 209923.162 | 1871.1796 | 4279.5676
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.86647 | 0.08622 | 4 | 60299.1681 | 135304.5591 | 1229.2801 | 2758.3665 | 162.4871 | 0 | 379.3949 | 434266.2063 | 24028.6055 | 295173.6407 | 143188.4592 | 0 | 85987.8486 | 0 | 383231.4565 | 997089.6382 | 680534.1662 | 3043500.0213 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 20795901.0632 | 46663665.7507 | 316.2278 | 0.34488 | 60299.1681 | 135304.5591 | 1229.2801 | 2758.3665
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.935 | 1.2237 | 0.13132 | 4 | 41309.5183 | 90555.1661 | 842.1504 | 1846.0895 | 169.6843 | 0 | 502.39 | 568658.0956 | 33651.8614 | 387148.4278 | 187632.499 | 0 | 97157.9754 | 0 | 496957.0551 | 1292980.3174 | 882485.6347 | 3946671.8665 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 21699072.9084 | 47566837.5959 | 421.6965 | 0.52528 | 41309.5183 | 90555.1661 | 842.1504 | 1846.0895
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 1.7034 | 0.19388 | 4 | 29449.1067 | 62804.8494 | 600.3599 | 1280.3618 | 175.5476 | 0 | 84.4099 | 734510.8125 | 46342.4995 | 502273.2875 | 248542.2445 | 0 | 110341.4279 | 0 | 640384.006 | 1666147.8229 | 1137180.125 | 5085722.2258 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 22838123.2677 | 48705887.9552 | 562.3413 | 0.77551 | 29449.1067 | 62804.8494 | 600.3599 | 1280.3618
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0058 | 2.3852 | 0.27877 | 4 | 21787.1273 | 44984.9402 | 444.1601 | 917.0789 | 180.2843 | 0 | 88.895 | 938429.7467 | 60717.9315 | 656458.949 | 329364.3411 | 0 | 127324.6408 | 0 | 823795.2876 | 2143346.3546 | 1462877.9284 | 6542315.1796 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 24294716.2215 | 50162480.909 | 749.8942 | 1.1151 | 21787.1273 | 44984.9402 | 444.1601 | 917.0789
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5721 | 3.3119 | 0.39004 | 4 | 16722.3 | 33302.6453 | 340.9067 | 678.9195 | 184.0167 | 0 | 87.454 | 1181756.5984 | 76401.731 | 853589.3318 | 431231.7589 | 0 | 148706.3965 | 0 | 1049757.4685 | 2731253.5981 | 1864136.7024 | 8336833.5856 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 26089234.6276 | 51956999.3151 | 1000 | 1.5601 | 16722.3 | 33302.6453 | 340.9067 | 678.9195
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 4.5151 | 0.53437 | 4 | 13227.4807 | 25329.3647 | 269.6601 | 516.3734 | 186.6528 | 0 | 75.6922 | 1469655.8469 | 94910.5711 | 1093752.6972 | 564214.5579 | 0 | 174451.8618 | 0 | 1324824.3586 | 3446921.2222 | 2352594.5613 | 10521325.6769 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 28273726.7188 | 54141491.4063 | 1333.5214 | 2.1375 | 13227.4807 | 25329.3647 | 269.6601 | 516.3734
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3905 | 6.1775 | 0.73455 | 4 | 10580.5418 | 19384.5119 | 215.6987 | 395.1795 | 189.3659 | 0 | 105.5646 | 1832941.6866 | 118199.2431 | 1405508.7286 | 743249.3214 | 0 | 205616.9569 | 0 | 1679151.2153 | 4368807.0208 | 2981800.5617 | 13335274.7344 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 31087675.7764 | 56955440.4639 | 1778.2794 | 2.9382 | 10580.5418 | 19384.5119 | 215.6987 | 395.1795
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0595 | 8.3593 | 0.99667 | 4 | 8671.5058 | 15160.061 | 176.7804 | 309.0583 | 191.1687 | 0 | 83.618 | 2269088.1565 | 146071.2499 | 1790273.2333 | 980362.5323 | 0 | 244202.2498 | 0 | 2117698.9945 | 5509818.384 | 3760564.2625 | 16818079.0629 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 34570480.1049 | 60438244.7924 | 2371.3737 | 3.9867 | 8671.5058 | 15160.061 | 176.7804 | 309.0583
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.922 | 11.2513 | 1.3442 | 4 | 7238.9728 | 12050.0473 | 147.5763 | 245.6565 | 192.5504 | 0 | 106.013 | 2799286.3395 | 179840.5303 | 2270624.9663 | 1294223.6403 | 0 | 290942.7392 | 0 | 2665618.1041 | 6935391.5133 | 4733547.2159 | 21169475.0488 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 38921876.0907 | 64789640.7782 | 3162.2777 | 5.3767 | 7238.9728 | 12050.0473 | 147.5763 | 245.6565
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.348 | 15.0742 | 1.8036 | 4 | 6148.179 | 9733.6915 | 125.3389 | 198.4345 | 193.6039 | 0 | 90.1095 | 3443157.7915 | 220703.9164 | 2869267.7926 | 1708909.2715 | 0 | 347436.2 | 0 | 3349895.2391 | 8715740.2541 | 5948671.814 | 26603782.2793 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 44356183.3212 | 70223948.0087 | 4216.965 | 7.2145 | 6148.179 | 9733.6915 | 125.3389 | 198.4345
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8205 | 20.1154 | 2.4094 | 4 | 5306.4282 | 7990.4848 | 108.1787 | 162.8968 | 194.4051 | 0 | 105.9311 | 4224352.1766 | 270095.6205 | 3614167.1095 | 2255564.3895 | 0 | 415898.6611 | 0 | 4204230.4034 | 10938545.1033 | 7465781.7976 | 33388635.2616 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 51141036.3035 | 77008800.9911 | 5623.4133 | 9.6376 | 5306.4282 | 7990.4848 | 108.1787 | 162.8968
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.8559 | 26.6798 | 3.1983 | 4 | 4652.7559 | 6674.769 | 94.8527 | 136.0742 | 195.0001 | 0 | 85.7108 | 5161848.372 | 329135.3758 | 4530337.3078 | 2967473.0337 | 0 | 497558.7922 | 0 | 5259677.6238 | 13684602.2689 | 9340022.2389 | 41770655.0131 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 59523056.055 | 85390820.7425 | 7498.9421 | 12.7931 | 4652.7559 | 6674.769 | 94.8527 | 136.0742
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.048 | 35.0923 | 4.2086 | 4 | 4143.301 | 5679.918 | 84.4668 | 115.7928 | 195.3746 | 0 | 110.0906 | 6271717.2518 | 398744.9986 | 5640975.0586 | 3882071.625 | 0 | 594552.2714 | 0 | 6547343.8701 | 17034845.7051 | 11626632.2248 | 51996883.0054 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 69749284.0474 | 95617048.7349 | 10000 | 16.8342 | 4143.301 | 5679.918 | 84.4668 | 115.7928
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.7831 | 45.4697 | 5.4528 | 4 | 3751.6764 | 4937.6678 | 76.483 | 100.661 | 195.3986 | 0 | 122.0005 | 7541031.7317 | 478026.7735 | 6940042.7904 | 5021829.526 | 0 | 706993.8037 | 0 | 8068290.6039 | 20992037.1173 | 14327496.6758 | 64075749.0223 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 81828150.0643 | 107695914.7518 | 13335.2143 | 21.8111 | 3751.6764 | 4937.6678 | 76.483 | 100.661
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.0742 | 57.5626 | 6.8969 | 4 | 3459.252 | 4396.9074 | 70.5215 | 89.6369 | 194.883 | 0 | 114.0491 | 8920216.1994 | 563826.1991 | 8381023.1544 | 6381413.1294 | 0 | 833946.2712 | 0 | 9781365.7319 | 25449107.2003 | 17369538.5911 | 77680436.4768 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 95432837.5187 | 121300602.2063 | 17782.7941 | 27.5877 | 3459.252 | 4396.9074 | 70.5215 | 89.6369
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.2884 | 70.6277 | 8.4457 | 4 | 3250.7095 | 4016.4217 | 66.2701 | 81.8802 | 193.7113 | 0 | 128.662 | 10320624.6103 | 650623.3227 | 9871085.138 | 7910200.1044 | 0 | 972217.7293 | 0 | 11592652.8528 | 30161704.743 | 20585983.2482 | 92065091.7488 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 109817492.7907 | 135685257.4782 | 23713.7371 | 33.7826 | 3250.7095 | 4016.4217 | 66.2701 | 81.8802
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1326 | 83.7255 | 9.9825 | 4 | 3107.5537 | 3755.3843 | 63.3517 | 76.5586 | 192.0705 | 0 | 141.2058 | 11652508.3188 | 732904.5388 | 11310216.977 | 9519561.1644 | 0 | 1115765.7082 | 0 | 13389073.1158 | 34835621.7708 | 23776027.659 | 106331679.2529 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 124084080.2948 | 149951844.9823 | 31622.7766 | 39.9298 | 3107.5537 | 3755.3843 | 63.3517 | 76.5586
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.624 | 89.7653 | 10.8325 | 4 | 3006.0494 | 3603.0412 | 61.2824 | 73.4529 | 191.2132 | 0 | 174.2809 | 12246547.9169 | 769525.5008 | 11958360.1234 | 10288631.0808 | 0 | 1059528.3133 | 0 | 14165811.2447 | 36856535.0513 | 25155342.4986 | 112500281.7298 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 130252682.7717 | 156120447.4592 | 42169.6503 | 43.3302 | 3006.0494 | 3603.0412 | 61.2824 | 73.4529
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8445 | 93.6118 | 11.4407 | 4 | 2928.0977 | 3493.354 | 59.6932 | 71.2167 | 190.6128 | 0 | 200.9894 | 12618979.29 | 792461.7542 | 12366565.6751 | 10790557.9509 | 0 | 963337.2294 | 0 | 14637441.7408 | 38083620.8575 | 25992853.7754 | 116245818.2732 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 133998219.3151 | 159865984.0027 | 56234.1325 | 45.7629 | 2928.0977 | 3493.354 | 59.6932 | 71.2167
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.3159 | 96.5675 | 11.9252 | 4 | 2868.3434 | 3410.634 | 58.4751 | 69.5304 | 190.1221 | 0 | 266.5901 | 12902241.8488 | 809894.9115 | 12677964.1224 | 11183578.9332 | 0 | 870130.3206 | 0 | 14993085.9533 | 39008934.1456 | 26624399.1078 | 119070229.3432 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 136822630.3851 | 162690395.0726 | 74989.4209 | 47.7009 | 2868.3434 | 3410.634 | 58.4751 | 69.5304
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.3996 | 98.843 | 12.3077 | 4 | 2822.6795 | 3348.1191 | 57.5441 | 68.2559 | 189.7262 | 0 | 279.6347 | 13118656.9624 | 823207.3607 | 12916403.5026 | 11490656.1815 | 0 | 785788.3489 | 0 | 15262537.8189 | 39709992.6278 | 27102885.9272 | 121210128.7301 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 138962529.772 | 164830294.4595 | 100000 | 49.2307 | 2822.6795 | 3348.1191 | 57.5441 | 68.2559
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.2117 | 100.5222 | 12.5997 | 4 | 2787.8827 | 3301.1462 | 56.8348 | 67.2983 | 189.4231 | 0 | 367.4212 | 13277455.0581 | 832971.9791 | 13091648.7103 | 11720122.5661 | 0 | 710660.3628 | 0 | 15456814.8838 | 40215461.6989 | 27447878.9546 | 122753014.2137 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 140505415.2556 | 166373179.9432 | 133352.1432 | 50.3986 | 2787.8827 | 3301.1462 | 56.8348 | 67.2983
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.0692 | 101.766 | 12.8217 | 4 | 2761.4253 | 3265.8019 | 56.2954 | 66.5778 | 189.1926 | 0 | 329.9597 | 13394599.1242 | 840173.3222 | 13221079.2752 | 11891858.2809 | 0 | 646344.0026 | 0 | 15597681.062 | 40581966.5991 | 27698026.0799 | 123871727.7461 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 141624128.7881 | 167491893.4756 | 177827.941 | 51.2866 | 2761.4253 | 3265.8019 | 56.2954 | 66.5778
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.1887 | 102.6801 | 12.9888 | 4 | 2741.3467 | 3239.2308 | 55.8861 | 66.0361 | 189.0197 | 0 | 314.6348 | 13480434.0207 | 845448.9217 | 13315998.9366 | 12019086.239 | 0 | 592544.0637 | 0 | 15698869.7509 | 40845238.8109 | 27877714.7741 | 124675335.5177 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 142427736.5596 | 168295501.2471 | 237137.3706 | 51.9554 | 2741.3467 | 3239.2308 | 55.8861 | 66.0361
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.8166 | 103.3766 | 13.1169 | 4 | 2726.1273 | 3219.1513 | 55.5758 | 65.6268 | 188.886 | 0 | 324.4138 | 13545695.5646 | 849459.455 | 13388213.9312 | 12116424.1661 | 0 | 549218.2714 | 0 | 15775114.4414 | 41043611.8557 | 28013108.4534 | 125280846.139 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143033247.1809 | 168901011.8684 | 316227.766 | 52.4676 | 2726.1273 | 3219.1513 | 55.5758 | 65.6268
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.9218 | 103.8468 | 13.2082 | 4 | 2714.6122 | 3204.226 | 55.341 | 65.3225 | 188.7945 | 0 | 386.1308 | 13589673.0384 | 852161.7303 | 13436899.4843 | 12182426.3136 | 0 | 513076.9596 | 0 | 15823952.6353 | 41170678.8179 | 28099834.2661 | 125668703.2456 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143421104.2875 | 169288868.975 | 421696.5034 | 52.833 | 2714.6122 | 3204.226 | 55.341 | 65.3225
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.7307 | 104.1895 | 13.2762 | 4 | 2705.9121 | 3193.0209 | 55.1637 | 65.094 | 188.7272 | 0 | 401.3368 | 13621696.8609 | 854129.349 | 13472362.9759 | 12230701.7333 | 0 | 484308.3604 | 0 | 15858647.719 | 41260948.3089 | 28161445.0486 | 125944240.356 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143696641.398 | 169564406.0855 | 562341.3252 | 53.1047 | 2705.9121 | 3193.0209 | 55.1637 | 65.094
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.3102 | 104.4343 | 13.3261 | 4 | 2699.3469 | 3184.632 | 55.0298 | 64.923 | 188.6788 | 0 | 383.5357 | 13644556.2883 | 855533.8122 | 13497683.543 | 12265279.0361 | 0 | 461510.726 | 0 | 15882579.7282 | 41323214.4877 | 28203942.995 | 126134300.6166 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143886701.6585 | 169754466.346 | 749894.2093 | 53.3043 | 2699.3469 | 3184.632 | 55.0298 | 64.923
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.7318 | 104.612 | 13.363 | 4 | 2694.3984 | 3178.3427 | 54.929 | 64.7948 | 188.6434 | 0 | 384.1622 | 13661137.815 | 856552.5284 | 13516053.3313 | 12290421.9508 | 0 | 443703.2828 | 0 | 15899468.8742 | 41367156.5813 | 28233934.3768 | 126268428.7406 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144020829.7825 | 169888594.4701 | 1000000 | 53.4519 | 2694.3984 | 3178.3427 | 54.929 | 64.7948
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.0218 | 104.734 | 13.3895 | 4 | 2690.672 | 3173.6565 | 54.853 | 64.6993 | 188.619 | 0 | 379.3706 | 13672518.4903 | 857251.7023 | 13528662.845 | 12307716.0157 | 0 | 429688.2869 | 0 | 15910376.5626 | 41395536.149 | 28253304.0149 | 126355054.0667 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144107455.1086 | 169975219.7961 | 1333521.4322 | 53.5582 | 2690.672 | 3173.6565 | 54.853 | 64.6993
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.2434 | 104.8271 | 13.4097 | 4 | 2687.8683 | 3170.1279 | 54.7958 | 64.6273 | 188.6004 | 0 | 397.3774 | 13681199.4355 | 857785.0075 | 13538281.9271 | 12320922.4144 | 0 | 419028.226 | 0 | 15918714.6341 | 41417230.1006 | 28268110.5826 | 126421272.3278 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144173673.3697 | 170041438.0572 | 1778279.41 | 53.6387 | 2687.8683 | 3170.1279 | 54.7958 | 64.6273
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.4091 | 104.8967 | 13.4248 | 4 | 2685.7602 | 3167.4776 | 54.7529 | 64.5733 | 188.5864 | 0 | 386.8731 | 13687690.0592 | 858183.7468 | 13545474.4375 | 12330804.7752 | 0 | 410912.0795 | 0 | 15924895.3883 | 41433311.1551 | 28279086.2328 | 126470357.8743 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144222758.9163 | 170090523.6038 | 2371373.7057 | 53.699 | 2685.7602 | 3167.4776 | 54.7529 | 64.5733
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.2775 | 103.9909 | 13.3337 | 4 | 2683.9431 | 3168.9521 | 54.7158 | 64.6034 | 188.76 | 0 | 376.0821 | 13603143.7393 | 852989.4164 | 13451815.9095 | 12203459.0631 | 0 | 374351.0711 | 0 | 15789446.0877 | 41080899.8595 | 28038558.2822 | 125394663.4288 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143147064.4707 | 169014829.1582 | 3162277.6602 | 53.3346 | 2683.9431 | 3168.9521 | 54.7158 | 64.6034
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.228 | 104.3953 | 13.3817 | 4 | 2682.6903 | 3165.957 | 54.6903 | 64.5423 | 188.6825 | 0 | 550.9841 | 13640916.0121 | 855310.1609 | 13493651.0159 | 12260248.3553 | 0 | 380606.3555 | 0 | 15845985.4409 | 41228003.6586 | 28138959.6478 | 125843680.647 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143596081.6889 | 169463846.3765 | 4216965.0343 | 53.5269 | 2682.6903 | 3165.957 | 54.6903 | 64.5423
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.358 | 104.8744 | 13.4368 | 4 | 2681.754 | 3163.0412 | 54.6712 | 64.4829 | 188.5901 | 0 | 369.3201 | 13685609.7585 | 858055.948 | 13543169.1338 | 12327733.2609 | 0 | 390595.8143 | 0 | 15914013.927 | 41404999.8251 | 28259763.1683 | 126383940.8359 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144136341.8778 | 170004106.5653 | 5623413.2519 | 53.747 | 2681.754 | 3163.0412 | 54.6712 | 64.4829
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.0502 | 105.1668 | 13.4707 | 4 | 2681.0839 | 3161.1577 | 54.6575 | 64.4445 | 188.5333 | 0 | 377.075 | 13712861.6639 | 859730.0706 | 13573371.7384 | 12369050.4933 | 0 | 396124.2871 | 0 | 15955343.9188 | 41512531.9857 | 28333156.0775 | 126712170.2354 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144464571.2773 | 170332335.9648 | 7498942.0933 | 53.8829 | 2681.0839 | 3161.1577 | 54.6575 | 64.4445
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.1985 | 105.2293 | 13.4792 | 4 | 2680.5899 | 3160.3601 | 54.6475 | 64.4282 | 188.521 | 0 | 390.1743 | 13718681.2708 | 860087.566 | 13579822.3498 | 12377901.6458 | 0 | 395562.2846 | 0 | 15963501.4956 | 41533756.3272 | 28347642.1267 | 126776955.0664 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144529356.1084 | 170397120.7959 | 10000000 | 53.917 | 2680.5899 | 3160.3601 | 54.6475 | 64.4282
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.83292 | 0.19027 | 0.0091153 | 4 | 528561.2404 | 1256513.7674 | 10775.4358 | 25615.7327 | 122.3978 | 0 | 48.5019 | 126948.2481 | 5153.4539 | 90164.7317 | 56563.916 | 0 | 56293.0477 | 0 | 130698.125 | 340049.7115 | 232090.9154 | 1037962.1494 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19271911.9721 | 45813844.9528 | 100 | 0.036461 | 528561.2404 | 1256513.7674 | 10775.4358 | 25615.7327
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.29198 | 0.01944 | 4 | 252324.7446 | 593658.3925 | 5143.9812 | 12102.5293 | 135.1343 | 0 | 50.9563 | 181705.3244 | 8093.0607 | 125905.9129 | 69893.7708 | 0 | 62119.7289 | 0 | 174609.9411 | 454299.2493 | 310068.5726 | 1386695.5607 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19620645.3835 | 46162578.3641 | 133.3521 | 0.077759 | 252324.7446 | 593658.3925 | 5143.9812 | 12102.5293
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3936 | 0.44521 | 0.036316 | 4 | 138390.6023 | 321103.2922 | 2821.2796 | 6546.1249 | 147.2296 | 0 | 49.7892 | 256739.8813 | 12525.6181 | 175035.3851 | 89390.6901 | 0 | 69905.3913 | 0 | 235402.8167 | 612469.8413 | 418023.2517 | 1869492.8757 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20103442.6984 | 46645375.6791 | 177.8279 | 0.14527 | 138390.6023 | 321103.2922 | 2821.2796 | 6546.1249
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.64464 | 0.060237 | 4 | 85827.4641 | 195983.912 | 1749.7089 | 3995.3971 | 157.0887 | 0 | 285.6338 | 345880.1041 | 18269.8254 | 233823.902 | 114647.0336 | 0 | 77102.2048 | 0 | 307991.9973 | 801331.999 | 546925.5551 | 2445972.6213 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20679922.4441 | 47221855.4247 | 237.1374 | 0.24095 | 85827.4641 | 195983.912 | 1749.7089 | 3995.3971
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.92175 | 0.094879 | 4 | 56445.2938 | 126381.8314 | 1150.7137 | 2576.4646 | 165.7271 | 0 | 373.6236 | 459001.0752 | 26113.2451 | 309497.6466 | 148548.8731 | 0 | 86092.9275 | 0 | 401408.9693 | 1044383.7978 | 712813.4019 | 3187859.9363 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 21421809.7591 | 47963742.7398 | 316.2278 | 0.37951 | 56445.2938 | 126381.8314 | 1150.7137 | 2576.4646
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0128 | 1.3052 | 0.14485 | 4 | 38639.3485 | 84447.2859 | 787.7154 | 1721.5721 | 173.0505 | 0 | 496.5879 | 603167.6435 | 36978.1513 | 406659.5861 | 197188.7662 | 0 | 97315.2596 | 0 | 523110.6686 | 1361026.655 | 928928.6584 | 4154375.3888 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 22388325.2115 | 48930258.1922 | 421.6965 | 0.57942 | 38639.3485 | 84447.2859 | 787.7154 | 1721.5721
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 1.8294 | 0.21296 | 4 | 27702.6306 | 58861.6344 | 564.7556 | 1199.974 | 178.9523 | 0 | 79.4173 | 778646.1705 | 50309.0761 | 530982.2128 | 261334.0481 | 0 | 110510.3495 | 0 | 675394.9242 | 1757239.0503 | 1199351.7595 | 5363767.591 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 23597717.4137 | 50139650.3944 | 562.3413 | 0.85182 | 27702.6306 | 58861.6344 | 564.7556 | 1199.974
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.13 | 2.576 | 0.30324 | 4 | 20707.2446 | 42588.9368 | 422.1452 | 868.2331 | 183.7717 | 0 | 88.0155 | 990519.2207 | 64078.6981 | 698146.6715 | 341583.5166 | 0 | 128095.0807 | 0 | 866745.0432 | 2255092.8084 | 1539147.1793 | 6883408.2184 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 25117358.0412 | 51659291.0219 | 749.8942 | 1.213 | 20707.2446 | 42588.9368 | 422.1452 | 868.2331
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7185 | 3.5553 | 0.42151 | 4 | 15996.0931 | 31738.2789 | 326.102 | 647.0277 | 187.5175 | 0 | 72.682 | 1242174.1576 | 80290.0812 | 903415.4055 | 445688.3781 | 0 | 149021.3683 | 0 | 1100029.8624 | 2862052.0548 | 1953409.3367 | 8736080.6447 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 26970030.4674 | 53511963.4481 | 1000 | 1.686 | 15996.0931 | 31738.2789 | 326.102 | 647.0277
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8379 | 4.8462 | 0.577 | 4 | 12678.6851 | 24178.6239 | 258.4721 | 492.914 | 190.2128 | 0 | 75.3592 | 1544740.519 | 99729.774 | 1157450.1026 | 583609.5585 | 0 | 175217.3899 | 0 | 1388691.4642 | 3613090.33 | 2466008.3918 | 11028537.5299 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 29262487.3527 | 55804420.3333 | 1333.5214 | 2.308 | 12678.6851 | 24178.6239 | 258.4721 | 492.914
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6754 | 6.6295 | 0.79261 | 4 | 10161.2848 | 18533.0085 | 207.1515 | 377.8204 | 192.9879 | 0 | 80.9516 | 1926562.1837 | 124189.7432 | 1487208.5422 | 769384.0816 | 0 | 206865.8223 | 0 | 1760542.0455 | 4580569.2655 | 3126332.645 | 13981654.329 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 32215604.1518 | 58757537.1325 | 1778.2794 | 3.1704 | 10161.2848 | 18533.0085 | 207.1515 | 377.8204
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4079 | 8.9437 | 1.0722 | 4 | 8353.9753 | 14542.8161 | 170.3071 | 296.475 | 194.8052 | 0 | 89.6543 | 2380032.7521 | 153147.2798 | 1889725.8107 | 1012550.1877 | 0 | 244913.0303 | 0 | 2215343.9337 | 5763870.4859 | 3933960.0423 | 17593543.5225 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 35827493.3452 | 62369426.3259 | 2371.3737 | 4.2887 | 8353.9753 | 14542.8161 | 170.3071 | 296.475
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.3842 | 12.0301 | 1.4448 | 4 | 6985.5977 | 11578.2677 | 142.4109 | 236.0386 | 196.2086 | 0 | 101.6593 | 2935012.9458 | 188467.0711 | 2395521.9781 | 1336553.5036 | 0 | 291801.3658 | 0 | 2787469.1771 | 7252423.0104 | 4949927.727 | 22137176.779 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 40371126.6017 | 66913059.5824 | 3162.2777 | 5.7792 | 6985.5977 | 11578.2677 | 142.4109 | 236.0386
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.9548 | 16.1065 | 1.9371 | 4 | 5941.9961 | 9367.4955 | 121.1356 | 190.9691 | 197.2776 | 0 | 87.0196 | 3608575.4223 | 231178.7847 | 3025421.3555 | 1764308.2998 | 0 | 348358.4602 | 0 | 3501358.5058 | 9109816.6047 | 6217637.0207 | 27806654.4539 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 46040604.2767 | 72582537.2573 | 4216.965 | 7.7483 | 5941.9961 | 9367.4955 | 121.1356 | 190.9691
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5905 | 21.465 | 2.5843 | 4 | 5136.3873 | 7703.9907 | 104.7122 | 157.0563 | 198.0887 | 0 | 112.1792 | 4423485.2145 | 282656.4322 | 3806884.9316 | 2326397.8632 | 0 | 416393.0737 | 0 | 4389768.8309 | 11421278.0327 | 7795256.9411 | 34862121.3199 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 53096071.1427 | 79638004.1234 | 5623.4133 | 10.3372 | 5136.3873 | 7703.9907 | 104.7122 | 157.0563
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.8622 | 28.456 | 3.4285 | 4 | 4508.5334 | 6443.9059 | 91.9126 | 131.3677 | 198.6904 | 0 | 97.1276 | 5403644.3427 | 344325.4287 | 4770064.9394 | 3059757.5754 | 0 | 498105.36 | 0 | 5489600.082 | 14282813.3415 | 9748313.588 | 43596624.6576 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 61830574.4803 | 88372507.461 | 7498.9421 | 13.7141 | 4508.5334 | 6443.9059 | 91.9126 | 131.3677
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.3005 | 37.377 | 4.5054 | 4 | 4019.7267 | 5492.5089 | 81.9476 | 111.9722 | 199.0563 | 0 | 109.5862 | 6559426.0404 | 416744.3488 | 5932911.3637 | 3998471.4 | 0 | 594426.6545 | 0 | 6825772.1249 | 17759258.9105 | 12121059.1227 | 54208069.9654 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 72442019.7882 | 98983952.7689 | 10000 | 18.0216 | 4019.7267 | 5492.5089 | 81.9476 | 111.9722
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.3178 | 48.3565 | 5.8284 | 4 | 3643.8821 | 4782.355 | 74.2855 | 97.4948 | 199.0448 | 0 | 114.8407 | 7878863.7454 | 499074.7903 | 7290358.8223 | 5166490.8188 | 0 | 706285.1797 | 0 | 8401018.6091 | 21857727.1349 | 14918347.9009 | 66718167.0014 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 84952116.8242 | 111494049.8049 | 13335.2143 | 23.3136 | 3643.8821 | 4782.355 | 74.2855 | 97.4948
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.84 | 61.0739 | 7.355 | 4 | 3363.8132 | 4265.9871 | 68.5759 | 86.9679 | 198.46 | 0 | 116.9407 | 9304688.7274 | 587686.4555 | 8787573.2838 | 6552868.7811 | 0 | 831997.3757 | 0 | 10165277.7032 | 26447967.3986 | 18051281.201 | 80729340.9265 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 98963290.7492 | 125505223.7299 | 17782.7941 | 29.42 | 3363.8132 | 4265.9871 | 68.5759 | 86.9679
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.2032 | 74.7385 | 8.9833 | 4 | 3164.383 | 3903.0258 | 64.5102 | 79.5685 | 197.1902 | 0 | 128.7254 | 10745611.7175 | 676905.3351 | 10328092.2636 | 8105638.0946 | 0 | 968813.0368 | 0 | 12021773.5746 | 31278188.8362 | 21348006.5832 | 95473029.4416 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 113706979.2644 | 140248912.245 | 23713.7371 | 35.9334 | 3164.383 | 3903.0258 | 64.5102 | 79.5685
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.0421 | 88.3651 | 10.5921 | 4 | 3027.0151 | 3653.4737 | 61.7098 | 74.481 | 195.4661 | 0 | 150.0495 | 12109859.5795 | 761103.0951 | 11808896.3334 | 9730577.3231 | 0 | 1109834.1503 | 0 | 13852905.4877 | 36042418.4575 | 24599691.1949 | 110015285.6214 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 128249235.4442 | 154791168.4249 | 31622.7766 | 42.3682 | 3027.0151 | 3653.4737 | 61.7098 | 74.481
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.0003 | 95.3723 | 11.5449 | 4 | 2931.1385 | 3505.8911 | 59.7552 | 71.4723 | 194.4519 | 0 | 147.4532 | 12787994.4859 | 802864.8468 | 12552273.7266 | 10599485.6154 | 0 | 1073238.5365 | 0 | 14748184.3123 | 38371750.3121 | 26189508.0486 | 117125299.8841 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 135359249.7068 | 161901182.6875 | 42169.6503 | 46.1798 | 2931.1385 | 3505.8911 | 59.7552 | 71.4723
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.1696 | 99.3311 | 12.1717 | 4 | 2857.873 | 3403.0312 | 58.2616 | 69.3754 | 193.8173 | 0 | 215.0592 | 13164886.969 | 826050.393 | 12967396.8032 | 11104209.8921 | 0 | 974084.6609 | 0 | 15224285.2001 | 39610467.1604 | 27034957.7507 | 120906338.8294 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 139140288.6522 | 165682221.6328 | 56234.1325 | 48.6867 | 2857.873 | 3403.0312 | 58.2616 | 69.3754
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.5561 | 102.3501 | 12.6678 | 4 | 2801.7097 | 3325.5156 | 57.1166 | 67.7951 | 193.3028 | 0 | 233.7945 | 13449474.057 | 843546.1557 | 13281754.1982 | 11496139.284 | 0 | 878146.5458 | 0 | 15580133.4939 | 40536311.4262 | 27666865.4863 | 123732370.647 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 141966320.4698 | 168508253.4505 | 74989.4209 | 50.6713 | 2801.7097 | 3325.5156 | 57.1166 | 67.7951
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.5667 | 104.6731 | 13.0589 | 4 | 2758.8054 | 3266.9247 | 56.242 | 66.6007 | 192.8886 | 0 | 251.9973 | 13666839.7933 | 856902.8324 | 13522370.8361 | 11802664.7236 | 0 | 791741.3418 | 0 | 15849802.6156 | 41237935.1643 | 28145738.1044 | 125873995.4115 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 144107945.2343 | 170649878.215 | 100000 | 52.2356 | 2758.8054 | 3266.9247 | 56.242 | 66.6007
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.301 | 106.3764 | 13.356 | 4 | 2726.108 | 3222.9238 | 55.5754 | 65.7037 | 192.5736 | 0 | 298.369 | 13825361.145 | 866640.1562 | 13698124.3632 | 12030184.1499 | 0 | 714814.3883 | 0 | 16042698.439 | 41739810.5284 | 28488278.353 | 127405911.5232 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 145639861.3459 | 172181794.3266 | 133352.1432 | 53.4241 | 2726.108 | 3222.9238 | 55.5754 | 65.7037
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.1218 | 107.6479 | 13.5828 | 4 | 2701.2475 | 3189.7697 | 55.0686 | 65.0278 | 192.3323 | 0 | 310.9935 | 13943228.1816 | 873878.363 | 13828953.244 | 12201820.5354 | 0 | 649438.9398 | 0 | 16183954.5129 | 42107329.857 | 28739117.8465 | 128527721.4802 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 146761671.3029 | 173303604.2836 | 177827.941 | 54.3311 | 2701.2475 | 3189.7697 | 55.0686 | 65.0278
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.1776 | 108.5663 | 13.7517 | 4 | 2682.3767 | 3164.8963 | 54.6839 | 64.5207 | 192.1545 | 0 | 346.3945 | 14028115.3462 | 879090.2882 | 13923253.549 | 12326788.6919 | 0 | 594387.2117 | 0 | 16283137.6839 | 42365384.1227 | 28915245.1854 | 129315402.0789 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 147549351.9017 | 174091284.8824 | 237137.3706 | 55.0069 | 2682.3767 | 3164.8963 | 54.6839 | 64.5207
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.6929 | 109.2386 | 13.8782 | 4 | 2668.0773 | 3146.2009 | 54.3924 | 64.1396 | 192.0225 | 0 | 328.6733 | 14090129.5072 | 882897.3292 | 13992185.5534 | 12418834.9169 | 0 | 549312.1944 | 0 | 16354010.2054 | 42549779.8858 | 29041099.0826 | 129878248.6749 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 148112198.4977 | 174654131.4783 | 316227.766 | 55.5127 | 2668.0773 | 3146.2009 | 54.3924 | 64.1396
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.9498 | 109.7926 | 13.9791 | 4 | 2657.2498 | 3131.9215 | 54.1716 | 63.8485 | 191.9126 | 0 | 326.1581 | 14141152.1505 | 886029.2737 | 14048925.8075 | 12494738.5901 | 0 | 514788.8379 | 0 | 16413397.5173 | 42704293.4892 | 29146557.7918 | 130349883.4579 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 148583833.2807 | 175125766.2614 | 421696.5034 | 55.9164 | 2657.2498 | 3131.9215 | 54.1716 | 63.8485
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.7392 | 110.1386 | 14.0479 | 4 | 2649.0672 | 3121.4154 | 54.0048 | 63.6343 | 191.8429 | 0 | 345.1313 | 14172980.2738 | 887982.843 | 14084332.4028 | 12542308.9754 | 0 | 485554.1433 | 0 | 16447531.8689 | 42793104.0703 | 29207172.8383 | 130620967.4158 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 148854917.2386 | 175396850.2193 | 562341.3252 | 56.1914 | 2649.0672 | 3121.4154 | 54.0048 | 63.6343
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.3117 | 110.3888 | 14.0987 | 4 | 2642.8919 | 3113.5375 | 53.8789 | 63.4737 | 191.7923 | 0 | 349.5669 | 14195978.8101 | 889394.3921 | 14109922.3218 | 12576796.9319 | 0 | 462490.77 | 0 | 16471487.4581 | 42855431.5993 | 29249712.6576 | 130811214.9408 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149045164.7636 | 175587097.7443 | 749894.2093 | 56.3947 | 2642.8919 | 3113.5375 | 53.8789 | 63.4737
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.7092 | 110.562 | 14.1354 | 4 | 2638.2367 | 3107.6603 | 53.784 | 63.3539 | 191.7569 | 0 | 345.9587 | 14211897.0072 | 890371.346 | 14127636.8796 | 12600732.6056 | 0 | 444237.1623 | 0 | 16487201.2502 | 42896315.6631 | 29277616.8712 | 130936008.7852 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149169958.608 | 175711891.5887 | 1000000 | 56.5415 | 2638.2367 | 3107.6603 | 53.784 | 63.3539
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.989 | 110.6838 | 14.1621 | 4 | 2634.7309 | 3103.269 | 53.7126 | 63.2643 | 191.732 | 0 | 359.9949 | 14223079.515 | 891057.6374 | 14140082.6778 | 12617581.1475 | 0 | 429977.8535 | 0 | 16497693.7442 | 42923614.9801 | 29296249.216 | 131019336.7714 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149253286.5942 | 175795219.5749 | 1333521.4322 | 56.6484 | 2634.7309 | 3103.269 | 53.7126 | 63.2643
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.1935 | 110.7727 | 14.1819 | 4 | 2632.093 | 3099.9767 | 53.6588 | 63.1972 | 191.7137 | 0 | 330.3728 | 14231237.8172 | 891558.3187 | 14149163.3274 | 12629890.2832 | 0 | 419012.0595 | 0 | 16505136.1043 | 42942978.4746 | 29309465.1989 | 131078441.5838 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149312391.4065 | 175854324.3872 | 1778279.41 | 56.7276 | 2632.093 | 3099.9767 | 53.6588 | 63.1972
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.3398 | 110.8362 | 14.1964 | 4 | 2630.1095 | 3097.5141 | 53.6183 | 63.147 | 191.7006 | 0 | 316.2111 | 14237068.2388 | 891916.1316 | 14155653.2776 | 12638696.7005 | 0 | 410577.7719 | 0 | 16510225.727 | 42956220.6287 | 29318503.2411 | 131118861.7173 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149352811.5401 | 175894744.5207 | 2371373.7057 | 56.7858 | 2630.1095 | 3097.5141 | 53.6183 | 63.147
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.105 | 110.2937 | 14.1446 | 4 | 2628.3483 | 3097.4661 | 53.5824 | 63.146 | 191.8071 | 0 | 486.7257 | 14187245.2551 | 888858.3719 | 14100204.1491 | 12564215.1318 | 0 | 385112.7789 | 0 | 16428997.9178 | 42744882.5314 | 29174260.6472 | 130473776.7831 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 148707726.6059 | 175249659.5866 | 3162277.6602 | 56.5784 | 2628.3483 | 3097.4661 | 53.5824 | 63.146
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.5032 | 110.9072 | 14.2154 | 4 | 2627.1871 | 3093.968 | 53.5588 | 63.0747 | 191.6861 | 0 | 348.3349 | 14243589.611 | 892316.3435 | 14162912.6959 | 12648532.1384 | 0 | 397344.6982 | 0 | 16514431.24 | 42967162.5108 | 29325971.3005 | 131152260.5383 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149386210.3611 | 175928143.3418 | 4216965.0343 | 56.8617 | 2627.1871 | 3093.968 | 53.5588 | 63.0747
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.0561 | 111.1488 | 14.2448 | 4 | 2626.3576 | 3092.1769 | 53.5419 | 63.0382 | 191.638 | 0 | 350.7843 | 14265752.4636 | 893676.4261 | 14187586.619 | 12681856.0706 | 0 | 400123.4582 | 0 | 16547308.0646 | 43052701.2646 | 29384353.2576 | 131413357.6245 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149647307.4472 | 176189240.4279 | 5623413.2519 | 56.979 | 2626.3576 | 3092.1769 | 53.5419 | 63.0382
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.1 | 111.1678 | 14.2492 | 4 | 2625.7387 | 3091.4124 | 53.5292 | 63.0226 | 191.634 | 0 | 342.0345 | 14267493.4977 | 893783.2669 | 14189525.0985 | 12684498.156 | 0 | 397407.6468 | 0 | 16548755.9897 | 43056468.4686 | 29386924.4518 | 131424856.576 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149658806.3988 | 176200739.3794 | 7498942.0933 | 56.9968 | 2625.7387 | 3091.4124 | 53.5292 | 63.0226
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.1339 | 111.1824 | 14.2526 | 4 | 2625.2743 | 3090.8375 | 53.5198 | 63.0109 | 191.631 | 0 | 342.8473 | 14268835.9693 | 893865.6493 | 14191019.8342 | 12686535.2876 | 0 | 395375.7485 | 0 | 16549896.6707 | 43059436.2865 | 29388950.0485 | 131433915.4945 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149667865.3173 | 176209798.2979 | 10000000 | 57.0104 | 2625.2743 | 3090.8375 | 53.5198 | 63.0109
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85236 | 0.20152 | 0.010439 | 4 | 474155.4859 | 1126146.2135 | 9666.3009 | 22958.0138 | 124.7845 | 0 | 51.6856 | 133712.3497 | 5520.4611 | 94253.6338 | 57869.0901 | 0 | 56474.6223 | 0 | 135653.7612 | 352943.2602 | 240891.0273 | 1077318.2055 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 19798676.9 | 47022982.3011 | 100 | 0.041756 | 474155.4859 | 1126146.2135 | 9666.3009 | 22958.0138
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.31592 | 0.022263 | 4 | 226690.6454 | 532401.931 | 4621.3954 | 10853.7335 | 138.3912 | 0 | 58.2123 | 194737.7779 | 8881.52 | 133811.7195 | 72641.7485 | 0 | 63241.3245 | 0 | 184592.4953 | 480271.8076 | 327795.3773 | 1465973.7706 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20187332.4651 | 47411637.8661 | 133.3521 | 0.089052 | 226690.6454 | 532401.931 | 4621.3954 | 10853.7335
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.46785 | 0.039801 | 4 | 129754.0632 | 300757.0402 | 2645.2121 | 6131.3391 | 149.8293 | 0 | 58.7646 | 268642.5059 | 13372.5887 | 181808.1297 | 91857.3729 | 0 | 69378.7518 | 0 | 243773.1461 | 634247.7215 | 432887.1024 | 1935967.319 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20657326.0134 | 47881631.4145 | 177.8279 | 0.1592 | 129754.0632 | 300757.0402 | 2645.2121 | 6131.3391
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.69271 | 0.067195 | 4 | 79258.4635 | 180546.376 | 1615.791 | 3680.6821 | 160.4565 | 0 | 295.0335 | 368513.9903 | 20020.4144 | 247120.9054 | 119972.4844 | 0 | 77962.616 | 0 | 325100.2601 | 845844.1896 | 577306.0398 | 2581840.9001 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 21303199.5945 | 48527504.9956 | 237.1374 | 0.26878 | 79258.4635 | 180546.376 | 1615.791 | 3680.6821
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 0.9915 | 0.10567 | 4 | 52278.3227 | 116688.6933 | 1065.7643 | 2378.8568 | 169.2171 | 0 | 389.6999 | 489860.9052 | 28828.2138 | 327294.7357 | 156629.8577 | 0 | 87093.2661 | 0 | 424985.7216 | 1105725.671 | 754680.4909 | 3375098.8619 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 22096457.5564 | 49320762.9574 | 316.2278 | 0.42267 | 52278.3227 | 116688.6933 | 1065.7643 | 2378.8568
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0906 | 1.3883 | 0.15923 | 4 | 36248.1165 | 78993.1179 | 738.9669 | 1610.3816 | 176.413 | 0 | 518.7292 | 638809.3024 | 40718.2241 | 426173.4265 | 206366.8288 | 0 | 97270.6573 | 0 | 549641.9912 | 1430055.7141 | 976042.4096 | 4365078.5539 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 23086437.2483 | 50310742.6494 | 421.6965 | 0.6369 | 36248.1165 | 78993.1179 | 738.9669 | 1610.3816
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0311 | 1.9853 | 0.23298 | 4 | 26167.9676 | 55380.5138 | 533.4694 | 1129.0067 | 182.4515 | 0 | 81.3734 | 825086.5038 | 53398.644 | 566828.0052 | 272246.521 | 0 | 111669.2049 | 0 | 713399.2628 | 1856118.5435 | 1266839.0454 | 5665585.7306 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 24386944.4251 | 51611249.8261 | 562.3413 | 0.93194 | 26167.9676 | 55380.5138 | 533.4694 | 1129.0067
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2615 | 2.7752 | 0.3288 | 4 | 19733.8672 | 40433.8443 | 402.3016 | 824.2986 | 187.276 | 0 | 94.7098 | 1043703.2926 | 67508.1996 | 741010.2418 | 353982.6827 | 0 | 128874.9583 | 0 | 910680.9562 | 2369405.0418 | 1617167.6274 | 7232333.0005 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 25953691.6949 | 53177997.096 | 749.8942 | 1.3152 | 19733.8672 | 40433.8443 | 402.3016 | 824.2986
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9011 | 3.8261 | 0.45612 | 4 | 15291.1715 | 30212.7559 | 311.7312 | 615.9279 | 191.0743 | 0 | 85.9611 | 1307993.2653 | 84523.5081 | 958056.3505 | 462180.1674 | 0 | 150276.6733 | 0 | 1155581.6862 | 3006586.5052 | 2052057.0689 | 9177255.225 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 27898613.9195 | 55122919.3205 | 1000 | 1.8245 | 15291.1715 | 30212.7559 | 311.7312 | 615.9279
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0548 | 5.1989 | 0.62254 | 4 | 12159.5798 | 23092.4023 | 247.8895 | 470.7699 | 193.8962 | 0 | 75.4707 | 1623120.0388 | 104757.1239 | 1224368.8069 | 603574.0636 | 0 | 175792.145 | 0 | 1455328.7495 | 3786466.8772 | 2584341.4478 | 11557749.2527 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 30279107.9472 | 57503413.3482 | 1333.5214 | 2.4901 | 12159.5798 | 23092.4023 | 247.8895 | 470.7699
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9506 | 7.0849 | 0.85153 | 4 | 9787.4877 | 17780.2176 | 199.5312 | 362.4738 | 196.5971 | 0 | 94.1381 | 2019008.6115 | 130100.9041 | 1568380.3686 | 794299.345 | 0 | 207272.6219 | 0 | 1840434.1219 | 4788432.0603 | 3268203.2736 | 14616131.3069 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 33337490.0014 | 60561795.4024 | 1778.2794 | 3.4061 | 9787.4877 | 17780.2176 | 199.5312 | 362.4738
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.7757 | 9.5526 | 1.1509 | 4 | 8060.4655 | 13973.936 | 164.3235 | 284.8776 | 198.4419 | 0 | 95.7796 | 2493416.2806 | 160373.3836 | 1991967.411 | 1045416.7527 | 0 | 245451.7394 | 0 | 2315283.9713 | 6023893.9632 | 4111431.4085 | 18387234.9102 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 37108593.6047 | 64332899.0057 | 2371.3737 | 4.6038 | 8060.4655 | 13973.936 | 164.3235 | 284.8776
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.84 | 12.8209 | 1.5476 | 4 | 6755.3942 | 11153.2143 | 137.7178 | 227.3734 | 199.858 | 0 | 86.3301 | 3070260.8767 | 197056.2913 | 2520693.0149 | 1377679.3319 | 0 | 291657.6438 | 0 | 2908365.3918 | 7566970.1618 | 5164612.6211 | 23097295.3333 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 41818654.0277 | 69042959.4288 | 3162.2777 | 6.1904 | 6755.3942 | 11153.2143 | 137.7178 | 227.3734
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.5662 | 17.1632 | 2.0744 | 4 | 5752.794 | 9033.8546 | 117.2785 | 184.1673 | 200.9443 | 0 | 105.3006 | 3774776.473 | 241694.2547 | 3183200.4176 | 1818982.1419 | 0 | 348333.3997 | 0 | 3653124.8079 | 9504681.3913 | 6487140.3512 | 29011933.2373 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 47733291.9318 | 74957597.3328 | 4216.965 | 8.2974 | 5752.794 | 9033.8546 | 117.2785 | 184.1673
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.3869 | 22.8479 | 2.7666 | 4 | 4976.4258 | 7436.5542 | 101.4512 | 151.6042 | 201.7662 | 0 | 102.9519 | 4626217.9571 | 295870.5846 | 4001500.2879 | 2396337.7955 | 0 | 415899.8875 | 0 | 4576972.3399 | 11908343.1622 | 8127688.9002 | 36348830.9146 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 55070189.6091 | 82294495.0101 | 5623.4133 | 11.0662 | 4976.4258 | 7436.5542 | 101.4512 | 151.6042
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.8757 | 30.2616 | 3.6664 | 4 | 4373.6027 | 6229.9488 | 89.1618 | 127.0059 | 202.3723 | 0 | 113.018 | 5647431.0722 | 360062.6103 | 5010333.0184 | 3149713.2 | 0 | 497018.7005 | 0 | 5719177.8546 | 14880127.6129 | 10155992.8518 | 45419856.9207 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 64141215.6152 | 91365521.0163 | 7498.9421 | 14.6655 | 4373.6027 | 6229.9488 | 89.1618 | 127.0059
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.589 | 39.7211 | 4.8125 | 4 | 3904.3089 | 5318.5449 | 79.5946 | 108.4257 | 202.7281 | 0 | 115.2003 | 6850725.8529 | 435179.172 | 6228566.9648 | 4114270.728 | 0 | 592983.9686 | 0 | 7106473.4077 | 18489586.0686 | 12619522.4148 | 56437308.5775 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 75158667.2719 | 102382972.673 | 10000 | 19.2502 | 3904.3089 | 5318.5449 | 79.5946 | 108.4257
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.8595 | 51.287 | 6.2139 | 4 | 3543.3211 | 4638.6254 | 72.2354 | 94.5647 | 202.6777 | 0 | 117.224 | 8217772.8775 | 520493.0126 | 7641423.1198 | 5307515.0053 | 0 | 703458.0203 | 0 | 8732358.1939 | 22719804.7675 | 15506733.5992 | 69349558.5962 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 88070917.2907 | 115295222.6917 | 13335.2143 | 24.8555 | 3543.3211 | 4638.6254 | 72.2354 | 94.5647
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.6279 | 64.6112 | 7.8271 | 4 | 3273.1299 | 4142.6796 | 66.7272 | 84.4541 | 202.0203 | 0 | 135.6092 | 9692106.5986 | 612864.985 | 9191383.0129 | 6717881.409 | 0 | 827610.5683 | 0 | 10546320.1638 | 27439361.7185 | 18727928.1954 | 83755456.6515 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 102476815.3459 | 129701120.747 | 17782.7941 | 31.3085 | 3273.1299 | 4142.6796 | 66.7272 | 84.4541
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1252 | 78.895 | 9.5294 | 4 | 3084.4958 | 3798.7174 | 62.8816 | 77.442 | 200.6499 | 0 | 137.9205 | 11168670.3099 | 703042.5335 | 10785102.9608 | 8295878.7379 | 0 | 963245.6649 | 0 | 12447216.6807 | 32385104.5281 | 22103499.2878 | 98851760.7036 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 117573119.3981 | 144797424.7992 | 23713.7371 | 38.1175 | 3084.4958 | 3798.7174 | 62.8816 | 77.442
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9595 | 93.0421 | 11.209 | 4 | 2952.6056 | 3559.8038 | 60.1929 | 72.5714 | 198.8439 | 0 | 136.479 | 12564099.7171 | 789083.084 | 12306326.9036 | 9936224.125 | 0 | 1101783.7253 | 0 | 14312031.8465 | 37236971.0631 | 25414997.8938 | 113661518.3584 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 132382877.0529 | 159607182.4539 | 31622.7766 | 44.8359 | 2952.6056 | 3559.8038 | 60.1929 | 72.5714
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.389 | 101.0617 | 12.2697 | 4 | 2861.7859 | 3416.49 | 58.3414 | 69.6498 | 197.6603 | 0 | 174.793 | 13328312.0676 | 836098.5765 | 13147823.8495 | 10905609.7954 | 0 | 1085409.729 | 0 | 15328269.067 | 39881011.852 | 27219610.0618 | 121732144.9988 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 140453503.6933 | 167677809.0943 | 42169.6503 | 49.079 | 2861.7859 | 3416.49 | 58.3414 | 69.6498
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.483 | 105.1112 | 12.9122 | 4 | 2792.8598 | 3319.9646 | 56.9362 | 67.682 | 196.9937 | 0 | 204.8871 | 13707678.7658 | 859411.6846 | 13567627.135 | 11410295.1203 | 0 | 983271.0648 | 0 | 15806030.6705 | 41124049.5419 | 28068008.8271 | 125526372.81 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 144247731.5045 | 171472036.9055 | 56234.1325 | 51.6488 | 2792.8598 | 3319.9646 | 56.9362 | 67.682
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.7887 | 108.1879 | 13.4188 | 4 | 2740.0266 | 3247.2296 | 55.8591 | 66.1992 | 196.4559 | 0 | 223.9235 | 13993162.6333 | 876944.3521 | 13884417.0391 | 11800644.4197 | 0 | 884951.346 | 0 | 16161646.7182 | 42049289.5512 | 28699504.1452 | 128350560.2048 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 147071918.8993 | 174296224.3004 | 74989.4209 | 53.6754 | 2740.0266 | 3247.2296 | 55.8591 | 66.1992
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.6607 | 110.5199 | 13.8141 | 4 | 2699.6783 | 3192.3686 | 55.0366 | 65.0808 | 196.0296 | 0 | 256.2286 | 14208027.5364 | 890133.866 | 14123330.5332 | 12101599.5838 | 0 | 795899.7804 | 0 | 16426406.6069 | 42738140.4719 | 29169659.053 | 130453197.4316 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 149174556.1261 | 176398861.5271 | 100000 | 55.2564 | 2699.6783 | 3192.3686 | 55.0366 | 65.0808
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.4339 | 112.2966 | 14.121 | 4 | 2668.9238 | 3150.9064 | 54.4096 | 64.2355 | 195.6933 | 0 | 283.5547 | 14370872.9461 | 900126.6715 | 14304676.6141 | 12333550.3 | 0 | 718912.9267 | 0 | 16624974.3887 | 43254773.1083 | 29522271.4432 | 132030158.3986 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 150751517.093 | 177975822.4941 | 133352.1432 | 56.484 | 2668.9238 | 3150.9064 | 54.4096 | 64.2355
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.1787 | 113.5733 | 14.3498 | 4 | 2645.5395 | 3119.8358 | 53.9329 | 63.6021 | 195.445 | 0 | 326.4388 | 14487440.415 | 907277.8615 | 14434630.8683 | 12502015.574 | 0 | 652181.0903 | 0 | 16763582.8655 | 43615403.9324 | 29768409.3908 | 133130941.9978 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 151852300.6923 | 179076606.0933 | 177827.941 | 57.3994 | 2645.5395 | 3119.8358 | 53.9329 | 63.6021
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.225 | 114.5165 | 14.5225 | 4 | 2627.7902 | 3096.4476 | 53.5711 | 63.1253 | 195.2579 | 0 | 339.7442 | 14573323.8249 | 912545.6748 | 14530453.3629 | 12627497.3291 | 0 | 596727.8996 | 0 | 16863813.7556 | 43876184.1482 | 29946397.2466 | 133926943.2418 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 152648301.9362 | 179872607.3373 | 237137.3706 | 58.09 | 2627.7902 | 3096.4476 | 53.5711 | 63.1253
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.6944 | 115.1891 | 14.6497 | 4 | 2614.3382 | 3078.9253 | 53.2968 | 62.7681 | 195.1225 | 0 | 331.4734 | 14634448.4903 | 916294.368 | 14598690.9497 | 12717541.3942 | 0 | 550862.4962 | 0 | 16932956.7024 | 44056079.9126 | 30069179.8022 | 134476054.1156 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 153197412.81 | 180421718.2111 | 316227.766 | 58.5989 | 2614.3382 | 3078.9253 | 53.2968 | 62.7681
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.764 | 115.6763 | 14.7441 | 4 | 2604.1587 | 3065.7724 | 53.0893 | 62.4999 | 195.0233 | 0 | 332.0306 | 14678656.4828 | 919005.3273 | 14648063.4967 | 12783061.9276 | 0 | 513819.192 | 0 | 16981616.5063 | 44182682.7409 | 30155588.834 | 134862494.5075 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 153583853.202 | 180808158.603 | 421696.5034 | 58.9764 | 2604.1587 | 3065.7724 | 53.0893 | 62.4999
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.6675 | 116.086 | 14.82 | 4 | 2596.4624 | 3055.7104 | 52.9324 | 62.2948 | 194.9395 | 0 | 338.5712 | 14715796.3054 | 921282.68 | 14689555.1976 | 12838191.0171 | 0 | 485913.7973 | 0 | 17023788.209 | 44292404.8607 | 30230476.4353 | 135197408.5024 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 153918767.1968 | 181143072.5979 | 562341.3252 | 59.2802 | 2596.4624 | 3055.7104 | 52.9324 | 62.2948
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.2151 | 116.3331 | 14.8708 | 4 | 2590.6527 | 3048.3332 | 52.814 | 62.1444 | 194.8882 | 0 | 385.6584 | 14738177.6081 | 922654.9913 | 14714564.785 | 12871537.9519 | 0 | 462427.653 | 0 | 17046651.5658 | 44351890.6253 | 30271076.692 | 135378981.8724 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154100340.5669 | 181324645.9679 | 749894.2093 | 59.4832 | 2590.6527 | 3048.3332 | 52.814 | 62.1444
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.5977 | 116.5054 | 14.9076 | 4 | 2586.2727 | 3042.8239 | 52.7247 | 62.0321 | 194.8523 | 0 | 398.2013 | 14753770.7662 | 923611.0545 | 14731991.6304 | 12894833.4857 | 0 | 443896.5824 | 0 | 17061760.3724 | 44391200.6408 | 30297906.5853 | 135498971.1177 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154220329.8121 | 181444635.2132 | 1000000 | 59.6303 | 2586.2727 | 3042.8239 | 52.7247 | 62.0321
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.8756 | 116.6302 | 14.9348 | 4 | 2582.9739 | 3038.694 | 52.6574 | 61.9479 | 194.8261 | 0 | 372.3145 | 14765069.7682 | 924303.8135 | 14744620.6525 | 12911744.2378 | 0 | 429541.1908 | 0 | 17072359.0685 | 44418776.2738 | 30316727.5215 | 135583142.5266 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154304501.2211 | 181528806.6221 | 1333521.4322 | 59.7391 | 2582.9739 | 3038.694 | 52.6574 | 61.9479
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.0628 | 116.7142 | 14.9542 | 4 | 2580.4916 | 3035.6212 | 52.6068 | 61.8852 | 194.8084 | 0 | 393.539 | 14772666.9339 | 924769.5994 | 14753112.7071 | 12923138.0417 | 0 | 418294.895 | 0 | 17078873.0491 | 44435724.3151 | 30328294.9079 | 135634874.4492 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154356233.1436 | 181580538.5447 | 1778279.41 | 59.8166 | 2580.4916 | 3035.6212 | 52.6068 | 61.8852
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.587 | 116.0434 | 14.8901 | 4 | 2578.3957 | 3035.483 | 52.5641 | 61.8824 | 194.9425 | 0 | 593.4597 | 14711932.1919 | 921045.746 | 14685237.7499 | 12833130.8303 | 0 | 386885.4963 | 0 | 16979910.4856 | 44178244.025 | 30152559.3192 | 134848945.8443 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 153570304.5387 | 180794609.9398 | 2371373.7057 | 59.5604 | 2578.3957 | 3035.483 | 52.5641 | 61.8824
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.399 | 116.8656 | 14.9853 | 4 | 2576.936 | 3031.1206 | 52.5343 | 61.7935 | 194.7771 | 0 | 391.1666 | 14786359.1141 | 925609.0577 | 14768418.975 | 12943611.2998 | 0 | 402859.5072 | 0 | 17092474.602 | 44471112.7657 | 30352448.2526 | 135742893.5741 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154464252.2685 | 181688557.6696 | 3162277.6602 | 59.9411 | 2576.936 | 3031.1206 | 52.5343 | 61.7935
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.8548 | 117.0713 | 15.0119 | 4 | 2575.8999 | 3029.2796 | 52.5132 | 61.756 | 194.7351 | 0 | 373.3984 | 14804954.546 | 926749.0981 | 14789209.0849 | 12971385.274 | 0 | 403010.5127 | 0 | 17119170.3211 | 44540569.5509 | 30399853.9357 | 135954902.3234 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154676261.0178 | 181900566.4189 | 4216965.0343 | 60.0475 | 2575.8999 | 3029.2796 | 52.5132 | 61.756
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.913 | 117.0972 | 15.0179 | 4 | 2575.1242 | 3028.3218 | 52.4974 | 61.7364 | 194.7295 | 0 | 367.5294 | 14807301.8242 | 926893.0012 | 14791833.6054 | 12974923.0879 | 0 | 399384.2754 | 0 | 17121130.9597 | 44545670.7304 | 30403335.5955 | 135970473.0797 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154691831.7742 | 181916137.1752 | 5623413.2519 | 60.0716 | 2575.1242 | 3028.3218 | 52.4974 | 61.7364
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.9667 | 117.1213 | 15.0229 | 4 | 2574.542 | 3027.5881 | 52.4855 | 61.7215 | 194.7245 | 0 | 354.8321 | 14809473.4279 | 927026.1339 | 14794261.7441 | 12978191.1254 | 0 | 396784.9128 | 0 | 17123237.5642 | 44551151.683 | 30407076.4582 | 135987203.0494 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154708561.7438 | 181932867.1449 | 7498942.0933 | 60.0917 | 2574.542 | 3027.5881 | 52.4855 | 61.7215
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.9861 | 117.1299 | 15.0257 | 4 | 2574.105 | 3027.0684 | 52.4766 | 61.7109 | 194.7226 | 0 | 360.4353 | 14810251.5419 | 927073.837 | 14795131.7878 | 12979372.1599 | 0 | 394553.9325 | 0 | 17123489.4711 | 44551807.0931 | 30407523.7891 | 135989203.6124 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154710562.3068 | 181934867.7079 | 10000000 | 60.1027 | 2574.105 | 3027.0684 | 52.4766 | 61.7109
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.21866 | 0.012241 | 4 | 415684.8521 | 985788.7378 | 8474.298 | 20096.6368 | 127.9387 | 0 | 54.2535 | 143739.2896 | 6071.4563 | 100391.2401 | 59998.485 | 0 | 57607.7469 | 0 | 143445.205 | 373214.9987 | 254726.9054 | 1139195.327 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20353822.984 | 48268704.9326 | 100 | 0.048965 | 415684.8521 | 985788.7378 | 8474.298 | 20096.6368
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.33902 | 0.025184 | 4 | 206039.9931 | 483145.877 | 4200.4039 | 9849.5822 | 141.4319 | 0 | 45.2159 | 207310.2555 | 9673.9493 | 141290.602 | 75405.1465 | 0 | 63945.6197 | 0 | 194073.9734 | 504940.6688 | 344632.382 | 1541272.5972 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20755900.2542 | 48670782.2028 | 133.3521 | 0.10074 | 206039.9931 | 483145.877 | 4200.4039 | 9849.5822
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.49933 | 0.044292 | 4 | 119917.2881 | 277478.6246 | 2444.6761 | 5656.7771 | 152.882 | 0 | 65.7345 | 284711.3984 | 14526.506 | 191136.113 | 95603.001 | 0 | 69739.5072 | 0 | 255729.445 | 665355.5585 | 454118.8404 | 2030920.3694 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21245548.0264 | 49160429.975 | 177.8279 | 0.17717 | 119917.2881 | 277478.6246 | 2444.6761 | 5656.7771
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.73208 | 0.073518 | 4 | 74488.0303 | 169413.938 | 1518.5393 | 3453.7323 | 163.4307 | 0 | 297.5217 | 387456.1889 | 21595.0842 | 257790.6011 | 124101.366 | 0 | 77595.0486 | 0 | 338729.9326 | 881305.8016 | 601509.3186 | 2690083.3416 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21904710.9986 | 49819592.9472 | 237.1374 | 0.29407 | 74488.0303 | 169413.938 | 1518.5393 | 3453.7323
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 1.0533 | 0.11615 | 4 | 48979.8922 | 109063.9633 | 998.5214 | 2223.4164 | 172.4501 | 0 | 394.3679 | 518071.648 | 31571.4144 | 342694.5019 | 164066.6576 | 0 | 86958.9094 | 0 | 445911.6212 | 1160170.5693 | 791840.2527 | 3541285.5744 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22755913.2314 | 50670795.1801 | 316.2278 | 0.4646 | 48979.8922 | 109063.9633 | 998.5214 | 2223.4164
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1684 | 1.4979 | 0.17475 | 4 | 34082.385 | 74018.8655 | 694.8155 | 1508.9747 | 179.7716 | 0 | 521.781 | 677186.9038 | 43814.7008 | 452453.0082 | 216820.8209 | 0 | 97606.1906 | 0 | 580273.8335 | 1509753.4842 | 1030437.7753 | 4608346.7173 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 23822974.3744 | 51737856.323 | 421.6965 | 0.69898 | 34082.385 | 74018.8655 | 694.8155 | 1508.9747
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1238 | 2.1328 | 0.2521 | 4 | 24943.3448 | 52625.9724 | 508.5038 | 1072.8516 | 185.8479 | 0 | 79.1648 | 867613.8339 | 56145.9571 | 600277.6434 | 281348.9172 | 0 | 111792.5345 | 0 | 747699.7656 | 1945361.4157 | 1327749.1394 | 5937989.2068 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 25152616.8638 | 53067498.8125 | 562.3413 | 1.0084 | 24943.3448 | 52625.9724 | 508.5038 | 1072.8516
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3884 | 2.9755 | 0.35468 | 4 | 18882.1293 | 38558.0217 | 384.9377 | 786.0574 | 190.7605 | 0 | 77.255 | 1096062.7779 | 70882.7004 | 783491.3141 | 365811.4205 | 0 | 129181.0624 | 0 | 953717.4174 | 2481377.0857 | 1693590.8482 | 7574114.6266 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 26788742.2837 | 54703624.2323 | 749.8942 | 1.4187 | 18882.1293 | 38558.0217 | 384.9377 | 786.0574
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0669 | 4.0916 | 0.49048 | 4 | 14685.1392 | 28913.3774 | 299.3764 | 589.4383 | 194.5927 | 0 | 78.1634 | 1371224.4904 | 88588.0309 | 1010886.7914 | 477184.4035 | 0 | 150559.552 | 0 | 1208392.8746 | 3143990.3842 | 2145838.0397 | 9596664.5666 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 28811292.2237 | 56726174.1723 | 1000 | 1.9619 | 14685.1392 | 28913.3774 | 299.3764 | 589.4383
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2789 | 5.5707 | 0.67075 | 4 | 11672.712 | 22077.1391 | 237.964 | 450.0723 | 197.6883 | 0 | 78.8991 | 1704087.7104 | 109947.003 | 1293933.8119 | 623735.0814 | 0 | 175964.3098 | 0 | 1523990.4875 | 3965110.6349 | 2706269.4832 | 12103038.5222 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 31317666.1792 | 59232548.1278 | 1333.5214 | 2.683 | 11672.712 | 22077.1391 | 237.964 | 450.0723
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2406 | 7.5598 | 0.9131 | 4 | 9440.6484 | 17083.5664 | 192.4604 | 348.2716 | 200.2088 | 0 | 87.3952 | 2113616.4975 | 136146.0555 | 1651938.8523 | 819761.1409 | 0 | 207503.7226 | 0 | 1922296.8448 | 5001422.0729 | 3413573.3337 | 15266258.5201 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 34480886.1771 | 62395768.1258 | 1778.2794 | 3.6524 | 9440.6484 | 17083.5664 | 192.4604 | 348.2716
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.1506 | 10.1741 | 1.233 | 4 | 7785.9697 | 13445.9927 | 158.7275 | 274.1147 | 202.0739 | 0 | 89.9177 | 2608617.1953 | 168010.2634 | 2094757.0168 | 1077636.6578 | 0 | 245270.2977 | 0 | 2415773.6581 | 6285347.5151 | 4289878.83 | 19185291.4342 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 38399919.0912 | 66314801.0399 | 2371.3737 | 4.9319 | 7785.9697 | 13445.9927 | 158.7275 | 274.1147
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3394 | 13.6578 | 1.6563 | 4 | 6537.7643 | 10751.1588 | 133.2812 | 219.1769 | 203.5091 | 0 | 107.7907 | 3210805.5956 | 205974.8211 | 2651490.3367 | 1421128.573 | 0 | 291634.2821 | 0 | 3034603.1073 | 7895414.8025 | 5388782.8373 | 24099834.3556 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 43314462.0126 | 71229343.9613 | 3162.2777 | 6.6253 | 6537.7643 | 10751.1588 | 133.2812 | 219.1769
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1922 | 18.2529 | 2.2165 | 4 | 5577.1611 | 8725.7637 | 113.698 | 177.8865 | 204.6049 | 0 | 81.8775 | 3943108.7871 | 252335.6527 | 3343870.5541 | 1873890.5267 | 0 | 347496.311 | 0 | 3806673.7143 | 9904184.1484 | 6759809.1919 | 30231368.8862 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 49445996.5432 | 77360878.4919 | 4216.965 | 8.8658 | 5577.1611 | 8725.7637 | 113.698 | 177.8865
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.1984 | 24.2925 | 2.9527 | 4 | 4832.4971 | 7195.973 | 98.517 | 146.6996 | 205.4367 | 0 | 100.6961 | 4829486.9074 | 308231.6445 | 4203026.7153 | 2468742.4668 | 0 | 414802.3699 | 0 | 4767473.1405 | 12403987.1684 | 8465976.1189 | 37861726.5318 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 57076354.1888 | 84991236.1374 | 5623.4133 | 11.8109 | 4832.4971 | 7195.973 | 98.517 | 146.6996
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.9279 | 32.1538 | 3.911 | 4 | 4250.9641 | 6035.3571 | 86.6617 | 123.0389 | 206.0468 | 0 | 111.2604 | 5893690.607 | 375067.7476 | 5259818.0178 | 3243406.8857 | 0 | 495435.9712 | 0 | 5954293.4994 | 15491850.2919 | 10573506.1499 | 47287069.1705 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 66501696.8275 | 94416578.7761 | 7498.9421 | 15.6439 | 4250.9641 | 6035.3571 | 86.6617 | 123.0389
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.8996 | 42.1402 | 5.1278 | 4 | 3798.116 | 5159.0712 | 77.4297 | 105.1746 | 206.3893 | 0 | 105.4146 | 7143740.5819 | 453246.6119 | 6530432.8922 | 4231259.3971 | 0 | 590189.3927 | 0 | 7390058.8615 | 19227417.2482 | 13123107.3558 | 58689452.3412 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 77904079.9982 | 105818961.9468 | 10000 | 20.5112 | 3798.116 | 5159.0712 | 77.4297 | 105.1746
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.4453 | 54.3187 | 6.6093 | 4 | 3450.9166 | 4506.8082 | 70.3516 | 91.8774 | 206.2959 | 0 | 119.0807 | 8559075.5885 | 541391.6534 | 8000999.5298 | 5451337.0624 | 0 | 699457.9553 | 0 | 9068382.0979 | 23594070.0377 | 16103437.6104 | 72018151.5353 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 91232779.1923 | 119147661.141 | 13335.2143 | 26.4373 | 3450.9166 | 4506.8082 | 70.3516 | 91.8774
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.4527 | 68.3003 | 8.3033 | 4 | 3192.9163 | 4033.3912 | 65.0919 | 82.2261 | 205.5605 | 0 | 124.0094 | 10076911.2595 | 635539.6901 | 9609984.1158 | 6890299.5025 | 0 | 822558.2228 | 0 | 10933764.1884 | 28447411.5948 | 19415942.9493 | 86832411.5233 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 106047039.1803 | 133961921.1289 | 17782.7941 | 33.2132 | 3192.9163 | 4033.3912 | 65.0919 | 82.2261
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0548 | 83.107 | 10.085 | 4 | 3010.1825 | 3702.1696 | 61.3666 | 75.4737 | 204.0896 | 0 | 124.607 | 11591006.1126 | 729110.4369 | 11243326.6063 | 8483485.7977 | 0 | 955430.4727 | 0 | 12870920.1762 | 33487494.1098 | 22855902.8292 | 102216676.5415 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 121431304.1985 | 149346186.1472 | 23713.7371 | 40.3402 | 3010.1825 | 3702.1696 | 61.3666 | 75.4737
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.8742 | 97.7105 | 11.8383 | 4 | 2881.7371 | 3471.2409 | 58.7481 | 70.7659 | 202.2067 | 0 | 141.1066 | 13018059.7007 | 818273.5551 | 12796676.2432 | 10130713.6262 | 0 | 1090716.2108 | 0 | 14763231.341 | 38410899.5943 | 26216228.2381 | 117244798.5095 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 136459426.1665 | 164374308.1151 | 31622.7766 | 47.3532 | 2881.7371 | 3471.2409 | 58.7481 | 70.7659
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.7749 | 106.8269 | 13.0066 | 4 | 2797.1941 | 3333.7446 | 57.0246 | 67.9629 | 200.8392 | 0 | 161.6269 | 13867164.6582 | 869207.4906 | 13744510.531 | 11206033.561 | 0 | 1095602.7229 | 0 | 15905182.3958 | 41382021.9924 | 28244080.3254 | 126313803.6773 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 145528431.3343 | 173443313.2829 | 42169.6503 | 52.0266 | 2797.1941 | 3333.7446 | 57.0246 | 67.9629
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.6593 | 110.8888 | 13.6563 | 4 | 2732.3219 | 3243.3483 | 55.7021 | 66.12 | 200.1527 | 0 | 207.4623 | 14241901.8956 | 892212.7701 | 14161033.9397 | 11701102.5829 | 0 | 988939.5499 | 0 | 16374224.3879 | 42602373.042 | 29076994.9924 | 130038783.1604 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 149253410.8174 | 177168292.766 | 56234.1325 | 54.6251 | 2732.3219 | 3243.3483 | 55.7021 | 66.12
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.9487 | 114.0519 | 14.1756 | 4 | 2682.6286 | 3174.9329 | 54.689 | 64.7253 | 199.5865 | 0 | 226.8206 | 14531040.9899 | 909952.2835 | 14483269.1936 | 12094277.7877 | 0 | 889508.2681 | 0 | 16734138.9239 | 43538796.836 | 29716123.4734 | 132897107.756 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 152111735.413 | 180026617.3616 | 74989.4209 | 56.7025 | 2682.6286 | 3174.9329 | 54.689 | 64.7253
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.7734 | 116.4311 | 14.5784 | 4 | 2644.6825 | 3123.3845 | 53.9154 | 63.6744 | 199.141 | 0 | 284.3631 | 14747049.6724 | 923198.9674 | 14724479.9088 | 12395103.1613 | 0 | 799301.9876 | 0 | 16999762.1421 | 44229893.9629 | 30187811.4631 | 135006601.2657 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 154221228.9227 | 182136110.8713 | 100000 | 58.3137 | 2644.6825 | 3123.3845 | 53.9154 | 63.6744
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.5077 | 118.2432 | 14.8909 | 4 | 2615.7615 | 3084.4198 | 53.3258 | 62.8801 | 198.79 | 0 | 310.5899 | 14910734.6826 | 933233.501 | 14907529.9356 | 12627034.4328 | 0 | 721514.8006 | 0 | 17199018.4676 | 44748318.0488 | 30541646.5543 | 136589030.4234 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 155803658.0804 | 183718540.029 | 133352.1432 | 59.5634 | 2615.7615 | 3084.4198 | 53.3258 | 62.8801
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.2191 | 119.5422 | 15.1233 | 4 | 2593.7669 | 3055.2232 | 52.8774 | 62.2849 | 198.5313 | 0 | 338.7421 | 15027633.3908 | 940398.0662 | 15038398.3149 | 12794952.9419 | 0 | 654178.0022 | 0 | 17337668.6792 | 45109057.4585 | 30787858.6139 | 137690145.4676 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 156904773.1246 | 184819655.0733 | 177827.941 | 60.493 | 2593.7669 | 3055.2232 | 52.8774 | 62.2849
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.205 | 120.4849 | 15.2967 | 4 | 2577.072 | 3033.2961 | 52.5371 | 61.8378 | 198.3398 | 0 | 332.4152 | 15112252.0515 | 945583.3092 | 15133201.2226 | 12917846.5498 | 0 | 597854.0127 | 0 | 17435627.4868 | 45363926.1817 | 30961811.7545 | 138468102.5686 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 157682730.2256 | 185597612.1742 | 237137.3706 | 61.1868 | 2577.072 | 3033.2961 | 52.5371 | 61.8378
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.6755 | 121.1783 | 15.4267 | 4 | 2564.419 | 3016.7984 | 52.2792 | 61.5015 | 198.197 | 0 | 382.8502 | 15174370.1594 | 949389.2783 | 15202833.8709 | 13008798.4418 | 0 | 551943.1902 | 0 | 17506060.6269 | 45547178.7643 | 31086885.4076 | 139027459.7394 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 158242087.3964 | 186156969.3451 | 316227.766 | 61.7068 | 2564.419 | 3016.7984 | 52.2792 | 61.5015
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.7085 | 121.6628 | 15.5212 | 4 | 2554.8427 | 3004.4686 | 52.0839 | 61.2502 | 198.096 | 0 | 399.1414 | 15217717.0291 | 952044.8909 | 15251443.6434 | 13072660.2503 | 0 | 514387.7629 | 0 | 17553218.8949 | 45669874.9041 | 31170628.0442 | 139401975.4197 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 158616603.0767 | 186531485.0253 | 421696.5034 | 62.0847 | 2554.8427 | 3004.4686 | 52.0839 | 61.2502
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.4466 | 122.0077 | 15.5904 | 4 | 2547.6053 | 2995.2334 | 51.9364 | 61.0619 | 198.0235 | 0 | 373.6173 | 15248540.3725 | 953933.1371 | 15286018.9137 | 13118278.8807 | 0 | 484324.6769 | 0 | 17585527.4325 | 45753935.0918 | 31228000.8495 | 139658559.3546 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 158873187.0117 | 186788068.9603 | 562341.3252 | 62.3618 | 2547.6053 | 2995.2334 | 51.9364 | 61.0619
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.1628 | 122.3415 | 15.6507 | 4 | 2542.1394 | 2988.0433 | 51.825 | 60.9153 | 197.9534 | 0 | 393.2878 | 15278355.4683 | 955759.5213 | 15319470.7461 | 13162365.1575 | 0 | 463014.3685 | 0 | 17619796.452 | 45843096.051 | 31288855.0362 | 139930712.8009 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159145340.458 | 187060222.4066 | 749894.2093 | 62.6029 | 2542.1394 | 2988.0433 | 51.825 | 60.9153
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.5332 | 122.5131 | 15.6876 | 4 | 2538.0176 | 2982.874 | 51.7409 | 60.8099 | 197.9167 | 0 | 379.6667 | 15293675.149 | 956697.9227 | 15336661.9438 | 13185101.7632 | 0 | 444304.3107 | 0 | 17634412.0249 | 45881122.7734 | 31314809.0557 | 140046784.9434 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159261412.6004 | 187176294.549 | 1000000 | 62.7503 | 2538.0176 | 2982.874 | 51.7409 | 60.8099
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.8038 | 122.6383 | 15.7149 | 4 | 2534.913 | 2978.9962 | 51.6776 | 60.7309 | 197.8898 | 0 | 371.4459 | 15304844.3272 | 957382.0707 | 15349196.8261 | 13201707.597 | 0 | 429838.6273 | 0 | 17644758.0849 | 45908041.0993 | 31333181.3662 | 140128949.9987 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159343577.6557 | 187258459.6044 | 1333521.4322 | 62.8596 | 2534.913 | 2978.9962 | 51.6776 | 60.7309
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.0083 | 122.7328 | 15.7355 | 4 | 2532.5768 | 2976.0789 | 51.63 | 60.6714 | 197.8695 | 0 | 362.6681 | 15313274.5391 | 957898.4396 | 15358658.5232 | 13214255.7237 | 0 | 418807.2751 | 0 | 17652528.8552 | 45928259.0498 | 31346980.5328 | 140190662.9385 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159405290.5955 | 187320172.5441 | 1778279.41 | 62.9419 | 2532.5768 | 2976.0789 | 51.63 | 60.6714
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.787 | 122.6291 | 15.7331 | 4 | 2530.5631 | 2974.1326 | 51.589 | 60.6317 | 197.8905 | 0 | 361.7189 | 15304022.6125 | 957331.7385 | 15348274.6014 | 13200640.245 | 0 | 403886.1355 | 0 | 17633520.5798 | 45878803.4162 | 31313226.0467 | 140039705.3756 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159254333.0326 | 187169214.9812 | 2371373.7057 | 62.9324 | 2530.5631 | 2974.1326 | 51.589 | 60.6317
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.7124 | 123.06 | 15.7857 | 4 | 2529.2559 | 2971.3469 | 51.5623 | 60.5749 | 197.8011 | 0 | 345.0403 | 15342448.1265 | 959685.3269 | 15391406.2213 | 13257505.9866 | 0 | 408425.6122 | 0 | 17690193.7967 | 46026255.5012 | 31413865.1245 | 140489785.6958 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159704413.3528 | 187619295.3015 | 3162277.6602 | 63.1428 | 2529.2559 | 2971.3469 | 51.5623 | 60.5749
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.7829 | 123.0924 | 15.7935 | 4 | 2528.284 | 2970.1559 | 51.5425 | 60.5506 | 197.794 | 0 | 364.183 | 15345335.6296 | 959862.1821 | 15394647.8617 | 13261832.0875 | 0 | 403525.1307 | 0 | 17692429.1277 | 46032071.3741 | 31417834.5773 | 140507537.9706 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159722165.6276 | 187637047.5762 | 4216965.0343 | 63.1741 | 2528.284 | 2970.1559 | 51.5425 | 60.5506
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.8413 | 123.1192 | 15.7997 | 4 | 2527.5542 | 2969.2543 | 51.5276 | 60.5323 | 197.7881 | 0 | 375.0098 | 15347725.4505 | 960008.5543 | 15397330.8341 | 13265409.9476 | 0 | 399899.9677 | 0 | 17694446.1541 | 46037319.2631 | 31421416.3694 | 140523556.5408 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159738184.1978 | 187653066.1465 | 5623413.2519 | 63.1987 | 2527.5542 | 2969.2543 | 51.5276 | 60.5323
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.8903 | 123.1418 | 15.8046 | 4 | 2527.0064 | 2968.5702 | 51.5164 | 60.5183 | 197.7832 | 0 | 359.1947 | 15349738.0688 | 960131.8231 | 15399590.3704 | 13268420.5469 | 0 | 397239.8107 | 0 | 17696297.0418 | 46042134.893 | 31424703.1358 | 140538255.6905 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159752883.3475 | 187667765.2961 | 7498942.0933 | 63.2182 | 2527.0064 | 2968.5702 | 51.5164 | 60.5183
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9144 | 123.1528 | 15.8076 | 4 | 2526.5954 | 2968.075 | 51.5081 | 60.5082 | 197.7808 | 0 | 365.7429 | 15350719.4481 | 960191.9304 | 15400692.1623 | 13269895.9114 | 0 | 395067.5327 | 0 | 17696861.1242 | 46043602.5197 | 31425704.8211 | 140542735.45 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159757363.107 | 187672245.0557 | 10000000 | 63.2303 | 2526.5954 | 2968.075 | 51.5081 | 60.5082
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.23104 | 0.013797 | 4 | 378606.7092 | 897068.0213 | 7718.4099 | 18287.945 | 130.3271 | 0 | 58.1887 | 151070.7042 | 6491.9957 | 104743.5407 | 61442.5421 | 0 | 57682.3545 | 0 | 148758.1435 | 387038.175 | 264161.5073 | 1181388.963 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 20895145.6734 | 49508808.2969 | 100 | 0.05519 | 378606.7092 | 897068.0213 | 7718.4099 | 18287.945
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1619 | 0.35561 | 0.02765 | 4 | 192639.2565 | 451348.3227 | 3927.2118 | 9201.3461 | 143.8234 | 0 | 50.323 | 216538.6263 | 10288.1795 | 146562.6497 | 77256.4039 | 0 | 63510.4925 | 0 | 200520.9773 | 521714.4503 | 356080.8325 | 1592472.612 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21306229.3224 | 49919891.9459 | 133.3521 | 0.1106 | 192639.2565 | 451348.3227 | 3927.2118 | 9201.3461
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.53996 | 0.049857 | 4 | 109644.2372 | 253122.0828 | 2235.2461 | 5160.236 | 156.372 | 0 | 57.5763 | 304860.9853 | 15997.2223 | 203016.2937 | 100152.6524 | 0 | 70942.9572 | 0 | 271038.3432 | 705186.1715 | 481304.0522 | 2152498.6778 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21866255.3882 | 50479918.0117 | 177.8279 | 0.19943 | 109644.2372 | 253122.0828 | 2235.2461 | 5160.236
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.78411 | 0.081486 | 4 | 69178.3301 | 156965.722 | 1410.2938 | 3199.9586 | 166.7888 | 0 | 311.9567 | 411817.0483 | 23659.6074 | 271734.1508 | 129709.8011 | 0 | 78218.3446 | 0 | 356904.1914 | 928591.4949 | 633782.7759 | 2834417.4145 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22548174.1249 | 51161836.7483 | 237.1374 | 0.32594 | 69178.3301 | 156965.722 | 1410.2938 | 3199.9586
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 1.1177 | 0.12725 | 4 | 46020.8326 | 102234.9336 | 938.1969 | 2084.1974 | 175.6808 | 0 | 411.8276 | 547245.8402 | 34576.4689 | 358498.8015 | 171276.3773 | 0 | 86692.5256 | 0 | 467333.1052 | 1215904.8766 | 829880.0626 | 3711408.0578 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 23425164.7682 | 52038827.3917 | 316.2278 | 0.50901 | 46020.8326 | 102234.9336 | 938.1969 | 2084.1974
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2656 | 1.6282 | 0.1913 | 4 | 32128.5639 | 69521.978 | 654.9842 | 1417.2996 | 183.281 | 0 | 543.7385 | 718025.2363 | 46476.6285 | 483662.0677 | 225808.049 | 0 | 98779.8541 | 0 | 613373.2159 | 1595871.2876 | 1089214.9457 | 4871211.2848 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 24584967.9952 | 53198630.6186 | 421.6965 | 0.76521 | 32128.5639 | 69521.978 | 654.9842 | 1417.2996
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.246 | 2.3034 | 0.27382 | 4 | 23706.6841 | 49831.2827 | 483.2928 | 1015.8781 | 189.3862 | 0 | 75.0118 | 915715.8047 | 59251.8668 | 638375.519 | 292178.5569 | 0 | 112918.2674 | 0 | 787191.6058 | 2048111.083 | 1397877.8986 | 6251620.6021 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 25965377.3125 | 54579039.9359 | 562.3413 | 1.0953 | 23706.6841 | 49831.2827 | 483.2928 | 1015.8781
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5394 | 3.1964 | 0.383 | 4 | 18055.4096 | 36732.6437 | 368.0839 | 748.8446 | 194.3106 | 0 | 87.7275 | 1152629.3504 | 74526.3434 | 829685.8472 | 378981.4718 | 0 | 130084.4506 | 0 | 1000703.9107 | 2603626.3031 | 1777028.4511 | 7947266.1284 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 27661022.8388 | 56274685.4622 | 749.8942 | 1.532 | 18055.4096 | 36732.6437 | 368.0839 | 748.8446
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.23 | 4.361 | 0.52555 | 4 | 14140.4578 | 27751.6612 | 288.2724 | 565.7551 | 198.0977 | 0 | 95.8636 | 1434149.7938 | 92630.5556 | 1063776.0353 | 491791.5649 | 0 | 150358.5749 | 0 | 1260755.5445 | 3280227.3103 | 2238822.5412 | 10012511.9204 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 29726268.6309 | 58339931.2543 | 1000 | 2.1022 | 14140.4578 | 27751.6612 | 288.2724 | 565.7551
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5152 | 5.95 | 0.72022 | 4 | 11234.4499 | 21166.6457 | 229.0295 | 431.5107 | 201.3608 | 0 | 92.2921 | 1785509.6854 | 115242.8537 | 1363888.3546 | 644039.391 | 0 | 176090.0593 | 0 | 1593060.4341 | 4144816.468 | 2828922.4068 | 12651569.6528 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 32365326.3633 | 60978988.9867 | 1333.5214 | 2.8809 | 11234.4499 | 21166.6457 | 229.0295 | 431.5107
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5185 | 8.0374 | 0.97553 | 4 | 9127.9082 | 16460.7887 | 186.0848 | 335.5754 | 203.8058 | 0 | 91.1716 | 2207034.1529 | 142111.0817 | 1734911.242 | 844162.5606 | 0 | 206746.4675 | 0 | 2002636.5469 | 5210449.4977 | 3556238.8462 | 15904290.3955 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 35618047.106 | 64231709.7294 | 1778.2794 | 3.9021 | 9127.9082 | 16460.7887 | 186.0848 | 335.5754
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5332 | 10.8266 | 1.3168 | 4 | 7539.6595 | 12972.1191 | 153.7062 | 264.4542 | 205.7011 | 0 | 88.788 | 2724139.5311 | 175061.2709 | 2201794.7931 | 1111188.6191 | 0 | 244786.7837 | 0 | 2518218.6892 | 6551888.4716 | 4471798.5097 | 19998876.6686 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 39712633.379 | 68326296.0024 | 2371.3737 | 5.2672 | 7539.6595 | 12972.1191 | 153.7062 | 264.4542
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.8191 | 14.5008 | 1.7667 | 4 | 6339.2331 | 10388.1679 | 129.2338 | 211.7769 | 207.1482 | 0 | 100.0216 | 3349887.5414 | 214793.6381 | 2781623.6375 | 1462775.1087 | 0 | 290144.9301 | 0 | 3158697.6937 | 8218283.4611 | 5609147.3311 | 25085353.3417 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 44799110.0521 | 73412772.6755 | 3162.2777 | 7.067 | 6339.2331 | 10388.1679 | 129.2338 | 211.7769
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8379 | 19.3811 | 2.3636 | 4 | 5414.2247 | 8440.7466 | 110.3763 | 172.076 | 208.2598 | 0 | 50.8378 | 4114395.3656 | 263154.879 | 3508221.0816 | 1929494.7603 | 0 | 346632.8559 | 0 | 3963140.5875 | 10311278.8569 | 7037659.6954 | 31473978.0823 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 51187734.7927 | 79801397.4161 | 4216.965 | 9.4543 | 5414.2247 | 8440.7466 | 110.3763 | 172.076
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.0265 | 25.7715 | 3.1467 | 4 | 4695.5297 | 6968.8327 | 95.7247 | 142.0691 | 209.0998 | 0 | 58.5259 | 5036436.1023 | 321250.9743 | 4406523.8763 | 2540589.4456 | 0 | 412286.6998 | 0 | 4959663.9683 | 12904028.2786 | 8807264.4514 | 39388043.7967 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 59101800.5072 | 87715463.1306 | 5623.4133 | 12.5868 | 4695.5297 | 6968.8327 | 95.7247 | 142.0691
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50 | 34.0915 | 4.166 | 4 | 4133.5249 | 5850.6262 | 84.2675 | 119.2729 | 209.7127 | 0 | 61.2052 | 6144015.6374 | 390750.1153 | 5511901.5888 | 3336410.8843 | 0 | 491316.8873 | 0 | 6191014.0941 | 16107748.7213 | 10993869.4834 | 49167027.4119 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 68880784.1224 | 97494446.7458 | 7498.9421 | 16.6639 | 4133.5249 | 5850.6262 | 84.2675 | 119.2729
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2226 | 44.6137 | 5.4547 | 4 | 3696.8912 | 5008.3213 | 75.3661 | 102.1014 | 210.0393 | 0 | 70.5586 | 7439706.0655 | 471709.6905 | 6835328.3052 | 4347344.8597 | 0 | 583827.7763 | 0 | 7674387.5119 | 19967182.0727 | 13628012.0492 | 60947498.3311 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 80661255.0415 | 109274917.6649 | 10000 | 21.8187 | 3696.8912 | 5008.3213 | 75.3661 | 102.1014
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0654 | 57.4237 | 7.0198 | 4 | 3362.5723 | 4381.6111 | 68.5506 | 89.3251 | 209.8996 | 0 | 60.2298 | 8904877.9481 | 562873.8098 | 8364845.8628 | 5594954.3539 | 0 | 691928.7097 | 0 | 9406597.4668 | 24474037.0503 | 16704033.178 | 74704148.3793 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 94417905.0897 | 123031567.7131 | 13335.2143 | 28.0791 | 3362.5723 | 4381.6111 | 68.5506 | 89.3251
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.2775 | 72.0154 | 8.7942 | 4 | 3115.7433 | 3929.1682 | 63.5186 | 80.1014 | 209.0837 | 0 | 62.3639 | 10464851.0438 | 659545.4957 | 10025938.7697 | 7057110.0872 | 0 | 814407.1054 | 0 | 11318522.4757 | 29448473.7335 | 20099188.4288 | 89888037.1397 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 109601793.8502 | 138215456.4736 | 17782.7941 | 35.1768 | 3115.7433 | 3929.1682 | 63.5186 | 80.1014
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.0032 | 87.3729 | 10.6462 | 4 | 2942.136 | 3614.0593 | 59.9794 | 73.6775 | 207.4994 | 0 | 83.5763 | 12012633.0179 | 755110.7615 | 11702700.1524 | 8667622.6895 | 0 | 948995.5342 | 0 | 13293954.2407 | 34588141.9692 | 23607117.6092 | 105576275.9747 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 125290032.6851 | 153903695.3085 | 23713.7371 | 42.5847 | 2942.136 | 3614.0593 | 59.9794 | 73.6775
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.8279 | 102.53 | 12.4682 | 4 | 2818.7346 | 3392.4686 | 57.4637 | 69.1601 | 205.5437 | 0 | 133.6123 | 13466351.4 | 844583.4331 | 13300421.0716 | 10332865.0482 | 0 | 1078776.6608 | 0 | 15218969.0693 | 39596635.6785 | 27025517.4801 | 120864119.8415 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 140577876.5519 | 169191539.1754 | 31622.7766 | 49.8727 | 2818.7346 | 3392.4686 | 57.4637 | 69.1601
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.1124 | 112.6508 | 13.7544 | 4 | 2736.772 | 3256.8528 | 55.7928 | 66.3953 | 203.9916 | 0 | 135.9893 | 14403245.1468 | 902112.796 | 14340754.5138 | 11500358.9581 | 0 | 1102963.6114 | 0 | 16477279.6602 | 42870501.7209 | 29259998.3253 | 130857214.7324 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 150570971.4429 | 179184634.0663 | 42169.6503 | 55.0177 | 2736.772 | 3256.8528 | 55.7928 | 66.3953
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.9339 | 116.791 | 14.417 | 4 | 2675.7183 | 3171.8984 | 54.5481 | 64.6634 | 203.2736 | 0 | 167.7811 | 14779614.9564 | 925195.5805 | 14760879.5884 | 11994501.5056 | 0 | 994210.6737 | 0 | 16947216.8988 | 44093182.0185 | 30094502.7519 | 134589303.9737 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 154303060.6842 | 182916723.3076 | 56234.1325 | 57.6679 | 2675.7183 | 3171.8984 | 54.5481 | 64.6634
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.5823 | 121.7162 | 15.1264 | 4 | 2628.0938 | 3101.0027 | 53.5772 | 63.2181 | 202.3631 | 0 | 231.9319 | 15229013.4697 | 953910.282 | 15255655.6134 | 12596781.2742 | 0 | 940217.3382 | 0 | 17540475.4112 | 45636718.9737 | 31147998.4404 | 139300770.8028 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 159014527.5132 | 187628190.1366 | 74989.4209 | 60.5057 | 2628.0938 | 3101.0027 | 53.5772 | 63.2181
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.2453 | 123.5224 | 15.481 | 4 | 2591.6689 | 3053.7467 | 52.8347 | 62.2548 | 202.0009 | 0 | 261.1179 | 15393973.2495 | 964702.0942 | 15435840.9325 | 12823309.3762 | 0 | 832924.1449 | 0 | 17725792.421 | 46118875.8193 | 31477080.3948 | 140772498.4324 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 160486255.1429 | 189099917.7663 | 100000 | 61.9239 | 2591.6689 | 3053.7467 | 52.8347 | 62.2548
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.1667 | 123.4712 | 15.6021 | 4 | 2564.4355 | 3022.927 | 52.2795 | 61.6265 | 201.9996 | 0 | 289.3967 | 15389418.1243 | 964423.5327 | 15430722.9658 | 12818143.2937 | 0 | 704608.9646 | 0 | 17669853.5836 | 45973334.4392 | 31377745.4123 | 140328250.3162 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 160042007.0266 | 188655669.65 | 133352.1432 | 62.4083 | 2564.4355 | 3022.927 | 52.2795 | 61.6265
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.642 | 123.7032 | 15.7201 | 4 | 2544.1175 | 2999.1655 | 51.8653 | 61.142 | 201.9467 | 0 | 315.5535 | 15409536.453 | 965559.1845 | 15454008.8067 | 12848008.309 | 0 | 608727.2532 | 0 | 17661477.6025 | 45951541.8545 | 31362871.5254 | 140261730.9888 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 159975487.6992 | 188589150.3226 | 177827.941 | 62.8805 | 2544.1175 | 2999.1655 | 51.8653 | 61.142
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.4855 | 124.6259 | 15.8878 | 4 | 2528.7529 | 2978.9996 | 51.552 | 60.7309 | 201.7613 | 0 | 347.888 | 15489690.8951 | 970128.9201 | 15546493.0572 | 12964321.3695 | 0 | 550730.6558 | 0 | 17753332.3101 | 46190528.9616 | 31525985.1368 | 140991211.3061 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 160704968.0165 | 189318630.64 | 237137.3706 | 63.5511 | 2528.7529 | 2978.9996 | 51.552 | 60.7309
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.8083 | 125.284 | 16.0111 | 4 | 2517.0927 | 2963.8704 | 51.3143 | 60.4225 | 201.6272 | 0 | 361.9106 | 15546728.1289 | 973374.0674 | 15612385.222 | 13047796.1641 | 0 | 502852.0202 | 0 | 17816422.885 | 46354677.696 | 31638020.0209 | 141492256.2045 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161206012.9149 | 189819675.5383 | 316227.766 | 64.0445 | 2517.0927 | 2963.8704 | 51.3143 | 60.4225
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.7339 | 125.7424 | 16.1006 | 4 | 2508.2558 | 2952.5515 | 51.1342 | 60.1918 | 201.5327 | 0 | 381.0546 | 15586383.5935 | 975626.671 | 15658239.4526 | 13106207.1589 | 0 | 463684.5621 | 0 | 17858155.1609 | 46463256.5174 | 31712127.2976 | 141823680.4142 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161537437.1246 | 190151099.7481 | 421696.5034 | 64.4023 | 2508.2558 | 2952.5515 | 51.1342 | 60.1918
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.3749 | 126.0588 | 16.1651 | 4 | 2501.5675 | 2944.0902 | 50.9978 | 60.0193 | 201.4668 | 0 | 354.2805 | 15613718.83 | 977177.4933 | 15689869.4122 | 13146666.2291 | 0 | 432043.8192 | 0 | 17885195.5557 | 46533610.0778 | 31760145.0482 | 142038426.4654 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161752183.1759 | 190365845.7993 | 562341.3252 | 64.6603 | 2501.5675 | 2944.0902 | 50.9978 | 60.0193
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.8204 | 126.278 | 16.2117 | 4 | 2496.5118 | 2937.7615 | 50.8948 | 59.8902 | 201.4208 | 0 | 359.1784 | 15632645.5548 | 978250.2273 | 15711781.0517 | 13174781.7651 | 0 | 406831.4067 | 0 | 17902673.1022 | 46579083.0687 | 31791181.2989 | 142177227.4755 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161890984.1859 | 190504646.8093 | 749894.2093 | 64.8469 | 2496.5118 | 2937.7615 | 50.8948 | 59.8902
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.1371 | 126.4336 | 16.2458 | 4 | 2492.695 | 2933.0179 | 50.817 | 59.7935 | 201.388 | 0 | 356.8996 | 15646067.9466 | 979010.4504 | 15727325.9947 | 13194772.6262 | 0 | 387045.2049 | 0 | 17914346.6669 | 46609455.2894 | 31811910.9636 | 142269935.1426 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161983691.853 | 190597354.4765 | 1000000 | 64.9834 | 2492.695 | 2933.0179 | 50.817 | 59.7935
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.7755 | 126.7491 | 16.2939 | 4 | 2489.5892 | 2928.6139 | 50.7536 | 59.7038 | 201.3235 | 0 | 347.4193 | 15673293.4998 | 980556.1846 | 15758834.6426 | 13235109.729 | 0 | 375730.4794 | 0 | 17949174.5688 | 46700070.346 | 31873757.6016 | 142546527.0517 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162260283.7621 | 190873946.3856 | 1333521.4322 | 65.1755 | 2489.5892 | 2928.6139 | 50.7536 | 59.7038
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.9265 | 126.8228 | 16.3115 | 4 | 2487.4653 | 2926.0163 | 50.7103 | 59.6508 | 201.3076 | 0 | 353.0519 | 15679642.0918 | 980914.9631 | 15766194.9328 | 13244636.2243 | 0 | 363986.4567 | 0 | 17953796.1208 | 46712094.6763 | 31881964.4542 | 142583229.92 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162296986.6304 | 190910649.2538 | 1778279.41 | 65.2459 | 2487.4653 | 2926.0163 | 50.7103 | 59.6508
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.0191 | 126.8679 | 16.3236 | 4 | 2485.867 | 2924.0926 | 50.6778 | 59.6116 | 201.2978 | 0 | 350.2323 | 15683521.0624 | 981133.8751 | 15770694.3942 | 13250478.8072 | 0 | 354760.2918 | 0 | 17955829.488 | 46717385.0807 | 31885575.2638 | 142599378.2632 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162313134.9737 | 190926797.5971 | 2371373.7057 | 65.2944 | 2485.867 | 2924.0926 | 50.6778 | 59.6116
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.0922 | 126.9035 | 16.3329 | 4 | 2484.6652 | 2922.6416 | 50.6533 | 59.582 | 201.29 | 0 | 340.9828 | 15686587.0062 | 981306.942 | 15774250.5866 | 13255094.9915 | 0 | 347805.958 | 0 | 17957567.7389 | 46721907.6529 | 31888662.0123 | 142613182.8885 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162326939.5989 | 190940602.2224 | 3162277.6602 | 65.3315 | 2484.6652 | 2922.6416 | 50.6533 | 59.582
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.1239 | 126.9187 | 16.3386 | 4 | 2483.7619 | 2921.5848 | 50.6348 | 59.5605 | 201.2865 | 0 | 352.6753 | 15687896.0638 | 981380.4828 | 15775771.5457 | 13257090.1693 | 0 | 342225.8613 | 0 | 17957302.0079 | 46721216.2755 | 31888190.133 | 142611072.5394 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162324829.2499 | 190938491.8733 | 4216965.0343 | 65.3544 | 2483.7619 | 2921.5848 | 50.6348 | 59.5605
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.1628 | 126.9376 | 16.3437 | 4 | 2483.0835 | 2920.7696 | 50.621 | 59.5438 | 201.2824 | 0 | 356.1354 | 15689523.5782 | 981472.3079 | 15777659.6792 | 13259544.1342 | 0 | 338217.1787 | 0 | 17958102.5825 | 46723299.2062 | 31889611.7761 | 142617430.4429 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162331187.1534 | 190944849.7768 | 5623413.2519 | 65.3748 | 2483.0835 | 2920.7696 | 50.621 | 59.5438
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.1823 | 126.947 | 16.347 | 4 | 2482.574 | 2920.1716 | 50.6106 | 59.5316 | 201.2803 | 0 | 359.5471 | 15690329.4517 | 981517.6194 | 15778595.7403 | 13260769.9336 | 0 | 335061.62 | 0 | 17958047.0023 | 46723154.598 | 31889513.078 | 142616989.0431 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162330745.7536 | 190944408.377 | 7498942.0933 | 65.3881 | 2482.574 | 2920.1716 | 50.6106 | 59.5316
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.1971 | 126.9541 | 16.3495 | 4 | 2482.1916 | 2919.7224 | 50.6028 | 59.5225 | 201.2786 | 0 | 341.2583 | 15690943.6681 | 981552.1593 | 15779309.1521 | 13261703.9227 | 0 | 332688.4522 | 0 | 17958016.9682 | 46723076.4555 | 31889459.7441 | 142616750.5222 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162330507.2327 | 190944169.8561 | 10000000 | 65.3981 | 2482.1916 | 2919.7224 | 50.6028 | 59.5225
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.24389 | 0.015452 | 4 | 346932.6447 | 821312.2016 | 7072.6912 | 16743.5601 | 132.7177 | 0 | 62.322 | 158624.4546 | 6935.2678 | 109202.1057 | 62915.404 | 0 | 57708.6123 | 0 | 154200.4793 | 401198.0162 | 273825.8899 | 1224610.2297 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21443356.0844 | 50764003.5098 | 100 | 0.061808 | 346932.6447 | 821312.2016 | 7072.6912 | 16743.5601
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2008 | 0.3828 | 0.031171 | 4 | 175626.8617 | 410788.5384 | 3580.3911 | 8374.48 | 147.0615 | 0 | 57.7473 | 231013.5563 | 11246.7575 | 155132.2048 | 80282.1765 | 0 | 64394.6581 | 0 | 211407.0477 | 550037.7726 | 375412.0819 | 1678926.2553 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21897672.1101 | 51218319.5355 | 133.3521 | 0.12468 | 175626.8617 | 410788.5384 | 3580.3911 | 8374.48
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.57435 | 0.055031 | 4 | 102087.5737 | 235288.3713 | 2081.1933 | 4796.6717 | 159.415 | 0 | 62.9111 | 322142.127 | 17340.4324 | 212865.8335 | 104009.4276 | 0 | 71107.5649 | 0 | 283711.5003 | 738159.1266 | 503808.7715 | 2253144.7838 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22471890.6385 | 51792538.0639 | 177.8279 | 0.22012 | 102087.5737 | 235288.3713 | 2081.1933 | 4796.6717
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.83878 | 0.090224 | 4 | 64302.2793 | 145546.4 | 1310.8889 | 2967.1602 | 170.1387 | 0 | 338.537 | 437672.2018 | 26011.9615 | 286095.3496 | 136119.4038 | 0 | 78718.6393 | 0 | 376200.8468 | 978797.434 | 668049.361 | 2987665.1977 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 23206411.0524 | 52527058.4779 | 237.1374 | 0.3609 | 64302.2793 | 145546.4 | 1310.8889 | 2967.1602
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5849 | 1.2106 | 0.14076 | 4 | 42901.4441 | 94977.6104 | 874.604 | 1936.2471 | 179.1514 | 0 | 444.5611 | 583225.1327 | 37687.4062 | 381621.9703 | 180801.5341 | 0 | 87538.8594 | 0 | 495641.2121 | 1289556.7638 | 880148.9891 | 3936221.8677 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 24154967.7225 | 53475615.1479 | 316.2278 | 0.56303 | 42901.4441 | 94977.6104 | 874.604 | 1936.2471
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3434 | 1.748 | 0.20685 | 4 | 30604.1648 | 66041.6681 | 623.9073 | 1346.3487 | 186.6305 | 0 | 543.4455 | 754661.1277 | 48846.2454 | 511945.6097 | 233239.6179 | 0 | 98845.7674 | 0 | 642539.9635 | 1671757.182 | 1141008.6279 | 5102844.1415 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 25321589.9962 | 54642237.4217 | 421.6965 | 0.82739 | 30604.1648 | 66041.6681 | 623.9073 | 1346.3487
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3406 | 2.4585 | 0.29408 | 4 | 22734.939 | 47660.3481 | 463.4825 | 971.6207 | 192.7835 | 0 | 78.0659 | 958576.7239 | 62018.0157 | 672547.3811 | 301002.2142 | 0 | 112616.8041 | 0 | 821636.8442 | 2137730.5278 | 1459045.0112 | 6525173.5222 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 26743919.3769 | 56064566.8023 | 562.3413 | 1.1763 | 22734.939 | 47660.3481 | 463.4825 | 971.6207
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6636 | 3.4036 | 0.4101 | 4 | 17375.6727 | 35249.6438 | 354.2266 | 718.6117 | 197.7753 | 0 | 88.4576 | 1204663.5638 | 77876.2439 | 872442.3696 | 390173.7841 | 0 | 129629.0771 | 0 | 1043166.1651 | 2714104.3787 | 1852432.0077 | 8284487.5901 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 28503233.4448 | 57823880.8702 | 749.8942 | 1.6404 | 17375.6727 | 35249.6438 | 354.2266 | 718.6117
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4152 | 4.6496 | 0.56339 | 4 | 13611.1742 | 26622.0007 | 277.4822 | 542.7255 | 201.629 | 0 | 85.1399 | 1500973.5623 | 97038.9265 | 1119657.8977 | 507412.1786 | 0 | 150430.4383 | 0 | 1316450.0714 | 3425133.0446 | 2337723.6824 | 10454819.8018 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 30673565.6566 | 59994213.082 | 1000 | 2.2536 | 13611.1742 | 26622.0007 | 277.4822 | 542.7255
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7394 | 6.3281 | 0.76938 | 4 | 10853.592 | 20381.0089 | 221.2652 | 415.4944 | 204.9458 | 0 | 90.2213 | 1864352.1875 | 120209.5948 | 1432861.8947 | 663553.9421 | 0 | 175441.3313 | 0 | 1660003.3906 | 4318988.3089 | 2947798.2672 | 13183208.917 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 33401954.7717 | 62722602.1971 | 1333.5214 | 3.0775 | 10853.592 | 20381.0089 | 221.2652 | 415.4944
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8326 | 8.5517 | 1.0421 | 4 | 8829.4942 | 15863.4462 | 180.0012 | 323.3978 | 207.418 | 0 | 94.4928 | 2305858.3063 | 148417.0421 | 1823168.3692 | 870640.5627 | 0 | 207150.83 | 0 | 2088541.693 | 5433957.0664 | 3708787.3544 | 16586521.2241 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 36805267.0788 | 66125914.5042 | 1778.2794 | 4.1684 | 8829.4942 | 15863.4462 | 180.0012 | 323.3978
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9205 | 11.4927 | 1.4042 | 4 | 7305.9832 | 12526.1863 | 148.9423 | 255.3633 | 209.3223 | 0 | 58.1562 | 2841635.9519 | 182532.9533 | 2309516.5184 | 1144257.9923 | 0 | 243248.3082 | 0 | 2621264.7724 | 6819993.2424 | 4654785.5248 | 20817235.2637 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 41035981.1185 | 70356628.5439 | 2371.3737 | 5.6168 | 7305.9832 | 12526.1863 | 148.9423 | 255.3633
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.3332 | 15.3886 | 1.884 | 4 | 6147.0726 | 10037.8779 | 125.3164 | 204.6357 | 210.7864 | 0 | 56.6155 | 3493882.5921 | 223916.9703 | 2917055.9756 | 1506457.7071 | 0 | 287078.002 | 0 | 3287072.5863 | 8552288.5984 | 5837112.7003 | 26104865.132 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 46323610.9868 | 75644258.4122 | 3162.2777 | 7.5359 | 6147.0726 | 10037.8779 | 125.3164 | 204.6357
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2984 | 20.4035 | 2.5015 | 4 | 5272.881 | 8203.131 | 107.4948 | 167.2319 | 211.8838 | 0 | 98.1472 | 4267175.8399 | 272797.7946 | 3655519.9467 | 1972438.1548 | 0 | 339028.4386 | 0 | 4097714.4681 | 10661412.4892 | 7276633.094 | 32542720.226 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 52761466.0807 | 82082113.5061 | 4216.965 | 10.0062 | 5272.881 | 8203.131 | 107.4948 | 167.2319
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5601 | 27.0729 | 3.3229 | 4 | 4579.9173 | 6785.8591 | 93.3678 | 138.3389 | 212.7336 | 0 | 104.112 | 5215751.0007 | 332522.895 | 4583664.4011 | 2591949.7837 | 0 | 402578.8229 | 0 | 5119322.0923 | 13319425.9669 | 9090781.9092 | 40655996.8719 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 60874742.7266 | 90195390.152 | 5623.4133 | 13.2917 | 4579.9173 | 6785.8591 | 93.3678 | 138.3389
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.5816 | 35.7226 | 4.3882 | 4 | 4037.141 | 5707.5486 | 82.3026 | 116.3561 | 213.351 | 0 | 118.0534 | 6351615.0968 | 403745.2701 | 5721890.5938 | 3396019.3702 | 0 | 478360.6476 | 0 | 6377136.0816 | 16591999.9539 | 11324380.9 | 50645147.9141 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 70863893.7688 | 100184541.1942 | 7498.9421 | 17.553 | 4037.141 | 5707.5486 | 82.3026 | 116.3561
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.9265 | 46.7022 | 5.7396 | 4 | 3612.9194 | 4890.0441 | 73.6542 | 99.6902 | 213.673 | 0 | 115.6482 | 7685992.6555 | 487060.9011 | 7090139.3801 | 4421384.4717 | 0 | 568153.3815 | 0 | 7898565.008 | 20550445.9325 | 14026101.6183 | 62727843.3487 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 82946589.2034 | 112267236.6288 | 10000 | 22.9583 | 3612.9194 | 4890.0441 | 73.6542 | 99.6902
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.9131 | 60.0566 | 7.3797 | 4 | 3287.5166 | 4280.8058 | 67.0205 | 87.27 | 213.5051 | 0 | 129.3405 | 9193963.4697 | 580817.3364 | 8670285.6249 | 5686159.1212 | 0 | 672880.5729 | 0 | 9673601.3888 | 25168726.4852 | 17178172.9917 | 76824606.9909 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 97043352.8456 | 126364000.271 | 13335.2143 | 29.5187 | 3287.5166 | 4280.8058 | 67.0205 | 87.27
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4152 | 75.3378 | 9.2473 | 4 | 3046.1507 | 3838.8281 | 62.0999 | 78.2597 | 212.6251 | 0 | 134.4479 | 10807012.0983 | 680700.3055 | 10394293.5008 | 7175992.0107 | 0 | 793124.2381 | 0 | 11641937.6398 | 30289933.6491 | 20673502.1114 | 92456495.5538 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 112675241.4086 | 141995888.834 | 17782.7941 | 36.9894 | 3046.1507 | 3838.8281 | 62.0999 | 78.2597
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.5574 | 91.4728 | 11.2032 | 4 | 2876.0107 | 3530.3017 | 58.6314 | 71.97 | 210.9372 | 0 | 140.4747 | 12412420.6 | 779742.9663 | 12139992.7552 | 8825150.2592 | 0 | 926515.9827 | 0 | 13682690.7998 | 35599554.7552 | 24297427.6181 | 108663495.7365 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 128882241.5912 | 158202889.0166 | 23713.7371 | 44.8129 | 2876.0107 | 3530.3017 | 58.6314 | 71.97
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.7648 | 107.3464 | 13.1111 | 4 | 2758.2129 | 3317.2945 | 56.2299 | 67.6275 | 208.8634 | 0 | 95.9796 | 13915314.979 | 872164.3599 | 13797959.0032 | 10526263.0161 | 0 | 1063827.3558 | 0 | 15668456.1985 | 40766108.9861 | 27823707.0428 | 124433800.9413 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 144652546.796 | 173973194.2215 | 31622.7766 | 52.4443 | 2758.2129 | 3317.2945 | 56.2299 | 67.6275
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.2964 | 118.4699 | 14.5071 | 4 | 2679.9288 | 3185.2092 | 54.634 | 64.9348 | 207.1277 | 0 | 172.454 | 14931160.6929 | 934485.4906 | 14930388.5368 | 11780081.8965 | 0 | 1105620.806 | 0 | 17035877.5949 | 44323858.9629 | 30251944.5064 | 135293418.4871 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 155512164.3418 | 184832811.7672 | 42169.6503 | 58.0285 | 2679.9288 | 3185.2092 | 54.634 | 64.9348
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.1593 | 122.7417 | 15.187 | 4 | 2622.521 | 3105.1823 | 53.4636 | 63.3033 | 206.3688 | 0 | 166.6569 | 15314063.6482 | 957946.7738 | 15359544.2146 | 12280407.4392 | 0 | 996796.7615 | 0 | 17514415.9465 | 45568917.5922 | 31101722.6043 | 139093814.9803 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 159312560.835 | 188633208.2604 | 56234.1325 | 60.7479 | 2622.521 | 3105.1823 | 53.4636 | 63.3033
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.305 | 125.9995 | 15.722 | 4 | 2578.5831 | 3044.8191 | 52.5679 | 62.0728 | 205.7562 | 0 | 220.7619 | 15603565.3978 | 975674.7998 | 15684826.1712 | 12670070.2667 | 0 | 894590.2593 | 0 | 17873203.489 | 46502409.1802 | 31738849.7944 | 141943189.3584 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 162161935.2131 | 191482582.6385 | 74989.4209 | 62.888 | 2578.5831 | 3044.8191 | 52.5679 | 62.0728
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.9808 | 128.4292 | 16.1338 | 4 | 2545.0426 | 2999.3783 | 51.8841 | 61.1464 | 205.2787 | 0 | 270.3886 | 15818113.8257 | 988807.2923 | 15926333.0352 | 12965741.2497 | 0 | 802234.6462 | 0 | 18135479.7191 | 47184798.1307 | 32204594.2749 | 144026102.1738 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 164244848.0285 | 193565495.4539 | 100000 | 64.5352 | 2545.0426 | 2999.3783 | 51.8841 | 61.1464
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.6445 | 130.3035 | 16.4551 | 4 | 2519.4924 | 2964.9562 | 51.3633 | 60.4446 | 204.8982 | 0 | 275.3239 | 15982832.5761 | 998886.4795 | 16112000.9093 | 13196925.9791 | 0 | 723738.3835 | 0 | 18335609.8877 | 47705495.7771 | 32559981.1178 | 145615471.1101 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 165834216.9648 | 195154864.3902 | 133352.1432 | 65.8205 | 2519.4924 | 2964.9562 | 51.3633 | 60.4446
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.2749 | 131.6311 | 16.692 | 4 | 2500.0572 | 2939.1991 | 50.967 | 59.9195 | 204.6211 | 0 | 377.0354 | 16099108.5826 | 1005999.7644 | 16243195.4898 | 13362234.1558 | 0 | 655679.7835 | 0 | 18472824.9327 | 48062501.1775 | 32803644.6393 | 146705188.5256 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 166923934.3804 | 196244581.8058 | 177827.941 | 66.768 | 2500.0572 | 2939.1991 | 50.967 | 59.9195
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.2117 | 132.5998 | 16.8691 | 4 | 2485.3055 | 2919.8371 | 50.6663 | 59.5248 | 204.415 | 0 | 363.6993 | 16183739.5637 | 1011176.2704 | 16338752.295 | 13483885.7701 | 0 | 599093.2387 | 0 | 18570492.3838 | 48316611.8508 | 32977080.3953 | 147480831.7678 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 167699577.6225 | 197020225.0479 | 237137.3706 | 67.4764 | 2485.3055 | 2919.8371 | 50.6663 | 59.5248
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 206.6271 | 133.3028 | 17.0007 | 4 | 2474.1255 | 2905.2934 | 50.4384 | 59.2283 | 204.2632 | 0 | 352.341 | 16245052.1778 | 1014926.0399 | 16408015.6356 | 13572751.905 | 0 | 552827.9986 | 0 | 18639493.7652 | 48496139.2912 | 33099611.5622 | 148028818.3756 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168247564.2303 | 197568211.6557 | 316227.766 | 68.0028 | 2474.1255 | 2905.2934 | 50.4384 | 59.2283
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.6406 | 133.8035 | 17.0973 | 4 | 2465.6641 | 2894.3972 | 50.2659 | 59.0062 | 204.1538 | 0 | 360.0745 | 16288665.3328 | 1017593.1106 | 16457302.3193 | 13636363.0129 | 0 | 515329.3478 | 0 | 18686948.7181 | 48619607.3442 | 33183881.0454 | 148405690.231 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168624436.0857 | 197945083.5111 | 421696.5034 | 68.3891 | 2465.6641 | 2894.3972 | 50.2659 | 59.0062
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.3787 | 134.1668 | 17.1687 | 4 | 2459.2688 | 2886.2169 | 50.1355 | 58.8394 | 204.0738 | 0 | 337.3043 | 16320279.511 | 1019526.2891 | 16493038.4302 | 13682679.4542 | 0 | 485528.5846 | 0 | 18720410.385 | 48706667.7376 | 33243301.5529 | 148671431.9447 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168890177.7994 | 198210825.2249 | 562341.3252 | 68.675 | 2459.2688 | 2886.2169 | 50.1355 | 58.8394
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.8896 | 134.4174 | 17.2202 | 4 | 2454.4409 | 2880.1134 | 50.0371 | 58.715 | 204.0182 | 0 | 454.4674 | 16342078.1333 | 1020859.1965 | 16517683.7645 | 13714732.1048 | 0 | 461737.7882 | 0 | 18742265.485 | 48763530.2248 | 33282111.3688 | 148844998.0659 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169063743.9206 | 198384391.346 | 749894.2093 | 68.8808 | 2454.4409 | 2880.1134 | 50.0371 | 58.715
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.477 | 134.7054 | 17.2698 | 4 | 2450.798 | 2875.2486 | 49.9628 | 58.6158 | 203.9549 | 0 | 443.1968 | 16367111.1439 | 1022389.8161 | 16545990.4498 | 13751392.9778 | 0 | 446103.2572 | 0 | 18771865.1815 | 48840542.5632 | 33334673.8722 | 149080069.2617 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169298815.1164 | 198619462.5418 | 1000000 | 69.0791 | 2450.798 | 2875.2486 | 49.9628 | 58.6158
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.7398 | 134.8334 | 17.2974 | 4 | 2448.0538 | 2871.8253 | 49.9069 | 58.546 | 203.926 | 0 | 428.0992 | 16378227.729 | 1023069.509 | 16558562.3667 | 13767748.1229 | 0 | 431668.86 | 0 | 18782117.8692 | 48867217.9534 | 33352880.3741 | 149161492.7843 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169380238.639 | 198700886.0645 | 1333521.4322 | 69.1898 | 2448.0538 | 2871.8253 | 49.9069 | 58.546
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.3468 | 135.1311 | 17.3413 | 4 | 2445.7713 | 2868.4705 | 49.8604 | 58.4777 | 203.8613 | 0 | 423.5263 | 16404082.022 | 1024650.2501 | 16587805.1094 | 13805569.3708 | 0 | 424783.3635 | 0 | 18816287.1452 | 48956119.4006 | 33413557.4386 | 149432854.1003 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169651599.9551 | 198972247.3805 | 1778279.41 | 69.3653 | 2445.7713 | 2868.4705 | 49.8604 | 58.4777
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.5318 | 135.221 | 17.3588 | 4 | 2444.2504 | 2866.5251 | 49.8293 | 58.438 | 203.8411 | 0 | 399.3889 | 16411888.5275 | 1025127.5296 | 16596635.7545 | 13817084.4365 | 0 | 417121.0728 | 0 | 18824464.3552 | 48977394.8235 | 33428078.3519 | 149497794.8515 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169716540.7062 | 199037188.1317 | 2371373.7057 | 69.435 | 2444.2504 | 2866.5251 | 49.8293 | 58.438
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.6413 | 135.274 | 17.3703 | 4 | 2443.1075 | 2865.1024 | 49.8061 | 58.409 | 203.829 | 0 | 425.2139 | 16416489.8002 | 1025408.8425 | 16601840.8928 | 13823892.319 | 0 | 410914.9045 | 0 | 18828633.236 | 48988241.3963 | 33435481.3607 | 149530902.752 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169749648.6067 | 199070296.0321 | 3162277.6602 | 69.481 | 2443.1075 | 2865.1024 | 49.8061 | 58.409
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.7144 | 135.3094 | 17.3784 | 4 | 2442.2491 | 2864.046 | 49.7886 | 58.3875 | 203.8209 | 0 | 419.1557 | 16419558.9119 | 1025596.4809 | 16605312.8826 | 13828441.4766 | 0 | 406102.1225 | 0 | 18831154.631 | 48994801.549 | 33439958.7997 | 149550926.8541 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169769672.7088 | 199090320.1343 | 4216965.0343 | 69.5137 | 2442.2491 | 2864.046 | 49.7886 | 58.3875
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.7681 | 135.3353 | 17.3845 | 4 | 2441.6046 | 2863.2546 | 49.7754 | 58.3713 | 203.8149 | 0 | 405.3355 | 16421810.6969 | 1025734.1492 | 16607860.3031 | 13831781.1282 | 0 | 402455.4765 | 0 | 18832960.284 | 48999499.4877 | 33443165.2394 | 149565266.7649 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169784012.6196 | 199104660.045 | 5623413.2519 | 69.5379 | 2441.6046 | 2863.2546 | 49.7754 | 58.3713
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.805 | 135.3531 | 17.3888 | 4 | 2441.1209 | 2862.6652 | 49.7656 | 58.3593 | 203.8108 | 0 | 405.8662 | 16423353.7105 | 1025828.4847 | 16609605.9207 | 13834072.8136 | 0 | 399661.7472 | 0 | 18834083.844 | 49002422.7602 | 33445160.4329 | 149574189.7139 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169792935.5686 | 199113582.9941 | 7498942.0933 | 69.5553 | 2441.1209 | 2862.6652 | 49.7656 | 58.3593
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.8218 | 135.3612 | 17.3915 | 4 | 2440.7579 | 2862.237 | 49.7582 | 58.3506 | 203.8089 | 0 | 383.8573 | 16424051.1695 | 1025871.1254 | 16610394.965 | 13835118.1509 | 0 | 397411.9726 | 0 | 18834210.4795 | 49002752.2398 | 33445385.3095 | 149575195.4121 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169793941.2668 | 199114588.6923 | 10000000 | 69.5661 | 2440.7579 | 2862.237 | 49.7582 | 58.3506
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.26439 | 0.017792 | 4 | 309473.2939 | 731504.6596 | 6309.0317 | 14912.7119 | 136.0138 | 0 | 48.5205 | 170291.9667 | 7625.0304 | 116229.0532 | 65279.191 | 0 | 58854.8588 | 0 | 163129.239 | 424428.8175 | 289681.3891 | 1295519.5457 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22025114.6355 | 52060950.9902 | 100 | 0.07117 | 309473.2939 | 731504.6596 | 6309.0317 | 14912.7119
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.235 | 0.40889 | 0.034756 | 4 | 161770.2351 | 377816.3303 | 3297.9051 | 7702.2969 | 150.092 | 0 | 44.4512 | 244904.8105 | 12206.4859 | 163209.0178 | 83229.0206 | 0 | 64868.0462 | 0 | 221682.7786 | 576773.1164 | 393659.5035 | 1760532.7794 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22490127.8693 | 52525964.2239 | 133.3521 | 0.13903 | 161770.2351 | 377816.3303 | 3297.9051 | 7702.2969
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.61722 | 0.061331 | 4 | 94194.6142 | 216627.5736 | 1920.2846 | 4416.2461 | 162.799 | 0 | 247.8604 | 343251.2049 | 19025.2027 | 224977.1135 | 108825.4982 | 0 | 71916.2127 | 0 | 299518.1405 | 779284.7619 | 531877.8627 | 2378675.997 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23108271.0869 | 53144107.4415 | 177.8279 | 0.24532 | 94194.6142 | 216627.5736 | 1920.2846 | 4416.2461
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.89652 | 0.099641 | 4 | 59908.1889 | 135268.3125 | 1221.3095 | 2757.6275 | 173.481 | 0 | 332.4457 | 464748.1812 | 28610.4457 | 301026.5813 | 142788.9878 | 0 | 79098.8991 | 0 | 396346.5071 | 1031212.3097 | 703823.5907 | 3147655.5027 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23877250.5925 | 53913086.9471 | 237.1374 | 0.39856 | 59908.1889 | 135268.3125 | 1221.3095 | 2757.6275
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 1.3003 | 0.15259 | 4 | 40719.5492 | 89930.3431 | 830.1231 | 1833.3517 | 182.3754 | 0 | 428.7621 | 613469.1226 | 39708.498 | 404041.9144 | 186751.9603 | 0 | 87403.2174 | 0 | 519236.1379 | 1350945.9208 | 922048.3501 | 4123605.1214 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 24853200.2112 | 54889036.5659 | 316.2278 | 0.61035 | 40719.5492 | 89930.3431 | 830.1231 | 1833.3517
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4406 | 1.8845 | 0.22431 | 4 | 29082.3581 | 62557.5587 | 592.8832 | 1275.3205 | 190.1263 | 0 | 559.7719 | 795489.8457 | 51485.9075 | 543683.7093 | 241847.0192 | 0 | 99587.8599 | 0 | 675516.7932 | 1757556.1285 | 1199568.1718 | 5364735.4352 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 26094330.525 | 56130166.8796 | 421.6965 | 0.89726 | 29082.3581 | 62557.5587 | 592.8832 | 1275.3205
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4527 | 2.6294 | 0.31623 | 4 | 21782.7187 | 45528.0259 | 444.0702 | 928.1504 | 196.2601 | 0 | 79.961 | 1004887.0295 | 65005.373 | 709697.1205 | 310809.6933 | 0 | 112755.9285 | 0 | 859230.5065 | 2235541.5254 | 1525803.0269 | 6823730.2036 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 27553325.2935 | 57589161.6481 | 562.3413 | 1.2649 | 21782.7187 | 45528.0259 | 444.0702 | 928.1504
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.817 | 3.6358 | 0.44031 | 4 | 16687.4742 | 33741.1641 | 340.1967 | 687.8593 | 201.3177 | 0 | 61.8677 | 1262157.4625 | 81625.7609 | 919711.5334 | 403058.6256 | 0 | 129873.502 | 0 | 1090606.4849 | 2837534.3596 | 1936675.5059 | 8661243.2348 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 29390838.3246 | 59426674.6793 | 749.8942 | 1.7613 | 16687.4742 | 33741.1641 | 340.1967 | 687.8593
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6005 | 4.9488 | 0.60199 | 4 | 13135.553 | 25609.0629 | 267.786 | 522.0754 | 205.1486 | 0 | 82.1478 | 1567707.6604 | 101203.2603 | 1177014.734 | 523307.7111 | 0 | 150149.5536 | 0 | 1372559.3386 | 3571117.8483 | 2437361.3106 | 10900421.4169 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 31630016.5067 | 61665852.8613 | 1000 | 2.408 | 13135.553 | 25609.0629 | 267.786 | 522.0754
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9757 | 6.7222 | 0.82088 | 4 | 10494.7207 | 19642.1265 | 213.9491 | 400.4313 | 208.5251 | 0 | 69.7791 | 1945513.1528 | 125401.8335 | 1503808.8015 | 683533.734 | 0 | 174766.0477 | 0 | 1728879.1921 | 4498189.016 | 3070106.4319 | 13730198.2095 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 34459793.2994 | 64495629.654 | 1333.5214 | 3.2835 | 10494.7207 | 19642.1265 | 213.9491 | 400.4313
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0884 | 9.0362 | 1.1069 | 4 | 8566.4797 | 15349.95 | 174.6393 | 312.9295 | 210.9867 | 0 | 94.5697 | 2397388.9549 | 154253.772 | 1905337.6261 | 893154.3727 | 0 | 203510.1303 | 0 | 2165921.4938 | 5635283.4354 | 3846196.7382 | 17201046.5234 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 37930641.6133 | 67966477.9679 | 1778.2794 | 4.4278 | 8566.4797 | 15349.95 | 174.6393 | 312.9295
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.1789 | 12.0792 | 1.4834 | 4 | 7117.139 | 12179.0256 | 145.0925 | 248.2859 | 212.8896 | 0 | 90.5941 | 2943489.8716 | 189005.6172 | 2403346.6838 | 1168393.4509 | 0 | 237895.6703 | 0 | 2707431.2046 | 7044180.6238 | 4807798.0192 | 21501541.1413 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 42231136.2312 | 72266972.5858 | 2371.3737 | 5.9337 | 7117.139 | 12179.0256 | 145.0925 | 248.2859
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.589 | 16.1066 | 1.9818 | 4 | 6005.3386 | 9794.2912 | 122.4269 | 199.6699 | 214.3628 | 0 | 105.5185 | 3608583.4185 | 231179.2908 | 3025428.9255 | 1532505.209 | 0 | 279669.8328 | 0 | 3384173.0039 | 8804923.9667 | 6009541.5304 | 26876005.1776 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 47605600.2674 | 77641436.6221 | 3162.2777 | 7.9272 | 6005.3386 | 9794.2912 | 122.4269 | 199.6699
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7394 | 21.4311 | 2.6407 | 4 | 5143.1331 | 7986.6774 | 104.8497 | 162.8192 | 215.497 | 0 | 100.9519 | 4418523.9935 | 282343.6286 | 3802070.5526 | 2013655.6846 | 0 | 330556.1785 | 0 | 4230388.5147 | 11006603.1433 | 7512232.8084 | 33596374.5042 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 54325969.594 | 84361805.9487 | 4216.965 | 10.5628 | 5143.1331 | 7986.6774 | 104.8497 | 162.8192
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.1131 | 28.4128 | 3.5049 | 4 | 4470.487 | 6612.9347 | 91.1369 | 134.8136 | 216.36 | 0 | 107.2249 | 5397813.5034 | 343959.2947 | 4764268.5953 | 2644510.4823 | 0 | 391755.1344 | 0 | 5281499.7339 | 13741378.9232 | 9378773.4722 | 41943959.1394 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 62673554.2293 | 92709390.5839 | 5623.4133 | 14.0194 | 4470.487 | 6612.9347 | 91.1369 | 134.8136
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.281 | 37.4674 | 4.6255 | 4 | 3942.8813 | 5566.2492 | 80.381 | 113.4755 | 216.9842 | 0 | 107.7915 | 6570712.8521 | 417450.104 | 5944395.4553 | 3463391.6175 | 0 | 464886.4385 | 0 | 6575726.2223 | 17108690.7634 | 11677032.9945 | 52222286.4475 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 72951881.5374 | 102987717.892 | 7498.9421 | 18.5022 | 3942.8813 | 5566.2492 | 80.381 | 113.4755
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.789 | 48.938 | 6.0443 | 4 | 3530.5955 | 4772.918 | 71.976 | 97.3024 | 217.2973 | 0 | 121.9808 | 7946204.4709 | 503267.8204 | 7360401.5615 | 4505576.4061 | 0 | 551486.4558 | 0 | 8138105.3187 | 21173680.6843 | 14451472.1427 | 64630194.8604 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 85359789.9502 | 115395626.3048 | 10000 | 24.1772 | 3530.5955 | 4772.918 | 71.976 | 97.3024
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.9459 | 62.8582 | 7.7622 | 4 | 3214.5611 | 4181.9382 | 65.5332 | 85.2545 | 217.0947 | 0 | 126.964 | 9497661.9116 | 599653.3553 | 8992370.6921 | 5789257.0844 | 0 | 652855.1141 | 0 | 9957401.2814 | 25907115.5904 | 17682138.7284 | 79078453.7577 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 99808048.8476 | 129843885.2022 | 13335.2143 | 31.0487 | 3214.5611 | 4181.9382 | 65.5332 | 85.2545
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.6092 | 78.7428 | 9.7127 | 4 | 2980.3779 | 3753.4851 | 60.759 | 76.5199 | 216.1492 | 0 | 115.3813 | 11153288.3059 | 702092.6475 | 10768451.0444 | 7297930.2993 | 0 | 770098.9693 | 0 | 11969825.8939 | 31143031.6269 | 21255759.0107 | 95060477.7978 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 115790072.8877 | 145825909.2423 | 17782.7941 | 38.8508 | 2980.3779 | 3753.4851 | 60.759 | 76.5199
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.807 | 95.4176 | 11.7438 | 4 | 2815.7256 | 3455.125 | 57.4024 | 70.4374 | 214.3736 | 0 | 137.7409 | 12792333.3704 | 803131.8639 | 12557044.8563 | 8959469.021 | 0 | 900351.3226 | 0 | 14044808.8693 | 36541711.6915 | 24940469.0866 | 111539320.0816 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 132268915.1714 | 162304751.5261 | 23713.7371 | 46.9751 | 2815.7256 | 3455.125 | 57.4024 | 70.4374
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.048 | 111.8239 | 13.7256 | 4 | 2701.2545 | 3248.3306 | 55.0687 | 66.2216 | 212.2249 | 0 | 157.2446 | 14327618.8877 | 897472.7312 | 14256485.6131 | 10673372.3716 | 0 | 1035085.7738 | 0 | 16064113.7972 | 41795528.8974 | 28526307.2847 | 127575985.3565 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 148305580.4464 | 178341416.801 | 31622.7766 | 54.9025 | 2701.2545 | 3248.3306 | 55.0687 | 66.2216
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.6157 | 123.9029 | 15.2311 | 4 | 2625.3926 | 3118.3931 | 53.5222 | 63.5727 | 210.3341 | 0 | 108.0932 | 15417497.8555 | 964281.7213 | 15475682.8241 | 12002505.5865 | 0 | 1089944.596 | 0 | 17530465.9075 | 45610676.2983 | 31130223.7792 | 139221278.5683 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 159950873.6582 | 189986710.0128 | 42169.6503 | 60.9246 | 2625.3926 | 3118.3931 | 53.5222 | 63.5727
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.225 | 128.1404 | 15.9072 | 4 | 2572.1011 | 3044.149 | 52.4358 | 62.0591 | 209.5566 | 0 | 121.2333 | 15792673.3651 | 987250.3337 | 15897676.4595 | 12489998.9252 | 0 | 979768.3047 | 0 | 17997473.2814 | 46825733.6889 | 31959525.4153 | 142930099.7738 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 163659694.8637 | 193695531.2183 | 56234.1325 | 63.6288 | 2572.1011 | 3044.149 | 52.4358 | 62.0591
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.405 | 131.4968 | 16.4517 | 4 | 2531.2112 | 2987.6359 | 51.6022 | 60.907 | 208.9036 | 0 | 164.0514 | 16087361.0199 | 1005281.1599 | 16229935.8011 | 12884850.1735 | 0 | 879842.6802 | 0 | 18364035.6255 | 47779453.7159 | 32610458.9307 | 145841219.1066 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 166570814.1965 | 196606650.5511 | 74989.4209 | 65.8068 | 2531.2112 | 2987.6359 | 51.6022 | 60.907
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.1003 | 133.9892 | 16.8694 | 4 | 2499.8942 | 2945.0169 | 50.9637 | 60.0382 | 208.3941 | 0 | 212.5821 | 16304828.7366 | 1018581.5008 | 16475572.1689 | 13182606.2031 | 0 | 788923.5778 | 0 | 18630499.753 | 48472738.7164 | 33083640.1891 | 147957390.8458 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 168686985.9357 | 198722822.2903 | 100000 | 67.4777 | 2499.8942 | 2945.0169 | 50.9637 | 60.0382
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.7102 | 135.8741 | 17.1915 | 4 | 2475.9874 | 2912.7708 | 50.4764 | 59.3808 | 207.9948 | 0 | 246.4536 | 16468540.8771 | 1028590.9968 | 16660734.5519 | 13411278.2355 | 0 | 710429.4003 | 0 | 18829033.884 | 48989283.8003 | 33436192.8228 | 149534084.5686 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 170263679.6585 | 200299516.0131 | 133352.1432 | 68.766 | 2475.9874 | 2912.7708 | 50.4764 | 59.3808
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.1 | 139.2057 | 17.6415 | 4 | 2457.5052 | 2883.1469 | 50.0996 | 58.7768 | 207.3187 | 0 | 326.668 | 16756348.0991 | 1046181.2838 | 16986754.3007 | 13815865.2057 | 0 | 692314.0649 | 0 | 19226010.5522 | 50022135.6597 | 34141135.4398 | 152686744.606 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173416339.6958 | 203452176.0505 | 177827.941 | 70.566 | 2457.5052 | 2883.1469 | 50.0996 | 58.7768
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.1 | 139.1971 | 17.716 | 4 | 2443.5147 | 2867.3674 | 49.8144 | 58.4552 | 207.3125 | 0 | 314.2845 | 16755601.2628 | 1046135.6491 | 16985907.4834 | 13815710.677 | 0 | 610342.5933 | 0 | 19193342.0896 | 49937139.0213 | 34083123.4876 | 152427302.2641 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173156897.354 | 203192733.7086 | 237137.3706 | 70.8639 | 2443.5147 | 2867.3674 | 49.8144 | 58.4552
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.6427 | 139.4683 | 17.8014 | 4 | 2433.0066 | 2854.8249 | 49.6001 | 58.1995 | 207.2486 | 0 | 412.5296 | 16778949.7484 | 1047562.3108 | 17012383.7043 | 13849908.8818 | 0 | 552947.2457 | 0 | 19204283.2375 | 49965605.6437 | 34102552.5424 | 152514193.3145 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173243788.4044 | 203279624.759 | 316227.766 | 71.2056 | 2433.0066 | 2854.8249 | 49.6001 | 58.1995
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.6561 | 139.9804 | 17.8991 | 4 | 2425.0651 | 2844.5801 | 49.4382 | 57.9906 | 207.1341 | 0 | 407.2716 | 16822993.3801 | 1050253.3612 | 17062338.6759 | 13913879.4319 | 0 | 515811.2989 | 0 | 19252457.6977 | 50090945.7074 | 34188099.7113 | 152896779.2644 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173626374.3543 | 203662210.7089 | 421696.5034 | 71.5966 | 2425.0651 | 2844.5801 | 49.4382 | 57.9906
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.3749 | 140.3422 | 17.9704 | 4 | 2419.0631 | 2836.9147 | 49.3159 | 57.8343 | 207.0524 | 0 | 398.7316 | 16854079.1017 | 1052152.5732 | 17097605.4652 | 13959247.6924 | 0 | 486054.5309 | 0 | 19285164.3517 | 50176041.712 | 34246179.483 | 153156524.91 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173886119.9998 | 203921956.3545 | 562341.3252 | 71.8816 | 2419.0631 | 2836.9147 | 49.3159 | 57.8343
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.0936 | 140.7035 | 18.0338 | 4 | 2414.5312 | 2830.9128 | 49.2235 | 57.712 | 206.9712 | 0 | 392.3118 | 16885105.2966 | 1054048.0538 | 17132812.035 | 14004513.4685 | 0 | 465308.0314 | 0 | 19321296.8852 | 50270051.1525 | 34310342.8578 | 153443477.7808 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174173072.8706 | 204208909.2253 | 749894.2093 | 72.1354 | 2414.5312 | 2830.9128 | 49.2235 | 57.712
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.464 | 140.8884 | 18.0722 | 4 | 2411.1124 | 2826.611 | 49.1538 | 57.6243 | 206.9288 | 0 | 404.442 | 16900971.9702 | 1055017.3586 | 17150819.3554 | 14027732.625 | 0 | 446961.6173 | 0 | 19336786.1413 | 50310351.0195 | 34337848.3452 | 153566488.4326 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174296083.5225 | 204331919.8771 | 1000000 | 72.2887 | 2411.1124 | 2826.611 | 49.1538 | 57.6243
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.687 | 140.4944 | 18.0437 | 4 | 2408.3589 | 2824.514 | 49.0977 | 57.5815 | 207.0137 | 0 | 507.9824 | 16867150.4121 | 1052951.1491 | 17112437.0742 | 13978864.7596 | 0 | 417148.7611 | 0 | 19277135.3409 | 50155151.8728 | 34231921.7385 | 153092761.1083 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 173822356.1981 | 203858192.5528 | 1333521.4322 | 72.1746 | 2408.3589 | 2824.514 | 49.0977 | 57.5815
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.3675 | 141.3409 | 18.1465 | 4 | 2406.423 | 2820.2196 | 49.0582 | 57.494 | 206.8272 | 0 | 401.1983 | 16939786.3546 | 1057388.4495 | 17194878.3995 | 14084409.581 | 0 | 426607.1002 | 0 | 19384197.2551 | 50433705.0121 | 34422039.9798 | 153943012.1317 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174672607.2216 | 204708443.5762 | 1778279.41 | 72.586 | 2406.423 | 2820.2196 | 49.0582 | 57.494
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.5092 | 141.4112 | 18.1618 | 4 | 2404.9966 | 2818.4457 | 49.0291 | 57.4578 | 206.8108 | 0 | 387.6158 | 16945805.3438 | 1057756.1239 | 17201711.7038 | 14093285.3416 | 0 | 418454.3662 | 0 | 19389635.023 | 50447852.9687 | 34431696.2509 | 153986197.1219 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174715792.2118 | 204751628.5664 | 2371373.7057 | 72.647 | 2404.9966 | 2818.4457 | 49.0291 | 57.4578
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.6038 | 141.458 | 18.1726 | 4 | 2403.9248 | 2817.1281 | 49.0073 | 57.431 | 206.7997 | 0 | 410.6184 | 16949815.833 | 1058001.1057 | 17206264.9279 | 14099211.7748 | 0 | 412118.792 | 0 | 19392910.849 | 50456375.9961 | 34437513.3922 | 154012212.6706 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174741807.7605 | 204777644.1151 | 3162277.6602 | 72.6902 | 2403.9248 | 2817.1281 | 49.0073 | 57.431
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.677 | 141.4941 | 18.1808 | 4 | 2403.1198 | 2816.1362 | 48.9908 | 57.4107 | 206.7912 | 0 | 398.7155 | 16952916.2876 | 1058190.4967 | 17209785.0468 | 14103793.5433 | 0 | 407360.7139 | 0 | 19395497.9744 | 50463107.1658 | 34442107.5538 | 154032758.7824 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174762353.8723 | 204798190.2269 | 4216965.0343 | 72.7231 | 2403.1198 | 2816.1362 | 48.9908 | 57.4107
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.7307 | 141.5207 | 18.1869 | 4 | 2402.5154 | 2815.3931 | 48.9785 | 57.3956 | 206.785 | 0 | 409.993 | 16955191.0159 | 1058329.4477 | 17212367.7187 | 14107157.1449 | 0 | 403755.6127 | 0 | 19397352.3666 | 50467931.9138 | 34445400.5435 | 154047485.7639 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174777080.8537 | 204812917.2084 | 5623413.2519 | 72.7475 | 2402.5154 | 2815.3931 | 48.9785 | 57.3956
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.7696 | 141.5399 | 18.1914 | 4 | 2402.0617 | 2814.8372 | 48.9693 | 57.3843 | 206.7804 | 0 | 413.8639 | 16956836.873 | 1058429.984 | 17214236.4097 | 14109592.6137 | 0 | 401020.9573 | 0 | 19398645.5667 | 50471296.5553 | 34447696.9804 | 154057755.9403 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174787351.0301 | 204823187.3847 | 7498942.0933 | 72.7656 | 2402.0617 | 2814.8372 | 48.9693 | 57.3843
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.8085 | 141.5592 | 18.1953 | 4 | 2401.7213 | 2814.408 | 48.9623 | 57.3755 | 206.776 | 0 | 400.815 | 16958489.2448 | 1058530.918 | 17216112.5179 | 14112029.6172 | 0 | 399097.0192 | 0 | 19400261.1336 | 50475499.929 | 34450565.8693 | 154070586.2489 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 174800181.3388 | 204836017.6934 | 10000000 | 72.7812 | 2401.7213 | 2814.408 | 48.9623 | 57.3755
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.27849 | 0.019714 | 4 | 286445.5586 | 676512.2426 | 5839.5802 | 13791.6171 | 138.4069 | 0 | 52.7437 | 178453.9611 | 8132.5212 | 120968.1199 | 66883.0144 | 0 | 58766.413 | 0 | 168949.5715 | 439572.1288 | 300017.0102 | 1341742.74 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 22588047.1558 | 53347276.5669 | 100 | 0.078856 | 286445.5586 | 676512.2426 | 5839.5802 | 13791.6171
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.43906 | 0.038941 | 4 | 148313.058 | 345787.0181 | 3023.5623 | 7049.3361 | 153.3107 | 0 | 52.6542 | 260840.2943 | 13347.6004 | 172396.2961 | 86898.0971 | 0 | 65581.4304 | 0 | 233634.8501 | 607869.9549 | 414883.7347 | 1855452.2579 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23101756.6737 | 53860986.0848 | 133.3521 | 0.15576 | 148313.058 | 345787.0181 | 3023.5623 | 7049.3361
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.64976 | 0.066645 | 4 | 88961.6773 | 204345.4317 | 1813.6041 | 4165.858 | 165.6388 | 0 | 251.6618 | 359556.2732 | 20419.3326 | 233990.1376 | 111833.6796 | 0 | 71447.3532 | 0 | 310926.2427 | 808966.3038 | 552136.1249 | 2469275.4477 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23715579.8635 | 54474809.2746 | 177.8279 | 0.26658 | 88961.6773 | 204345.4317 | 1813.6041 | 4165.858
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.95549 | 0.10969 | 4 | 55971.1873 | 126078.1001 | 1141.0484 | 2570.2726 | 176.8162 | 0 | 333.5999 | 492809.1129 | 31553.3772 | 315971.7936 | 149327.422 | 0 | 79321.2942 | 0 | 416903.3699 | 1084697.05 | 740328.0249 | 3310911.4447 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 24557215.8605 | 55316445.2716 | 237.1374 | 0.43875 | 55971.1873 | 126078.1001 | 1141.0484 | 2570.2726
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7211 | 1.4071 | 0.16622 | 4 | 38487.651 | 84749.3693 | 784.6228 | 1727.7305 | 185.8326 | 0 | 434.1297 | 648281.0606 | 41962.8415 | 430361.8525 | 193827.9313 | 0 | 88092.4645 | 0 | 546985.1987 | 1423143.285 | 971324.5347 | 4343979.1689 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 25590283.5847 | 56349512.9958 | 316.2278 | 0.6649 | 38487.651 | 84749.3693 | 784.6228 | 1727.7305
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5184 | 2.0096 | 0.24069 | 4 | 27879.4569 | 59827.9906 | 568.3604 | 1219.6745 | 193.467 | 0 | 566.2269 | 832143.2286 | 53854.605 | 572362.843 | 248977.1152 | 0 | 99205.3474 | 0 | 704551.8243 | 1833099.3235 | 1251127.9547 | 5595322.2418 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 26841626.6576 | 57600856.0687 | 421.6965 | 0.96277 | 27879.4569 | 59827.9906 | 568.3604 | 1219.6745
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5842 | 2.8191 | 0.34063 | 4 | 20842.3973 | 43417.7565 | 424.9005 | 885.1297 | 199.8216 | 0 | 87.3052 | 1055261.4358 | 68253.2618 | 750364.1538 | 321805.317 | 0 | 113374.7927 | 0 | 900532.9948 | 2343002.1278 | 1599147.0961 | 7151741.1799 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 28398045.5957 | 59157275.0068 | 562.3413 | 1.3625 | 20842.3973 | 43417.7565 | 424.9005 | 885.1297
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9654 | 3.8716 | 0.47091 | 4 | 16075.0278 | 32404.6978 | 327.7112 | 660.6136 | 204.8373 | 0 | 88.4791 | 1318914.5105 | 85225.6994 | 967157.9544 | 415671.712 | 0 | 129572.2669 | 0 | 1137451.4358 | 2959415.3127 | 2019861.7608 | 9033270.6524 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 30279575.0683 | 61038804.4793 | 749.8942 | 1.8836 | 16075.0278 | 32404.6978 | 327.7112 | 660.6136
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7831 | 5.2513 | 0.64164 | 4 | 12697.9455 | 24682.6167 | 258.8648 | 503.1885 | 208.652 | 0 | 71.9532 | 1634641.4379 | 105495.8379 | 1234241.037 | 538712.9421 | 0 | 149371.921 | 0 | 1428360.6386 | 3716301.3847 | 2536452.0574 | 11343577.2566 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 32589881.6725 | 63349111.0835 | 1000 | 2.5665 | 12697.9455 | 24682.6167 | 258.8648 | 503.1885
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1601 | 7.0863 | 0.86977 | 4 | 10192.6523 | 19033.8735 | 207.791 | 388.0313 | 212.0422 | 0 | 87.0698 | 2019298.6555 | 130119.4435 | 1568635.793 | 699911.8052 | 0 | 171470.7661 | 0 | 1789880.2207 | 4656901.1794 | 3178430.7447 | 14214648.6081 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 35460953.0239 | 66220182.435 | 1333.5214 | 3.4791 | 10192.6523 | 19033.8735 | 207.791 | 388.0313
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.3079 | 9.5034 | 1.17 | 4 | 8338.5702 | 14911.1239 | 169.993 | 303.9834 | 214.5262 | 0 | 96.2263 | 2484336.3269 | 159794.9047 | 1983757.8981 | 912972.2338 | 0 | 198996.7505 | 0 | 2238544.6645 | 5824234.0283 | 3975159.4003 | 17777796.207 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 39024100.6229 | 69783330.0339 | 1778.2794 | 4.68 | 8338.5702 | 14911.1239 | 169.993 | 303.9834
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.4541 | 12.6903 | 1.5661 | 4 | 6936.1191 | 11846.1342 | 141.4022 | 241.4995 | 216.4552 | 0 | 105.7006 | 3048096.087 | 195649.1301 | 2500132.0525 | 1193626.3998 | 0 | 231956.293 | 0 | 2796089.3854 | 7274851.0239 | 4965235.307 | 22205635.6787 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 43451940.0946 | 74211169.5056 | 2371.3737 | 6.2646 | 6936.1191 | 11846.1342 | 141.4022 | 241.4995
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.94 | 16.9092 | 2.0907 | 4 | 5857.7954 | 9535.9057 | 119.4191 | 194.4023 | 217.9506 | 0 | 88.7138 | 3735099.1448 | 239184.6922 | 3145454.9813 | 1564882.1416 | 0 | 272073.5643 | 0 | 3493110.8644 | 9088357.9336 | 6202991.0368 | 27741154.3589 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 48987458.7748 | 79746688.1858 | 3162.2777 | 8.3628 | 5857.7954 | 9535.9057 | 119.4191 | 194.4023
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.199 | 22.494 | 2.785 | 4 | 5019.6493 | 7780.8177 | 102.3323 | 158.6225 | 219.1038 | 0 | 117.7942 | 4572910.456 | 292074.418 | 3952190.9368 | 2056170.0407 | 0 | 321168.3396 | 0 | 4365860.5345 | 11359073.5497 | 7752801.1033 | 34672249.3785 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 55918553.7943 | 86677783.2054 | 4216.965 | 11.1399 | 5019.6493 | 7780.8177 | 102.3323 | 158.6225
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.7005 | 29.8054 | 3.6942 | 4 | 4365.8703 | 6447.4577 | 89.0042 | 131.4401 | 219.9797 | 0 | 97.6338 | 5584463.4374 | 355675.4592 | 4950182.4989 | 2699279.0721 | 0 | 379985.0598 | 0 | 5448138.3556 | 14174938.4345 | 9674686.7474 | 43267349.0649 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 64513653.4807 | 95272882.8918 | 5623.4133 | 14.7768 | 4365.8703 | 6447.4577 | 89.0042 | 131.4401
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0238 | 39.2772 | 4.8721 | 4 | 3852.7958 | 5431.1384 | 78.5445 | 110.7211 | 220.6093 | 0 | 108.1821 | 6794935.49 | 431465.0578 | 6173016.992 | 3532926.9044 | 0 | 450207.7417 | 0 | 6779195.3525 | 17638075.7031 | 12038349.0936 | 53838172.3351 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 75084476.751 | 105843706.162 | 7498.9421 | 19.4883 | 3852.7958 | 5431.1384 | 78.5445 | 110.7211
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.7294 | 51.2723 | 6.3625 | 4 | 3451.6588 | 4660.2766 | 70.3667 | 95.006 | 220.911 | 0 | 140.383 | 8214319.3832 | 519954.1335 | 7639959.8833 | 4594314.5646 | 0 | 533776.7438 | 0 | 8385906.6363 | 21818408.8816 | 14891512.3852 | 66598152.6115 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 87844457.0274 | 118603686.4384 | 10000 | 25.4499 | 3451.6588 | 4660.2766 | 70.3667 | 95.006
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.0669 | 65.7694 | 8.1598 | 4 | 3144.8218 | 4087.2226 | 64.1114 | 83.3236 | 220.6691 | 0 | 115.7885 | 9809213.7827 | 618961.3832 | 9324030.2014 | 5897009.724 | 0 | 631563.8554 | 0 | 10249503.7892 | 26667106.3972 | 18200848.0703 | 81398237.2034 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 102644541.6193 | 133403771.0303 | 13335.2143 | 32.6392 | 3144.8218 | 4087.2226 | 64.1114 | 83.3236
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.8442 | 82.2267 | 10.1901 | 4 | 2918.006 | 3672.6401 | 59.4875 | 74.8717 | 219.6561 | 0 | 131.1391 | 11503249.5562 | 723695.8137 | 11147952.4357 | 7421976.4365 | 0 | 744919.4613 | 0 | 12301299.5443 | 32005458.0709 | 21844382.7798 | 97692934.0984 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 118939238.5142 | 149698467.9253 | 17782.7941 | 40.7605 | 2918.006 | 3672.6401 | 59.4875 | 74.8717
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.128 | 99.4559 | 12.298 | 4 | 2758.6438 | 3383.9347 | 56.2387 | 68.9861 | 217.7878 | 0 | 147.4214 | 13176704.1209 | 826777.0776 | 12980434.8166 | 9097865.3715 | 0 | 872424.9981 | 0 | 14412140.49 | 37497433.2185 | 25592768.6669 | 114456548.7601 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 135702853.176 | 166462082.587 | 23713.7371 | 49.1919 | 2758.6438 | 3383.9347 | 56.2387 | 68.9861
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.3199 | 116.3312 | 14.3465 | 4 | 2647.6754 | 3183.6805 | 53.9764 | 64.9036 | 215.5701 | 0 | 154.1421 | 14738003.3065 | 922644.3042 | 14714369.9981 | 10817749.3286 | 0 | 1003773.5176 | 0 | 16456650.7774 | 42816829.5996 | 29223365.9996 | 130693386.8316 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 151939691.2475 | 182698920.6585 | 31622.7766 | 57.3861 | 2647.6754 | 3183.6805 | 53.9764 | 64.9036
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.9519 | 130.5317 | 16.0719 | 4 | 2575.4421 | 3053.9061 | 52.5039 | 62.258 | 213.2799 | 0 | 154.5086 | 16002842.3575 | 1000110.6937 | 16134570.3447 | 12352109.6441 | 0 | 1107218.1435 | 0 | 18172771.9616 | 47281824.8959 | 32270817.0358 | 144322265.0767 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 165568569.4926 | 196327798.9036 | 42169.6503 | 64.2874 | 2575.4421 | 3053.9061 | 52.5039 | 62.258
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.5714 | 134.8639 | 16.7639 | 4 | 2524.8343 | 2983.5476 | 51.4722 | 60.8237 | 212.4703 | 0 | 160.0537 | 16380880.9354 | 1023231.7301 | 16561563.0611 | 12842553.2192 | 0 | 994637.6355 | 0 | 18643117.9667 | 48505568.7201 | 33106047.3413 | 148057600.6095 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 169303905.0254 | 200063134.4364 | 56234.1325 | 67.0555 | 2524.8343 | 2983.5476 | 51.4722 | 60.8237
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.6265 | 138.2225 | 17.3124 | 4 | 2486.1383 | 2930.3171 | 50.6833 | 59.7385 | 211.8072 | 0 | 203.2535 | 16671613.9096 | 1041003.3279 | 16890703.7249 | 13231125.2708 | 0 | 891920.9459 | 0 | 19003283.1998 | 49442644.7766 | 33745621.0048 | 150917916.1602 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 172164220.5761 | 202923449.9871 | 74989.4209 | 69.2497 | 2486.1383 | 2930.3171 | 50.6833 | 59.7385
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208 | 143.3318 | 18.0058 | 4 | 2456.3722 | 2883.4463 | 50.0765 | 58.783 | 210.7937 | 0 | 319.5642 | 17110126.503 | 1067792.4423 | 17388369.4153 | 13830373.0265 | 0 | 863800.2797 | 0 | 19601580.0501 | 50999290.4533 | 34808063.665 | 155669395.8353 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 176915700.2511 | 207674929.6622 | 100000 | 72.0232 | 2456.3722 | 2883.4463 | 50.0765 | 58.783
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.5 | 143.0509 | 18.1051 | 4 | 2433.5425 | 2858.275 | 49.6111 | 58.2698 | 210.8392 | 0 | 237.8677 | 17086129.8433 | 1066326.951 | 17361098.1912 | 13798366.7159 | 0 | 729651.8261 | 0 | 19516213.6757 | 50777184.6583 | 34656471.8961 | 154991443.7576 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 176237748.1735 | 206996977.5845 | 133352.1432 | 72.4202 | 2433.5425 | 2858.275 | 49.6111 | 58.2698
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.8781 | 143.7679 | 18.2766 | 4 | 2416.5754 | 2837.3205 | 49.2652 | 57.8426 | 210.6735 | 0 | 272.2159 | 17147346.5326 | 1070065.383 | 17430676.9831 | 13885534.5283 | 0 | 646719.2452 | 0 | 19570333.6422 | 50917993.7096 | 34752576.9669 | 155421246.991 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 176667551.4069 | 207426780.8179 | 177827.941 | 73.1066 | 2416.5754 | 2837.3205 | 49.2652 | 57.8426
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.8218 | 144.7798 | 18.4575 | 4 | 2403.7064 | 2820.3283 | 49.0028 | 57.4962 | 210.4438 | 0 | 324.8171 | 17233595.4835 | 1075331.8917 | 17528754.8761 | 14008576.534 | 0 | 591825.983 | 0 | 19670853.0597 | 51179524.6144 | 34931077.1834 | 156219539.6259 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 177465844.0417 | 208225073.4528 | 237137.3706 | 73.8301 | 2403.7064 | 2820.3283 | 49.0028 | 57.4962
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.2614 | 145.5235 | 18.5928 | 4 | 2393.9432 | 2807.5334 | 48.8038 | 57.2354 | 210.2722 | 0 | 354.1302 | 17296882.2664 | 1079195.8355 | 17600756.5542 | 14099660.2832 | 0 | 547156.4301 | 0 | 19743224.0341 | 51367819.0446 | 35059592.001 | 156794286.4491 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178040590.865 | 208799820.276 | 316227.766 | 74.3713 | 2393.9432 | 2807.5334 | 48.8038 | 57.2354
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.3091 | 146.0618 | 18.6929 | 4 | 2386.5484 | 2797.9248 | 48.653 | 57.0395 | 210.1466 | 0 | 348.1287 | 17342622.2345 | 1081988.2276 | 17652813.6131 | 14165935.3096 | 0 | 511124.2326 | 0 | 19794248.6108 | 51500574.5266 | 35150200.3454 | 157199507.1003 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178445811.5162 | 209205040.9272 | 421696.5034 | 74.7715 | 2386.5484 | 2797.9248 | 48.653 | 57.0395
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.0472 | 146.4391 | 18.7654 | 4 | 2380.9562 | 2790.7416 | 48.539 | 56.893 | 210.0575 | 0 | 332.6355 | 17374664.9835 | 1083944.295 | 17689290.9576 | 14212609.308 | 0 | 482120.687 | 0 | 19828625.7901 | 51590016.8955 | 35211246.6 | 157472519.5168 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178718823.9327 | 209478053.3437 | 562341.3252 | 75.0618 | 2380.9562 | 2790.7416 | 48.539 | 56.893
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.6003 | 146.7211 | 18.82 | 4 | 2376.733 | 2785.3314 | 48.4529 | 56.7827 | 209.9906 | 0 | 334.6108 | 17398588.6782 | 1085404.6662 | 17716530.5404 | 14247576.7861 | 0 | 459519.4974 | 0 | 19853971.8656 | 51655962.1847 | 35256255.615 | 157673809.8336 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178920114.2495 | 209679343.6605 | 749894.2093 | 75.2799 | 2376.733 | 2785.3314 | 48.4529 | 56.7827
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.9876 | 146.9179 | 18.8594 | 4 | 2373.5478 | 2781.2925 | 48.388 | 56.7004 | 209.9435 | 0 | 337.2789 | 17415284.15 | 1086423.7735 | 17735542.5476 | 14272056.4876 | 0 | 441679.0788 | 0 | 19870884.5546 | 51699965.5323 | 35286288.8039 | 157808124.9283 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179054429.3442 | 209813658.7552 | 1000000 | 75.4375 | 2373.5478 | 2781.2925 | 48.388 | 56.7004
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.7038 | 147.2841 | 18.9139 | 4 | 2370.9761 | 2777.5444 | 48.3356 | 56.624 | 209.8584 | 0 | 338.1731 | 17446328.0245 | 1088318.6501 | 17770899.2844 | 14317376.9532 | 0 | 432515.5847 | 0 | 19911621.0138 | 51805953.4429 | 35358627.7307 | 158131640.6844 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179377945.1002 | 210137174.5113 | 1333521.4322 | 75.6557 | 2370.9761 | 2777.5444 | 48.3356 | 56.624
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9085 | 147.3875 | 18.9352 | 4 | 2369.2083 | 2775.3203 | 48.2995 | 56.5787 | 209.8332 | 0 | 334.8536 | 17455086.5595 | 1088853.2428 | 17780875.9061 | 14330308.0015 | 0 | 422163.8956 | 0 | 19920142.1661 | 51828123.7333 | 35373759.4094 | 158199312.9144 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179445617.3303 | 210204846.7413 | 1778279.41 | 75.7408 | 2369.2083 | 2775.3203 | 48.2995 | 56.5787
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.0593 | 147.4635 | 18.951 | 4 | 2367.879 | 2773.6525 | 48.2724 | 56.5447 | 209.8147 | 0 | 328.6266 | 17461530.8621 | 1089246.5775 | 17788216.8051 | 14339833.7033 | 0 | 414258.6997 | 0 | 19926303.7926 | 51844155.0214 | 35384701.093 | 158248246.5547 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179494550.9706 | 210253780.3816 | 2371373.7057 | 75.8039 | 2367.879 | 2773.6525 | 48.2724 | 56.5447
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.1667 | 147.5177 | 18.9625 | 4 | 2366.88 | 2772.4067 | 48.2521 | 56.5193 | 209.8015 | 0 | 318.7321 | 17466115.4114 | 1089526.3979 | 17793439.3888 | 14346619.6817 | 0 | 408191.9114 | 0 | 19930518.1886 | 51855120.0152 | 35392184.9265 | 158281715.9214 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179528020.3373 | 210287249.7483 | 3162277.6602 | 75.8501 | 2366.88 | 2772.4067 | 48.2521 | 56.5193
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.2445 | 147.5568 | 18.971 | 4 | 2366.1297 | 2771.4748 | 48.2368 | 56.5003 | 209.7919 | 0 | 325.2261 | 17469431.6843 | 1089728.8071 | 17797217.2855 | 14351533.2083 | 0 | 403568.6525 | 0 | 19933477.0587 | 51862818.3884 | 35397439.2244 | 158305214.3091 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179551518.725 | 210310748.136 | 4216965.0343 | 75.8841 | 2366.1297 | 2771.4748 | 48.2368 | 56.5003
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.2982 | 147.5838 | 18.9771 | 4 | 2365.5663 | 2770.7808 | 48.2253 | 56.4861 | 209.7852 | 0 | 319.1386 | 17471717.4861 | 1089868.3207 | 17799821.317 | 14354925.1982 | 0 | 400017.7027 | 0 | 19935376.5096 | 51867760.3701 | 35400812.2285 | 158320299.133 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179566603.5489 | 210325832.9599 | 5623413.2519 | 75.9085 | 2365.5663 | 2770.7808 | 48.2253 | 56.4861
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.3519 | 147.6109 | 18.9825 | 4 | 2365.1434 | 2770.2439 | 48.2166 | 56.4752 | 209.7786 | 0 | 312.6013 | 17474012.4971 | 1090008.3959 | 17802435.8783 | 14358319.1736 | 0 | 397526.6417 | 0 | 19937698.0088 | 51873800.4346 | 35404934.6966 | 158338735.7267 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179585040.1425 | 210344269.5536 | 7498942.0933 | 75.9299 | 2365.1434 | 2770.2439 | 48.2166 | 56.4752
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.3714 | 147.6206 | 18.9853 | 4 | 2364.8261 | 2769.8661 | 48.2102 | 56.4675 | 209.7762 | 0 | 315.9535 | 17474831.7376 | 1090058.3978 | 17803369.1966 | 14359545.6679 | 0 | 395366.7572 | 0 | 19938036.9853 | 51874682.382 | 35405536.6438 | 158341427.7682 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 179587732.184 | 210346961.5951 | 10000000 | 75.9412 | 2364.8261 | 2769.8661 | 48.2102 | 56.4675
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.30343 | 0.022692 | 4 | 255545.7894 | 602478.5769 | 5209.6466 | 12282.3407 | 141.9557 | 0 | 59.9621 | 192403.2562 | 9006.0582 | 129249.5983 | 69886.5454 | 0 | 60128.5043 | 0 | 179662.8453 | 467445.8696 | 319041.4111 | 1426824.0884 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23195697.9212 | 54686524.5158 | 100 | 0.090769 | 255545.7894 | 602478.5769 | 5209.6466 | 12282.3407
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3128 | 0.4702 | 0.04335 | 4 | 136789.8081 | 318395.928 | 2788.6453 | 6490.9317 | 156.5191 | 0 | 59.803 | 277063.1427 | 14546.9519 | 181729.6542 | 90284.7558 | 0 | 66199.2835 | 0 | 245631.2773 | 639082.1977 | 436186.7317 | 1950723.9947 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23719597.8274 | 55210424.4221 | 133.3521 | 0.1734 | 136789.8081 | 318395.928 | 2788.6453 | 6490.9317
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.7011 | 0.074491 | 4 | 81848.8228 | 187535.778 | 1668.599 | 3823.1705 | 169.2172 | 0 | 261.0168 | 384651.1838 | 22618.3322 | 248044.6819 | 117806.8248 | 0 | 72488.0805 | 0 | 329787.5503 | 858039.557 | 585629.6286 | 2619065.8391 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 24387939.6718 | 55878766.2665 | 177.8279 | 0.29796 | 81848.8228 | 187535.778 | 1668.599 | 3823.1705
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 1.02 | 0.11893 | 4 | 53039.2952 | 119237.7581 | 1081.2778 | 2430.823 | 179.7877 | 0 | 339.5363 | 517625.6849 | 33483.534 | 332720.309 | 155311.1344 | 0 | 78653.9447 | 0 | 435939.8967 | 1134226.1877 | 774132.6791 | 3462093.3705 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 25230967.2032 | 56721793.7979 | 237.1374 | 0.4757 | 53039.2952 | 119237.7581 | 1081.2778 | 2430.823
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7989 | 1.5162 | 0.18024 | 4 | 36523.8872 | 80202.1431 | 744.5888 | 1635.0292 | 189.281 | 0 | 447.9829 | 683095.6732 | 44216.4629 | 456876.1253 | 200743.1524 | 0 | 88583.329 | 0 | 574670.7496 | 1495175.4094 | 1020487.9397 | 4563848.8414 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 26332722.6742 | 57823549.2688 | 316.2278 | 0.72097 | 36523.8872 | 80202.1431 | 744.5888 | 1635.0292
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6157 | 2.1523 | 0.25915 | 4 | 26650.9085 | 57030.0782 | 543.3148 | 1162.6353 | 196.9496 | 0 | 575.5495 | 873171.0349 | 56504.8642 | 604665.0267 | 257323.4383 | 0 | 99451.1389 | 0 | 737535.0462 | 1918914.9009 | 1309698.8496 | 5857264.2998 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 27626138.1325 | 59116964.7272 | 421.6965 | 1.0366 | 26650.9085 | 57030.0782 | 543.3148 | 1162.6353
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.689 | 2.9929 | 0.36351 | 4 | 20088.6768 | 41746.2476 | 409.5348 | 851.0537 | 203.2512 | 0 | 82.8127 | 1100563.4091 | 71172.6767 | 787155.4797 | 330892.9843 | 0 | 112578.9332 | 0 | 936921.7584 | 2437678.2263 | 1663765.4787 | 7440728.9465 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 29209602.7792 | 60700429.3739 | 562.3413 | 1.454 | 20088.6768 | 41746.2476 | 409.5348 | 851.0537
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1117 | 4.1109 | 0.50225 | 4 | 15516.4904 | 31191.2539 | 316.3246 | 635.8759 | 208.343 | 0 | 53.7071 | 1375765.2795 | 88879.8231 | 1014693.0233 | 427960.0843 | 0 | 128933.6326 | 0 | 1184130.4187 | 3080864.4509 | 2102753.2932 | 9403980.0055 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 31172853.8382 | 62663680.4329 | 749.8942 | 2.009 | 15516.4904 | 31191.2539 | 316.3246 | 635.8759
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9365 | 5.5385 | 0.68005 | 4 | 12321.9825 | 23898.6357 | 251.2003 | 487.206 | 212.0999 | 0 | 57.5666 | 1697139.7703 | 109501.7891 | 1287947.4422 | 552048.5151 | 0 | 146851.8007 | 0 | 1479460.8338 | 3849253.6104 | 2627194.6833 | 11749398.445 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 33518272.2777 | 65009098.8724 | 1000 | 2.7202 | 12321.9825 | 23898.6357 | 251.2003 | 487.206
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3453 | 7.4591 | 0.91992 | 4 | 9911.5451 | 18469.5846 | 202.0603 | 376.5275 | 215.5534 | 0 | 91.7363 | 2093690.2851 | 134873.181 | 1634299.7876 | 716246.9208 | 0 | 167810.3992 | 0 | 1851299.0237 | 4816700.3061 | 3287496.9322 | 14702416.8358 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 36471290.6685 | 67962117.2632 | 1333.5214 | 3.6797 | 9911.5451 | 18469.5846 | 202.0603 | 376.5275
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.5294 | 9.9825 | 1.2349 | 4 | 8123.9796 | 14499.2703 | 165.6183 | 295.5872 | 218.0595 | 0 | 122.2935 | 2572205.3426 | 165391.5517 | 2063359.1793 | 932954.3236 | 0 | 193800.1764 | 0 | 2311807.1237 | 6014847.919 | 4105257.2975 | 18359622.9137 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 40128496.7465 | 71619323.3411 | 1778.2794 | 4.9395 | 8123.9796 | 14499.2703 | 165.6183 | 295.5872
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7442 | 13.3262 | 1.6524 | 4 | 6762.7716 | 11527.3215 | 137.8682 | 235 | 220.018 | 0 | 102.2352 | 3155414.1656 | 202460.7008 | 2599854.3695 | 1219834.0518 | 0 | 225447.9746 | 0 | 2887174.3923 | 7511835.5279 | 5126982.1006 | 22929003.2831 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 44697877.1159 | 76188703.7105 | 2371.3737 | 6.6094 | 6762.7716 | 11527.3215 | 137.8682 | 235
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.3273 | 17.7579 | 2.2057 | 4 | 5714.3614 | 9283.5976 | 116.495 | 189.2587 | 221.5376 | 0 | 105.1053 | 3867005.7816 | 247525.7724 | 3271125.7314 | 1599731.8897 | 0 | 264116.7167 | 0 | 3607307.2978 | 9385473.6284 | 6405778.6036 | 28648065.4215 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 50416939.2542 | 81907765.8489 | 3162.2777 | 8.8228 | 5714.3614 | 9283.5976 | 116.495 | 189.2587
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.6742 | 23.5922 | 2.9345 | 4 | 4901.8515 | 7584.6836 | 99.9309 | 154.624 | 222.7037 | 0 | 106.6043 | 4730256.7943 | 301984.9974 | 4105821.1712 | 2099739.4 | 0 | 310683.8704 | 0 | 4503909.631 | 11718248.9809 | 7997945.7154 | 35768590.5605 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 57537464.3933 | 89028290.9879 | 4216.965 | 11.7379 | 4901.8515 | 7584.6836 | 99.9309 | 154.624
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.3259 | 31.2578 | 3.8919 | 4 | 4265.2876 | 6288.1211 | 86.9537 | 128.1919 | 223.5928 | 0 | 100.4597 | 5776484.7819 | 367720.1418 | 5142223.4592 | 2756512.4823 | 0 | 367167.3424 | 0 | 5619942.201 | 14621936.7982 | 9979772.3155 | 44631759.5223 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 66400633.355 | 97891459.9497 | 5623.4133 | 15.5677 | 4265.2876 | 6288.1211 | 86.9537 | 128.1919
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.8131 | 41.1633 | 5.1293 | 4 | 3766.2909 | 5301.1375 | 76.7809 | 108.0709 | 224.2259 | 0 | 121.5022 | 7025501.4839 | 445865.7616 | 6409038.6965 | 3606073.8282 | 0 | 434250.3788 | 0 | 6989084.7581 | 18184164.8823 | 12411066.1794 | 55505045.9688 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 77273919.8015 | 108764746.3962 | 7498.9421 | 20.5172 | 3766.2909 | 5301.1375 | 76.7809 | 108.0709
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.6916 | 53.6727 | 6.6907 | 4 | 3376.4552 | 4553.1116 | 68.8336 | 92.8213 | 224.5132 | 0 | 118.1348 | 8486439.4293 | 536876.7268 | 7924788.8323 | 4684991.8113 | 0 | 513981.1713 | 0 | 8637360.4087 | 22472640.0172 | 15338038.5783 | 68595116.9752 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 90363990.808 | 121854817.4026 | 10000 | 26.763 | 3376.4552 | 4553.1116 | 68.8336 | 92.8213
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.2311 | 68.7702 | 8.5706 | 4 | 3078.2865 | 3996.8525 | 62.755 | 81.4812 | 224.2286 | 0 | 114.0619 | 10126306.6617 | 638597.5291 | 9662845.1412 | 6008286.8208 | 0 | 608171.3943 | 0 | 10547240.9434 | 27441757.3981 | 18729563.2959 | 83762769.1845 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 105531643.0172 | 137022469.6118 | 13335.2143 | 34.2826 | 3078.2865 | 3996.8525 | 62.755 | 81.4812
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.1541 | 85.8209 | 10.6833 | 4 | 2858.477 | 3595.3959 | 58.2739 | 73.297 | 223.1429 | 0 | 146.5602 | 11859925.1091 | 745696.4794 | 11536103.503 | 7550654.0385 | 0 | 717853.626 | 0 | 12639990.7748 | 32886663.1775 | 22445823.372 | 100382710.0803 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 122151583.913 | 153642410.5076 | 17782.7941 | 42.7331 | 2858.477 | 3595.3959 | 58.2739 | 73.297
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4795 | 103.5672 | 12.8639 | 4 | 2704.4454 | 3316.4457 | 55.1338 | 67.6102 | 221.1824 | 0 | 142.9527 | 13563524.1026 | 850554.9892 | 13407948.9633 | 9237360.8327 | 0 | 841907.9204 | 0 | 14781505.7552 | 38458445.8713 | 26248679.5492 | 117389927.9838 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 139158801.8165 | 170649628.4112 | 23713.7371 | 51.4556 | 2704.4454 | 3316.4457 | 55.1338 | 67.6102
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.6622 | 120.9298 | 14.981 | 4 | 2596.87 | 3122.3826 | 52.9407 | 63.654 | 218.8931 | 0 | 147.4368 | 15152117.4535 | 948025.9052 | 15177885.493 | 10965947.1472 | 0 | 970445.9193 | 0 | 16853624.5481 | 43849673.9203 | 29928303.4713 | 133846023.8579 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 155614897.6906 | 187105724.2853 | 31622.7766 | 59.924 | 2596.87 | 3122.3826 | 52.9407 | 63.654
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.822 | 136.4334 | 16.8509 | 4 | 2527.1316 | 2994.329 | 51.519 | 61.0434 | 216.3557 | 0 | 176.4304 | 16516992.1264 | 1031552.8312 | 16715574.0408 | 12607351.5688 | 0 | 1096547.0754 | 0 | 18707526.8807 | 48673147.5021 | 33220423.3033 | 148569115.3288 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 170337989.1616 | 201828815.7562 | 42169.6503 | 67.4037 | 2527.1316 | 2994.329 | 51.519 | 61.0434
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.8233 | 141.0785 | 17.5758 | 4 | 2479.6966 | 2927.6252 | 50.552 | 59.6836 | 215.4683 | 0 | 186.3921 | 16917279.1644 | 1056013.5495 | 17169328.6151 | 13124142.9018 | 0 | 990367.071 | 0 | 19210281.2077 | 49981211.1321 | 34113203.6088 | 152561827.2505 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 174330701.0833 | 205821527.6779 | 56234.1325 | 70.3032 | 2479.6966 | 2927.6252 | 50.552 | 59.6836
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.813 | 144.4656 | 18.1278 | 4 | 2443.4535 | 2877.7425 | 49.8131 | 58.6667 | 214.7824 | 0 | 202.6385 | 17206837.1936 | 1073698.0615 | 17498320.7896 | 13509827.5704 | 0 | 887681.5664 | 0 | 19568782.4208 | 50913957.7496 | 34749822.3413 | 155408927.6932 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 177177801.5259 | 208668628.1205 | 74989.4209 | 72.5112 | 2443.4535 | 2877.7425 | 49.8131 | 58.6667
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 206.3749 | 146.9922 | 18.5511 | 4 | 2415.8095 | 2840.1893 | 49.2495 | 57.9011 | 214.2482 | 0 | 249.1204 | 17421582.8734 | 1086808.2466 | 17742715.7666 | 13802638.6714 | 0 | 796047.9036 | 0 | 19831419.45 | 51597285.4255 | 35216207.5211 | 157494705.8583 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 179263579.691 | 210754406.2857 | 100000 | 74.2044 | 2415.8095 | 2840.1893 | 49.2495 | 57.9011
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.9628 | 148.9467 | 18.8812 | 4 | 2394.7627 | 2811.7239 | 48.8205 | 57.3208 | 213.8213 | 0 | 265.309 | 17586998.1336 | 1096903.817 | 17931200.9788 | 14032257.3663 | 0 | 718993.318 | 0 | 20032877.9094 | 52121439.0119 | 35573953.1141 | 159094623.6491 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 180863497.4818 | 212354324.0765 | 133352.1432 | 75.5246 | 2394.7627 | 2811.7239 | 48.8205 | 57.3208
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.5445 | 150.3336 | 19.124 | 4 | 2378.7594 | 2790.4259 | 48.4942 | 56.8866 | 213.51 | 0 | 286.2139 | 17704004.6234 | 1104043.3544 | 18064646.6037 | 14196845.8684 | 0 | 652605.9899 | 0 | 20171637.1115 | 52482461.9925 | 35820358.7166 | 160196604.2604 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 181965478.0931 | 213456304.6878 | 177827.941 | 76.496 | 2378.7594 | 2790.4259 | 48.4942 | 56.8866
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.4345 | 151.3392 | 19.3045 | 4 | 2366.6175 | 2774.4353 | 48.2467 | 56.5606 | 213.2798 | 0 | 340.2196 | 17788656.2968 | 1109207.8523 | 18161253.5344 | 14317283.8528 | 0 | 597487.2759 | 0 | 20269816.6368 | 52737904.9777 | 35994703.8029 | 160976314.2296 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 182745188.0623 | 214236014.657 | 237137.3706 | 77.2179 | 2366.6175 | 2774.4353 | 48.2467 | 56.5606
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.8159 | 152.0688 | 19.4383 | 4 | 2357.4183 | 2762.4279 | 48.0592 | 56.3158 | 213.1103 | 0 | 378.48 | 17849979.1263 | 1112948.6656 | 18231269.2234 | 14405277.1258 | 0 | 552578.0039 | 0 | 20339300.3365 | 52918687.3115 | 36118091.4604 | 161528131.2534 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183297005.0861 | 214787831.6808 | 316227.766 | 77.7533 | 2357.4183 | 2762.4279 | 48.0592 | 56.3158
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.8707 | 152.6232 | 19.5401 | 4 | 2350.4579 | 2753.3577 | 47.9173 | 56.1309 | 212.9803 | 0 | 347.8904 | 17896510.5511 | 1115786.9395 | 18284414.794 | 14472439.2056 | 0 | 517156.2914 | 0 | 20391660.0348 | 53054916.506 | 36211070.6849 | 161943955.0073 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183712828.84 | 215203655.4347 | 421696.5034 | 78.1604 | 2350.4579 | 2753.3577 | 47.9173 | 56.1309
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.6017 | 153.0053 | 19.6131 | 4 | 2345.1972 | 2746.5968 | 47.81 | 55.9931 | 212.8897 | 0 | 352.0352 | 17928560.0642 | 1117741.7439 | 18321028.978 | 14518894.6624 | 0 | 488516.7315 | 0 | 20426149.4502 | 53144650.8901 | 36272316.2459 | 162217858.7662 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183986732.5989 | 215477559.1936 | 562341.3252 | 78.4526 | 2345.1972 | 2746.5968 | 47.81 | 55.9931
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.1151 | 153.2727 | 19.666 | 4 | 2341.227 | 2741.5477 | 47.7291 | 55.8902 | 212.8257 | 0 | 416.515 | 17950972.8674 | 1119108.7171 | 18346638.3101 | 14551508.2011 | 0 | 465770.517 | 0 | 20449259.459 | 53204778.3923 | 36313354.5016 | 162401390.9656 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184170264.7983 | 215661091.393 | 749894.2093 | 78.664 | 2341.227 | 2741.5477 | 47.7291 | 55.8902
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.4574 | 152.9236 | 19.6463 | 4 | 2338.0842 | 2738.8071 | 47.665 | 55.8343 | 212.9033 | 0 | 423.06 | 17921712.679 | 1117324.1076 | 18313205.7315 | 14509613.7554 | 0 | 432717.9561 | 0 | 20394883.9495 | 53063304.4707 | 36216795.6431 | 161969558.2928 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183738432.1256 | 215229258.7202 | 1000000 | 78.585 | 2338.0842 | 2738.8071 | 47.665 | 55.8343
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.2017 | 153.8399 | 19.7602 | 4 | 2335.8416 | 2734.254 | 47.6193 | 55.7415 | 212.6921 | 0 | 410.1921 | 17998481.3719 | 1122006.1409 | 18400934.3865 | 14620591.7187 | 0 | 439362.0581 | 0 | 20506736.5137 | 53354321.8985 | 36415421.0174 | 162857855.1055 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184626728.9383 | 216117555.5329 | 1333521.4322 | 79.0408 | 2335.8416 | 2734.254 | 47.6193 | 55.7415
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.4038 | 153.9443 | 19.7815 | 4 | 2334.1825 | 2732.1657 | 47.5855 | 55.6989 | 212.6667 | 0 | 449.9443 | 18007218.521 | 1122538.9748 | 18410921.5727 | 14633423.1753 | 0 | 429184.4086 | 0 | 20515281.7944 | 53376554.9662 | 36430595.5429 | 162925718.9559 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184694592.7887 | 216185419.3833 | 1778279.41 | 79.126 | 2334.1825 | 2732.1657 | 47.5855 | 55.6989
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.5307 | 154.0096 | 19.7961 | 4 | 2332.9354 | 2730.6256 | 47.56 | 55.6675 | 212.6505 | 0 | 428.7782 | 18012683.3822 | 1122872.245 | 18417168.5766 | 14641476.5205 | 0 | 421115.4266 | 0 | 20519973.2989 | 53388761.2984 | 36438926.6155 | 162962977.3637 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184731851.1964 | 216222677.791 | 2371373.7057 | 79.1843 | 2332.9354 | 2730.6256 | 47.56 | 55.6675
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.6427 | 154.0674 | 19.808 | 4 | 2331.9983 | 2729.4495 | 47.5409 | 55.6435 | 212.6364 | 0 | 416.5957 | 18017520.0393 | 1123167.2024 | 18422697.6441 | 14648591.8258 | 0 | 415238.0789 | 0 | 20524613.7683 | 53400834.8479 | 36447167.0611 | 162999830.4677 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184768704.3004 | 216259530.8951 | 3162277.6602 | 79.2319 | 2331.9983 | 2729.4495 | 47.5409 | 55.6435
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.7157 | 154.1049 | 19.8163 | 4 | 2331.2945 | 2728.5794 | 47.5266 | 55.6258 | 212.6271 | 0 | 418.5304 | 18020661.364 | 1123358.771 | 18426288.7668 | 14653224.7609 | 0 | 410645.2664 | 0 | 20527329.7823 | 53407901.3593 | 36451990.1003 | 163021400.1709 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184790274.0036 | 216281100.5983 | 4216965.0343 | 79.2651 | 2331.2945 | 2728.5794 | 47.5266 | 55.6258
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.7741 | 154.1349 | 19.8227 | 4 | 2330.7662 | 2727.9223 | 47.5158 | 55.6124 | 212.6197 | 0 | 407.8026 | 18023174.3032 | 1123512.0178 | 18429161.5776 | 14656928.7148 | 0 | 407231.3969 | 0 | 20529603.124 | 53413816.128 | 36456027.0515 | 163039454.3137 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184808328.1464 | 216299154.7411 | 5623413.2519 | 79.2908 | 2330.7662 | 2727.9223 | 47.5158 | 55.6124
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.813 | 154.1549 | 19.8272 | 4 | 2330.3696 | 2727.4347 | 47.5077 | 55.6024 | 212.6148 | 0 | 404.1648 | 18024845.6415 | 1123613.9408 | 18431072.289 | 14659397.3045 | 0 | 404593.2489 | 0 | 20530973.7457 | 53417382.2044 | 36458460.9719 | 163050339.3468 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184819213.1795 | 216310039.7741 | 7498942.0933 | 79.309 | 2330.3696 | 2727.4347 | 47.5077 | 55.6024
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.7484 | 153.5969 | 19.7682 | 4 | 2329.9164 | 2728.1669 | 47.4985 | 55.6174 | 212.7434 | 0 | 380.9018 | 17978134.9713 | 1120765.2909 | 18377679.1078 | 14591657.9677 | 0 | 386111.2947 | 0 | 20457195.9667 | 53225427.5574 | 36327447.9811 | 162464420.1376 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 184233293.9704 | 215724120.565 | 10000000 | 79.0729 | 2329.9164 | 2728.1669 | 47.4985 | 55.6174
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0452 | 0.32451 | 0.025452 | 4 | 233712.7214 | 550297.9791 | 4764.5499 | 11218.5686 | 144.9431 | 0 | 44.3416 | 204195.8485 | 9777.3522 | 136113.4131 | 72327.6547 | 0 | 60694.9397 | 0 | 188412.5912 | 490210.9136 | 334579.0214 | 1496311.7344 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 23793615.0749 | 56024242.9803 | 100 | 0.10181 | 233712.7214 | 550297.9791 | 4764.5499 | 11218.5686
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.49854 | 0.047652 | 4 | 127662.3728 | 296756.1698 | 2602.5701 | 6049.7759 | 159.4274 | 0 | 64.0304 | 291940.2225 | 15706.7337 | 190072.8385 | 93452.5336 | 0 | 66237.2871 | 0 | 256389.75 | 667073.5367 | 455291.3958 | 2036164.2979 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 24333467.6384 | 56564095.5439 | 133.3521 | 0.19061 | 127662.3728 | 296756.1698 | 2602.5701 | 6049.7759
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.74201 | 0.081483 | 4 | 76811.4811 | 175699.2666 | 1565.9059 | 3581.8672 | 172.2474 | 0 | 270.9376 | 405390.1003 | 24639.2162 | 258965.9104 | 122761.512 | 0 | 72241.0019 | 0 | 344759.1189 | 896992.5076 | 612215.8178 | 2737965.185 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25035268.5255 | 57265896.431 | 177.8279 | 0.32593 | 76811.4811 | 175699.2666 | 1565.9059 | 3581.8672
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2349 | 1.1173 | 0.13117 | 4 | 49506.4215 | 110934.887 | 1009.2554 | 2261.5577 | 183.4662 | 0 | 356.6921 | 551713.5146 | 35707.1389 | 357855.9491 | 162231.9858 | 0 | 79995.2113 | 0 | 463126.4819 | 1204960.1055 | 822410.0315 | 3678000.4185 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25975303.759 | 58205931.6644 | 237.1374 | 0.52469 | 49506.4215 | 110934.887 | 1009.2554 | 2261.5577
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8766 | 1.6281 | 0.19467 | 4 | 34777.603 | 76168.1637 | 708.9885 | 1552.791 | 192.7212 | 0 | 463.2933 | 717995.3755 | 46474.6967 | 483639.0924 | 207569.1672 | 0 | 88866.3631 | 0 | 602372.431 | 1567249.502 | 1069679.9888 | 4783846.6168 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 27081149.9572 | 59311777.8627 | 316.2278 | 0.7787 | 34777.603 | 76168.1637 | 708.9885 | 1552.791
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.717 | 2.3019 | 0.27851 | 4 | 25513.5802 | 54444.4025 | 520.1288 | 1109.9228 | 200.4544 | 0 | 63.4687 | 915292.5199 | 59224.5426 | 638039.0858 | 265829.127 | 0 | 99598.3528 | 0 | 771413.615 | 2007059.9874 | 1369859.6824 | 6126316.9128 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 28423620.2533 | 60654248.1588 | 421.6965 | 1.1141 | 25513.5802 | 54444.4025 | 520.1288 | 1109.9228
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8205 | 3.1923 | 0.38943 | 4 | 19302.7431 | 39993.4608 | 393.5125 | 815.3208 | 206.7963 | 0 | 93.3328 | 1151579.5954 | 74458.7438 | 828825.821 | 341717.4769 | 0 | 112489.495 | 0 | 978537.7415 | 2545954.4778 | 1737666.2452 | 7771229.5967 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 30068532.9372 | 62299160.8427 | 562.3413 | 1.5577 | 19302.7431 | 39993.4608 | 393.5125 | 815.3208
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2432 | 4.3443 | 0.53338 | 4 | 15023.0281 | 30129.9525 | 306.2647 | 614.2398 | 211.8002 | 0 | 80.0936 | 1430291.3527 | 92382.7429 | 1060524.2014 | 439194.3606 | 0 | 126956.1162 | 0 | 1228246.0218 | 3195644.2007 | 2181092.8309 | 9754331.8272 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 32051635.1677 | 64282263.0732 | 749.8942 | 2.1335 | 15023.0281 | 30129.9525 | 306.2647 | 614.2398
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0802 | 5.8243 | 0.71857 | 4 | 11982.7781 | 23196.311 | 244.2851 | 472.8882 | 215.5234 | 0 | 72.0432 | 1758406.4939 | 113426.8022 | 1340841.7963 | 564669.1639 | 0 | 143657.4335 | 0 | 1529190.659 | 3978640.4146 | 2715503.8358 | 12144336.5991 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 34441639.9396 | 66672267.8451 | 1000 | 2.8743 | 11982.7781 | 23196.311 | 244.2851 | 472.8882
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5279 | 7.8384 | 0.97124 | 4 | 9649.296 | 17945.5612 | 196.7139 | 365.8445 | 219.0548 | 0 | 109.2936 | 2168299.8606 | 139638.2534 | 1700453.0561 | 732448.4892 | 0 | 163437.3223 | 0 | 1912668.0228 | 4976369.8532 | 3396474.679 | 15189789.5364 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 37487092.8769 | 69717720.7824 | 1333.5214 | 3.885 | 9649.296 | 17945.5612 | 196.7139 | 365.8445
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7754 | 10.4923 | 1.3038 | 4 | 7913.4875 | 14093.54 | 161.3271 | 287.3159 | 221.6 | 0 | 85.5808 | 2664394.9116 | 171259.984 | 2147240.2378 | 954636.355 | 0 | 188428.6129 | 0 | 2389124.4395 | 6216011.7147 | 4242555.7216 | 18973651.977 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 41270955.3175 | 73501583.223 | 1778.2794 | 5.2153 | 7913.4875 | 14093.54 | 161.3271 | 287.3159
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.0459 | 13.986 | 1.742 | 4 | 6596.7674 | 11222.2581 | 134.484 | 228.7809 | 223.5768 | 0 | 101.4531 | 3265231.9932 | 209426.6596 | 2702333.8337 | 1246819.0551 | 0 | 218206.6554 | 0 | 2980387.0968 | 7754355.8644 | 5292507.2135 | 23669268.3717 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 45966571.7121 | 78197199.6176 | 2371.3737 | 6.968 | 6596.7674 | 11222.2581 | 134.484 | 228.7809
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.717 | 18.6285 | 2.3242 | 4 | 5578.2871 | 9045.1082 | 113.7209 | 184.3968 | 225.1163 | 0 | 76.9754 | 4000468.856 | 255959.7608 | 3398812.9287 | 1634827.292 | 0 | 254959.924 | 0 | 3722561.217 | 9685340.6844 | 6610444.0309 | 29563374.6939 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 51860678.0344 | 84091305.9399 | 3162.2777 | 9.2969 | 5578.2871 | 9045.1082 | 113.7209 | 184.3968
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.1884 | 24.748 | 3.0918 | 4 | 4787.5217 | 7393.641 | 97.6001 | 150.7294 | 226.2992 | 0 | 106.6084 | 4893596.8694 | 312266.048 | 4265957.1217 | 2146211.7433 | 0 | 299416.1434 | 0 | 4647804.6911 | 12092634.4104 | 8253471.4639 | 36911358.4912 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 59208661.8317 | 91439289.7371 | 4216.965 | 12.3673 | 4787.5217 | 7393.641 | 97.6001 | 150.7294
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.9689 | 32.7592 | 4.0969 | 4 | 4169.0212 | 6135.774 | 84.9911 | 125.0861 | 227.1975 | 0 | 132.6655 | 5972346.867 | 379996.9275 | 5338891.9959 | 2815427.2112 | 0 | 352798.2973 | 0 | 5795189.9066 | 15077895.3801 | 10290973.4167 | 46023520.0024 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 68320823.3428 | 100551451.2483 | 5623.4133 | 16.3877 | 4169.0212 | 6135.774 | 84.9911 | 125.0861
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.6368 | 43.121 | 5.3969 | 4 | 3683.2012 | 5176.2121 | 75.087 | 105.5241 | 227.8332 | 0 | 119.6892 | 7261675.1477 | 460605.7079 | 6651750.7916 | 3682017.8555 | 0 | 416583.6963 | 0 | 7204326.9476 | 18744180.907 | 12793288.6234 | 57214429.6769 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 79511733.0174 | 111742360.9228 | 7498.9421 | 21.5877 | 3683.2012 | 5176.2121 | 75.087 | 105.5241
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.681 | 56.156 | 7.0312 | 4 | 3304.5758 | 4450.5691 | 67.3682 | 90.7309 | 228.1034 | 0 | 104.5324 | 8764350.7241 | 554146.3119 | 8216783.323 | 4780761.9739 | 0 | 492109.7754 | 0 | 8895179.3223 | 23143431.9443 | 15795867.852 | 70642631.2269 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 92939934.5674 | 125170562.4729 | 10000 | 28.1246 | 3304.5758 | 4450.5691 | 67.3682 | 90.7309
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.4226 | 71.8541 | 8.9942 | 4 | 3014.705 | 3910.5804 | 61.4588 | 79.7225 | 227.7729 | 0 | 126.7586 | 10448122.3666 | 658510.7777 | 10007964.7369 | 6121991.0557 | 0 | 582182.4435 | 0 | 10849320.8383 | 28227707.3196 | 19265990.267 | 86161789.8052 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 108459093.1457 | 140689721.0512 | 13335.2143 | 35.9767 | 3014.705 | 3910.5804 | 61.4588 | 79.7225
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5185 | 89.5209 | 11.192 | 4 | 2801.5628 | 3521.5095 | 57.1136 | 71.7907 | 226.6098 | 0 | 119.8749 | 12222729.9472 | 768058.0676 | 11932302.2056 | 7683615.0767 | 0 | 688367.4335 | 0 | 12985078.3649 | 33784510.2997 | 23058622.4818 | 103123283.877 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 125420587.2175 | 157651215.123 | 17782.7941 | 44.7681 | 2801.5628 | 3521.5095 | 57.1136 | 71.7907
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.917 | 107.798 | 13.4469 | 4 | 2652.7023 | 3251.9239 | 54.0789 | 66.2949 | 224.5512 | 0 | 108.8204 | 13957116.6179 | 874731.1456 | 13844377.3086 | 9382659.8255 | 0 | 809393.7072 | 0 | 15158628.6559 | 39439642.3003 | 26918366.2735 | 120384915.8345 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 142682219.1749 | 174912847.0804 | 23713.7371 | 53.7875 | 2652.7023 | 3251.9239 | 54.0789 | 66.2949
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0654 | 125.6219 | 15.6297 | 4 | 2548.5151 | 3064.0506 | 51.9549 | 62.4648 | 222.1936 | 0 | 130.2719 | 15570121.4789 | 973627.2675 | 15647213.6729 | 11117599.4968 | 0 | 934718.3402 | 0 | 17254879.2999 | 44893656.476 | 30640843.0172 | 137032659.0493 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 159329962.3898 | 191560590.2952 | 31622.7766 | 62.5187 | 2548.5151 | 3064.0506 | 51.9549 | 62.4648
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.0937 | 141.4518 | 17.5472 | 4 | 2481.1928 | 2940.3908 | 50.5825 | 59.9438 | 219.5783 | 0 | 153.3854 | 16949291.0386 | 1057969.0486 | 17205669.1068 | 12757756.0986 | 0 | 1058238.932 | 0 | 19121280.4476 | 49749649.4107 | 33955157.9759 | 151855012.0587 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 174152315.3992 | 206382943.3047 | 42169.6503 | 70.1889 | 2481.1928 | 2940.3908 | 50.5825 | 59.9438
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.083 | 147.3888 | 18.4033 | 4 | 2436.6861 | 2874.5238 | 49.6751 | 58.6011 | 218.4321 | 0 | 181.6407 | 17455196.8988 | 1088859.9775 | 17781001.5943 | 13405902.4726 | 0 | 983302.0974 | 0 | 19778562.5858 | 51459762.7072 | 35122345.4401 | 157074933.7736 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 179372237.1141 | 211602865.0196 | 56234.1325 | 73.6132 | 2436.6861 | 2874.5238 | 49.6751 | 58.6011
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9749 | 150.781 | 18.9556 | 4 | 2402.8162 | 2827.8974 | 48.9847 | 57.6505 | 217.7274 | 0 | 203.0601 | 17741691.1907 | 1106342.6502 | 18107649.2007 | 13786765.2962 | 0 | 880614.699 | 0 | 20132994.5843 | 52381922.0634 | 35751738.1491 | 159889717.8336 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 182187021.174 | 214417649.0795 | 74989.4209 | 75.8223 | 2402.8162 | 2827.8974 | 48.9847 | 57.6505
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.4714 | 153.3172 | 19.3791 | 4 | 2377.0046 | 2792.7947 | 48.4585 | 56.9349 | 217.1777 | 0 | 219.0846 | 17954704.1947 | 1119336.2889 | 18350902.1508 | 14076962.0372 | 0 | 789570.1295 | 0 | 20393675.1724 | 53060159.4807 | 36214649.1228 | 161959958.577 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 184257261.9175 | 216487889.8229 | 100000 | 77.5166 | 2377.0046 | 2792.7947 | 48.4585 | 56.9349
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.1371 | 155.3491 | 19.7166 | 4 | 2357.3497 | 2766.0241 | 48.0578 | 56.3891 | 216.7231 | 0 | 267.9888 | 18124652.6784 | 1129699.9952 | 18545209.9569 | 14312270.9385 | 0 | 715000.0233 | 0 | 20602465.101 | 53603388.0462 | 36585413.781 | 163618100.5206 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 185915403.8611 | 218146031.7665 | 133352.1432 | 78.8663 | 2357.3497 | 2766.0241 | 48.0578 | 56.3891
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.6922 | 156.7449 | 19.9595 | 4 | 2342.4081 | 2746.1075 | 47.7532 | 55.9831 | 216.4016 | 0 | 290.0148 | 18241033.4214 | 1136795.5245 | 18678390.2034 | 14475655.5229 | 0 | 649534.3895 | 0 | 20740749.5341 | 53963175.7749 | 36830976.2988 | 164716310.6695 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187013614.0099 | 219244241.9154 | 177827.941 | 79.8382 | 2342.4081 | 2746.1075 | 47.7532 | 55.9831
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.5823 | 157.7674 | 20.1411 | 4 | 2331.0745 | 2731.1347 | 47.5221 | 55.6779 | 216.1615 | 0 | 314.2721 | 18326104.3059 | 1141981.3602 | 18775801.4483 | 14596454.8623 | 0 | 595533.1694 | 0 | 20839991.307 | 54221382.5107 | 37007207.7015 | 165504456.6653 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187801760.0057 | 220032387.9112 | 237137.3706 | 80.5645 | 2331.0745 | 2731.1347 | 47.5221 | 55.6779
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.0024 | 158.5301 | 20.2779 | 4 | 2322.4894 | 2719.8502 | 47.3471 | 55.4478 | 215.98 | 0 | 326.2215 | 18389458.203 | 1145842.9203 | 18848378.4467 | 14687173.6977 | 0 | 552093.5431 | 0 | 20912949.2562 | 54411204.1289 | 37136764.8564 | 166083865.0524 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188381168.3928 | 220611796.2983 | 316227.766 | 81.1117 | 2322.4894 | 2719.8502 | 47.3471 | 55.4478
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.0176 | 159.0718 | 20.3779 | 4 | 2315.9937 | 2711.4058 | 47.2147 | 55.2757 | 215.8494 | 0 | 364.5041 | 18434411.7209 | 1148582.7148 | 18899893.3581 | 14751921.9189 | 0 | 516932.6537 | 0 | 20963179.5229 | 54541892.9792 | 37225962.6821 | 166482777.5507 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188780080.8912 | 221010708.7967 | 421696.5034 | 81.5115 | 2315.9937 | 2711.4058 | 47.2147 | 55.2757
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.7487 | 159.4603 | 20.4512 | 4 | 2311.0863 | 2705.0808 | 47.1146 | 55.1467 | 215.7549 | 0 | 368.193 | 18466613.3548 | 1150545.2037 | 18936803.7969 | 14798533.6054 | 0 | 488939.1025 | 0 | 20998159.6747 | 54632904.1588 | 37288079.6823 | 166760578.5791 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189057881.9196 | 221288509.825 | 562341.3252 | 81.8048 | 2311.0863 | 2705.0808 | 47.1146 | 55.1467
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.2823 | 159.7429 | 20.5054 | 4 | 2307.3834 | 2700.3362 | 47.0391 | 55.05 | 215.6856 | 0 | 373.905 | 18490029.2409 | 1151972.1969 | 18963648.2959 | 14832551.5441 | 0 | 466988.3459 | 0 | 21023023.9533 | 54697595.9112 | 37332233.1326 | 166958042.6208 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189255345.9613 | 221485973.8667 | 749894.2093 | 82.0216 | 2307.3834 | 2700.3362 | 47.0391 | 55.05
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.0595 | 160.1564 | 20.5693 | 4 | 2304.4422 | 2696.1747 | 46.9792 | 54.9652 | 215.5867 | 0 | 374.5813 | 18524274.5957 | 1154059.0618 | 19002914.8103 | 14882143.6829 | 0 | 454018.5769 | 0 | 21066790.1838 | 54811466.6654 | 37409952.2621 | 167305619.839 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189602923.1795 | 221833551.085 | 1000000 | 82.2771 | 2304.4422 | 2696.1747 | 46.9792 | 54.9652
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.354 | 160.3114 | 20.5992 | 4 | 2302.3867 | 2693.55 | 46.9373 | 54.9117 | 215.5482 | 0 | 367.6014 | 18537097.2522 | 1154840.4296 | 19017619.6611 | 14900911.4667 | 0 | 441334.4033 | 0 | 21080203.253 | 54846364.7201 | 37433770.9016 | 167412142.0875 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189709445.428 | 221940073.3335 | 1333521.4322 | 82.3969 | 2302.3867 | 2693.55 | 46.9373 | 54.9117
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.5586 | 160.4188 | 20.6207 | 4 | 2300.8406 | 2691.5958 | 46.9057 | 54.8718 | 215.5213 | 0 | 364.9971 | 18545986.4424 | 1155382.097 | 19027814.3353 | 14913951.9874 | 0 | 431444.5342 | 0 | 21089085.9645 | 54869475.7134 | 37449544.6294 | 167482685.7036 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189779989.044 | 222010616.9495 | 1778279.41 | 82.4829 | 2300.8406 | 2691.5958 | 46.9057 | 54.8718
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.7024 | 160.4941 | 20.6363 | 4 | 2299.6783 | 2690.139 | 46.8821 | 54.8421 | 215.5023 | 0 | 368.1867 | 18552215.7326 | 1155761.6777 | 19034958.7981 | 14923107.722 | 0 | 423801.2669 | 0 | 21095039.627 | 54884965.9217 | 37460117.0149 | 167529967.7609 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189827271.1014 | 222057899.0069 | 2371373.7057 | 82.5451 | 2299.6783 | 2690.139 | 46.8821 | 54.8421
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.7557 | 159.4525 | 20.527 | 4 | 2298.7198 | 2691.2591 | 46.8625 | 54.865 | 215.7462 | 0 | 333.8335 | 18465967.9466 | 1150505.871 | 18936063.9405 | 14798793.0497 | 0 | 388554.9178 | 0 | 20958555.433 | 54529862.0458 | 37217751.3228 | 166446054.5272 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188743357.8676 | 220973985.7731 | 3162277.6602 | 82.108 | 2298.7198 | 2691.2591 | 46.8625 | 54.865
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.023 | 160.1302 | 20.6059 | 4 | 2298.0904 | 2689.1271 | 46.8497 | 54.8215 | 215.5868 | 0 | 329.751 | 18522105.8982 | 1153926.9075 | 19000427.8899 | 14879705.2413 | 0 | 401128.6222 | 0 | 21043344.8781 | 54750466.7892 | 37368318.5932 | 167119424.8198 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189416728.1602 | 221647356.0657 | 4216965.0343 | 82.4235 | 2298.0904 | 2689.1271 | 46.8497 | 54.8215
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.8 | 160.5442 | 20.6551 | 4 | 2297.5396 | 2687.6443 | 46.8385 | 54.7913 | 215.4888 | 0 | 350.5704 | 18556365.3331 | 1156014.531 | 19039718.1842 | 14929312.1045 | 0 | 407300.13 | 0 | 21094597.0103 | 54883814.3239 | 37459331.0257 | 167526452.6425 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189823755.983 | 222054383.8885 | 5623413.2519 | 82.6205 | 2297.5396 | 2687.6443 | 46.8385 | 54.7913
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.9996 | 160.6497 | 20.6684 | 4 | 2297.2877 | 2687.1424 | 46.8333 | 54.781 | 215.4631 | 0 | 366.3477 | 18565086.5188 | 1156545.9458 | 19049721.3409 | 14942045.4451 | 0 | 407902.5591 | 0 | 21107307.7058 | 54916884.9462 | 37481902.4049 | 167627396.8665 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189924700.207 | 222155328.1125 | 7498942.0933 | 82.6734 | 2297.2877 | 2687.1424 | 46.8333 | 54.781
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.0385 | 160.6701 | 20.6723 | 4 | 2297.0104 | 2686.79 | 46.8277 | 54.7738 | 215.458 | 0 | 367.3178 | 18566773.1721 | 1156648.7192 | 19051655.9847 | 14944524.0428 | 0 | 406102.1886 | 0 | 21109024.6019 | 54921351.9577 | 37484951.2321 | 167641031.899 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 189938335.2395 | 222168963.1449 | 10000000 | 82.6894 | 2297.0104 | 2686.79 | 46.8277 | 54.7738
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.34322 | 0.028078 | 4 | 217138.0118 | 510768.2752 | 4426.6521 | 10412.7022 | 147.607 | 0 | 51.6338 | 214655.3163 | 10486.6292 | 142112.2555 | 74335.9569 | 0 | 60767.9035 | 0 | 195919.644 | 509742.725 | 347909.884 | 1555930.3143 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24387523.2534 | 57366156.5969 | 100 | 0.11231 | 217138.0118 | 510768.2752 | 4426.6521 | 10412.7022
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3834 | 0.53256 | 0.052751 | 4 | 118340.674 | 274634.6397 | 2412.5347 | 5598.7986 | 162.6228 | 0 | 70.0708 | 309535.0149 | 17120.1232 | 199953.831 | 97249.0115 | 0 | 66672.6764 | 0 | 269306.9563 | 700681.4577 | 478229.4925 | 2138748.5635 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24970341.5026 | 57948974.8461 | 133.3521 | 0.211 | 118340.674 | 274634.6397 | 2412.5347 | 5598.7986
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.78488 | 0.088877 | 4 | 72267.8512 | 165032.7958 | 1473.2779 | 3364.4168 | 175.2766 | 0 | 273.4237 | 426839.4216 | 26826.3151 | 270276.2852 | 127615.9591 | 0 | 71895.6233 | 0 | 360146.9057 | 937028.3722 | 639541.118 | 2860170.0002 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25691762.9392 | 58670396.2827 | 177.8279 | 0.35551 | 72267.8512 | 165032.7958 | 1473.2779 | 3364.4168
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 1.2014 | 0.14207 | 4 | 46961.975 | 104993.9281 | 957.3834 | 2140.4432 | 186.782 | 0 | 362.2548 | 580457.7945 | 37569.93 | 379270.1142 | 167616.2814 | 0 | 80107.7248 | 0 | 485558.5195 | 1263323.666 | 862244.3608 | 3856148.3912 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 26687741.3303 | 59666374.6738 | 237.1374 | 0.56828 | 46961.975 | 104993.9281 | 957.3834 | 2140.4432
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9544 | 1.7425 | 0.20952 | 4 | 33213.9553 | 72564.9073 | 677.1114 | 1479.3338 | 196.1534 | 0 | 468.7131 | 752984.4299 | 48737.8176 | 510647.0665 | 214277.8738 | 0 | 88926.5886 | 0 | 630073.7728 | 1639322.7109 | 1118871.4349 | 5003841.6949 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 27835434.634 | 60814067.9775 | 316.2278 | 0.83806 | 33213.9553 | 72564.9073 | 677.1114 | 1479.3338
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 2.4459 | 0.29745 | 4 | 24549.809 | 52267.5668 | 500.4811 | 1065.545 | 203.8692 | 0 | 77.9194 | 955126.3698 | 61795.3841 | 669788.8854 | 273510.0919 | 0 | 98961.5408 | 0 | 803081.0861 | 2089452.2514 | 1426094.0955 | 6377809.7049 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 29209402.644 | 62188035.9875 | 421.6965 | 1.1898 | 24549.809 | 52267.5668 | 500.4811 | 1065.545
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9428 | 3.3893 | 0.41544 | 4 | 18607.0975 | 38452.9192 | 379.3309 | 783.9148 | 210.291 | 0 | 55.5839 | 1201106.9991 | 77647.3307 | 869512.1287 | 351856.361 | 0 | 111416.8246 | 0 | 1018500.4612 | 2649929.2769 | 1808631.1821 | 8088600.5643 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 30920193.5034 | 63898826.8469 | 562.3413 | 1.6617 | 18607.0975 | 38452.9192 | 379.3309 | 783.9148
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3675 | 4.5772 | 0.56463 | 4 | 14579.3654 | 29181.1234 | 297.2201 | 594.8967 | 215.2307 | 0 | 83.7928 | 1483864.851 | 95822.7989 | 1105775.2602 | 449881.7898 | 0 | 124467.7722 | 0 | 1271326.8641 | 3307731.7154 | 2257594.8628 | 10096465.9143 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 32928058.8534 | 65906692.1969 | 749.8942 | 2.2585 | 14579.3654 | 29181.1234 | 297.2201 | 594.8967
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2311 | 6.1224 | 0.75879 | 4 | 11657.6083 | 22523.1674 | 237.6561 | 459.1652 | 218.9469 | 0 | 84.987 | 1821393.4708 | 117460.0032 | 1395467.1546 | 577814.1903 | 0 | 140174.8495 | 0 | 1580400.7707 | 4111878.6205 | 2806441.6491 | 12551030.7086 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 35382623.6476 | 68361256.9912 | 1000 | 3.0352 | 11657.6083 | 22523.1674 | 237.6561 | 459.1652
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7326 | 8.2451 | 1.0261 | 4 | 9389.5726 | 17424.2485 | 191.4191 | 355.2169 | 222.5716 | 0 | 110.4487 | 2247157.566 | 144671.8783 | 1770685.6222 | 750184.1677 | 0 | 158976.4958 | 0 | 1977953.5347 | 5146229.3632 | 3512407.2848 | 15708265.9127 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 38539858.8518 | 71518492.1953 | 1333.5214 | 4.1045 | 9389.5726 | 17424.2485 | 191.4191 | 355.2169
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0117 | 11.0065 | 1.3738 | 4 | 7717.8064 | 13719.0136 | 157.3379 | 279.6806 | 225.1268 | 0 | 91.8062 | 2756076.1783 | 177092.6791 | 2231018.4486 | 975702.3543 | 0 | 181944.8033 | 0 | 2465515.4408 | 6414765.4303 | 4378209.2164 | 19580324.5511 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 42411917.4902 | 75390550.8337 | 1778.2794 | 5.4953 | 7717.8064 | 13719.0136 | 157.3379 | 279.6806
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3775 | 14.6873 | 1.8372 | 4 | 6433.7468 | 10921.2995 | 131.1606 | 222.6455 | 227.1377 | 0 | 77.413 | 3380347.3265 | 216724.117 | 2810213.4934 | 1276085.9583 | 0 | 210542.4642 | 0 | 3078626.2102 | 8009953.8859 | 5466958.1152 | 24449451.5707 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 47281044.5098 | 80259677.8533 | 2371.3737 | 7.3489 | 6433.7468 | 10921.2995 | 131.1606 | 222.6455
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0849 | 19.5203 | 2.4461 | 4 | 5450.5991 | 8821.1003 | 111.1178 | 179.8301 | 228.6816 | 0 | 86.6081 | 4135325.0499 | 264476.2871 | 3528361.1032 | 1674688.0205 | 0 | 244498.0051 | 0 | 3840465.9017 | 9992104.4883 | 6819816.6305 | 30499735.4862 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 53331328.4253 | 86309961.7688 | 3162.2777 | 9.7845 | 5450.5991 | 8821.1003 | 111.1178 | 179.8301
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.707 | 25.9392 | 3.2546 | 4 | 4678.3905 | 7211.624 | 95.3753 | 147.0187 | 229.8858 | 0 | 104.8449 | 5059688.2087 | 322713.0876 | 4429451.8481 | 2194208.8196 | 0 | 286616.3354 | 0 | 4794144.5368 | 12473380.6704 | 8513338.6099 | 38073542.1165 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 60905135.0555 | 93883768.399 | 4216.965 | 13.0184 | 4678.3905 | 7211.624 | 95.3753 | 147.0187
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.6365 | 34.3224 | 4.3108 | 4 | 4076.3396 | 5988.886 | 83.1017 | 122.0915 | 230.794 | 0 | 88.689 | 6173576.608 | 392601.1275 | 5541751.9982 | 2877798.1499 | 0 | 336879.0683 | 0 | 5975816.7112 | 15547849.2741 | 10611726.6059 | 47457999.5431 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 70289592.4821 | 103268225.8257 | 5623.4133 | 17.2433 | 4076.3396 | 5988.886 | 83.1017 | 122.0915
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.4721 | 45.1422 | 5.6741 | 4 | 3603.6918 | 5056.7273 | 73.4661 | 103.0882 | 231.4301 | 0 | 117.3453 | 7502332.0322 | 475614.2959 | 6900029.1227 | 3761232.2061 | 0 | 396733.5101 | 0 | 7424017.0551 | 19315769.5021 | 13183409.5846 | 58959137.3087 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 81790730.2477 | 114769363.5913 | 7498.9421 | 22.6964 | 3603.6918 | 5056.7273 | 73.4661 | 103.0882
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.7474 | 58.7525 | 7.3874 | 4 | 3234.8055 | 4350.8418 | 65.9459 | 88.6978 | 231.6811 | 0 | 115.0158 | 9051234.1742 | 571959.8429 | 8519339.7617 | 4879742.9977 | 0 | 468278.5458 | 0 | 9161316.5757 | 23835866.4854 | 16268468.6544 | 72756207.0377 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 95587799.9768 | 128566433.3203 | 10000 | 29.5498 | 3234.8055 | 4350.8418 | 65.9459 | 88.6978
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6742 | 75.0624 | 9.4354 | 4 | 2953.5915 | 3827.3966 | 60.213 | 78.0267 | 231.3003 | 0 | 132.1143 | 10778820.6234 | 678957.9429 | 10363892.3482 | 6243683.2995 | 0 | 553907.1462 | 0 | 11161511.9304 | 29039964.5021 | 19820372.4843 | 88641110.2769 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 111472703.2159 | 144451336.5595 | 13335.2143 | 37.7414 | 2953.5915 | 3827.3966 | 60.213 | 78.0267
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.9191 | 93.3302 | 11.717 | 4 | 2747.1441 | 3450.7912 | 56.0042 | 70.349 | 230.057 | 0 | 133.1604 | 12591862.2425 | 790792.3356 | 12336796.7891 | 7823170.7151 | 0 | 656043.1422 | 0 | 13337479.4376 | 34701385.6034 | 23684408.7165 | 105921938.982 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 128753531.9211 | 161732165.2646 | 17782.7941 | 46.8681 | 2747.1441 | 3450.7912 | 56.0042 | 70.349
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.3884 | 112.1358 | 14.0463 | 4 | 2603.0462 | 3190.0081 | 53.0666 | 65.0326 | 227.9123 | 0 | 162.2949 | 14356167.2076 | 899224.3947 | 14288290.5357 | 9531286.6006 | 0 | 773678.1852 | 0 | 15540972.3003 | 40434422.0337 | 27597323.8823 | 123421365.1402 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 146252958.0792 | 179231591.4227 | 23713.7371 | 56.1853 | 2603.0462 | 3190.0081 | 53.0666 | 65.0326
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.5005 | 130.3944 | 16.2914 | 4 | 2502.3579 | 3008.4317 | 51.014 | 61.331 | 225.4735 | 0 | 146.6321 | 15990803.6106 | 999374.1586 | 16120991.2171 | 11270524.7134 | 0 | 895906.4832 | 0 | 17658264.0713 | 45943180.9054 | 31357165.0059 | 140236210.1654 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 163067803.1045 | 196046436.448 | 31622.7766 | 65.1657 | 2502.3579 | 3008.4317 | 51.014 | 61.331
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.4185 | 146.5508 | 18.2563 | 4 | 2437.4361 | 2889.0428 | 49.6904 | 58.897 | 222.7782 | 0 | 151.5498 | 17384142.4967 | 1084522.8362 | 17700081.5747 | 12910758.318 | 0 | 1017290.1502 | 0 | 19537750.1966 | 50833218.2679 | 34694715.986 | 155162479.8263 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 177994072.7654 | 210972706.1089 | 42169.6503 | 73.0251 | 2437.4361 | 2889.0428 | 49.6904 | 58.897
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.3667 | 153.8067 | 19.2479 | 4 | 2395.5744 | 2823.9147 | 48.837 | 57.5693 | 221.3589 | 0 | 161.2904 | 17995703.3142 | 1121836.72 | 18397758.9821 | 13689063.0662 | 0 | 973375.8438 | 0 | 20349317.7913 | 52944750.6738 | 36135880.2407 | 161607686.6322 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 184439279.5712 | 217417912.9147 | 56234.1325 | 76.9917 | 2395.5744 | 2823.9147 | 48.837 | 57.5693
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.166 | 157.1993 | 19.7992 | 4 | 2363.9924 | 2780.4068 | 48.1932 | 56.6824 | 220.6355 | 0 | 210.0904 | 18278855.4049 | 1139101.1964 | 18721692.3504 | 14064817.8981 | 0 | 871178.9632 | 0 | 20699501.8671 | 53855857.8064 | 36757729.5801 | 164388735.0665 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 187220328.0056 | 220198961.3491 | 74989.4209 | 79.1967 | 2363.9924 | 2780.4068 | 48.1932 | 56.6824
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.6554 | 159.7724 | 20.2253 | 4 | 2339.9465 | 2747.5876 | 47.703 | 56.0133 | 220.0635 | 0 | 244.3729 | 18492477.4575 | 1152121.3914 | 18966455.2068 | 14355572.4398 | 0 | 781894.2297 | 0 | 20961923.0828 | 54538623.9798 | 37223731.5229 | 166472799.3108 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 189304392.2498 | 222283025.5933 | 100000 | 80.9012 | 2339.9465 | 2747.5876 | 47.703 | 56.0133
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.2434 | 161.7922 | 20.5601 | 4 | 2321.6412 | 2722.6434 | 47.3298 | 55.5048 | 219.5996 | 0 | 278.5865 | 18659482.0097 | 1162297.3805 | 19158026.1887 | 14586528.8535 | 0 | 708010.5321 | 0 | 21166994.5362 | 55072177.8355 | 37587892.9928 | 168101410.329 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 190933003.268 | 223911636.6116 | 133352.1432 | 82.2405 | 2321.6412 | 2722.6434 | 47.3298 | 55.5048
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.8009 | 163.2121 | 20.8045 | 4 | 2307.7372 | 2704.0296 | 47.0463 | 55.1253 | 219.2644 | 0 | 305.3799 | 18776533.2212 | 1169428.0951 | 19292410.4624 | 14750910.5857 | 0 | 644134.348 | 0 | 21307032.5178 | 55436527.9381 | 37836569.4245 | 169213546.5929 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 192045139.5319 | 225023772.8755 | 177827.941 | 83.2179 | 2307.7372 | 2704.0296 | 47.0463 | 55.1253
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.6808 | 164.2453 | 20.9862 | 4 | 2297.1939 | 2690.0549 | 46.8314 | 54.8404 | 219.0156 | 0 | 381.639 | 18861533.1339 | 1174605.4879 | 19390056.1745 | 14871685.721 | 0 | 591336.5231 | 0 | 21406794.6458 | 55696088.5309 | 38013724.8625 | 170005825.0797 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 192837418.0188 | 225816051.3623 | 237137.3706 | 83.9448 | 2297.1939 | 2690.0549 | 46.8314 | 54.8404
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.1714 | 165.058 | 21.1276 | 4 | 2289.205 | 2679.4362 | 46.6685 | 54.6239 | 218.8174 | 0 | 391.4665 | 18928288.3607 | 1178671.1348 | 19466777.464 | 14967122.956 | 0 | 549968.4878 | 0 | 21485423.0773 | 55900663.5808 | 38153351.5377 | 170630266.5991 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193461859.5381 | 226440492.8817 | 316227.766 | 84.5105 | 2289.205 | 2679.4362 | 46.6685 | 54.6239
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.1971 | 165.6136 | 21.2284 | 4 | 2283.1627 | 2671.5413 | 46.5454 | 54.463 | 218.68 | 0 | 412.9728 | 18973867.1244 | 1181446.8269 | 19519178.2326 | 15032757.7685 | 0 | 515879.9292 | 0 | 21537020.6538 | 56034909.8909 | 38244977.4028 | 171040037.8292 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193871630.7683 | 226850264.1118 | 421696.5034 | 84.9136 | 2283.1627 | 2671.5413 | 46.5454 | 54.463
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.9398 | 166.0141 | 21.3025 | 4 | 2278.5989 | 2665.626 | 46.4523 | 54.3424 | 218.58 | 0 | 412.7668 | 19006696.5537 | 1183445.9857 | 19556930.1519 | 15080274.8754 | 0 | 488802.7814 | 0 | 21573298.6358 | 56129297.7582 | 38309399.0617 | 171328145.8038 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194159738.7428 | 227138372.0863 | 562341.3252 | 85.2101 | 2278.5989 | 2665.626 | 46.4523 | 54.3424
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 224.4734 | 166.3008 | 21.3568 | 4 | 2275.156 | 2661.1998 | 46.3821 | 54.2522 | 218.5079 | 0 | 407.0388 | 19030185.6432 | 1184876.3028 | 19583945.7136 | 15114407.0361 | 0 | 467460.9144 | 0 | 21598541.4879 | 56194974.4816 | 38354224.7749 | 171528616.3545 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194360209.2936 | 227338842.6371 | 749894.2093 | 85.4272 | 2275.156 | 2661.1998 | 46.3821 | 54.2522
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.2971 | 166.7457 | 21.4237 | 4 | 2272.4461 | 2657.284 | 46.3269 | 54.1723 | 218.3988 | 0 | 388.9458 | 19066609.9308 | 1187094.1841 | 19625845.8532 | 15167145.6177 | 0 | 455818.7321 | 0 | 21645980.584 | 56318401.2783 | 38438466.0999 | 171905362.2801 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194736955.2191 | 227715588.5626 | 1000000 | 85.6949 | 2272.4461 | 2657.284 | 46.3269 | 54.1723
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.5601 | 166.8857 | 21.4518 | 4 | 2270.5362 | 2654.8709 | 46.288 | 54.1231 | 218.3627 | 0 | 390.2238 | 19078071.0134 | 1187792.0272 | 19639031.7957 | 15183958.7066 | 0 | 443084.3539 | 0 | 21657455.7797 | 56348257.3839 | 38458843.5054 | 171996494.5657 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194828087.5048 | 227806720.8483 | 1333521.4322 | 85.8071 | 2270.5362 | 2654.8709 | 46.288 | 54.1231
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.7575 | 166.9908 | 21.4728 | 4 | 2269.0998 | 2653.0575 | 46.2587 | 54.0862 | 218.3357 | 0 | 389.4854 | 19086664.0218 | 1188315.2312 | 19648918.6093 | 15196579.5519 | 0 | 433388.1413 | 0 | 21666007.5667 | 56370507.3792 | 38474029.5844 | 172064410.0859 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194896003.0249 | 227874636.3685 | 1778279.41 | 85.8913 | 2269.0998 | 2653.0575 | 46.2587 | 54.0862
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.9109 | 167.0723 | 21.489 | 4 | 2268.0202 | 2651.6898 | 46.2367 | 54.0583 | 218.3147 | 0 | 353.4365 | 19093337.122 | 1188721.533 | 19656596.7879 | 15206384.8717 | 0 | 426101.8687 | 0 | 21672745.4515 | 56388037.9733 | 38485994.5751 | 172117920.1832 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194949513.1222 | 227928146.4658 | 2371373.7057 | 85.9558 | 2268.0202 | 2651.6898 | 46.2367 | 54.0583
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.9304 | 167.0824 | 21.4963 | 4 | 2267.0671 | 2650.6057 | 46.2172 | 54.0362 | 218.3118 | 0 | 352.9444 | 19094158.3875 | 1188771.5367 | 19657541.7703 | 15207623.4168 | 0 | 418076.7005 | 0 | 21670807.0066 | 56382994.5374 | 38482552.3265 | 172102525.6823 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 194934118.6214 | 227912751.9649 | 3162277.6602 | 85.9852 | 2267.0671 | 2650.6057 | 46.2172 | 54.0362
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.1083 | 167.1772 | 21.5099 | 4 | 2266.6001 | 2649.8964 | 46.2077 | 54.0217 | 218.2876 | 0 | 369.113 | 19101915.379 | 1189243.8273 | 19666467.5129 | 15219005.5896 | 0 | 416369.7945 | 0 | 21681270.8203 | 56410219.2342 | 38501133.7415 | 172185625.8993 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 195017218.8384 | 227995852.1819 | 4216965.0343 | 86.0395 | 2266.6001 | 2649.8964 | 46.2077 | 54.0217
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.1667 | 167.2081 | 21.5163 | 4 | 2266.143 | 2649.3249 | 46.1984 | 54.0101 | 218.2795 | 0 | 357.0125 | 19104443.9695 | 1189397.7813 | 19669377.1756 | 15222734.2102 | 0 | 413142.7723 | 0 | 21683647.4045 | 56416402.6188 | 38505354.0285 | 172204499.9608 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 195036092.8999 | 228014726.2434 | 5623413.2519 | 86.0652 | 2266.143 | 2649.3249 | 46.1984 | 54.0101
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.2056 | 167.2287 | 21.5208 | 4 | 2265.7998 | 2648.9011 | 46.1914 | 54.0014 | 218.2742 | 0 | 366.602 | 19106126.18 | 1189500.203 | 19671312.9283 | 15225219.3562 | 0 | 410646.7542 | 0 | 21685094.1145 | 56420166.6614 | 38507923.0649 | 172215989.2624 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 195047582.2015 | 228026215.545 | 7498942.0933 | 86.0833 | 2265.7998 | 2648.9011 | 46.1914 | 54.0014
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.2445 | 167.2494 | 21.5248 | 4 | 2265.5424 | 2648.5729 | 46.1861 | 53.9947 | 218.2688 | 0 | 375.4784 | 19107816.5415 | 1189603.1207 | 19673258.0795 | 15227706.1288 | 0 | 408902.8527 | 0 | 21686841.822 | 56424713.838 | 38511026.6064 | 172229868.9896 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 195061461.9286 | 228040095.2721 | 10000000 | 86.0992 | 2265.5424 | 2648.5729 | 46.1861 | 53.9947
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0887 | 0.36008 | 0.030622 | 4 | 203943.6018 | 479360.0885 | 4157.6662 | 9772.4038 | 150.0076 | 0 | 54.201 | 224145.8793 | 11156.8252 | 147435.8649 | 76200.2225 | 0 | 60432.9569 | 0 | 202554.982 | 527006.5135 | 359692.7744 | 1608626.0187 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 24980368.6472 | 58715211.556 | 100 | 0.12249 | 203943.6018 | 479360.0885 | 4157.6662 | 9772.4038
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.56436 | 0.057726 | 4 | 110882.5826 | 256981.3629 | 2260.4914 | 5238.9127 | 165.629 | 0 | 57.5041 | 325938.1456 | 18498.9226 | 209046.7916 | 100300.948 | 0 | 66701.0107 | 0 | 280989.4692 | 731076.96 | 498975.0473 | 2231527.2949 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25603269.9235 | 59338112.8322 | 133.3521 | 0.2309 | 110882.5826 | 256981.3629 | 2260.4914 | 5238.9127
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.85026 | 0.09863 | 4 | 66933.6806 | 152442.1521 | 1364.5336 | 3107.7395 | 178.8228 | 0 | 288.8132 | 455710.9458 | 29444.535 | 287645.2283 | 134434.3041 | 0 | 72654.0406 | 0 | 382156.731 | 994293.4229 | 678625.6918 | 3034964.8994 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 26406707.5279 | 60141550.4366 | 177.8279 | 0.39452 | 66933.6806 | 152442.1521 | 1364.5336 | 3107.7395
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 1.2874 | 0.15326 | 4 | 44705.6213 | 99735.7074 | 911.3846 | 2033.2473 | 190.0921 | 0 | 370.6723 | 609207.955 | 39432.4927 | 400833.9007 | 172898.7764 | 0 | 80051.9374 | 0 | 507945.7743 | 1321570.7106 | 901999.1656 | 4033940.7127 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 27405683.3412 | 61140526.2499 | 237.1374 | 0.61303 | 44705.6213 | 99735.7074 | 911.3846 | 2033.2473
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 1.8596 | 0.22479 | 4 | 31802.9127 | 69321.0892 | 648.3454 | 1413.2042 | 199.5779 | 0 | 481.2716 | 788113.7582 | 51009.117 | 537933.4247 | 220899.5516 | 0 | 88752.5762 | 0 | 657816.2868 | 1711503.0416 | 1168135.9938 | 5224163.7499 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 28595906.3784 | 62330749.2871 | 316.2278 | 0.89916 | 31802.9127 | 69321.0892 | 648.3454 | 1413.2042
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 2.5956 | 0.31718 | 4 | 23650.8928 | 50240.8573 | 482.1554 | 1024.2278 | 207.2965 | 0 | 75.7564 | 995781.887 | 64418.1383 | 702374.84 | 281278.5184 | 0 | 98135.5216 | 0 | 835375.6731 | 2173476.1423 | 1483442.1276 | 6634282.8483 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 30006025.4768 | 63740868.3855 | 421.6965 | 1.2687 | 23650.8928 | 50240.8573 | 482.1554 | 1024.2278
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.04 | 3.5702 | 0.43966 | 4 | 18049.3027 | 37231.7312 | 367.9594 | 759.0192 | 213.6686 | 0 | 73.0178 | 1245827.3862 | 80525.123 | 906438.5109 | 360244.7436 | 0 | 109470.8869 | 0 | 1053977.5937 | 2742233.4982 | 1871630.7098 | 8370348.452 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 31742091.0806 | 65476933.9893 | 562.3413 | 1.7586 | 18049.3027 | 37231.7312 | 367.9594 | 759.0192
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.499 | 4.822 | 0.59751 | 4 | 14151.7488 | 28266.5948 | 288.5025 | 576.2528 | 218.6732 | 0 | 92.4423 | 1539312.043 | 99381.4606 | 1152831.2819 | 461090.3595 | 0 | 121761.0881 | 0 | 1316006.7309 | 3423979.5637 | 2336936.408 | 10451298.9357 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 33823041.5642 | 67557884.473 | 749.8942 | 2.39 | 14151.7488 | 28266.5948 | 288.5025 | 576.2528
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3969 | 6.4399 | 0.80157 | 4 | 11337.7656 | 21859.2831 | 231.1357 | 445.6311 | 222.3802 | 0 | 75.8537 | 1887524.9891 | 121692.3969 | 1453079.1169 | 592002.9623 | 0 | 136578.9761 | 0 | 1634442.5921 | 4252484.3545 | 2902407.9518 | 12980213.3398 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 36351955.9683 | 70086798.8771 | 1000 | 3.2063 | 11337.7656 | 21859.2831 | 231.1357 | 445.6311
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.93 | 8.6562 | 1.082 | 4 | 9148.2671 | 16942.8452 | 186.4998 | 345.4028 | 226.0734 | 0 | 106.1909 | 2325730.4313 | 149684.5584 | 1840973.8094 | 767539.5109 | 0 | 153566.7351 | 0 | 2042623.0676 | 5314486.2223 | 3627246.0485 | 16221850.3837 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 39593593.0122 | 73328435.9209 | 1333.5214 | 4.328 | 9148.2671 | 16942.8452 | 186.4998 | 345.4028
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.2675 | 11.5607 | 1.4491 | 4 | 7523.7373 | 13343.7807 | 153.3816 | 272.031 | 228.6572 | 0 | 101.923 | 2853529.4988 | 183288.9742 | 2320451.8987 | 1001708.9373 | 0 | 175279.9587 | 0 | 2548361.1144 | 6630312.879 | 4525324.7792 | 20238258.0403 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 43610000.6688 | 77344843.5776 | 1778.2794 | 5.7963 | 7523.7373 | 13343.7807 | 153.3816 | 272.031
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.7064 | 15.4068 | 1.9354 | 4 | 6279.1155 | 10636.82 | 128.0083 | 216.846 | 230.6889 | 0 | 80.1613 | 3496806.3172 | 224102.1411 | 2919813.0462 | 1305985.0813 | 0 | 201660.2888 | 0 | 3177863.0811 | 8268147.8677 | 5643180.8132 | 25237558.6368 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 48609301.2653 | 82344144.174 | 2371.3737 | 7.7414 | 6279.1155 | 10636.82 | 128.0083 | 216.846
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.5453 | 20.4815 | 2.5772 | 4 | 5320.4923 | 8592.9056 | 108.4654 | 175.178 | 232.2568 | 0 | 94.7324 | 4278730.8614 | 273526.8254 | 3666686.7521 | 1710241.3595 | 0 | 233512.4749 | 0 | 3963452.3266 | 10312089.9379 | 7038213.2749 | 31476453.8126 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 54848196.4411 | 88583039.3499 | 3162.2777 | 10.3089 | 5320.4923 | 8592.9056 | 108.4654 | 175.178
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2406 | 27.1728 | 3.4237 | 4 | 4573.3127 | 7036.6579 | 93.2332 | 143.4518 | 233.4645 | 0 | 106.6349 | 5229406.1675 | 333380.9404 | 4597184.3 | 2243101.0688 | 0 | 272199.7584 | 0 | 4943356.1717 | 12861598.737 | 8778305.4174 | 39258532.5611 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 62630275.1897 | 96365118.0984 | 4216.965 | 13.6947 | 4573.3127 | 7036.6579 | 93.2332 | 143.4518
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.3332 | 35.9493 | 4.534 | 4 | 3986.6552 | 5846.7738 | 81.2734 | 119.1944 | 234.3825 | 0 | 105.2047 | 6380249.0043 | 405536.9388 | 5750918.7346 | 2941955.3603 | 0 | 319098.5691 | 0 | 6161125.8568 | 16029985.6587 | 10940794.5953 | 48929664.7179 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 72301407.3464 | 106036250.2551 | 5623.4133 | 18.1359 | 3986.6552 | 5846.7738 | 81.2734 | 119.1944
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.3541 | 47.2517 | 5.9639 | 4 | 3526.5372 | 4940.661 | 71.8932 | 100.7221 | 235.0174 | 0 | 125.8584 | 7750270.2386 | 491065.4973 | 7156801.1073 | 3843233.708 | 0 | 374748.9802 | 0 | 7650286.6173 | 19904476.4886 | 13585214.1995 | 60756096.8368 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 84127839.4653 | 117862682.3741 | 7498.9421 | 23.8557 | 3526.5372 | 4940.661 | 71.8932 | 100.7221
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.8385 | 61.4377 | 7.757 | 4 | 3167.6863 | 4254.9247 | 64.5776 | 86.7424 | 235.2457 | 0 | 123.7384 | 9344167.3948 | 590135.1385 | 8829431.1292 | 4982319.6477 | 0 | 441586.4153 | 0 | 9433179.493 | 24543198.0296 | 16751236.9675 | 74915254.2158 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 98286996.8443 | 132021839.7531 | 10000 | 31.028 | 3167.6863 | 4254.9247 | 64.5776 | 86.7424
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.9654 | 78.3714 | 9.8917 | 4 | 2894.6739 | 3747.2796 | 59.0118 | 76.3934 | 234.8108 | 0 | 113.321 | 11115732.31 | 699773.3118 | 10727805.6095 | 6367154.1278 | 0 | 522424.393 | 0 | 11478827.0033 | 29865553.2315 | 20383853.7562 | 91161123.7431 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 114532866.3716 | 148267709.2804 | 13335.2143 | 39.5668 | 2894.6739 | 3747.2796 | 59.0118 | 76.3934
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.3736 | 97.2527 | 12.259 | 4 | 2694.7181 | 3382.6806 | 54.9355 | 68.9605 | 233.4826 | 0 | 149.6605 | 12967552.8017 | 813913.0176 | 12749873.8832 | 7965114.2639 | 0 | 620502.8204 | 0 | 13695613.1468 | 35633176.0515 | 24320374.8437 | 108766120.8288 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 132137863.4573 | 165872706.366 | 17782.7941 | 49.0359 | 2694.7181 | 3382.6806 | 54.9355 | 68.9605
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8984 | 116.595 | 14.664 | 4 | 2555.4718 | 3130.602 | 52.0967 | 63.8216 | 231.2548 | 0 | 146.2851 | 14761884.767 | 924108.5377 | 14741060.6295 | 9688018.185 | 0 | 734672.3263 | 0 | 15931400.3337 | 41450235.6888 | 28290637.5748 | 126522018.0429 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 149893760.6714 | 183628603.5802 | 23713.7371 | 58.656 | 2555.4718 | 3130.602 | 52.0967 | 63.8216
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.94 | 135.3678 | 16.9817 | 4 | 2459.0638 | 2955.6992 | 50.1313 | 60.2559 | 228.7319 | 0 | 158.6522 | 16424629.4364 | 1025906.4789 | 16611049.1686 | 11468937.775 | 0 | 853974.2206 | 0 | 18089953.861 | 47066349.1865 | 32123750.4366 | 143664550.5636 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 167036293.1921 | 200771136.1009 | 31622.7766 | 67.9268 | 2459.0638 | 2955.6992 | 50.1313 | 60.2559
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.7802 | 151.7304 | 18.9784 | 4 | 2395.6509 | 2840.0351 | 48.8386 | 57.898 | 225.9559 | 0 | 144.7726 | 17821543.5652 | 1111214.0841 | 18198799.3918 | 13066666.3426 | 0 | 973212.9113 | 0 | 19956860.155 | 51923656.4085 | 35438962.4232 | 158490915.2816 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 181862657.9101 | 215597500.8189 | 42169.6503 | 75.9137 | 2395.6509 | 2840.0351 | 48.8386 | 57.898
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.5339 | 160.2507 | 20.1017 | 4 | 2356.1656 | 2775.718 | 48.0336 | 56.5868 | 224.2652 | 0 | 154.62 | 18532077.7477 | 1154534.5604 | 19011863.2245 | 13965004.8404 | 0 | 958177.5311 | 0 | 20912446.5826 | 54409896.2753 | 37135872.2195 | 166079872.9814 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 189451615.61 | 223186458.5187 | 56234.1325 | 80.4067 | 2356.1656 | 2775.718 | 48.0336 | 56.5868
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.4381 | 163.7571 | 20.6629 | 4 | 2326.8164 | 2734.974 | 47.4353 | 55.7561 | 223.4985 | 0 | 202.6555 | 18821387.0965 | 1172160.2505 | 19343931.2782 | 14348826.2685 | 0 | 859804.417 | 0 | 21272982.6311 | 55347937.1175 | 37776104.3691 | 168943133.4283 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 192314876.0568 | 226049718.9656 | 74989.4209 | 82.6515 | 2326.8164 | 2734.974 | 47.4353 | 55.7561
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.954 | 166.3807 | 21.0924 | 4 | 2304.4738 | 2704.3199 | 46.9798 | 55.1312 | 222.8995 | 0 | 213.5155 | 19036726.4905 | 1185274.5848 | 19591469.2189 | 14641607.9541 | 0 | 773104.2757 | 0 | 21538991.1844 | 56040036.8071 | 38248476.6285 | 171055687.144 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 194427429.7725 | 228162272.6812 | 100000 | 84.3696 | 2304.4738 | 2704.3199 | 46.9798 | 55.1312
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.3586 | 168.3242 | 21.4173 | 4 | 2287.4868 | 2681.2663 | 46.6335 | 54.6612 | 222.4406 | 0 | 271.6684 | 19195630.4164 | 1194949.3227 | 19774334.7017 | 14861744.9208 | 0 | 698783.3156 | 0 | 21732922.6441 | 56544606.6846 | 38592855.9377 | 172595827.9437 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 195967570.5723 | 229702413.481 | 133352.1432 | 85.6694 | 2287.4868 | 2681.2663 | 46.6335 | 54.6612
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.9191 | 169.7667 | 21.6626 | 4 | 2274.5936 | 2663.9156 | 46.3707 | 54.3075 | 222.0914 | 0 | 299.3711 | 19313243.9481 | 1202108.6987 | 19909792.8119 | 15027224.8338 | 0 | 636777.1567 | 0 | 21874767.5052 | 56913657.9168 | 38844740.9869 | 173722313.8582 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197094056.4867 | 230828899.3954 | 177827.941 | 86.6502 | 2274.5936 | 2663.9156 | 46.3707 | 54.3075
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 224.0092 | 170.931 | 21.8572 | 4 | 2264.8104 | 2650.6657 | 46.1712 | 54.0374 | 221.8045 | 0 | 340.3991 | 19407969.2362 | 1207873.9413 | 20018957.2239 | 15161561.0011 | 0 | 588354.8436 | 0 | 21990039.336 | 57213571.5749 | 39049438.2212 | 174637765.3782 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 198009508.0067 | 231744350.9154 | 237137.3706 | 87.4287 | 2264.8104 | 2650.6657 | 46.1712 | 54.0374
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.446 | 171.7237 | 21.9954 | 4 | 2257.3997 | 2640.83 | 46.0201 | 53.8369 | 221.6054 | 0 | 411.2739 | 19472353.6213 | 1211792.1067 | 20093189.8939 | 15253636.8389 | 0 | 547570.5531 | 0 | 22065631.7754 | 57410247.5962 | 39183673.647 | 175238096.0326 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 198609838.6611 | 232344681.5698 | 316227.766 | 87.9817 | 2257.3997 | 2640.83 | 46.0201 | 53.8369
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.4614 | 172.2803 | 22.0955 | 4 | 2251.7968 | 2633.4904 | 45.9059 | 53.6873 | 221.4638 | 0 | 414.9463 | 19517511.3949 | 1214540.006 | 20145271.4339 | 15318682.6651 | 0 | 514418.326 | 0 | 22117065.2921 | 57544067.0562 | 39275008.1782 | 175646564.3526 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 199018306.9811 | 232753149.8898 | 421696.5034 | 88.382 | 2251.7968 | 2633.4904 | 45.9059 | 53.6873
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.2191 | 172.6938 | 22.1704 | 4 | 2247.5661 | 2627.9696 | 45.8197 | 53.5747 | 221.3578 | 0 | 433.3795 | 19551041.5955 | 1216580.2406 | 20183951.3425 | 15367216.0359 | 0 | 488415.3585 | 0 | 22154809.7835 | 57642270.4803 | 39342034.033 | 175946318.8699 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 199318061.4985 | 233052904.4072 | 562341.3252 | 88.6817 | 2247.5661 | 2627.9696 | 45.8197 | 53.5747
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.046 | 172.5945 | 22.1823 | 4 | 2244.2591 | 2624.4588 | 45.7523 | 53.5031 | 221.3788 | 0 | 522.5384 | 19542988.4042 | 1216090.2316 | 20174660.6307 | 15356048.9634 | 0 | 457174.4635 | 0 | 22131315.4504 | 57581143.045 | 39300313.3024 | 175759734.4911 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 199131477.1196 | 232866320.0284 | 749894.2093 | 88.7293 | 2244.2591 | 2624.4588 | 45.7523 | 53.5031
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.5755 | 173.4337 | 22.2916 | 4 | 2241.8876 | 2620.2241 | 45.7039 | 53.4168 | 221.1692 | 0 | 477.5153 | 19610970.4574 | 1220226.5301 | 20253102.8125 | 15454134.3324 | 0 | 456873.5544 | 0 | 22228169.9978 | 57833138.7098 | 39472305.5216 | 176528921.916 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 199900664.5445 | 233635507.4532 | 1000000 | 89.1662 | 2241.8876 | 2620.2241 | 45.7039 | 53.4168
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.8534 | 173.5835 | 22.3204 | 4 | 2240.1188 | 2617.9664 | 45.6679 | 53.3708 | 221.1297 | 0 | 477.7064 | 19623093.4304 | 1220964.0981 | 20267094.2991 | 15471916.1137 | 0 | 444768.0876 | 0 | 22240856.0513 | 57866145.2185 | 39494833.142 | 176629670.4407 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200001413.0693 | 233736255.978 | 1333521.4322 | 89.2816 | 2240.1188 | 2617.9664 | 45.6679 | 53.3708
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.823 | 173.0155 | 22.2669 | 4 | 2238.7369 | 2617.493 | 45.6397 | 53.3611 | 221.2685 | 0 | 444.3262 | 19577100.4064 | 1218165.7914 | 20214017.5015 | 15405781.4831 | 0 | 418128.2996 | 0 | 22164945.458 | 57668641.4263 | 39360032.7455 | 176026813.112 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 199398555.7405 | 233133398.6493 | 1778279.41 | 89.0674 | 2238.7369 | 2617.493 | 45.6397 | 53.3611
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.2212 | 173.7815 | 22.3585 | 4 | 2237.7892 | 2614.9934 | 45.6204 | 53.3102 | 221.0774 | 0 | 485.93 | 19639116.4345 | 1221938.9266 | 20285588.4121 | 15495458.0019 | 0 | 428604.1975 | 0 | 22257575.3293 | 57909645.3504 | 39524522.8759 | 176762449.5283 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200134192.1568 | 233869035.0655 | 2371373.7057 | 89.4339 | 2237.7892 | 2614.9934 | 45.6204 | 53.3102
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.3527 | 173.8524 | 22.3715 | 4 | 2237.0383 | 2614.0226 | 45.6051 | 53.2904 | 221.0587 | 0 | 482.8569 | 19644847.4839 | 1222287.5943 | 20292203.7287 | 15503876.3258 | 0 | 423509.0394 | 0 | 22263822.4271 | 57925899.0174 | 39535616.3375 | 176812061.954 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200183804.5826 | 233918647.4913 | 3162277.6602 | 89.4861 | 2237.0383 | 2614.0226 | 45.6051 | 53.2904
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.4381 | 173.8982 | 22.3805 | 4 | 2236.4746 | 2613.3076 | 45.5936 | 53.2758 | 221.0465 | 0 | 488.3409 | 19648555.7822 | 1222513.1996 | 20296484.3106 | 15509339.6731 | 0 | 419481.3656 | 0 | 22267585.9892 | 57935691.0338 | 39542299.59 | 176841950.9442 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200213693.5727 | 233948536.4814 | 4216965.0343 | 89.522 | 2236.4746 | 2613.3076 | 45.5936 | 53.2758
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.4964 | 173.9295 | 22.3869 | 4 | 2236.0514 | 2612.7768 | 45.5849 | 53.265 | 221.0382 | 0 | 496.9506 | 19651084.5088 | 1222667.0415 | 20299403.3351 | 15513072.2603 | 0 | 416368.2296 | 0 | 22270012.1964 | 57942003.5274 | 39546607.9966 | 176861219.0957 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200232961.7242 | 233967804.633 | 5623413.2519 | 89.5476 | 2236.0514 | 2612.7768 | 45.5849 | 53.265
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.5501 | 173.9584 | 22.3923 | 4 | 2235.7338 | 2612.3684 | 45.5785 | 53.2567 | 221.0305 | 0 | 482.6722 | 19653420.7426 | 1222809.1721 | 20302100.1937 | 15516510.3373 | 0 | 414160.4881 | 0 | 22272510.3642 | 57948503.2475 | 39551044.1891 | 176881058.7344 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200252801.3629 | 233987644.2717 | 7498942.0933 | 89.5692 | 2235.7338 | 2612.3684 | 45.5785 | 53.2567
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.587 | 173.9782 | 22.3961 | 4 | 2235.4956 | 2612.0656 | 45.5736 | 53.2505 | 221.0253 | 0 | 487.1584 | 19655021.3433 | 1222906.5484 | 20303947.8864 | 15518869.6294 | 0 | 412453.4342 | 0 | 22274147.5483 | 57952762.8647 | 39553951.4653 | 176894060.72 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 200265803.3485 | 234000646.2573 | 10000000 | 89.5845 | 2235.4956 | 2612.0656 | 45.5736 | 53.2505
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1276 | 0.38957 | 0.034612 | 4 | 185072.6684 | 434261.7634 | 3772.9567 | 8853.0134 | 153.5083 | 0 | 62.2408 | 240241.2533 | 12305.0902 | 156645.1181 | 79770.6562 | 0 | 61472.4472 | 0 | 214669.4803 | 558525.9531 | 381205.4395 | 1704835.438 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25622587.8468 | 60121844.448 | 100 | 0.13845 | 185072.6684 | 434261.7634 | 3772.9567 | 8853.0134
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.60141 | 0.06361 | 4 | 103206.8003 | 238795.4252 | 2104.0102 | 4868.1677 | 168.8117 | 0 | 63.8987 | 345075.5131 | 20195.4228 | 219469.628 | 104551.4388 | 0 | 66943.1357 | 0 | 294931.704 | 767351.7949 | 523733.3675 | 2342252.0048 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 26260004.4137 | 60759261.0149 | 133.3521 | 0.25444 | 103206.8003 | 238795.4252 | 2104.0102 | 4868.1677
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.91036 | 0.10663 | 4 | 63513.3561 | 144402.1624 | 1294.8057 | 2943.8334 | 181.8457 | 0 | 285.2255 | 478170.3741 | 30938.3872 | 303778.4399 | 138618.4665 | 0 | 72251.6005 | 0 | 399265.3346 | 1038806.5 | 709006.7816 | 3170835.8845 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 27088588.2933 | 61587844.8945 | 177.8279 | 0.4265 | 63513.3561 | 144402.1624 | 1294.8057 | 2943.8334
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4099 | 1.3753 | 0.16473 | 4 | 42688.7232 | 95044.4712 | 870.2674 | 1937.6101 | 193.3966 | 0 | 369.5147 | 637992.7282 | 41296.6853 | 422562.7988 | 178088.1101 | 0 | 79819.9168 | 0 | 530306.4933 | 1379748.7147 | 941706.8488 | 4211522.296 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 28129274.7049 | 62628531.3061 | 237.1374 | 0.65894 | 42688.7232 | 95044.4712 | 870.2674 | 1937.6101
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.11 | 1.9797 | 0.24052 | 4 | 30520.4552 | 66379.7379 | 622.2008 | 1353.2407 | 202.995 | 0 | 485.9911 | 823436.9894 | 53292.569 | 565532.6955 | 227465.8332 | 0 | 88332.9828 | 0 | 685643.8173 | 1783904.5677 | 1217551.523 | 5445160.9778 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 29362913.3867 | 63862169.9879 | 316.2278 | 0.96207 | 30520.4552 | 66379.7379 | 622.2008 | 1353.2407
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0117 | 2.766 | 0.33953 | 4 | 22709.4044 | 48111.7414 | 462.9619 | 980.8229 | 210.8525 | 0 | 53.0131 | 1041271.8829 | 67351.4546 | 739044.2521 | 290388.6818 | 0 | 97535.9491 | 0 | 871880.966 | 2268455.4262 | 1548267.4404 | 6924196.0531 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 30841948.4619 | 65341205.0631 | 421.6965 | 1.3581 | 22709.4044 | 48111.7414 | 462.9619 | 980.8229
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.13 | 3.749 | 0.46393 | 4 | 17545.6182 | 36136.5426 | 357.6912 | 736.6923 | 217.0096 | 0 | 85.2951 | 1289398.3482 | 83327.7661 | 942582.3677 | 368152.0573 | 0 | 106664.5979 | 0 | 1088148.8035 | 2831139.9767 | 1932311.2082 | 8641725.1256 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 32559477.5344 | 67058734.1356 | 562.3413 | 1.8557 | 17545.6182 | 36136.5426 | 357.6912 | 736.6923
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 5.0689 | 0.6309 | 4 | 13758.0167 | 27428.65 | 280.4758 | 559.1701 | 222.0958 | 0 | 76.0117 | 1594431.0886 | 102917.3715 | 1199825.5547 | 472030.2547 | 0 | 118409.8011 | 0 | 1360169.4875 | 3538881.9975 | 2415359.68 | 10802025.2357 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 34719777.6445 | 69219034.2457 | 749.8942 | 2.5236 | 13758.0167 | 27428.65 | 280.4758 | 559.1701
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.5601 | 6.7634 | 0.84538 | 4 | 11038.5566 | 21240.879 | 225.0359 | 433.024 | 225.7999 | 0 | 87.4608 | 1953914.4358 | 125939.1174 | 1511174.5568 | 606081.0055 | 0 | 132287.4089 | 0 | 1688464.6445 | 4393038.6534 | 2998339.1489 | 13409238.9713 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 37326991.3801 | 71826247.9813 | 1000 | 3.3815 | 11038.5566 | 21240.879 | 225.0359 | 433.024
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1541 | 9.1027 | 1.1425 | 4 | 8904.9805 | 16454.292 | 181.5401 | 335.443 | 229.5943 | 0 | 109.2345 | 2409854.4111 | 155048.3896 | 1916558.9949 | 787147.7774 | 0 | 148032.4812 | 0 | 2112490.4011 | 5496266.6924 | 3751314.9546 | 16776714.1023 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 40694466.5111 | 75193723.1123 | 1333.5214 | 4.5699 | 8904.9805 | 16454.292 | 181.5401 | 335.443
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5453 | 12.1306 | 1.5268 | 4 | 7336.5649 | 12985.4839 | 149.5658 | 264.7267 | 232.1922 | 0 | 90.3688 | 2952343.9935 | 189568.098 | 2411522.5464 | 1023181.5487 | 0 | 167535.7665 | 0 | 2630219.2617 | 6843290.9867 | 4670686.714 | 20888348.9153 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 44806101.3241 | 79305357.9253 | 1778.2794 | 6.1072 | 7336.5649 | 12985.4839 | 149.5658 | 264.7267
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0502 | 16.158 | 2.038 | 4 | 6129.2155 | 10361.1472 | 124.9523 | 211.226 | 234.2363 | 0 | 83.248 | 3616744.357 | 231695.8384 | 3033155.9007 | 1336842.5056 | 0 | 191724.6401 | 0 | 3279963.6643 | 8533792.6415 | 5824488.8297 | 26048408.3773 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 49966160.7861 | 84465417.3873 | 2371.3737 | 8.1521 | 6129.2155 | 10361.1472 | 124.9523 | 211.226
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9863 | 21.4689 | 2.7125 | 4 | 5197.586 | 8377.2797 | 105.9598 | 170.7822 | 235.8184 | 0 | 100.2971 | 4424050.4196 | 282692.0678 | 3807433.4493 | 1750172.6949 | 0 | 220866.2303 | 0 | 4089233.7961 | 10639347.5204 | 7261573.2994 | 32475369.4778 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 56393121.8866 | 90892378.4878 | 3162.2777 | 10.8499 | 5197.586 | 8377.2797 | 105.9598 | 170.7822
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.8131 | 28.4749 | 3.6023 | 4 | 4470.3766 | 6864.6482 | 91.1347 | 139.9451 | 237.038 | 0 | 113.1374 | 5406184.6485 | 344484.9387 | 4772590.4511 | 2295271.9065 | 0 | 256365.0491 | 0 | 5099209.8276 | 13267097.9797 | 9055066.9828 | 40496271.7841 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 64414024.1929 | 98913280.7941 | 4216.965 | 14.4091 | 4470.3766 | 6864.6482 | 91.1347 | 139.9451
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.0495 | 37.6383 | 4.7663 | 4 | 3899.9945 | 5709.5394 | 79.5067 | 116.3967 | 237.9617 | 0 | 124.7308 | 6592017.9306 | 418782.2202 | 5966079.2897 | 3008248.0622 | 0 | 299058.8114 | 0 | 6350832.6625 | 16523563.8529 | 11277671.8549 | 50436254.6844 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 74354007.0933 | 108853263.6945 | 5623.4133 | 19.0652 | 3899.9945 | 5709.5394 | 79.5067 | 116.3967
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.2775 | 49.4555 | 6.2673 | 4 | 3451.6094 | 4827.7778 | 70.3657 | 98.4208 | 238.5944 | 0 | 94.2291 | 8005948.5472 | 506987.1499 | 7422601.1719 | 3929197.5506 | 0 | 350231.014 | 0 | 7883836.5191 | 20512125.4255 | 13999947.0849 | 62610874.4631 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 86528626.8719 | 121027883.4731 | 7498.9421 | 25.0691 | 3451.6094 | 4827.7778 | 70.3657 | 98.4208
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.9789 | 64.2369 | 8.143 | 4 | 3102.6016 | 4161.7688 | 63.2507 | 84.8433 | 238.7965 | 0 | 118.2853 | 9645710.6864 | 608830.3683 | 9149819.5997 | 5089804.8028 | 0 | 411889.7522 | 0 | 9713361.5317 | 25272174.221 | 17248778.1971 | 77140369.1593 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 101058121.5681 | 135557378.1693 | 10000 | 32.5721 | 3102.6016 | 4161.7688 | 63.2507 | 84.8433
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.3273 | 81.8211 | 10.3681 | 4 | 2837.539 | 3669.3979 | 57.8471 | 74.8056 | 238.3023 | 0 | 132.5 | 11462720.475 | 721194.7994 | 11103933.4689 | 6497028.1353 | 0 | 487760.808 | 0 | 11806328.6978 | 30717645.4605 | 20965424.2113 | 93762036.0562 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 117679788.465 | 152179045.0662 | 13335.2143 | 41.4725 | 2837.539 | 3669.3979 | 57.8471 | 74.8056
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.8622 | 101.2875 | 12.818 | 4 | 2644.2232 | 3317.0908 | 53.9061 | 67.6234 | 236.887 | 0 | 128.9772 | 13349576.1856 | 837405.7647 | 13171318.8203 | 8110837.9403 | 0 | 581128.1727 | 0 | 14059604.0846 | 36580205.8067 | 24966742.1111 | 111656818.8858 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 135574571.2947 | 170073827.8959 | 17782.7941 | 51.272 | 2644.2232 | 3317.0908 | 53.9061 | 67.6234
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.4648 | 121.1708 | 15.2993 | 4 | 2509.5896 | 3073.327 | 51.1614 | 62.6539 | 234.574 | 0 | 144.1947 | 15173702.9268 | 949348.3992 | 15202085.7499 | 9846570.4728 | 0 | 692023.7723 | 0 | 16326855.2152 | 42479128.1714 | 28992877.8358 | 129662592.5432 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 153580344.9521 | 188079601.5533 | 23713.7371 | 61.1974 | 2509.5896 | 3073.327 | 51.1614 | 62.6539
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.5166 | 140.2723 | 17.6654 | 4 | 2415.8898 | 2904.1214 | 49.2512 | 59.2044 | 231.9615 | 0 | 132.8326 | 16848073.0786 | 1051785.6368 | 17090791.0526 | 11595199.8389 | 0 | 808721.8626 | 0 | 18483882.8731 | 48091271.6701 | 32823281.0916 | 146793007.1043 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 170710759.5131 | 205210016.1143 | 31622.7766 | 70.6617 | 2415.8898 | 2904.1214 | 49.2512 | 59.2044
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.181 | 157.0096 | 19.7161 | 4 | 2355.7154 | 2793.1663 | 48.0244 | 56.9425 | 229.1095 | 0 | 175.3341 | 18263067.8178 | 1138138.7827 | 18703616.0184 | 13229875.4634 | 0 | 925826.7939 | 0 | 20381604.7018 | 53028754.592 | 36193214.641 | 161864098.8111 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 185781851.2199 | 220281107.8211 | 42169.6503 | 78.8643 | 2355.7154 | 2793.1663 | 48.0244 | 56.9425
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.7982 | 166.853 | 20.9786 | 4 | 2318.3068 | 2729.4307 | 47.2618 | 55.6431 | 227.1241 | 0 | 148.8988 | 19075390.1064 | 1187628.793 | 19635947.3403 | 14248668.9446 | 0 | 940473.0346 | 0 | 21484362.2054 | 55897903.4097 | 38151467.6642 | 170621841.4981 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 194539593.907 | 229038850.5082 | 56234.1325 | 83.9145 | 2318.3068 | 2729.4307 | 47.2618 | 55.6431
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.6318 | 170.3635 | 21.5376 | 4 | 2291.1219 | 2691.5762 | 46.7076 | 54.8714 | 226.3358 | 0 | 182.6068 | 19361820.5701 | 1205065.3038 | 19965766.5751 | 14628923.9644 | 0 | 843872.6557 | 0 | 21842125.1369 | 56828729.1704 | 38786775.3724 | 173463078.7488 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 197380831.1576 | 231880087.7588 | 74989.4209 | 86.1503 | 2291.1219 | 2691.5762 | 46.7076 | 54.8714
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.3038 | 173.111 | 21.9776 | 4 | 2270.4382 | 2662.8745 | 46.286 | 54.2863 | 225.6918 | 0 | 232.5961 | 19584842.518 | 1218636.8496 | 20222951.0653 | 14931984.2611 | 0 | 761989.6023 | 0 | 22120957.6756 | 57554194.2395 | 39281920.1889 | 175677476.4002 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 199595228.809 | 234094485.4102 | 100000 | 87.9104 | 2270.4382 | 2662.8745 | 46.286 | 54.2863
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.7038 | 175.0723 | 22.3022 | 4 | 2254.7122 | 2641.4371 | 45.9654 | 53.8493 | 225.2153 | 0 | 267.7924 | 19743439.1101 | 1228285.3058 | 20406041.217 | 15151465.082 | 0 | 689969.0109 | 0 | 22315487.893 | 58060321.9617 | 39627362.7592 | 177222372.3397 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 201140124.7485 | 235639381.3497 | 133352.1432 | 89.2088 | 2254.7122 | 2641.4371 | 45.9654 | 53.8493
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.2512 | 176.5222 | 22.5463 | 4 | 2242.7846 | 2625.3231 | 45.7222 | 53.5208 | 224.854 | 0 | 316.4057 | 19860356.071 | 1235396.7382 | 20541120.2082 | 15315867.6411 | 0 | 629868.0606 | 0 | 22457217.4005 | 58429073.0674 | 39879042.9659 | 178347942.1529 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202265694.5617 | 236764951.1629 | 177827.941 | 90.1851 | 2242.7846 | 2625.3231 | 45.7222 | 53.5208
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.1466 | 177.5899 | 22.7288 | 4 | 2233.7491 | 2613.2148 | 45.538 | 53.2739 | 224.5828 | 0 | 330.8932 | 19946285.2506 | 1240622.6058 | 20640454.4696 | 15438206.1896 | 0 | 580619.9106 | 0 | 22560013.4862 | 58696527.3961 | 40061586.0409 | 179164315.3495 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 203082067.7583 | 237581324.3595 | 237137.3706 | 90.9153 | 2233.7491 | 2613.2148 | 45.538 | 53.2739
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.5614 | 178.3806 | 22.8656 | 4 | 2226.9119 | 2604.1081 | 45.3986 | 53.0883 | 224.3789 | 0 | 398.0189 | 20009830.3432 | 1244486.7592 | 20713943.4791 | 15529505.1471 | 0 | 541027.6881 | 0 | 22635129.4325 | 58891963.6799 | 40194975.3204 | 179760861.8493 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 203678614.2582 | 238177870.8594 | 316227.766 | 91.4624 | 2226.9119 | 2604.1081 | 45.3986 | 53.0883
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.5897 | 178.9517 | 22.9663 | 4 | 2221.7446 | 2597.2874 | 45.2933 | 52.9492 | 224.2299 | 0 | 404.1972 | 20055680.0423 | 1247274.6496 | 20766984.2212 | 15595852.0259 | 0 | 509263.3693 | 0 | 22688271.1802 | 59030227.6066 | 40289343.2914 | 180182896.3866 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 204100648.7954 | 238599905.3966 | 421696.5034 | 91.865 | 2221.7446 | 2597.2874 | 45.2933 | 52.9492
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 230.364 | 179.38 | 23.042 | 4 | 2217.8439 | 2592.1519 | 45.2137 | 52.8445 | 224.1173 | 0 | 472.4444 | 20090029.7931 | 1249363.1692 | 20806730.2508 | 15645806.1268 | 0 | 484458.3692 | 0 | 22727791.2065 | 59133050.6083 | 40359522.1028 | 180496751.6265 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 204414504.0353 | 238913760.6365 | 562341.3252 | 92.1681 | 2217.8439 | 2592.1519 | 45.2137 | 52.8445
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.4332 | 179.973 | 23.1299 | 4 | 2214.8001 | 2587.6857 | 45.1517 | 52.7535 | 223.9643 | 0 | 468.5109 | 20137566.5301 | 1252253.3141 | 20861747.4416 | 15714772.8675 | 0 | 470848.4922 | 0 | 22790503.5717 | 59296215.3186 | 40470885.3703 | 180994792.9062 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 204912545.315 | 239411801.9162 | 749894.2093 | 92.5197 | 2214.8001 | 2587.6857 | 45.1517 | 52.7535
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.8398 | 180.1952 | 23.1704 | 4 | 2212.6328 | 2584.8676 | 45.1075 | 52.696 | 223.9044 | 0 | 469.2202 | 20155359.8017 | 1253335.0628 | 20882344.4242 | 15740863.4202 | 0 | 456106.0669 | 0 | 22810323.4225 | 59347782.5048 | 40506081.0345 | 181152195.7376 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205069948.1464 | 239569204.7476 | 1000000 | 92.6814 | 2212.6328 | 2584.8676 | 45.1075 | 52.696
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.1325 | 180.3547 | 23.1999 | 4 | 2211.0022 | 2582.7624 | 45.0743 | 52.6531 | 223.8612 | 0 | 447.5822 | 20168132.7077 | 1254111.58 | 20897131.2278 | 15759641.1379 | 0 | 444672.3883 | 0 | 22824238.7262 | 59383987.2705 | 40530791.531 | 181262706.5694 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205180458.9782 | 239679715.5794 | 1333521.4322 | 92.7998 | 2211.0022 | 2582.7624 | 45.0743 | 52.6531
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.354 | 180.4753 | 23.2223 | 4 | 2209.7762 | 2581.1791 | 45.0493 | 52.6208 | 223.8285 | 0 | 469.6549 | 20177787.9553 | 1254698.5528 | 20908309.5079 | 15773854.4089 | 0 | 435998.8699 | 0 | 22834753.225 | 59411343.8394 | 40549462.9515 | 181346209.3107 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205263961.7195 | 239763218.3207 | 1778279.41 | 92.889 | 2209.7762 | 2581.1791 | 45.0493 | 52.6208
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.4808 | 180.5439 | 23.2366 | 4 | 2208.8551 | 2580.0292 | 45.0305 | 52.5974 | 223.8095 | 0 | 455.354 | 20183280.9476 | 1255032.4856 | 20914669.2393 | 15781988.9623 | 0 | 428893.114 | 0 | 22839907.252 | 59424753.5607 | 40558615.3617 | 181387140.9233 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205304893.3321 | 239804149.9333 | 2371373.7057 | 92.9463 | 2208.8551 | 2580.0292 | 45.0305 | 52.5974
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.6512 | 180.637 | 23.252 | 4 | 2208.1631 | 2579.0917 | 45.0164 | 52.5783 | 223.7846 | 0 | 470.1901 | 20190731.0633 | 1255485.3928 | 20923295.2175 | 15792929.3615 | 0 | 424533.3636 | 0 | 22848920.0155 | 59448202.9223 | 40574620.0329 | 181458717.3692 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205376469.778 | 239875726.3792 | 3162277.6602 | 93.0078 | 2208.1631 | 2579.0917 | 45.0164 | 52.5783
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.7413 | 180.6859 | 23.2612 | 4 | 2207.6437 | 2578.4254 | 45.0058 | 52.5647 | 223.7713 | 0 | 488.5655 | 20194641.0779 | 1255723.0884 | 20927822.4977 | 15798703.7713 | 0 | 420731.458 | 0 | 22853072.5384 | 59459006.9351 | 40581993.9936 | 181491695.3603 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205409447.7691 | 239908704.3703 | 4216965.0343 | 93.0447 | 2207.6437 | 2578.4254 | 45.0058 | 52.5647
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.8 | 180.7176 | 23.2675 | 4 | 2207.2538 | 2577.9341 | 44.9979 | 52.5547 | 223.7625 | 0 | 480.0823 | 20197184.4715 | 1255877.7043 | 20930767.4639 | 15802470.9519 | 0 | 417748.2087 | 0 | 22855579.0321 | 59465528.3177 | 40586444.9713 | 181511601.1215 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205429353.5303 | 239928610.1315 | 5623413.2519 | 93.0701 | 2207.2538 | 2577.9341 | 44.9979 | 52.5547
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.8487 | 180.744 | 23.2726 | 4 | 2206.9612 | 2577.5609 | 44.9919 | 52.5471 | 223.7553 | 0 | 467.8675 | 20199296.1212 | 1256006.0737 | 20933212.5503 | 15805593.8947 | 0 | 415565.3965 | 0 | 22857772.8742 | 59471236.2447 | 40590340.7487 | 181529023.9039 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205446776.3127 | 239946032.9139 | 7498942.0933 | 93.0903 | 2206.9612 | 2577.5609 | 44.9919 | 52.5471
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.8876 | 180.7651 | 23.2765 | 4 | 2206.7417 | 2577.2787 | 44.9874 | 52.5413 | 223.7495 | 0 | 474.5301 | 20200984.8598 | 1256108.7335 | 20935167.967 | 15808089.3507 | 0 | 413956.1471 | 0 | 22859579.7527 | 59475937.3719 | 40593549.3647 | 181543373.5475 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 205461125.9563 | 239960382.5575 | 10000000 | 93.1061 | 2206.7417 | 2577.2787 | 44.9874 | 52.5413
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1619 | 0.4172 | 0.038523 | 4 | 170426.6395 | 399325.9715 | 3474.3776 | 8140.8001 | 156.7317 | 0 | 49.4919 | 255185.1252 | 13413.5565 | 165125.1164 | 82771.612 | 0 | 62080.5961 | 0 | 225644.6424 | 587081.0735 | 400694.896 | 1791996.6182 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 26261618.8982 | 61533493.3191 | 100 | 0.15409 | 170426.6395 | 399325.9715 | 3474.3776 | 8140.8001
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4908 | 0.63654 | 0.069573 | 4 | 96724.3714 | 223468.1929 | 1971.8571 | 4555.7014 | 171.8112 | 0 | 50.902 | 363655.3474 | 21989.7937 | 229147.4065 | 108817.7937 | 0 | 66786.5893 | 0 | 308254.8029 | 802015.7655 | 547392.2397 | 2448059.7386 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 26917682.0187 | 62189556.4395 | 133.3521 | 0.27829 | 96724.3714 | 223468.1929 | 1971.8571 | 4555.7014
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.98829 | 0.11657 | 4 | 59652.5668 | 135295.6739 | 1216.0983 | 2758.1853 | 185.3691 | 0 | 291.9938 | 506399.1508 | 32769.285 | 324409.2912 | 143876.5862 | 0 | 72847.9967 | 0 | 421317.9008 | 1096182.7538 | 748167.2538 | 3345970.2182 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 27815592.4982 | 63087466.919 | 177.8279 | 0.46629 | 59652.5668 | 135295.6739 | 1216.0983 | 2758.1853
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4682 | 1.465 | 0.17652 | 4 | 40872.5968 | 90828.1831 | 833.2432 | 1851.6554 | 196.696 | 0 | 375.7223 | 666844.3949 | 43164.5955 | 444476.0677 | 183196.6767 | 0 | 79404.1054 | 0 | 552663.4777 | 1437917.0022 | 981407.9003 | 4389074.2206 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 28858696.5006 | 64130570.9214 | 237.1374 | 0.70606 | 40872.5968 | 90828.1831 | 833.2432 | 1851.6554
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1878 | 2.1026 | 0.25671 | 4 | 29348.8162 | 63698.7816 | 598.3153 | 1298.5858 | 206.4049 | 0 | 493.785 | 858971.6779 | 55587.7676 | 593462.1412 | 233970.4916 | 0 | 87654.2211 | 0 | 713562.0568 | 1856542.1 | 1267128.1314 | 5666878.5875 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 30136500.8675 | 65408375.2883 | 316.2278 | 1.0268 | 29348.8162 | 63698.7816 | 598.3153 | 1298.5858
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0849 | 2.9063 | 0.35845 | 4 | 22054.2167 | 46654.6988 | 449.605 | 951.1191 | 214.1322 | 0 | 72.3879 | 1078089.2225 | 69724.5305 | 768878.003 | 296751.1591 | 0 | 95521.2465 | 0 | 900496.023 | 2342905.9348 | 1599081.4424 | 7151447.5619 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 31621069.8419 | 66892944.2627 | 421.6965 | 1.4338 | 22054.2167 | 46654.6988 | 449.605 | 951.1191
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2421 | 3.9518 | 0.49115 | 4 | 17010.7587 | 34964.6232 | 346.7873 | 712.8011 | 220.4412 | 0 | 90.5109 | 1338073.6954 | 86457.3839 | 983148.546 | 377551.9399 | 0 | 104244.9687 | 0 | 1126895.8483 | 2931951.839 | 2001117.3757 | 8949441.597 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 33419063.877 | 68690938.2979 | 562.3413 | 1.9646 | 17010.7587 | 34964.6232 | 346.7873 | 712.8011
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7574 | 5.3262 | 0.66577 | 4 | 13379.9779 | 26624.8255 | 272.7689 | 542.7831 | 225.5224 | 0 | 85.5967 | 1651038.5425 | 106547.0433 | 1248306.4431 | 483304.597 | 0 | 114677.7418 | 0 | 1405511.0034 | 3656851.321 | 2495876.1674 | 11162112.8596 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 35631735.1396 | 70903609.5604 | 749.8942 | 2.6631 | 13379.9779 | 26624.8255 | 272.7689 | 542.7831
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.7453 | 7.1161 | 0.89298 | 4 | 10734.8972 | 20609.6459 | 218.8454 | 420.1555 | 229.2474 | 0 | 82.5322 | 2025278.6923 | 130501.6736 | 1573903.0899 | 622030.9567 | 0 | 127944.3521 | 0 | 1747066.9182 | 4545509.7484 | 3102403.8042 | 13874639.2354 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 38344261.5154 | 73616135.9362 | 1000 | 3.5719 | 10734.8972 | 20609.6459 | 218.8454 | 420.1555
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.371 | 9.5548 | 1.2041 | 4 | 8677.9706 | 16001.3096 | 176.9122 | 326.2083 | 233.0996 | 0 | 115.716 | 2493825.252 | 160399.4381 | 1992337.265 | 806261.9173 | 0 | 141374.9828 | 0 | 2181737.5536 | 5676433.5785 | 3874282.5564 | 17326652.5437 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 41796274.8237 | 77068149.2446 | 1333.5214 | 4.8164 | 8677.9706 | 16001.3096 | 176.9122 | 326.2083
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.8205 | 12.7236 | 1.6079 | 4 | 7157.1176 | 12641.2666 | 145.9075 | 257.7093 | 235.7169 | 0 | 107.7319 | 3053757.6022 | 196008.576 | 2505382.1519 | 1047738.0729 | 0 | 158804.95 | 0 | 2715059.6277 | 7064028.2159 | 4821344.4086 | 21562123.6053 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 46031745.8853 | 81303620.3061 | 1778.2794 | 6.4316 | 7157.1176 | 12641.2666 | 145.9075 | 257.7093
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.4032 | 16.939 | 2.1451 | 4 | 5984.4033 | 10095.1577 | 122.0002 | 205.8034 | 237.7776 | 0 | 96.3379 | 3739764.5466 | 239479.8015 | 3149890.6918 | 1368689.1581 | 0 | 180473.6812 | 0 | 3384536.1729 | 8805868.858 | 6010186.4381 | 26878889.348 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 51348511.628 | 86620386.0489 | 2371.3737 | 8.5804 | 5984.4033 | 10095.1577 | 122.0002 | 205.8034
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4468 | 22.5028 | 2.8544 | 4 | 5077.9265 | 8167.2039 | 103.5204 | 166.4995 | 239.3742 | 0 | 110.0541 | 4574185.3117 | 292154.7429 | 3953433.1482 | 1792067.783 | 0 | 206674.3828 | 0 | 4219220.9938 | 10977547.5446 | 7492401.7652 | 33507685.6722 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 57977307.9522 | 93249182.3731 | 3162.2777 | 11.4175 | 5077.9265 | 8167.2039 | 103.5204 | 166.4995
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4005 | 29.8288 | 3.7885 | 4 | 4370.7434 | 6698.2989 | 89.1035 | 136.5539 | 240.603 | 0 | 104.1402 | 5587570.253 | 355870.4057 | 4953283.4279 | 2349340.0396 | 0 | 238401.4421 | 0 | 5258941.5716 | 13682687.2121 | 9338715.1734 | 41764809.5255 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 66234431.8055 | 101506306.2263 | 4216.965 | 15.154 | 4370.7434 | 6698.2989 | 89.1035 | 136.5539
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.807 | 39.4142 | 5.0109 | 4 | 3815.2644 | 5575.0218 | 77.7793 | 113.6544 | 241.533 | 0 | 107.8342 | 6811780.4713 | 432517.5279 | 6190228.9065 | 3078503.3283 | 0 | 276686.7736 | 0 | 6547989.6329 | 17036525.8475 | 11627778.9566 | 52002011.4446 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 76471633.7246 | 111743508.1454 | 5623.4133 | 20.0436 | 3815.2644 | 5575.0218 | 77.7793 | 113.6544
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.23 | 51.7489 | 6.5838 | 4 | 3378.9133 | 4718.2524 | 68.8837 | 96.188 | 242.1601 | 0 | 122.8475 | 8268633.8099 | 523332.8714 | 7696723.969 | 4018541.8726 | 0 | 322515.231 | 0 | 8123601.6241 | 21135945.046 | 14425716.7941 | 64515011.2181 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 88984633.4982 | 124256507.919 | 7498.9421 | 26.3353 | 3378.9133 | 4718.2524 | 68.8837 | 96.188
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.158 | 67.1477 | 8.5454 | 4 | 3039.4493 | 4071.3421 | 61.9633 | 82.9998 | 242.3327 | 0 | 99.4158 | 9955356.5435 | 628013.2428 | 9480029.058 | 5201513.3567 | 0 | 378448.5816 | 0 | 10000910.7052 | 26020318.186 | 17759401.826 | 79423991.4998 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 103893613.7799 | 139165488.2007 | 10000 | 34.1817 | 3039.4493 | 4071.3421 | 61.9633 | 82.9998
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7085 | 85.3765 | 10.8608 | 4 | 2782.3781 | 3594.286 | 56.7225 | 73.2744 | 241.7759 | 0 | 137.3131 | 11816053.1144 | 742991.2518 | 11488286.7449 | 6630232.0839 | 0 | 448647.8846 | 0 | 12139222.3211 | 31583766.3825 | 21556569.5376 | 96405769.3207 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 120875391.6007 | 156147266.0216 | 13335.2143 | 43.4432 | 2782.3781 | 3594.286 | 56.7225 | 73.2744
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.4164 | 105.4692 | 13.3984 | 4 | 2595.3334 | 3253.4693 | 52.9094 | 66.3264 | 240.2669 | 0 | 117.7978 | 13741017.5587 | 861459.6357 | 13604583.3963 | 8263345.2995 | 0 | 537747.4717 | 0 | 14433179.8111 | 37552173.2163 | 25630129.8401 | 114623636.2295 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 139093258.5096 | 174365132.9304 | 17782.7941 | 53.5936 | 2595.3334 | 3253.4693 | 52.9094 | 66.3264
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.0654 | 125.864 | 15.9528 | 4 | 2465.3489 | 3018.1023 | 50.2595 | 61.5281 | 237.8705 | 0 | 125.0083 | 15591569.834 | 974940.4105 | 15671334.3833 | 10009121.7126 | 0 | 645004.421 | 0 | 16727868.5969 | 43522482.7316 | 29704988.7619 | 132847310.8518 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 157316933.1318 | 192588807.5527 | 23713.7371 | 63.8112 | 2465.3489 | 3018.1023 | 50.2595 | 61.5281
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.0869 | 145.3712 | 18.3774 | 4 | 2375.0849 | 2854.9105 | 48.4193 | 58.2012 | 235.1696 | 0 | 164.7689 | 17283928.37 | 1078404.9729 | 17586016.4255 | 11761966.145 | 0 | 759194.1384 | 0 | 18903108.9203 | 49182011.8497 | 33567733.6767 | 150122364.4987 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 174591986.7787 | 209863861.1996 | 31622.7766 | 73.5098 | 2375.0849 | 2854.9105 | 48.4193 | 58.2012
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.6185 | 162.3736 | 20.4677 | 4 | 2317.29 | 2748.1126 | 47.2411 | 56.024 | 232.2397 | 0 | 143.6389 | 18707448.3794 | 1165219.622 | 19213084.0682 | 13393232.9258 | 0 | 874477.7983 | 0 | 20807850.4895 | 54137758.6967 | 36950132.7302 | 165249204.7102 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 189718826.9902 | 224990701.411 | 42169.6503 | 81.871 | 2317.29 | 2748.1126 | 47.2411 | 56.024
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.1675 | 173.6383 | 21.8821 | 4 | 2281.9514 | 2684.9274 | 46.5207 | 54.7359 | 229.9311 | 0 | 136.7895 | 19627528.2091 | 1221233.9092 | 20272212.8518 | 14546568.2632 | 0 | 920053.6707 | 0 | 22069162.7926 | 57419434.5785 | 39189943.9512 | 175266138.2263 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 199735760.5063 | 235007634.9272 | 56234.1325 | 87.5285 | 2281.9514 | 2684.9274 | 46.5207 | 54.7359
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.9427 | 177.1499 | 22.4377 | 4 | 2256.8497 | 2649.8476 | 46.0089 | 54.0207 | 229.1195 | 0 | 149.5309 | 19910894.0703 | 1238470.3325 | 20599536.4054 | 14922812.4848 | 0 | 825807.7654 | 0 | 22424033.2128 | 58342734.6181 | 39820115.2001 | 178084404.0895 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 202554026.3695 | 237825900.7904 | 74989.4209 | 89.7508 | 2256.8497 | 2649.8476 | 46.0089 | 54.0207
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.787 | 181.7759 | 23.0737 | 4 | 2237.99 | 2620.1555 | 45.6245 | 53.4154 | 227.9989 | 0 | 166.8111 | 20281799.2179 | 1261021.2276 | 21028765.4925 | 15426303.4455 | 0 | 791320.1401 | 0 | 22927791.7142 | 59653410.9036 | 40714678.6967 | 182085090.8382 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 206554713.1182 | 241826587.5391 | 100000 | 92.2947 | 2237.99 | 2620.1555 | 45.6245 | 53.4154
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.9085 | 182.4113 | 23.2555 | 4 | 2223.2689 | 2602.446 | 45.3243 | 53.0544 | 227.8264 | 0 | 256.5282 | 20332534.7376 | 1264105.0277 | 21087547.6258 | 15498696.7734 | 0 | 689816.5857 | 0 | 22960353.2926 | 59738129.4512 | 40772500.8463 | 182343684.3402 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 206813306.6203 | 242085181.0411 | 133352.1432 | 93.0222 | 2223.2689 | 2602.446 | 45.3243 | 53.0544
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.5109 | 183.3284 | 23.4399 | 4 | 2212.2332 | 2588.4273 | 45.0994 | 52.7686 | 227.5884 | 0 | 283.0847 | 20405679.1982 | 1268550.5064 | 21172321.5655 | 15602348.3205 | 0 | 619186.438 | 0 | 23036553.5511 | 59936386.8931 | 40907815.6242 | 182948842.0969 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 207418464.3769 | 242690338.7978 | 177827.941 | 93.7598 | 2212.2332 | 2588.4273 | 45.0994 | 52.7686
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 230.4186 | 184.4136 | 23.6225 | 4 | 2203.9249 | 2577.2111 | 44.93 | 52.5399 | 227.3049 | 0 | 331.9432 | 20492103.3546 | 1273802.5062 | 21272530.3123 | 15725755.4732 | 0 | 572114.9235 | 0 | 23141159.5622 | 60208550.2764 | 41093572.7256 | 183779589.134 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 208249211.414 | 243521085.8349 | 237137.3706 | 94.4902 | 2203.9249 | 2577.2111 | 44.93 | 52.5399
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.8601 | 185.2271 | 23.7603 | 4 | 2197.6411 | 2568.7629 | 44.8019 | 52.3677 | 227.0893 | 0 | 396.6802 | 20556789.9811 | 1277733.1092 | 21347565.2979 | 15818982.4843 | 0 | 534540.9419 | 0 | 23218888.6076 | 60410785.3081 | 41231602.2903 | 184396888.0203 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 208866510.3004 | 244138384.7212 | 316227.766 | 95.0412 | 2197.6411 | 2568.7629 | 44.8019 | 52.3677
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.9855 | 185.8583 | 23.8665 | 4 | 2192.8927 | 2562.3639 | 44.7051 | 52.2373 | 226.9204 | 0 | 405.0068 | 20606926.0808 | 1280779.3288 | 21405740.1459 | 15891660.2944 | 0 | 505419.892 | 0 | 23279305.0393 | 60567976.4703 | 41338888.4884 | 184876695.7399 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 209346318.0199 | 244618192.4407 | 421696.5034 | 95.4658 | 2192.8927 | 2562.3639 | 44.7051 | 52.2373
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 233.7648 | 186.2926 | 23.942 | 4 | 2189.3084 | 2557.6136 | 44.632 | 52.1404 | 226.8027 | 0 | 865.9391 | 20641395.1191 | 1282873.5127 | 21445745.0655 | 15941896.8622 | 0 | 481772.6645 | 0 | 23319536.4574 | 60672650.3674 | 41410330.574 | 185196200.6227 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 209665822.9027 | 244937697.3236 | 562341.3252 | 95.7681 | 2189.3084 | 2557.6136 | 44.632 | 52.1404
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 234.7124 | 186.822 | 24.0221 | 4 | 2186.5346 | 2553.6127 | 44.5755 | 52.0588 | 226.6614 | 0 | 435.5166 | 20683387.2698 | 1285424.6346 | 21494491.4157 | 16003024.6019 | 0 | 467598.5716 | 0 | 23374231.3325 | 60814955.2129 | 41507456.5552 | 185630569.5941 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210100191.8741 | 245372066.2949 | 749894.2093 | 96.0882 | 2186.5346 | 2553.6127 | 44.5755 | 52.0588
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.1339 | 187.0547 | 24.0631 | 4 | 2184.5464 | 2550.9975 | 44.5349 | 52.0055 | 226.5971 | 0 | 440.1613 | 20701828.5842 | 1286544.9418 | 21515902.4022 | 16030186.2681 | 0 | 453720.1774 | 0 | 23395391.1258 | 60870008.6547 | 41545031.6605 | 185798613.8149 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210268236.0949 | 245540110.5157 | 1000000 | 96.2526 | 2184.5464 | 2550.9975 | 44.5349 | 52.0055
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.887 | 187.4742 | 24.122 | 4 | 2182.9629 | 2548.5196 | 44.5027 | 51.955 | 226.4851 | 0 | 435.9961 | 20735062.7574 | 1288563.8425 | 21554493.7681 | 16078782.6745 | 0 | 448056.6998 | 0 | 23440934.2995 | 60988502.6505 | 41625906.2474 | 186160302.9396 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210629925.2196 | 245901799.6405 | 1333521.4322 | 96.4881 | 2182.9629 | 2548.5196 | 44.5027 | 51.955
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.6797 | 187.3551 | 24.1166 | 4 | 2181.9266 | 2547.5651 | 44.4815 | 51.9356 | 226.5136 | 0 | 474.4029 | 20725632.8815 | 1287991.0081 | 21543543.1387 | 16065352.5016 | 0 | 434951.0206 | 0 | 23422413.5147 | 60940315.3676 | 41593017.4367 | 186013216.8696 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210482839.1496 | 245754713.5704 | 1778279.41 | 96.4665 | 2181.9266 | 2547.5651 | 44.4815 | 51.9356
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.8501 | 187.4487 | 24.1335 | 4 | 2181.082 | 2546.4648 | 44.4643 | 51.9131 | 226.4875 | 0 | 470.6507 | 20733044.4108 | 1288441.2351 | 21552149.8766 | 16076329.9543 | 0 | 428735.8944 | 0 | 23430693.5348 | 60961858.2813 | 41607720.9179 | 186078974.1052 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210548596.3853 | 245820470.8061 | 2371373.7057 | 96.534 | 2181.082 | 2546.4648 | 44.4643 | 51.9131
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.9692 | 187.5139 | 24.1456 | 4 | 2180.4477 | 2545.6472 | 44.4514 | 51.8965 | 226.4692 | 0 | 452.0248 | 20738213.4735 | 1288755.2366 | 21558152.7231 | 16084002.037 | 0 | 423920.8274 | 0 | 23436287.276 | 60976412.0487 | 41617654.1632 | 186123397.7856 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210593020.0656 | 245864894.4864 | 3162277.6602 | 96.5825 | 2180.4477 | 2545.6472 | 44.4514 | 51.8965
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 236.0741 | 187.5715 | 24.1557 | 4 | 2179.9715 | 2545.019 | 44.4417 | 51.8837 | 226.4531 | 0 | 454.6454 | 20742773.3584 | 1289032.231 | 21563448.2684 | 16090756.2372 | 0 | 420493.8417 | 0 | 23441536.5353 | 60990069.5446 | 41626975.6848 | 186165085.7013 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210634707.9813 | 245906582.4022 | 4216965.0343 | 96.6227 | 2179.9715 | 2545.019 | 44.4417 | 51.8837
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.005 | 186.9725 | 24.0919 | 4 | 2179.5307 | 2545.545 | 44.4327 | 51.8944 | 226.6099 | 0 | 567.5613 | 20695318.0007 | 1286149.428 | 21508343.1526 | 16021715.7476 | 0 | 401639.0423 | 0 | 23366134.4948 | 60793888.9022 | 41493078.3652 | 185566267.1333 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210035889.4133 | 245307763.8342 | 5623413.2519 | 96.3675 | 2179.5307 | 2545.545 | 44.4327 | 51.8944
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.446 | 187.2194 | 24.1217 | 4 | 2179.2489 | 2544.8113 | 44.4269 | 51.8794 | 226.5449 | 0 | 503.0407 | 20714882.012 | 1287337.9188 | 21531059.1576 | 16050187.7242 | 0 | 404744.8752 | 0 | 23395402.5583 | 60870038.3996 | 41545051.962 | 185798704.6077 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210268326.8877 | 245540201.3086 | 7498942.0933 | 96.4866 | 2179.2489 | 2544.8113 | 44.4269 | 51.8794
1 | 6000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.8649 | 187.4536 | 24.1495 | 4 | 2179.0405 | 2544.1818 | 44.4227 | 51.8666 | 226.4832 | 0 | 485.9216 | 20733432.2254 | 1288464.7935 | 21552600.241 | 16077236.6079 | 0 | 408263.1688 | 0 | 23423398.8443 | 60942878.9931 | 41594767.1637 | 186021042.0377 | 961560.8286 | 23508061.4514 | 23508061.4514 | 1478867.319 | 10284945.6504 | 0 | 210490664.3177 | 245762538.7386 | 10000000 | 96.5979 | 2179.0405 | 2544.1818 | 44.4227 | 51.8666
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1813 | 0.43662 | 0.041675 | 4 | 161240.1355 | 377514.6541 | 3287.0983 | 7696.1469 | 159.1395 | 0 | 53.681 | 265947.1075 | 14267.4802 | 170968.7145 | 84961.446 | 0 | 61539.6395 | 0 | 233096.9112 | 606470.3483 | 413928.4744 | 1851180.1218 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 26878532.3638 | 62931228.7315 | 100 | 0.1667 | 161240.1355 | 377514.6541 | 3287.0983 | 7696.1469
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5297 | 0.67698 | 0.076346 | 4 | 90362.2692 | 208418.7708 | 1842.1571 | 4248.8985 | 174.9831 | 0 | 59.8718 | 384542.1197 | 24076.0817 | 240169.9644 | 113485.2397 | 0 | 66828.2998 | 0 | 323349.6651 | 841289.5006 | 574197.3709 | 2567938.2421 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 27595290.4841 | 63647986.8518 | 133.3521 | 0.30539 | 90362.2692 | 208418.7708 | 1842.1571 | 4248.8985
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 1.068 | 0.1268 | 4 | 56283.8484 | 127363.513 | 1147.4224 | 2596.4775 | 188.8761 | 0 | 301.0149 | 534614.2476 | 34598.7224 | 345188.9014 | 149022.5527 | 0 | 73285.5699 | 0 | 443316.8977 | 1153419.6309 | 787232.5985 | 3520679.1211 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 28548031.3631 | 64600727.7308 | 177.8279 | 0.50722 | 56283.8484 | 127363.513 | 1147.4224 | 2596.4775
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 1.5742 | 0.19059 | 4 | 38869.972 | 86161.5141 | 792.417 | 1756.519 | 200.3108 | 0 | 390.5979 | 701275.0686 | 45392.8975 | 470794.6314 | 189615.0963 | 0 | 79775.7054 | 0 | 579872.8256 | 1508710.1441 | 1029725.6742 | 4605162.043 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 29632514.2851 | 65685210.6528 | 237.1374 | 0.76235 | 38869.972 | 86161.5141 | 792.417 | 1756.519
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2656 | 2.2287 | 0.27342 | 4 | 28268.94 | 61233.8929 | 576.3006 | 1248.3357 | 209.8078 | 0 | 483.2098 | 894777.3419 | 57900.0836 | 621758.2288 | 240448.4441 | 0 | 86628.7542 | 0 | 741590.0125 | 1929465.0916 | 1316899.5715 | 5889467.5282 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 30916819.7703 | 66969516.138 | 316.2278 | 1.0937 | 28268.94 | 61233.8929 | 576.3006 | 1248.3357
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1775 | 3.0677 | 0.38004 | 4 | 21339.784 | 45056.1149 | 435.0404 | 918.5298 | 217.5406 | 0 | 68.542 | 1119825.7687 | 72413.6051 | 802859.9664 | 304485.4782 | 0 | 93698.3213 | 0 | 933380.4245 | 2428464.4019 | 1657476.8543 | 7412604.8205 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 32439957.0625 | 68492653.4303 | 421.6965 | 1.5202 | 21339.784 | 45056.1149 | 435.0404 | 918.5298
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.3541 | 4.1601 | 0.51923 | 4 | 16508.6693 | 33867.3427 | 336.5516 | 690.4316 | 223.8659 | 0 | 92.4493 | 1387321.9731 | 89622.4047 | 1024387.5376 | 387021.1457 | 0 | 101375.605 | 0 | 1165994.1798 | 3033677.6775 | 2070547.3507 | 9259947.8741 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 34287300.1161 | 70339996.4839 | 562.3413 | 2.0769 | 16508.6693 | 33867.3427 | 336.5516 | 690.4316
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9011 | 5.6029 | 0.70319 | 4 | 13002.9062 | 25820.4712 | 265.0818 | 526.3852 | 228.9714 | 0 | 92.5066 | 1711033.6623 | 110392.0642 | 1299921.5901 | 495915.3304 | 0 | 110770.3693 | 0 | 1453932.8763 | 3782835.1016 | 2581862.6863 | 11546663.6806 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 36574015.9226 | 72626712.2903 | 749.8942 | 2.8128 | 13002.9062 | 25820.4712 | 265.0818 | 526.3852
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9085 | 7.4597 | 0.93994 | 4 | 10463.9638 | 20053.0272 | 213.3221 | 408.8081 | 232.6814 | 0 | 95.4704 | 2093826.9393 | 134881.911 | 1634420.6845 | 636461.6597 | 0 | 122171.3172 | 0 | 1802487.3796 | 4689702.4207 | 3200818.2659 | 14314770.578 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 39342122.8201 | 75394819.1878 | 1000 | 3.7598 | 10463.9638 | 20053.0272 | 213.3221 | 408.8081
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.6022 | 10.0334 | 1.2694 | 4 | 8454.7458 | 15555.2354 | 172.3614 | 317.1145 | 236.6104 | 0 | 93.6776 | 2581469.3437 | 165981.4186 | 2071771.5411 | 826581.4775 | 0 | 134017.4368 | 0 | 2254130.2749 | 5864784.5896 | 4002835.9916 | 17901572.0737 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 42928924.3158 | 78981620.6835 | 1333.5214 | 5.0775 | 8454.7458 | 15555.2354 | 172.3614 | 317.1145
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1178 | 13.355 | 1.6942 | 4 | 6979.3544 | 12299.2214 | 142.2836 | 250.7363 | 239.2453 | 0 | 101.7025 | 3160246.9699 | 202767.3452 | 2604355.0917 | 1074218.4517 | 0 | 149194.5887 | 0 | 2804405.1544 | 7296486.9491 | 4980002.2706 | 22271676.8212 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 47299029.0632 | 83351725.431 | 1778.2794 | 6.777 | 6979.3544 | 12299.2214 | 142.2836 | 250.7363
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.771 | 17.7575 | 2.2575 | 4 | 5843.2122 | 9835.7281 | 119.1218 | 200.5146 | 241.3143 | 0 | 108.6532 | 3866944.2724 | 247521.8842 | 3271067.0066 | 1402111.9004 | 0 | 167792.62 | 0 | 3492620.6966 | 9087082.6174 | 6202120.6073 | 27737261.6048 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 52764613.8469 | 88817310.2146 | 2371.3737 | 9.0301 | 5843.2122 | 9835.7281 | 119.1218 | 200.5146
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9265 | 23.5861 | 3.0034 | 4 | 4961.1949 | 7962.2052 | 101.1407 | 162.3203 | 242.9237 | 0 | 100.29 | 4729376.5954 | 301929.5761 | 4104960.0235 | 1835942.3304 | 0 | 190603.5121 | 0 | 4353496.6946 | 11326905.3744 | 7730845.6627 | 34574059.7692 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 59601412.0112 | 95654108.3789 | 3162.2777 | 12.0135 | 4961.1949 | 7962.2052 | 101.1407 | 162.3203
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0117 | 31.2461 | 3.9839 | 4 | 4273.5467 | 6535.946 | 87.122 | 133.2441 | 244.1603 | 0 | 101.1868 | 5774947.9206 | 367623.7752 | 5140683.3781 | 2405937.2197 | 0 | 218028.5788 | 0 | 5423816.1402 | 14111657.0192 | 9631495.8811 | 43074189.9129 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 68101542.155 | 104154238.5227 | 4216.965 | 15.9356 | 4273.5467 | 6535.946 | 87.122 | 133.2441
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.599 | 41.2761 | 5.2679 | 4 | 3732.4631 | 5443.4248 | 76.0913 | 110.9716 | 245.0953 | 0 | 93.0786 | 7039195.6593 | 446720.7366 | 6423086.0199 | 3152322.1221 | 0 | 251306.7929 | 0 | 6751926.219 | 17567127.0114 | 11989925.1536 | 53621609.7149 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 78648961.9569 | 114701658.3247 | 5623.4133 | 21.0716 | 3732.4631 | 5443.4248 | 76.0913 | 110.9716
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.2311 | 54.1561 | 6.9167 | 4 | 3307.7929 | 4610.9031 | 67.4338 | 93.9995 | 245.7148 | 0 | 108.4819 | 8540813.8594 | 540256.6239 | 7981831.9752 | 4112771.8863 | 0 | 291151.1566 | 0 | 8372061.9455 | 21782387.8363 | 14866927.2816 | 66488202.5648 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 91515554.8068 | 127568251.1746 | 7498.9421 | 27.6667 | 3307.7929 | 4610.9031 | 67.4338 | 93.9995
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.3736 | 70.1757 | 8.9651 | 4 | 2978.0403 | 3983.3974 | 60.7114 | 81.2069 | 245.8538 | 0 | 138.8594 | 10273467.3978 | 647705.4087 | 9820507.2859 | 5317690.8821 | 0 | 340446.6706 | 0 | 10295928.8816 | 26787894.9644 | 18283288.7494 | 81766930.2403 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 106794282.4824 | 142846978.8501 | 10000 | 35.8606 | 2978.0403 | 3983.3974 | 60.7114 | 81.2069
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.1311 | 89.0632 | 11.373 | 4 | 2728.809 | 3521.3171 | 55.6305 | 71.7868 | 245.23 | 0 | 125.0496 | 12178078.9748 | 765306.91 | 11883467.7487 | 6768380.4042 | 0 | 404520.8745 | 0 | 12479904.4157 | 32470151.3094 | 22161545.4635 | 99111356.1008 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 124138708.3429 | 160191404.7106 | 13335.2143 | 45.4919 | 2728.809 | 3521.3171 | 55.6305 | 71.7868
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120 | 109.7753 | 13.9978 | 4 | 2548.0162 | 3191.9141 | 51.9448 | 65.0715 | 243.6241 | 0 | 128.6018 | 14139564.8141 | 885931.842 | 14047160.2423 | 8420102.9602 | 0 | 489098.1895 | 0 | 14812924.6388 | 38540191.3614 | 26304472.5259 | 117639446.5742 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 142666798.8163 | 178719495.184 | 17782.7941 | 55.9913 | 2548.0162 | 3191.9141 | 51.9448 | 65.0715
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.722 | 130.7008 | 16.6277 | 4 | 2422.5316 | 2964.5899 | 49.3866 | 60.4372 | 241.1414 | 0 | 169.1691 | 16017664.5845 | 1001017.5027 | 16151290.6903 | 10178021.0186 | 0 | 593196.0875 | 0 | 17137064.0547 | 44587125.375 | 30431629.2423 | 136097008.5557 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 161124360.7978 | 197177057.1655 | 23713.7371 | 66.5107 | 2422.5316 | 2964.5899 | 49.3866 | 60.4372
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.6948 | 150.5879 | 19.1078 | 4 | 2335.7159 | 2807.417 | 47.6167 | 57.233 | 238.3526 | 0 | 144.1589 | 17725426.7487 | 1105350.3564 | 18089089.2514 | 11933373.1602 | 0 | 704953.3394 | 0 | 19327695.2139 | 50286698.2912 | 34321704.872 | 153494291.2333 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 178521643.4754 | 214574339.8431 | 31622.7766 | 76.4312 | 2335.7159 | 2807.417 | 47.6167 | 57.233
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.0922 | 167.838 | 21.2355 | 4 | 2280.2856 | 2704.725 | 46.4867 | 55.1395 | 235.3451 | 0 | 143.362 | 19155928.3417 | 1192532.3023 | 19728629.8949 | 13560313.1666 | 0 | 818750.8564 | 0 | 21237900.2791 | 55256660.034 | 37713805.884 | 168664520.759 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 193691873.0011 | 229744569.3688 | 42169.6503 | 84.9419 | 2280.2856 | 2704.725 | 46.4867 | 55.1395
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.4271 | 180.4454 | 22.7953 | 4 | 2246.7432 | 2642.1392 | 45.8029 | 53.8636 | 232.7161 | 0 | 147.6461 | 20175394.1445 | 1254553.0263 | 20905538.0383 | 14833741.4409 | 0 | 892998.0168 | 0 | 22644267.62 | 58915739.3693 | 40211202.7169 | 179833434.3729 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 204860786.615 | 240913482.9827 | 56234.1325 | 91.1812 | 2246.7432 | 2642.1392 | 45.8029 | 53.8636
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.2607 | 184.0285 | 23.354 | 4 | 2223.6942 | 2609.6306 | 45.333 | 53.2008 | 231.8651 | 0 | 180.6545 | 20461450.0132 | 1271939.7724 | 21236982.375 | 15214503.4056 | 0 | 803388.7894 | 0 | 23005423.0987 | 59855391.8416 | 40852534.8372 | 182701614.133 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 207728966.375 | 243781662.7427 | 74989.4209 | 93.4162 | 2223.6942 | 2609.6306 | 45.333 | 53.2008
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.7519 | 186.7218 | 23.7812 | 4 | 2206.205 | 2585.2098 | 44.9765 | 52.703 | 231.1967 | 0 | 199.4348 | 20675438.1542 | 1284941.7183 | 21485262.8818 | 15506564.9124 | 0 | 725540.8701 | 0 | 23274321.9293 | 60555011.4402 | 41330039.589 | 184837121.4954 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 209864473.7374 | 245917170.1051 | 100000 | 95.1246 | 2206.205 | 2585.2098 | 44.9765 | 52.703
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.213 | 188.7587 | 24.1077 | 4 | 2192.9456 | 2566.8164 | 44.7062 | 52.328 | 230.6739 | 0 | 256.5423 | 20836703.9613 | 1294737.7517 | 21672561.8424 | 15731155.8809 | 0 | 660213.58 | 0 | 23476195.4764 | 61080244.9997 | 41688522.2858 | 186440335.7782 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 211467688.0202 | 247520384.3879 | 133352.1432 | 96.4309 | 2192.9456 | 2566.8164 | 44.7062 | 52.328
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.807 | 190.2628 | 24.3526 | 4 | 2182.901 | 2553.0119 | 44.5014 | 52.0466 | 230.2774 | 0 | 319.4538 | 20955478.6132 | 1301951.3122 | 21810613.8047 | 15899250.4888 | 0 | 605776.5243 | 0 | 23623497.5898 | 61463494.883 | 41950098.2062 | 187610161.4221 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 212637513.6642 | 248690210.0319 | 177827.941 | 97.4105 | 2182.901 | 2553.0119 | 44.5014 | 52.0466
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 233.8829 | 191.4537 | 24.5447 | 4 | 2175.2998 | 2542.5149 | 44.3464 | 51.8326 | 229.958 | 0 | 326.2323 | 21049324.8296 | 1307650.0763 | 21919753.155 | 16033650.6766 | 0 | 563149.268 | 0 | 23740675.9221 | 61768368.8672 | 42158180.9649 | 188540753.7596 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 213568106.0017 | 249620802.3694 | 237137.3706 | 98.1787 | 2175.2998 | 2542.5149 | 44.3464 | 51.8326
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.3413 | 192.2808 | 24.6823 | 4 | 2169.5485 | 2534.7165 | 44.2292 | 51.6736 | 229.7317 | 0 | 404.2352 | 21114416.4749 | 1311602.3134 | 21995483.9854 | 16127618.4168 | 0 | 527622.6134 | 0 | 23819930.0835 | 61974571.9378 | 42298918.7977 | 189170164.623 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 214197516.8651 | 250250213.2328 | 316227.766 | 98.7291 | 2169.5485 | 2534.7165 | 44.2292 | 51.6736
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 236.4233 | 192.8906 | 24.7847 | 4 | 2165.2058 | 2528.864 | 44.1406 | 51.5543 | 229.5628 | 0 | 396.2219 | 21162345.4139 | 1314512.2452 | 22051263.5193 | 16197323.9657 | 0 | 499409.2457 | 0 | 23877693.212 | 62124859.7493 | 42401493.3171 | 189628900.668 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 214656252.9101 | 250708949.2778 | 421696.5034 | 99.139 | 2165.2058 | 2528.864 | 44.1406 | 51.5543
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 236.223 | 192.7696 | 24.7979 | 4 | 2161.859 | 2525.3238 | 44.0724 | 51.4821 | 229.589 | 0 | 539.7535 | 21152840.1583 | 1313935.163 | 22040200.2152 | 16184290.2679 | 0 | 463292.8888 | 0 | 23850277.8903 | 62053530.7059 | 42352809.7793 | 189411177.0686 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 214438529.3107 | 250491225.6784 | 562341.3252 | 99.1917 | 2161.859 | 2525.3238 | 44.0724 | 51.4821
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.1593 | 193.8652 | 24.9397 | 4 | 2159.4164 | 2520.8157 | 44.0226 | 51.3902 | 229.2927 | 0 | 459.0684 | 21238871.6941 | 1319158.0358 | 22140353.719 | 16309185.2059 | 0 | 464017.6733 | 0 | 23973918.668 | 62375218.6471 | 42572368.4092 | 190393092.0524 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215420444.2944 | 251473140.6621 | 749894.2093 | 99.7586 | 2159.4164 | 2520.8157 | 44.0226 | 51.3902
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.0109 | 193.7773 | 24.9449 | 4 | 2157.519 | 2518.8419 | 43.9839 | 51.35 | 229.3128 | 0 | 411.1983 | 21231972.8266 | 1318739.2357 | 22132320.7412 | 16299549.8457 | 0 | 442564.4435 | 0 | 23955807.3661 | 62328096.7549 | 42540206.7495 | 190249257.9632 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215276610.2052 | 251329306.5729 | 1000000 | 99.7797 | 2157.519 | 2518.8419 | 43.9839 | 51.35
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.9124 | 194.2828 | 25.0118 | 4 | 2156.2356 | 2516.5928 | 43.9578 | 51.3041 | 229.1734 | 0 | 420.8977 | 21271630.8465 | 1321146.6483 | 22178502.1412 | 16357665.9553 | 0 | 441017.0623 | 0 | 24012285.4349 | 62475041.1046 | 42640499.2876 | 190697788.4808 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215725140.7229 | 251777837.0906 | 1333521.4322 | 100.0471 | 2156.2356 | 2516.5928 | 43.9578 | 51.3041
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.1487 | 194.4134 | 25.0346 | 4 | 2155.2096 | 2515.2384 | 43.9369 | 51.2765 | 229.1359 | 0 | 442.7146 | 21281873.9998 | 1321768.4312 | 22190431.7588 | 16372877.6956 | 0 | 433369.8056 | 0 | 24024125.4595 | 62505846.4198 | 42661524.5482 | 190791818.1185 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215819170.3605 | 251871866.7282 | 1778279.41 | 100.1384 | 2155.2096 | 2515.2384 | 43.9369 | 51.2765
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 237.546 | 193.5056 | 24.9391 | 4 | 2154.3984 | 2515.8057 | 43.9203 | 51.2881 | 229.3783 | 0 | 685.6713 | 21210648.7603 | 1317444.7207 | 22107493.0342 | 16269418.2242 | 0 | 403407.5004 | 0 | 23910280.7735 | 62209645.8998 | 42459361.607 | 189887700.5202 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 214915052.7623 | 250967749.13 | 2371373.7057 | 99.7564 | 2154.3984 | 2515.8057 | 43.9203 | 51.2881
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.869 | 194.2531 | 25.028 | 4 | 2153.7732 | 2513.8975 | 43.9076 | 51.2492 | 229.1768 | 0 | 485.6154 | 21269298.5806 | 1321005.0732 | 22175785.9732 | 16354786.8865 | 0 | 414533.422 | 0 | 23998809.8748 | 62439980.4615 | 42616569.6783 | 190590769.95 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215618122.1921 | 251670818.5598 | 3162277.6602 | 100.1118 | 2153.7732 | 2513.8975 | 43.9076 | 51.2492
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.2218 | 194.451 | 25.0537 | 4 | 2153.3269 | 2513.081 | 43.8985 | 51.2326 | 229.1225 | 0 | 443.8583 | 21284816.2307 | 1321947.0298 | 22193858.526 | 16377542.5866 | 0 | 414459.5285 | 0 | 24021123.3216 | 62498035.4729 | 42656193.4165 | 190767976.1125 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215795328.3546 | 251848024.7223 | 4216965.0343 | 100.2148 | 2153.3269 | 2513.081 | 43.8985 | 51.2326
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.2996 | 194.494 | 25.0612 | 4 | 2152.9928 | 2512.6395 | 43.8917 | 51.2236 | 229.1102 | 0 | 465.6459 | 21288191.2234 | 1322151.897 | 22197789.3886 | 16382551.2295 | 0 | 411923.9804 | 0 | 24025017.0104 | 62508166.0524 | 42663107.7451 | 190798898.5268 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215826250.7688 | 251878947.1366 | 5623413.2519 | 100.2448 | 2152.9928 | 2512.6395 | 43.8917 | 51.2236
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.3675 | 194.5317 | 25.0674 | 4 | 2152.7421 | 2512.2997 | 43.8866 | 51.2166 | 229.0995 | 0 | 517.3626 | 21291141.9866 | 1322331.012 | 22201226.2069 | 16386922.776 | 0 | 410141.841 | 0 | 24028587.8908 | 62517456.7508 | 42669448.8377 | 190827257.3018 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215854609.5439 | 251907305.9116 | 7498942.0933 | 100.2696 | 2152.7421 | 2512.2997 | 43.8866 | 51.2166
1 | 6100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.4038 | 194.5517 | 25.0711 | 4 | 2152.5541 | 2512.0581 | 43.8827 | 51.2117 | 229.0937 | 0 | 538.0927 | 21292709.7038 | 1322426.1741 | 22203052.183 | 16389258.4249 | 0 | 408608.0598 | 0 | 24030261.2728 | 62521810.5474 | 42672420.3934 | 190840546.7592 | 961560.8286 | 24065791.4134 | 24065791.4134 | 1478867.319 | 10508037.6352 | 0 | 215867899.0013 | 251920595.369 | 10000000 | 100.2845 | 2152.5541 | 2512.0581 | 43.8827 | 51.2117
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2202 | 0.46963 | 0.046501 | 4 | 148088.6249 | 346156.5106 | 3018.9869 | 7056.8687 | 162.6015 | 0 | 61.7172 | 283586.5335 | 15673.2349 | 180818.8335 | 88607.4479 | 0 | 62312.0558 | 0 | 246089.2612 | 640273.7777 | 437000.0096 | 1954361.154 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 27545303.449 | 64387025.8908 | 100 | 0.18601 | 148088.6249 | 346156.5106 | 3018.9869 | 7056.8687
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5834 | 0.73511 | 0.085118 | 4 | 83183.5795 | 191390.9069 | 1695.8098 | 3901.7625 | 178.6936 | 0 | 50.1494 | 411787.4277 | 26610.7351 | 256026.7965 | 119564.9091 | 0 | 67713.2984 | 0 | 343864.2351 | 894664.2034 | 610626.7024 | 2730858.3078 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 28321800.6028 | 65163523.0445 | 133.3521 | 0.34047 | 83183.5795 | 191390.9069 | 1695.8098 | 3901.7625
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 1.132 | 0.13535 | 4 | 54015.2551 | 122062.681 | 1101.174 | 2488.4129 | 191.8901 | 0 | 307.2644 | 556799.9895 | 36036.8154 | 361634.4422 | 152684.2564 | 0 | 72466.48 | 0 | 460052.5736 | 1196962.4267 | 816951.4513 | 3653588.435 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 29244530.73 | 66086253.1718 | 177.8279 | 0.54141 | 54015.2551 | 122062.681 | 1101.174 | 2488.4129
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 1.6684 | 0.20308 | 4 | 37392.448 | 82746.3569 | 762.2956 | 1686.8964 | 203.5956 | 0 | 400.795 | 730410.8576 | 47277.8426 | 493202.7566 | 194612.1222 | 0 | 78947.0067 | 0 | 602335.7284 | 1567154.0093 | 1069614.8131 | 4783555.1366 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 30374497.4315 | 67216219.8733 | 237.1374 | 0.81232 | 37392.448 | 82746.3569 | 762.2956 | 1686.8964
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3434 | 2.3579 | 0.29058 | 4 | 27276.9732 | 58973.5572 | 556.078 | 1202.2557 | 213.2037 | 0 | 491.9345 | 930881.6416 | 60230.7807 | 650443.1066 | 246903.8794 | 0 | 85469.1486 | 0 | 769832.1372 | 2002945.3067 | 1367051.3282 | 6113757.329 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 31704699.6239 | 68546422.0657 | 316.2278 | 1.1623 | 27276.9732 | 58973.5572 | 556.078 | 1202.2557
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 3.231 | 0.40202 | 4 | 20684.593 | 43595.2085 | 421.6834 | 888.7473 | 220.9252 | 0 | 85.3707 | 1161375.4396 | 75089.5257 | 836855.1786 | 312043.7945 | 0 | 91409.2443 | 0 | 965941.5413 | 2513181.7486 | 1715298.1841 | 7671194.6568 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 33262136.9517 | 70103859.3935 | 421.6965 | 1.6081 | 20684.593 | 43595.2085 | 421.6834 | 888.7473
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.481 | 4.3882 | 0.54989 | 4 | 15997.9878 | 32747.6799 | 326.1406 | 667.6057 | 227.3456 | 0 | 77.248 | 1440453.2484 | 93035.3836 | 1069090.9194 | 397598.9898 | 0 | 98493.0308 | 0 | 1208481.9131 | 3144222.0441 | 2145996.1524 | 9597371.6816 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 35188313.9766 | 72030036.4183 | 562.3413 | 2.1995 | 15997.9878 | 32747.6799 | 326.1406 | 667.6057
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0474 | 5.8884 | 0.74195 | 4 | 12644.4896 | 25058.2833 | 257.775 | 510.847 | 232.4169 | 0 | 80.3274 | 1772039.7059 | 114299.9404 | 1352644.3219 | 508326.6509 | 0 | 106245.6029 | 0 | 1502886.9266 | 3910203.4985 | 2668794.2343 | 11935440.8814 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 37526383.1764 | 74368105.6181 | 749.8942 | 2.9678 | 12644.4896 | 25058.2833 | 257.775 | 510.847
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.0937 | 7.8392 | 0.99168 | 4 | 10181.5446 | 19469.2284 | 207.5646 | 396.9066 | 236.2207 | 0 | 92.7809 | 2168460.091 | 139648.484 | 1700595.4389 | 652684.3886 | 0 | 115903.2736 | 0 | 1863143.7537 | 4847517.8637 | 3308530.5485 | 14796483.842 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 40387426.137 | 77229148.5788 | 1000 | 3.9667 | 10181.5446 | 19469.2284 | 207.5646 | 396.9066
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.8191 | 10.5127 | 1.3353 | 4 | 8248.5002 | 15146.3989 | 168.1568 | 308.7798 | 240.0986 | 0 | 98.0054 | 2668051.06 | 171492.6495 | 2150574.4317 | 846207.7563 | 0 | 125197.9568 | 0 | 2324994.3032 | 6049158.2549 | 4128674.8068 | 18464351.2192 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 44055293.5141 | 80897015.9559 | 1333.5214 | 5.341 | 8248.5002 | 15146.3989 | 168.1568 | 308.7798
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4079 | 13.9988 | 1.7828 | 4 | 6811.2373 | 11977.5897 | 138.8563 | 244.1794 | 242.7601 | 0 | 99.1606 | 3267344.4604 | 209560.6158 | 2704309.3545 | 1100555.999 | 0 | 137900.5597 | 0 | 2893671.6858 | 7528740.1529 | 5138519.8545 | 22980602.6825 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 48571544.9774 | 85413267.4192 | 1778.2794 | 7.1311 | 6811.2373 | 11977.5897 | 138.8563 | 244.1794
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1601 | 18.6217 | 2.3764 | 4 | 5704.2676 | 9580.0657 | 116.2892 | 195.3026 | 244.8483 | 0 | 106.9563 | 3999431.7968 | 255894.2465 | 3397818.7245 | 1437543.6069 | 0 | 153452.4226 | 0 | 3605214.911 | 9380029.667 | 6402062.9881 | 28631448.3634 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 54222390.6584 | 91064113.1002 | 2371.3737 | 9.5056 | 5704.2676 | 9580.0657 | 116.2892 | 195.3026
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.4212 | 24.7178 | 3.1595 | 4 | 4847.473 | 7762.6549 | 98.8223 | 158.2522 | 246.4658 | 0 | 96.2785 | 4889357.6374 | 311999.309 | 4261792.8053 | 1881629.0345 | 0 | 172148.9623 | 0 | 4491601.8219 | 11686226.5864 | 7976089.7732 | 35670845.93 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 61261788.225 | 98103510.6668 | 3162.2777 | 12.6379 | 4847.473 | 7762.6549 | 98.8223 | 158.2522
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.6574 | 32.7412 | 4.1904 | 4 | 4177.9086 | 6375.9147 | 85.1723 | 129.9816 | 247.7106 | 0 | 103.3955 | 5970020.1715 | 379851.1398 | 5336551.1544 | 2465952.2405 | 0 | 194779.8742 | 0 | 5595390.2864 | 14558057.7528 | 9936173.5545 | 44436776.1741 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 70027718.4691 | 106869440.9109 | 4216.965 | 16.7614 | 4177.9086 | 6375.9147 | 85.1723 | 129.9816
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.4079 | 43.2131 | 5.5361 | 4 | 3651.9372 | 5315.6404 | 74.4497 | 108.3665 | 248.6472 | 0 | 110.4984 | 7272709.9681 | 461294.1397 | 6663114.1291 | 3228726.9234 | 0 | 221917.7421 | 0 | 6960627.5319 | 18110125.017 | 12360532.45 | 55279047.9012 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 80869990.1962 | 117711712.6379 | 5623.4133 | 22.1444 | 3651.9372 | 5315.6404 | 74.4497 | 108.3665
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.24 | 56.6458 | 7.2622 | 4 | 3238.8665 | 4507.1375 | 66.0287 | 91.8841 | 249.2565 | 0 | 96.802 | 8818752.6585 | 557525.3559 | 8274069.781 | 4209456.8256 | 0 | 254681.9782 | 0 | 8624649.7737 | 22439569.5522 | 15315467.3064 | 68494173.2315 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 94085115.5264 | 130926837.9682 | 7498.9421 | 29.0488 | 3238.8665 | 4507.1375 | 66.0287 | 91.8841
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6259 | 73.3289 | 9.4034 | 4 | 2918.1537 | 3897.635 | 59.4905 | 79.4586 | 249.3589 | 0 | 111.5397 | 10600645.7643 | 667943.297 | 10171965.1116 | 5438750.58 | 0 | 296721.1383 | 0 | 10598650.0976 | 27575513.4718 | 18820854.5646 | 84171044.0252 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 109761986.3202 | 146603708.762 | 10000 | 37.6135 | 2918.1537 | 3897.635 | 59.4905 | 79.4586
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.6005 | 92.8948 | 11.9066 | 4 | 2676.6025 | 3450.1616 | 54.5662 | 70.3362 | 248.6634 | 0 | 121.9563 | 12549894.0336 | 788208.4472 | 12290738.8824 | 6912410.2214 | 0 | 354216.8973 | 0 | 12829232.708 | 33379031.8686 | 22781875.1209 | 101885608.1794 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 127476550.4743 | 164318272.9161 | 13335.2143 | 47.6263 | 2676.6025 | 3450.1616 | 54.5662 | 70.3362
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.617 | 114.2167 | 14.6178 | 4 | 2502.0789 | 3132.1618 | 51.0083 | 63.8534 | 246.9575 | 0 | 115.0074 | 14546045.7057 | 910872.6111 | 14500011.4403 | 8581756.5296 | 0 | 434127.3726 | 0 | 15199397.3271 | 39545714.0201 | 26990762.4019 | 120708687.4084 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 146299629.7034 | 183141352.1452 | 17782.7941 | 58.4712 | 2502.0789 | 3132.1618 | 51.0083 | 63.8534
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.3958 | 135.6561 | 17.3214 | 4 | 2381.0646 | 2912.8031 | 48.5412 | 59.3814 | 244.3897 | 0 | 141.7028 | 16449638.4137 | 1027435.4218 | 16639344.7562 | 10350258.8152 | 0 | 535157.5829 | 0 | 17550715.646 | 45663361.9642 | 31166182.8288 | 139382095.4289 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 164973037.7238 | 201814760.1656 | 23713.7371 | 69.2854 | 2381.0646 | 2912.8031 | 48.5412 | 59.3814
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.3273 | 155.9196 | 19.8565 | 4 | 2297.6467 | 2761.4966 | 46.8406 | 56.2968 | 241.5113 | 0 | 159.4263 | 18172253.6172 | 1132602.2914 | 18599670.4949 | 12108819.8624 | 0 | 645034.795 | 0 | 19756768.6138 | 51403059.2625 | 35083644.1739 | 156901853.1111 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 182492795.4061 | 219334517.8479 | 31622.7766 | 79.426 | 2297.6467 | 2761.4966 | 46.8406 | 56.2968
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.6005 | 173.4097 | 22.0204 | 4 | 2244.5696 | 2662.8386 | 45.7586 | 54.2856 | 238.4247 | 0 | 150.8766 | 19609021.1804 | 1220107.9339 | 20250853.1838 | 13731872.8869 | 0 | 757994.3437 | 0 | 21672241.3162 | 56386726.3168 | 38485099.3426 | 172113916.5044 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 197704858.7994 | 234546581.2412 | 42169.6503 | 88.0814 | 2244.5696 | 2662.8386 | 45.7586 | 54.2856
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.6844 | 187.3559 | 23.7274 | 4 | 2212.6577 | 2600.8348 | 45.108 | 53.0215 | 235.4635 | 0 | 166.564 | 20725699.6118 | 1287995.0618 | 21543620.6286 | 15122646.9516 | 0 | 860356.5667 | 0 | 23220724.34 | 60415561.5071 | 41234862.1442 | 184411466.8117 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 210002409.1067 | 246844131.5485 | 56234.1325 | 94.9096 | 2212.6577 | 2600.8348 | 45.108 | 53.0215
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 224.4861 | 190.9503 | 24.282 | 4 | 2191.6153 | 2570.9266 | 44.679 | 52.4118 | 234.5853 | 0 | 166.5521 | 21009678.6638 | 1305242.6703 | 21873639.6368 | 15501957.2011 | 0 | 774698.4408 | 0 | 23581434.479 | 61354055.2969 | 41875403.4399 | 187276109.8285 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 212867052.1235 | 249708774.5653 | 74989.4209 | 97.1279 | 2191.6153 | 2570.9266 | 44.679 | 52.4118
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.0823 | 193.7295 | 24.7137 | 4 | 2175.6779 | 2548.3629 | 44.3541 | 51.9518 | 233.8763 | 0 | 116.7528 | 21228226.2798 | 1318511.7976 | 22127958.4186 | 15801525.1028 | 0 | 702300.9511 | 0 | 23859623.7945 | 62077846.8315 | 42369406.0347 | 189485399.2107 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 215076341.5056 | 251918063.9474 | 100000 | 98.8549 | 2175.6779 | 2548.3629 | 44.3541 | 51.9518
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.5628 | 195.7909 | 25.0391 | 4 | 2163.6026 | 2531.445 | 44.108 | 51.6069 | 233.3311 | 0 | 152.3102 | 21389764.8439 | 1328317.1413 | 22316124.8878 | 16027285.6522 | 0 | 640717.9249 | 0 | 24063862.0755 | 62609232.9437 | 42732087.9752 | 191107393.4446 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 216698335.7395 | 253540058.1813 | 133352.1432 | 100.1563 | 2163.6026 | 2531.445 | 44.108 | 51.6069
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.2371 | 197.3511 | 25.287 | 4 | 2154.4647 | 2518.7006 | 43.9217 | 51.3471 | 232.9076 | 0 | 170.3028 | 21511709.4547 | 1335717.7583 | 22458275.7208 | 16200546.077 | 0 | 590305.6428 | 0 | 24217656.3149 | 63009374.0069 | 43005192.4729 | 192328777.4482 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 217919719.7432 | 254761442.185 | 177827.941 | 101.148 | 2154.4647 | 2518.7006 | 43.9217 | 51.3471
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 237.2056 | 198.4849 | 25.4703 | 4 | 2147.5526 | 2509.1677 | 43.7808 | 51.1528 | 232.5929 | 0 | 174.4493 | 21600153.0685 | 1341084.5133 | 22561430.6305 | 16327728.1266 | 0 | 548728.6275 | 0 | 24327858.7369 | 63296098.1034 | 43200887.5603 | 193203969.367 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 218794911.6619 | 255636634.1037 | 237137.3706 | 101.881 | 2147.5526 | 2509.1677 | 43.7808 | 51.1528
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.6935 | 199.3344 | 25.6084 | 4 | 2142.3312 | 2501.9958 | 43.6743 | 51.0066 | 232.3537 | 0 | 211.7479 | 21666332.4876 | 1345099.8714 | 22638648.7997 | 16423836.0891 | 0 | 515614.3933 | 0 | 24409917.34 | 63509597.7562 | 43346605.4603 | 193855652.1975 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 219446594.4925 | 256288316.9342 | 316227.766 | 102.4336 | 2142.3312 | 2501.9958 | 43.6743 | 51.0066
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.7996 | 199.9616 | 25.7113 | 4 | 2138.391 | 2496.616 | 43.594 | 50.8969 | 232.1749 | 0 | 231.5862 | 21715140.2688 | 1348061.0034 | 22695614.5656 | 16495265.9078 | 0 | 489347.6628 | 0 | 24469937.4693 | 63665757.8208 | 43453187.9132 | 194332312.6119 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 219923254.9068 | 256764977.3486 | 421696.5034 | 102.8452 | 2138.391 | 2496.616 | 43.594 | 50.8969
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 241.0272 | 200.6579 | 25.8146 | 4 | 2135.3498 | 2492.1414 | 43.532 | 50.8057 | 231.9784 | 0 | 302.9654 | 21769276.4132 | 1351345.1831 | 22758815.976 | 16574562.4053 | 0 | 473288.0834 | 0 | 24541642.3438 | 63852319.1956 | 43580519.8849 | 194901769.4854 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 220492711.7804 | 257334434.2222 | 562341.3252 | 103.2584 | 2135.3498 | 2492.1414 | 43.532 | 50.8057
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 241.2 | 200.7498 | 25.8431 | 4 | 2133.1643 | 2489.5617 | 43.4874 | 50.7531 | 231.9473 | 0 | 310.067 | 21776420.3865 | 1351778.5563 | 22767157.5374 | 16585599.7888 | 0 | 452136.1705 | 0 | 24543906.0514 | 63858208.8984 | 43584539.7282 | 194919747.1176 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 220510689.4125 | 257352411.8543 | 749894.2093 | 103.3726 | 2133.1643 | 2489.5617 | 43.4874 | 50.7531
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.077 | 201.2438 | 25.9123 | 4 | 2131.5151 | 2486.9607 | 43.4538 | 50.7001 | 231.8065 | 0 | 337.7627 | 21814793.0854 | 1354106.2819 | 22811968.0964 | 16642062.4021 | 0 | 445625.5518 | 0 | 24596736.6128 | 63995663.1821 | 43678355.1012 | 195339310.3137 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 220930252.6086 | 257771975.0504 | 1000000 | 103.6494 | 2131.5151 | 2486.9607 | 43.4538 | 50.7001
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.413 | 201.4306 | 25.9437 | 4 | 2130.2775 | 2485.294 | 43.4286 | 50.6661 | 231.7513 | 0 | 364.0581 | 21829297.5563 | 1354986.1071 | 22828908.2952 | 16663663.9345 | 0 | 436440.7241 | 0 | 24614185.6807 | 64041062.0775 | 43709340.7801 | 195477885.1556 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221068827.4506 | 257910549.8924 | 1333521.4322 | 103.7747 | 2130.2775 | 2485.294 | 43.4286 | 50.6661
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 241.305 | 200.7989 | 25.8807 | 4 | 2129.2945 | 2485.1749 | 43.4085 | 50.6637 | 231.9244 | 0 | 584.9168 | 21780237.3238 | 1352010.1007 | 22771614.4561 | 16592198.692 | 0 | 411118.199 | 0 | 24533799.7209 | 63831914.2995 | 43566593.1241 | 194839485.9161 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 220430428.211 | 257272150.6528 | 1778279.41 | 103.5228 | 2129.2945 | 2485.1749 | 43.4085 | 50.6637
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.5445 | 201.5011 | 25.9658 | 4 | 2128.5615 | 2483.2751 | 43.3936 | 50.6249 | 231.7282 | 0 | 443.8087 | 21834766.4138 | 1355317.8376 | 22835295.8602 | 16672077.5861 | 0 | 419251.5254 | 0 | 24615516.597 | 64044524.8487 | 43711704.1926 | 195488454.8615 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221079397.1564 | 257921119.5982 | 2371373.7057 | 103.8633 | 2128.5615 | 2483.2751 | 43.3936 | 50.6249
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.6862 | 201.5798 | 25.9791 | 4 | 2128.0242 | 2482.5559 | 43.3827 | 50.6103 | 231.705 | 0 | 425.6251 | 21840878.8674 | 1355688.6047 | 22842435.3489 | 16681188.6473 | 0 | 415113.4915 | 0 | 24622768.9343 | 64063393.9428 | 43724582.737 | 195546050.574 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221136992.869 | 257978715.3108 | 3162277.6602 | 103.9166 | 2128.0242 | 2482.5559 | 43.3827 | 50.6103
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.7808 | 201.6323 | 25.9884 | 4 | 2127.6209 | 2482.0264 | 43.3744 | 50.5995 | 231.6894 | 0 | 453.1681 | 21844949.1105 | 1355935.4945 | 22847189.6113 | 16687272.0298 | 0 | 411839.8576 | 0 | 24627402.5804 | 64075449.7394 | 43732811.0659 | 195582849.4894 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221173791.7843 | 258015514.2261 | 4216965.0343 | 103.9536 | 2127.6209 | 2482.0264 | 43.3744 | 50.5995
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.8681 | 201.6808 | 25.9964 | 4 | 2127.3183 | 2481.6151 | 43.3683 | 50.5911 | 231.6751 | 0 | 516.1336 | 21848716.3263 | 1356164.0023 | 22851590.0095 | 16692887.9225 | 0 | 409586.5689 | 0 | 24631988.4835 | 64087381.3184 | 43740954.6138 | 195619269.2451 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221210211.5401 | 258051933.9819 | 5623413.2519 | 103.9855 | 2127.3183 | 2481.6151 | 43.3683 | 50.5911
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.9265 | 201.7132 | 26.0019 | 4 | 2127.0912 | 2481.3126 | 43.3636 | 50.5849 | 231.6655 | 0 | 524.1059 | 21851227.6068 | 1356316.3283 | 22854523.4254 | 16696639.1382 | 0 | 407797.724 | 0 | 24634936.6469 | 64095051.8349 | 43746189.8989 | 195642682.6034 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221233624.8984 | 258075347.3402 | 7498942.0933 | 104.0076 | 2127.0912 | 2481.3126 | 43.3636 | 50.5849
1 | 6200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.9607 | 201.7321 | 26.0054 | 4 | 2126.9208 | 2481.094 | 43.3602 | 50.5805 | 231.6598 | 0 | 503.9443 | 21852694.2209 | 1356405.288 | 22856236.5883 | 16698840.6298 | 0 | 406329.1817 | 0 | 24636497.3044 | 64099112.3456 | 43748961.2809 | 195655076.8397 | 961560.8286 | 24629381.4663 | 24629381.4663 | 1478867.319 | 10733473.6564 | 0 | 221246019.1346 | 258087741.5764 | 10000000 | 104.0217 | 2126.9208 | 2481.094 | 43.3602 | 50.5805
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2545 | 0.50043 | 0.05121 | 4 | 137709.145 | 321457.6481 | 2807.3872 | 6553.349 | 165.8001 | 0 | 47.0781 | 299987.3649 | 17045.098 | 189853.7252 | 91645.8099 | 0 | 62660.49 | 0 | 257865.0704 | 670912.0177 | 457911.2379 | 2047880.8141 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 28208273.2528 | 65847225.8958 | 100 | 0.20484 | 137709.145 | 321457.6481 | 2807.3872 | 6553.349
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.78277 | 0.091539 | 4 | 79205.8748 | 182000.9245 | 1614.7189 | 3710.335 | 181.492 | 0 | 240.223 | 430341.4358 | 27834.9622 | 269210.3574 | 122943.0841 | 0 | 67017.9231 | 0 | 357765.6274 | 930832.7748 | 635312.4955 | 2841258.6603 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 29001651.099 | 66640603.7421 | 133.3521 | 0.36616 | 79205.8748 | 182000.9245 | 1614.7189 | 3710.335
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 1.2152 | 0.14612 | 4 | 51307.2512 | 115703.7893 | 1045.9677 | 2358.7782 | 195.3784 | 0 | 310.266 | 585092.2212 | 37870.21 | 382736.4754 | 157668.3554 | 0 | 72579.1526 | 0 | 482019.1017 | 1254114.827 | 855959.1389 | 3828039.4823 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 29988431.9211 | 67627384.5641 | 177.8279 | 0.58449 | 51307.2512 | 115703.7893 | 1045.9677 | 2358.7782
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6822 | 1.7832 | 0.21802 | 4 | 35732.5201 | 78892.4227 | 728.4558 | 1608.3287 | 207.1838 | 0 | 407.8651 | 765264.0936 | 49531.8652 | 520166.1695 | 200943.6437 | 0 | 78840.0511 | 0 | 629750.871 | 1638482.5866 | 1118298.0328 | 5001277.3133 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 31161669.7521 | 68800622.3951 | 237.1374 | 0.87208 | 35732.5201 | 78892.4227 | 728.4558 | 1608.3287
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4212 | 2.4906 | 0.30831 | 4 | 26353.5821 | 56874.3862 | 537.2534 | 1159.4613 | 216.5929 | 0 | 500.2178 | 967341.943 | 62583.5487 | 679560.9155 | 253374.1992 | 0 | 83935.5688 | 0 | 798250.5083 | 2076884.079 | 1417516.0596 | 6339446.822 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 32499839.2608 | 70138791.9038 | 316.2278 | 1.2332 | 26353.5821 | 56874.3862 | 537.2534 | 1159.4613
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3795 | 3.4201 | 0.42721 | 4 | 19973.1241 | 41999.0857 | 407.1791 | 856.2082 | 224.4485 | 0 | 86.2194 | 1208755.6005 | 78139.6123 | 875815.1812 | 321211.9853 | 0 | 89512.0636 | 0 | 1003639.4327 | 2611263.9292 | 1782241.2878 | 7970579.0926 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 34130971.5314 | 71769924.1744 | 421.6965 | 1.7088 | 19973.1241 | 41999.0857 | 407.1791 | 856.2082
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5905 | 4.6065 | 0.57962 | 4 | 15558.3565 | 31792.7655 | 317.1781 | 648.1385 | 230.7447 | 0 | 95.2605 | 1490546.9439 | 96251.7544 | 1111434.2753 | 407213.0787 | 0 | 94535.4489 | 0 | 1247992.7855 | 3247021.2293 | 2216158.7086 | 9911154.2246 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 36071546.6633 | 73710499.3064 | 562.3413 | 2.3185 | 15558.3565 | 31792.7655 | 317.1781 | 648.1385
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.1984 | 6.1873 | 0.78262 | 4 | 12297.6101 | 24321.0641 | 250.7034 | 495.8178 | 235.8629 | 0 | 88.2576 | 1834989.7661 | 118330.3405 | 1407290.4477 | 521387.552 | 0 | 101141.9808 | 0 | 1553424.634 | 4041692.2464 | 2758538.0066 | 12336794.974 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 38497187.4127 | 76136140.0558 | 749.8942 | 3.1305 | 12297.6101 | 24321.0641 | 250.7034 | 495.8178
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2984 | 8.2624 | 1.0495 | 4 | 9882.6112 | 18848.741 | 201.4704 | 384.2571 | 239.9753 | 0 | 87.2048 | 2250484.3097 | 144884.1687 | 1773655.4075 | 670737.2079 | 0 | 108448.7281 | 0 | 1929801.8305 | 5020948.5063 | 3426900.5257 | 15325860.6844 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 41486253.1231 | 79125205.7661 | 1000 | 4.1979 | 9882.6112 | 18848.741 | 201.4704 | 384.2571
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.0775 | 11.0478 | 1.4084 | 4 | 8032.0214 | 14712.9555 | 163.7436 | 299.9435 | 243.6174 | 0 | 82.3412 | 2763392.9886 | 177558.0262 | 2237719.6543 | 869090.1672 | 0 | 115860.0016 | 0 | 2403812.1268 | 6254226.0643 | 4268637.8004 | 19090296.8296 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 45250689.2683 | 82889641.9114 | 1333.5214 | 5.6338 | 8032.0214 | 14712.9555 | 163.7436 | 299.9435
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.722 | 14.6868 | 1.8774 | 4 | 6643.4569 | 11655.5812 | 135.4359 | 237.6148 | 246.2787 | 0 | 121.9362 | 3380252.5853 | 216718.113 | 2810124.5191 | 1129061.5057 | 0 | 125206.0109 | 0 | 2987931.4662 | 7773984.7662 | 5305904.3423 | 23729183.3087 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 49889575.7474 | 87528528.3905 | 1778.2794 | 7.5096 | 6643.4569 | 11655.5812 | 135.4359 | 237.6148
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.5576 | 19.5222 | 2.5007 | 4 | 5569.2921 | 9332.2045 | 113.5376 | 190.2496 | 248.3746 | 0 | 99.7741 | 4135623.5737 | 264495.1336 | 3528648.4536 | 1474214.1756 | 0 | 136784.527 | 0 | 3720508.6867 | 9680000.4216 | 6606799.1919 | 29547074.1637 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 55707466.6025 | 93346419.2455 | 2371.3737 | 10.0026 | 5569.2921 | 9332.2045 | 113.5376 | 190.2496
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.9205 | 25.8909 | 3.3219 | 4 | 4737.3551 | 7570.0343 | 96.5774 | 154.3254 | 249.9979 | 0 | 112.3362 | 5052999.2958 | 322292.497 | 4422854.8781 | 1928530.521 | 0 | 150541.3392 | 0 | 4632115.2271 | 12051813.6434 | 8225610.4516 | 36786757.8532 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 62947150.2919 | 100586102.935 | 3162.2777 | 13.2874 | 4737.3551 | 7570.0343 | 96.5774 | 154.3254
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.2958 | 34.2785 | 4.4036 | 4 | 4085.8553 | 6222.6915 | 83.2957 | 126.858 | 251.2489 | 0 | 105.2804 | 6167960.5586 | 392249.4835 | 5536079.6501 | 2526745.5198 | 0 | 167241.8654 | 0 | 5768208.0602 | 15007694.1505 | 10243059.635 | 45809238.9231 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 71969631.3618 | 109608584.0048 | 4216.965 | 17.6143 | 4085.8553 | 6222.6915 | 83.2957 | 126.858
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2432 | 45.2398 | 5.8174 | 4 | 3573.0588 | 5190.5645 | 72.8416 | 105.8167 | 252.1887 | 0 | 106.268 | 7513868.8619 | 476333.5131 | 6911955.1269 | 3308594.967 | 0 | 187414.6526 | 0 | 7175285.1774 | 18668620.1782 | 12741716.8734 | 56983789.3504 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 83144181.7891 | 120783134.4322 | 5623.4133 | 23.2697 | 3573.0588 | 5190.5645 | 72.8416 | 105.8167
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3018 | 59.2673 | 7.6266 | 4 | 3170.9244 | 4404.7228 | 64.6436 | 89.7962 | 252.7861 | 0 | 105.0803 | 9107676.893 | 575462.9605 | 8578998.8615 | 4311754.3113 | 0 | 211978.5109 | 0 | 8886489.8995 | 23120823.8487 | 15780437.3622 | 70573622.6476 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 96734015.0863 | 134372967.7294 | 7498.9421 | 30.5066 | 3170.9244 | 4404.7228 | 64.6436 | 89.7962
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.917 | 76.6168 | 9.8615 | 4 | 2859.5096 | 3813.6988 | 58.295 | 77.7474 | 252.8474 | 0 | 90.4927 | 10937588.571 | 688769.0655 | 10535223.7104 | 5564884.4621 | 0 | 245359.3025 | 0 | 10909011.7935 | 28383010.9407 | 19371988.1796 | 86635836.0252 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 112796228.464 | 150435181.107 | 10000 | 39.446 | 2859.5096 | 3813.6988 | 58.295 | 77.7474
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.1131 | 96.8772 | 12.4625 | 4 | 2625.5664 | 3380.6082 | 53.5257 | 68.9183 | 252.0753 | 0 | 130.4641 | 12931778.1082 | 811712.1265 | 12710479.4894 | 7062371.1475 | 0 | 295713.0167 | 0 | 13186701.0165 | 34309091.0805 | 23416659.6438 | 104724505.6291 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 130884898.0678 | 168523850.7109 | 13335.2143 | 49.8502 | 2625.5664 | 3380.6082 | 53.5257 | 68.9183
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.2884 | 118.8196 | 15.2618 | 4 | 2457.2477 | 3073.8037 | 50.0943 | 62.6636 | 250.2642 | 0 | 136.6139 | 14962654.62 | 936415.7872 | 14965640.1152 | 8750137.1591 | 0 | 371364.6437 | 0 | 15594622.8068 | 40574009.6464 | 27692595.2962 | 123847440.0747 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 150007832.5135 | 187646785.1565 | 17782.7941 | 61.0471 | 2457.2477 | 3073.8037 | 50.0943 | 62.6636
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1326 | 140.7762 | 18.0395 | 4 | 2340.6766 | 2862.2943 | 47.7179 | 58.3517 | 247.61 | 0 | 148.4139 | 16891347.7786 | 1054429.4138 | 17139896.4918 | 10529749.7653 | 0 | 470064.1189 | 0 | 17973340.1517 | 46762944.2357 | 31916670.3232 | 142738442.279 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 168898834.7177 | 206537787.3608 | 23713.7371 | 72.1581 | 2340.6766 | 2862.2943 | 47.7179 | 58.3517
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.9863 | 161.3737 | 20.6246 | 4 | 2260.7283 | 2716.9672 | 46.088 | 55.3891 | 244.6447 | 0 | 151.8528 | 18624929.3748 | 1160192.2119 | 19118375.0089 | 12288469.0599 | 0 | 578388.2374 | 0 | 20190438.0182 | 52531378.0951 | 35853744.9618 | 160345914.9679 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 186506307.4066 | 224145260.0497 | 31622.7766 | 82.4983 | 2260.7283 | 2716.9672 | 46.088 | 55.3891
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.1474 | 179.0978 | 22.8237 | 4 | 2209.9959 | 2622.2754 | 45.0538 | 53.4586 | 241.4772 | 0 | 140.1033 | 20067397.7162 | 1247987.1141 | 20780541.8646 | 13908275.8022 | 0 | 691387.0707 | 0 | 22111279.9314 | 57529014.7344 | 39264734.6592 | 175600618.8928 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 201761011.3315 | 239399963.9745 | 42169.6503 | 91.2947 | 2209.9959 | 2622.2754 | 45.0538 | 53.4586
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.399 | 193.3824 | 24.5733 | 4 | 2179.6415 | 2562.5661 | 44.4349 | 52.2414 | 238.4024 | 0 | 149.0927 | 21200980.6942 | 1316857.7916 | 22096237.3772 | 15312885.3148 | 0 | 799067.1877 | 0 | 23683151.0626 | 61618700.9825 | 42056029.5582 | 188083909.9688 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 214244302.4075 | 251883255.0506 | 56234.1325 | 98.2934 | 2179.6415 | 2562.5661 | 44.4349 | 52.2414
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.8165 | 198.0374 | 25.235 | 4 | 2160.4971 | 2533.3811 | 44.0447 | 51.6464 | 237.2506 | 0 | 179.4514 | 21565263.8191 | 1338967.5094 | 22520732.4392 | 15797951.353 | 0 | 741799.0043 | 0 | 24166238.5087 | 62875595.4226 | 42913885.8402 | 191920433.8965 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 218080826.3353 | 255719778.9783 | 74989.4209 | 100.9401 | 2160.4971 | 2533.3811 | 44.0447 | 51.6464
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.364 | 200.8017 | 25.6598 | 4 | 2146.0653 | 2512.7769 | 43.7504 | 51.2264 | 236.5233 | 0 | 205.3686 | 21780449.7449 | 1352022.9866 | 22771862.4962 | 16094060.1987 | 0 | 673214.7556 | 0 | 24441927.971 | 63592882.8517 | 43403449.2493 | 194109870.254 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 220270262.6927 | 257909215.3358 | 100000 | 102.6391 | 2146.0653 | 2512.7769 | 43.7504 | 51.2264
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.9151 | 202.9175 | 25.9867 | 4 | 2135.157 | 2497.2555 | 43.5281 | 50.9099 | 235.9473 | 0 | 187.601 | 21944603.33 | 1361979.8398 | 22963621.7987 | 16324861.9775 | 0 | 616476.5863 | 0 | 24652501.9776 | 64140753.2222 | 43777382.0348 | 195782180.767 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 221942573.2057 | 259581525.8487 | 133352.1432 | 103.9467 | 2135.157 | 2497.2555 | 43.5281 | 50.9099
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.548 | 204.4599 | 26.2291 | 4 | 2126.9098 | 2485.662 | 43.3599 | 50.6736 | 235.515 | 0 | 272.9457 | 22063962.1469 | 1369218.3078 | 23103153.5015 | 16495425.0061 | 0 | 568815.1333 | 0 | 24804223.8973 | 64535502.5349 | 44046806.552 | 196987107.08 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 223147499.5187 | 260786452.1618 | 177827.941 | 104.9163 | 2126.9098 | 2485.662 | 43.3599 | 50.6736
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 240.5649 | 205.6276 | 26.4133 | 4 | 2120.6808 | 2476.9308 | 43.2329 | 50.4956 | 235.1813 | 0 | 358.2597 | 22154158.1827 | 1374687.4731 | 23208649.3373 | 16626034.4917 | 0 | 530597.5248 | 0 | 24918709.5338 | 64833370.6767 | 44250107.6794 | 197896314.8994 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 224056707.3382 | 261695659.9812 | 237137.3706 | 105.6532 | 2120.6808 | 2476.9308 | 43.2329 | 50.4956
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.1313 | 206.5261 | 26.5547 | 4 | 2115.9788 | 2470.3317 | 43.1371 | 50.3611 | 234.9207 | 0 | 367.1769 | 22223465.2347 | 1378889.5754 | 23289745.2923 | 16727365.9758 | 0 | 500710.2235 | 0 | 25006868.7577 | 65062742.8934 | 44406658.9304 | 198596446.8832 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 224756839.322 | 262395791.965 | 316227.766 | 106.2189 | 2115.9788 | 2470.3317 | 43.1371 | 50.3611
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 243.2567 | 207.1661 | 26.6574 | 4 | 2112.4314 | 2465.4195 | 43.0648 | 50.2609 | 234.7323 | 0 | 367.1078 | 22272779.351 | 1381879.2747 | 23347464.7075 | 16800009.3949 | 0 | 476466.7084 | 0 | 25068653.7803 | 65223494.8483 | 44516375.4428 | 199087123.5079 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 225247515.9466 | 262886468.5897 | 421696.5034 | 106.6295 | 2112.4314 | 2465.4195 | 43.0648 | 50.2609
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 244.3887 | 207.8095 | 26.7533 | 4 | 2109.7145 | 2461.4365 | 43.0094 | 50.1797 | 234.5441 | 0 | 406.8572 | 22322308.6071 | 1384881.8277 | 23405450.2331 | 16873119.8734 | 0 | 460769.6676 | 0 | 25134146.7815 | 65393894.2029 | 44632676.5037 | 199607247.6969 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 225767640.1356 | 263406592.7787 | 562341.3252 | 107.0134 | 2109.7145 | 2461.4365 | 43.0094 | 50.1797
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 244.8445 | 208.0644 | 26.7998 | 4 | 2107.6791 | 2458.7918 | 42.9679 | 50.1258 | 234.4663 | 0 | 397.2588 | 22341924.5115 | 1386070.9268 | 23428419.1719 | 16902510.5707 | 0 | 443639.1736 | 0 | 25156000.0983 | 65450752.0505 | 44671483.1529 | 199780799.6562 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 225941192.095 | 263580144.738 | 749894.2093 | 107.199 | 2107.6791 | 2458.7918 | 42.9679 | 50.1258
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.4681 | 208.4146 | 26.8516 | 4 | 2106.269 | 2456.7044 | 42.9391 | 50.0832 | 234.3611 | 0 | 423.4094 | 22368855.7305 | 1387703.4257 | 23459957.5157 | 16942755.1868 | 0 | 435393.9901 | 0 | 25191919.6811 | 65544207.4369 | 44735268.3744 | 200066061.3412 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226226453.78 | 263865406.423 | 1000000 | 107.4063 | 2106.269 | 2456.7044 | 42.9391 | 50.0832
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.0149 | 208.1524 | 26.8321 | 4 | 2105.0985 | 2455.7887 | 42.9153 | 50.0646 | 234.433 | 0 | 418.9625 | 22348693.4594 | 1386481.2477 | 23436345.6867 | 16913388.3206 | 0 | 416129.5038 | 0 | 25155404.9051 | 65449203.48 | 44670426.2217 | 199776072.825 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 225936465.2637 | 263575417.9067 | 1333521.4322 | 107.3282 | 2105.0985 | 2455.7887 | 42.9153 | 50.0646
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.7971 | 208.5961 | 26.8896 | 4 | 2104.2388 | 2454.1779 | 42.8978 | 50.0317 | 234.3039 | 0 | 440.3642 | 22382808.3443 | 1388549.174 | 23476298.6637 | 16963940.3961 | 0 | 416167.1485 | 0 | 25204827.8534 | 65577791.8535 | 44758190.4289 | 200168573.8624 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226328966.3011 | 263967918.9442 | 1778279.41 | 107.5586 | 2104.2388 | 2454.1779 | 42.8978 | 50.0317
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.0017 | 208.7105 | 26.9081 | 4 | 2103.5965 | 2453.2949 | 42.8847 | 50.0137 | 234.2693 | 0 | 441.4036 | 22391603.3499 | 1389082.2823 | 23486599.8595 | 16977146.9016 | 0 | 411281.2265 | 0 | 25215728.3117 | 65606152.61 | 44777547.228 | 200255141.7695 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226415534.2082 | 264054486.8513 | 2371373.7057 | 107.6326 | 2103.5965 | 2453.2949 | 42.8847 | 50.0137
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.1332 | 208.7837 | 26.9206 | 4 | 2103.1142 | 2452.651 | 42.8748 | 50.0006 | 234.2469 | 0 | 455.0448 | 22397229.8078 | 1389423.3263 | 23493190.1131 | 16985628.703 | 0 | 407306.6663 | 0 | 25222383.6604 | 65623468.4621 | 44789365.6528 | 200307996.3917 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226468388.8305 | 264107341.4735 | 3162277.6602 | 107.6824 | 2103.1142 | 2452.651 | 42.8748 | 50.0006
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.2575 | 208.8532 | 26.9316 | 4 | 2102.7523 | 2452.1463 | 42.8674 | 49.9903 | 234.2259 | 0 | 461.0786 | 22402567.2886 | 1389746.8519 | 23499442.0589 | 16993648.8022 | 0 | 404636.3795 | 0 | 25229116.1386 | 65640984.9894 | 44801321.0426 | 200361463.5518 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226521855.9906 | 264160808.6336 | 4216965.0343 | 107.7264 | 2102.7523 | 2452.1463 | 42.8674 | 49.9903
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.3371 | 208.8975 | 26.939 | 4 | 2102.4806 | 2451.7792 | 42.8619 | 49.9828 | 234.2124 | 0 | 504.6069 | 22405972.2711 | 1389953.24 | 23503430.5 | 16998781.5081 | 0 | 402450.1915 | 0 | 25233229.2071 | 65651686.3499 | 44808624.9411 | 200394128.2088 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226554520.6475 | 264193473.2906 | 5623413.2519 | 107.7558 | 2102.4806 | 2451.7792 | 42.8619 | 49.9828
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.3908 | 208.9273 | 26.9441 | 4 | 2102.2768 | 2451.5088 | 42.8578 | 49.9773 | 234.2032 | 0 | 488.273 | 22408264.8429 | 1390092.2005 | 23506115.9519 | 17002245.5571 | 0 | 400729.2176 | 0 | 25235904.6303 | 65658647.2522 | 44813375.8999 | 200415375.5523 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226575767.9911 | 264214720.6341 | 7498942.0933 | 107.7764 | 2102.2768 | 2451.5088 | 42.8578 | 49.9773
1 | 6300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.4445 | 208.9573 | 26.9488 | 4 | 2102.1239 | 2451.2947 | 42.8546 | 49.973 | 234.1941 | 0 | 476.5224 | 22410569.5493 | 1390231.896 | 23508815.6487 | 17005712.1249 | 0 | 399607.0071 | 0 | 25238825.1281 | 65666245.7885 | 44818562.0571 | 200438569.1997 | 961560.8286 | 25198831.6101 | 25198831.6101 | 1478867.319 | 10961253.7139 | 0 | 226598961.6384 | 264237914.2814 | 10000000 | 107.7952 | 2102.1239 | 2451.2947 | 42.8546 | 49.973
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2934 | 0.53652 | 0.056849 | 4 | 127071.3765 | 296135.3244 | 2590.5219 | 6037.1191 | 169.2274 | 0 | 55.2013 | 319270.2477 | 18758.2929 | 200248.4737 | 95803.3977 | 0 | 63234.4803 | 0 | 271952.808 | 707565.4213 | 482927.939 | 2159761.0607 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 28895463.734 | 67339850.7056 | 100 | 0.2274 | 127071.3765 | 296135.3244 | 2590.5219 | 6037.1191
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.85799 | 0.10103 | 4 | 73622.4764 | 168750.1278 | 1500.8938 | 3440.1996 | 185.3346 | 0 | 250.1536 | 458794.4919 | 29681.3554 | 289714.0694 | 128118.3994 | 0 | 68005.3059 | 0 | 379982.3126 | 988636.0323 | 674764.4065 | 3017696.3733 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 29753399.0467 | 68197786.0182 | 133.3521 | 0.40413 | 73622.4764 | 168750.1278 | 1500.8938 | 3440.1996
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 1.3004 | 0.15721 | 4 | 48881.4156 | 110016.9659 | 996.5138 | 2242.8447 | 198.8528 | 0 | 318.8075 | 613493.2893 | 39710.0632 | 404060.1169 | 162602.6836 | 0 | 72508.7247 | 0 | 504026.2023 | 1311372.7885 | 895038.8742 | 4002812.7427 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 30738515.4161 | 69182902.3876 | 177.8279 | 0.62884 | 48881.4156 | 110016.9659 | 996.5138 | 2242.8447
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7405 | 1.8822 | 0.23131 | 4 | 34495.8668 | 76047.0664 | 703.2449 | 1550.3223 | 210.4557 | 0 | 391.6476 | 794812.0289 | 51442.095 | 543154.9949 | 205867.7306 | 0 | 77457.9163 | 0 | 652366.5587 | 1697323.9668 | 1158458.4839 | 5180883.7751 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 31916586.4485 | 70360973.42 | 237.1374 | 0.92523 | 34495.8668 | 76047.0664 | 703.2449 | 1550.3223
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.499 | 2.6268 | 0.32658 | 4 | 25493.3623 | 54922.8655 | 519.7167 | 1119.6769 | 219.9754 | 0 | 510.1445 | 1004180.0481 | 64959.7783 | 709128.2572 | 259853.065 | 0 | 82086.0998 | 0 | 826880.8269 | 2151374.295 | 1468357.1627 | 6566819.5331 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 33302522.2064 | 71746909.178 | 316.2278 | 1.3063 | 25493.3623 | 54922.8655 | 519.7167 | 1119.6769
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4721 | 3.5954 | 0.45099 | 4 | 19387.8164 | 40699.0908 | 395.2469 | 829.706 | 227.8362 | 0 | 86.6118 | 1252017.9436 | 80923.3929 | 911563.9325 | 329071.2897 | 0 | 86480.0791 | 0 | 1037422.0888 | 2699159.4705 | 1842231.8008 | 8238869.9979 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 34974572.6712 | 73418959.6428 | 421.6965 | 1.8039 | 19387.8164 | 40699.0908 | 395.2469 | 829.706
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7322 | 4.8631 | 0.61417 | 4 | 15067.4917 | 30716.3112 | 307.1712 | 626.1936 | 234.267 | 0 | 82.6303 | 1548553.0862 | 99974.3943 | 1160695.2758 | 419104.8676 | 0 | 90915.7841 | 0 | 1294504.9291 | 3368036.286 | 2298753.9714 | 10280538.5945 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 37016241.2678 | 75460628.2394 | 562.3413 | 2.4567 | 15067.4917 | 30716.3112 | 307.1712 | 626.1936
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3615 | 6.5074 | 0.82616 | 4 | 11952.0169 | 23585.4162 | 243.658 | 480.8206 | 239.3261 | 0 | 99.5202 | 1901447.3307 | 122583.1442 | 1465240.9425 | 535502.9903 | 0 | 95522.9951 | 0 | 1606915.9871 | 4180865.7746 | 2853526.7994 | 12761605.9638 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 39497308.6372 | 77941695.6087 | 749.8942 | 3.3047 | 11952.0169 | 23585.4162 | 243.658 | 480.8206
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4958 | 8.6884 | 1.108 | 4 | 9608.2603 | 18282.7174 | 195.8774 | 372.7179 | 243.6482 | 0 | 86.9917 | 2331825.7684 | 150073.3065 | 1846439.0758 | 688495.7844 | 0 | 99703.1876 | 0 | 1995449.4779 | 5191750.2184 | 3543476.2039 | 15847213.0229 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 42582915.6963 | 81027302.6678 | 1000 | 4.4319 | 9608.2603 | 18282.7174 | 195.8774 | 372.7179
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.3138 | 11.5779 | 1.4816 | 4 | 7834.4823 | 14321.563 | 159.7165 | 291.9644 | 247.1055 | 0 | 89.4329 | 2856536.1799 | 183480.0873 | 2323217.2532 | 890768.5015 | 0 | 104466.6181 | 0 | 2479802.7696 | 6451938.129 | 4403580.3471 | 19693789.8856 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 46429492.559 | 84873879.5305 | 1333.5214 | 5.9263 | 7834.4823 | 14321.563 | 159.7165 | 291.9644
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.0385 | 15.4 | 1.9758 | 4 | 6481.5124 | 11345.81 | 132.1344 | 231.2997 | 249.7885 | 0 | 98.8134 | 3495702.4406 | 224032.2287 | 2918772.0582 | 1158276.3398 | 0 | 110269.4042 | 0 | 3083750.4639 | 8023286.1428 | 5476057.6545 | 24490146.7328 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 51225849.4062 | 89670236.3777 | 1778.2794 | 7.9034 | 6481.5124 | 11345.81 | 132.1344 | 231.2997
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9495 | 20.4471 | 2.6288 | 4 | 5439.9064 | 9095.9174 | 110.8999 | 185.4326 | 251.8884 | 0 | 120.3294 | 4273641.5574 | 273205.7352 | 3661767.9828 | 1511249.6709 | 0 | 116928.157 | 0 | 3836349.3103 | 9981393.9619 | 6812506.4761 | 30467042.8515 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 57202745.5248 | 95647132.4964 | 2371.3737 | 10.5154 | 5439.9064 | 9095.9174 | 110.8999 | 185.4326
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4347 | 27.1184 | 3.4922 | 4 | 4629.4595 | 7381.6258 | 94.3778 | 150.4844 | 253.5217 | 0 | 107.4489 | 5221973.39 | 332913.8951 | 4589824.6253 | 1977454.5516 | 0 | 124866.8303 | 0 | 4776342.984 | 12427064.6817 | 8481726.9959 | 37932167.9538 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 64667870.6272 | 103112257.5987 | 3162.2777 | 13.9688 | 4629.4595 | 7381.6258 | 94.3778 | 150.4844
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.9802 | 35.914 | 4.6307 | 4 | 3994.0648 | 6069.5971 | 81.4244 | 123.7369 | 254.7808 | 0 | 93.2404 | 6375796.9841 | 405258.3805 | 5746404.4017 | 2591953.0671 | 0 | 134428.6008 | 0 | 5948998.1593 | 15478072.9033 | 10564102.7991 | 47245015.2959 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 73980717.9693 | 112425104.9408 | 4216.965 | 18.5227 | 3994.0648 | 6069.5971 | 81.4244 | 123.7369
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.0863 | 47.3421 | 6.1103 | 4 | 3496.0564 | 5068.989 | 71.2718 | 103.3382 | 255.7184 | 0 | 109.0944 | 7760819.7517 | 491722.6757 | 7167748.1363 | 3390586.9052 | 0 | 145325.6766 | 0 | 7392919.2268 | 19234859.3319 | 13128186.7308 | 58712168.4351 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 85447871.1084 | 123892258.08 | 5623.4133 | 24.4412 | 3496.0564 | 5068.989 | 71.2718 | 103.3382
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.371 | 61.9836 | 8.0056 | 4 | 3104.5166 | 4305.0582 | 63.2898 | 87.7644 | 256.3016 | 0 | 137.7769 | 9403275.0693 | 593800.8558 | 8892139.3482 | 4416872.3214 | 0 | 159472.4442 | 0 | 9151568.4152 | 23810503.7715 | 16251158.081 | 72678790.3066 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 99414492.9799 | 137858879.9515 | 7498.9421 | 32.0225 | 3104.5166 | 4305.0582 | 63.2898 | 87.7644
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.24 | 80.0414 | 10.34 | 4 | 2801.8519 | 3731.3556 | 57.1195 | 76.0687 | 256.3185 | 0 | 103.1513 | 11284240.3462 | 710178.297 | 10910298.5192 | 5696080.5653 | 0 | 182516.1536 | 0 | 11225492.4136 | 29206428.5952 | 19933987.6483 | 89149222.5383 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 115884925.2117 | 154329312.1832 | 10000 | 41.3601 | 2801.8519 | 3731.3556 | 57.1195 | 76.0687
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6548 | 101.0039 | 13.0404 | 4 | 2575.5082 | 3312.5339 | 52.5052 | 67.5305 | 255.4658 | 0 | 133.4376 | 13322868.6703 | 835763.941 | 13141810.0641 | 7217055.3738 | 0 | 225132.4951 | 0 | 13549625.9123 | 35253347.2132 | 24061133.8569 | 107606737.5266 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 134342440.2 | 172786827.1715 | 13335.2143 | 52.1615 | 2575.5082 | 3312.5339 | 52.5052 | 67.5305
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.9669 | 123.5509 | 15.926 | 4 | 2413.5121 | 3016.9981 | 49.2027 | 61.5056 | 253.5476 | 0 | 136.5059 | 15386178.5497 | 962363.6539 | 15440507.351 | 8922275.5766 | 0 | 297366.3871 | 0 | 15993389.6921 | 41611519.2836 | 28400716.9423 | 127014317.4364 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 153750020.1098 | 192194407.0813 | 17782.7941 | 63.7039 | 2413.5121 | 3016.9981 | 49.2027 | 61.5056
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.8789 | 146.0266 | 18.7784 | 4 | 2301.3489 | 2813.1646 | 46.9161 | 57.3502 | 250.8067 | 0 | 144.4093 | 17339636.2803 | 1081805.9434 | 17649414.8003 | 10713592.0192 | 0 | 395149.2642 | 0 | 18400043.3399 | 47873138.4026 | 32674400.6544 | 146127180.7043 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 172862883.3777 | 211307270.3492 | 23713.7371 | 75.1137 | 2301.3489 | 2813.1646 | 46.9161 | 57.3502
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.699 | 166.9792 | 21.4158 | 4 | 2224.7785 | 2673.5649 | 45.3551 | 54.5042 | 247.7485 | 0 | 131.0088 | 19085719.0776 | 1188257.6966 | 19647831.3653 | 12474696.7402 | 0 | 503749.6325 | 0 | 20631099.2597 | 53677888.2535 | 36636261.7033 | 163845503.7287 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 190581206.4021 | 229025593.3736 | 31622.7766 | 85.663 | 2224.7785 | 2673.5649 | 45.3551 | 54.5042
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.6937 | 184.8802 | 23.6433 | 4 | 2176.4598 | 2582.9643 | 44.3701 | 52.6572 | 244.5071 | 0 | 165.4387 | 20529217.1291 | 1276057.7213 | 21315578.2017 | 14086958.4356 | 0 | 617222.7578 | 0 | 22551763.3557 | 58675062.2489 | 40046935.6368 | 179098795.4868 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 205834498.1602 | 244278885.1317 | 42169.6503 | 94.5731 | 2176.4598 | 2582.9643 | 44.3701 | 52.6572
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.7802 | 199.2782 | 25.4114 | 4 | 2147.6635 | 2525.8832 | 43.783 | 51.4935 | 241.3678 | 0 | 154.1231 | 21661955.5077 | 1344834.314 | 22633540.9263 | 15483435.0441 | 0 | 726174.9512 | 0 | 24121476.8898 | 62759134.8721 | 42834399.1215 | 191564951.6267 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 218300654.3 | 256745041.2716 | 56234.1325 | 101.6456 | 2147.6635 | 2525.8832 | 43.783 | 51.4935
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.1003 | 205.1994 | 26.204 | 4 | 2130.2494 | 2497.0287 | 43.428 | 50.9053 | 239.8824 | 0 | 175.1983 | 22121095.089 | 1372682.7188 | 23169972.2517 | 16093633.8197 | 0 | 701690.5353 | 0 | 24749039.0216 | 64391922.8083 | 43948810.4384 | 196548846.6827 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 223284549.3561 | 261728936.3276 | 74989.4209 | 104.8162 | 2130.2494 | 2497.0287 | 43.428 | 50.9053
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 235.6381 | 207.9705 | 26.6234 | 4 | 2117.3024 | 2478.3036 | 43.1641 | 50.5236 | 239.1309 | 0 | 201.8137 | 22334697.8467 | 1385632.8561 | 23419956.96 | 16389451.7456 | 0 | 638025.0101 | 0 | 25025428.1232 | 65111030.5554 | 44439616.252 | 198743839.3491 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 225479542.0225 | 263923928.994 | 100000 | 106.4938 | 2117.3024 | 2478.3036 | 43.1641 | 50.5236
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 239.2332 | 210.1194 | 26.949 | 4 | 2107.5303 | 2464.171 | 42.9649 | 50.2355 | 238.5273 | 0 | 232.8185 | 22499790.6459 | 1395639.5563 | 23613351.5249 | 16622764.263 | 0 | 586223.0143 | 0 | 25239929.9118 | 65669120.2089 | 44820523.9081 | 200447343.0334 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 227183045.7067 | 265627432.6783 | 133352.1432 | 107.7959 | 2107.5303 | 2464.171 | 42.9649 | 50.2355
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 241.9392 | 211.7097 | 27.1927 | 4 | 2100.1556 | 2453.5999 | 42.8145 | 50.02 | 238.0678 | 0 | 268.1476 | 22621663.048 | 1403025.2151 | 23756217.7034 | 16798069.9208 | 0 | 543150.4392 | 0 | 25397629.2673 | 66079421.5834 | 45100563.027 | 201699740.204 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 228435442.8774 | 266879829.8489 | 177827.941 | 108.7707 | 2100.1556 | 2453.5999 | 42.8145 | 50.02
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 244.0534 | 212.9358 | 27.3803 | 4 | 2094.5891 | 2445.6114 | 42.701 | 49.8571 | 237.7061 | 0 | 324.0139 | 22715454.8377 | 1408708.3723 | 23866224.3513 | 16934627.7598 | 0 | 509162.8357 | 0 | 25519329.4811 | 66396060.5756 | 45316675.6455 | 202666243.859 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 229401946.5324 | 267846333.5039 | 237137.3706 | 109.5212 | 2094.5891 | 2445.6114 | 42.701 | 49.8571
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.5855 | 213.8148 | 27.5171 | 4 | 2090.3918 | 2439.6688 | 42.6155 | 49.7359 | 237.4419 | 0 | 353.2704 | 22782596.0218 | 1412776.2694 | 23945003.9974 | 17033486.5167 | 0 | 481239.4785 | 0 | 25605489.8907 | 66620232.2874 | 45469677.445 | 203350501.907 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 230086204.5803 | 268530591.5519 | 316227.766 | 110.0685 | 2090.3918 | 2439.6688 | 42.6155 | 49.7359
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 246.7418 | 214.4734 | 27.62 | 4 | 2087.2288 | 2435.2046 | 42.551 | 49.6449 | 237.2417 | 0 | 658.6135 | 22832852.6981 | 1415820.9574 | 24003989.1996 | 17108083.8276 | 0 | 459311.7752 | 0 | 25669822.7986 | 66787613.3172 | 45583918.4372 | 203861413.0108 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 230597115.6841 | 269041502.6557 | 421696.5034 | 110.48 | 2087.2288 | 2435.2046 | 42.551 | 49.6449
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 247.8628 | 215.1109 | 27.7138 | 4 | 2084.8261 | 2431.6243 | 42.502 | 49.572 | 237.0485 | 0 | 414.7166 | 22881458.4309 | 1418765.4447 | 24061050.4384 | 17180435.8554 | 0 | 445166.5538 | 0 | 25734881.9221 | 66956883.8111 | 45699449.0275 | 204378091.484 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231113794.1574 | 269558181.1289 | 562341.3252 | 110.8552 | 2084.8261 | 2431.6243 | 42.502 | 49.572
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 248.5692 | 215.5083 | 27.7747 | 4 | 2083.0737 | 2429.1117 | 42.4663 | 49.5207 | 236.9253 | 0 | 390.9142 | 22911741.9276 | 1420599.8988 | 24096608.8913 | 17225920.4736 | 0 | 433076.8741 | 0 | 25774299.7455 | 67059440.9021 | 45769446.3494 | 204691135.0625 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231426837.7358 | 269871224.7074 | 749894.2093 | 111.0987 | 2083.0737 | 2429.1117 | 42.4663 | 49.5207
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 247.605 | 214.9497 | 27.7235 | 4 | 2081.7285 | 2428.4058 | 42.4389 | 49.5063 | 237.0845 | 0 | 575.2994 | 22869178.085 | 1418021.5304 | 24046632.5186 | 17163565.724 | 0 | 404597.6404 | 0 | 25701778.2444 | 66870754.8323 | 45640664.2296 | 204115192.8047 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 230850895.4781 | 269295282.4496 | 1000000 | 110.8939 | 2081.7285 | 2428.4058 | 42.4389 | 49.5063
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.1734 | 215.8444 | 27.8343 | 4 | 2080.6928 | 2425.9896 | 42.4177 | 49.4571 | 236.8182 | 0 | 422.7178 | 22937337.9722 | 1422150.3516 | 24126667.4734 | 17264736.6818 | 0 | 411849.5084 | 0 | 25803469.3751 | 67135334.2946 | 45821245.1492 | 204922790.8063 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231658493.4797 | 270102880.4512 | 1333521.4322 | 111.3372 | 2080.6928 | 2425.9896 | 42.4177 | 49.4571
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.4318 | 215.9886 | 27.8575 | 4 | 2079.9314 | 2424.9402 | 42.4022 | 49.4357 | 236.7729 | 0 | 418.2704 | 22948318.7972 | 1422815.4881 | 24139563.8897 | 17281349.569 | 0 | 405758.9571 | 0 | 25817144.6134 | 67170914.4596 | 45845529.3429 | 205031395.117 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231767097.7904 | 270211484.7619 | 1778279.41 | 111.4302 | 2079.9314 | 2424.9402 | 42.4022 | 49.4357
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.6292 | 216.0987 | 27.8752 | 4 | 2079.3597 | 2424.1499 | 42.3906 | 49.4196 | 236.7382 | 0 | 419.2277 | 22956700.9659 | 1423323.2112 | 24149408.7784 | 17294044.2556 | 0 | 401191.5123 | 0 | 25827620.8021 | 67198171.3537 | 45864132.7332 | 205114593.6125 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231850296.2859 | 270294683.2574 | 2371373.7057 | 111.5008 | 2079.3597 | 2424.1499 | 42.3906 | 49.4196
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.7802 | 216.1829 | 27.8886 | 4 | 2078.9306 | 2423.5547 | 42.3818 | 49.4074 | 236.7117 | 0 | 428.2802 | 22963105.038 | 1423711.1139 | 24156930.6542 | 17303750.5746 | 0 | 397776.129 | 0 | 25835656.6688 | 67219079.0303 | 45878402.6521 | 205178411.8608 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231914114.5342 | 270358501.5057 | 3162277.6602 | 111.5545 | 2078.9306 | 2423.5547 | 42.3818 | 49.4074
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.9038 | 216.2518 | 27.8994 | 4 | 2078.6085 | 2423.1 | 42.3752 | 49.3982 | 236.6901 | 0 | 519.6766 | 22968353.7963 | 1424029.0355 | 24163095.7346 | 17311700.915 | 0 | 395330.1353 | 0 | 25842378.7505 | 67236568.508 | 45890339.58 | 205231796.4552 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 231967499.1285 | 270411886.1001 | 4216965.0343 | 111.5975 | 2078.6085 | 2423.1 | 42.3752 | 49.3982
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.9964 | 216.3035 | 27.9074 | 4 | 2078.3668 | 2422.7589 | 42.3703 | 49.3912 | 236.6739 | 0 | 513.6435 | 22972283.1392 | 1424267.0376 | 24167711.1599 | 17317656.903 | 0 | 393486.1132 | 0 | 25847407.6977 | 67249652.7969 | 45899269.8761 | 205271734.7237 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 232007437.397 | 270451824.3686 | 5623413.2519 | 111.6297 | 2078.3668 | 2422.7589 | 42.3703 | 49.3912
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 250.0501 | 216.3333 | 27.9124 | 4 | 2078.1855 | 2422.5157 | 42.3666 | 49.3863 | 236.6644 | 0 | 504.4791 | 22974548.4622 | 1424404.2487 | 24170372.0592 | 17321108.7229 | 0 | 391901.5202 | 0 | 25850110.6552 | 67256685.3379 | 45904069.7298 | 205293200.7361 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 232028903.4095 | 270473290.381 | 7498942.0933 | 111.6498 | 2078.1855 | 2422.5157 | 42.3666 | 49.3863
1 | 6400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 250.1085 | 216.3658 | 27.9174 | 4 | 2078.0494 | 2422.3189 | 42.3638 | 49.3822 | 236.6542 | 0 | 515.8505 | 22977026.8922 | 1424554.3674 | 24173283.3121 | 17324861.9699 | 0 | 390936.4886 | 0 | 25853358.5817 | 67265135.7766 | 45909837.3278 | 205318994.7162 | 961560.8286 | 25774141.8447 | 25774141.8447 | 1478867.319 | 11191377.8078 | 0 | 232054697.3896 | 270499084.3611 | 10000000 | 111.6695 | 2078.0494 | 2422.3189 | 42.3638 | 49.3822
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.56873 | 0.062269 | 4 | 118744.4789 | 276358.4503 | 2420.7668 | 5633.9408 | 172.2712 | 0 | 57.8302 | 336848.3458 | 20460.4279 | 209332.8101 | 99710.5869 | 0 | 63214.606 | 0 | 284531.0429 | 740291.4084 | 505264.0977 | 2259653.3257 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 29576526.3246 | 68834551.7518 | 100 | 0.24908 | 118744.4789 | 276358.4503 | 2420.7668 | 5633.9408
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7098 | 0.91643 | 0.10872 | 4 | 70053.0456 | 160326.8885 | 1428.1261 | 3268.4805 | 188.4729 | 0 | 254.1305 | 480392.1181 | 31082.5085 | 305396.235 | 131716.7945 | 0 | 67664.6357 | 0 | 396338.3938 | 1031191.2005 | 703809.1832 | 3147591.0692 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 30464464.0681 | 69722489.4953 | 133.3521 | 0.43488 | 70053.0456 | 160326.8885 | 1428.1261 | 3268.4805
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 1.3871 | 0.16868 | 4 | 46679.1424 | 104864.6852 | 951.6175 | 2137.8084 | 202.3142 | 0 | 329.5115 | 642131.1293 | 41619.7754 | 425443.8804 | 167420.8275 | 0 | 72236.3907 | 0 | 526052.2813 | 1368680.1277 | 934152.3107 | 4177736.7228 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 31494609.7217 | 70752635.1489 | 177.8279 | 0.6747 | 46679.1424 | 104864.6852 | 951.6175 | 2137.8084
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8183 | 2.003 | 0.24716 | 4 | 33094.0287 | 72802.9189 | 674.6665 | 1484.186 | 214.0194 | 0 | 409.314 | 830239.7875 | 53731.6201 | 570869.2877 | 212171.7627 | 0 | 76918.9514 | 0 | 680133.2497 | 1769567.2012 | 1207765.9758 | 5401397.8363 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 32718270.8351 | 71976296.2623 | 237.1374 | 0.98865 | 33094.0287 | 72802.9189 | 674.6665 | 1484.186
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5768 | 2.7666 | 0.34542 | 4 | 24689.1019 | 53101.9761 | 503.3207 | 1082.5556 | 223.3513 | 0 | 525.5856 | 1041428.2038 | 67361.5322 | 739170.6318 | 266346.5022 | 0 | 79902.1275 | 0 | 855741.5091 | 2226463.8698 | 1519607.3404 | 6796021.7169 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 34112894.7158 | 73370920.143 | 316.2278 | 1.3817 | 24689.1019 | 53101.9761 | 503.3207 | 1082.5556
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5648 | 3.7762 | 0.47558 | 4 | 18833.8095 | 39470.7634 | 383.9527 | 804.6649 | 231.2174 | 0 | 83.6289 | 1295967.9257 | 83750.2452 | 948046.0283 | 337146.4586 | 0 | 83007.8792 | 0 | 1071688.2294 | 2788312.9394 | 1903080.8753 | 8511000.5811 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 35827873.5799 | 75085899.0072 | 421.6965 | 1.9023 | 18833.8095 | 39470.7634 | 383.9527 | 804.6649
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8559 | 5.1093 | 0.64774 | 4 | 14643.725 | 29795.6945 | 298.5321 | 607.4255 | 237.7067 | 0 | 73.8852 | 1603364.4298 | 103490.2927 | 1207461.9542 | 429836.1569 | 0 | 86084.6285 | 0 | 1337792.6102 | 3480661.9527 | 2375623.3032 | 10624315.3282 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 37941188.327 | 77199213.7543 | 562.3413 | 2.591 | 14643.725 | 29795.6945 | 298.5321 | 607.4255
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5079 | 6.82 | 0.86912 | 4 | 11644.5368 | 22937.0002 | 237.3896 | 467.6018 | 242.7374 | 0 | 86.9013 | 1965448.0252 | 126676.6647 | 1521293.08 | 548598.0988 | 0 | 88565.6555 | 0 | 1657726.7945 | 4313065.0727 | 2943755.5367 | 13165128.9282 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 40482001.927 | 79740027.3542 | 749.8942 | 3.4765 | 11644.5368 | 22937.0002 | 237.3896 | 467.6018
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7005 | 9.1274 | 1.1683 | 4 | 9349.5982 | 17750.0603 | 190.6042 | 361.859 | 247.1986 | 0 | 87.6657 | 2414474.3673 | 155342.8745 | 1920719.7172 | 706941.3619 | 0 | 90034.1313 | 0 | 2062129.8563 | 5365238.8852 | 3661885.7838 | 16376766.9774 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 43693639.9763 | 82951665.4035 | 1000 | 4.6733 | 9349.5982 | 17750.0603 | 190.6042 | 361.859
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5768 | 12.1535 | 1.5609 | 4 | 7633.1875 | 13920.9601 | 155.6129 | 283.7976 | 250.6084 | 0 | 103.1803 | 2956287.2819 | 189818.596 | 2415164.7425 | 914795.5965 | 0 | 91467.7611 | 0 | 2561338.2514 | 6664076.7274 | 4548369.2996 | 20341318.2564 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 47658191.2552 | 86916216.6824 | 1333.5214 | 6.2436 | 7633.1875 | 13920.9601 | 155.6129 | 283.7976
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.3675 | 16.1503 | 2.0797 | 4 | 6322.245 | 11041.5482 | 128.8875 | 225.0969 | 253.2945 | 0 | 106.3528 | 3615519.0335 | 231618.2828 | 3031995.5982 | 1188959.7279 | 0 | 92489.7723 | 0 | 3182627.1417 | 8280542.9762 | 5651640.7294 | 25275393.2621 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 52592266.261 | 91850291.6882 | 1778.2794 | 8.3186 | 6322.245 | 11041.5482 | 128.8875 | 225.0969
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.371 | 21.4344 | 2.7658 | 4 | 5310.2452 | 8858.7891 | 108.2565 | 180.5984 | 255.4009 | 0 | 125.9554 | 4419005.6277 | 282373.9958 | 3802537.9027 | 1551101.0335 | 0 | 93034.7476 | 0 | 3957740.7898 | 10297229.6909 | 7028070.8509 | 31431094.6388 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 58747967.6377 | 98005993.0649 | 2371.3737 | 11.0631 | 5310.2452 | 8858.7891 | 108.2565 | 180.5984
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.9754 | 28.4164 | 3.6726 | 4 | 4522.2052 | 7194.5418 | 92.1913 | 146.6705 | 257.0392 | 0 | 89.7713 | 5398295.8948 | 343989.5857 | 4764748.1045 | 2029412.2647 | 0 | 93031.2183 | 0 | 4925496.0566 | 12815130.381 | 8746589.8096 | 39116693.3153 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 66433566.3141 | 105691591.7414 | 3162.2777 | 14.6905 | 4522.2052 | 7194.5418 | 92.1913 | 146.6705
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.6648 | 37.6074 | 4.8667 | 4 | 3904.3697 | 5921.0464 | 79.5959 | 120.7085 | 258.3006 | 0 | 107.0201 | 6588167.481 | 418541.475 | 5962159.7723 | 2658761.6912 | 0 | 92197.3442 | 0 | 6130732.8278 | 15950909.2317 | 10886823.3091 | 48688293.1323 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 76005166.1311 | 115263191.5584 | 4216.965 | 19.4667 | 3904.3697 | 5921.0464 | 79.5959 | 120.7085
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.9754 | 49.5662 | 6.4207 | 4 | 3418.9343 | 4947.5175 | 69.6996 | 100.8618 | 259.2381 | 0 | 96.6495 | 8018714.8002 | 507781.8213 | 7435899.2021 | 3477908.8379 | 0 | 90008.2072 | 0 | 7616822.0188 | 19817408.4679 | 13525788.4864 | 60490331.8419 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 87807204.8408 | 127065230.268 | 5623.4133 | 25.6826 | 3418.9343 | 4947.5175 | 69.6996 | 100.8618
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.571 | 36.4374 | 4.7326 | 4 | 3937.0799 | 6010.8856 | 80.2627 | 122.54 | 258.1294 | 0 | 102.1579 | 6441732.5873 | 409383.4686 | 5813301.0075 | 2579322.3925 | 0 | 0 | 0 | 5945058.3878 | 15467822.4259 | 10557106.6376 | 47213726.9072 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 74530599.9061 | 113788625.3333 | 7498.9421 | 18.9304 | 3937.0799 | 6010.8856 | 80.2627 | 122.54
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2969 | 47.7739 | 6.205 | 4 | 3456.8477 | 5038.5499 | 70.4725 | 102.7177 | 259.0804 | 0 | 77.1292 | 7811155.8809 | 494858.0655 | 7220005.0055 | 3356024.7083 | 0 | 0 | 0 | 7363997.0275 | 19159609.702 | 13076827.3122 | 58482477.7017 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 85799350.7006 | 125057376.1278 | 10000 | 24.8201 | 3456.8477 | 5038.5499 | 70.4725 | 102.7177
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.7005 | 61.8917 | 8.0387 | 4 | 3083.6651 | 4304.5738 | 62.8647 | 87.7546 | 259.6814 | 0 | 81.3569 | 9393333.9517 | 593184.3701 | 8881589.4538 | 4325870.062 | 0 | 0 | 0 | 9045651.3567 | 23534929.312 | 16063072.8498 | 71837631.3563 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 99154504.3551 | 138412529.7823 | 13335.2143 | 32.1548 | 3083.6651 | 4304.5738 | 62.8647 | 87.7546
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.7562 | 78.5997 | 10.2088 | 4 | 2798.5176 | 3759.8973 | 57.0516 | 76.6506 | 259.785 | 0 | 104.8633 | 11138822.4517 | 701199.3067 | 10752793.3272 | 5483943.2359 | 0 | 0 | 0 | 10949935.7454 | 28489486.6688 | 19444660.0519 | 86960840.7875 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 114277713.7864 | 153535739.2136 | 17782.7941 | 40.8351 | 2798.5176 | 3759.8973 | 57.0516 | 76.6506
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8996 | 96.9992 | 12.5986 | 4 | 2586.4188 | 3365.4365 | 52.7276 | 68.609 | 259.2193 | 0 | 100.8665 | 12943411.6917 | 812427.8521 | 12723288.7994 | 6783823.5281 | 0 | 0 | 0 | 12972551.2298 | 33751917.2639 | 23036377.0652 | 103023797.4303 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 130340670.4291 | 169598695.8563 | 23713.7371 | 50.3943 | 2586.4188 | 3365.4365 | 52.7276 | 68.609
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.9984 | 115.5984 | 15.0143 | 4 | 2433.6046 | 3087.2828 | 49.6123 | 62.9384 | 257.9589 | 0 | 108.8119 | 14671588.9199 | 918571.9388 | 14640169.1376 | 8138633.4881 | 0 | 0 | 0 | 14963895.7589 | 38932987.2476 | 26572563.7893 | 118838410.2801 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 146155283.279 | 185413308.7062 | 31622.7766 | 60.0571 | 2433.6046 | 3087.2828 | 49.6123 | 62.9384
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.2795 | 190.7927 | 24.4834 | 4 | 2143.8053 | 2544.6688 | 43.7044 | 51.8765 | 247.508 | 0 | 167.482 | 20997255.5386 | 1304488.2834 | 21859191.9622 | 14271161.3707 | 0 | 534269.8255 | 0 | 22996883.1223 | 59833172.5749 | 40837369.7311 | 182633792.4087 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 209950665.4076 | 249208690.8348 | 42169.6503 | 97.9336 | 2143.8053 | 2544.6688 | 43.7044 | 51.8765
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.181 | 205.2722 | 26.2661 | 4 | 2116.6055 | 2490.2626 | 43.1499 | 50.7674 | 244.3077 | 0 | 182.9658 | 22126719.0966 | 1373023.732 | 23176550.7416 | 15657427.6205 | 0 | 645562.817 | 0 | 24561920.763 | 63905079.4826 | 43616529.865 | 195062814.1183 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 222379687.1171 | 261637712.5444 | 56234.1325 | 105.0643 | 2116.6055 | 2490.2626 | 43.1499 | 50.7674
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 234.3204 | 212.4242 | 27.1881 | 4 | 2100.7639 | 2461.7488 | 42.8269 | 50.1861 | 242.4837 | 0 | 172.6136 | 22676333.3649 | 1406337.9533 | 23820333.3578 | 16387502.9984 | 0 | 653011.3404 | 0 | 25327972.4158 | 65898188.7443 | 44976867.8904 | 201146548.0653 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 228463421.0642 | 267721446.4914 | 74989.4209 | 108.7525 | 2100.7639 | 2461.7488 | 42.8269 | 50.1861
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 238.9755 | 215.2751 | 27.6094 | 4 | 2089.268 | 2444.7446 | 42.5926 | 49.8394 | 241.6866 | 0 | 194.2055 | 22893970.8404 | 1419523.4053 | 24075741.6995 | 16690756.739 | 0 | 596619.3235 | 0 | 25613878.683 | 66642058.2041 | 45484574.0817 | 203417122.9763 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 230733995.9751 | 269992021.4024 | 100000 | 110.4377 | 2089.268 | 2444.7446 | 42.5926 | 49.8394
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.5318 | 217.405 | 27.9273 | 4 | 2080.6181 | 2432.0482 | 42.4162 | 49.5806 | 241.0686 | 0 | 214.0101 | 23056043.9483 | 1429340.1928 | 24266117.8353 | 16921777.448 | 0 | 549121.0084 | 0 | 25826736.1688 | 67195869.7192 | 45862561.8204 | 205107568.1411 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 232424441.14 | 271682466.5672 | 133352.1432 | 111.7093 | 2080.6181 | 2432.0482 | 42.4162 | 49.5806
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.3692 | 219.0742 | 28.1754 | 4 | 2074.0975 | 2422.4332 | 42.2833 | 49.3846 | 240.5708 | 0 | 252.4003 | 23182746.8361 | 1437013.2274 | 24415050.5279 | 17105192.5076 | 0 | 511768.0701 | 0 | 25994190.7559 | 67631552.2052 | 46159924.0695 | 206437438.1998 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 233754311.1986 | 273012336.6258 | 177827.941 | 112.7017 | 2074.0975 | 2422.4332 | 42.2833 | 49.3846
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 247.4614 | 220.2874 | 28.3582 | 4 | 2069.1859 | 2415.2767 | 42.1832 | 49.2387 | 240.2003 | 0 | 334.4206 | 23274671.9677 | 1442579.395 | 24523160.3366 | 17240254.526 | 0 | 480759.8702 | 0 | 26114956.1772 | 67945759.0591 | 46374376.7036 | 207396518.0354 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 234713391.0343 | 273971416.4615 | 237137.3706 | 113.4327 | 2069.1859 | 2415.2767 | 42.1832 | 49.2387
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 249.0576 | 221.2037 | 28.4965 | 4 | 2065.487 | 2409.8974 | 42.1077 | 49.129 | 239.916 | 0 | 343.4881 | 23344003.179 | 1446777.0594 | 24604729.6037 | 17343246.5352 | 0 | 456271.7922 | 0 | 26206060.9862 | 68182795.0838 | 46536158.661 | 208120042.9007 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 235436915.8995 | 274694941.3268 | 316227.766 | 113.9862 | 2065.487 | 2409.8974 | 42.1077 | 49.129
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 250.4601 | 222.0051 | 28.614 | 4 | 2062.655 | 2405.6516 | 42.05 | 49.0425 | 239.6668 | 0 | 377.4309 | 23404574.524 | 1450444.0647 | 24676014.7458 | 17433721.515 | 0 | 438964.9346 | 0 | 26287450.7158 | 68394554.4649 | 46680688.7898 | 208766413.7545 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 236083286.7533 | 275341312.1806 | 421696.5034 | 114.456 | 2062.655 | 2405.6516 | 42.05 | 49.0425
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 250.923 | 222.2612 | 28.6625 | 4 | 2060.5981 | 2403.0147 | 42.0081 | 48.9887 | 239.5804 | 0 | 363.8721 | 23423922.4425 | 1451615.3354 | 24698789.2183 | 17463467.0253 | 0 | 418901.47 | 0 | 26308111.2417 | 68448308.9152 | 46717377.3067 | 208930492.955 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 236247365.9538 | 275505391.3811 | 562341.3252 | 114.6499 | 2060.5981 | 2403.0147 | 42.0081 | 48.9887
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 251.9904 | 222.8662 | 28.7458 | 4 | 2059.0652 | 2400.4896 | 41.9768 | 48.9372 | 239.3901 | 0 | 706.2222 | 23469591.1097 | 1454379.8833 | 24752554.1651 | 17532322.4985 | 0 | 412582.5738 | 0 | 26372357.7898 | 68615465.2547 | 46831464.9432 | 209440718.218 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 236757591.2169 | 276015616.6441 | 749894.2093 | 114.983 | 2059.0652 | 2400.4896 | 41.9768 | 48.9372
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 252.2823 | 223.0282 | 28.7756 | 4 | 2057.8478 | 2398.9179 | 41.952 | 48.9052 | 239.3364 | 0 | 404.6868 | 23481815.3471 | 1455119.85 | 24766947.5215 | 17551104.1192 | 0 | 400629.4841 | 0 | 26385690.3655 | 68650153.8818 | 46855140.6439 | 209546601.2131 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 236863474.212 | 276121499.6392 | 1000000 | 115.1025 | 2057.8478 | 2398.9179 | 41.952 | 48.9052
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 252.6649 | 223.2425 | 28.8084 | 4 | 2056.9583 | 2397.6402 | 41.9339 | 48.8791 | 239.2673 | 0 | 431.4917 | 23497982.7483 | 1456098.4903 | 24785985.0087 | 17575764.4262 | 0 | 393841.2787 | 0 | 26406772.0614 | 68705004.1299 | 46892577.0653 | 209714025.2088 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237030898.2077 | 276288923.6349 | 1333521.4322 | 115.2337 | 2056.9583 | 2397.6402 | 41.9339 | 48.8791
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 252.9324 | 223.3918 | 28.8317 | 4 | 2056.2903 | 2396.6967 | 41.9203 | 48.8599 | 239.2187 | 0 | 420.6132 | 23509242.6709 | 1456780.0612 | 24799244.6848 | 17592997.4397 | 0 | 388441.0875 | 0 | 26421215.3182 | 68742582.5215 | 46918225.0897 | 209828728.8735 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237145601.8724 | 276403627.2996 | 1778279.41 | 115.3269 | 2056.2903 | 2396.6967 | 41.9203 | 48.8599
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.1519 | 223.5143 | 28.8504 | 4 | 2055.7887 | 2395.9746 | 41.91 | 48.8452 | 239.179 | 0 | 413.3646 | 23518485.249 | 1457339.5138 | 24810129.2638 | 17607142.1261 | 0 | 384582.8324 | 0 | 26433294.8042 | 68774010.8662 | 46939675.5808 | 209924660.2363 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237241533.2352 | 276499558.6624 | 2371373.7057 | 115.4017 | 2055.7887 | 2395.9746 | 41.91 | 48.8452
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.3 | 223.5968 | 28.8634 | 4 | 2055.4123 | 2395.4456 | 41.9024 | 48.8344 | 239.1521 | 0 | 517.6178 | 23524699.8234 | 1457715.678 | 24817448.1623 | 17616683.0166 | 0 | 381464.1358 | 0 | 26441224.2183 | 68794641.575 | 46953756.4635 | 209987633.0729 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237304506.0717 | 276562531.4989 | 3162277.6602 | 115.4535 | 2055.4123 | 2395.4456 | 41.9024 | 48.8344
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.4265 | 223.6673 | 28.8741 | 4 | 2055.1299 | 2395.037 | 41.8966 | 48.8261 | 239.1292 | 0 | 496.0939 | 23530017.0089 | 1458037.5216 | 24823710.3768 | 17624834.0056 | 0 | 379301.0017 | 0 | 26448200.9667 | 68812793.6433 | 46966145.6231 | 210043040.1477 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237359913.1465 | 276617938.5738 | 4216965.0343 | 115.4963 | 2055.1299 | 2395.037 | 41.8966 | 48.8261
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.5191 | 223.7189 | 28.882 | 4 | 2054.9179 | 2394.7324 | 41.8923 | 48.8199 | 239.1124 | 0 | 488.2524 | 23533905.7021 | 1458272.8987 | 24828290.3109 | 17630801.9486 | 0 | 377643.9357 | 0 | 26453276.7705 | 68825999.8436 | 46975159.1261 | 210083350.5362 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237400223.5351 | 276658248.9623 | 5623413.2519 | 115.5278 | 2054.9179 | 2394.7324 | 41.8923 | 48.8199
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.5728 | 223.7486 | 28.8868 | 4 | 2054.7589 | 2394.5159 | 41.889 | 48.8154 | 239.1026 | 0 | 470.8575 | 23536146.52 | 1458408.5318 | 24830929.4871 | 17634260.57 | 0 | 376204.519 | 0 | 26456020.3549 | 68833138.0875 | 46980031.1242 | 210105139.1945 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237422012.1934 | 276680037.6206 | 7498942.0933 | 115.5474 | 2054.7589 | 2394.5159 | 41.889 | 48.8154
1 | 6500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.6239 | 223.777 | 28.8912 | 4 | 2054.6397 | 2394.3453 | 41.8866 | 48.812 | 239.0933 | 0 | 489.678 | 23538290.0726 | 1458538.2772 | 24833454.133 | 17637554.0917 | 0 | 375255.2307 | 0 | 26458805.804 | 68840385.2548 | 46984977.4648 | 210127260.3288 | 961560.8286 | 26355312.1702 | 26355312.1702 | 1478867.319 | 11423845.938 | 0 | 237444133.3277 | 276702158.7549 | 10000000 | 115.5649 | 2054.6397 | 2394.3453 | 41.8866 | 48.812
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3639 | 0.60798 | 0.068764 | 4 | 110100.6377 | 255816.1616 | 2244.5504 | 5215.1585 | 175.6714 | 0 | 65.5487 | 357813.1761 | 22574.4019 | 220265.9174 | 104151.2683 | 0 | 63582.8833 | 0 | 299671.1824 | 779682.9455 | 532149.6312 | 2379891.4061 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 30283794.8213 | 70363662.8314 | 100 | 0.27506 | 110100.6377 | 255816.1616 | 2244.5504 | 5215.1585
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.97603 | 0.11659 | 4 | 66860.5947 | 152802.2028 | 1363.0437 | 3115.0796 | 191.6072 | 0 | 159.9956 | 502003.4736 | 32484.222 | 321186.0825 | 135261.8904 | 0 | 67199.2385 | 0 | 412672.6138 | 1073689.4902 | 732815.1392 | 3277312.1503 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 31181215.5656 | 71261083.5757 | 133.3521 | 0.46636 | 66860.5947 | 152802.2028 | 1363.0437 | 3115.0796
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 1.4771 | 0.18038 | 4 | 44708.4637 | 100258.468 | 911.4425 | 2043.9045 | 205.7632 | 0 | 229.2249 | 670716.904 | 43415.2622 | 447427.2018 | 172322.2888 | 0 | 71779.0287 | 0 | 548207.6673 | 1426323.8976 | 973495.3681 | 4353687.6185 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 32257591.0337 | 72337459.0438 | 177.8279 | 0.72151 | 44708.4637 | 100258.468 | 911.4425 | 2043.9045
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8766 | 2.1074 | 0.26125 | 4 | 32045.0424 | 70398.3087 | 653.2815 | 1435.1647 | 217.2789 | 0 | 318.8498 | 860350.8081 | 55676.848 | 594549.1609 | 217092.5652 | 0 | 75138.9912 | 0 | 703095.2656 | 1829309.6564 | 1248541.429 | 5583754.7242 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 33487658.1394 | 73567526.1495 | 237.1374 | 1.045 | 32045.0424 | 70398.3087 | 653.2815 | 1435.1647
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.674 | 2.9306 | 0.36729 | 4 | 23801.7678 | 51082.6991 | 485.2312 | 1041.3899 | 226.9098 | 0 | 411.1917 | 1084409.7404 | 70131.8325 | 774013.2484 | 274293.4936 | 0 | 78056.4317 | 0 | 889552.8512 | 2314434.0464 | 1579648.7935 | 7064540.4376 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 34968443.8528 | 75048311.863 | 316.2278 | 1.4692 | 23801.7678 | 51082.6991 | 485.2312 | 1041.3899
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6768 | 3.9823 | 0.50342 | 4 | 18237.3351 | 38141.2595 | 371.7927 | 777.5612 | 234.7133 | 0 | 64.8796 | 1345341.3283 | 86924.5403 | 989222.04 | 346598.6806 | 0 | 79600.6256 | 0 | 1110598.0138 | 2889548.2169 | 1972176.0323 | 8820009.478 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 36723912.8932 | 76803780.9033 | 421.6965 | 2.0137 | 18237.3351 | 38141.2595 | 371.7927 | 777.5612
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9802 | 5.3637 | 0.68255 | 4 | 14239.7382 | 28920.0248 | 290.2963 | 589.5738 | 241.1392 | 0 | 60.0446 | 1659202.4329 | 107070.3702 | 1255316.103 | 440776.7331 | 0 | 80510.8628 | 0 | 1381721.8358 | 3594956.7866 | 2453631.8758 | 10973187.0003 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 38877090.4155 | 78956958.4256 | 562.3413 | 2.7302 | 14239.7382 | 28920.0248 | 290.2963 | 589.5738
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.671 | 7.1601 | 0.91575 | 4 | 11330.4433 | 22272.2411 | 230.9864 | 454.0498 | 246.1744 | 0 | 82.027 | 2034100.1084 | 131065.487 | 1581676.7062 | 563122.0554 | 0 | 80885.4143 | 0 | 1712431.4108 | 4455395.263 | 3040898.8162 | 13599575.2615 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 41503478.6767 | 81583346.6868 | 749.8942 | 3.663 | 11330.4433 | 22272.2411 | 230.9864 | 454.0498
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9025 | 9.5751 | 1.2301 | 4 | 9106.7538 | 17252.3594 | 185.6535 | 351.7127 | 250.6872 | 0 | 89.9449 | 2497571.7113 | 160638.1123 | 1995725.7341 | 725499.2699 | 0 | 78699.4327 | 0 | 2128672.3615 | 5538368.8339 | 3780050.5312 | 16905225.987 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 44809129.4022 | 84888997.4123 | 1000 | 4.9204 | 9106.7538 | 17252.3594 | 185.6535 | 351.7127
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8428 | 12.7521 | 1.6437 | 4 | 7438.1472 | 13534.2763 | 151.6367 | 275.9145 | 254.1034 | 0 | 82.5926 | 3058594.3931 | 196315.6515 | 2509868.4126 | 939502.8977 | 0 | 75677.7678 | 0 | 2644184.0579 | 6879624.5218 | 4695485.0983 | 20999252.8007 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 48903156.2159 | 88983024.226 | 1333.5214 | 6.5746 | 7438.1472 | 13534.2763 | 151.6367 | 275.9145
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.699 | 16.9297 | 2.1879 | 4 | 6167.3532 | 10747.1582 | 125.7298 | 219.0954 | 256.7909 | 0 | 79.344 | 3738305.9444 | 239387.5385 | 3148503.8281 | 1220508.6896 | 0 | 70199.5978 | 0 | 3282593.1834 | 8540634.1107 | 5829158.273 | 26069291.1655 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 53973194.5807 | 94053062.5908 | 1778.2794 | 8.7514 | 6167.3532 | 10747.1582 | 125.7298 | 219.0954
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7996 | 22.4645 | 2.9091 | 4 | 5182.7548 | 8627.0941 | 105.6575 | 175.875 | 258.9042 | 0 | 96.62 | 4568659.7476 | 291806.5898 | 3948049.3756 | 1592428.0176 | 0 | 61532.9417 | 0 | 4080365.9022 | 10616275.0794 | 7245825.8843 | 32404943.5383 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 60308846.9535 | 100388714.9636 | 2371.3737 | 11.6364 | 5182.7548 | 8627.0941 | 105.6575 | 175.875
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5092 | 16.7202 | 2.1717 | 4 | 6159.7553 | 10773.6973 | 125.5749 | 219.6364 | 256.6593 | 0 | 68.4584 | 3705463.6391 | 237309.9402 | 3117294.3695 | 1206597.4432 | 0 | 0 | 0 | 3223999.5029 | 8388185.3734 | 5725108.8773 | 25603959.1457 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 53507862.5609 | 93587730.571 | 3162.2777 | 8.6867 | 6159.7553 | 10773.6973 | 125.5749 | 219.6364
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.5757 | 22.2151 | 2.8854 | 4 | 5184.7738 | 8657.4584 | 105.6986 | 176.494 | 258.7955 | 0 | 100.3757 | 4532606.3382 | 289534.7399 | 3912940.498 | 1575982.545 | 0 | 0 | 0 | 4021315.0072 | 10462636.7636 | 7140964.5768 | 31935980.4687 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 59839883.8839 | 99919751.894 | 4216.965 | 11.5415 | 5184.7738 | 8657.4584 | 105.6986 | 176.494
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.2311 | 29.4409 | 3.8239 | 4 | 4426.7005 | 7047.0662 | 90.2443 | 143.664 | 260.4472 | 0 | 74.9623 | 5535853.8184 | 352625.0017 | 4901691.9114 | 2061474.9323 | 0 | 0 | 0 | 5012141.8089 | 13040564.8551 | 8900453.4704 | 39804805.7981 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 67708709.2133 | 107788577.2235 | 5623.4133 | 15.2955 | 4426.7005 | 7047.0662 | 90.2443 | 143.664
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.8816 | 38.8383 | 5.0444 | 4 | 3835.7173 | 5822.0581 | 78.1963 | 118.6905 | 261.7069 | 0 | 84.2424 | 6740824.1292 | 428083.7999 | 6117761.1294 | 2692714.4846 | 0 | 0 | 0 | 6231959.5818 | 16214280.4813 | 11066579.5986 | 49492203.2049 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 77396106.6201 | 117475974.6302 | 7498.9421 | 20.1777 | 3835.7173 | 5822.0581 | 78.1963 | 118.6905
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.9559 | 50.863 | 6.6062 | 4 | 3373.946 | 4890.6885 | 68.7825 | 99.7033 | 262.6347 | 0 | 67.4416 | 8167556.5364 | 517044.7396 | 7591123.1467 | 3500667.5164 | 0 | 0 | 0 | 7712792.8562 | 20067104.9006 | 13696211.4324 | 61252501.1283 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 89156404.5435 | 129236272.5537 | 10000 | 26.425 | 3373.946 | 4890.6885 | 68.7825 | 99.7033
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.7654 | 65.7921 | 8.5453 | 4 | 3015.0176 | 4187.5901 | 61.4652 | 85.3697 | 263.1922 | 0 | 106.9558 | 9811631.7725 | 619111.1763 | 9326609.0833 | 4506998.8673 | 0 | 0 | 0 | 9463096.8508 | 24621036.8577 | 16804363.5671 | 75152848.1752 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 103056751.5904 | 143136619.6005 | 13335.2143 | 34.1811 | 3015.0176 | 4187.5901 | 61.4652 | 85.3697
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.2117 | 83.3239 | 10.8224 | 4 | 2741.6991 | 3667.5564 | 55.8932 | 74.7681 | 263.2128 | 0 | 85.9425 | 11612585.3263 | 730441.727 | 11266791.7248 | 5700916.2552 | 0 | 0 | 0 | 11431186.663 | 29741602.8384 | 20299255.066 | 90782779.6007 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 118686683.0159 | 158766551.0261 | 17782.7941 | 43.2895 | 2741.6991 | 3667.5564 | 55.8932 | 74.7681
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.6453 | 102.4211 | 13.3028 | 4 | 2539.4151 | 3292.6392 | 51.7694 | 67.1249 | 262.53 | 0 | 93.9228 | 13456131.633 | 843955.3327 | 13289117.3682 | 7028919.3368 | 0 | 0 | 0 | 13501068.2316 | 35127010.0887 | 23974906.1734 | 107221108.1646 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 135125011.5798 | 175204879.5899 | 23713.7371 | 53.2111 | 2539.4151 | 3292.6392 | 51.7694 | 67.1249
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.9654 | 121.5803 | 15.7912 | 4 | 2393.8265 | 3028.3539 | 48.8014 | 61.7371 | 261.1363 | 0 | 111.7495 | 15210337.3276 | 951592.7933 | 15243166.8354 | 8404988.6201 | 0 | 0 | 0 | 15525933.3748 | 40395293.8345 | 27570618.0823 | 123301930.8682 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 151205834.2834 | 191285702.2935 | 31622.7766 | 63.1649 | 2393.8265 | 3028.3539 | 48.8014 | 61.7371
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.7816 | 139.2287 | 18.0835 | 4 | 2292.0818 | 2846.1775 | 46.7272 | 58.0232 | 259.2173 | 0 | 113.6267 | 16758324.8404 | 1046302.0705 | 16988995.694 | 9726843.0506 | 0 | 0 | 0 | 17362981.6057 | 45174916.5007 | 30832808.7634 | 137891172.5253 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 165795075.9405 | 205874943.9506 | 42169.6503 | 72.3338 | 2292.0818 | 2846.1775 | 46.7272 | 58.0232
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.148 | 154.8325 | 20.1101 | 4 | 2219.7003 | 2717.955 | 45.2516 | 55.4092 | 257.2784 | 0 | 123.0951 | 18081499.9162 | 1127068.7301 | 18495852.4876 | 10935418.3912 | 0 | 0 | 0 | 18969537.4148 | 49354845.1661 | 33685695.9665 | 150649918.0724 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 178553821.4876 | 218633689.4978 | 56234.1325 | 80.4405 | 2219.7003 | 2717.955 | 45.2516 | 55.4092
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.3226 | 167.8724 | 21.8038 | 4 | 2168.8821 | 2628.4337 | 44.2156 | 53.5842 | 255.4422 | 0 | 66.1626 | 19158736.8234 | 1192703.2842 | 19731862.655 | 11980724.3431 | 0 | 0 | 0 | 20304970.5712 | 52829368.3041 | 36057129.4025 | 161255495.3836 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 189159398.7988 | 229239266.8089 | 74989.4209 | 87.2152 | 2168.8821 | 2628.4337 | 44.2156 | 53.5842
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 242.2398 | 222.6333 | 28.6093 | 4 | 2061.873 | 2412.108 | 42.0341 | 49.1741 | 244.2121 | 0 | 104.7619 | 23452018.3842 | 1453316.1385 | 24731864.7193 | 16989744.7128 | 0 | 545748.2815 | 0 | 26197349.9722 | 68160130.8122 | 46520689.8299 | 208050862.8505 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 235954766.2658 | 276034634.2759 | 100000 | 114.4371 | 2061.873 | 2412.108 | 42.0341 | 49.1741
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 245.9204 | 224.8374 | 28.9293 | 4 | 2054.3174 | 2400.6779 | 41.88 | 48.9411 | 243.5516 | 0 | 119.8029 | 23618161.4663 | 1463372.5082 | 24927543.6737 | 17228239.6762 | 0 | 505272.047 | 0 | 26419609.8548 | 68738405.4351 | 46915374.1425 | 209815978.8039 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 237719882.2191 | 277799750.2292 | 133352.1432 | 115.7172 | 2054.3174 | 2400.6779 | 41.88 | 48.9411
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 248.6996 | 226.4709 | 29.1686 | 4 | 2048.6428 | 2392.1616 | 41.7644 | 48.7675 | 243.0472 | 0 | 148.4884 | 23741011.0953 | 1470807.0894 | 25072330.9491 | 17407979.5745 | 0 | 471601.8984 | 0 | 26583854.9366 | 69165737.4465 | 47207037.021 | 211120360.0108 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 239024263.426 | 279104131.4361 | 177827.941 | 116.6744 | 2048.6428 | 2392.1616 | 41.7644 | 48.7675
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 250.8675 | 227.7273 | 29.3525 | 4 | 2044.3761 | 2385.7432 | 41.6774 | 48.6366 | 242.6509 | 0 | 178.4065 | 23835322.5747 | 1476513.8563 | 25183540.297 | 17547894.7471 | 0 | 445156.9098 | 0 | 26710487.0702 | 69495208.2823 | 47431907.6364 | 212126031.3738 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 240029934.789 | 280109802.7991 | 237137.3706 | 117.4099 | 2044.3761 | 2385.7432 | 41.6774 | 48.6366
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 252.4534 | 228.6356 | 29.487 | 4 | 2041.1687 | 2380.9782 | 41.612 | 48.5395 | 242.3587 | 0 | 188.5707 | 23903420.1099 | 1480634.0196 | 25263869.2516 | 17650178.0364 | 0 | 423418.3889 | 0 | 26801392.7245 | 69731726.1475 | 47593335.9394 | 212847974.6178 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 240751878.033 | 280831746.0431 | 316227.766 | 117.9481 | 2041.1687 | 2380.9782 | 41.612 | 48.5395
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 253.8681 | 229.4423 | 29.6027 | 4 | 2038.7325 | 2377.2135 | 41.5623 | 48.4627 | 242.0987 | 0 | 222.6927 | 23963831.3619 | 1484288.8505 | 25335152.5672 | 17741461.7029 | 0 | 408735.6338 | 0 | 26884053.3454 | 69946792.1271 | 47740122.8896 | 213504438.4784 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 241408341.8936 | 281488209.9037 | 421696.5034 | 118.411 | 2038.7325 | 2377.2135 | 41.5623 | 48.4627
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 254.8576 | 229.9998 | 29.6838 | 4 | 2036.9571 | 2374.5137 | 41.5261 | 48.4077 | 241.9148 | 0 | 234.2871 | 24005545.5548 | 1486812.37 | 25384385.5814 | 17805147.2576 | 0 | 396956.3414 | 0 | 26940750.371 | 70094306.1577 | 47840804.2466 | 213954707.8806 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 241858611.2958 | 281938479.3059 | 562341.3252 | 118.7353 | 2036.9571 | 2374.5137 | 41.5261 | 48.4077
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 255.3569 | 230.2778 | 29.729 | 4 | 2035.5807 | 2372.624 | 41.4981 | 48.3691 | 241.8207 | 0 | 245.4616 | 24026339.4373 | 1488070.2585 | 25408931.0205 | 17837192.1823 | 0 | 384397.8032 | 0 | 26966522.9737 | 70161361.1831 | 47886570.6793 | 214159385.538 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242063288.9532 | 282143156.9633 | 749894.2093 | 118.9161 | 2035.5807 | 2372.624 | 41.4981 | 48.3691
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 255.8755 | 230.5677 | 29.7722 | 4 | 2034.5564 | 2371.1108 | 41.4772 | 48.3383 | 241.724 | 0 | 297.5603 | 24048012.5363 | 1489381.3002 | 25434516.8051 | 17870504.198 | 0 | 376660.6847 | 0 | 26995439.4545 | 70236595.9345 | 47937919.943 | 214389030.8563 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242292934.2716 | 282372802.2817 | 1000000 | 119.0888 | 2034.5564 | 2371.1108 | 41.4772 | 48.3383
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 256.2628 | 230.7836 | 29.8044 | 4 | 2033.7872 | 2369.9775 | 41.4615 | 48.3152 | 241.6516 | 0 | 341.6876 | 24064146.1829 | 1490357.2292 | 25453564.7476 | 17895378.5178 | 0 | 370732.6487 | 0 | 27016929.9372 | 70292509.7622 | 47976082.2794 | 214559701.305 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242463604.7202 | 282543472.7303 | 1333521.4322 | 119.2178 | 2033.7872 | 2369.9775 | 41.4615 | 48.3152
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 256.5601 | 230.949 | 29.829 | 4 | 2033.2097 | 2369.1228 | 41.4497 | 48.2978 | 241.596 | 0 | 247.8876 | 24076507.5452 | 1491104.9588 | 25468159.9575 | 17914472.2579 | 0 | 366308.2006 | 0 | 27033455.6388 | 70335506.2479 | 48005428.2643 | 214690943.071 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242594846.4863 | 282674714.4964 | 1778279.41 | 119.3162 | 2033.2097 | 2369.1228 | 41.4497 | 48.2978
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 256.7398 | 231.0484 | 29.8447 | 4 | 2032.7764 | 2368.5136 | 41.4409 | 48.2854 | 241.5621 | 0 | 267.8368 | 24083930.9391 | 1491553.9891 | 25476925.2472 | 17926009.1963 | 0 | 362436.4227 | 0 | 27042933.7598 | 70360166.3745 | 48022259.3074 | 214766215.2361 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242670118.6513 | 282749986.6614 | 2371373.7057 | 119.3787 | 2032.7764 | 2368.5136 | 41.4409 | 48.2854
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 256.9284 | 231.1533 | 29.8599 | 4 | 2032.4511 | 2368.0173 | 41.4343 | 48.2752 | 241.527 | 0 | 379.4952 | 24091768.7287 | 1492028.0813 | 25486180.1658 | 17938124.2963 | 0 | 360158.9576 | 0 | 27053621.4896 | 70387973.655 | 48041238.3478 | 214851093.722 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242754997.1373 | 282834865.1474 | 3162277.6602 | 119.4395 | 2032.4511 | 2368.0173 | 41.4343 | 48.2752
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 257.0223 | 231.2013 | 29.868 | 4 | 2032.1885 | 2367.6632 | 41.4289 | 48.268 | 241.5072 | 0 | 358.2742 | 24095357.0484 | 1492245.13 | 25490417.391 | 17944090.0503 | 0 | 357411.4376 | 0 | 27058013.2123 | 70399400.0168 | 48049037.0745 | 214885971.3609 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 242789874.7761 | 282869742.7863 | 4216965.0343 | 119.4721 | 2032.1885 | 2367.6632 | 41.4289 | 48.268
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 257.7922 | 231.6354 | 29.9198 | 4 | 2032.0119 | 2366.9066 | 41.4253 | 48.2526 | 241.3673 | 0 | 363.3028 | 24127771.3816 | 1494205.7524 | 25528696.6404 | 17993666.853 | 0 | 364095.4573 | 0 | 27108290.073 | 70530210.0951 | 48138317.6408 | 215285253.8937 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 243189157.3089 | 283269025.319 | 5623413.2519 | 119.679 | 2032.0119 | 2366.9066 | 41.4253 | 48.2526
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 258.287 | 231.9137 | 29.953 | 4 | 2031.889 | 2366.4118 | 41.4228 | 48.2425 | 241.2774 | 0 | 382.3804 | 24148546.9395 | 1495462.3486 | 25553234.2374 | 18025526.2149 | 0 | 368207.6786 | 0 | 27140481.1934 | 70613964.7871 | 48195481.9391 | 215540905.3386 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 243444808.7538 | 283524676.7639 | 7498942.0933 | 119.8121 | 2031.889 | 2366.4118 | 41.4228 | 48.2425
1 | 6600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 258.3038 | 231.9252 | 29.9552 | 4 | 2031.7987 | 2366.2977 | 41.421 | 48.2402 | 241.2755 | 0 | 507.7399 | 24149405.1902 | 1495514.2587 | 25554247.9504 | 18026643.166 | 0 | 367289.8635 | 0 | 27141309.1673 | 70616119.0052 | 48196952.2372 | 215547480.8385 | 961560.8286 | 26942342.5866 | 26942342.5866 | 1478867.319 | 11658658.1045 | 0 | 243451384.2537 | 283531252.2638 | 10000000 | 119.8206 | 2031.7987 | 2366.2977 | 41.421 | 48.2402
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3982 | 0.65099 | 0.07531 | 4 | 102897.2992 | 238702.8314 | 2097.7006 | 4866.2801 | 178.8297 | 0 | 51.2671 | 378269.0568 | 24423.3385 | 232314.3107 | 108567.0205 | 0 | 63554.0889 | 0 | 314779.848 | 818992.5943 | 558979.2742 | 2499879.5319 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 30996673.4543 | 71906588.1746 | 100 | 0.30124 | 102897.2992 | 238702.8314 | 2097.7006 | 4866.2801
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 1.0368 | 0.12464 | 4 | 63989.5903 | 146043.4044 | 1304.5144 | 2977.2923 | 194.7377 | 0 | 255.6329 | 523626.726 | 33886.3717 | 337078.5505 | 138734.3041 | 0 | 66604.9227 | 0 | 428973.0412 | 1116099.8588 | 761761.0872 | 3406764.8622 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 31903558.7846 | 72813473.5048 | 133.3521 | 0.49857 | 63989.5903 | 146043.4044 | 1304.5144 | 2977.2923
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 1.5689 | 0.19249 | 4 | 42893.9794 | 96025.8013 | 874.4518 | 1957.6158 | 209.2006 | 0 | 329.7801 | 699622.1151 | 45285.9408 | 469527.0651 | 177148.8443 | 0 | 71095.1207 | 0 | 570444.8435 | 1484180.4686 | 1012983.6667 | 4530288.0648 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 33027081.9872 | 73936996.7074 | 177.8279 | 0.76997 | 42893.9794 | 96025.8013 | 874.4518 | 1957.6158
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9544 | 2.2348 | 0.27816 | 4 | 30831.4981 | 67600.2871 | 628.5418 | 1378.1233 | 220.8202 | 0 | 423.5967 | 896489.4705 | 58010.6297 | 623115.0951 | 223408.5656 | 0 | 73906.9139 | 0 | 731222.9632 | 1902492.1557 | 1298489.9886 | 5807135.7823 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 34303929.7047 | 75213844.4249 | 237.1374 | 1.1126 | 30831.4981 | 67600.2871 | 628.5418 | 1378.1233
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7559 | 3.0836 | 0.38801 | 4 | 23068.9655 | 49427.6413 | 470.2921 | 1007.6493 | 230.3089 | 0 | 72.9475 | 1123890.0219 | 72675.4037 | 806178.0773 | 281311.1838 | 0 | 75240.1504 | 0 | 920124.9864 | 2393976.4711 | 1633938.1328 | 7307334.4273 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 35804128.3498 | 76714043.07 | 316.2278 | 1.552 | 23068.9655 | 49427.6413 | 470.2921 | 1007.6493
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7816 | 4.1871 | 0.5313 | 4 | 17700.0671 | 36949.8702 | 360.8398 | 753.2731 | 238.1544 | 0 | 83.1502 | 1393666.4482 | 90030.0391 | 1029714.1535 | 355640.8391 | 0 | 75364.4442 | 0 | 1148322.2104 | 2987698.8381 | 2039165.8481 | 9119602.8206 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 37616396.743 | 78526311.4632 | 421.6965 | 2.1252 | 17700.0671 | 36949.8702 | 360.8398 | 753.2731
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1117 | 5.6338 | 0.71955 | 4 | 13840.3025 | 28054.056 | 282.1533 | 571.9199 | 244.5899 | 0 | 83.7867 | 1717675.6046 | 110817.6223 | 1305650.2042 | 452392.0766 | 0 | 74209.9816 | 0 | 1427690.7409 | 3714558.4481 | 2535262.4673 | 11338257.1456 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 39835051.0681 | 80744965.7883 | 562.3413 | 2.8782 | 13840.3025 | 28054.056 | 282.1533 | 571.9199
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8368 | 7.5139 | 0.96442 | 4 | 11027.2616 | 21632.0534 | 224.8056 | 440.9987 | 249.6027 | 0 | 92.44 | 2104541.5533 | 135566.3764 | 1643902.9203 | 578091.3515 | 0 | 71874.3629 | 0 | 1768250.8601 | 4600626.02 | 3140021.792 | 14042875.2366 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 42539669.159 | 83449583.8792 | 749.8942 | 3.8577 | 11027.2616 | 21632.0534 | 224.8056 | 440.9987
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1212 | 10.0558 | 1.2964 | 4 | 8862.5393 | 16751.3907 | 180.6749 | 341.4998 | 254.1806 | 0 | 96.9358 | 2585541.1665 | 166240.6727 | 2075470.2351 | 745611.7579 | 0 | 65182.8193 | 0 | 2198838.1941 | 5720925.9373 | 3904649.5055 | 17462460.2884 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 45959254.2108 | 86869168.9311 | 1000 | 5.1858 | 8862.5393 | 16751.3907 | 180.6749 | 341.4998
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1032 | 13.3657 | 1.7289 | 4 | 7251.5429 | 13167.1631 | 147.8325 | 268.4304 | 257.5825 | 0 | 105.8324 | 3162043.9171 | 202881.3604 | 2606028.78 | 964333.9835 | 0 | 55354.9197 | 0 | 2726350.7547 | 7093405.4123 | 4841394.9488 | 21651794.0765 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 50148587.9989 | 91058502.7192 | 1333.5214 | 6.9156 | 7251.5429 | 13167.1631 | 147.8325 | 268.4304
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0474 | 17.7557 | 2.3027 | 4 | 6011.6045 | 10453.0496 | 122.5547 | 213.0996 | 260.285 | 0 | 88.3463 | 3866671.1169 | 247504.6169 | 3270806.2174 | 1253957.1239 | 0 | 38353.5389 | 0 | 3384144.1195 | 8804848.8154 | 6009490.2381 | 26875775.7869 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 55372569.7094 | 96282484.4296 | 1778.2794 | 9.2109 | 6011.6045 | 10453.0496 | 122.5547 | 213.0996
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1226 | 13.3853 | 1.7385 | 4 | 7190.2536 | 13073.1121 | 146.583 | 266.5131 | 257.5796 | 0 | 91.9609 | 3165314.61 | 203088.881 | 2609075.4258 | 965724.1248 | 0 | 0 | 0 | 2707849.1862 | 7045268.1263 | 4808540.262 | 21504860.6162 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 50001654.5387 | 90911569.2589 | 2371.3737 | 6.9541 | 7190.2536 | 13073.1121 | 146.583 | 266.5131
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.1252 | 17.8381 | 2.3169 | 4 | 5972.5713 | 10386.92 | 121.7589 | 211.7514 | 260.2952 | 0 | 82.5692 | 3879386.5181 | 248308.3848 | 3282948.3441 | 1259594.9722 | 0 | 0 | 0 | 3381392.9055 | 8797690.721 | 6004604.6915 | 26853926.5372 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 55350720.4596 | 96260635.1798 | 3162.2777 | 9.2675 | 5972.5713 | 10386.92 | 121.7589 | 211.7514
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.3721 | 23.6856 | 3.0764 | 4 | 5036.7341 | 8361.2765 | 102.6806 | 170.4559 | 262.401 | 0 | 89.2418 | 4743531.483 | 302820.8067 | 4118810.8847 | 1645178.6323 | 0 | 0 | 0 | 4216033.3046 | 10969253.8312 | 7486741.1354 | 33482370.0779 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 61979164.0004 | 102889078.7206 | 4216.965 | 12.3054 | 5036.7341 | 8361.2765 | 102.6806 | 170.4559
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.2595 | 31.3691 | 4.0743 | 4 | 4308.1438 | 6818.3743 | 87.8273 | 139.0018 | 264.0285 | 0 | 68.4827 | 5791101.8707 | 368636.6566 | 5156873.6139 | 2151516.503 | 0 | 0 | 0 | 5252570.1712 | 13666110.1352 | 9327400.9778 | 41714209.9284 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 70211003.8509 | 111120918.5711 | 5623.4133 | 16.2973 | 4308.1438 | 6818.3743 | 87.8273 | 139.0018
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.2117 | 41.3617 | 5.3722 | 4 | 3739.0058 | 5642.7882 | 76.2247 | 115.0359 | 265.2691 | 0 | 76.2201 | 7049579.8115 | 447369.0304 | 6433740.1121 | 2809880.2049 | 0 | 0 | 0 | 6528821.972 | 16986655.5256 | 11593741.4371 | 51849788.0936 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 80346582.016 | 121256496.7362 | 7498.9421 | 21.4888 | 3739.0058 | 5642.7882 | 76.2247 | 115.0359
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.6468 | 54.1164 | 7.0288 | 4 | 3294.4042 | 4749.4832 | 67.1609 | 96.8246 | 266.1723 | 0 | 88.0597 | 8536358.7366 | 539979.714 | 7977156.5938 | 3650725.2653 | 0 | 0 | 0 | 8074645.9208 | 21008572.3482 | 14338782.3107 | 64126220.8894 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 92623014.8118 | 133532929.5321 | 10000 | 28.1153 | 3294.4042 | 4749.4832 | 67.1609 | 96.8246
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.8459 | 69.8688 | 9.0748 | 4 | 2949.478 | 4076.501 | 60.1291 | 83.105 | 266.6807 | 0 | 101.8691 | 10241403.8455 | 645721.2471 | 9786133.2709 | 4693274.2788 | 0 | 0 | 0 | 9892947.7305 | 25739420.6721 | 17567683.5009 | 78566584.5457 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 107063378.4681 | 147973293.1883 | 13335.2143 | 36.2991 | 2949.478 | 4076.501 | 60.1291 | 83.105
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.6742 | 88.2376 | 11.4606 | 4 | 2687.4425 | 3579.8482 | 54.7872 | 72.98 | 266.6121 | 0 | 109.7099 | 12097379.5705 | 760333.9872 | 11795259.4946 | 5923053.7756 | 0 | 0 | 0 | 11924650.4629 | 31025494.4223 | 21175537.4534 | 94701709.1665 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 123198503.0889 | 164108417.8091 | 17782.7941 | 45.8423 | 2687.4425 | 3579.8482 | 54.7872 | 72.98
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.4226 | 108.0662 | 14.036 | 4 | 2494.1619 | 3222.8233 | 50.8469 | 65.7016 | 265.8055 | 0 | 101.7707 | 13981917.0813 | 876253.8971 | 13871924.2755 | 7280917.8229 | 0 | 0 | 0 | 14044295.0999 | 36540374.9689 | 24939556.7459 | 111535239.8914 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 140032033.8138 | 180941948.5341 | 23713.7371 | 56.1439 | 2494.1619 | 3222.8233 | 50.8469 | 65.7016
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.9085 | 127.7288 | 16.5898 | 4 | 2355.794 | 2972.2853 | 48.026 | 60.5941 | 264.2788 | 0 | 111.2784 | 15756384.3493 | 985029.3263 | 15856808.9216 | 8674466.2848 | 0 | 0 | 0 | 16096348.664 | 41879397.4086 | 28583549.267 | 127831984.2217 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 156328778.1441 | 197238692.8643 | 31622.7766 | 66.3593 | 2355.794 | 2972.2853 | 48.026 | 60.5941
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7831 | 145.6866 | 18.9222 | 4 | 2259.3435 | 2799.8441 | 46.0598 | 57.0786 | 262.236 | 0 | 119.4081 | 17310744.7313 | 1080042.1501 | 17616531.912 | 10004576.2381 | 0 | 0 | 0 | 17944639.0623 | 46688269.8885 | 31865703.5469 | 142510507.5294 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 171007301.4518 | 211917216.172 | 42169.6503 | 75.6889 | 2259.3435 | 2799.8441 | 46.0598 | 57.0786
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1689 | 161.5797 | 20.9865 | 4 | 2190.1274 | 2677.4641 | 44.6487 | 54.5837 | 260.2559 | 0 | 133.6474 | 18641937.4197 | 1161228.4647 | 19137891.7101 | 11218033.6559 | 0 | 0 | 0 | 19562045.5877 | 50896429.8918 | 34737859.2182 | 155355425.9482 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 183852219.8706 | 224762134.5908 | 56234.1325 | 83.9459 | 2190.1274 | 2677.4641 | 44.6487 | 54.5837
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2721 | 174.7253 | 22.6939 | 4 | 2141.9571 | 2592.6286 | 43.6667 | 52.8542 | 258.3565 | 0 | 132.1648 | 19715409.9877 | 1226580.2704 | 20373671.2867 | 12260953.3424 | 0 | 0 | 0 | 20894879.806 | 54364191.126 | 37104677.5159 | 165940363.335 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 194437157.2574 | 235347071.9776 | 74989.4209 | 90.7755 | 2141.9571 | 2592.6286 | 43.6667 | 52.8542
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.8863 | 185.1978 | 24.0541 | 4 | 2108.5113 | 2533.6983 | 42.9849 | 51.6529 | 256.6411 | 0 | 85.7126 | 20554463.6562 | 1277591.7589 | 21344866.3576 | 13123400.6925 | 0 | 0 | 0 | 21957125.7614 | 57127937.2054 | 38990991.0044 | 174376376.4364 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 202873170.3589 | 243783085.0791 | 100000 | 96.2163 | 2108.5113 | 2533.6983 | 42.9849 | 51.6529
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.0884 | 193.3181 | 25.1088 | 4 | 2085.2393 | 2492.5665 | 42.5104 | 50.8143 | 255.172 | 0 | 116.1512 | 21195926.8731 | 1316550.9812 | 22090353.897 | 13814820.1442 | 0 | 0 | 0 | 22782884.2393 | 59276391.3784 | 40457355.1238 | 180934282.637 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 209431076.5595 | 250340991.2797 | 133352.1432 | 100.435 | 2085.2393 | 2492.5665 | 42.5104 | 50.8143
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 252.0176 | 233.9519 | 30.1786 | 4 | 2023.7015 | 2362.6003 | 41.2559 | 48.1648 | 245.4819 | 0 | 193.9115 | 24300466.4459 | 1504650.1572 | 25732734.2522 | 17712458.6201 | 0 | 422005.6168 | 0 | 27172202.8859 | 70696498.124 | 48251812.6374 | 215792828.7394 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 244289622.6618 | 285199537.382 | 177827.941 | 120.7143 | 2023.7015 | 2362.6003 | 41.2559 | 48.1648
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 254.1829 | 235.2031 | 30.3578 | 4 | 2020.0724 | 2356.9708 | 41.1819 | 48.05 | 245.0729 | 0 | 275.1845 | 24393550.0624 | 1510278.8619 | 25842778.3408 | 17852199.8846 | 0 | 399539.9491 | 0 | 27299355.3685 | 71027322.8012 | 48477607.2773 | 216802632.5458 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 245299426.4682 | 286209341.1885 | 237137.3706 | 121.431 | 2020.0724 | 2356.9708 | 41.1819 | 48.05
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 255.9151 | 236.1926 | 30.4984 | 4 | 2017.3464 | 2352.6911 | 41.1263 | 47.9628 | 244.7443 | 0 | 321.18 | 24467058.4266 | 1514723.426 | 25929713.2852 | 17963630.0314 | 0 | 382790.47 | 0 | 27400587.0992 | 71290706.999 | 48657372.4044 | 217606582.1417 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 246103376.0641 | 287013290.7844 | 316227.766 | 121.9936 | 2017.3464 | 2352.6911 | 41.1263 | 47.9628
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 257.3176 | 236.9873 | 30.6103 | 4 | 2015.2921 | 2349.411 | 41.0845 | 47.8959 | 244.4776 | 0 | 362.6702 | 24526041.2884 | 1518289.4503 | 25999490.4942 | 18053776.7761 | 0 | 370618.4164 | 0 | 27482604.4059 | 71504099.2068 | 48803016.9709 | 218257937.009 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 246754730.9314 | 287664645.6516 | 421696.5034 | 122.4412 | 2015.2921 | 2349.411 | 41.0845 | 47.8959
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 258.2452 | 237.5063 | 30.6852 | 4 | 2013.7864 | 2347.0899 | 41.0538 | 47.8486 | 244.299 | 0 | 623.1876 | 24564528.4407 | 1520616.198 | 26045031.1238 | 18113338.4702 | 0 | 359949.2259 | 0 | 27535350.7489 | 71641334.3715 | 48896682.7908 | 218676831.3698 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 247173625.2922 | 288083540.0124 | 562341.3252 | 122.7407 | 2013.7864 | 2347.0899 | 41.0538 | 47.8486
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 258.8186 | 237.8257 | 30.7338 | 4 | 2012.6102 | 2345.3868 | 41.0298 | 47.8139 | 244.1884 | 0 | 415.3177 | 24588201.965 | 1522047.3329 | 26073047.178 | 18150153.5548 | 0 | 349679.8421 | 0 | 27566420.6504 | 71722171.8819 | 48951856.0527 | 218923578.4578 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 247420372.3802 | 288330287.1005 | 749894.2093 | 122.9351 | 2012.6102 | 2345.3868 | 41.0298 | 47.8139
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 259.3593 | 238.1267 | 30.7772 | 4 | 2011.7444 | 2344.0515 | 41.0121 | 47.7867 | 244.0843 | 0 | 382.8107 | 24610503.4607 | 1523395.4882 | 26099442.2563 | 18184879.3672 | 0 | 343351.7625 | 0 | 27597013.2106 | 71801767.4481 | 49006181.6621 | 219166534.6556 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 247663328.578 | 288573243.2982 | 1000000 | 123.1087 | 2011.7444 | 2344.0515 | 41.0121 | 47.7867
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 259.8346 | 238.3913 | 30.8143 | 4 | 2011.0946 | 2343.0017 | 40.9989 | 47.7653 | 243.9932 | 0 | 268.2856 | 24630102.1305 | 1524580.2248 | 26122640.5721 | 18215406.917 | 0 | 339341.4775 | 0 | 27624507.8156 | 71873302.7705 | 49055005.9895 | 219384887.8977 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 247881681.8201 | 288791596.5404 | 1333521.4322 | 123.2571 | 2011.0946 | 2343.0017 | 40.9989 | 47.7653
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 260.1681 | 238.576 | 30.8405 | 4 | 2010.606 | 2342.2307 | 40.9889 | 47.7495 | 243.929 | 0 | 334.6011 | 24643780.5864 | 1525407.0693 | 26138832.5308 | 18236741.0645 | 0 | 336007.3302 | 0 | 27643499.7466 | 71922715.8793 | 49088731.4516 | 219535715.6587 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248032509.5811 | 288942424.3013 | 1778279.41 | 123.3621 | 2010.606 | 2342.2307 | 40.9889 | 47.7495
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.0371 | 239.0588 | 30.9003 | 4 | 2010.2235 | 2341.2063 | 40.9811 | 47.7287 | 243.7633 | 0 | 387.3694 | 24679510.9642 | 1527566.8606 | 26181133.2801 | 18292366.1951 | 0 | 340263.7136 | 0 | 27698127.9953 | 72064847.3765 | 49185739.119 | 219969555.5044 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248466349.4269 | 289376264.1471 | 2371373.7057 | 123.6014 | 2010.2235 | 2341.2063 | 40.9811 | 47.7287
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.8265 | 239.5031 | 30.9541 | 4 | 2009.991 | 2340.399 | 40.9764 | 47.7122 | 243.6166 | 0 | 427.3839 | 24712382.0573 | 1529553.737 | 26220054.9404 | 18343024.1416 | 0 | 346080.8483 | 0 | 27748927.3326 | 72197016.8317 | 49275947.488 | 220372987.3769 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248869781.2993 | 289779696.0196 | 3162277.6602 | 123.8164 | 2009.991 | 2340.399 | 40.9764 | 47.7122
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.8802 | 239.5383 | 30.9597 | 4 | 2009.8208 | 2340.1687 | 40.9729 | 47.7075 | 243.6093 | 0 | 482.8852 | 24714986.4457 | 1529711.1547 | 26223138.9623 | 18346553.8594 | 0 | 344526.5335 | 0 | 27751977.6127 | 72204953.0349 | 49281364.1097 | 220397211.7129 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248894005.6354 | 289803920.3556 | 4216965.0343 | 123.8389 | 2009.8208 | 2340.1687 | 40.9729 | 47.7075
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.9339 | 239.5721 | 30.9648 | 4 | 2009.6926 | 2339.9861 | 40.9703 | 47.7038 | 243.6012 | 0 | 475.7122 | 24717487.2056 | 1529862.3083 | 26226100.3049 | 18350060.6889 | 0 | 343496.8631 | 0 | 27755132.8746 | 72213162.3792 | 49286967.1559 | 220422269.7805 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248919063.7029 | 289828978.4231 | 5623413.2519 | 123.8593 | 2009.6926 | 2339.9861 | 40.9703 | 47.7038
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.9728 | 239.5967 | 30.9686 | 4 | 2009.596 | 2339.8497 | 40.9683 | 47.701 | 243.5954 | 0 | 486.4051 | 24719305.526 | 1529972.2128 | 26228253.5391 | 18352601.8301 | 0 | 342702.692 | 0 | 27757405.962 | 72219076.4863 | 49291003.6555 | 220440321.9037 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248937115.8262 | 289847030.5464 | 7498942.0933 | 123.8742 | 2009.596 | 2339.8497 | 40.9683 | 47.701
1 | 6700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.9922 | 239.6098 | 30.9707 | 4 | 2009.5234 | 2339.7539 | 40.9669 | 47.699 | 243.5929 | 0 | 488.9889 | 24720272.2273 | 1530030.6429 | 26229398.3028 | 18353885.1783 | 0 | 341996.4564 | 0 | 27758477.295 | 72221863.875 | 49292906.1056 | 220448830.0835 | 961560.8286 | 27535233.0938 | 27535233.0938 | 1478867.319 | 11895814.3074 | 0 | 248945624.0059 | 289855538.7261 | 10000000 | 123.8829 | 2009.5234 | 2339.7539 | 40.9669 | 47.699
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.68575 | 0.080166 | 4 | 98784.688 | 228977.9394 | 2013.8595 | 4668.025 | 181.2603 | 0 | 56.3872 | 392406.5771 | 25372.4341 | 242167.7652 | 110909.5842 | 0 | 62480.3614 | 0 | 325001.3216 | 845586.7719 | 577130.3469 | 2581055.1624 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 31676599.6829 | 73424765.2404 | 100 | 0.32066 | 98784.688 | 228977.9394 | 2013.8595 | 4668.025
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 1.1186 | 0.13517 | 4 | 60439.8681 | 137655.3432 | 1232.1485 | 2806.2904 | 198.5092 | 0 | 194.9944 | 552171.8229 | 35736.8446 | 358196.2092 | 143601.315 | 0 | 66975.7593 | 0 | 451105.9609 | 1173685.1757 | 801064.2492 | 3582537.3368 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 32678081.8573 | 74426247.4149 | 133.3521 | 0.54067 | 60439.8681 | 137655.3432 | 1232.1485 | 2806.2904
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 1.663 | 0.20497 | 4 | 41230.0154 | 92150.4297 | 840.5296 | 1878.6112 | 212.627 | 0 | 266.2641 | 728744.3375 | 47170.0435 | 491917.7539 | 181942.7933 | 0 | 70199.0985 | 0 | 592789.8704 | 1542317.6449 | 1052663.4841 | 4707745.0263 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 33803289.5468 | 75551455.1043 | 177.8279 | 0.81987 | 41230.0154 | 92150.4297 | 840.5296 | 1878.6112
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0128 | 2.345 | 0.29316 | 4 | 29922.8603 | 65525.2855 | 610.018 | 1335.8216 | 224.0681 | 0 | 343.278 | 927294.4305 | 59999.2502 | 647586.361 | 228368.8341 | 0 | 71575.5035 | 0 | 754581.5079 | 1963266.2977 | 1339969.5892 | 5992641.7741 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 35088186.2946 | 76836351.8521 | 237.1374 | 1.1726 | 29922.8603 | 65525.2855 | 610.018 | 1335.8216
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8459 | 3.2497 | 0.41047 | 4 | 22329.837 | 47756.5809 | 455.2239 | 973.5825 | 233.7762 | 0 | 66.3469 | 1166112.6872 | 75394.5485 | 840741.342 | 288912.2572 | 0 | 72232.9847 | 0 | 952923.5896 | 2479311.7088 | 1692181.186 | 7567810.304 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 36663354.8245 | 78411520.3821 | 316.2278 | 1.6419 | 22329.837 | 47756.5809 | 455.2239 | 973.5825
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8937 | 4.4064 | 0.56117 | 4 | 17165.7152 | 35764.4717 | 349.9463 | 729.1071 | 241.6298 | 0 | 68.5135 | 1444646.766 | 93304.692 | 1072628.4333 | 365342.2476 | 0 | 70618.4421 | 0 | 1188150.8266 | 3091324.7275 | 2109892.6469 | 9435908.7819 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 38531453.3025 | 80279618.86 | 421.6965 | 2.2447 | 17165.7152 | 35764.4717 | 349.9463 | 729.1071
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.258 | 5.9294 | 0.75998 | 4 | 13430.6876 | 27163.9691 | 273.8027 | 553.7743 | 248.0849 | 0 | 54.3706 | 1780723.3095 | 114856.0313 | 1360167.9288 | 465293.5646 | 0 | 67075.7795 | 0 | 1477365.4794 | 3843801.928 | 2623473.7981 | 11732757.8193 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 40828302.3398 | 82576467.8973 | 562.3413 | 3.0399 | 13430.6876 | 27163.9691 | 273.8027 | 553.7743
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.007 | 7.8843 | 1.0155 | 4 | 10731.8949 | 21009.6909 | 218.7842 | 428.311 | 253.0252 | 0 | 70.1621 | 2177260.8392 | 140210.3901 | 1708417.9307 | 593656.2329 | 0 | 61104.5679 | 0 | 1825453.4847 | 4749455.5153 | 3241600.9808 | 14497159.9417 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 43592704.4622 | 85340870.0198 | 749.8942 | 4.062 | 10731.8949 | 21009.6909 | 218.7842 | 428.311
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3453 | 10.5597 | 1.3662 | 4 | 8623.302 | 16262.7493 | 175.7977 | 331.5381 | 257.6691 | 0 | 83.095 | 2676481.7404 | 172029.1305 | 2158264.8893 | 766560.5124 | 0 | 47693.3097 | 0 | 2270201.5371 | 5906598.7172 | 4031374.993 | 18029204.8296 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 47124749.3501 | 88872914.9076 | 1000 | 5.4648 | 8623.302 | 16262.7493 | 175.7977 | 331.5381
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.381 | 14.0213 | 1.8201 | 4 | 7060.7168 | 12795.1925 | 143.9423 | 260.8473 | 261.0658 | 0 | 80.8439 | 3271064.394 | 209796.5011 | 2707788.516 | 990993.7987 | 0 | 22844.2082 | 0 | 2808970.093 | 7308363.9831 | 4988108.5903 | 22307930.0846 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 51403474.6051 | 93151640.1626 | 1333.5214 | 7.2802 | 7060.7168 | 12795.1925 | 143.9423 | 260.8473
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.4768 | 10.7085 | 1.3909 | 4 | 8478.6049 | 15982.6492 | 172.8478 | 325.8279 | 257.8458 | 0 | 85.0995 | 2703104.1755 | 173723.0459 | 2182569.6254 | 776261.3842 | 0 | 0 | 0 | 2275906.7101 | 5921442.407 | 4041506.1162 | 18074513.4643 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 47170057.9848 | 88918223.5423 | 1778.2794 | 5.5634 | 8478.6049 | 15982.6492 | 172.8478 | 325.8279
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.622 | 14.294 | 1.8566 | 4 | 6957.261 | 12579.0003 | 141.8332 | 256.4399 | 261.2492 | 0 | 100.6731 | 3315987.9456 | 212644.7755 | 2749842.7377 | 1008778.6158 | 0 | 0 | 0 | 2842029.0891 | 7394376.7096 | 5046814.0435 | 22570473.9169 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 51666018.4374 | 93414183.9949 | 2371.3737 | 7.4262 | 6957.261 | 12579.0003 | 141.8332 | 256.4399
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7442 | 19.0063 | 2.4686 | 4 | 5796.2603 | 10024.1747 | 118.1646 | 204.3564 | 263.9113 | 0 | 81.9026 | 4057827.4699 | 259582.7772 | 3453849.9497 | 1313921.8799 | 0 | 0 | 0 | 3543221.0099 | 9218734.2532 | 6291975.5538 | 28139112.8936 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 57234657.4141 | 98982822.9716 | 3162.2777 | 9.8744 | 5796.2603 | 10024.1747 | 118.1646 | 204.3564
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.1958 | 25.2494 | 3.2795 | 4 | 4893.893 | 8076.4284 | 99.7686 | 164.6489 | 265.995 | 0 | 86.6321 | 4963784.5448 | 316681.6815 | 4334967.3331 | 1717843.2868 | 0 | 0 | 0 | 4419977.97 | 11499876.0157 | 7848901.6795 | 35102032.5113 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 64197577.0318 | 105945742.5893 | 4216.965 | 13.1179 | 4893.893 | 8076.4284 | 99.7686 | 164.6489
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3259 | 33.4234 | 4.3411 | 4 | 4193.2655 | 6597.481 | 85.4854 | 134.4986 | 267.5982 | 0 | 85.7267 | 6058181.58 | 385374.3661 | 5425324.1736 | 2246431.7792 | 0 | 0 | 0 | 5504971.6406 | 14322806.9838 | 9775610.0707 | 43718700.5939 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 72814245.1144 | 114562410.6719 | 5623.4133 | 17.3646 | 4193.2655 | 6597.481 | 85.4854 | 134.4986
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.5736 | 44.0303 | 5.7188 | 4 | 3645.945 | 5470.9887 | 74.3275 | 111.5335 | 268.8167 | 0 | 89.1754 | 7370324.4734 | 467383.0108 | 6763722.8848 | 2932177.4989 | 0 | 0 | 0 | 6838107.0685 | 17791351.9036 | 12142963.2499 | 54306030.0899 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 83401574.6104 | 125149740.168 | 7498.9421 | 22.8752 | 3645.945 | 5470.9887 | 74.3275 | 111.5335
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.371 | 57.5467 | 7.4743 | 4 | 3217.9094 | 4614.2908 | 65.6014 | 94.0686 | 269.6925 | 0 | 112.3206 | 8918462.7138 | 563717.3229 | 8379173.5845 | 3806735.6714 | 0 | 0 | 0 | 8450554.8241 | 21986610.2051 | 15006313.2447 | 67111567.5664 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 96207112.0869 | 137955277.6445 | 10000 | 29.8974 | 3217.9094 | 4614.2908 | 65.6014 | 94.0686
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.9459 | 74.135 | 9.6289 | 4 | 2886.6904 | 3970.6211 | 58.8491 | 80.9465 | 270.1461 | 0 | 96.6707 | 10683639.9188 | 673074.5028 | 10261319.1878 | 4885080.0294 | 0 | 0 | 0 | 10336214.3191 | 26892709.4093 | 18354826.7618 | 82086864.129 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 111182408.6495 | 152930574.2071 | 13335.2143 | 38.5155 | 2886.6904 | 3970.6211 | 58.8491 | 80.9465
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.1615 | 93.3687 | 12.127 | 4 | 2635.3036 | 3495.9475 | 53.7242 | 71.2696 | 269.9814 | 0 | 113.061 | 12595568.3275 | 791020.5004 | 12340864.8681 | 6151727.4717 | 0 | 0 | 0 | 12432880.6554 | 32347805.1308 | 22078041.6827 | 98737908.6366 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 127833453.1571 | 169581618.7147 | 17782.7941 | 48.5081 | 2635.3036 | 3495.9475 | 53.7242 | 71.2696
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2064 | 113.9196 | 14.7962 | 4 | 2450.7394 | 3156.1241 | 49.9616 | 64.3419 | 269.0462 | 0 | 121.8727 | 14519000.6228 | 909213.7588 | 14469835.9845 | 7538787.2933 | 0 | 0 | 0 | 14600366.6872 | 37987159.173 | 25927016.6936 | 115951380.2131 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 145046924.7336 | 186795090.2912 | 23713.7371 | 59.185 | 2450.7394 | 3156.1241 | 49.9616 | 64.3419
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.8682 | 134.0914 | 17.4162 | 4 | 2319.1345 | 2918.4062 | 47.2787 | 59.4957 | 267.382 | 0 | 100.1254 | 16313719.501 | 1019125.1587 | 16485622.4669 | 8950570.9011 | 0 | 0 | 0 | 16679924.8308 | 43397742.8867 | 29619851.2546 | 132466556.9997 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 161562101.5202 | 203310267.0778 | 31622.7766 | 69.6648 | 2319.1345 | 2918.4062 | 47.2787 | 59.4957
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7863 | 152.3612 | 19.7892 | 4 | 2227.5553 | 2754.9675 | 45.4117 | 56.1637 | 265.2428 | 0 | 120.0839 | 17874529.3981 | 1114446.1819 | 18259307.2218 | 10287445.1135 | 0 | 0 | 0 | 18538933.887 | 48234503.1157 | 32921039.4964 | 147230204.4143 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 176325748.9348 | 218073914.4923 | 42169.6503 | 79.1566 | 2227.5553 | 2754.9675 | 45.4117 | 56.1637
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.158 | 168.4816 | 21.8829 | 4 | 2161.6567 | 2638.6058 | 44.0683 | 53.7915 | 263.202 | 0 | 113.6524 | 19208482.9133 | 1195731.7395 | 19789132.6942 | 11503395.818 | 0 | 0 | 0 | 20161729.8344 | 52456685.2895 | 35802765.5872 | 160117923.8761 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 189213468.3966 | 230961633.9541 | 56234.1325 | 87.5317 | 2161.6567 | 2638.6058 | 44.0683 | 53.7915
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.181 | 181.7125 | 23.6014 | 4 | 2116.0157 | 2558.2371 | 43.1378 | 52.1531 | 261.2406 | 0 | 130.1571 | 20276735.3042 | 1260713.4216 | 21022899.3468 | 12542705.3465 | 0 | 0 | 0 | 21490190.8335 | 55913068.3044 | 38161818.0164 | 170668130.5734 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 199763675.0939 | 241511840.6515 | 74989.4209 | 94.4056 | 2116.0157 | 2558.2371 | 43.1378 | 52.1531
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.6442 | 192.167 | 24.9593 | 4 | 2084.4779 | 2502.6411 | 42.4949 | 51.0197 | 259.4855 | 0 | 114.1027 | 21105463.8029 | 1311058.745 | 21985066.4598 | 13395588.3572 | 0 | 0 | 0 | 22540899.1723 | 58646795.8722 | 40027643.2539 | 179012515.6633 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 208108060.1838 | 249856225.7413 | 100000 | 99.837 | 2084.4779 | 2502.6411 | 42.4949 | 51.0197
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.7757 | 200.31 | 26.0169 | 4 | 2062.4043 | 2463.5682 | 42.0449 | 50.2232 | 257.9781 | 0 | 131.3242 | 21742239.0729 | 1349704.9866 | 22727248.9595 | 14083515.7095 | 0 | 0 | 0 | 23362056.4041 | 60783278.5468 | 41485836.5797 | 185533880.2591 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 214629424.7797 | 256377590.3372 | 133352.1432 | 104.0676 | 2062.4043 | 2463.5682 | 42.0449 | 50.2232
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.7124 | 206.4912 | 26.8197 | 4 | 2046.9238 | 2436.0793 | 41.7293 | 49.6628 | 256.7688 | 0 | 93.842 | 22220769.1108 | 1378726.1158 | 23286590.0402 | 14618778.5534 | 0 | 0 | 0 | 23986896.8899 | 62408985.3183 | 42595414.8561 | 190496160.8844 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 219591705.405 | 261339870.9625 | 177827.941 | 107.2789 | 2046.9238 | 2436.0793 | 41.7293 | 49.6628
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.8442 | 211.1533 | 27.4253 | 4 | 2035.9232 | 2416.4863 | 41.505 | 49.2633 | 255.8219 | 0 | 115.4336 | 22579054.1322 | 1400443.1771 | 23706259.2177 | 15030226.642 | 0 | 0 | 0 | 24459233.4359 | 63637908.1216 | 43434179.9212 | 194247304.6477 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 223342849.1683 | 265091014.7258 | 237137.3706 | 109.701 | 2035.9232 | 2416.4863 | 41.505 | 49.2633
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.5842 | 214.6753 | 27.8827 | 4 | 2028.0237 | 2402.3433 | 41.344 | 48.975 | 255.0733 | 0 | 66.2446 | 22848255.444 | 1416754.0599 | 24022069.9657 | 15347236.1458 | 0 | 0 | 0 | 24817383.09 | 64569740.055 | 44070174.363 | 197091613.1235 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 226187157.644 | 267935323.2015 | 316227.766 | 111.5308 | 2028.0237 | 2402.3433 | 41.344 | 48.975
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.2117 | 217.322 | 28.2265 | 4 | 2022.3167 | 2392.0776 | 41.2277 | 48.7657 | 254.4907 | 0 | 60.8261 | 23049735.6394 | 1428958.1347 | 24258705.1134 | 15589207.3027 | 0 | 0 | 0 | 25087376.4142 | 65272207.3013 | 44549622.6929 | 199235812.5987 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 228331357.1192 | 270079522.6767 | 421696.5034 | 112.9058 | 2022.3167 | 2392.0776 | 41.2277 | 48.7657
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 261.5371 | 245.0425 | 31.697 | 4 | 1990.9683 | 2320.2435 | 40.5886 | 47.3013 | 246.6565 | 0 | 210.4838 | 25120776.0629 | 1554232.559 | 26704097.0752 | 18417630.3065 | 0 | 310861.528 | 0 | 28121963.0373 | 73167579.2152 | 49938376.2578 | 223335516.0419 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 252431060.5624 | 294179226.1199 | 562341.3252 | 126.7881 | 1990.9683 | 2320.2435 | 40.5886 | 47.3013
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 262.2681 | 245.4479 | 31.7538 | 4 | 1990.0215 | 2318.7075 | 40.5693 | 47.27 | 246.5117 | 0 | 220.003 | 25150561.3537 | 1556031.9958 | 26739433.8051 | 18464403.4951 | 0 | 304413.043 | 0 | 28163789.0402 | 73276401.8951 | 50012649.9729 | 223667684.601 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 252763229.1215 | 294511394.679 | 749894.2093 | 127.0153 | 1990.0215 | 2318.7075 | 40.5693 | 47.27
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 262.8212 | 245.7534 | 31.7966 | 4 | 1989.3114 | 2317.5549 | 40.5548 | 47.2465 | 246.4019 | 0 | 229.1707 | 25172995.8585 | 1557387.3044 | 26766052.7491 | 18499786.2377 | 0 | 299499.251 | 0 | 28195331.3462 | 73358468.5052 | 50068662.1206 | 223918183.3727 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 253013727.8932 | 294761893.4507 | 1000000 | 127.1866 | 1989.3114 | 2317.5549 | 40.5548 | 47.2465
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 263.3813 | 246.0592 | 31.8381 | 4 | 1988.7514 | 2316.5673 | 40.5434 | 47.2264 | 246.2893 | 0 | 210.7149 | 25195449.5084 | 1558743.7345 | 26792697.0336 | 18535578.1611 | 0 | 296753.7927 | 0 | 28227896.6698 | 73443196.797 | 50126490.9208 | 224176806.6179 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 253272351.1384 | 295020516.6959 | 1333521.4322 | 127.3524 | 1988.7514 | 2316.5673 | 40.5434 | 47.2264
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.1717 | 247.0615 | 31.9584 | 4 | 1988.4219 | 2315.0036 | 40.5367 | 47.1945 | 245.9446 | 0 | 262.87 | 25268977.5586 | 1563185.3353 | 26879966.3346 | 18650449.763 | 0 | 312101.2433 | 0 | 28343125.2916 | 73742998.0342 | 50331111.4254 | 225091914.986 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254187459.5065 | 295935625.064 | 1778279.41 | 127.8338 | 1988.4219 | 2315.0036 | 40.5367 | 47.1945
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.3102 | 247.1482 | 31.9706 | 4 | 1988.1992 | 2314.6569 | 40.5321 | 47.1874 | 245.9229 | 0 | 250.5455 | 25275340.444 | 1563569.6798 | 26887519.6646 | 18659482.1386 | 0 | 310757.6017 | 0 | 28351701.1162 | 73765310.5707 | 50346340.1901 | 225160021.4056 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254255565.9261 | 296003731.4836 | 2371373.7057 | 127.8823 | 1988.1992 | 2314.6569 | 40.5321 | 47.1874
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.4003 | 247.2057 | 31.9788 | 4 | 1988.0301 | 2314.4037 | 40.5287 | 47.1822 | 245.9093 | 0 | 275.4497 | 25279550.331 | 1563823.9727 | 26892517.303 | 18665367.068 | 0 | 309562.865 | 0 | 28357220.4005 | 73779670.6163 | 50356141.2162 | 225203853.7726 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254299398.2932 | 296047563.8507 | 3162277.6602 | 127.9153 | 1988.0301 | 2314.4037 | 40.5287 | 47.1822
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.454 | 247.2412 | 31.9841 | 4 | 1987.902 | 2314.2216 | 40.5261 | 47.1785 | 245.9018 | 0 | 277.3804 | 25282152.5983 | 1563981.1588 | 26895606.5509 | 18668899.4306 | 0 | 308497.4317 | 0 | 28360463.4964 | 73788108.4866 | 50361900.2361 | 225229609.3893 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254325153.9098 | 296073319.4673 | 4216965.0343 | 127.9365 | 1987.902 | 2314.2216 | 40.5261 | 47.1785
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.5271 | 247.2858 | 31.9902 | 4 | 1987.8053 | 2314.0627 | 40.5241 | 47.1753 | 245.8897 | 0 | 273.7081 | 25285423.7465 | 1564178.747 | 26899489.9019 | 18673649.2673 | 0 | 308038.3743 | 0 | 28365004.2144 | 73799922.5034 | 50369963.5453 | 225265670.3 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254361214.8205 | 296109380.378 | 5623413.2519 | 127.9608 | 1987.8053 | 2314.0627 | 40.5241 | 47.1753
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.566 | 247.3104 | 31.9937 | 4 | 1987.7326 | 2313.9539 | 40.5226 | 47.1731 | 245.8838 | 0 | 280.808 | 25287230.9861 | 1564287.9099 | 26901635.3943 | 18676189.9532 | 0 | 307516.9105 | 0 | 28367375.8501 | 73806093.013 | 50374175.0449 | 225284505.0621 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254380049.5826 | 296128215.1401 | 7498942.0933 | 127.975 | 1987.7326 | 2313.9539 | 40.5226 | 47.1731
1 | 6800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 265.6003 | 247.3317 | 31.9967 | 4 | 1987.6779 | 2313.8688 | 40.5215 | 47.1713 | 245.8783 | 0 | 276.5817 | 25288790.3712 | 1564382.1015 | 26903486.656 | 18678420.851 | 0 | 307176.5045 | 0 | 28369480.0288 | 73811567.6545 | 50377911.6003 | 225301215.7678 | 961560.8286 | 28133983.6919 | 28133983.6919 | 1478867.319 | 12135314.5466 | 0 | 254396760.2884 | 296144925.8459 | 10000000 | 127.9869 | 1987.6779 | 2313.8688 | 40.5215 | 47.1713
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.74058 | 0.087263 | 4 | 92855.6781 | 214884.492 | 1892.9886 | 4380.711 | 184.6383 | 0 | 40.707 | 414027.7355 | 26776.0782 | 257538.32 | 114530.7981 | 0 | 62570.9017 | 0 | 341423.0951 | 888312.8579 | 606291.7785 | 2711471.565 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 32411626.7745 | 75006247.2965 | 100 | 0.34905 | 92855.6781 | 214884.492 | 1892.9886 | 4380.711
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 1.1818 | 0.14372 | 4 | 58121.4948 | 132215.992 | 1184.8853 | 2695.4018 | 201.6252 | 0 | 195.1232 | 574032.8339 | 37198.5232 | 374267.0567 | 146929.2577 | 0 | 66080.3699 | 0 | 467418.1362 | 1216126.1098 | 830031.0588 | 3712083.3464 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 33412238.5559 | 76006859.0779 | 133.3521 | 0.57487 | 58121.4948 | 132215.992 | 1184.8853 | 2695.4018
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4293 | 1.7596 | 0.21783 | 4 | 39693.5978 | 88577.66 | 809.2077 | 1805.7754 | 216.0427 | 0 | 264.2595 | 758144.3294 | 49071.4887 | 514644.4635 | 186747.861 | 0 | 69063.5719 | 0 | 615291.9687 | 1600863.4887 | 1092622.2255 | 4886449.3973 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 34586604.6068 | 77181225.1288 | 177.8279 | 0.87134 | 39693.5978 | 88577.66 | 809.2077 | 1805.7754
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0906 | 2.4795 | 0.31117 | 4 | 28859.2454 | 63080.8143 | 588.3348 | 1285.9877 | 227.5882 | 0 | 343.7323 | 964307.9292 | 62387.7997 | 677132.2786 | 234770.5265 | 0 | 69675.0406 | 0 | 783226.6941 | 2037795.1961 | 1390837.0938 | 6220132.5586 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 35920287.768 | 78514908.2901 | 237.1374 | 1.2447 | 28859.2454 | 63080.8143 | 588.3348 | 1285.9877
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 3.4021 | 0.4314 | 4 | 21730.6233 | 46414.4517 | 443.0081 | 946.2214 | 237.0786 | 0 | 63.8472 | 1204276.4416 | 77851.3277 | 872123.3662 | 295357.9618 | 0 | 68231.1726 | 0 | 981957.7053 | 2554852.5219 | 1743739.3431 | 7798389.8402 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 37498545.0497 | 80093165.5717 | 316.2278 | 1.7256 | 21730.6233 | 46414.4517 | 443.0081 | 946.2214
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0058 | 4.6328 | 0.59213 | 4 | 16658.4994 | 34642.0893 | 339.606 | 706.2258 | 245.0944 | 0 | 91.0695 | 1496519.1195 | 96635.1156 | 1116494.8358 | 375188.0034 | 0 | 65034.9632 | 0 | 1228450.0946 | 3196175.1564 | 2181455.219 | 9755952.5074 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 39456107.7168 | 82050728.2389 | 421.6965 | 2.3685 | 16658.4994 | 34642.0893 | 339.606 | 706.2258
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 6.2151 | 0.79945 | 4 | 13072.1363 | 26392.1896 | 266.4932 | 538.0405 | 251.5033 | 0 | 98.0449 | 1840814.2122 | 118703.1512 | 1412358.7863 | 477154.623 | 0 | 58198.7015 | 0 | 1523819.4949 | 3964665.7474 | 2705965.8384 | 12101680.5549 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 41801835.7643 | 84396456.2864 | 562.3413 | 3.1978 | 13072.1363 | 26392.1896 | 266.4932 | 538.0405
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1922 | 8.2843 | 1.0707 | 4 | 10432.1742 | 20378.0459 | 212.674 | 415.434 | 256.4613 | 0 | 82.3662 | 2254688.9184 | 145152.4714 | 1777409.6539 | 610642.8177 | 0 | 47720.7767 | 0 | 1885889.7088 | 4906698.1732 | 3348922.3258 | 14977124.8459 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 44677280.0553 | 87271900.5774 | 749.8942 | 4.2826 | 10432.1742 | 20378.0459 | 212.674 | 415.434
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5622 | 11.0735 | 1.4377 | 4 | 8392.3515 | 15799.171 | 171.0894 | 322.0875 | 261.1356 | 0 | 101.5317 | 2767942.2059 | 177847.3446 | 2241887.2334 | 787413.9645 | 0 | 17958.8497 | 0 | 2337289.3432 | 6081147.427 | 4150508.074 | 18561994.4422 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 48262149.6517 | 90856770.1737 | 1000 | 5.7507 | 8392.3515 | 15799.171 | 171.0894 | 322.0875
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.358 | 8.4717 | 1.1003 | 4 | 10175.3797 | 19853.0755 | 207.4389 | 404.7318 | 256.7636 | 0 | 54.2082 | 2290598.7945 | 147443.6172 | 1809508.9099 | 622870.0532 | 0 | 0 | 0 | 1899464.3362 | 4942016.5691 | 3373027.8567 | 15084930.1369 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 44785085.3464 | 87379705.8684 | 1333.5214 | 4.4013 | 10175.3797 | 19853.0755 | 207.4389 | 404.7318
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8595 | 11.4201 | 1.4833 | 4 | 8199.6159 | 15378.7401 | 167.1603 | 313.5164 | 261.5319 | 0 | 79.174 | 2828937.2384 | 181725.6913 | 2297847.1105 | 809544.841 | 0 | 0 | 0 | 2386041.4037 | 6207990.288 | 4237080.933 | 18949167.506 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 48649322.7155 | 91243943.2375 | 1778.2794 | 5.9331 | 8199.6159 | 15378.7401 | 167.1603 | 313.5164
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1238 | 15.2441 | 1.9799 | 4 | 6738.3749 | 12116.6217 | 137.3709 | 247.0137 | 264.8966 | 0 | 78.1642 | 3470603.9445 | 222442.5415 | 2895114.3495 | 1052932.4606 | 0 | 0 | 0 | 2980026.3854 | 7753417.3675 | 5291866.6701 | 23666403.719 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 53366558.9285 | 95961179.4505 | 2371.3737 | 7.9198 | 6738.3749 | 12116.6217 | 137.3709 | 247.0137
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3969 | 20.2642 | 2.632 | 4 | 5623.4507 | 9669.3304 | 114.6416 | 197.1224 | 267.5227 | 0 | 63.1909 | 4246483.1536 | 271492.1523 | 3635531.6516 | 1372021.2864 | 0 | 0 | 0 | 3714956.0151 | 9665553.5091 | 6596938.8772 | 29502976.6453 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 59203131.8548 | 101797752.3768 | 3162.2777 | 10.5279 | 5623.4507 | 9669.3304 | 114.6416 | 197.1224
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0311 | 26.895 | 3.4932 | 4 | 4757.8157 | 7806.2074 | 96.9945 | 159.1401 | 269.5725 | 0 | 83.002 | 5191381.6144 | 330991.4875 | 4559546.9786 | 1793096.2509 | 0 | 0 | 0 | 4631256.3693 | 12049579.0715 | 8224085.3104 | 36779937.0826 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 66480092.292 | 109074712.8141 | 4216.965 | 13.9728 | 4757.8157 | 7806.2074 | 96.9945 | 159.1401
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4099 | 35.5883 | 4.6223 | 4 | 4083.3791 | 6387.1237 | 83.2452 | 130.2102 | 271.1521 | 0 | 112.0528 | 6334625.2536 | 402682.1053 | 5704674.1719 | 2344879.9984 | 0 | 0 | 0 | 5766875.9964 | 15004228.3937 | 10240694.1847 | 45798660.104 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 75498815.3134 | 118093435.8355 | 5623.4133 | 18.4893 | 4083.3791 | 6387.1237 | 83.2452 | 130.2102
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.9495 | 46.8321 | 6.0827 | 4 | 3557.045 | 5307.6918 | 72.5152 | 108.2045 | 272.3475 | 0 | 108.7335 | 7701201.2916 | 488008.4927 | 7105906.2313 | 3058421.8165 | 0 | 0 | 0 | 7157879.7545 | 18623334.8383 | 12710808.6984 | 56845561.1233 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 86545716.3328 | 129140336.8548 | 7498.9421 | 24.3308 | 3557.045 | 5307.6918 | 72.5152 | 108.2045
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.1226 | 61.1577 | 7.9434 | 4 | 3144.3897 | 4484.9641 | 64.1026 | 91.4321 | 273.1942 | 0 | 103.3475 | 9313790.7766 | 588251.0365 | 8797222.0384 | 3968504.1302 | 0 | 0 | 0 | 8840429.5129 | 23000984.1711 | 15698644.3197 | 70207825.9855 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 99907981.195 | 142502601.717 | 10000 | 31.7734 | 3144.3897 | 4484.9641 | 64.1026 | 91.4321
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.0996 | 78.642 | 10.2143 | 4 | 2825.8315 | 3868.359 | 57.6084 | 78.8617 | 273.5873 | 0 | 84.5455 | 11143100.5235 | 701463.5026 | 10757423.6318 | 5085457.1213 | 0 | 0 | 0 | 10798103.4639 | 28094450.2175 | 19175039.5567 | 85755038.0173 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 115455193.2267 | 158049813.7488 | 13335.2143 | 40.8571 | 2825.8315 | 3868.359 | 57.6084 | 78.8617
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6636 | 98.7178 | 12.8218 | 4 | 2585.2218 | 3415.7347 | 52.7032 | 69.6344 | 273.3199 | 0 | 108.3941 | 13106784.8099 | 822477.2107 | 12903311.4155 | 6386674.7665 | 0 | 0 | 0 | 12955506.799 | 33707571.1511 | 23006109.932 | 102888436.0847 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 132588591.2941 | 175183211.8162 | 17782.7941 | 51.2871 | 2585.2218 | 3415.7347 | 52.7032 | 69.6344
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.9863 | 119.9785 | 15.5832 | 4 | 2409.0668 | 3092.4093 | 49.1121 | 63.0429 | 272.2519 | 0 | 103.1599 | 15066825.0992 | 942799.7427 | 15082299.4215 | 7801764.8232 | 0 | 0 | 0 | 15168538.7438 | 39465426.3162 | 26935964.3942 | 120463618.5407 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 150163773.7501 | 192758394.2722 | 23713.7371 | 62.3328 | 2409.0668 | 3092.4093 | 49.1121 | 63.0429
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.8011 | 140.6305 | 18.2655 | 4 | 2283.9711 | 2866.9628 | 46.5618 | 58.4469 | 270.4495 | 0 | 114.2095 | 16878841.0383 | 1053665.3596 | 17125703.1616 | 9229950.2211 | 0 | 0 | 0 | 17272382.3145 | 44939195.7294 | 30671924.4935 | 137171662.318 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 166871817.5274 | 209466438.0495 | 31622.7766 | 73.0621 | 2283.9711 | 2866.9628 | 46.5618 | 58.4469
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.805 | 159.2767 | 20.6874 | 4 | 2196.62 | 2711.3623 | 44.7811 | 55.2748 | 268.2333 | 0 | 111.5143 | 18451395.0586 | 1149617.7551 | 18919359.2472 | 10577594.954 | 0 | 0 | 0 | 19148207.1358 | 49819707.1301 | 34002973.8089 | 152068855.0898 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 181769010.2992 | 224363630.8213 | 42169.6503 | 82.7494 | 2196.62 | 2711.3623 | 44.7811 | 55.2748
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.1152 | 175.5441 | 22.8002 | 4 | 2134.2063 | 2601.2481 | 43.5087 | 53.03 | 266.1162 | 0 | 128.5722 | 19781511.6553 | 1230601.1832 | 20450018.2043 | 11791927.6814 | 0 | 0 | 0 | 20769082.9024 | 54036893.3875 | 36881290.0841 | 164941325.0982 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 194641480.3077 | 237236100.8297 | 56234.1325 | 91.2009 | 2134.2063 | 2601.2481 | 43.5087 | 53.03
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.058 | 188.8465 | 24.528 | 4 | 2090.962 | 2525.1052 | 42.6271 | 51.4777 | 264.0933 | 0 | 113.9087 | 20843647.7108 | 1295159.4993 | 21680630.1628 | 12826918.7188 | 0 | 0 | 0 | 22092078.8758 | 57479057.5263 | 39230637.8382 | 175448130.3321 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 205148285.5415 | 247742906.0636 | 74989.4209 | 98.1119 | 2090.962 | 2525.1052 | 42.6271 | 51.4777
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.358 | 199.2625 | 25.8808 | 4 | 2061.2777 | 2472.727 | 42.0219 | 50.4099 | 262.301 | 0 | 96.7359 | 21660736.1362 | 1344760.3328 | 22632117.9575 | 13669845.8579 | 0 | 0 | 0 | 23129909.5109 | 60179279.9506 | 41073595.1268 | 183690244.8728 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 213390400.0822 | 255985020.6043 | 100000 | 103.5234 | 2061.2777 | 2472.727 | 42.0219 | 50.4099
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.4358 | 207.4267 | 26.9412 | 4 | 2040.3088 | 2435.5637 | 41.5945 | 49.6523 | 260.7517 | 0 | 100.6349 | 22292844.4613 | 1383095.6808 | 23370953.8652 | 14353813.6515 | 0 | 0 | 0 | 23946275.9869 | 62303298.0613 | 42523281.1316 | 190173562.8385 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 219873718.0479 | 262468338.57 | 133352.1432 | 107.7649 | 2040.3088 | 2435.5637 | 41.5945 | 49.6523
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 206.2043 | 213.5616 | 27.7381 | 4 | 2025.6642 | 2409.5649 | 41.2959 | 49.1222 | 259.5534 | 0 | 104.1858 | 22763262.7295 | 1411604.9542 | 23922316.7657 | 14878527.9212 | 0 | 0 | 0 | 24560527.8246 | 63901455.3425 | 43614056.3149 | 195051751.8526 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 224751907.062 | 267346527.5841 | 177827.941 | 110.9522 | 2025.6642 | 2409.5649 | 41.2959 | 49.1222
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.2601 | 218.2065 | 28.3413 | 4 | 2015.2577 | 2390.9863 | 41.0838 | 48.7435 | 258.5914 | 0 | 128.506 | 23116921.8647 | 1433027.0652 | 24337665.3743 | 15285478.1579 | 0 | 0 | 0 | 25027506.0602 | 65116436.9213 | 44443306.2078 | 198760341.6513 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 228460496.8608 | 271055117.3828 | 237137.3706 | 113.3654 | 2015.2577 | 2390.9863 | 41.0838 | 48.7435
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.94 | 221.7129 | 28.7968 | 4 | 2007.786 | 2377.5724 | 40.9314 | 48.47 | 257.8313 | 0 | 131.4135 | 23382499.2555 | 1449107.6536 | 24650032.4543 | 15598867.7565 | 0 | 0 | 0 | 25381397.7767 | 66037190.5745 | 45071739.4957 | 201570834.9668 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 231270990.1763 | 273865610.6983 | 316227.766 | 115.1871 | 2007.786 | 2377.5724 | 40.9314 | 48.47
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.5085 | 224.3364 | 29.1375 | 4 | 2002.401 | 2367.863 | 40.8217 | 48.2721 | 257.2423 | 0 | 144.381 | 23580441.3708 | 1461089.5509 | 24883104.5079 | 15836800.9953 | 0 | 0 | 0 | 25646960.2057 | 66728129.5403 | 45543319.5372 | 203679845.7079 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 233380000.9174 | 275974621.4395 | 421696.5034 | 116.5501 | 2002.401 | 2367.863 | 40.8217 | 48.2721
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.2347 | 226.3112 | 29.394 | 4 | 1998.4638 | 2360.7367 | 40.7414 | 48.1268 | 256.7867 | 0 | 134.1969 | 23729011.639 | 1470080.9582 | 25058185.0458 | 16017999.9105 | 0 | 0 | 0 | 25847358.2459 | 67249524.1337 | 45899182.0608 | 205271341.994 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 234971497.2034 | 277566117.7255 | 562341.3252 | 117.5761 | 1998.4638 | 2360.7367 | 40.7414 | 48.1268
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.2958 | 227.787 | 29.5857 | 4 | 1995.5848 | 2355.5106 | 40.6827 | 48.0203 | 256.4392 | 0 | 123.0318 | 23839802.7448 | 1476784.9343 | 25188824.3977 | 16154574.4751 | 0 | 0 | 0 | 25997394.7552 | 67639888.3541 | 46165613.6624 | 206462883.3236 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 236163038.5331 | 278757659.0551 | 749894.2093 | 118.3428 | 1995.5848 | 2355.5106 | 40.6827 | 48.0203
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.8622 | 228.8991 | 29.7301 | 4 | 1993.4539 | 2351.6311 | 40.6393 | 47.9412 | 256.1732 | 0 | 92.3068 | 23923152.9164 | 1481827.8673 | 25287151.1305 | 16258277.2003 | 0 | 0 | 0 | 26110659.5547 | 67934580.1286 | 46366746.8538 | 207362395.6516 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 237062550.8611 | 279657171.3832 | 1000000 | 118.9205 | 1993.4539 | 2351.6311 | 40.6393 | 47.9412
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.0459 | 229.7339 | 29.8386 | 4 | 1991.8757 | 2348.7514 | 40.6071 | 47.8825 | 255.9712 | 0 | 95.6788 | 23985654.9184 | 1485609.0925 | 25360908.5522 | 16336586.3027 | 0 | 0 | 0 | 26195815.9577 | 68156139.6211 | 46517965.7601 | 208038680.2047 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 237738835.4141 | 280333455.9362 | 1333521.4322 | 119.3542 | 1991.8757 | 2348.7514 | 40.6071 | 47.8825
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.9279 | 230.3529 | 29.919 | 4 | 1990.7166 | 2346.6333 | 40.5835 | 47.8393 | 255.8201 | 0 | 102.2127 | 24031955.4142 | 1488409.9815 | 25415560.6152 | 16394865.3118 | 0 | 0 | 0 | 26259008.6159 | 68320553.9552 | 46630181.9214 | 208540535.8153 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 238240691.0247 | 280835311.5468 | 1778279.41 | 119.6758 | 1990.7166 | 2346.6333 | 40.5835 | 47.8393
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.5884 | 230.8148 | 29.979 | 4 | 1989.8584 | 2345.0628 | 40.566 | 47.8073 | 255.7067 | 0 | 89.219 | 24066480.3175 | 1490498.4201 | 25456320.6251 | 16438493.1064 | 0 | 0 | 0 | 26306199.0629 | 68443333.8184 | 46713981.7009 | 208915307.0513 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 238615462.2608 | 281210082.7828 | 2371373.7057 | 119.9158 | 1989.8584 | 2345.0628 | 40.566 | 47.8073
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 268.8381 | 254.9147 | 33.0108 | 4 | 1966.4043 | 2288.9857 | 40.0878 | 46.6641 | 248.1823 | 0 | 372.5644 | 25842274.4843 | 1597803.6282 | 27561359.8508 | 18981536.8611 | 0 | 260149.1043 | 0 | 28954818.3322 | 75334497.8505 | 51417342.7521 | 229949782.8634 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 259649938.0729 | 302244558.5949 | 3162277.6602 | 132.043 | 1966.4043 | 2288.9857 | 40.0878 | 46.6641
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 268.9501 | 254.982 | 33.0194 | 4 | 1966.3198 | 2288.8166 | 40.0861 | 46.6606 | 248.1628 | 0 | 391.8385 | 25847165.7727 | 1598098.8898 | 27567180.6391 | 18988785.458 | 0 | 260284.1275 | 0 | 28961990.8059 | 75353159.1558 | 51430079.4764 | 230006744.3252 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 259706899.5347 | 302301520.0567 | 4216965.0343 | 132.0776 | 1966.3198 | 2288.8166 | 40.0861 | 46.6606
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 269.0085 | 255.0185 | 33.0243 | 4 | 1966.2558 | 2288.7052 | 40.0848 | 46.6584 | 248.1534 | 0 | 479.2923 | 25849820.5294 | 1598259.1429 | 27570339.9347 | 18992584.6609 | 0 | 260101.39 | 0 | 28965731.2066 | 75362890.911 | 51436721.5993 | 230036449.3748 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 259736604.5842 | 302331225.1063 | 5623413.2519 | 132.0971 | 1966.2558 | 2288.7052 | 40.0848 | 46.6584
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 269.0427 | 255.0408 | 33.0273 | 4 | 1966.2073 | 2288.6271 | 40.0838 | 46.6568 | 248.1483 | 0 | 458.4958 | 25851437.2596 | 1598356.7358 | 27572263.9436 | 18994829.2792 | 0 | 259857.0735 | 0 | 28967930.2738 | 75368612.4328 | 51440626.6555 | 230053913.6538 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 259754068.8633 | 302348689.3854 | 7498942.0933 | 132.1092 | 1966.2073 | 2288.6271 | 40.0838 | 46.6568
1 | 6900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 269.0692 | 255.0579 | 33.0296 | 4 | 1966.1708 | 2288.5678 | 40.0831 | 46.6556 | 248.1442 | 0 | 440.9751 | 25852681.2895 | 1598431.8308 | 27573744.425 | 18996564.1118 | 0 | 259678.2435 | 0 | 28969628.9612 | 75373032.0691 | 51443643.1481 | 230067404.0791 | 961560.8286 | 28738594.3808 | 28738594.3808 | 1478867.319 | 12377158.8222 | 0 | 259767559.2885 | 302362179.8106 | 10000000 | 132.1185 | 1966.1708 | 2288.5678 | 40.0831 | 46.6556
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.8119 | 0.096286 | 4 | 86177.1379 | 198989.68 | 1756.8375 | 4056.6738 | 188.697 | 0 | 44.1152 | 441451.5459 | 28555.9919 | 277194.7737 | 119225.6995 | 0 | 63472.8837 | 0 | 362661.3489 | 943570.4379 | 644006.2123 | 2880138.8938 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 33190764.8831 | 76640044.4969 | 100 | 0.38515 | 86177.1379 | 198989.68 | 1756.8375 | 4056.6738
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 1.2679 | 0.15481 | 4 | 55228.3163 | 125394.0783 | 1125.9039 | 2556.3279 | 205.3576 | 0 | 222.4128 | 602739.1509 | 39013.4682 | 395969.7077 | 151760.1514 | 0 | 66089.6353 | 0 | 489673.1243 | 1274029.0236 | 869550.9873 | 3888825.2486 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 34199451.2378 | 77648730.8516 | 133.3521 | 0.61924 | 55228.3163 | 125394.0783 | 1125.9039 | 2556.3279
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4877 | 1.8587 | 0.2311 | 4 | 38269.6019 | 85271.3392 | 780.1776 | 1738.3716 | 219.4484 | 0 | 277.0487 | 787844.6719 | 50991.7225 | 537723.7849 | 191564.1252 | 0 | 67681.5022 | 0 | 637964.2646 | 1659852.152 | 1132883.2003 | 5066505.4236 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 35377131.4128 | 78826411.0266 | 177.8279 | 0.92442 | 38269.6019 | 85271.3392 | 780.1776 | 1738.3716
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1684 | 2.6184 | 0.32985 | 4 | 27862.1691 | 60793.1492 | 568.008 | 1239.3506 | 231.0951 | 0 | 364.61 | 1001919.485 | 64813.9878 | 707309.6797 | 241335.5219 | 0 | 67383.3465 | 0 | 812277.1881 | 2113378.6226 | 1442424.3355 | 6450842.1671 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 36761468.1564 | 80210747.7702 | 237.1374 | 1.3194 | 27862.1691 | 60793.1492 | 568.008 | 1239.3506
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0117 | 3.5812 | 0.45577 | 4 | 21052.353 | 44885.0324 | 429.1807 | 915.0421 | 240.5519 | 0 | 66.8522 | 1248536.3127 | 80699.4049 | 908680.9373 | 303338.1568 | 0 | 64230.8287 | 0 | 1016139.3997 | 2643786.2792 | 1804438.4599 | 8069849.7791 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 38380475.7684 | 81829755.3821 | 316.2278 | 1.8231 | 21052.353 | 44885.0324 | 429.1807 | 915.0421
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1178 | 4.8667 | 0.62424 | 4 | 16175.6594 | 33576.3981 | 329.7627 | 684.5003 | 248.5485 | 0 | 78.7421 | 1549348.3521 | 100025.4188 | 1161372.3183 | 385201.4817 | 0 | 58437.6743 | 0 | 1269210.2456 | 3302224.7083 | 2253836.2173 | 10079656.4163 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 40390282.4056 | 83839562.0194 | 421.6965 | 2.497 | 16175.6594 | 33576.3981 | 329.7627 | 684.5003
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5332 | 6.5309 | 0.84298 | 4 | 12697.0554 | 25582.695 | 258.8466 | 521.5378 | 254.9729 | 0 | 83.4238 | 1906304.3288 | 122893.8709 | 1469486.4288 | 490518.8857 | 0 | 47522.3817 | 0 | 1574323.0994 | 4096065.7666 | 2795649.0515 | 12502763.8135 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 42813389.8028 | 86262669.4165 | 562.3413 | 3.3719 | 12697.0554 | 25582.695 | 258.8466 | 521.5378
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.358 | 8.6755 | 1.125 | 4 | 10161.8329 | 19816.9225 | 207.1627 | 403.9948 | 259.8413 | 0 | 69.83 | 2329388.3058 | 149917.8521 | 1844253.3564 | 626521.5591 | 0 | 28223.1589 | 0 | 1941538.6506 | 5051485.3045 | 3447742.518 | 15419070.7055 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 45729696.6948 | 89178976.3085 | 749.8942 | 4.5001 | 10161.8329 | 19816.9225 | 207.1627 | 403.9948
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9742 | 7.0513 | 0.91584 | 4 | 11851.5636 | 23712.0505 | 241.6102 | 483.4022 | 256.4376 | 0 | 80.0267 | 2012244.5945 | 129668.5423 | 1562425.021 | 523410.6139 | 0 | 3730.3715 | 0 | 1650276.8659 | 4293681.8867 | 2930526.114 | 13105964.0098 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 43416589.9991 | 86865869.6129 | 1000 | 3.6634 | 11851.5636 | 23712.0505 | 241.6102 | 483.4022
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6721 | 9.0401 | 1.1742 | 4 | 9822.3996 | 19073.5232 | 200.2429 | 388.8396 | 260.3952 | 0 | 53.3105 | 2398135.1397 | 154301.3398 | 1906009.1341 | 649866.0944 | 0 | 0 | 0 | 1992241.5661 | 5183403.8901 | 3537779.6633 | 15821736.8274 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 46132362.8167 | 89581642.4305 | 1333.5214 | 4.6966 | 9822.3996 | 19073.5232 | 200.2429 | 388.8396
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2662 | 12.1906 | 1.5834 | 4 | 7925.0776 | 14785.4003 | 161.5634 | 301.4204 | 265.2231 | 0 | 69.0262 | 2962664.7541 | 190223.7136 | 2421056.5327 | 845351.9121 | 0 | 0 | 0 | 2503525.7959 | 6513660.5772 | 4445707.1862 | 19882190.4718 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 50192816.4611 | 93642096.0749 | 1778.2794 | 6.3334 | 7925.0776 | 14785.4003 | 161.5634 | 301.4204
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.6185 | 16.2267 | 2.1076 | 4 | 6535.003 | 11688.9542 | 133.2249 | 238.2951 | 268.5149 | 0 | 53.5464 | 3627628.9944 | 232384.7489 | 3043465.064 | 1097581.9346 | 0 | 0 | 0 | 3120413.6893 | 8118676.3348 | 5541163.4206 | 24781314.1867 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 55091940.176 | 98541219.7898 | 2371.3737 | 8.4303 | 6535.003 | 11688.9542 | 133.2249 | 238.2951
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0548 | 21.5833 | 2.8033 | 4 | 5459.7363 | 9334.5552 | 111.3041 | 190.2975 | 271.1147 | 0 | 54.518 | 4440768.2448 | 283746.0683 | 3823661.5234 | 1431864.7128 | 0 | 0 | 0 | 3892215.8142 | 10126747.1454 | 6911713.0106 | 30910716.5196 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 61221342.5088 | 104670622.1226 | 3162.2777 | 11.2132 | 5459.7363 | 9334.5552 | 111.3041 | 190.2975
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.8937 | 28.6462 | 3.7207 | 4 | 4626.1692 | 7545.6266 | 94.3107 | 153.8278 | 273.1374 | 0 | 70.0611 | 5429276.8188 | 345934.862 | 4795554.6499 | 1872211.1625 | 0 | 0 | 0 | 4852761.2223 | 12625889.2623 | 8617428.8576 | 38539056.8354 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 68849682.8247 | 112298962.4384 | 4216.965 | 14.8827 | 4626.1692 | 7545.6266 | 94.3107 | 153.8278
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.499 | 37.8561 | 4.9169 | 4 | 3978.8753 | 6188.0713 | 81.1148 | 126.1522 | 274.6881 | 0 | 62.2038 | 6619119.565 | 420476.633 | 5993674.7287 | 2446170.8341 | 0 | 0 | 0 | 6036982.2867 | 15706989.5547 | 10720343.1174 | 47943756.7196 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 78254382.7088 | 121703662.3226 | 5623.4133 | 19.6675 | 3978.8753 | 6188.0713 | 81.1148 | 126.1522
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.3721 | 49.816 | 6.4703 | 4 | 3470.5841 | 5149.3926 | 70.7526 | 104.9773 | 275.8641 | 0 | 73.5744 | 8047465.2723 | 509571.3682 | 7465856.3569 | 3191431.6413 | 0 | 0 | 0 | 7493586.6091 | 19496775.2108 | 13306949.7001 | 59511636.1587 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 89822262.1479 | 133271541.7617 | 7498.9421 | 25.881 | 3470.5841 | 5149.3926 | 70.7526 | 104.9773
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.8937 | 64.9523 | 8.4362 | 4 | 3073.7939 | 4361.3778 | 62.6634 | 88.9126 | 276.676 | 0 | 73.0631 | 9722168.2069 | 613568.3597 | 9231241.8774 | 4135948.9142 | 0 | 0 | 0 | 9244141.6697 | 24051360.3903 | 16415547.6724 | 73413977.0907 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 103724603.0799 | 147173882.6937 | 10000 | 33.7448 | 3073.7939 | 4361.3778 | 62.6634 | 88.9126
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.2721 | 83.3639 | 10.8276 | 4 | 2767.3459 | 3770.5557 | 56.4161 | 76.8679 | 277.0029 | 0 | 86.2095 | 11616567.1245 | 730687.3699 | 11271122.0584 | 5292350.5591 | 0 | 0 | 0 | 11275183.5736 | 29335714.8004 | 20022228.14 | 89543853.6259 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 119854479.6152 | 163303759.229 | 13335.2143 | 43.3103 | 2767.3459 | 3770.5557 | 56.4161 | 76.8679
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.1922 | 104.3111 | 13.5483 | 4 | 2536.9024 | 3338.6531 | 51.7182 | 68.063 | 276.626 | 0 | 54.1361 | 13633053.8231 | 854827.1184 | 13484942.0703 | 6629361.4573 | 0 | 0 | 0 | 13494851.943 | 35110836.5809 | 23963867.422 | 107171740.4151 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 137482366.4044 | 180931646.0182 | 17782.7941 | 54.193 | 2536.9024 | 3338.6531 | 51.7182 | 68.063
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7831 | 126.2756 | 16.4011 | 4 | 2368.8496 | 3031.1431 | 48.2922 | 61.794 | 275.4203 | 0 | 111.8323 | 15628002.2297 | 977170.8184 | 15712314.676 | 8071848.0392 | 0 | 0 | 0 | 15751840.9477 | 40983058.999 | 27971779.8845 | 125096015.5944 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 155406641.5837 | 198855921.1975 | 23713.7371 | 65.6043 | 2368.8496 | 3031.1431 | 48.2922 | 61.794
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7294 | 147.377 | 19.1418 | 4 | 2250.0699 | 2817.5364 | 45.8707 | 57.4393 | 273.4784 | 0 | 126.981 | 17454196.5926 | 1088798.9224 | 17779862.142 | 9514774.0379 | 0 | 0 | 0 | 17876676.361 | 46511444.8809 | 31745016.8458 | 141970769.7826 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 172281395.7719 | 215730675.3857 | 31622.7766 | 76.5671 | 2250.0699 | 2817.5364 | 45.8707 | 57.4393
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7768 | 166.3561 | 21.6068 | 4 | 2166.8685 | 2669.5943 | 44.1745 | 54.4233 | 271.1936 | 0 | 64.107 | 19034710.2536 | 1185151.8135 | 19589150.0437 | 10870128.107 | 0 | 0 | 0 | 19764864.6849 | 51424123.579 | 35098021.0027 | 156966149.4845 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 187276775.4737 | 230726055.0875 | 42169.6503 | 86.4274 | 2166.8685 | 2669.5943 | 44.1745 | 54.4233
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0608 | 182.7912 | 23.7415 | 4 | 2107.637 | 2565.1617 | 42.967 | 52.2943 | 268.9957 | 0 | 102.6855 | 20362849.9733 | 1265947.5418 | 21122678.6556 | 12085240.9549 | 0 | 0 | 0 | 21386319.6789 | 55642816.8672 | 37977365.8574 | 169843219.5291 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 200153845.5184 | 243603125.1321 | 56234.1325 | 94.966 | 2107.637 | 2565.1617 | 42.967 | 52.2943
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.9279 | 196.1569 | 25.4775 | 4 | 2066.6779 | 2493.0279 | 42.132 | 50.8237 | 266.911 | 0 | 69.3254 | 21418390.9967 | 1330054.522 | 22349486.306 | 13116313.6406 | 0 | 0 | 0 | 22703555.7315 | 59069994.8736 | 40316485.2683 | 180304281.3386 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 210614907.3278 | 254064186.9416 | 74989.4209 | 101.9099 | 2066.6779 | 2493.0279 | 42.132 | 50.8237
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.1736 | 206.6094 | 26.8351 | 4 | 2038.5176 | 2443.2982 | 41.5579 | 49.8099 | 265.0666 | 0 | 102.081 | 22229886.3039 | 1379278.8674 | 23297259.989 | 13955408.0794 | 0 | 0 | 0 | 23736114.9635 | 61756502.1884 | 42150081.7128 | 188504532.1043 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 218815158.0936 | 262264437.7074 | 100000 | 107.3403 | 2038.5176 | 2443.2982 | 41.5579 | 49.8099
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.9884 | 214.652 | 27.8797 | 4 | 2018.8937 | 2408.508 | 41.1579 | 49.1007 | 263.5305 | 0 | 112.0574 | 22846474.7448 | 1416646.1856 | 24019979.5935 | 14622230.2985 | 0 | 0 | 0 | 24533079.0207 | 63830039.1854 | 43565313.3202 | 194833762.3487 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 225144388.3379 | 268593667.9517 | 133352.1432 | 111.5187 | 2018.8937 | 2408.508 | 41.1579 | 49.1007
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.6527 | 220.7552 | 28.6724 | 4 | 2005.0658 | 2383.9084 | 40.876 | 48.5992 | 262.3146 | 0 | 94.5062 | 23310081.3183 | 1444723.302 | 24564816.6357 | 15140531.4602 | 0 | 0 | 0 | 25139459.5593 | 65407716.9611 | 44642110.8201 | 199649440.0567 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 229960066.046 | 273409345.6597 | 177827.941 | 114.6895 | 2005.0658 | 2383.9084 | 40.876 | 48.5992
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.6379 | 225.3796 | 29.273 | 4 | 1995.2143 | 2366.2838 | 40.6751 | 48.2399 | 261.337 | 0 | 113.5976 | 23658964.821 | 1465841.9576 | 24975624.1768 | 15542580.0717 | 0 | 0 | 0 | 25600774.3005 | 66607963.2891 | 45461303.6016 | 203313052.2184 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 233623678.2076 | 277072957.8214 | 237137.3706 | 117.092 | 1995.2143 | 2366.2838 | 40.6751 | 48.2399
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.24 | 228.8509 | 29.7239 | 4 | 1988.1677 | 2353.6087 | 40.5315 | 47.9815 | 260.5693 | 0 | 105.7352 | 23919545.905 | 1481609.6429 | 25282895.2159 | 15850233.1893 | 0 | 0 | 0 | 25948370.7417 | 67512337.9272 | 46078557.8751 | 206073550.4971 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 236384176.4864 | 279833456.1002 | 316227.766 | 118.8955 | 1988.1677 | 2353.6087 | 40.5315 | 47.9815
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.7742 | 231.4668 | 30.0636 | 4 | 1983.0587 | 2344.3696 | 40.4273 | 47.7931 | 259.9701 | 0 | 128.2477 | 24115183.4408 | 1493444.3637 | 25513830.4126 | 16085848.8935 | 0 | 0 | 0 | 26211239.7731 | 68196269.2251 | 46545355.0393 | 208161171.1482 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 238471797.1374 | 281921076.7512 | 421696.5034 | 120.2545 | 1983.0587 | 2344.3696 | 40.4273 | 47.7931
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.4468 | 233.4153 | 30.3167 | 4 | 1979.3587 | 2337.6535 | 40.3519 | 47.6562 | 259.5117 | 0 | 129.9685 | 24260504.8398 | 1502233.5147 | 25685505.6694 | 16263332.4561 | 0 | 0 | 0 | 26407514.8272 | 68706936.6542 | 46893896.0529 | 209719924.0142 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 240030550.0035 | 283479829.6173 | 562341.3252 | 121.2668 | 1979.3587 | 2337.6535 | 40.3519 | 47.6562
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.4884 | 234.8869 | 30.5079 | 4 | 1976.6286 | 2332.6785 | 40.2962 | 47.5548 | 259.1582 | 0 | 118.9232 | 24370040.4294 | 1508857.3085 | 25814980.6982 | 16398753.1266 | 0 | 0 | 0 | 26556126.3095 | 69093593.2468 | 47157797.1223 | 210900148.2414 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 241210774.2307 | 284660053.8444 | 749894.2093 | 122.0314 | 1976.6286 | 2332.6785 | 40.2962 | 47.5548
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.0205 | 235.982 | 30.6501 | 4 | 1974.6324 | 2329.0301 | 40.2556 | 47.4804 | 258.8912 | 0 | 130.138 | 24451423.442 | 1513778.1143 | 25911220.0889 | 16500282.856 | 0 | 0 | 0 | 26666914.7555 | 69381842.0574 | 47354532.8585 | 211779994.1726 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 242090620.1618 | 285539899.7756 | 1000000 | 122.6003 | 1974.6324 | 2329.0301 | 40.2556 | 47.4804
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 230.1795 | 236.8049 | 30.757 | 4 | 1973.1525 | 2326.3187 | 40.2254 | 47.4252 | 258.6883 | 0 | 143.7359 | 24512508.2151 | 1517471.2808 | 25983479.1146 | 16577026.0895 | 0 | 0 | 0 | 26750289.033 | 69598764.8251 | 47502587.1047 | 212442125.6629 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 242752751.6521 | 286202031.2659 | 1333521.4322 | 123.0279 | 1973.1525 | 2326.3187 | 40.2254 | 47.4252
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.0615 | 237.4279 | 30.8379 | 4 | 1972.0441 | 2324.2837 | 40.2028 | 47.3837 | 258.5331 | 0 | 149.637 | 24558710.4055 | 1520264.4744 | 26038146.32 | 16635397.221 | 0 | 0 | 0 | 26813482.1841 | 69763180.4416 | 47614804.1414 | 212943985.1881 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 243254611.1773 | 286703890.7911 | 1778279.41 | 123.3515 | 1972.0441 | 2324.2837 | 40.2028 | 47.3837
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.707 | 237.8824 | 30.8969 | 4 | 1971.2411 | 2322.8077 | 40.1864 | 47.3536 | 258.4195 | 0 | 134.6657 | 24592397.6989 | 1522300.9733 | 26078012.8635 | 16678106.8151 | 0 | 0 | 0 | 26859619.1568 | 69883219.3806 | 47696733.1838 | 213310390.0721 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 243621016.0614 | 287070295.6752 | 2371373.7057 | 123.5876 | 1971.2411 | 2322.8077 | 40.1864 | 47.3536
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.2166 | 238.2397 | 30.9433 | 4 | 1970.6144 | 2321.6537 | 40.1736 | 47.3301 | 258.3293 | 0 | 126.4428 | 24618869.2757 | 1523901.2038 | 26109344.3529 | 16711804.1102 | 0 | 0 | 0 | 26895928.3876 | 69977688.551 | 47761210.3338 | 213598746.2149 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 243909372.2042 | 287358651.8179 | 3162277.6602 | 123.7733 | 1970.6144 | 2321.6537 | 40.1736 | 47.3301
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.589 | 238.5005 | 30.9772 | 4 | 1970.1587 | 2320.8142 | 40.1644 | 47.3129 | 258.2634 | 0 | 134.813 | 24638183.5177 | 1525068.7355 | 26132206.8451 | 16736435.1591 | 0 | 0 | 0 | 26922438.7604 | 70046663.1031 | 47808286.8828 | 213809283.0038 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 244119908.993 | 287569188.6068 | 4216965.0343 | 123.9088 | 1970.1587 | 2320.8142 | 40.1644 | 47.3129
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.8669 | 238.6947 | 31.0024 | 4 | 1969.8204 | 2320.1905 | 40.1575 | 47.3002 | 258.2142 | 0 | 129.3872 | 24652565.5132 | 1525938.0994 | 26149232.2678 | 16754805.7693 | 0 | 0 | 0 | 26942191.2434 | 70098055.012 | 47843362.9167 | 213966150.8218 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 244276776.8111 | 287726056.4249 | 5623413.2519 | 124.0097 | 1969.8204 | 2320.1905 | 40.1575 | 47.3002
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 233.0689 | 238.8359 | 31.0208 | 4 | 1969.5748 | 2319.7377 | 40.1524 | 47.291 | 258.1784 | 0 | 144.2003 | 24663019.2586 | 1526569.999 | 26161608.1129 | 16768167.3016 | 0 | 0 | 0 | 26956552.2221 | 70135419.3327 | 47868864.8333 | 214080201.0603 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 244390827.0495 | 287840106.6633 | 7498942.0933 | 124.083 | 1969.5748 | 2319.7377 | 40.1524 | 47.291
1 | 7000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R245fa | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 233.2347 | 238.9514 | 31.0358 | 4 | 1969.3748 | 2319.3685 | 40.1484 | 47.2835 | 258.1489 | 0 | 136.9614 | 24671567.6132 | 1527086.7173 | 26171728.6599 | 16779123.6154 | 0 | 0 | 0 | 26968307.5763 | 70166004.353 | 47889739.7381 | 214173558.2733 | 961560.8286 | 29349065.1606 | 29349065.1606 | 1478867.319 | 12621347.1341 | 0 | 244484184.2625 | 287933463.8763 | 10000000 | 124.143 | 1969.3748 | 2319.3685 | 40.1484 | 47.2835

## Water (R600a)
Time [year] | Depth [m] | Res Length [m] | Temp Gradient [C/m] | Temp Surface Air [C] | Temp Surface Rock [C] | dT Approach [C] | Transmissivity [m^3] | Config Number [-] | Fluid | Reservoir | Cooling Wet/Dry | orcFluid | Method | Silica? | CostYear | mass flow [kg/s] | Reservoir Heat [MWth] | Electric Power I-P Pair [MWe] | N_IP_Multiplier | SpCC (Brownfield) [$/kWe] | SpCC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh] | Temp Production [C] | dP Surface [Mpa] | SolveTime [s] | C_T_G_N | C_pump_orc_N | C_coolingTowers_N | C_heatExchanger_N | C_recuperator_N | C_pump_prod_N | C_pump_inj_N | C_plant_otherEquipment_N | C_plant_installation_N | C_plant_indirectContingency_N | C_surfacePlant_N | C_gatheringSystem_N | C_wells_production_N | C_wells_injection_N | C_wellfield_N | C_exploration_N | C_stimulation_N | CapitalCost_N (Brownfield) | CapitalCost_N (Greenfield) | Trans [mD-m] | Electric Power 5-spot [MW] | Sp CC (Brownfield) [$/kWe] | Sp CC (Greenfield) [$/kWe] | LCOE (Brownfield) [$/MWh] | LCOE (Greenfield) [$/MWh]
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.4026 | [19 empty] | 100 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7734 | [19 empty] | 133.3521 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.2156 | [19 empty] | 177.8279 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.9966 | [19 empty] | 237.1374 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3271 | [19 empty] | 316.2278 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0098 | [19 empty] | 421.6965 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2675 | [19 empty] | 562.3413 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.252 | [19 empty] | 749.8942 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.887 | [19 empty] | 1000 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.9056 | [19 empty] | 1333.5214 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2574 | [19 empty] | 1778.2794 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5452 | [19 empty] | 2371.3737 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 34.2268 | [19 empty] | 3162.2777 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 38.627 | [19 empty] | 4216.965 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 38.5828 | [19 empty] | 5623.4133 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 37.9924 | [19 empty] | 7498.9421 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 37.1089 | [19 empty] | 10000 | 0
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0109 | 0.041866 | 9.8204e-05 | 4 | 11153194.5275 | 28186652.9281 | 227372.9563 | 574623.0452 | 50.6332 | 0 | 59.6255 | 20995.4124 | 957.4565 | 28505.8503 | 40336.1889 | 0 | 14598.1818 | 0 | 41103.3051 | 106942.3683 | 72990.3638 | 326429.127 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4381169.1544 | 11072208.4214 | 13335.2143 | 0.00039282 | 11153194.5275 | 28186652.9281 | 227372.9563 | 574623.0452
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3986 | 0.0609 | 0.00023541 | 4 | 4738471.4949 | 11844319.2209 | 96600.1507 | 241462.4679 | 51.6826 | 0 | 213.0439 | 27813.8141 | 1286.2019 | 38432.7715 | 47310.7984 | 0 | 16601.9399 | 0 | 51263.7551 | 133377.775 | 91033.0721 | 407120.128 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4461860.1554 | 11152899.4224 | 17782.7941 | 0.00094162 | 4738471.4949 | 11844319.2209 | 96600.1507 | 241462.4679
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.084829 | 0.00042849 | 4 | 2658241.6751 | 6562051.5451 | 54191.8521 | 133776.2966 | 52.4123 | 0 | 295.3352 | 35496.6021 | 1658.8507 | 50065.6392 | 56057.0713 | 0 | 18615.051 | 0 | 63138.3536 | 164273.0445 | 112119.7284 | 501424.3408 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4556164.3681 | 11247203.6352 | 23713.7371 | 0.001714 | 2658241.6751 | 6562051.5451 | 54191.8521 | 133776.2966
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.11548 | 0.000693 | 4 | 1684586.4871 | 4098380.3248 | 34342.5741 | 83551.0264 | 52.9453 | 0 | 397.2137 | 44398.2448 | 2092.428 | 64044.2687 | 67247.2343 | 0 | 20760.0531 | 0 | 77431.4693 | 201460.7997 | 137501.1354 | 614935.6332 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4669675.6606 | 11360714.9276 | 31622.7766 | 0.002772 | 1684586.4871 | 4098380.3248 | 34342.5741 | 83551.0264
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.156 | 0.0010494 | 4 | 1146284.0815 | 2740323.0957 | 23368.5515 | 55865.1929 | 53.3499 | 0 | 78.1893 | 55070.9052 | 2613.6633 | 81432.9623 | 82016.8378 | 0 | 23221.1192 | 0 | 95298.6402 | 247947.5134 | 169229.2727 | 756830.914 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4811570.9413 | 11502610.2084 | 42169.6503 | 0.0041975 | 1146284.0815 | 2740323.0957 | 23368.5515 | 55865.1929
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3749 | 0.20782 | 0.001525 | 4 | 816985.3447 | 1913860.0873 | 16655.3513 | 39016.6266 | 53.6497 | 0 | 72.5494 | 67514.2881 | 3222.7393 | 102407.9788 | 100896.1816 | 0 | 25885.0255 | 0 | 116971.2232 | 304335.1287 | 207714.9788 | 928947.5441 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 4983687.5714 | 11674726.8385 | 56234.1325 | 0.0061001 | 816985.3447 | 1913860.0873 | 16655.3513 | 39016.6266
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6971 | 0.27322 | 0.0021529 | 4 | 602745.6126 | 1379739.6731 | 12287.7846 | 28127.8595 | 53.8705 | 0 | 101.2258 | 81896.2252 | 3927.8975 | 127439.1711 | 124717.3569 | 0 | 28721.2692 | 0 | 143013.7488 | 372092.4382 | 253960.7348 | 1135768.8416 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5190508.8689 | 11881548.136 | 74989.4209 | 0.0086114 | 602745.6126 | 1379739.6731 | 12287.7846 | 28127.8595
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2977 | 0.35222 | 0.0029606 | 4 | 458443.8789 | 1023452.4807 | 9345.9986 | 20864.4631 | 54.019 | 0 | 107.0419 | 97875.789 | 4712.1042 | 156130.096 | 153513.7606 | 0 | 31490.6087 | 0 | 173051.7198 | 450245.0771 | 307301.5167 | 1374320.672 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5429060.6994 | 12120099.9664 | 100000 | 0.011842 | 458443.8789 | 1023452.4807 | 9345.9986 | 20864.4631
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5876 | 0.46586 | 0.0040659 | 4 | 354158.7655 | 765572.265 | 7220.0055 | 15607.2261 | 54.1752 | 0 | 95.4809 | 119110.5617 | 5756.2779 | 195244.5716 | 194852.0531 | 0 | 35567.7136 | 0 | 214707.1594 | 558623.9862 | 381272.3492 | 1705134.6726 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 5759874.6999 | 12450913.967 | 133352.1432 | 0.016264 | 354158.7655 | 765572.265 | 7220.0055 | 15607.2261
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2166 | 0.59606 | 0.0054499 | 4 | 280841.8319 | 587773.3083 | 5725.3406 | 11982.5539 | 54.2715 | 0 | 95.2499 | 141520.3583 | 6858.6889 | 237775.4051 | 242247.4003 | 0 | 39141.3789 | 0 | 260341.8603 | 677356.1169 | 462309.4681 | 2067550.6767 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 6122290.704 | 12813329.9711 | 177827.941 | 0.0218 | 280841.8319 | 587773.3083 | 5725.3406 | 11982.5539
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.405 | 0.75398 | 0.0071941 | 4 | 227482.9099 | 460002.3638 | 4637.5468 | 9377.7704 | 54.3444 | 0 | 109.3555 | 166774.3983 | 8101.6877 | 286939.8381 | 299729.6709 | 0 | 42833.6007 | 0 | 313707.8863 | 816203.5699 | 557075.7077 | 2491366.3596 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 6546106.3869 | 13237145.654 | 237137.3706 | 0.028776 | 227482.9099 | 460002.3638 | 4637.5468 | 9377.7704
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.1271 | 0.93834 | 0.0093298 | 4 | 188223.1857 | 367515.3773 | 3837.1842 | 7492.2981 | 54.399 | 0 | 92.3933 | 194295.6033 | 9456.7265 | 341798.2711 | 366836.0112 | 0 | 46397.227 | 0 | 373925.6972 | 972877.9615 | 664009.1994 | 2969596.6973 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 7024336.7246 | 13715375.9917 | 316227.766 | 0.037319 | 188223.1857 | 367515.3773 | 3837.1842 | 7492.2981
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.2929 | 1.1447 | 0.011849 | 4 | 159151.0063 | 300321.3762 | 3244.5085 | 6122.4575 | 54.4398 | 0 | 99.3 | 223216.6811 | 10880.9078 | 400696.5307 | 441943.3407 | 0 | 49591.3115 | 0 | 439268.221 | 1142885.8047 | 780043.0457 | 3488525.8431 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 7543265.8704 | 14234305.1375 | 421696.5034 | 0.047397 | 159151.0063 | 300321.3762 | 3244.5085 | 6122.4575
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.7265 | 1.3643 | 0.014685 | 4 | 137561.225 | 251468.2892 | 2804.3716 | 5126.5212 | 54.47 | 0 | 88.2967 | 252315.5599 | 12313.8652 | 461093.3472 | 521885.3154 | 0 | 52180.0121 | 0 | 506917.3589 | 1318894.9848 | 900172.9277 | 4025773.3711 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 8080513.3984 | 14771552.6654 | 562341.3252 | 0.058741 | 137561.225 | 251468.2892 | 2804.3716 | 5126.5212
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2017 | 1.5861 | 0.017712 | 4 | 121523.8975 | 215964.4587 | 2477.429 | 4402.7276 | 54.4925 | 0 | 94.6441 | 280289.1707 | 13691.2967 | 520113.685 | 602581.7827 | 0 | 54024.5134 | 0 | 573573.1749 | 1492319.745 | 1018538.8901 | 4555132.2583 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 8609872.2856 | 15300911.5527 | 749894.2093 | 0.070849 | 121523.8975 | 215964.4587 | 2477.429 | 4402.7276
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4593 | 1.797 | 0.02076 | 4 | 109624.0817 | 190201.1736 | 2234.8352 | 3877.5082 | 54.5089 | 0 | 116.0008 | 305830.6764 | 14948.7945 | 574747.7687 | 679356.4908 | 0 | 55054.3346 | 0 | 635675.8453 | 1653898.1545 | 1128819.4746 | 5048331.5393 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9103071.5667 | 15794110.8337 | 1000000 | 0.083039 | 109624.0817 | 190201.1736 | 2234.8352 | 3877.5082
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.2844 | 1.9866 | 0.023655 | 4 | 100805.4199 | 171519.3856 | 2055.0548 | 3496.6547 | 54.5208 | 0 | 118.0067 | 328020.5325 | 16041.0949 | 622746.2338 | 748335.3443 | 0 | 55324.7709 | 0 | 690482.5108 | 1796493.8556 | 1226143.9707 | 5483588.3133 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9538328.3406 | 16229367.6077 | 1333521.4322 | 0.094621 | 100805.4199 | 171519.3856 | 2055.0548 | 3496.6547
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5823 | 2.15 | 0.026275 | 4 | 94274.1235 | 157938.3693 | 1921.9055 | 3219.7873 | 54.5294 | 0 | 135.5545 | 346645.8988 | 16957.7706 | 663395.0269 | 807805.9126 | 0 | 55051.0722 | 0 | 737043.7156 | 1917636.5596 | 1308826.3554 | 5853362.3118 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 9908102.3391 | 16599141.6061 | 1778279.41 | 0.1051 | 94274.1235 | 157938.3693 | 1921.9055 | 3219.7873
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.3233 | 2.2858 | 0.028545 | 4 | 89435.4358 | 148036.3838 | 1823.2623 | 3017.9219 | 54.5354 | 0 | 113.8379 | 361803.3678 | 17703.641 | 696707.7817 | 857231.8235 | 0 | 54434.5635 | 0 | 775273.6592 | 2017103.0307 | 1376714.2658 | 6156972.1332 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10211712.1605 | 16902751.4276 | 2371373.7057 | 0.11418 | 89435.4358 | 148036.3838 | 1823.2623 | 3017.9219
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.5398 | 2.3956 | 0.030446 | 4 | 85846.9208 | 140788.7252 | 1750.1056 | 2870.1686 | 54.5396 | 0 | 108.9799 | 373861.4261 | 18296.9029 | 723353.1256 | 897196.1765 | 0 | 53655.82 | 0 | 805881.746 | 2096738.9939 | 1431067.447 | 6400051.6381 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10454791.6654 | 17145830.9324 | 3162277.6602 | 0.12178 | 85846.9208 | 140788.7252 | 1750.1056 | 2870.1686
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.2861 | 2.4821 | 0.031992 | 4 | 83181.6183 | 135467.8354 | 1695.7698 | 2761.6951 | 54.5426 | 0 | 111.5998 | 383243.1806 | 18758.4274 | 744171.1112 | 928679.7973 | 0 | 52828.3571 | 0 | 829795.5407 | 2158957.7824 | 1473533.0486 | 6589967.2453 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10644707.2726 | 17335746.5396 | 4216965.0343 | 0.12797 | 83181.6183 | 135467.8354 | 1695.7698 | 2761.6951
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.646 | 2.5494 | 0.033226 | 4 | 81198.8345 | 131543.8455 | 1655.3481 | 2681.6992 | 54.5446 | 0 | 129.5315 | 390479.4537 | 19114.3675 | 760279.3132 | 953193.8379 | 0 | 52049.4509 | 0 | 848295.405 | 2207090.6345 | 1506384.7092 | 6736887.1718 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10791627.1991 | 17482666.4662 | 5623413.2519 | 0.1329 | 81198.8345 | 131543.8455 | 1655.3481 | 2681.6992
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.7003 | 2.6016 | 0.034197 | 4 | 79721.5405 | 128636.783 | 1625.2314 | 2622.4348 | 54.5461 | 0 | 130.7423 | 396048.9794 | 19388.298 | 772707.215 | 972197.0446 | 0 | 51374.1685 | 0 | 862569.1252 | 2244227.9265 | 1531731.6741 | 6850244.4314 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10904984.4587 | 17596023.7258 | 7498942.0933 | 0.13679 | 79721.5405 | 128636.783 | 1625.2314 | 2622.4348
1 | 1000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.5117 | 2.6418 | 0.034953 | 4 | 78619.3894 | 126476.8732 | 1602.7626 | 2578.4021 | 54.5472 | 0 | 120.426 | 400312.1911 | 19597.9638 | 782237.6593 | 986822.3323 | 0 | 50812.7209 | 0 | 873515.3183 | 2272707.6756 | 1551169.688 | 6937175.5493 | 961560.8286 | 3093179.1987 | 3093179.1987 | 1478867.319 | 2118992.7493 | 0 | 10991915.5766 | 17682954.8437 | 10000000 | 0.13981 | 78619.3894 | 126476.8732 | 1602.7626 | 2578.4021
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 14.6851 | [19 empty] | 100 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.7414 | [19 empty] | 133.3521 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.3025 | [19 empty] | 177.8279 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6256 | [19 empty] | 237.1374 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.385 | [19 empty] | 316.2278 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3306 | [19 empty] | 421.6965 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.3953 | [19 empty] | 562.3413 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6866 | [19 empty] | 749.8942 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8031 | [19 empty] | 1000 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4224 | [19 empty] | 1333.5214 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2141 | [19 empty] | 1778.2794 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.4958 | [19 empty] | 2371.3737 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 35.8525 | [19 empty] | 3162.2777 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 38.4787 | [19 empty] | 4216.965 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 37.2466 | [19 empty] | 5623.4133 | 0
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.043011 | 0.00012906 | 4 | 9024159.1045 | 22702765.9648 | 183969.6894 | 462826.592 | 53.3263 | 0 | 62.0355 | 22825.457 | 1059.9255 | 29052.2976 | 40058.0546 | 0 | 16554.7239 | 0 | 42724.6788 | 111160.8503 | 75869.5645 | 339305.5522 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4658770.9984 | 11720425.852 | 7498.9421 | 0.00051626 | 9024159.1045 | 22702765.9648 | 183969.6894 | 462826.592
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2625 | 0.062636 | 0.00031945 | 4 | 3711725.874 | 9238116.3876 | 75668.5524 | 188331.498 | 54.6644 | 0 | 188.7305 | 30372.9745 | 1432.4254 | 39194.9093 | 46861.2818 | 0 | 18840.1877 | 0 | 53313.6937 | 138711.295 | 94673.3091 | 423400.0766 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4742865.5228 | 11804520.3764 | 10000 | 0.0012778 | 3711725.874 | 9238116.3876 | 75668.5524 | 188331.498
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.089368 | 0.00059054 | 4 | 2052981.6971 | 5042494.554 | 41852.8088 | 102798.072 | 55.6679 | 0 | 263.9589 | 39560.2142 | 1888.9839 | 52035.904 | 56093.1646 | 0 | 21531.2334 | 0 | 66732.705 | 173624.8098 | 118502.5003 | 529969.5152 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4849434.9614 | 11911089.815 | 13335.2143 | 0.0023621 | 2052981.6971 | 5042494.554 | 41852.8088 | 102798.072
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2932 | 0.12178 | 0.00096245 | 4 | 1290901.8258 | 3125199.0558 | 26316.7798 | 63711.4099 | 56.3545 | 0 | 361.171 | 49597.2336 | 2389.9231 | 66609.6315 | 67260.407 | 0 | 24081.2101 | 0 | 81875.9781 | 213024.4999 | 145393.5984 | 650232.4816 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 4969697.9278 | 12031352.7814 | 17782.7941 | 0.0038498 | 1290901.8258 | 3125199.0558 | 26316.7798 | 63711.4099
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0519 | 0.1655 | 0.0014667 | 4 | 873210.0438 | 2076864.7669 | 17801.5678 | 42339.6974 | 56.8884 | 0 | 61.0203 | 61875.0629 | 3004.4352 | 85093.5209 | 82299.8954 | 0 | 27157.5448 | 0 | 101177.8791 | 263244.087 | 179669.4985 | 803521.9238 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5122987.37 | 12184642.2236 | 23713.7371 | 0.0058668 | 873210.0438 | 2076864.7669 | 17801.5678 | 42339.6974
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0071 | 0.22065 | 0.0021404 | 4 | 619706.8222 | 1444519.9664 | 12633.5618 | 29448.4934 | 57.2788 | 0 | 61.6758 | 75976.4522 | 3711.6384 | 107069.219 | 101251.3609 | 0 | 30391.9196 | 0 | 124176.2302 | 323081.0788 | 220509.475 | 986167.3741 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5305632.8203 | 12367287.6739 | 31622.7766 | 0.0085615 | 619706.8222 | 1444519.9664 | 12633.5618 | 29448.4934
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2561 | 0.29282 | 0.0030369 | 4 | 455477.0729 | 1036791.2972 | 9285.5162 | 21136.393 | 57.5773 | 0 | 99.6069 | 92850.3738 | 4559.167 | 134233.9499 | 126039.6597 | 0 | 34132.4367 | 0 | 152808.079 | 397575.2762 | 271353.2954 | 1213552.2377 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5533017.6839 | 12594672.5375 | 42169.6503 | 0.012148 | 455477.0729 | 1036791.2972 | 9285.5162 | 21136.393
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7862 | 0.38113 | 0.0042046 | 4 | 344727.3429 | 764604.3696 | 7027.7332 | 15587.4943 | 57.7856 | 0 | 81.1788 | 111800.547 | 5511.8097 | 165711.9257 | 156380.4462 | 0 | 37886.7816 | 0 | 186143.689 | 484307.6954 | 330549.9536 | 1478292.8482 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 5797758.2944 | 12859413.148 | 56234.1325 | 0.016818 | 344727.3429 | 764604.3696 | 7027.7332 | 15587.4943
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.2586 | 0.52418 | 0.0058233 | 4 | 266663.2466 | 569824.8656 | 5436.291 | 11616.6506 | 57.9939 | 0 | 92.5273 | 139882.5883 | 6925.4317 | 213794.1387 | 205480.2378 | 0 | 44787.641 | 0 | 238239.3146 | 619849.827 | 423060.2436 | 1892019.4227 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 6211484.8689 | 13273139.7225 | 74989.4209 | 0.023293 | 266663.2466 | 569824.8656 | 5436.291 | 11616.6506
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3586 | 0.64574 | 0.0077856 | 4 | 210027.1964 | 436779.5378 | 4281.6885 | 8904.3417 | 58.1024 | 0 | 90.2245 | 161926.2612 | 8035.8323 | 252588.3141 | 247194.0068 | 0 | 47447.4559 | 0 | 279704.8294 | 727734.5908 | 496693.8116 | 2221325.1021 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 6540790.5483 | 13602445.4019 | 100000 | 0.031143 | 210027.1964 | 436779.5378 | 4281.6885 | 8904.3417
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4324 | 0.82352 | 0.010356 | 4 | 169247.1141 | 339718.2624 | 3450.3313 | 6925.6163 | 58.1996 | 0 | 106.9711 | 191988.9467 | 9550.3424 | 306809.4811 | 308218.8371 | 0 | 52423.1011 | 0 | 338906.3763 | 881764.8719 | 601822.6436 | 2691484.6003 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 7010950.0466 | 14072604.9001 | 133352.1432 | 0.041424 | 169247.1141 | 339718.2624 | 3450.3313 | 6925.6163
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1332 | 1.0376 | 0.01358 | 4 | 139113.5426 | 269113.8567 | 2836.0177 | 5486.25 | 58.2733 | 0 | 103.8336 | 225676.3406 | 11247.6803 | 369079.4726 | 381695.5225 | 0 | 57492.3206 | 0 | 407624.6213 | 1060555.6492 | 723851.0228 | 3237222.6299 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 7556688.0762 | 14618342.9297 | 177827.941 | 0.05432 | 139113.5426 | 269113.8567 | 2836.0177 | 5486.25
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4381 | 1.2866 | 0.017511 | 4 | 116647.6314 | 217467.5592 | 2378.0197 | 4433.3703 | 58.3289 | 0 | 100.8926 | 262314.8096 | 13093.6248 | 438365.4274 | 467167.7076 | 0 | 62352.6254 | 0 | 484884.736 | 1261570.6195 | 861047.8705 | 3850797.4208 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 8170262.8671 | 15231917.7206 | 237137.3706 | 0.070042 | 116647.6314 | 217467.5592 | 2378.0197 | 4433.3703
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.2318 | 1.5639 | 0.022123 | 4 | 99810.5829 | 179609.2949 | 2034.7737 | 3661.5784 | 58.3705 | 0 | 96.3549 | 300681.0311 | 15026.265 | 512435.0869 | 562352.0362 | 0 | 66637.4015 | 0 | 568281.4101 | 1478551.6585 | 1009141.8881 | 4513106.7774 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 8832572.2237 | 15894227.0772 | 316227.766 | 0.088493 | 99810.5829 | 179609.2949 | 2034.7737 | 3661.5784
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.3667 | 1.8611 | 0.027311 | 4 | 87168.1701 | 151808.1193 | 1777.0411 | 3094.8138 | 58.4018 | 0 | 102.3643 | 339575.1068 | 16984.9479 | 588918.2579 | 664316.7425 | 0 | 70179.4439 | 0 | 655190.0546 | 1704670.1242 | 1163472.3872 | 5203307.065 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 9522772.5112 | 16584427.3648 | 421696.5034 | 0.10925 | 87168.1701 | 151808.1193 | 1777.0411 | 3094.8138
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.507 | 2.1585 | 0.032815 | 4 | 77682.5495 | 131480.9726 | 1583.6638 | 2680.4175 | 58.4249 | 0 | 117.9988 | 376688.986 | 18853.3521 | 663071.4675 | 766395.5079 | 0 | 72559.7547 | 0 | 740051.9366 | 1925463.3334 | 1314168.2894 | 5877252.6274 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 10196718.0737 | 17258372.9272 | 562341.3252 | 0.13126 | 77682.5495 | 131480.9726 | 1583.6638 | 2680.4175
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.423 | 2.443 | 0.038352 | 4 | 70582.1098 | 116614.2013 | 1438.9118 | 2377.3382 | 58.4418 | 0 | 118.5184 | 410774.9928 | 20568.6999 | 732092.894 | 864019.5412 | 0 | 73869.8005 | 0 | 819517.1121 | 2132215.4196 | 1455280.8365 | 6508339.2967 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 10827804.7429 | 17889459.5965 | 749894.2093 | 0.15341 | 70582.1098 | 116614.2013 | 1438.9118 | 2377.3382
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.8297 | 2.6979 | 0.043592 | 4 | 65281.2234 | 105779.4828 | 1330.846 | 2156.4578 | 58.4537 | 0 | 105.3771 | 440327.715 | 22055.3595 | 792597.2855 | 951523.6554 | 0 | 74090.1708 | 0 | 889431.7326 | 2314118.9207 | 1579433.7138 | 7063578.5532 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 11383043.9995 | 18444698.853 | 1000000 | 0.17437 | 65281.2234 | 105779.4828 | 1330.846 | 2156.4578
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.6151 | 2.9169 | 0.048313 | 4 | 61331.606 | 97872.4061 | 1250.3277 | 1995.2614 | 58.4617 | 0 | 121.6385 | 465043.1356 | 23298.2267 | 843647.3432 | 1026677.8415 | 0 | 73524.0801 | 0 | 948554.3445 | 2467943.8293 | 1684422.3746 | 7533111.1755 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 11852576.6218 | 18914231.4753 | 1333521.4322 | 0.19325 | 61331.606 | 97872.4061 | 1250.3277 | 1995.2614
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.748 | 3.0981 | 0.052388 | 4 | 58391.4081 | 92090.0847 | 1190.3878 | 1877.3809 | 58.4669 | 0 | 133.8361 | 485070.841 | 24305.0251 | 885305.0834 | 1088864.6854 | 0 | 72468.017 | 0 | 996845.3242 | 2593587.0525 | 1770176.4562 | 7916622.4849 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12236087.9311 | 19297742.7847 | 1778279.41 | 0.20955 | 58391.4081 | 92090.0847 | 1190.3878 | 1877.3809
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.287 | 3.2448 | 0.055797 | 4 | 56202.4987 | 87842.6544 | 1145.764 | 1790.7913 | 58.4702 | 0 | 131.2607 | 501035.7981 | 25107.3505 | 918694.3777 | 1139248.4436 | 0 | 71225.2333 | 0 | 1035571.3692 | 2694344.2779 | 1838945.3329 | 8224172.1831 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12543637.6294 | 19605292.483 | 2371373.7057 | 0.22319 | 56202.4987 | 87842.6544 | 1145.764 | 1790.7913
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.2936 | 3.3607 | 0.058568 | 4 | 54571.8103 | 84715.0111 | 1112.5202 | 1727.0301 | 58.4722 | 0 | 124.2864 | 513492.9851 | 25733.2338 | 944858.1196 | 1179056.8367 | 0 | 69952.9401 | 0 | 1065906.705 | 2773270.5988 | 1892814.1687 | 8465085.5878 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12784551.034 | 19846205.8876 | 3162277.6602 | 0.23427 | 54571.8103 | 84715.0111 | 1112.5202 | 1727.0301
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8381 | 3.4499 | 0.060764 | 4 | 53355.8306 | 82409.3185 | 1087.7308 | 1680.0254 | 58.4734 | 0 | 141.9132 | 522989.0027 | 26210.2416 | 964867.0957 | 1209691.6415 | 0 | 68730.4801 | 0 | 1089070.5 | 2833538.0419 | 1933947.937 | 8649044.9405 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 12968510.3868 | 20030165.2403 | 4216965.0343 | 0.24306 | 53355.8306 | 82409.3185 | 1087.7308 | 1680.0254
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.0561 | 3.5202 | 0.062505 | 4 | 52448.1864 | 80692.7289 | 1069.2272 | 1645.0304 | 58.4741 | 0 | 129.8971 | 530422.2338 | 26583.5688 | 980568.3303 | 1233845.4226 | 0 | 67723.2495 | 0 | 1107265.694 | 2880878.2043 | 1966258.5706 | 8793545.2739 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13113010.7202 | 20174665.5737 | 5623413.2519 | 0.25002 | 52448.1864 | 80692.7289 | 1069.2272 | 1645.0304
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.9723 | 3.5731 | 0.063845 | 4 | 51770.0682 | 79421.5329 | 1055.4029 | 1619.1154 | 58.4746 | 0 | 147.1769 | 535982.5471 | 26862.7937 | 992335.549 | 1252012.6426 | 0 | 66842.7183 | 0 | 1120874.1377 | 2916284.5835 | 1990424.1519 | 8901619.1238 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13221084.5701 | 20282739.4236 | 7498942.0933 | 0.25538 | 51770.0682 | 79421.5329 | 1055.4029 | 1619.1154
1 | 1100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.6808 | 3.614 | 0.064883 | 4 | 51263.0318 | 78472.0805 | 1045.0662 | 1599.7595 | 58.4748 | 0 | 141.2381 | 540263.6032 | 27077.7557 | 1001408.3762 | 1266057.9397 | 0 | 66149.3414 | 0 | 1131373.2363 | 2943601.0844 | 2009068.225 | 8984999.5619 | 961560.8286 | 3357904.6176 | 3357904.6176 | 1478867.319 | 2224882.9169 | 0 | 13304465.0082 | 20366119.8618 | 10000000 | 0.25953 | 51263.0318 | 78472.0805 | 1045.0662 | 1599.7595
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 17.3771 | [19 empty] | 100 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4354 | [19 empty] | 133.3521 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2233 | [19 empty] | 177.8279 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2383 | [19 empty] | 237.1374 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7051 | [19 empty] | 316.2278 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.7312 | [19 empty] | 421.6965 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6418 | [19 empty] | 562.3413 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2395 | [19 empty] | 749.8942 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6498 | [19 empty] | 1000 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.2484 | [19 empty] | 1333.5214 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 32.1603 | [19 empty] | 1778.2794 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 35.4336 | [19 empty] | 2371.3737 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 39.2035 | [19 empty] | 3162.2777 | 0
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.03678 | 7.881e-05 | 4 | 15565922.224 | 39168448.1797 | 317332.379 | 798501.7954 | 54.93 | 0 | 76.224 | 21254.1507 | 994.0509 | 25594.8526 | 37400.5541 | 0 | 17092.1471 | 0 | 39910.9446 | 103840.091 | 70872.9958 | 316959.7868 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 4907010.7428 | 12347485.3101 | 4216.965 | 0.00031524 | 15565922.224 | 39168448.1797 | 317332.379 | 798501.7954
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0452 | 0.056935 | 0.00029166 | 4 | 4283953.5021 | 10661583.1186 | 87334.1866 | 217350.7927 | 57.0048 | 0 | 70.9377 | 29880.2185 | 1427.8748 | 36233.7506 | 44072.323 | 0 | 20061.2351 | 0 | 51353.4068 | 133611.0304 | 91192.2737 | 407832.1127 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 4997883.0688 | 12438357.636 | 5623.4133 | 0.0011667 | 4283953.5021 | 10661583.1186 | 87334.1866 | 217350.7927
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.082689 | 0.00060336 | 4 | 2114744.8891 | 5197665.2684 | 43111.935 | 105961.4369 | 58.4131 | 0 | 238.9182 | 39604.2645 | 1921.1836 | 48775.571 | 52519.1219 | 0 | 23062.419 | 0 | 64694.1983 | 168321.0335 | 114882.564 | 513780.3556 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5103831.3117 | 12544305.8789 | 7498.9421 | 0.0024135 | 2114744.8891 | 5197665.2684 | 43111.935 | 105961.4369
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.11472 | 0.0010398 | 4 | 1256545.7534 | 3045544.946 | 25616.3848 | 62087.5531 | 59.3978 | 0 | 339.8277 | 50472.0172 | 2475.8001 | 63323.5016 | 62991.476 | 0 | 26061.6072 | 0 | 80076.5168 | 208342.6708 | 142198.1538 | 635941.7436 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5225992.6996 | 12666467.2669 | 10000 | 0.004159 | 1256545.7534 | 3045544.946 | 25616.3848 | 62087.5531
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.15708 | 0.0016372 | 4 | 821194.5116 | 1957372.3738 | 16741.1609 | 39903.6834 | 60.1457 | 0 | 469.2165 | 63477.3891 | 3142.0654 | 81362.7411 | 76814.8925 | 0 | 29523.6616 | 0 | 99185.0924 | 258059.2647 | 176130.7507 | 787695.8575 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5377746.8135 | 12818221.3808 | 13335.2143 | 0.0065487 | 821194.5116 | 1957372.3738 | 16741.1609 | 39903.6834
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.21237 | 0.0024426 | 4 | 569516.7343 | 1331053.2048 | 11610.369 | 27135.32 | 60.7069 | 0 | 79.2192 | 78876.0074 | 3932.5898 | 103511.4715 | 94828.9669 | 0 | 33427.856 | 0 | 122684.9877 | 319201.1719 | 217861.3588 | 974324.4101 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5564375.3661 | 13004849.9334 | 17782.7941 | 0.0097703 | 569516.7343 | 1331053.2048 | 11610.369 | 27135.32
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4675 | 0.28315 | 0.0035179 | 4 | 411486.6066 | 940240.881 | 8388.7111 | 19168.0821 | 61.1247 | 0 | 81.0052 | 96851.01 | 4856.8538 | 130244.9968 | 117869.6203 | 0 | 37703.9057 | 0 | 151135.2907 | 393223.0244 | 268382.7941 | 1200267.4958 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 5790318.4518 | 13230793.0191 | 23713.7371 | 0.014072 | 411486.6066 | 940240.881 | 8388.7111 | 19168.0821
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8091 | 0.37218 | 0.0049372 | 4 | 306859.1246 | 683615.8179 | 6255.7383 | 13936.4331 | 61.4321 | 0 | 117.4013 | 117562.9136 | 5922.8478 | 162043.1744 | 146840.367 | 0 | 42255.6522 | 0 | 185103.7324 | 481601.9417 | 328703.2212 | 1470033.8502 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6060084.8062 | 13500559.3735 | 31622.7766 | 0.019749 | 306859.1246 | 683615.8179 | 6255.7383 | 13936.4331
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4487 | 0.4807 | 0.0067683 | 4 | 235406.9032 | 510234.483 | 4799.0881 | 10401.8201 | 61.6396 | 0 | 105.7368 | 140783.6505 | 7118.0972 | 198811.6969 | 182183.5773 | 0 | 46831.7301 | 0 | 224534.2133 | 584191.9647 | 398723.0198 | 1783177.9499 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6373228.9059 | 13813703.4732 | 42169.6503 | 0.027073 | 235406.9032 | 510234.483 | 4799.0881 | 10401.8201
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7728 | 0.63554 | 0.0092839 | 4 | 183197.1516 | 383555.9409 | 3734.7217 | 7819.3067 | 61.8604 | 0 | 100.6313 | 171422.9595 | 8698.1034 | 248525.5573 | 232483.6764 | 0 | 53410.2446 | 0 | 278670.8111 | 725044.2871 | 494857.6241 | 2213113.2635 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 6803164.2195 | 14243638.7868 | 56234.1325 | 0.037136 | 183197.1516 | 383555.9409 | 3734.7217 | 7819.3067
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4964 | 0.81651 | 0.012462 | 4 | 146090.8579 | 295355.2712 | 2978.2597 | 6021.2167 | 61.9973 | 0 | 119.5385 | 204396.2961 | 10397.7829 | 303651.1866 | 291331.7764 | 0 | 59454.1557 | 0 | 339000.1671 | 882008.8963 | 601989.1952 | 2692229.4563 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 7282280.4123 | 14722754.9796 | 74989.4209 | 0.049848 | 146090.8579 | 295355.2712 | 2978.2597 | 6021.2167
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.8675 | 1.0405 | 0.016529 | 4 | 118766.9906 | 231304.3412 | 2421.2257 | 4715.4519 | 62.1022 | 0 | 132.2611 | 242265.5882 | 12349.9489 | 368590.2874 | 364157.3434 | 0 | 65924.8169 | 0 | 410782.3141 | 1068771.3182 | 729458.3857 | 3262300.0028 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 7852350.9589 | 15292825.5262 | 100000 | 0.066116 | 118766.9906 | 231304.3412 | 2421.2257 | 4715.4519
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8971 | 1.3082 | 0.021617 | 4 | 98402.5775 | 184451.1738 | 2006.0696 | 3760.2867 | 62.1814 | 0 | 113.9975 | 284428.8833 | 14523.0757 | 442655.5797 | 451212.7261 | 0 | 72381.6524 | 0 | 493428.7477 | 1283800.3855 | 876220.1425 | 3918651.193 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 8508702.149 | 15949176.7163 | 133352.1432 | 0.086468 | 98402.5775 | 184451.1738 | 2006.0696 | 3760.2867
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.5982 | 1.6205 | 0.027826 | 4 | 83092.927 | 149941.5243 | 1693.9617 | 3056.7608 | 62.2415 | 0 | 110.4206 | 330456.3944 | 16894.5826 | 525335.0638 | 552780.4428 | 0 | 78599.0362 | 0 | 586585.5527 | 1526175.2829 | 1041645.9904 | 4658472.3458 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 9248523.3018 | 16688997.8691 | 177827.941 | 0.1113 | 83092.927 | 149941.5243 | 1693.9617 | 3056.7608
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8971 | 1.9727 | 0.035151 | 4 | 71523.5097 | 124440.7737 | 1458.1035 | 2536.8935 | 62.2871 | 0 | 115.5637 | 379251.9661 | 19407.5998 | 614796.9325 | 667269.6499 | 0 | 84247.1114 | 0 | 688339.5713 | 1790918.3666 | 1222338.5849 | 5466569.7824 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 10056620.7385 | 17497095.3057 | 237137.3706 | 0.14061 | 71523.5097 | 124440.7737 | 1458.1035 | 2536.8935
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5728 | 2.3499 | 0.043407 | 4 | 62764.6242 | 105617.3844 | 1279.5418 | 2153.1532 | 62.3214 | 0 | 119.0167 | 428710.3157 | 21953.4435 | 707147.221 | 789908.7127 | 0 | 88825.5965 | 0 | 794252.6628 | 2066482.5051 | 1410416.7717 | 6307697.2289 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 10897748.1849 | 18338222.7522 | 316227.766 | 0.17363 | 62764.6242 | 105617.3844 | 1279.5418 | 2153.1532
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.3534 | 2.734 | 0.052248 | 4 | 56141.0922 | 91742.9912 | 1144.5121 | 1870.305 | 62.3468 | 0 | 126.8271 | 476701.2038 | 24422.3828 | 798198.2356 | 914816.4107 | 0 | 92075.5708 | 0 | 899423.3834 | 2340115.1466 | 1597176.6721 | 7142929.0057 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 11732979.9617 | 19173454.529 | 421696.5034 | 0.20899 | 56141.0922 | 91742.9912 | 1144.5121 | 1870.305
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.8614 | 3.1001 | 0.06115 | 4 | 51148.2033 | 81567.0478 | 1042.7253 | 1662.8546 | 62.3648 | 0 | 129.4981 | 520580.7876 | 26678.512 | 882585.3192 | 1033826.2368 | 0 | 93705.1159 | 0 | 997376.6289 | 2594969.3983 | 1771119.9356 | 7920841.9342 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 12510892.8902 | 19951367.4575 | 562341.3252 | 0.2446 | 51148.2033 | 81567.0478 | 1042.7253 | 1662.8546
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.8675 | 3.4326 | 0.069645 | 4 | 47398.6859 | 74107.2941 | 966.2863 | 1510.7774 | 62.3768 | 0 | 125.106 | 559117.9668 | 28658.7991 | 957537.8664 | 1141968.5634 | 0 | 93973.75 | 0 | 1084690.2088 | 2822141.4228 | 1926169.5103 | 8614258.0876 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 13204309.0436 | 20644783.6109 | 749894.2093 | 0.27858 | 47398.6859 | 74107.2941 | 966.2863 | 1510.7774
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.1787 | 3.7189 | 0.07732 | 4 | 44591.6314 | 68649.0072 | 909.0607 | 1399.5029 | 62.384 | 0 | 136.4424 | 591392.3536 | 30316.3226 | 1020889.2549 | 1235065.5089 | 0 | 93118.8541 | 0 | 1158605.0948 | 3014452.794 | 2057425.9727 | 9201266.1557 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 13791317.1118 | 21231791.679 | 1000000 | 0.30928 | 44591.6314 | 68649.0072 | 909.0607 | 1399.5029
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.7675 | 3.9569 | 0.08397 | 4 | 42494.0951 | 64646.1456 | 866.2996 | 1317.8991 | 62.3879 | 0 | 132.6749 | 617667.6354 | 31665.0409 | 1072845.4568 | 1312527.256 | 0 | 91596.4984 | 0 | 1219257.7361 | 3172258.5253 | 2165131.6269 | 9682949.7759 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14273000.732 | 21713475.2992 | 1333521.4322 | 0.33588 | 42494.0951 | 64646.1456 | 866.2996 | 1317.8991
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.6614 | 4.1488 | 0.089528 | 4 | 40927.9145 | 61704.978 | 834.3709 | 1257.9394 | 62.3897 | 0 | 146.5064 | 638488.6346 | 32733.2958 | 1114255.476 | 1374960.4327 | 0 | 89746.5348 | 0 | 1267571.9058 | 3297962.0841 | 2250926.8887 | 10066645.2524 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14656696.2084 | 22097170.7757 | 1778279.41 | 0.35811 | 40927.9145 | 61704.978 | 834.3709 | 1257.9394
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.9607 | 4.3011 | 0.09406 | 4 | 39758.4658 | 59534.4389 | 810.5301 | 1213.6901 | 62.3902 | 0 | 153.8461 | 654810.2323 | 33570.3746 | 1146863.3705 | 1424546.6972 | 0 | 87884.412 | 0 | 1305593.2838 | 3396885.9103 | 2318444.4328 | 10368598.7135 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 14958649.6695 | 22399124.2368 | 2371373.7057 | 0.37624 | 39758.4658 | 59534.4389 | 810.5301 | 1213.6901
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.7512 | 4.4196 | 0.097672 | 4 | 38884.8767 | 57929.4058 | 792.7208 | 1180.9693 | 62.3901 | 0 | 152.4144 | 667388.1545 | 34215.2464 | 1172079.4798 | 1463144.1911 | 0 | 86145.8345 | 0 | 1334959.4335 | 3473290.6081 | 2370592.209 | 10601815.157 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15191866.113 | 22632340.6803 | 3162277.6602 | 0.39069 | 38884.8767 | 57929.4058 | 792.7208 | 1180.9693
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.1324 | 4.511 | 0.10051 | 4 | 38231.912 | 56738.8933 | 779.4092 | 1156.6991 | 62.3897 | 0 | 153.0048 | 677013.9417 | 34708.6355 | 1191428.4731 | 1492908.1266 | 0 | 84623.789 | 0 | 1357466.3567 | 3531849.0056 | 2410559.5185 | 10780557.8468 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15370608.8028 | 22811083.3701 | 4216965.0343 | 0.40204 | 38231.912 | 56738.8933 | 779.4092 | 1156.6991
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1996 | 4.5816 | 0.10272 | 4 | 37743.5584 | 55852.1247 | 769.4535 | 1138.6211 | 62.3892 | 0 | 152.7159 | 684406.8989 | 35087.4998 | 1206319.3643 | 1515900.4496 | 0 | 83369.513 | 0 | 1374782.653 | 3576902.4564 | 2441309.4245 | 10918078.2594 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15508129.2154 | 22948603.7827 | 5623413.2519 | 0.41088 | 37743.5584 | 55852.1247 | 769.4535 | 1138.6211
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70 | 4.6345 | 0.10441 | 4 | 37378.1171 | 55193.5041 | 762.0035 | 1125.1942 | 62.3887 | 0 | 167.9754 | 689925.9799 | 35370.2898 | 1217452.9626 | 1533139.9315 | 0 | 82316.0927 | 0 | 1387700.05 | 3610510.8738 | 2464247.8599 | 11020664.0403 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15610714.9964 | 23051189.5636 | 7498942.0933 | 0.41764 | 37378.1171 | 55193.5041 | 762.0035 | 1125.1942
1 | 1200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.6151 | 4.6752 | 0.10571 | 4 | 37104.5266 | 54700.8165 | 756.426 | 1115.1501 | 62.3883 | 0 | 140.7188 | 694152.8162 | 35586.841 | 1225989.5867 | 1546386.2382 | 0 | 81495.5576 | 0 | 1397608.3054 | 3636290.1219 | 2481842.7265 | 11099352.1933 | 961560.8286 | 3628490.1274 | 3628490.1274 | 1478867.319 | 2333117.1208 | 0 | 15689403.1494 | 23129877.7166 | 10000000 | 0.42284 | 37104.5266 | 54700.8165 | 756.426 | 1115.1501
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.2747 | [19 empty] | 100 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0892 | [19 empty] | 133.3521 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0372 | [19 empty] | 177.8279 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2831 | [19 empty] | 237.1374 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8437 | [19 empty] | 316.2278 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.4085 | [19 empty] | 421.6965 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8031 | [19 empty] | 562.3413 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4625 | [19 empty] | 749.8942 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.6294 | [19 empty] | 1000 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.615 | [19 empty] | 1333.5214 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 31.5954 | [19 empty] | 1778.2794 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 33.8646 | [19 empty] | 2371.3737 | 0
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.77197 | 0.043759 | 0.00015514 | 4 | 8414597.6788 | 21027958.5777 | 171542.9553 | 428683.378 | 58.0258 | 0 | 80.3379 | 25464.9177 | 1218.7152 | 29325.765 | 39213.5337 | 0 | 19513.2418 | 0 | 44747.1076 | 116422.7952 | 79460.95 | 355367.0262 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5221863.5829 | 13049361.9911 | 3162.2777 | 0.00062057 | 8414597.6788 | 21027958.5777 | 171542.9553 | 428683.378
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.068276 | 0.00047108 | 4 | 2828499.5839 | 6982480.7839 | 57662.7898 | 142347.3153 | 60.3548 | 0 | 180.9571 | 36005.8123 | 1762.334 | 41770.4943 | 46934.2299 | 0 | 23126.9099 | 0 | 58343.9143 | 151798.8971 | 103605.8664 | 463348.4583 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5329845.0149 | 13157343.4231 | 4216.965 | 0.0018843 | 2828499.5839 | 6982480.7839 | 57662.7898 | 142347.3153
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4764 | 0.095735 | 0.00092092 | 4 | 1476633.8306 | 3601543.7081 | 30103.1779 | 73422.3399 | 61.7776 | 0 | 249.0891 | 46488.8865 | 2307.6164 | 54670.0098 | 55506.2607 | 0 | 26016.0091 | 0 | 72145.6252 | 187708.1177 | 128114.6473 | 572957.1728 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5439453.7295 | 13266952.1376 | 5623.4133 | 0.0036837 | 1476633.8306 | 3601543.7081 | 30103.1779 | 73422.3399
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.13351 | 0.0015358 | 4 | 908466.7868 | 2182607.5348 | 18520.3242 | 44495.4068 | 62.9061 | 0 | 340.6144 | 59494.3063 | 2987.7822 | 71260.3621 | 67253.6303 | 0 | 29704.1256 | 0 | 89973.0805 | 234091.4995 | 159772.2585 | 714537.0449 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5581033.6016 | 13408532.0098 | 7498.9421 | 0.0061434 | 908466.7868 | 2182607.5348 | 18520.3242 | 44495.4068
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6426 | 0.18314 | 0.002391 | 4 | 601712.1357 | 1420130.856 | 12266.7158 | 28951.2884 | 63.7531 | 0 | 70.2777 | 74918.7452 | 3796.8747 | 91694.3999 | 82641.4329 | 0 | 33777.6717 | 0 | 111863.3585 | 291045.5125 | 198644.5427 | 888382.538 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5754879.0947 | 13582377.5029 | 10000 | 0.0095642 | 601712.1357 | 1420130.856 | 12266.7158 | 28951.2884
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5272 | 0.2497 | 0.0035446 | 4 | 421402.0114 | 973470.3752 | 8590.85 | 19845.5103 | 64.4039 | 0 | 73.5289 | 93684.5195 | 4783.5664 | 117433.154 | 103252.7942 | 0 | 38695.1446 | 0 | 139561.1797 | 363109.5617 | 247829.737 | 1108349.6572 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 5974846.2139 | 13802344.6221 | 13335.2143 | 0.014178 | 421402.0114 | 973470.3752 | 8590.85 | 19845.5103
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.687 | 0.33702 | 0.005059 | 4 | 308759.9482 | 695573.0641 | 6294.4892 | 14180.1977 | 64.892 | 0 | 65.6839 | 116081.5158 | 5962.9362 | 149207.8174 | 130278.7265 | 0 | 44518.4996 | 0 | 173959.3032 | 452606.4231 | 308913.1839 | 1381528.4056 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6248024.9623 | 14075523.3705 | 17782.7941 | 0.020236 | 308759.9482 | 695573.0641 | 6294.4892 | 14180.1977
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.287 | 0.45765 | 0.0071498 | 4 | 230970.4018 | 504665.5228 | 4708.6441 | 10288.2893 | 65.2669 | 0 | 84.3335 | 144207.9796 | 7444.5159 | 190527.5419 | 167597.9772 | 0 | 51720.5023 | 0 | 218984.4216 | 569752.545 | 388867.8192 | 1739103.3025 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6605599.8592 | 14433098.2674 | 23713.7371 | 0.028599 | 230970.4018 | 504665.5228 | 4708.6441 | 10288.2893
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.946 | 0.58224 | 0.0097008 | 4 | 179188.43 | 380912.0392 | 3652.9985 | 7765.4071 | 65.4664 | 0 | 67.8798 | 170847.8591 | 8846.8015 | 230959.3129 | 206197.7839 | 0 | 56831.3297 | 0 | 262736.404 | 683586.2285 | 466561.6472 | 2086567.3668 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 6953063.9235 | 14780562.3316 | 31622.7766 | 0.038803 | 179188.43 | 380912.0392 | 3652.9985 | 7765.4071
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2332 | 0.75593 | 0.013249 | 4 | 139992.728 | 287688.1768 | 2853.9411 | 5864.9126 | 65.7125 | 0 | 95.8561 | 205461.1296 | 10673.4197 | 284540.5275 | 259776.052 | 0 | 63755.336 | 0 | 321440.5213 | 836322.2999 | 570807.1544 | 2552776.4404 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7419272.997 | 15246771.4052 | 42169.6503 | 0.052998 | 139992.728 | 287688.1768 | 2853.9411 | 5864.9126
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0908 | 0.97187 | 0.017766 | 4 | 112214.9856 | 222359.3337 | 2287.6543 | 4533.0958 | 65.866 | 0 | 75.7751 | 245149.219 | 12765.343 | 347849.6462 | 326512.9897 | 0 | 71241.9863 | 0 | 391372.4818 | 1018270.9162 | 694990.8237 | 3108153.4058 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 7974649.9625 | 15802148.3707 | 56234.1325 | 0.071066 | 112214.9856 | 222359.3337 | 2287.6543 | 4533.0958
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6009 | 1.2372 | 0.023538 | 4 | 91659.5566 | 174797.8774 | 1868.604 | 3563.4912 | 65.9828 | 0 | 97.716 | 290408.5729 | 15150.3064 | 421894.3694 | 408495.0883 | 0 | 79089.0182 | 0 | 473864.5685 | 1232898.4043 | 841478.4945 | 3763278.8224 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 8629775.3791 | 16457273.7873 | 74989.4209 | 0.09415 | 91659.5566 | 174797.8774 | 1868.604 | 3563.4912
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.825 | 1.5562 | 0.03078 | 4 | 76254.0734 | 139831.121 | 1554.5424 | 2850.6465 | 66.0717 | 0 | 93.5064 | 341136.2794 | 17822.717 | 506846.9167 | 507090.47 | 0 | 87034.3741 | 0 | 569372.9953 | 1481391.7393 | 1011080.3016 | 4521775.7933 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 9388272.35 | 17215770.7582 | 100000 | 0.12312 | 76254.0734 | 139831.121 | 1554.5424 | 2850.6465
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.8091 | 1.9326 | 0.039673 | 4 | 64605.9322 | 113931.5865 | 1317.0793 | 2322.6495 | 66.1397 | 0 | 112.2182 | 397126.0155 | 20770.7685 | 602715.0756 | 623416.7312 | 0 | 94877.2393 | 0 | 678173.2737 | 1764467.7458 | 1204285.4927 | 5385832.3424 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 10252328.8991 | 18079827.3073 | 133352.1432 | 0.15869 | 64605.9322 | 113931.5865 | 1317.0793 | 2322.6495
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4512 | 2.3587 | 0.050221 | 4 | 55748.7634 | 94714.1843 | 1136.5139 | 1930.8768 | 66.1913 | 0 | 90.5751 | 456705.6571 | 23905.7737 | 706842.6227 | 755108.5665 | 0 | 101988.5199 | 0 | 797374.9445 | 2074606.0416 | 1415961.2523 | 6332493.3783 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 11198989.935 | 19026488.3432 | 177827.941 | 0.20088 | 55748.7634 | 94714.1843 | 1136.5139 | 1930.8768
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5802 | 2.8217 | 0.062233 | 4 | 48998.4383 | 80442.5813 | 998.8994 | 1639.9308 | 66.2304 | 0 | 103.6598 | 517896.4461 | 27123.2485 | 815777.7118 | 898171.4653 | 0 | 107919.2703 | 0 | 923086.3754 | 2401681.3977 | 1639196.9035 | 7330852.8185 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 12197349.3752 | 20024847.7834 | 237137.3706 | 0.24893 | 48998.4383 | 80442.5813 | 998.8994 | 1639.9308
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.8944 | 3.2987 | 0.075234 | 4 | 43859.2525 | 69869.8072 | 894.1302 | 1424.3905 | 66.2592 | 0 | 112.2245 | 577880.2627 | 30274.8796 | 924315.9552 | 1045556.897 | 0 | 112196.6835 | 0 | 1049187.6245 | 2729770.9809 | 1863124.7856 | 8332308.069 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 13198804.6257 | 21026303.0339 | 316227.766 | 0.30094 | 43859.2525 | 69869.8072 | 894.1302 | 1424.3905
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.0233 | 3.7615 | 0.088511 | 4 | 39960.8438 | 62069.6775 | 814.6559 | 1265.3743 | 66.279 | 0 | 125.1845 | 633657.1837 | 33203.1626 | 1026669.0121 | 1188595.2815 | 0 | 114529.4629 | 0 | 1168695.1001 | 3040704.9181 | 2075343.5868 | 9281397.7078 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 14147894.2645 | 21975392.6727 | 421696.5034 | 0.35404 | 39960.8438 | 62069.6775 | 814.6559 | 1265.3743
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6233 | 4.1841 | 0.10128 | 4 | 37017.339 | 56338.4736 | 754.6485 | 1148.536 | 66.2911 | 0 | 158.8361 | 682810.5889 | 35781.6184 | 1117942.5581 | 1319238.394 | 0 | 114930.4111 | 0 | 1275574.3924 | 3318782.9129 | 2265137.5322 | 10130198.4079 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 14996694.9646 | 22824193.3728 | 562341.3252 | 0.40513 | 37017.339 | 56338.4736 | 754.6485 | 1148.536
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.4908 | 4.5511 | 0.11292 | 4 | 34803.9462 | 52133.1053 | 709.5255 | 1062.8039 | 66.2973 | 0 | 113.9001 | 724285.4784 | 37955.5418 | 1195714.3342 | 1432730.2666 | 0 | 113799.6809 | 0 | 1366749.2678 | 3556001.2359 | 2427043.912 | 10854279.7176 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 15720776.2743 | 23548274.6825 | 749894.2093 | 0.4517 | 34803.9462 | 52133.1053 | 709.5255 | 1062.8039
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.5781 | 4.8589 | 0.12309 | 4 | 33144.2513 | 49041.8152 | 675.6904 | 999.7837 | 66.2993 | 0 | 140.7346 | 758288.8695 | 39736.5136 | 1259983.0211 | 1527965.8853 | 0 | 111743.424 | 0 | 1442109.9083 | 3752074.1639 | 2560867.7143 | 11452769.5 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 16319266.0567 | 24146764.4648 | 1000000 | 0.49237 | 33144.2513 | 49041.8152 | 675.6904 | 999.7837
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.9085 | 5.1094 | 0.13166 | 4 | 31901.6548 | 46764.928 | 650.3584 | 953.3663 | 66.2989 | 0 | 152.031 | 785474.5321 | 41159.4538 | 1311691.5468 | 1605512.4648 | 0 | 109248.2589 | 0 | 1502703.64 | 3909726.6243 | 2668468.7579 | 11933985.2785 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 16800481.8352 | 24627980.2434 | 1333521.4322 | 0.52663 | 31901.6548 | 46764.928 | 650.3584 | 953.3663
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5419 | 5.3073 | 0.13865 | 4 | 30971.9013 | 45086.0205 | 631.4041 | 919.1395 | 66.2973 | 0 | 129.7007 | 806655.3807 | 42267.4691 | 1352178.54 | 1666791.9946 | 0 | 106627.2737 | 0 | 1550063.0567 | 4032946.1118 | 2752568.59 | 12310098.4166 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17176594.9733 | 25004093.3815 | 1778279.41 | 0.55459 | 30971.9013 | 45086.0205 | 631.4041 | 919.1395
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.6218 | 5.4634 | 0.14426 | 4 | 30276.2673 | 43840.7412 | 617.2227 | 893.7528 | 66.2952 | 0 | 158.2433 | 823193.9825 | 43132.2384 | 1383913.5515 | 1715164.0944 | 0 | 104230.1738 | 0 | 1587157.2758 | 4129457.6609 | 2818439.7054 | 12604688.6826 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17471185.2393 | 25298683.6475 | 2371373.7057 | 0.57706 | 30276.2673 | 43840.7412 | 617.2227 | 893.7528
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.2102 | 5.5826 | 0.14866 | 4 | 29755.6863 | 42918.8522 | 606.6099 | 874.9589 | 66.2932 | 0 | 133.032 | 835714.6607 | 43786.6761 | 1408009.7531 | 1752089.4367 | 0 | 102059.5589 | 0 | 1615247.4334 | 4202542.4889 | 2868321.6023 | 12827771.6102 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17694268.1669 | 25521766.575 | 3162277.6602 | 0.59465 | 29755.6863 | 42918.8522 | 606.6099 | 874.9589
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.4406 | 5.6748 | 0.1521 | 4 | 29365.9827 | 42231.7284 | 598.6653 | 860.9509 | 66.2913 | 0 | 148.1201 | 845348.8505 | 44290.0947 | 1426592.5294 | 1780680.8442 | 0 | 100263.807 | 0 | 1636898.6891 | 4258874.6149 | 2906769.4358 | 12999718.8657 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17866215.4224 | 25693713.8306 | 4216965.0343 | 0.6084 | 29365.9827 | 42231.7284 | 598.6653 | 860.9509
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.3808 | 5.7453 | 0.15475 | 4 | 29074.1575 | 41719.462 | 592.716 | 850.5077 | 66.2897 | 0 | 148.3739 | 852673.3391 | 44672.7366 | 1440744.5341 | 1802521.7542 | 0 | 98799.3615 | 0 | 1653370.573 | 4301731.0779 | 2936019.8524 | 13130533.2288 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 17997029.7855 | 25824528.1937 | 5623413.2519 | 0.619 | 29074.1575 | 41719.462 | 592.716 | 850.5077
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0996 | 5.7991 | 0.15679 | 4 | 28855.563 | 41336.6307 | 588.2597 | 842.7031 | 66.2884 | 0 | 139.4117 | 858251.9456 | 44964.1197 | 1451537.306 | 1819216.8856 | 0 | 97640.7058 | 0 | 1665928.2755 | 4334403.6439 | 2958319.5501 | 13230262.4322 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 18096758.9889 | 25924257.397 | 7498942.0933 | 0.62715 | 28855.563 | 41336.6307 | 588.2597 | 842.7031
1 | 1300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.6332 | 5.8391 | 0.15832 | 4 | 28691.7822 | 41051.6803 | 584.9208 | 836.894 | 66.2873 | 0 | 138.3858 | 862381.1626 | 45179.769 | 1459533.8292 | 1831607.9917 | 0 | 96699.7667 | 0 | 1675206.9825 | 4358544.9363 | 2974796.4782 | 13303950.9163 | 961560.8286 | 3904935.7281 | 3904935.7281 | 1478867.319 | 2443695.3611 | 0 | 18170447.473 | 25997945.8812 | 10000000 | 0.6333 | 28691.7822 | 41051.6803 | 584.9208 | 836.894
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 18.4947 | [19 empty] | 100 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.7559 | [19 empty] | 133.3521 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.503 | [19 empty] | 177.8279 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4352 | [19 empty] | 237.1374 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2847 | [19 empty] | 316.2278 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1086 | [19 empty] | 421.6965 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6946 | [19 empty] | 562.3413 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.682 | [19 empty] | 749.8942 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.5249 | [19 empty] | 1000 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.4638 | [19 empty] | 1333.5214 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.7747 | [19 empty] | 1778.2794 | 0
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79142 | 0.049782 | 0.00020971 | 4 | 6602427.388 | 16405147.5626 | 134599.4127 | 334441.1227 | 60.91 | 0 | 76.567 | 29302.921 | 1431.3153 | 32426.0215 | 40616.1347 | 0 | 21964.5905 | 0 | 49038.9834 | 127589.3755 | 87082.3705 | 389451.7124 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5538253.9606 | 13760980.3369 | 2371.3737 | 0.00083882 | 6602427.388 | 16405147.5626 | 134599.4127 | 334441.1227
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.07732 | 0.00061013 | 4 | 2318333.9583 | 5687583.3642 | 47262.3735 | 115949.0799 | 63.4692 | 0 | 168.5655 | 41286.7703 | 2063.616 | 46010.4676 | 48895.4968 | 0 | 26128.6857 | 0 | 64110.1642 | 166801.4964 | 113845.4487 | 509142.1457 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5657944.3939 | 13880670.7702 | 3162.2777 | 0.0024405 | 2318333.9583 | 5687583.3642 | 47262.3735 | 115949.0799
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5347 | 0.1114 | 0.0011955 | 4 | 1211374.6367 | 2930886.0229 | 24695.5105 | 59750.0759 | 65.1798 | 0 | 237.5093 | 54431.9865 | 2763.7595 | 61525.6718 | 59050.5507 | 0 | 30156.5708 | 0 | 81092.1303 | 210985.0888 | 144001.6584 | 644007.4167 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5792809.6649 | 14015536.0412 | 4216.965 | 0.004782 | 1211374.6367 | 2930886.0229 | 24695.5105 | 59750.0759
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 0.1556 | 0.0020132 | 4 | 739499.1375 | 1760599.8181 | 15075.6902 | 35892.2087 | 66.4318 | 0 | 329.8757 | 69732.2744 | 3582.8301 | 80294.721 | 72158.6224 | 0 | 34540.0208 | 0 | 101520.3028 | 264135.0032 | 180277.5671 | 806241.3418 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 5955043.59 | 14177769.9663 | 5623.4133 | 0.0080528 | 739499.1375 | 1760599.8181 | 15075.6902 | 35892.2087
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7398 | 0.21284 | 0.0031302 | 4 | 491336.9615 | 1148070.5184 | 10016.5685 | 23404.9704 | 67.3667 | 0 | 84.5272 | 87691.5239 | 4548.0891 | 103076.3867 | 89102.1516 | 0 | 39434.0551 | 0 | 126302.3605 | 328612.8338 | 224285.0114 | 1003052.4121 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6151854.6603 | 14374581.0366 | 7498.9421 | 0.012521 | 491336.9615 | 1148070.5184 | 10016.5685 | 23404.9704
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6218 | 0.28735 | 0.0046359 | 4 | 344750.8647 | 788179.7287 | 7028.2127 | 16068.1099 | 68.0711 | 0 | 91.3759 | 108924.8332 | 5691.2383 | 130968.762 | 111122.5146 | 0 | 44967.1968 | 0 | 156653.0725 | 407579.1606 | 278181.1521 | 1244087.93 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6392890.1782 | 14615616.5545 | 10000 | 0.018544 | 344750.8647 | 788179.7287 | 7028.2127 | 16068.1099
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7498 | 0.3827 | 0.0066446 | 4 | 251496.4768 | 560874.3527 | 5127.0959 | 11434.1823 | 68.5983 | 0 | 61.8947 | 133742.5312 | 7028.9417 | 164637.3915 | 139288.0004 | 0 | 51076.9111 | 0 | 193351.7726 | 503061.6504 | 343349.9133 | 1535537.1121 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 6684339.3603 | 14907065.7366 | 13335.2143 | 0.026578 | 251496.4768 | 560874.3527 | 5127.0959 | 11434.1823
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.177 | 0.50334 | 0.0092936 | 4 | 189214.9789 | 410408.2552 | 3857.4033 | 8366.7274 | 68.9871 | 0 | 112.126 | 162522.836 | 8580.7703 | 204917.92 | 174916.1981 | 0 | 57714.4846 | 0 | 237374.3615 | 617599.3965 | 421524.2785 | 1885150.2455 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7033952.4937 | 15256678.87 | 17782.7941 | 0.037174 | 189214.9789 | 410408.2552 | 3857.4033 | 8366.7274
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8554 | 0.64469 | 0.012667 | 4 | 146486.7445 | 308768.0888 | 2986.3304 | 6294.6551 | 69.2327 | 0 | 108.2142 | 193566.5497 | 10253.0251 | 249734.4021 | 216719.8272 | 0 | 63801.8657 | 0 | 286289.5113 | 744866.5822 | 508386.7479 | 2273618.5112 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7422420.7594 | 15645147.1357 | 23713.7371 | 0.05067 | 146486.7445 | 308768.0888 | 2986.3304 | 6294.6551
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3575 | 0.85746 | 0.017409 | 4 | 114695.8963 | 232780.6698 | 2338.231 | 4745.5488 | 69.5338 | 0 | 100.9299 | 236885.0834 | 12591.9515 | 313655.882 | 279398.9451 | 0 | 73745.2999 | 0 | 357348.0931 | 929746.4362 | 634571.0471 | 2837942.7383 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 7986744.9865 | 16209471.3628 | 31622.7766 | 0.069634 | 114695.8963 | 232780.6698 | 2338.231 | 4745.5488
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.2493 | 1.1024 | 0.023351 | 4 | 92115.0782 | 180150.3348 | 1877.8905 | 3672.6082 | 69.7092 | 0 | 88.1202 | 282743.4085 | 15064.5082 | 383433.0899 | 351667.0009 | 0 | 82593.2462 | 0 | 435045.4889 | 1131899.122 | 772544.409 | 3454990.2735 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 8603792.5217 | 16826518.898 | 42169.6503 | 0.093403 | 92115.0782 | 180150.3348 | 1877.8905 | 3672.6082
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.8102 | 1.4041 | 0.030957 | 4 | 75369.8886 | 141775.2575 | 1536.5171 | 2890.2804 | 69.843 | 0 | 90.968 | 335170.2475 | 17889.8426 | 465238.2248 | 440660.7221 | 0 | 91904.4491 | 0 | 526836.7596 | 1370721.1794 | 935545.3704 | 4183966.7955 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 9332769.0437 | 17555495.42 | 56234.1325 | 0.12383 | 75369.8886 | 141775.2575 | 1536.5171 | 2890.2804
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.382 | 1.7067 | 0.039933 | 4 | 62786.2584 | 114264.9692 | 1279.9828 | 2329.446 | 69.9308 | 0 | 113.1555 | 384438.5971 | 20543.4264 | 543816.3109 | 529929.3905 | 0 | 96889.3742 | 0 | 614490.6686 | 1598778.6705 | 1091199.2942 | 4880085.7324 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 10028887.9806 | 18251614.3569 | 74989.4209 | 0.15973 | 62786.2584 | 114264.9692 | 1279.9828 | 2329.446
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2307 | 2.2023 | 0.052364 | 4 | 53241.8295 | 92499.1224 | 1085.4067 | 1885.7197 | 70.0236 | 0 | 109.0699 | 459824.2215 | 24600.6264 | 666787.1596 | 676112.2328 | 0 | 110872.6525 | 0 | 755896.7882 | 1966688.3871 | 1342305.2356 | 6003087.3036 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 11151889.5518 | 19374615.9281 | 100000 | 0.20946 | 53241.8295 | 92499.1224 | 1085.4067 | 1885.7197
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.3 | 2.9708 | 0.069896 | 4 | 45919.8621 | 75330.4414 | 936.1385 | 1535.7129 | 70.1081 | 0 | 140.8061 | 567418.456 | 30384.7557 | 847149.5942 | 902807.396 | 0 | 134973.1586 | 0 | 968266.0106 | 2519229.5409 | 1719425.9266 | 7689654.8386 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 12838457.0868 | 21061183.4631 | 133352.1432 | 0.27958 | 45919.8621 | 75330.4414 | 936.1385 | 1535.7129
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.5741 | 3.2483 | 0.082888 | 4 | 40362.3563 | 65163.1475 | 822.8412 | 1328.4389 | 70.129 | 0 | 95.4195 | 604148.764 | 32357.5498 | 909861.2541 | 984649.0533 | 0 | 127266.2388 | 0 | 1036730.3154 | 2697359.618 | 1841003.3645 | 8233376.158 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 13382178.4062 | 21604904.7825 | 177827.941 | 0.33155 | 40362.3563 | 65163.1475 | 822.8412 | 1328.4389
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.3487 | 3.8224 | 0.10084 | 4 | 36083.4122 | 56468.8069 | 735.6092 | 1151.193 | 70.1624 | 0 | 108.6819 | 677328.0308 | 36285.2439 | 1036350.3064 | 1153986.4007 | 0 | 132912.4688 | 0 | 1184376.3558 | 3081504.3287 | 2103190.0229 | 9405933.158 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 14554735.4062 | 22777461.7825 | 237137.3706 | 0.40336 | 36083.4122 | 56468.8069 | 735.6092 | 1151.193
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0501 | 4.39 | 0.11949 | 4 | 32818.4759 | 50022.7796 | 669.049 | 1019.782 | 70.1849 | 0 | 129.3447 | 746524.9437 | 39995.5011 | 1157724.1931 | 1321451.5932 | 0 | 136238.1905 | 0 | 1326754.4245 | 3451942.8577 | 2356021.9307 | 10536653.6345 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 15685455.8827 | 23908182.259 | 316227.766 | 0.47795 | 32818.4759 | 50022.7796 | 669.049 | 1019.782
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.2593 | 4.9155 | 0.13768 | 4 | 30340.2324 | 45271.1342 | 618.5267 | 922.9133 | 70.1976 | 0 | 114.0086 | 808215.2 | 43299.8112 | 1267300.4571 | 1476527.7751 | 0 | 137037.6819 | 0 | 1455628.5609 | 3787246.9249 | 2584873.8464 | 11560130.2574 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 16708932.5056 | 24931658.8819 | 421696.5034 | 0.55072 | 30340.2324 | 45271.1342 | 618.5267 | 922.9133
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.7498 | 5.3795 | 0.15452 | 4 | 28468.4743 | 41772.2098 | 580.3684 | 851.583 | 70.2025 | 0 | 124.2018 | 861041.0055 | 46126.3526 | 1362125.5995 | 1613542.6157 | 0 | 135851.4683 | 0 | 1567287.9462 | 4077761.741 | 2783156.1778 | 12446892.9065 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 17595695.1547 | 25818421.531 | 562341.3252 | 0.61808 | 28468.4743 | 41772.2098 | 580.3684 | 851.583
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.4102 | 5.7727 | 0.16939 | 4 | 27060.0336 | 39195.5358 | 551.6554 | 799.054 | 70.2022 | 0 | 123.2067 | 904718.6172 | 48461.0779 | 1441211.9459 | 1729731.3294 | 0 | 133335.9516 | 0 | 1660408.9796 | 4320043.5682 | 2948518.5033 | 13186429.9731 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 18335232.2213 | 26557958.5976 | 749894.2093 | 0.67758 | 27060.0336 | 39195.5358 | 551.6554 | 799.054
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.2151 | 6.0932 | 0.182 | 4 | 26002.6924 | 37297.805 | 530.1001 | 760.3662 | 70.1988 | 0 | 138.9427 | 939636.9469 | 50325.9243 | 1504880.2386 | 1824495.7453 | 0 | 130051.9741 | 0 | 1735262.4234 | 4514796.8744 | 3081441.6366 | 13780891.7636 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 18929694.0118 | 27152420.3881 | 1000000 | 0.72799 | 26002.6924 | 37297.805 | 530.1001 | 760.3662
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.2749 | 6.3505 | 0.1924 | 4 | 25209.9181 | 35894.1394 | 513.9383 | 731.7506 | 70.1942 | 0 | 154.8843 | 967258.2759 | 51799.9421 | 1555521.7957 | 1900634.9232 | 0 | 126637.4737 | 0 | 1794722.4401 | 4669499.641 | 3187029.4536 | 14253103.9453 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 19401906.1935 | 27624632.5698 | 1333521.4322 | 0.76961 | 25209.9181 | 35894.1394 | 513.9383 | 731.7506
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.6797 | 6.5525 | 0.20078 | 4 | 24615.8377 | 34854.4745 | 501.8271 | 710.5556 | 70.1894 | 0 | 152.3037 | 988690.3241 | 52942.9449 | 1594985.4128 | 1960429.6175 | 0 | 123379.6253 | 0 | 1840966.8906 | 4789818.2151 | 3269149.3527 | 14620362.3831 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 19769164.6313 | 27991891.0076 | 1778279.41 | 0.80311 | 24615.8377 | 34854.4745 | 501.8271 | 710.5556
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.546 | 6.7091 | 0.2074 | 4 | 24170.7225 | 34082.5349 | 492.7529 | 694.8186 | 70.185 | 0 | 142.2542 | 1005158.9469 | 53820.7941 | 1625410.6413 | 2006802.0665 | 0 | 120474.611 | 0 | 1876550.1533 | 4882398.5657 | 3332337.3443 | 14902953.1232 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20051755.3714 | 28274481.7477 | 2371373.7057 | 0.82959 | 24170.7225 | 34082.5349 | 492.7529 | 694.8186
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.9823 | 6.8295 | 0.21256 | 4 | 23837.2084 | 33508.0695 | 485.9537 | 683.1073 | 70.1811 | 0 | 170.4736 | 1017737.6748 | 54491.0255 | 1648708.6564 | 2042470.6244 | 0 | 118004.7854 | 0 | 1903750.9789 | 4953169.5342 | 3380639.9845 | 15118973.2641 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20267775.5123 | 28490501.8886 | 3162277.6602 | 0.85026 | 23837.2084 | 33508.0695 | 485.9537 | 683.1073
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.0714 | 6.9207 | 0.21654 | 4 | 23587.2863 | 33080.4958 | 480.8587 | 674.3907 | 70.178 | 0 | 135.9265 | 1027221.5484 | 54996.1962 | 1666308.4563 | 2069506.2281 | 0 | 115945.3637 | 0 | 1924251.3391 | 5006507.2662 | 3417044.0826 | 15281780.4807 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20430582.7289 | 28653309.1052 | 4216965.0343 | 0.86617 | 23587.2863 | 33080.4958 | 480.8587 | 674.3907
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9191 | 6.9917 | 0.21963 | 4 | 23399.9806 | 32759.851 | 477.0403 | 667.8539 | 70.1754 | 0 | 152.8865 | 1034571.5327 | 55387.6077 | 1679968.4048 | 2090543.3237 | 0 | 114349.8049 | 0 | 1940180.0628 | 5047950.5377 | 3445329.967 | 15408281.2414 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20557083.4896 | 28779809.8659 | 5623413.2519 | 0.87851 | 23399.9806 | 32759.851 | 477.0403 | 667.8539
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.5381 | 7.0435 | 0.22194 | 4 | 23259.5858 | 32521.9768 | 474.1781 | 663.0045 | 70.1734 | 0 | 152.5271 | 1039920.638 | 55672.4129 | 1689920.798 | 2105899.9821 | 0 | 113017.3655 | 0 | 1951728.1666 | 5077996.3351 | 3465836.8411 | 15499992.5393 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20648794.7875 | 28871521.1638 | 7498942.0933 | 0.88775 | 23259.5858 | 32521.9768 | 474.1781 | 663.0045
1 | 1400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.023 | 7.084 | 0.22372 | 4 | 23154.3424 | 32342.8083 | 472.0326 | 659.3519 | 70.1718 | 0 | 143.1229 | 1044100.9126 | 55894.9542 | 1697704.9958 | 2117928.3152 | 0 | 112031.0706 | 0 | 1960787.4969 | 5101566.8541 | 3481924.2046 | 15571938.8041 | 961560.8286 | 4187241.4196 | 4187241.4196 | 1478867.319 | 2556617.6377 | 0 | 20720741.0523 | 28943467.4286 | 10000000 | 0.8949 | 23154.3424 | 32342.8083 | 472.0326 | 659.3519
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.1516 | [19 empty] | 100 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.8733 | [19 empty] | 133.3521 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1332 | [19 empty] | 177.8279 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4779 | [19 empty] | 237.1374 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.1662 | [19 empty] | 316.2278 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6234 | [19 empty] | 421.6965 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6581 | [19 empty] | 562.3413 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2236 | [19 empty] | 749.8942 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6847 | [19 empty] | 1000 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 30.7122 | [19 empty] | 1333.5214 | 0
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75252 | 0.050943 | 0.00022259 | 4 | 6555849.6262 | 16244339.451 | 133649.8621 | 331162.8318 | 63.0555 | 0 | 66.1699 | 30844.9516 | 1527.1791 | 32964.8554 | 40519.545 | 0 | 23303.2198 | 0 | 50372.3029 | 131058.3993 | 89450.0505 | 400040.5037 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5837008.5343 | 14463167.0059 | 1778.2794 | 0.00089035 | 6555849.6262 | 16244339.451 | 133649.8621 | 331162.8318
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0874 | 0.081508 | 0.00070529 | 4 | 2116336.6887 | 5173978.8964 | 43144.386 | 105478.5581 | 66.173 | 0 | 160.3725 | 44581.1297 | 2266.1981 | 47878.9994 | 49344.0058 | 0 | 28210.785 | 0 | 67189.636 | 174813.6505 | 119313.9085 | 533598.3131 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 5970566.3437 | 14596724.8153 | 2371.3737 | 0.0028212 | 2116336.6887 | 5173978.8964 | 43144.386 | 105478.5581
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.11921 | 0.0014204 | 4 | 1077131.9549 | 2595344.6478 | 21958.7918 | 52909.6111 | 68.2246 | 0 | 230.4877 | 59588.8929 | 3083.7689 | 64780.004 | 60124.1948 | 0 | 32961.8819 | 0 | 86010.1095 | 223780.6619 | 152734.9 | 683064.4139 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6120032.4445 | 14746190.9161 | 3162.2777 | 0.0056818 | 1077131.9549 | 2595344.6478 | 21958.7918 | 52909.6111
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.16816 | 0.0024264 | 4 | 649033.466 | 1537806.865 | 13231.4251 | 31350.273 | 69.71 | 0 | 330.1101 | 77025.7656 | 4039.4116 | 85188.7672 | 74045.1462 | 0 | 38124.7163 | 0 | 108585.2847 | 282516.6368 | 192823.4098 | 862349.1382 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6299317.1687 | 14925475.6404 | 4216.965 | 0.0097057 | 649033.466 | 1537806.865 | 13231.4251 | 31350.273
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7009 | 0.23185 | 0.0038054 | 4 | 428138.7097 | 994842.4506 | 8728.1867 | 20281.209 | 70.8101 | 0 | 88.0585 | 97499.2017 | 5165.3713 | 110041.0996 | 92107.139 | 0 | 43884.4584 | 0 | 135991.9353 | 353823.1199 | 241491.5497 | 1080003.8749 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6516971.9054 | 15143130.3771 | 5623.4133 | 0.015222 | 428138.7097 | 994842.4506 | 8728.1867 | 20281.209
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5707 | 0.31358 | 0.0056655 | 4 | 299131.5296 | 679773.8304 | 6098.2008 | 13858.109 | 71.6252 | 0 | 89.4241 | 121345.4314 | 6479.1868 | 140010.212 | 115242.091 | 0 | 50205.0719 | 0 | 168979.9773 | 439651.2384 | 300071.0041 | 1341984.2129 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 6778952.2434 | 15405110.7151 | 7498.9421 | 0.022662 | 299131.5296 | 679773.8304 | 6098.2008 | 13858.109
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.687 | 0.41861 | 0.008151 | 4 | 217660.798 | 482233.1764 | 4437.3098 | 9830.9756 | 72.2378 | 0 | 107.6858 | 149315.3943 | 8021.7293 | 176320.1997 | 144948.1007 | 0 | 57249.3301 | 0 | 208983.3541 | 543731.819 | 371108.139 | 1659678.0661 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7096646.0967 | 15722804.5683 | 10000 | 0.032604 | 217660.798 | 482233.1764 | 4437.3098 | 9830.9756
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0797 | 0.54963 | 0.011425 | 4 | 163493.39 | 352251.0902 | 3333.0339 | 7181.1149 | 72.6858 | 0 | 146.013 | 181308.8609 | 9786.6464 | 219148.989 | 181998.1438 | 0 | 64668.5753 | 0 | 256195.374 | 666567.8102 | 454946.2271 | 2034620.6266 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7471588.6572 | 16097747.1288 | 13335.2143 | 0.0457 | 163493.39 | 352251.0902 | 3333.0339 | 7181.1149
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7434 | 0.70557 | 0.015613 | 4 | 126410.2324 | 264530.8064 | 2577.0436 | 5392.8183 | 72.9787 | 0 | 137.621 | 216376.8236 | 11719.0289 | 267549.7622 | 226154.6902 | 0 | 71752.6652 | 0 | 309485.6584 | 805218.1988 | 549577.9663 | 2457834.7936 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 7894802.8241 | 16520961.2958 | 17782.7941 | 0.062454 | 126410.2324 | 264530.8064 | 2577.0436 | 5392.8183
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1944 | 0.93734 | 0.021461 | 4 | 99022.8591 | 199507.7673 | 2018.7149 | 4067.2357 | 73.3196 | 0 | 109.19 | 264649.4793 | 14384.266 | 335709.7645 | 291421.6674 | 0 | 82995.147 | 0 | 385772.5264 | 1003700.981 | 685046.5435 | 3063680.3751 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 8500648.4057 | 17126806.8773 | 23713.7371 | 0.085845 | 99022.8591 | 199507.7673 | 2018.7149 | 4067.2357
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.0371 | 1.2052 | 0.028814 | 4 | 79518.8716 | 154363.3158 | 1621.0998 | 3146.905 | 73.5235 | 0 | 104.1126 | 315975.8714 | 17213.5439 | 410406.4309 | 366960.6904 | 0 | 93070.8322 | 0 | 469414.6738 | 1221320.691 | 833576.4673 | 3727939.2008 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9164907.2314 | 17791065.703 | 31622.7766 | 0.11525 | 79518.8716 | 154363.3158 | 1621.0998 | 3146.905
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5667 | 1.5378 | 0.038262 | 4 | 65048.9969 | 121411.3037 | 1326.1118 | 2475.1336 | 73.6801 | 0 | 108.6705 | 375132.5746 | 20472.2695 | 498691.406 | 460756.3866 | 0 | 103876.688 | 0 | 568982.4366 | 1480375.5858 | 1010386.756 | 4518674.1031 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 9955642.1336 | 18581800.6053 | 42169.6503 | 0.15305 | 65048.9969 | 121411.3037 | 1326.1118 | 2475.1336
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.8593 | 1.9424 | 0.050216 | 4 | 54163.7462 | 97109.3332 | 1104.2012 | 1979.7051 | 73.7999 | 0 | 95.3277 | 442120.049 | 24159.3635 | 601078.4167 | 574833.6738 | 0 | 115009.806 | 0 | 685308.5105 | 1783032.1683 | 1216956.0925 | 5442498.0803 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 10879466.1108 | 19505624.5825 | 56234.1325 | 0.20086 | 54163.7462 | 97109.3332 | 1104.2012 | 1979.7051
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9749 | 2.4245 | 0.065051 | 4 | 45886.4356 | 79038.0807 | 935.4571 | 1611.2982 | 73.8917 | 0 | 120.3566 | 516719.3542 | 28261.6278 | 717688.6426 | 710789.13 | 0 | 126085.6551 | 0 | 818822.3198 | 2130407.7125 | 1454047.0393 | 6502821.4813 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 11939789.5118 | 20565947.9835 | 74989.4209 | 0.2602 | 45886.4356 | 79038.0807 | 935.4571 | 1611.2982
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.9575 | 2.9885 | 0.083058 | 4 | 39543.8132 | 65508.1055 | 806.1541 | 1335.4713 | 73.9625 | 0 | 155.2796 | 598565.8237 | 32757.8825 | 848338.6677 | 869795.9476 | 0 | 136852.9259 | 0 | 969661.3865 | 2522860.0227 | 1721903.8051 | 7700736.4616 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 13137704.4922 | 21763862.9638 | 100000 | 0.33223 | 39543.8132 | 65508.1055 | 806.1541 | 1335.4713
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6519 | 3.6196 | 0.10411 | 4 | 34662.5134 | 55375.7067 | 706.6422 | 1128.9087 | 74.0164 | 0 | 134.8145 | 684895.1623 | 37495.4459 | 988822.8418 | 1047761.7783 | 0 | 146335.8564 | 0 | 1133071.323 | 2948019.1577 | 2012083.6508 | 8998485.2163 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 14435453.2469 | 23061611.7185 | 133352.1432 | 0.41646 | 34662.5134 | 55375.7067 | 706.6422 | 1128.9087
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.4 | 4.4443 | 0.1303 | 4 | 30883.0899 | 47434.2105 | 629.5936 | 967.0105 | 74.063 | 0 | 115.2555 | 791260.2528 | 43325.4757 | 1165241.1656 | 1280393.098 | 0 | 161140.2802 | 0 | 1342130.5062 | 3491948.2682 | 2383326.4454 | 10658765.492 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 16095733.5226 | 24721891.9942 | 177827.941 | 0.52118 | 30883.0899 | 47434.2105 | 629.5936 | 967.0105
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0124 | 4.9731 | 0.15258 | 4 | 28020.5722 | 42154.1935 | 571.2373 | 859.3703 | 74.0825 | 0 | 133.3207 | 856352.7614 | 46888.9921 | 1274871.1468 | 1429584.5221 | 0 | 158477.5311 | 0 | 1468808.2318 | 3821537.7252 | 2608278.0222 | 11664798.9328 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 17101766.9633 | 25727925.435 | 237137.3706 | 0.61033 | 28020.5722 | 42154.1935 | 571.2373 | 859.3703
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.8575 | 5.6173 | 0.17742 | 4 | 25820.1731 | 37974.8996 | 526.3792 | 774.1697 | 74.0966 | 0 | 173.4482 | 932912.9662 | 51075.5235 | 1405346.6815 | 1611427.0432 | 0 | 160182.4091 | 0 | 1622768.4031 | 4222110.5094 | 2881677.1783 | 12887500.7142 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 18324468.7448 | 26950627.2164 | 316227.766 | 0.7097 | 25820.1731 | 37974.8996 | 526.3792 | 774.1697
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.9935 | 6.1938 | 0.20078 | 4 | 24150.6753 | 34891.4798 | 492.3442 | 711.31 | 74.1005 | 0 | 162.4212 | 999178.7834 | 54694.3381 | 1519581.013 | 1774255.7546 | 0 | 159163.6174 | 0 | 1757680.6675 | 4573124.547 | 3121251.4716 | 13958930.1925 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 19395898.223 | 28022056.6947 | 421696.5034 | 0.80312 | 24150.6753 | 34891.4798 | 492.3442 | 711.31
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.2601 | 6.6876 | 0.22169 | 4 | 22889.8072 | 32617.7104 | 466.6397 | 664.9561 | 74.0974 | 0 | 198.3114 | 1054432.3109 | 57707.9028 | 1615745.1644 | 1913834.5467 | 0 | 156217.2359 | 0 | 1871195.4927 | 4868466.837 | 3322828.6533 | 14860428.1437 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 20297396.1743 | 28923554.6459 | 562341.3252 | 0.88674 | 22889.8072 | 32617.7104 | 466.6397 | 664.9561
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.6381 | 7.0971 | 0.23967 | 4 | 21940.5498 | 30938.3926 | 447.2878 | 630.721 | 74.0904 | 0 | 184.6993 | 1099299.2017 | 60152.1133 | 1694442.5319 | 2029711.3099 | 0 | 152229.8694 | 0 | 1963975.6602 | 5109861.8011 | 3487585.6764 | 15597258.1639 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 21034226.1945 | 29660384.6661 | 749894.2093 | 0.95869 | 21940.5498 | 30938.3926 | 447.2878 | 630.721
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.1607 | 7.426 | 0.25461 | 4 | 21227.2655 | 29697.3486 | 432.7465 | 605.4206 | 74.082 | 0 | 164.4051 | 1134734.6889 | 62080.5728 | 1756984.7753 | 2122835.0746 | 0 | 147814.4702 | 0 | 2037535.3369 | 5301248.9907 | 3618211.3659 | 16181445.2754 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 21618413.3059 | 30244571.7776 | 1000000 | 1.0184 | 21227.2655 | 29697.3486 | 432.7465 | 605.4206
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.9593 | 7.6868 | 0.26674 | 4 | 20691.8697 | 28776.7685 | 421.8318 | 586.6533 | 74.0735 | 0 | 165.6502 | 1162479.1123 | 63589.194 | 1806192.5448 | 2196736.9133 | 0 | 143555.5371 | 0 | 2095295.7876 | 5451529.835 | 3720781.1301 | 16640160.0543 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22077128.0849 | 30703286.5565 | 1333521.4322 | 1.0669 | 20691.8697 | 28776.7685 | 421.8318 | 586.6533
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.1519 | 7.8908 | 0.2764 | 4 | 20290.2207 | 28092.3626 | 413.6436 | 572.7008 | 74.0658 | 0 | 156.9696 | 1183971.83 | 64757.0693 | 1844457.7989 | 2254585.1846 | 0 | 139730.627 | 0 | 2140125.9788 | 5568168.7966 | 3800389.6181 | 16996186.9033 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22433154.9339 | 31059313.4055 | 1778279.41 | 1.1056 | 20290.2207 | 28092.3626 | 413.6436 | 572.7008
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.8427 | 8.048 | 0.28398 | 4 | 19988.9869 | 27583.0971 | 407.5025 | 562.3187 | 74.0592 | 0 | 182.4925 | 1200402.5045 | 65649.3924 | 1873796.7812 | 2299162.2105 | 0 | 136426.9887 | 0 | 2174420.7722 | 5657396.8141 | 3861289.5735 | 17268545.0371 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22705513.0676 | 31331671.5393 | 2371373.7057 | 1.1359 | 19988.9869 | 27583.0971 | 407.5025 | 562.3187
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.1145 | 8.1661 | 0.28979 | 4 | 19763.0893 | 27204.79 | 402.8973 | 554.6064 | 74.0539 | 0 | 157.0013 | 1212679.3451 | 66315.8437 | 1895767.4775 | 2332670.0282 | 0 | 133601.0683 | 0 | 2200003.1675 | 5723956.9592 | 3906718.2402 | 17471712.1298 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 22908680.1604 | 31534838.632 | 3162277.6602 | 1.1592 | 19763.0893 | 27204.79 | 402.8973 | 554.6064
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.1077 | 8.2582 | 0.29432 | 4 | 19593.6939 | 26920.9713 | 399.444 | 548.8204 | 74.0496 | 0 | 190.0968 | 1222219.9869 | 66833.5893 | 1912870.4131 | 2358828.2664 | 0 | 131397.8036 | 0 | 2219938.5231 | 5775824.6651 | 3942119.0153 | 17630032.2626 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23067000.2932 | 31693158.7649 | 4216965.0343 | 1.1773 | 19593.6939 | 26920.9713 | 399.444 | 548.8204
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.8434 | 8.3264 | 0.29773 | 4 | 19466.6698 | 26709.8616 | 396.8544 | 544.5167 | 74.0462 | 0 | 215.5727 | 1229259.8937 | 67215.5294 | 1925506.7192 | 2378196.6181 | 0 | 129587.052 | 0 | 2234608.6668 | 5813993.3698 | 3968169.9405 | 17746537.7894 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23183505.82 | 31809664.2916 | 5623413.2519 | 1.1909 | 19466.6698 | 26709.8616 | 396.8544 | 544.5167
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.4159 | 8.3795 | 0.30037 | 4 | 19371.418 | 26551.0844 | 394.9126 | 541.2798 | 74.0436 | 0 | 225.6693 | 1234722.7349 | 67511.8508 | 1935321.8059 | 2393265.076 | 0 | 128223.3798 | 0 | 2246027.4905 | 5843702.8066 | 3988447.2416 | 17837222.386 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23274190.4166 | 31900348.8882 | 7498942.0933 | 1.2015 | 19371.418 | 26551.0844 | 394.9126 | 541.2798
1 | 1500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.8445 | 8.4192 | 0.30236 | 4 | 19299.9913 | 26432.4453 | 393.4564 | 538.8612 | 74.0415 | 0 | 198.4748 | 1238803.6001 | 67733.1766 | 1942659.3491 | 2404543.8015 | 0 | 127154.9365 | 0 | 2254548.9969 | 5865874.0183 | 4003579.5491 | 17904897.428 | 961560.8286 | 4475407.202 | 4475407.202 | 1478867.319 | 2671883.9507 | 0 | 23341865.4586 | 31968023.9302 | 10000000 | 1.2094 | 19299.9913 | 26432.4453 | 393.4564 | 538.8612
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.7898 | [19 empty] | 100 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.4303 | [19 empty] | 133.3521 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9822 | [19 empty] | 177.8279 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0556 | [19 empty] | 237.1374 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0535 | [19 empty] | 316.2278 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.3983 | [19 empty] | 421.6965 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.8193 | [19 empty] | 562.3413 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 29.0183 | [19 empty] | 749.8942 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.7135 | [19 empty] | 1000 | 0
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.69881 | 0.049988 | 0.00018304 | 4 | 8374812.4166 | 20718832.0077 | 170731.8789 | 422381.4148 | 64.7292 | 0 | 84.1425 | 31250.0854 | 1562.4241 | 32420.8842 | 39861.9474 | 0 | 24279.5769 | 0 | 50456.218 | 131276.7292 | 89599.0652 | 400706.9304 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6131700.8342 | 15169495.5283 | 1333.5214 | 0.00073216 | 8374812.4166 | 20718832.0077 | 170731.8789 | 422381.4148
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0304 | 0.082992 | 0.0007278 | 4 | 2156601.9575 | 5261105.2461 | 43965.2479 | 107254.7466 | 68.5875 | 0 | 61.5728 | 46722.8023 | 2410.5713 | 48469.935 | 49064.5782 | 0 | 30030.9819 | 0 | 68912.5588 | 179296.342 | 122373.4376 | 547281.207 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6278275.1108 | 15316069.805 | 1778.2794 | 0.0029112 | 2156601.9575 | 5261105.2461 | 43965.2479 | 107254.7466
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4375 | 0.12436 | 0.0015542 | 4 | 1036467.8031 | 2490217.0624 | 21129.7981 | 50766.4431 | 71.09 | 0 | 241.3975 | 63750.9376 | 3357.6863 | 66841.3429 | 60453.1912 | 0 | 35674.6054 | 0 | 89730.3277 | 233459.9065 | 159341.1833 | 712609.181 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6443603.0849 | 15481397.779 | 2371.3737 | 0.0062169 | 1036467.8031 | 2490217.0624 | 21129.7981 | 50766.4431
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.17633 | 0.0027273 | 4 | 608128.5235 | 1436598.5734 | 12397.5225 | 29287.0051 | 72.8259 | 0 | 347.8674 | 82840.6834 | 4427.2084 | 88245.6208 | 74663.2542 | 0 | 41401.2658 | 0 | 113715.4327 | 295864.2297 | 201933.4162 | 903091.1111 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6634085.015 | 15671879.7091 | 3162.2777 | 0.010909 | 608128.5235 | 1436598.5734 | 12397.5225 | 29287.0051
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5849 | 0.24257 | 0.0043333 | 4 | 395752.8328 | 917173.1212 | 8067.9568 | 18697.8146 | 74.0952 | 0 | 480.4774 | 104789.2168 | 5661.3716 | 113771.7885 | 92624.607 | 0 | 47541.2354 | 0 | 142111.4056 | 369744.7262 | 252358.3731 | 1128602.7243 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 6859596.6281 | 15897391.3223 | 4216.965 | 0.017333 | 395752.8328 | 917173.1212 | 8067.9568 | 18697.8146
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4003 | 0.32708 | 0.0065097 | 4 | 273805.2714 | 620897.424 | 5581.8908 | 12657.8338 | 75.0405 | 0 | 78.7809 | 130260.7565 | 7097.0675 | 144386.0145 | 115584.5391 | 0 | 54204.8141 | 0 | 176097.9447 | 458170.7295 | 312710.9374 | 1398512.8033 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7129506.7071 | 16167301.4012 | 5623.4133 | 0.026039 | 273805.2714 | 620897.424 | 5581.8908 | 12657.8338
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4675 | 0.43742 | 0.0093861 | 4 | 198715.2868 | 439438.6742 | 4051.0799 | 8958.5518 | 75.7696 | 0 | 78.8009 | 160538.153 | 8803.0797 | 182084.3673 | 145035.586 | 0 | 61980.4693 | 0 | 217792.2455 | 566650.7476 | 386750.7787 | 1729635.4271 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7460629.3309 | 16498424.0251 | 7498.9421 | 0.037544 | 198715.2868 | 439438.6742 | 4051.0799 | 8958.5518
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8091 | 0.57612 | 0.01318 | 4 | 148964.0434 | 320389.9204 | 3036.8335 | 6531.5819 | 76.3087 | 0 | 115.8008 | 195403.4919 | 10767.6033 | 226870.6882 | 181956.6839 | 0 | 70313.1167 | 0 | 267271.5178 | 695385.6643 | 474615.0046 | 2122583.7707 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 7853577.6745 | 16891372.3687 | 10000 | 0.052721 | 148964.0434 | 320389.9204 | 3036.8335 | 6531.5819
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4339 | 0.74362 | 0.018071 | 4 | 114866.7428 | 239900.174 | 2341.7139 | 4890.6895 | 76.6759 | 0 | 122.6883 | 234152.1821 | 12948.6139 | 278176.5391 | 226565.6427 | 0 | 78544.8822 | 0 | 323851.2654 | 842594.5615 | 575088.1018 | 2571921.7887 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8302915.6925 | 17340710.3867 | 13335.2143 | 0.072283 | 114866.7428 | 239900.174 | 2341.7139 | 4890.6895
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.7728 | 0.98647 | 0.024827 | 4 | 89911.8962 | 180920.3234 | 1832.9756 | 3688.3055 | 77.0604 | 0 | 97.3058 | 286114.2475 | 15877.8975 | 348637.5889 | 291020.3205 | 0 | 90847.6859 | 0 | 402674.1187 | 1047675.457 | 715060.027 | 3197907.3429 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 8928901.2467 | 17966695.9409 | 17782.7941 | 0.099307 | 89911.8962 | 180920.3234 | 1832.9756 | 3688.3055
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5307 | 1.2725 | 0.033445 | 4 | 71979.098 | 139535.9262 | 1467.3913 | 2844.6286 | 77.3038 | 0 | 102.1326 | 342505.9239 | 19053.6117 | 427310.9236 | 367487.6783 | 0 | 102310.1244 | 0 | 490880.6222 | 1277170.6854 | 871695.236 | 3898414.8055 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 9629408.7093 | 18667203.4034 | 23713.7371 | 0.13378 | 71979.098 | 139535.9262 | 1467.3913 | 2844.6286
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9406 | 1.6262 | 0.044531 | 4 | 58711.6642 | 109449.9518 | 1196.9167 | 2231.2853 | 77.4894 | 0 | 121.5535 | 407188.3242 | 22693.2042 | 519867.0917 | 462040.9305 | 0 | 114422.0445 | 0 | 595222.5221 | 1548646.9056 | 1056983.3346 | 4727064.3576 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 10458058.2614 | 19495852.9556 | 31622.7766 | 0.17813 | 58711.6642 | 109449.9518 | 1196.9167 | 2231.2853
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.1212 | 2.0599 | 0.058635 | 4 | 48745.9572 | 87280.3951 | 993.7523 | 1779.3289 | 77.6319 | 0 | 108.446 | 480979.1322 | 26841.3126 | 628026.4734 | 577967.9922 | 0 | 127103.546 | 0 | 717958.198 | 1867979.9577 | 1274934.7043 | 5701791.3165 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 11432785.2203 | 20470579.9144 | 42169.6503 | 0.23454 | 48745.9572 | 87280.3951 | 993.7523 | 1779.3289
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1512 | 2.5818 | 0.076273 | 4 | 41169.917 | 70792.9667 | 839.3044 | 1443.2104 | 77.7414 | 0 | 111.8226 | 563865.1384 | 31495.7019 | 752311.3687 | 717459.3637 | 0 | 139942.2715 | 0 | 859978.7992 | 2237488.4297 | 1527131.8291 | 6829672.9022 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 12560666.806 | 21598461.5002 | 56234.1325 | 0.30509 | 41169.917 | 70792.9667 | 839.3044 | 1443.2104
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.1003 | 3.1991 | 0.097906 | 4 | 35358.5537 | 58436.4059 | 720.8319 | 1191.3052 | 77.826 | 0 | 119.0001 | 655708.4178 | 36647.1229 | 893001.236 | 882444.6683 | 0 | 152647.0919 | 0 | 1021974.9294 | 2658969.1305 | 1814801.0679 | 8116193.6647 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 13847187.5685 | 22884982.2627 | 74989.4209 | 0.39162 | 35358.5537 | 58436.4059 | 720.8319 | 1191.3052
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8702 | 3.9017 | 0.12358 | 4 | 30875.3953 | 49158.8952 | 629.4367 | 1002.1706 | 77.8907 | 0 | 110.7592 | 754053.0533 | 42156.5338 | 1046663.1561 | 1070208.619 | 0 | 164210.801 | 0 | 1200143.9436 | 3122528.3579 | 2131189.7658 | 9531154.2305 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 15262148.1343 | 24299942.8284 | 100000 | 0.49431 | 30875.3953 | 49158.8952 | 629.4367 | 1002.1706
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.2903 | 4.6717 | 0.15291 | 4 | 27410.5533 | 42186.9652 | 558.8012 | 860.0383 | 77.939 | 0 | 126.0547 | 855984.0894 | 47859.6418 | 1208833.3574 | 1275996.7041 | 0 | 173935.468 | 0 | 1389417.6117 | 3614979.6168 | 2467297.8689 | 11034304.3581 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 16765298.262 | 25803092.9561 | 133352.1432 | 0.61164 | 27410.5533 | 42186.9652 | 558.8012 | 860.0383
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.9346 | 5.4645 | 0.18462 | 4 | 24738.8382 | 36977.3455 | 504.3347 | 753.8332 | 77.9714 | 0 | 122.4794 | 955839.3865 | 53438.9919 | 1370304.3322 | 1487936.9948 | 0 | 180564.9783 | 0 | 1578753.0266 | 4107591.5285 | 2803515.6207 | 12537944.8594 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 18268938.7633 | 27306733.4574 | 177827.941 | 0.73847 | 24738.8382 | 36977.3455 | 504.3347 | 753.8332
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3593 | 6.2336 | 0.21695 | 4 | 22689.6055 | 33104.0445 | 462.5583 | 674.8707 | 77.9885 | 0 | 121.9157 | 1048621.4632 | 58615.3936 | 1522508.1048 | 1693644.6314 | 0 | 183622.8415 | 0 | 1757734.8495 | 4573265.5174 | 3121347.6868 | 13959360.4883 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 19690354.3921 | 28728149.0863 | 237137.3706 | 0.86781 | 22689.6055 | 33104.0445 | 462.5583 | 674.8707
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.1682 | 6.9374 | 0.24804 | 4 | 21127.5767 | 30236.764 | 430.7142 | 616.4173 | 77.9923 | 0 | 145.0636 | 1130519.3699 | 63177.3285 | 1658540.8737 | 1882076.9543 | 0 | 183266.9441 | 0 | 1917856.7735 | 4989869.9181 | 3405688.7507 | 15230996.9128 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 20961990.8166 | 29999785.5107 | 316227.766 | 0.99216 | 21127.5767 | 30236.764 | 430.7142 | 616.4173
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.1165 | 7.5508 | 0.27639 | 4 | 19943.3764 | 28118.2254 | 406.5727 | 573.2281 | 77.9866 | 0 | 165.7744 | 1199808.8907 | 67030.8662 | 1774850.7411 | 2046466.0383 | 0 | 180261.4256 | 0 | 2054683.0052 | 5345863.706 | 3648661.8259 | 16317626.4991 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 22048620.4029 | 31086415.0971 | 421696.5034 | 1.1056 | 19943.3764 | 28118.2254 | 406.5727 | 573.2281
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.1324 | 8.0666 | 0.30116 | 4 | 19049.1945 | 26551.6093 | 388.3436 | 541.2905 | 77.9755 | 0 | 147.155 | 1256719.2301 | 70191.2844 | 1871217.1726 | 2184882.2637 | 0 | 175671.1809 | 0 | 2167885.6414 | 5640393.7443 | 3849684.629 | 17216645.1464 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 22947639.0502 | 31985433.7444 | 562341.3252 | 1.2047 | 19049.1945 | 26551.6093 | 388.3436 | 541.2905
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.2151 | 8.4853 | 0.32199 | 4 | 18375.7857 | 25392.9273 | 374.6152 | 517.6692 | 77.9624 | 0 | 158.2145 | 1302072.6492 | 72706.6415 | 1948557.1478 | 2297387.8183 | 0 | 170301.3299 | 0 | 2258499.9788 | 5876153.6628 | 4010595.6178 | 17936274.8461 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 23667268.7499 | 32705063.4441 | 749894.2093 | 1.288 | 18375.7857 | 25392.9273 | 374.6152 | 517.6692
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.4944 | 8.8209 | 0.33909 | 4 | 17869.4663 | 24532.6586 | 364.2932 | 500.1314 | 77.9492 | 0 | 154.5447 | 1337898.5099 | 74691.4053 | 2009992.8375 | 2387642.4822 | 0 | 164978.9661 | 0 | 2330329.6384 | 6063039.7027 | 4138149.1801 | 18506722.7221 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 24237716.6259 | 33275511.3201 | 1000000 | 1.3564 | 17869.4663 | 24532.6586 | 364.2932 | 500.1314
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.054 | 9.0824 | 0.35276 | 4 | 17489.1461 | 23894.2563 | 356.5399 | 487.1167 | 77.9373 | 0 | 176.5864 | 1365500.6299 | 76219.1932 | 2057533.9392 | 2458015.9993 | 0 | 159986.6771 | 0 | 2385730.0111 | 6207180.1085 | 4236527.9688 | 18946694.5272 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 24677688.431 | 33715483.1252 | 1333521.4322 | 1.411 | 17489.1461 | 23894.2563 | 356.5399 | 487.1167
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.0445 | 9.2854 | 0.36354 | 4 | 17203.6327 | 23418.7729 | 350.7193 | 477.4234 | 77.9271 | 0 | 151.1278 | 1386752.1746 | 77394.6275 | 2094261.0152 | 2512696.4878 | 0 | 155638.993 | 0 | 2428429.8863 | 6318276.4246 | 4312353.4874 | 19285803.0964 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25016797.0002 | 34054591.6944 | 1778279.41 | 1.4542 | 17203.6327 | 23418.7729 | 350.7193 | 477.4234
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.5696 | 9.4407 | 0.37192 | 4 | 16989.3656 | 23064.4924 | 346.3512 | 470.2009 | 77.9188 | 0 | 182.0254 | 1402909.8263 | 78287.8095 | 2122257.3875 | 2554561.4655 | 0 | 151962.7908 | 0 | 2460891.919 | 6402735.975 | 4369998.866 | 19543606.0395 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25274599.9433 | 34312394.6375 | 2371373.7057 | 1.4877 | 16989.3656 | 23064.4924 | 346.3512 | 470.2009
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.7339 | 9.5592 | 0.37838 | 4 | 16828.6006 | 22800.0138 | 343.0738 | 464.8091 | 77.9121 | 0 | 181.3406 | 1415173.4758 | 78965.4362 | 2143548.6673 | 2586505.3641 | 0 | 148958.0098 | 0 | 2485528.8718 | 6466836.2723 | 4413748.636 | 19739264.7333 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25470258.6371 | 34508053.3313 | 3162277.6602 | 1.5135 | 16828.6006 | 22800.0138 | 343.0738 | 464.8091
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.6112 | 9.6484 | 0.3833 | 4 | 16707.9955 | 22602.6807 | 340.6151 | 460.7862 | 77.9069 | 0 | 165.008 | 1424374.3993 | 79473.661 | 2159546.5711 | 2610567.2551 | 0 | 146527.7207 | 0 | 2503990.9468 | 6514870.8044 | 4446533.1912 | 19885884.5497 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25616878.4535 | 34654673.1476 | 4216965.0343 | 1.5332 | 16707.9955 | 22602.6807 | 340.6151 | 460.7862
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.2808 | 9.7164 | 0.38707 | 4 | 16617.527 | 22454.8648 | 338.7708 | 457.7728 | 77.9028 | 0 | 171.8709 | 1431372.8855 | 79860.1319 | 2171728.7954 | 2628924.4349 | 0 | 144634.1126 | 0 | 2518042.9405 | 6551431.2097 | 4471486.419 | 19997480.9296 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25728474.8334 | 34766269.5276 | 5623413.2519 | 1.5483 | 16617.527 | 22454.8648 | 338.7708 | 457.7728
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.7897 | 9.7681 | 0.38993 | 4 | 16549.6696 | 22344.1081 | 337.3874 | 455.5149 | 77.8997 | 0 | 186.4528 | 1436678.3394 | 80153.0524 | 2180971.9074 | 2642872.4802 | 0 | 143172.4857 | 0 | 2528700.8234 | 6579160.8346 | 4490412.4579 | 20082122.381 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25813116.2848 | 34850910.9789 | 7498942.0933 | 1.5597 | 16549.6696 | 22344.1081 | 337.3874 | 455.5149
1 | 1600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.177 | 9.8074 | 0.39211 | 4 | 16498.7748 | 22261.0281 | 336.3498 | 453.8212 | 77.8972 | 0 | 202.5637 | 1440708.3986 | 80375.5233 | 2187997.6212 | 2653485.816 | 0 | 142058.6926 | 0 | 2536804.1601 | 6600244.0546 | 4504802.1887 | 20146476.4551 | 961560.8286 | 4769433.0752 | 4769433.0752 | 1478867.319 | 2789494.2999 | 0 | 25877470.359 | 34915265.0531 | 10000000 | 1.5684 | 16498.7748 | 22261.0281 | 336.3498 | 453.8212
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.3431 | [19 empty] | 100 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8229 | [19 empty] | 133.3521 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7426 | [19 empty] | 177.8279 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7338 | [19 empty] | 237.1374 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.4024 | [19 empty] | 316.2278 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0804 | [19 empty] | 421.6965 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.9569 | [19 empty] | 562.3413 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 28.2371 | [19 empty] | 749.8942 | 0
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.62825 | 0.046354 | 8.9408e-05 | 4 | 17948146.6539 | 44393241.2598 | 365897.2462 | 905016.2694 | 65.6764 | 0 | 59.9729 | 30096.2766 | 1511.1605 | 30495.8426 | 38536.8817 | 0 | 24621.5562 | 0 | 48852.0699 | 127103.0648 | 86750.4534 | 387967.3057 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6418847.1736 | 15876482.2175 | 1000 | 0.00035763 | 17948146.6539 | 44393241.2598 | 365897.2462 | 905016.2694
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | 0.079604 | 0.00066307 | 4 | 2477235.4736 | 6043103.2674 | 50501.7958 | 123196.834 | 70.4133 | 0 | 66.0608 | 46535.6699 | 2425.689 | 46804.7974 | 47540.6492 | 0 | 30851.074 | 0 | 67921.573 | 176718.0003 | 120613.6664 | 539411.1193 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6570290.9872 | 16027926.0311 | 1333.5214 | 0.0026523 | 2477235.4736 | 6043103.2674 | 50501.7958 | 123196.834
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.243 | 0.11335 | 0.0015449 | 4 | 1085172.3271 | 2615667.3324 | 22122.7057 | 53323.9165 | 73.0064 | 0 | 195.3922 | 61276.737 | 3259.9837 | 61956.3596 | 56529.5229 | 0 | 34880.3827 | 0 | 84982.1645 | 221106.1597 | 150909.4973 | 674900.8073 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6705780.6752 | 16163415.7191 | 1778.2794 | 0.0061795 | 1085172.3271 | 2615667.3324 | 22122.7057 | 53323.9165
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.16121 | 0.0028127 | 4 | 611935.1467 | 1452559.8163 | 12475.1257 | 29612.3966 | 75.1644 | 0 | 280.3835 | 80086.7307 | 4333.9095 | 81973.3183 | 69089.089 | 0 | 40191.1084 | 0 | 107512.9207 | 279726.5658 | 190919.129 | 853832.7714 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 6884712.6393 | 16342347.6832 | 2371.3737 | 0.011251 | 611935.1467 | 1452559.8163 | 12475.1257 | 29612.3966
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.22647 | 0.0045398 | 4 | 391549.7081 | 912372.1112 | 7982.2704 | 18599.9396 | 76.8595 | 0 | 398.2584 | 103058.1026 | 5649.8646 | 107444.2158 | 85549.9228 | 0 | 46763.7379 | 0 | 135901.679 | 353588.2915 | 241331.2745 | 1079287.0886 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7110166.9566 | 16567802.0005 | 3162.2777 | 0.018159 | 391549.7081 | 912372.1112 | 7982.2704 | 18599.9396
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.164 | 0.32913 | 0.0069657 | 4 | 267234.0264 | 606671.2774 | 5447.9271 | 12367.8146 | 78.3039 | 0 | 72.2115 | 135493.4262 | 7515.6328 | 144729.488 | 111766.5751 | 0 | 57344.481 | 0 | 178171.3452 | 463565.2923 | 316392.8373 | 1414979.078 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7445858.9459 | 16903493.9898 | 4216.965 | 0.027863 | 267234.0264 | 606671.2774 | 5447.9271 | 12367.8146
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0434 | 0.42832 | 0.010124 | 4 | 191133.7865 | 424689.7256 | 3896.5208 | 8657.8745 | 79.1014 | 0 | 105.2532 | 163876.7346 | 9148.7158 | 178570.2734 | 136715.0973 | 0 | 63438.8786 | 0 | 215182.3829 | 559860.4202 | 382116.2408 | 1708908.7435 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 7739788.6114 | 17197423.6553 | 5623.4133 | 0.040494 | 191133.7865 | 424689.7256 | 3896.5208 | 8657.8745
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.407 | 0.58253 | 0.014435 | 4 | 141681.6217 | 305474.958 | 2888.3715 | 6227.5202 | 79.8337 | 0 | 117.7357 | 204321.9586 | 11478.0127 | 228241.0099 | 175755.1727 | 0 | 74366.1564 | 0 | 270723.301 | 704366.4963 | 480744.607 | 2149996.7147 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8180876.5826 | 17638511.6265 | 7498.9421 | 0.057741 | 141681.6217 | 305474.958 | 2888.3715 | 6227.5202
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.042 | 0.76726 | 0.020034 | 4 | 108283.2603 | 226301.6838 | 2207.5007 | 4613.4659 | 80.3208 | 0 | 106.1817 | 248593.7388 | 14025.6306 | 284392.8379 | 222596.695 | 0 | 84892.9734 | 0 | 333255.7315 | 867063.0532 | 591788.3502 | 2646609.0104 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 8677488.8783 | 18135123.9222 | 10000 | 0.080137 | 108283.2603 | 226301.6838 | 2207.5007 | 4613.4659
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3512 | 1.0295 | 0.027706 | 4 | 84373.0672 | 169711.3996 | 1720.0591 | 3459.7964 | 80.7692 | 0 | 97.3595 | 306344.382 | 17351.2397 | 359661.944 | 288936.854 | 0 | 99551.7813 | 0 | 418020.0184 | 1087602.3402 | 742310.9451 | 3319779.5047 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 9350659.3726 | 18808294.4165 | 13335.2143 | 0.11083 | 84373.0672 | 169711.3996 | 1720.0591 | 3459.7964
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7996 | 1.3071 | 0.03726 | 4 | 67227.9234 | 130684.6034 | 1370.5322 | 2664.1824 | 81.0425 | 0 | 99.9004 | 362753.7687 | 20595.6267 | 435284.2617 | 359221.7304 | 0 | 110003.1082 | 0 | 502264.8134 | 1306790.0157 | 891911.0375 | 3988824.3624 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 10019704.2303 | 19477339.2742 | 17782.7941 | 0.14904 | 67227.9234 | 130684.6034 | 1370.5322 | 2664.1824
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0586 | 1.6766 | 0.049779 | 4 | 54623.3805 | 102121.6904 | 1113.5715 | 2081.8888 | 81.2668 | 0 | 113.2757 | 432470.1154 | 24601.0783 | 531115.4971 | 452685.7305 | 0 | 123566.7929 | 0 | 610131.2935 | 1587436.4706 | 1083458.0098 | 4845464.9881 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 10876344.856 | 20333979.8999 | 23713.7371 | 0.19912 | 54623.3805 | 102121.6904 | 1113.5715 | 2081.8888
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.054 | 2.1297 | 0.065753 | 4 | 45175.601 | 81134.2783 | 920.9657 | 1654.032 | 81.438 | 0 | 107.254 | 511929.3824 | 29161.3232 | 643028.5629 | 567271.9545 | 0 | 137680.7541 | 0 | 736738.071 | 1916841.3351 | 1308283.5983 | 5850934.9814 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 11881814.8494 | 21339449.8933 | 31622.7766 | 0.26301 | 45175.601 | 81134.2783 | 920.9657 | 1654.032
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9332 | 2.683 | 0.085928 | 4 | 38000.7465 | 65516.9966 | 774.6966 | 1335.6526 | 81.5705 | 0 | 123.5845 | 602416.5066 | 34348.2384 | 773450.6502 | 707215.5437 | 0 | 152448.039 | 0 | 885252.8014 | 2303246.1989 | 1572012.8577 | 7030390.8359 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 13061270.7039 | 22518905.7478 | 42169.6503 | 0.34371 | 38000.7465 | 65516.9966 | 774.6966 | 1335.6526
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7339 | 3.341 | 0.11086 | 4 | 32496.2753 | 53823.492 | 662.4805 | 1097.2647 | 81.6724 | 0 | 93.0113 | 703057.9168 | 40109.8172 | 921706.0185 | 873592.8096 | 0 | 167064.7206 | 0 | 1055157.2003 | 2745302.5926 | 1873725.4298 | 8379716.5053 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 14410596.3732 | 23868231.4171 | 56234.1325 | 0.44345 | 32496.2753 | 53823.492 | 662.4805 | 1097.2647
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.4546 | 4.1033 | 0.14091 | 4 | 28243.2367 | 45022.7539 | 575.7766 | 917.8497 | 81.7508 | 0 | 100.9376 | 812587.9692 | 46371.8817 | 1086367.3573 | 1066368.5219 | 0 | 180869.8329 | 0 | 1245100.5696 | 3239496.2768 | 2211022.7739 | 9888185.1833 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 15919065.0512 | 25376700.0951 | 74989.4209 | 0.56364 | 28243.2367 | 45022.7539 | 575.7766 | 917.8497
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.9844 | 4.9574 | 0.17592 | 4 | 24945.8959 | 38385.9197 | 508.5558 | 782.5489 | 81.81 | 0 | 140.2535 | 928375.377 | 52982.4805 | 1263729.2702 | 1282348.4247 | 0 | 193068.1677 | 0 | 1450996.4508 | 3775195.1248 | 2576648.2451 | 11523343.5408 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 17554223.4087 | 27011858.4526 | 100000 | 0.70369 | 24945.8959 | 38385.9197 | 508.5558 | 782.5489
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9575 | 5.8614 | 0.21473 | 4 | 22391.7895 | 33403.0384 | 456.4869 | 680.9661 | 81.8508 | 0 | 142.8233 | 1044648.0903 | 59610.8347 | 1444899.6843 | 1511003.2337 | 0 | 202187.6855 | 0 | 1662316.3161 | 4325006.0666 | 2951905.5104 | 13201577.4217 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 19232457.2896 | 28690092.3335 | 133352.1432 | 0.85891 | 22391.7895 | 33403.0384 | 456.4869 | 680.9661
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.9159 | 6.7626 | 0.25535 | 4 | 20422.5937 | 29682.1207 | 416.3422 | 605.1102 | 81.8731 | 0 | 155.4326 | 1155326.3262 | 65909.7647 | 1620011.8517 | 1739111.7535 | 0 | 207319.3148 | 0 | 1867194.8142 | 4858057.8924 | 3315724.3346 | 14828656.0521 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 20859535.9201 | 30317170.964 | 177827.941 | 1.0214 | 20422.5937 | 29682.1207 | 416.3422 | 605.1102
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.3897 | 7.6071 | 0.29537 | 4 | 18914.1219 | 26918.944 | 385.59 | 548.7791 | 81.8784 | 0 | 139.5491 | 1255038.5673 | 71574.3171 | 1779913.8655 | 1953138.1148 | 0 | 208230.6034 | 0 | 2054479.2325 | 5345333.5314 | 3648299.9708 | 16316008.2028 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 22346888.0708 | 31804523.1147 | 237137.3706 | 1.1815 | 18914.1219 | 26918.944 | 385.59 | 548.7791
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.0787 | 8.3607 | 0.33275 | 4 | 17765.7116 | 24871.3033 | 362.1781 | 507.0352 | 81.8708 | 0 | 134.7007 | 1341172.2532 | 76458.3921 | 1919652.0368 | 2144465.2735 | 0 | 205714.4326 | 0 | 2218110.3314 | 5771068.0854 | 3938872.5519 | 17615513.3569 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 23646393.2248 | 33104028.2687 | 316227.766 | 1.331 | 17765.7116 | 24871.3033 | 362.1781 | 507.0352
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.7861 | 9.0018 | 0.36594 | 4 | 16895.6771 | 23356.81 | 344.4412 | 476.1602 | 81.8554 | 0 | 148.8521 | 1412529.686 | 80497.4053 | 2036549.1543 | 2307502.7045 | 0 | 200710.1608 | 0 | 2354737.7533 | 6126544.6108 | 4181492.5848 | 18700564.0598 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 24731443.9277 | 34189078.9716 | 421696.5034 | 1.4638 | 16895.6771 | 23356.81 | 344.4412 | 476.1602
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.5197 | 9.5318 | 0.39435 | 4 | 16238.7994 | 22234.5091 | 331.0499 | 453.2805 | 81.8366 | 0 | 140.087 | 1470311.9737 | 83762.7886 | 2131963.2464 | 2442552.3844 | 0 | 194498.1654 | 0 | 2466004.5378 | 6416037.9602 | 4379077.7442 | 19584208.8005 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 25615088.6684 | 35072723.7123 | 562341.3252 | 1.5774 | 16238.7994 | 22234.5091 | 331.0499 | 453.2805
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.3318 | 9.9575 | 0.41787 | 4 | 15743.9749 | 21402.2531 | 320.9622 | 436.3139 | 81.8176 | 0 | 154.8956 | 1515965.0754 | 86339.172 | 2207831.0665 | 2551185.9478 | 0 | 187926.7849 | 0 | 2554206.7382 | 6645521.9928 | 4535705.3119 | 20284682.0895 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 26315561.9574 | 35773197.0013 | 749894.2093 | 1.6715 | 15743.9749 | 21402.2531 | 320.9622 | 436.3139
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.3527 | 10.294 | 0.4369 | 4 | 15371.7613 | 20783.5695 | 313.3741 | 423.7012 | 81.8003 | 0 | 164.6512 | 1551605.3827 | 88348.1935 | 2267357.787 | 2637189.1224 | 0 | 181682.2339 | 0 | 2623211.2606 | 6825057.6055 | 4658242.0566 | 20832693.6422 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 26863573.5101 | 36321208.554 | 1000000 | 1.7476 | 15371.7613 | 20783.5695 | 313.3741 | 423.7012
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7085 | 10.556 | 0.452 | 4 | 15092.0333 | 20323.0285 | 307.6715 | 414.3124 | 81.7853 | 0 | 170.5676 | 1579077.4541 | 89895.3444 | 2313421.9102 | 2704202.4578 | 0 | 176096.9461 | 0 | 2676450.7039 | 6963575.716 | 4752783.5133 | 21255504.0457 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27286383.9136 | 36744018.9575 | 1333521.4322 | 1.808 | 15092.0333 | 20323.0285 | 307.6715 | 414.3124
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.513 | 10.7563 | 0.46377 | 4 | 14881.9356 | 19980.1697 | 303.3884 | 407.3228 | 81.773 | 0 | 171.132 | 1599934.0723 | 91069.0733 | 2348498.8946 | 2755500.3356 | 0 | 171269.3641 | 0 | 2716845.9785 | 7068675.9344 | 4824516.572 | 21576310.2246 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27607190.0926 | 37064825.1365 | 1778279.41 | 1.8551 | 14881.9356 | 19980.1697 | 303.3884 | 407.3228
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.9091 | 10.9111 | 0.47293 | 4 | 14724.1994 | 19723.7024 | 300.1727 | 402.0944 | 81.7631 | 0 | 173.9558 | 1615961.7475 | 91970.5337 | 2375516.6399 | 2795169.8464 | 0 | 167336.4301 | 0 | 2747922.5271 | 7149530.7391 | 4879701.6376 | 21823110.1014 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 27853989.9693 | 37311625.0133 | 2371373.7057 | 1.8917 | 14724.1994 | 19723.7024 | 300.1727 | 402.0944
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.9614 | 11.0276 | 0.47992 | 4 | 14605.8087 | 19532.4346 | 297.7592 | 398.1951 | 81.7553 | 0 | 174.7501 | 1627978.7594 | 92646.12 | 2395809.241 | 2825055.1012 | 0 | 164117.3274 | 0 | 2771186.5541 | 7210058.9652 | 4921013.3957 | 22007865.464 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28038745.3319 | 37496380.3758 | 3162277.6602 | 1.9197 | 14605.8087 | 19532.4346 | 297.7592 | 398.1951
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.7682 | 11.1169 | 0.48529 | 4 | 14516.9679 | 19389.0832 | 295.948 | 395.2727 | 81.7492 | 0 | 162.4233 | 1637156.9699 | 93161.937 | 2411328.6975 | 2847962.9468 | 0 | 161600.86 | 0 | 2788972.4504 | 7256334.219 | 4952597.2072 | 22149115.2877 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28179995.1556 | 37637630.1995 | 4216965.0343 | 1.9412 | 14516.9679 | 19389.0832 | 295.948 | 395.2727
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.3723 | 11.1837 | 0.48935 | 4 | 14450.3121 | 19282.0033 | 294.5892 | 393.0897 | 81.7445 | 0 | 181.855 | 1644009.6311 | 93546.9583 | 2422927.5589 | 2865113.1628 | 0 | 159609.5922 | 0 | 2802230.6923 | 7290829.4448 | 4976140.9077 | 22254407.9481 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28285287.816 | 37742922.8599 | 5623413.2519 | 1.9574 | 14450.3121 | 19282.0033 | 294.5892 | 393.0897
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.823 | 11.2336 | 0.49241 | 4 | 14400.3073 | 19201.9999 | 293.5697 | 391.4587 | 81.741 | 0 | 168.576 | 1649109.8515 | 93833.4618 | 2431566.7244 | 2877903.4987 | 0 | 158048.5188 | 0 | 2812080.2015 | 7316455.8473 | 4993631.4539 | 22332629.5579 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28363509.4258 | 37821144.4697 | 7498942.0933 | 1.9696 | 14400.3073 | 19201.9999 | 293.5697 | 391.4587
1 | 1700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1734 | 11.2723 | 0.49476 | 4 | 14362.7977 | 19141.713 | 292.8051 | 390.2297 | 81.7382 | 0 | 175.3549 | 1653068.9893 | 94055.8327 | 2438276.8509 | 2887847.5025 | 0 | 156892.6869 | 0 | 2819755.3263 | 7336424.9476 | 5007260.7752 | 22393582.9114 | 961560.8286 | 5069319.0393 | 5069319.0393 | 1478867.319 | 2909448.6856 | 0 | 28424462.7793 | 37882097.8232 | 10000000 | 1.979 | 14362.7977 | 19141.713 | 292.8051 | 390.2297
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 20.1388 | [19 empty] | 100 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.2557 | [19 empty] | 133.3521 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9157 | [19 empty] | 177.8279 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.8183 | [19 empty] | 237.1374 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2345 | [19 empty] | 316.2278 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9871 | [19 empty] | 421.6965 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.1243 | [19 empty] | 562.3413 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.8214 | [19 empty] | 749.8942 | 0
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.84513 | 0.074566 | 0.00050057 | 4 | 3426518.9105 | 8363684.8377 | 69854.2227 | 170505.0281 | 71.793 | 0 | 71.0099 | 45293.4554 | 2377.9628 | 44366.2301 | 45714.3258 | 0 | 31522.9821 | 0 | 66017.2329 | 171763.2981 | 117231.9803 | 524287.4676 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 6860913.3905 | 16746592.9114 | 1000 | 0.0020023 | 3426518.9105 | 8363684.8377 | 69854.2227 | 170505.0281
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1847 | 0.11505 | 0.0014246 | 4 | 1233447.3438 | 2968237.8231 | 25145.4925 | 60511.5429 | 75.4325 | 0 | 188.2383 | 63697.7915 | 3437.4003 | 62570.6508 | 56062.3019 | 0 | 37706.1889 | 0 | 87154.99 | 226759.4061 | 154767.9541 | 692156.6836 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7028782.6065 | 16914462.1273 | 1333.5214 | 0.0056985 | 1233447.3438 | 2968237.8231 | 25145.4925 | 60511.5429
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.16663 | 0.0027556 | 4 | 655219.5491 | 1552076.1939 | 13357.5368 | 31641.1726 | 78.0142 | 0 | 275.4549 | 84482.0633 | 4646.2933 | 83978.7991 | 68690.7486 | 0 | 44128.9319 | 0 | 111511.4661 | 290129.9607 | 198019.6597 | 885587.9228 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7222213.8456 | 17107893.3665 | 1778.2794 | 0.011023 | 655219.5491 | 1552076.1939 | 13357.5368 | 31641.1726
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.23755 | 0.0046228 | 4 | 403880.9602 | 938497.8503 | 8233.6597 | 19132.5481 | 80.0102 | 0 | 387.2214 | 110060.7185 | 6142.8051 | 111345.2842 | 85781.7863 | 0 | 52024.15 | 0 | 142488.3502 | 370725.4589 | 253027.7434 | 1131596.2967 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7468222.2195 | 17353901.7404 | 2371.3737 | 0.018491 | 403880.9602 | 938497.8503 | 8233.6597 | 19132.5481
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.923 | 0.32667 | 0.0071982 | 4 | 269352.5766 | 612693.1862 | 5491.1166 | 12490.5793 | 81.4324 | 0 | 93.899 | 139109.8796 | 7849.1258 | 143503.5599 | 107402.1948 | 0 | 60200.2351 | 0 | 178645.3481 | 464798.5506 | 317234.5615 | 1418743.4555 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 7755369.3783 | 17641048.8992 | 3162.2777 | 0.028793 | 269352.5766 | 612693.1862 | 5491.1166 | 12490.5793
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8413 | 0.43947 | 0.010651 | 4 | 190006.554 | 422046.0565 | 3873.5406 | 8603.9797 | 82.4854 | 0 | 84.088 | 172537.815 | 9814.7661 | 181785.9939 | 134572.9037 | 0 | 68986.8422 | 0 | 221402.3452 | 576043.4863 | 393161.5159 | 1758305.6682 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8094931.5911 | 17980611.112 | 4216.965 | 0.042603 | 190006.554 | 422046.0565 | 3873.5406 | 8603.9797
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0586 | 0.58935 | 0.015292 | 4 | 139308.543 | 300921.8446 | 2839.9931 | 6134.6988 | 83.3055 | 0 | 114.5291 | 213121.023 | 12202.6802 | 229738.8913 | 170731.3556 | 0 | 79572.8835 | 0 | 275093.0651 | 715735.726 | 488504.3399 | 2184699.9647 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 8521325.8875 | 18407005.4084 | 5623.4133 | 0.061169 | 139308.543 | 300921.8446 | 2839.9931 | 6134.6988
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5324 | 0.77098 | 0.021387 | 4 | 105303.4451 | 220860.3583 | 2146.7532 | 4502.5371 | 83.8829 | 0 | 119.533 | 258281.0557 | 14860.0488 | 284686.1562 | 214836.0735 | 0 | 90000.4216 | 0 | 336438.8648 | 875344.9131 | 597440.8897 | 2671888.4234 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9008514.3463 | 18894193.8671 | 7498.9421 | 0.085548 | 105303.4451 | 220860.3583 | 2146.7532 | 4502.5371
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2599 | 0.98237 | 0.029049 | 4 | 82132.1008 | 167210.9114 | 1674.374 | 3408.8206 | 84.2403 | 0 | 98.9707 | 306684.1402 | 17699.1438 | 345485.306 | 265961.2398 | 0 | 99494.6508 | 0 | 403776.5474 | 1050543.7505 | 717017.6962 | 3206662.4748 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 9543288.3976 | 19428967.9185 | 10000 | 0.11619 | 82132.1008 | 167210.9114 | 1674.374 | 3408.8206
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9176 | 1.3118 | 0.040009 | 4 | 64655.3907 | 126427.0904 | 1318.0876 | 2577.3872 | 84.7303 | 0 | 102.4775 | 376747.4249 | 21821.5133 | 435257.8289 | 344665.7698 | 0 | 116379.5456 | 0 | 505000.1122 | 1313906.7021 | 896768.3223 | 4010547.2191 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 10347173.142 | 20232852.6628 | 13335.2143 | 0.16004 | 64655.3907 | 126427.0904 | 1318.0876 | 2577.3872
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9682 | 1.6879 | 0.053655 | 4 | 52252.0139 | 98313.678 | 1065.228 | 2004.2573 | 85.0033 | 0 | 95.7942 | 450248.5212 | 26133.1381 | 532402.0671 | 434874.571 | 0 | 131161.543 | 0 | 614179.7377 | 1597969.6919 | 1090647.1497 | 4877616.4196 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 11214242.3425 | 21099921.8634 | 17782.7941 | 0.21462 | 52252.0139 | 98313.678 | 1065.228 | 2004.2573
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.064 | 2.0699 | 0.070186 | 4 | 42901.8029 | 78114.2516 | 874.6113 | 1592.4647 | 85.1816 | 0 | 141.3335 | 520036.7264 | 30223.4599 | 626708.726 | 526735.3825 | 0 | 139151.8335 | 0 | 718713.8901 | 1869946.1135 | 1276276.646 | 5707792.778 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 12044418.7009 | 21930098.2218 | 23713.7371 | 0.28074 | 42901.8029 | 78114.2516 | 874.6113 | 1592.4647
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.4575 | 2.7356 | 0.093901 | 4 | 35865.891 | 62185.3764 | 731.1747 | 1267.733 | 85.376 | 0 | 111.4633 | 633102.4542 | 36841.4492 | 783205.63 | 686782.3768 | 0 | 163629.1696 | 0 | 898388.8212 | 2337423.4278 | 1595339.5187 | 7134712.8476 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 13471338.7705 | 23357018.2913 | 31622.7766 | 0.3756 | 35865.891 | 62185.3764 | 731.1747 | 1267.733
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.0212 | 3.4223 | 0.12178 | 4 | 30514.5899 | 50808.2886 | 622.0812 | 1035.7957 | 85.4992 | 0 | 112.8464 | 741422.6488 | 43172.0282 | 936810.4812 | 851886.632 | 0 | 180102.8395 | 0 | 1073823.9056 | 2793869.5308 | 1906873.363 | 8527961.4291 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 14864587.352 | 24750266.8728 | 42169.6503 | 0.48713 | 30514.5899 | 50808.2886 | 622.0812 | 1035.7957
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.5982 | 4.2343 | 0.15591 | 4 | 26380.3836 | 42232.2393 | 537.7998 | 860.9613 | 85.5948 | 0 | 108.7184 | 861491.3851 | 50178.9831 | 1110667.0335 | 1047071.6937 | 0 | 196371.4687 | 0 | 1273654.42 | 3313787.5384 | 2261728.0865 | 10114950.6089 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 16451576.5318 | 26337256.0526 | 56234.1325 | 0.62363 | 26380.3836 | 42232.2393 | 537.7998 | 860.9613
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.089 | 5.1591 | 0.19634 | 4 | 23169.6706 | 35757.0255 | 472.3451 | 728.9553 | 85.6675 | 0 | 140.3788 | 990237.9762 | 57680.9929 | 1300746.2234 | 1269380.2543 | 0 | 211167.5641 | 0 | 1493393.0743 | 3885502.4422 | 2651935.2559 | 11860043.7833 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 18196669.7062 | 28082349.2271 | 74989.4209 | 0.78537 | 23169.6706 | 35757.0255 | 472.3451 | 728.9553
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.2519 | 6.1665 | 0.2423 | 4 | 20673.7753 | 30873.7098 | 421.4629 | 629.4023 | 85.7194 | 0 | 133.7556 | 1122939.704 | 65400.9634 | 1500193.6999 | 1511596.188 | 0 | 223207.7148 | 0 | 1725101.9254 | 4488361.3428 | 3063398.843 | 13700200.3814 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 20036826.3043 | 29922505.8251 | 100000 | 0.96919 | 20673.7753 | 30873.7098 | 421.4629 | 629.4023
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.6271 | 7.1989 | 0.29171 | 4 | 18740.1807 | 27212.329 | 382.0439 | 554.7601 | 85.7497 | 0 | 131.4736 | 1252383.2064 | 72917.7352 | 1697927.2342 | 1759990.3972 | 0 | 230981.9216 | 0 | 1955538.1929 | 5087909.2419 | 3472602.6036 | 15530250.533 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 21866876.4558 | 31752555.9767 | 133352.1432 | 1.1668 | 18740.1807 | 27212.329 | 382.0439 | 554.7601
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.7272 | 8.1951 | 0.3418 | 4 | 17251.4655 | 24482.1324 | 351.6945 | 499.1014 | 85.7589 | 0 | 133.4306 | 1372062.0393 | 79853.351 | 1883420.7387 | 1999991.6652 | 0 | 233918.2015 | 0 | 2172005.9383 | 5651113.9119 | 3857001.3636 | 17249367.2096 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 23585993.1325 | 33471672.6533 | 177827.941 | 1.3672 | 17251.4655 | 24482.1324 | 351.6945 | 499.1014
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1371 | 9.1035 | 0.3897 | 4 | 16112.9224 | 22454.7019 | 328.4837 | 457.7695 | 85.7507 | 0 | 148.1012 | 1477341.3308 | 85941.3026 | 2048687.6914 | 2219250.7791 | 0 | 232372.0943 | 0 | 2364801.3473 | 6152728.0182 | 4199363.2983 | 18780485.8619 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 25117111.7848 | 35002791.3057 | 237137.3706 | 1.5588 | 16112.9224 | 22454.7019 | 328.4837 | 457.7695
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.0493 | 9.5818 | 0.42472 | 4 | 15221.5553 | 21040.507 | 310.312 | 428.9392 | 85.7402 | 0 | 155.5066 | 1531433.1005 | 89063.8183 | 2134362.6685 | 2334871.2969 | 0 | 213567.9112 | 0 | 2458286.5302 | 6395957.2877 | 4365372.2726 | 19522914.8858 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 25859540.8087 | 35745220.3296 | 316227.766 | 1.6989 | 15221.5553 | 21040.507 | 310.312 | 428.9392
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.0324 | 10.5542 | 0.47106 | 4 | 14591.5444 | 19838.0712 | 297.4684 | 404.4259 | 85.7062 | 0 | 148.6996 | 1638834.5292 | 95251.6694 | 2306012.93 | 2570441.7822 | 0 | 220428.774 | 0 | 2664078.1771 | 6931384.9392 | 4730812.6467 | 21157245.4479 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 27493871.3707 | 37379550.8916 | 421696.5034 | 1.8842 | 14591.5444 | 19838.0712 | 297.4684 | 404.4259
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.4855 | 11.0943 | 0.50293 | 4 | 14096.5874 | 19010.6741 | 287.378 | 387.5583 | 85.6802 | 0 | 140.8907 | 1697096.7316 | 98601.095 | 2399996.3283 | 2701611.7227 | 0 | 212706.388 | 0 | 2772904.7836 | 7214529.4458 | 4924064.5905 | 22021511.0854 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 28358137.0083 | 38243816.5292 | 562341.3252 | 2.0117 | 14096.5874 | 19010.6741 | 287.378 | 387.5583
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.025 | 11.5223 | 0.52891 | 4 | 13723.6404 | 18396.2818 | 279.775 | 375.0331 | 85.656 | 0 | 151.7898 | 1742604.2198 | 101213.43 | 2473835.0851 | 2805739.9228 | 0 | 204974.3379 | 0 | 2858063.1283 | 7436093.9904 | 5075286.9449 | 22697811.0592 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29034436.982 | 38920116.5029 | 749894.2093 | 2.1157 | 13723.6404 | 18396.2818 | 279.775 | 375.0331
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.8165 | 11.859 | 0.54975 | 4 | 13442.9965 | 17938.4915 | 274.0537 | 365.7004 | 85.6349 | 0 | 177.4125 | 1778008.3937 | 103243.3534 | 2531544.2685 | 2887775.728 | 0 | 197936.1921 | 0 | 2924418.0949 | 7608736.0024 | 5193118.6655 | 23224780.6985 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29561406.6214 | 39447086.1423 | 1000000 | 2.199 | 13442.9965 | 17938.4915 | 274.0537 | 365.7004
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.9749 | 12.1188 | 0.56614 | 4 | 13231.9994 | 17597.4026 | 269.7522 | 358.7469 | 85.6173 | 0 | 183.7874 | 1805095.144 | 104794.9015 | 2575853.2188 | 2951150.3159 | 0 | 191773.1977 | 0 | 2975180.0434 | 7740808.1796 | 5283260.6403 | 23627915.6413 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 29964541.5641 | 39850221.085 | 1333521.4322 | 2.2646 | 13231.9994 | 17597.4026 | 269.7522 | 358.7469
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.6144 | 12.3159 | 0.5788 | 4 | 13073.4644 | 17343.3494 | 266.5203 | 353.5676 | 85.6032 | 0 | 173.5723 | 1825506.5067 | 105963.2027 | 2609333.2325 | 2999259.229 | 0 | 186520.8238 | 0 | 3013367.3679 | 7840163.7647 | 5351072.8687 | 23931186.9961 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30267812.919 | 40153492.4398 | 1778279.41 | 2.3152 | 13073.4644 | 17343.3494 | 266.5203 | 353.5676
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.8861 | 12.4685 | 0.58864 | 4 | 12954.4018 | 17152.921 | 264.093 | 349.6855 | 85.5919 | 0 | 151.9453 | 1841241.889 | 106863.3376 | 2635196.9581 | 3036555.0277 | 0 | 182324.0504 | 0 | 3042850.6925 | 7916873.3274 | 5403428.7214 | 24165334.0041 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30501959.927 | 40387639.4478 | 2371373.7057 | 2.3546 | 12954.4018 | 17152.921 | 264.093 | 349.6855
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.8406 | 12.583 | 0.59612 | 4 | 12865.0145 | 17010.8384 | 262.2707 | 346.789 | 85.5832 | 0 | 190.5568 | 1852997.3688 | 107535.5017 | 2654549.6455 | 3064536.4961 | 0 | 178918.7653 | 0 | 3064829.7332 | 7974058.2827 | 5442458.6285 | 24339884.4218 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30676510.3447 | 40562189.8656 | 3162277.6602 | 2.3845 | 12865.0145 | 17010.8384 | 262.2707 | 346.789
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.5787 | 12.6714 | 0.60188 | 4 | 12797.924 | 16904.0839 | 260.903 | 344.6126 | 85.5763 | 0 | 167.6594 | 1862055.6226 | 108053.2639 | 2669479.8681 | 3086167.2711 | 0 | 176304.6564 | 0 | 3081803.666 | 8018220.974 | 5472600.5727 | 24474685.8946 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30811311.8174 | 40696991.3383 | 4216965.0343 | 2.4075 | 12797.924 | 16904.0839 | 260.903 | 344.6126
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.1272 | 12.7371 | 0.60621 | 4 | 12747.5788 | 16824.4035 | 259.8766 | 342.9882 | 85.5711 | 0 | 170.5248 | 1868768.0696 | 108436.8406 | 2680553.7207 | 3102235.5152 | 0 | 174232.8224 | 0 | 3094348.5177 | 8050860.105 | 5494877.4503 | 24574313.0415 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30910938.9644 | 40796618.4852 | 5623413.2519 | 2.4248 | 12747.5788 | 16824.4035 | 259.8766 | 342.9882
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.5339 | 12.7858 | 0.60946 | 4 | 12709.8055 | 16764.9022 | 259.1066 | 341.7752 | 85.5672 | 0 | 167.4488 | 1873736.3743 | 108720.6941 | 2688755.7247 | 3114150.1577 | 0 | 172608.0725 | 0 | 3103608.6991 | 8074953.1972 | 5511321.4808 | 24647854.4003 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 30984480.3232 | 40870159.8441 | 7498942.0933 | 2.4378 | 12709.8055 | 16764.9022 | 259.1066 | 341.7752
1 | 1800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.846 | 12.8231 | 0.61194 | 4 | 12681.4682 | 16720.1626 | 258.5289 | 340.8631 | 85.5642 | 0 | 191.4222 | 1877542.9745 | 108938.144 | 2695043.0997 | 3123291.264 | 0 | 171389.3351 | 0 | 3110719.8787 | 8093455.028 | 5523949.3605 | 24704329.0845 | 961560.8286 | 5375065.0943 | 5375065.0943 | 1478867.319 | 3031747.1076 | 0 | 31040955.0073 | 40926634.5282 | 10000000 | 2.4477 | 12681.4682 | 16720.1626 | 258.5289 | 340.8631
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 19.9921 | [19 empty] | 100 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 23.9928 | [19 empty] | 133.3521 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4395 | [19 empty] | 177.8279 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.249 | [19 empty] | 237.1374 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7569 | [19 empty] | 316.2278 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1177 | [19 empty] | 421.6965 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9519 | [19 empty] | 562.3413 | 0
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.71826 | 0.063602 | 0.00027465 | 4 | 6488029.9096 | 15883599.6794 | 132267.2654 | 323808.6636 | 71.9244 | 0 | 89.8945 | 40689.8945 | 2132.6108 | 39061.6601 | 42505.8155 | 0 | 30420.2797 | 0 | 60376.0016 | 157085.9714 | 107214.4033 | 479486.637 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7127718.7057 | 17449646.8307 | 749.8942 | 0.0010986 | 6488029.9096 | 15883599.6794 | 132267.2654 | 323808.6636
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0291 | 0.10291 | 0.0011606 | 4 | 1571771.1939 | 3795139.2516 | 32042.6818 | 77369.0469 | 76.6619 | 0 | 158.8536 | 59777.1993 | 3242.5787 | 57173.8199 | 52105.2486 | 0 | 37136.5831 | 0 | 81679.8176 | 212514.1305 | 145045.2608 | 648674.6387 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7296906.7074 | 17618834.8324 | 1000 | 0.0046425 | 1571771.1939 | 3795139.2516 | 32042.6818 | 77369.0469
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4569 | 0.15827 | 0.0025141 | 4 | 746954.0557 | 1773357.226 | 15227.6688 | 36152.2857 | 80.1929 | 0 | 247.029 | 83352.7788 | 4636.3113 | 80451.0234 | 65094.3293 | 0 | 45242.2119 | 0 | 108722.8953 | 282874.6714 | 193067.7758 | 863441.9971 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7511674.0658 | 17833602.1908 | 1333.5214 | 0.010056 | 746954.0557 | 1773357.226 | 15227.6688 | 36152.2857
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.22727 | 0.0044566 | 4 | 435037.2449 | 1014063.7795 | 8868.8227 | 20673.0618 | 82.5886 | 0 | 352.3001 | 109486.9591 | 6195.4637 | 107255.4322 | 81136.0129 | 0 | 53304.9935 | 0 | 139377.756 | 362632.3307 | 247504.0171 | 1106892.9652 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 7755125.034 | 18077053.159 | 1778.2794 | 0.017826 | 435037.2449 | 1014063.7795 | 8868.8227 | 20673.0618
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6452 | 0.31516 | 0.0071543 | 4 | 281027.3885 | 641715.1407 | 5729.1234 | 13082.2311 | 84.3261 | 0 | 70.9314 | 139509.8255 | 7995.7802 | 139125.4131 | 101575.268 | 0 | 61878.7299 | 0 | 175533.1565 | 456701.2664 | 311707.9986 | 1394027.4382 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8042259.5069 | 18364187.6319 | 2371.3737 | 0.028617 | 281027.3885 | 641715.1407 | 5729.1234 | 13082.2311
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5124 | 0.43034 | 0.010792 | 4 | 194428.5793 | 433541.602 | 3963.6896 | 8838.332 | 85.647 | 0 | 80.1574 | 175124.0127 | 10133.7814 | 178316.151 | 127979.0101 | 0 | 71777.4808 | 0 | 219698.8701 | 571611.3935 | 390136.5215 | 1744777.2211 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8393009.2898 | 18714937.4148 | 3162.2777 | 0.043168 | 194428.5793 | 433541.602 | 3963.6896 | 8838.332
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6159 | 0.57748 | 0.015693 | 4 | 140417.3143 | 304857.4321 | 2862.5969 | 6214.9311 | 86.6311 | 0 | 117.6295 | 216646.7474 | 12630.0389 | 225442.7618 | 161907.1393 | 0 | 82631.9978 | 0 | 272710.8872 | 709537.7878 | 484274.1197 | 2165781.4797 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 8814013.5484 | 19135941.6734 | 4216.965 | 0.06277 | 140417.3143 | 304857.4321 | 2862.5969 | 6214.9311
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9944 | 0.76136 | 0.022157 | 4 | 105033.6408 | 221495.2811 | 2141.2528 | 4515.4809 | 87.3549 | 0 | 108.278 | 264178.9143 | 15486.2496 | 281083.0763 | 204221.9553 | 0 | 94126.0817 | 0 | 335047.5481 | 871724.9924 | 594970.2195 | 2660839.037 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9309071.1057 | 19630999.2307 | 5623.4133 | 0.088629 | 105033.6408 | 221495.2811 | 2141.2528 | 4515.4809
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6339 | 0.97932 | 0.030433 | 4 | 81016.4793 | 165809.4222 | 1651.6305 | 3380.2493 | 87.8384 | 0 | 99.8092 | 316044.6486 | 18596.2863 | 343670.7716 | 254379.1609 | 0 | 104997.3035 | 0 | 404698.3867 | 1052942.1871 | 718654.6785 | 3213983.4232 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 9862215.4919 | 20184143.6169 | 7498.9421 | 0.12173 | 81016.4793 | 165809.4222 | 1651.6305 | 3380.2493
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.048 | 1.3033 | 0.042014 | 4 | 63393.3205 | 124812.9132 | 1292.3586 | 2544.4801 | 88.3701 | 0 | 123.1882 | 387471.5548 | 22888.9125 | 431786.0966 | 328786.731 | 0 | 122274.5814 | 0 | 504351.0718 | 1312218.0321 | 895615.7703 | 4005392.7505 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 10653624.8192 | 20975552.9442 | 10000 | 0.16806 | 63393.3205 | 124812.9132 | 1292.3586 | 2544.4801
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8861 | 1.6831 | 0.056678 | 4 | 50856.4379 | 96384.8959 | 1036.7773 | 1964.9365 | 88.7019 | 0 | 96.1694 | 464483.5752 | 27506.0796 | 529647.7167 | 416220.6615 | 0 | 138255.2187 | 0 | 614684.1682 | 1599282.1165 | 1091542.9065 | 4881622.4428 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 11529854.5115 | 21851782.6365 | 13335.2143 | 0.22671 | 50856.4379 | 96384.8959 | 1036.7773 | 1964.9365
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.4035 | 2.1538 | 0.075571 | 4 | 41570.3907 | 75716.8898 | 847.4686 | 1543.5912 | 88.9553 | 0 | 88.815 | 553031.0409 | 32807.7917 | 645028.4452 | 524591.1674 | 0 | 155207.5286 | 0 | 745159.7298 | 1938752.7636 | 1323238.5986 | 5917817.0658 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 12566049.1345 | 22887977.2595 | 17782.7941 | 0.30228 | 41570.3907 | 75716.8898 | 847.4686 | 1543.5912
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.713 | 2.7305 | 0.099626 | 4 | 34579.9872 | 60481.7837 | 704.9598 | 1233.003 | 89.1497 | 0 | 108.7085 | 653968.5108 | 38842.2523 | 779739.3476 | 657293.4342 | 0 | 172833.8548 | 0 | 898044.1859 | 2336526.7576 | 1594727.5229 | 7131975.8662 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 13780207.9349 | 24102136.0599 | 23713.7371 | 0.3985 | 34579.9872 | 60481.7837 | 704.9598 | 1233.003
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.9749 | 3.4348 | 0.12996 | 4 | 29245.1087 | 49100.901 | 596.2011 | 1000.9883 | 89.3007 | 0 | 116.9191 | 768982.1859 | 45707.6938 | 936754.1703 | 819311.3694 | 0 | 191266.4783 | 0 | 1077188.5401 | 2802623.6195 | 1912848.2085 | 8554682.2657 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 15202914.3344 | 25524842.4594 | 31622.7766 | 0.51984 | 29245.1087 | 49100.901 | 596.2011 | 1000.9883
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2593 | 4.2761 | 0.16749 | 4 | 25130.682 | 40537.1976 | 512.3229 | 826.4056 | 89.4177 | 0 | 144.6552 | 897560.3134 | 53370.6948 | 1116091.9858 | 1012821.4958 | 0 | 209718.7159 | 0 | 1282929.6502 | 3337919.7847 | 2278198.8405 | 10188611.481 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 16836843.5498 | 27158771.6748 | 42169.6503 | 0.66997 | 25130.682 | 40537.1976 | 512.3229 | 826.4056
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.5869 | 5.2571 | 0.21324 | 4 | 21890.0633 | 33991.4371 | 446.2585 | 692.9614 | 89.5079 | 0 | 151.7747 | 1038402.3033 | 61750.9225 | 1316527.6346 | 1238467.2353 | 0 | 226680.7718 | 0 | 1513913.2583 | 3938891.7519 | 2688374.5568 | 12023008.4346 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 18671240.5033 | 28993168.6283 | 56234.1325 | 0.85296 | 21890.0633 | 33991.4371 | 446.2585 | 692.9614
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.9427 | 6.3755 | 0.26656 | 4 | 19410.8169 | 29091.6331 | 395.7158 | 593.0723 | 89.5753 | 0 | 141.8172 | 1189820.7983 | 70744.7866 | 1536116.8182 | 1495749.0601 | 0 | 243221.0314 | 0 | 1768904.4729 | 4602326.5862 | 3141182.4635 | 14048066.0171 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 20696298.0858 | 31018226.2108 | 74989.4209 | 1.0662 | 19410.8169 | 29091.6331 | 395.7158 | 593.0723
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.6003 | 7.5332 | 0.32494 | 4 | 17481.937 | 25423.2618 | 356.3929 | 518.2876 | 89.6168 | 0 | 127.4866 | 1338449.2672 | 79555.7284 | 1755421.8865 | 1762196.8574 | 0 | 254243.9607 | 0 | 2024048.403 | 5266158.7553 | 3594261.5592 | 16074336.4177 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 22722568.4864 | 33044496.6114 | 100000 | 1.2998 | 17481.937 | 25423.2618 | 356.3929 | 518.2876
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2165 | 8.6829 | 0.38584 | 4 | 15989.2221 | 22677.232 | 325.9619 | 462.306 | 89.6329 | 0 | 149.1578 | 1479378.6055 | 87891.7016 | 1966628.1871 | 2027101.1635 | 0 | 259868.5398 | 0 | 2270138.5971 | 5906434.9602 | 4031263.2254 | 18028704.9804 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 24676937.0491 | 34998865.1741 | 133352.1432 | 1.5433 | 15989.2221 | 22677.232 | 325.9619 | 462.306
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.3212 | 9.7607 | 0.44574 | 4 | 14841.9553 | 20631.2076 | 302.5733 | 420.5951 | 89.6266 | 0 | 150.3396 | 1606374.7957 | 95385.069 | 2159618.0669 | 2275886.6997 | 0 | 260074.9976 | 0 | 2494962.4553 | 6491380.5215 | 4430500.5905 | 19814183.1962 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 26462415.2649 | 36784343.3899 | 177827.941 | 1.7829 | 14841.9553 | 20631.2076 | 302.5733 | 420.5951
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.5561 | 10.7188 | 0.50148 | 4 | 13965.8149 | 19111.562 | 284.712 | 389.615 | 89.6041 | 0 | 154.1013 | 1715624.0574 | 101814.9811 | 2327660.4426 | 2497546.7753 | 0 | 255722.2952 | 0 | 2690363.7351 | 6999774.5693 | 4777489.9745 | 21365996.8306 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 28014228.8993 | 38336157.0243 | 237137.3706 | 2.0059 | 13965.8149 | 19111.562 | 284.712 | 389.615
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.7628 | 11.5373 | 0.55102 | 4 | 13300.1158 | 17983.2238 | 271.1409 | 366.6123 | 89.5728 | 0 | 180.8837 | 1806482.7524 | 107149.5605 | 2468854.3109 | 2687321.7045 | 0 | 248365.3941 | 0 | 2854087.7517 | 7425750.8761 | 5068227.5569 | 22666239.9072 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 29314471.9759 | 39636400.1009 | 316227.766 | 2.2041 | 13300.1158 | 17983.2238 | 271.1409 | 366.6123
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.923 | 12.215 | 0.59341 | 4 | 12796.18 | 17144.7152 | 260.8674 | 349.5182 | 89.5387 | 0 | 147.7725 | 1880122.2845 | 111463.6956 | 2584262.475 | 2844791.9282 | 0 | 239533.5656 | 0 | 2987467.8401 | 7772778.5059 | 5305081.0449 | 23725501.3397 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 30373733.4084 | 40695661.5334 | 421696.5034 | 2.3737 | 12796.18 | 17144.7152 | 260.8674 | 349.5182
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.066 | 12.757 | 0.62842 | 4 | 12415.684 | 16522.0135 | 253.1105 | 336.8236 | 89.5062 | 0 | 167.8388 | 1938052.7016 | 114851.1377 | 2675672.7325 | 2971003.3468 | 0 | 230223.2749 | 0 | 3092623.2455 | 8046371.3005 | 5491813.749 | 24560611.4884 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 31208843.5571 | 41530771.6821 | 562341.3252 | 2.5137 | 12415.684 | 16522.0135 | 253.1105 | 336.8236
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.3575 | 13.1863 | 0.65675 | 4 | 12128.9032 | 16058.0482 | 247.2641 | 327.365 | 89.4773 | 0 | 171.6237 | 1983343.8102 | 117495.3766 | 2747525.636 | 3071126.7142 | 0 | 221461.1629 | 0 | 3174971.5529 | 8260624.7045 | 5638046.0997 | 25214595.057 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 31862827.1257 | 42184755.2507 | 749894.2093 | 2.627 | 12128.9032 | 16058.0482 | 247.2641 | 327.365
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.923 | 13.52 | 0.67922 | 4 | 11913.0251 | 15712.2048 | 242.8631 | 320.3145 | 89.4529 | 0 | 153.9136 | 2018206.2292 | 119528.1859 | 2803067.7259 | 3149071.193 | 0 | 213633.7736 | 0 | 3238367.772 | 8425568.6622 | 5750623.74 | 25718067.2819 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32366299.3506 | 42688227.4756 | 1000000 | 2.7169 | 11913.0251 | 15712.2048 | 242.8631 | 320.3145
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.9077 | 13.7776 | 0.69681 | 4 | 11750.6653 | 15453.9325 | 239.5532 | 315.0493 | 89.433 | 0 | 165.9313 | 2044917.5133 | 121084.1474 | 2845762.7337 | 3209311.5292 | 0 | 206971.2352 | 0 | 3286938.3919 | 8551939.452 | 5836874.4008 | 26103799.4035 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 32752031.4722 | 43073959.5972 | 1333521.4322 | 2.7872 | 11750.6653 | 15453.9325 | 239.5532 | 315.0493
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.4204 | 13.9737 | 0.71039 | 4 | 11628.6373 | 15261.1214 | 237.0655 | 311.1186 | 89.4172 | 0 | 172.7543 | 2065126.7265 | 122260.4357 | 2878145.8124 | 3255190.1616 | 0 | 201426.7941 | 0 | 3323638.4728 | 8647425.5342 | 5902045.6139 | 26395259.5511 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33043491.6198 | 43365419.7448 | 1778279.41 | 2.8416 | 11628.6373 | 15261.1214 | 237.0655 | 311.1186
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5756 | 14.1232 | 0.72083 | 4 | 11536.9688 | 15116.8484 | 235.1967 | 308.1774 | 89.4047 | 0 | 168.97 | 2080473.9446 | 123153.1899 | 2902784.9332 | 3290205.9863 | 0 | 196965.5359 | 0 | 3351497.6001 | 8719909.2688 | 5951517.2522 | 26616507.711 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33264739.7797 | 43586667.9048 | 2371373.7057 | 2.8833 | 11536.9688 | 15116.8484 | 235.1967 | 308.1774
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.4427 | 14.2353 | 0.72875 | 4 | 11468.1337 | 15009.0881 | 233.7934 | 305.9806 | 89.3952 | 0 | 172.4963 | 2091946.1009 | 123820.2219 | 2921229.4285 | 3316479.6231 | 0 | 193387.3541 | 0 | 3372276.4642 | 8773971.6107 | 5988415.9114 | 26781526.7149 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33429758.7836 | 43751686.9086 | 3162277.6602 | 2.915 | 11468.1337 | 15009.0881 | 233.7934 | 305.9806
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.1077 | 14.3213 | 0.73482 | 4 | 11416.4605 | 14928.1938 | 232.74 | 304.3314 | 89.3878 | 0 | 158.5582 | 2100714.6993 | 124329.8803 | 2935342.6193 | 3336618.8452 | 0 | 190630.7294 | 0 | 3388178.3417 | 8815345.0341 | 6016654.123 | 26907814.2722 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33556046.3409 | 43877974.4659 | 4216965.0343 | 2.9393 | 11416.4605 | 14928.1938 | 232.74 | 304.3314
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.605 | 14.3855 | 0.73939 | 4 | 11377.6798 | 14867.7025 | 231.9494 | 303.0982 | 89.3821 | 0 | 171.2484 | 2107256.9323 | 124710.0332 | 2945881.157 | 3351677.1345 | 0 | 188476.539 | 0 | 3400020.7005 | 8846156.4224 | 6037683.5287 | 27001862.4476 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33650094.5163 | 43972022.6413 | 5623413.2519 | 2.9576 | 11377.6798 | 14867.7025 | 231.9494 | 303.0982
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.9749 | 14.4332 | 0.74282 | 4 | 11348.5804 | 14822.4864 | 231.3562 | 302.1764 | 89.3779 | 0 | 183.6617 | 2112113.7761 | 124992.1954 | 2953709.6222 | 3362874.1408 | 0 | 186800.6144 | 0 | 3408791.2361 | 8868975.557 | 6053258.0569 | 27071515.1988 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33719747.2675 | 44041675.3925 | 7498942.0933 | 2.9713 | 11348.5804 | 14822.4864 | 231.3562 | 302.1764
1 | 1900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.2675 | 14.471 | 0.74547 | 4 | 11326.7486 | 14788.283 | 230.9111 | 301.4792 | 89.3746 | 0 | 153.523 | 2115951.3675 | 125215.1095 | 2959898.1069 | 3371732.1525 | 0 | 185585.2629 | 0 | 3415768.9797 | 8887130.2146 | 6065648.9838 | 27126930.1773 | 961560.8286 | 5686671.2401 | 5686671.2401 | 1478867.319 | 3156389.5659 | 0 | 33775162.2461 | 44097090.3711 | 10000000 | 2.9819 | 11326.7486 | 14788.283 | 230.9111 | 301.4792
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0792 | [19 empty] | 100 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.966 | [19 empty] | 133.3521 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0766 | [19 empty] | 177.8279 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1593 | [19 empty] | 237.1374 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1386 | [19 empty] | 316.2278 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3201 | [19 empty] | 421.6965 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 27.5065 | [19 empty] | 562.3413 | 0
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.094897 | 0.00081751 | 4 | 2320771.1342 | 5613191.8265 | 47312.0586 | 114432.5078 | 77.8092 | 0 | 83.1985 | 57249.7238 | 3122.2958 | 53534.8574 | 49544.0049 | 0 | 37804.7549 | 0 | 78489.6983 | 204214.0945 | 139380.3157 | 623339.745 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7589038.0504 | 18355418.9068 | 749.8942 | 0.0032701 | 2320771.1342 | 5613191.8265 | 47312.0586 | 114432.5078
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.14445 | 0.0021316 | 4 | 913055.9258 | 2175743.6256 | 18613.88 | 44355.4767 | 81.8006 | 0 | 209.8516 | 79528.8129 | 4458.5681 | 74684.2049 | 60745.444 | 0 | 45180.8346 | 0 | 103193.1672 | 268487.4532 | 183248.2036 | 819526.6885 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 7785224.9939 | 18551605.8503 | 1000 | 0.0085266 | 913055.9258 | 2175743.6256 | 18613.88 | 44355.4767
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.21017 | 0.0040743 | 4 | 492282.4726 | 1152916.6022 | 10035.8441 | 23503.7644 | 84.744 | 0 | 302.6823 | 105856.6017 | 6057.0075 | 100577.5927 | 75428.9448 | 0 | 53365.7133 | 0 | 133101.4854 | 346302.7621 | 236358.751 | 1057048.8584 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8022747.1638 | 18789128.0202 | 1333.5214 | 0.016297 | 492282.4726 | 1152916.6022 | 10035.8441 | 23503.7644
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.29879 | 0.0068181 | 4 | 305028.0325 | 699800.1191 | 6218.409 | 14266.372 | 86.9764 | 0 | 422.3717 | 137699.1538 | 8003.3167 | 133040.6664 | 95113.5478 | 0 | 63029.4417 | 0 | 170385.5893 | 443308.3525 | 302567.0597 | 1353147.1279 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8318845.4333 | 19085226.2897 | 1778.2794 | 0.027272 | 305028.0325 | 699800.1191 | 6218.409 | 14266.372
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1808 | 0.41485 | 0.010587 | 4 | 204945.6373 | 459182.034 | 4178.094 | 9361.0469 | 88.633 | 0 | 100.6827 | 175309.357 | 10309.886 | 172760.8494 | 120803.5285 | 0 | 73990.8912 | 0 | 215738.0597 | 561306.1774 | 383102.9998 | 1713321.7491 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 8679020.0545 | 19445400.9109 | 2371.3737 | 0.042348 | 204945.6373 | 459182.034 | 4178.094 | 9361.0469
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1749 | 0.55795 | 0.015659 | 4 | 145173.087 | 317065.63 | 2959.5497 | 6463.8117 | 89.8181 | 0 | 111.2779 | 217493.091 | 12901.0224 | 218777.7974 | 152529.839 | 0 | 85076.4681 | 0 | 267843.505 | 696873.8577 | 475630.7272 | 2127126.3077 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9092824.6131 | 19859205.4695 | 3162.2777 | 0.062634 | 145173.087 | 317065.63 | 2959.5497 | 6463.8117
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4413 | 0.7404 | 0.022394 | 4 | 107049.4029 | 227243.5442 | 2182.3469 | 4632.667 | 90.7136 | 0 | 97.6626 | 266701.4844 | 15923.0086 | 274160.0275 | 192821.2907 | 0 | 97352.1596 | 0 | 330313.6086 | 859408.2529 | 586563.7917 | 2623243.6239 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 9588941.9293 | 20355322.7857 | 4216.965 | 0.089575 | 107049.4029 | 227243.5442 | 2182.3469 | 4632.667
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0077 | 0.9658 | 0.031176 | 4 | 81528.1432 | 167863.3501 | 1662.0615 | 3422.1214 | 91.3553 | 0 | 98.6811 | 322550.7137 | 19348.0184 | 338943.9089 | 242601.3402 | 0 | 110123.4776 | 0 | 403091.3089 | 1048760.9005 | 715800.8645 | 3201220.5327 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10166918.8381 | 20933299.6945 | 5623.4133 | 0.1247 | 81528.1432 | 167863.3501 | 1662.0615 | 3422.1214
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3272 | 1.3013 | 0.043329 | 4 | 63417.5022 | 125537.5775 | 1292.8516 | 2559.2533 | 91.9718 | 0 | 99.8218 | 399004.7438 | 24038.5357 | 430038.8995 | 316478.0306 | 0 | 130154.7838 | 0 | 506888.8474 | 1318820.8038 | 900122.2977 | 4025546.9424 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 10991245.2478 | 21757626.1041 | 7498.9421 | 0.17332 | 63417.5022 | 125537.5775 | 1292.8516 | 2559.2533
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7413 | 1.6503 | 0.058437 | 4 | 50447.5666 | 96507.4343 | 1028.4419 | 1967.4346 | 92.3451 | 0 | 95.9801 | 472425.9072 | 28537.01 | 519933.814 | 393606.9941 | 0 | 143746.5919 | 0 | 607717.6237 | 1581156.5969 | 1079171.8669 | 4826296.4047 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 11791994.71 | 22558375.5664 | 10000 | 0.23375 | 50447.5666 | 96507.4343 | 1028.4419 | 1967.4346
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.0003 | 2.1216 | 0.078343 | 4 | 40948.1071 | 75304.8697 | 834.7826 | 1535.1916 | 92.6559 | 0 | 107.844 | 564492.6422 | 34169.3978 | 635485.0614 | 497742.6359 | 0 | 162114.8734 | 0 | 738661.7982 | 1921846.4785 | 1311699.7116 | 5866212.5989 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 12831910.9043 | 23598291.7607 | 13335.2143 | 0.31337 | 40948.1071 | 75304.8697 | 834.7826 | 1535.1916
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0151 | 2.7021 | 0.10384 | 4 | 33839.9136 | 59761.591 | 689.8724 | 1218.3209 | 92.8939 | 0 | 109.8279 | 669892.0674 | 40607.4581 | 771026.2592 | 626039.7766 | 0 | 181386.3655 | 0 | 892691.2515 | 2322599.5201 | 1585221.8971 | 7089464.5955 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 14055162.9009 | 24821543.7573 | 17782.7941 | 0.41534 | 33839.9136 | 59761.591 | 689.8724 | 1218.3209
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9092 | 3.4099 | 0.13609 | 4 | 28442.0932 | 48220.7387 | 579.8305 | 983.045 | 93.077 | 0 | 129.4565 | 789624.354 | 47908.6003 | 928606.7933 | 782310.9032 | 0 | 201267.9014 | 0 | 1072390.2354 | 2790139.415 | 1904327.4824 | 8516575.685 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 15482273.9903 | 26248654.8467 | 23713.7371 | 0.54434 | 28442.0932 | 48220.7387 | 579.8305 | 983.045
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8434 | 4.268 | 0.17643 | 4 | 24292.4527 | 39548.5311 | 495.2345 | 806.2503 | 93.2198 | 0 | 134.5103 | 925298.7599 | 56167.2751 | 1111142.4778 | 971621.2899 | 0 | 221826.7561 | 0 | 1281562.0579 | 3334361.5901 | 2275770.2996 | 10177750.5063 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 17143448.8117 | 27909829.6681 | 31622.7766 | 0.70571 | 24292.4527 | 39548.5311 | 495.2345 | 806.2503
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.8567 | 5.2822 | 0.22581 | 4 | 21071.625 | 32991.4102 | 429.5736 | 672.5745 | 93.3303 | 0 | 136.9569 | 1075669.9783 | 65304.6801 | 1317679.5523 | 1195370.6889 | 0 | 241992.8655 | 0 | 1519446.9284 | 3953289.2263 | 2698201.1289 | 12066955.0487 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 19032653.3541 | 29799034.2105 | 42169.6503 | 0.90324 | 21071.625 | 32991.4102 | 429.5736 | 672.5745
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8734 | 6.4415 | 0.28444 | 4 | 18558.2521 | 28020.961 | 378.3351 | 571.2452 | 93.4137 | 0 | 143.2652 | 1237473.9417 | 75119.078 | 1544256.8562 | 1451123.4949 | 0 | 260368.5528 | 0 | 1781653.3502 | 4635496.5498 | 3163821.6452 | 14149313.4686 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 21115011.774 | 31881392.6304 | 56234.1325 | 1.1378 | 18558.2521 | 28020.961 | 378.3351 | 571.2452
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.6164 | 7.4161 | 0.34342 | 4 | 16578.1063 | 24415.7063 | 337.9671 | 497.7472 | 93.4602 | 0 | 130.8238 | 1366914.4486 | 82956.7219 | 1728438.905 | 1666191.1685 | 0 | 259172.2311 | 0 | 1990432.6553 | 5178697.4752 | 3534567.4384 | 15807371.044 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 22773069.3494 | 33539450.2058 | 74989.4209 | 1.3737 | 16578.1063 | 24415.7063 | 337.9671 | 497.7472
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.8996 | 9.044 | 0.42473 | 4 | 15047.0646 | 21384.2812 | 306.7548 | 435.9475 | 93.499 | 0 | 158.7572 | 1572382.3516 | 95369.0125 | 2025768.3749 | 2025798.2619 | 0 | 285343.0718 | 0 | 2341817.8183 | 6092929.5904 | 4158549.6427 | 18597958.1241 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 25563656.4295 | 36330037.2859 | 100000 | 1.6989 | 15047.0646 | 21384.2812 | 306.7548 | 435.9475
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.6233 | 10.2981 | 0.4976 | 4 | 13873.6074 | 19282.767 | 282.8323 | 393.1053 | 93.4981 | 0 | 158.2299 | 1723048.1719 | 104443.5182 | 2247549.1416 | 2303404.0028 | 0 | 288204.3535 | 0 | 2599993.1833 | 6764648.9311 | 4617011.8951 | 20648303.1974 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 27614001.5028 | 38380382.3592 | 133352.1432 | 1.9904 | 13873.6074 | 19282.767 | 282.8323 | 393.1053
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.6398 | 11.4457 | 0.56741 | 4 | 12973.1764 | 17716.8404 | 264.4757 | 361.1818 | 93.4749 | 0 | 164.5483 | 1855952.5483 | 112425.2756 | 2445807.6799 | 2558033.8432 | 0 | 285392.0687 | 0 | 2830468.4521 | 7364298.3035 | 5026284.9133 | 22478663.0847 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 29444361.3901 | 40210742.2464 | 177827.941 | 2.2696 | 12973.1764 | 17716.8404 | 264.4757 | 361.1818
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.6682 | 12.4469 | 0.63094 | 4 | 12286.313 | 16552.3407 | 250.4731 | 337.4419 | 93.4379 | 0 | 162.0337 | 1968466.9344 | 119163.1707 | 2615591.77 | 2780815.0927 | 0 | 278280.1439 | 0 | 3027303.6736 | 7876423.1733 | 5375820.6601 | 24041864.6189 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 31007562.9243 | 41773943.7806 | 237137.3706 | 2.5237 | 12286.313 | 16552.3407 | 250.4731 | 337.4419
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.5829 | 13.2854 | 0.68622 | 4 | 11764.7267 | 15687.0943 | 239.8399 | 319.8026 | 93.3953 | 0 | 161.8538 | 2060439.0656 | 124656.2768 | 2755722.5186 | 2967912.6941 | 0 | 268488.9262 | 0 | 3189115.5977 | 8297424.6077 | 5663162.7898 | 25326922.4766 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 32292620.782 | 43059001.6384 | 316227.766 | 2.7449 | 11764.7267 | 15687.0943 | 239.8399 | 319.8026
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.8493 | 13.4644 | 0.71476 | 4 | 11359.2589 | 15124.9958 | 231.5739 | 308.3435 | 93.3847 | 0 | 163.9586 | 2079816.1739 | 125811.7076 | 2785406.0757 | 3007920.2355 | 0 | 237646.9612 | 0 | 3212274.45 | 8357679.1909 | 5704287.7809 | 25510842.5758 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 32476540.8812 | 43242921.7376 | 421696.5034 | 2.859 | 11359.2589 | 15124.9958 | 231.5739 | 308.3435
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.3138 | 14.5156 | 0.77083 | 4 | 11071.8384 | 14563.6312 | 225.7144 | 296.8993 | 93.3144 | 0 | 158.3375 | 2191933.5333 | 132484.7048 | 2958219.9864 | 3243372.0117 | 0 | 247095.0491 | 0 | 3421511.0613 | 8902069.933 | 6075845.6485 | 27172531.928 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 34138230.2334 | 44904611.0898 | 562341.3252 | 3.0833 | 11071.8384 | 14563.6312 | 225.7144 | 296.8993
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.3681 | 14.9437 | 0.80134 | 4 | 10847.1049 | 14205.9808 | 221.1329 | 289.6081 | 93.2814 | 0 | 175.0969 | 2236785.8535 | 135147.661 | 3027882.6746 | 3339517.3468 | 0 | 237359.7579 | 0 | 3500910.3846 | 9108650.6852 | 6216841.2567 | 27803095.6202 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 34768793.9256 | 45535174.782 | 749894.2093 | 3.2054 | 10847.1049 | 14205.9808 | 221.1329 | 289.6081
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.7387 | 15.275 | 0.82536 | 4 | 10677.8906 | 13939.0021 | 217.6832 | 284.1654 | 93.2541 | 0 | 186.5229 | 2271200.8233 | 137188.2743 | 3081542.5755 | 3414057.3859 | 0 | 228867.0539 | 0 | 3561813.884 | 9267109.0978 | 6324992.3793 | 28286771.4739 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35252469.7793 | 46018850.6357 | 1000000 | 3.3014 | 10677.8906 | 13939.0021 | 217.6832 | 284.1654
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5487 | 15.5275 | 0.84398 | 4 | 10550.595 | 13739.771 | 215.0882 | 280.1038 | 93.2323 | 0 | 165.5043 | 2297246.8883 | 138731.0799 | 3122275.0919 | 3470919.0278 | 0 | 221666.6706 | 0 | 3607827.1158 | 9386826.0883 | 6406701.6853 | 28652193.648 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35617891.9534 | 46384272.8098 | 1333521.4322 | 3.3759 | 10550.595 | 13739.771 | 215.0882 | 280.1038
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.9512 | 15.7229 | 0.85844 | 4 | 10454.9005 | 13590.364 | 213.1373 | 277.058 | 93.2148 | 0 | 185.2785 | 2317295.2749 | 139917.6754 | 3153699.8879 | 3514951.9258 | 0 | 215882.0924 | 0 | 3643281.274 | 9479070.5351 | 6469660.4156 | 28933759.081 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 35899457.3864 | 46665838.2428 | 1778279.41 | 3.4337 | 10454.9005 | 13590.364 | 213.1373 | 277.058
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.9964 | 15.8682 | 0.86939 | 4 | 10383.0012 | 13478.9674 | 211.6715 | 274.787 | 93.2015 | 0 | 208.0817 | 2332158.8938 | 140796.8618 | 3177038.4988 | 3547747.1814 | 0 | 211148.9144 | 0 | 3669467.2366 | 9547201.0383 | 6516160.884 | 29141719.509 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36107417.8144 | 46873798.6708 | 2371373.7057 | 3.4776 | 10383.0012 | 13478.9674 | 211.6715 | 274.787
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.7929 | 15.9789 | 0.87775 | 4 | 10329.0036 | 13395.4627 | 210.5707 | 273.0846 | 93.1912 | 0 | 194.8125 | 2343442.0554 | 141463.953 | 3194778.3501 | 3572728.007 | 0 | 207445.1656 | 0 | 3689344.4371 | 9598917.4367 | 6551458.3886 | 29299577.7935 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36265276.0989 | 47031656.9552 | 3162277.6602 | 3.511 | 10329.0036 | 13395.4627 | 210.5707 | 273.0846
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.3996 | 16.0632 | 0.88413 | 4 | 10288.4641 | 13332.8169 | 209.7443 | 271.8075 | 93.1833 | 0 | 187.4321 | 2352013.0847 | 141970.515 | 3208267.5168 | 3591753.7062 | 0 | 204586.9933 | 0 | 3704450.8082 | 9638221.1157 | 6578283.9571 | 29419547.6971 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36385246.0025 | 47151626.8589 | 4216965.0343 | 3.5365 | 10288.4641 | 13332.8169 | 209.7443 | 271.8075
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.8406 | 16.1244 | 0.88886 | 4 | 10258.0368 | 13286.1907 | 209.124 | 270.857 | 93.1774 | 0 | 190.1266 | 2358228.9042 | 142337.7813 | 3218057.3485 | 3605578.2898 | 0 | 202303.5627 | 0 | 3715337.2957 | 9666545.523 | 6597615.9471 | 29506004.6524 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36471702.9578 | 47238083.8142 | 5623413.2519 | 3.5554 | 10258.0368 | 13286.1907 | 209.124 | 270.857
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.189 | 16.1727 | 0.89252 | 4 | 10235.2039 | 13250.9406 | 208.6585 | 270.1383 | 93.1728 | 0 | 196.5076 | 2363131.4138 | 142627.3918 | 3225783.037 | 3616497.8175 | 0 | 200633.2276 | 0 | 3723982.4262 | 9689038.3792 | 6612967.7836 | 29574661.4767 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36540359.7821 | 47306740.6385 | 7498942.0933 | 3.5701 | 10235.2039 | 13250.9406 | 208.6585 | 270.1383
1 | 2000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.4519 | 16.2092 | 0.89528 | 4 | 10218.0728 | 13224.5053 | 208.3092 | 269.5994 | 93.1692 | 0 | 189.3541 | 2366825.3646 | 142845.5738 | 3231606.728 | 3624734.7831 | 0 | 199363.9003 | 0 | 3730496.7764 | 9705987.3821 | 6624535.8264 | 29626396.3347 | 961560.8286 | 6004137.4768 | 6004137.4768 | 1478867.319 | 3283376.0606 | 0 | 36592094.6401 | 47358475.4964 | 10000000 | 3.5811 | 10218.0728 | 13224.5053 | 208.3092 | 269.5994
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.9731 | [19 empty] | 100 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.0586 | [19 empty] | 133.3521 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3384 | [19 empty] | 177.8279 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.417 | [19 empty] | 237.1374 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9385 | [19 empty] | 316.2278 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5892 | [19 empty] | 421.6965 | 0
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.73307 | 0.073072 | 0.00040944 | 4 | 4774685.2128 | 11624887.9565 | 97338.4163 | 236989.0648 | 76.5246 | 0 | 67.6247 | 47203.3053 | 2546.039 | 43480.1065 | 44026.6272 | 0 | 34121.0548 | 0 | 66837.0818 | 173896.3766 | 118687.8502 | 530798.4414 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 7819823.0743 | 19038860.7893 | 562.3413 | 0.0016378 | 4774685.2128 | 11624887.9565 | 97338.4163 | 236989.0648
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.12733 | 0.0016194 | 4 | 1242611.1914 | 2974567.6947 | 25332.3099 | 60640.5859 | 82.7375 | 0 | 175.3238 | 73567.9473 | 4139.1127 | 67466.8292 | 55978.1586 | 0 | 44290.2493 | 0 | 95722.4959 | 249050.2989 | 169981.9465 | 760197.0384 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8049221.6713 | 19268259.3863 | 749.8942 | 0.0064777 | 1242611.1914 | 2974567.6947 | 25332.3099 | 60640.5859
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5542 | 0.19445 | 0.0035098 | 4 | 591278.9904 | 1390409.1119 | 12054.022 | 28345.3704 | 86.6337 | 0 | 262.6582 | 102048.7295 | 5895.3538 | 94373.7299 | 70485.9081 | 0 | 53930.2806 | 0 | 127426.2607 | 331536.9917 | 226280.8093 | 1011978.0636 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8301002.6966 | 19520040.4115 | 1000 | 0.014039 | 591278.9904 | 1390409.1119 | 12054.022 | 28345.3704
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 0.2805 | 0.0062405 | 4 | 344336.798 | 793778.6844 | 7019.7714 | 16182.2521 | 89.37 | 0 | 373.137 | 134581.1822 | 7921.8976 | 126247.0727 | 88969.0123 | 0 | 64062.1347 | 0 | 164494.7068 | 427981.4845 | 292106.1573 | 1306363.648 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8595388.281 | 19814425.9959 | 1333.5214 | 0.024962 | 344336.798 | 793778.6844 | 7019.7714 | 16182.2521
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.813 | 0.38737 | 0.01001 | 4 | 223080.325 | 503277.1826 | 4547.7942 | 10259.9861 | 91.3142 | 0 | 84.5675 | 171002.5644 | 10201.3622 | 163203.7415 | 111764.3286 | 0 | 74322.561 | 0 | 206892.8775 | 538292.8278 | 367395.9158 | 1643076.1789 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 8932100.8119 | 20151138.5268 | 1778.2794 | 0.04004 | 223080.325 | 503277.1826 | 4547.7942 | 10259.9861
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7292 | 0.52912 | 0.015157 | 4 | 154220.0317 | 339261.503 | 3143.9839 | 6916.3046 | 92.8155 | 0 | 77.1508 | 214886.7004 | 12954.6718 | 209204.656 | 142035.5732 | 0 | 86447.9015 | 0 | 259556.5062 | 675312.7866 | 460914.8532 | 2061313.6489 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9350338.2819 | 20569375.9968 | 2371.3737 | 0.06063 | 154220.0317 | 339261.503 | 3143.9839 | 6916.3046
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9614 | 0.72007 | 0.022168 | 4 | 111411.3935 | 237934.099 | 2271.272 | 4850.6084 | 93.9852 | 0 | 56.1611 | 268640.4523 | 16328.1263 | 267449.8793 | 182605.1138 | 0 | 101220.7957 | 0 | 326135.3033 | 848537.1596 | 579144.0471 | 2590060.8775 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 9879085.5104 | 21098123.2254 | 3162.2777 | 0.088672 | 111411.3935 | 237934.099 | 2271.272 | 4850.6084
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3233 | 0.93132 | 0.031119 | 4 | 83740.4821 | 173870.6959 | 1707.163 | 3544.5893 | 94.7466 | 0 | 66.6614 | 323216.9842 | 19751.2583 | 328372.4224 | 227565.3441 | 0 | 113166.6229 | 0 | 394708.3264 | 1026950.0995 | 700914.5446 | 3134645.6024 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 10423670.2354 | 21642707.9503 | 4216.965 | 0.12448 | 83740.4821 | 173870.6959 | 1707.163 | 3544.5893
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0166 | 1.1926 | 0.042578 | 4 | 64956.5854 | 130830.4951 | 1324.2279 | 2667.1566 | 95.275 | 0 | 60.3124 | 385560.6306 | 23649.7641 | 400057.1413 | 283231.0083 | 0 | 125930.2185 | 0 | 475187.2175 | 1236339.6657 | 843827.2261 | 3773782.8721 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 11062807.5051 | 22281845.22 | 5623.4133 | 0.17031 | 64956.5854 | 130830.4951 | 1324.2279 | 2667.1566
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5692 | 1.5915 | 0.058831 | 4 | 51002.5984 | 98677.2382 | 1039.757 | 2011.669 | 95.9182 | 0 | 48.1885 | 473844.8989 | 29187.1918 | 503679.8297 | 367492.7924 | 0 | 147519.2874 | 0 | 593472.3601 | 1544093.343 | 1053875.4346 | 4713165.1379 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 12002189.7709 | 23221227.4858 | 7498.9421 | 0.23533 | 51002.5984 | 98677.2382 | 1039.757 | 2011.669
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.5124 | 2.0492 | 0.079175 | 4 | 41102.5533 | 76527.2866 | 837.9311 | 1560.1122 | 96.2979 | 0 | 45.8549 | 567000.8727 | 35009.6293 | 616384.1884 | 464476.2684 | 0 | 166568.3633 | 0 | 721281.3357 | 1876626.0803 | 1280835.8606 | 5728182.5988 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 13017207.2317 | 24236244.9467 | 10000 | 0.3167 | 41102.5533 | 76527.2866 | 837.9311 | 1560.1122
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.1735 | 2.6187 | 0.10539 | 4 | 33735.9001 | 60349.254 | 687.752 | 1230.3012 | 96.5904 | 0 | 55.1414 | 674611.556 | 41724.6499 | 749821.1445 | 585142.3555 | 0 | 186996.2428 | 0 | 872935.42 | 2271198.8992 | 1550139.9172 | 6932570.1851 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 14221594.818 | 25440632.533 | 13335.2143 | 0.42156 | 33735.9001 | 60349.254 | 687.752 | 1230.3012
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.705 | 3.3237 | 0.13889 | 4 | 28164.6714 | 48358.6392 | 574.1749 | 985.8563 | 96.8172 | 0 | 66.8846 | 798596.7193 | 49448.1037 | 907227.0306 | 734508.4979 | 0 | 208819.3203 | 0 | 1052453.872 | 2738269.0871 | 1868924.9177 | 8358247.5487 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 15647272.1816 | 26866309.8966 | 17782.7941 | 0.55556 | 28164.6714 | 48358.6392 | 574.1749 | 985.8563
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3024 | 4.1947 | 0.18165 | 4 | 23856.8633 | 39297.1401 | 486.3544 | 801.1254 | 96.9948 | 0 | 138.4063 | 941459.2566 | 58331.3881 | 1092747.4339 | 919017.4399 | 0 | 231826.6657 | 0 | 1264919.0518 | 3291059.9023 | 2246216.0078 | 10045577.1462 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 17334601.7791 | 28553639.494 | 23713.7371 | 0.72661 | 23856.8633 | 39297.1401 | 486.3544 | 801.1254
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.9332 | 5.2266 | 0.23415 | 4 | 20556.7294 | 32535.2816 | 419.0767 | 663.2757 | 97.1307 | 0 | 137.9067 | 1099801.9253 | 68158.5114 | 1302836.6891 | 1137517.6806 | 0 | 254552.8191 | 0 | 1506518.3739 | 3919651.7794 | 2675242.8802 | 11964280.6589 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 19253305.2918 | 30472343.0068 | 31622.7766 | 0.93659 | 20556.7294 | 32535.2816 | 419.0767 | 663.2757
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.6675 | 6.4303 | 0.29762 | 4 | 17982.1297 | 27405.9683 | 366.59 | 558.7077 | 97.2349 | 0 | 159.5315 | 1273288.2056 | 78905.1238 | 1537671.5719 | 1392377.2946 | 0 | 276189.9261 | 0 | 1777788.5276 | 4625441.0742 | 3156958.5765 | 14118620.3004 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 21407644.9333 | 32626682.6482 | 42169.6503 | 1.1905 | 17982.1297 | 27405.9683 | 366.59 | 558.7077
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.3445 | 7.7801 | 0.37168 | 4 | 15967.0523 | 23513.1762 | 325.51 | 479.3479 | 97.31 | 0 | 150.2881 | 1456821.5157 | 90251.0035 | 1790792.8091 | 1678257.5988 | 0 | 294920.3054 | 0 | 2071306.8607 | 5389115.568 | 3678182.1104 | 16449647.7716 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 23738672.4046 | 34957710.1195 | 56234.1325 | 1.4867 | 15967.0523 | 23513.1762 | 325.51 | 479.3479
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.5675 | 9.2128 | 0.4539 | 4 | 14392.6838 | 20571.912 | 293.4143 | 419.3863 | 97.3536 | 0 | 170.5434 | 1641538.7361 | 101643.1834 | 2050013.6565 | 1981945.3376 | 0 | 308443.608 | 0 | 2372597.9634 | 6173013.2139 | 4213208.3612 | 18842404.06 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 26131428.693 | 37350466.4079 | 74989.4209 | 1.8156 | 14392.6838 | 20571.912 | 293.4143 | 419.3863
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.8124 | 10.6447 | 0.54009 | 4 | 13169.5343 | 18362.6649 | 268.4788 | 374.3478 | 97.3639 | 0 | 143.7019 | 1817649.496 | 112474.3028 | 2301152.1951 | 2285983.1155 | 0 | 315221.8215 | 0 | 2664667.5631 | 6932918.4007 | 4731859.2657 | 21161926.1605 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 28450950.7934 | 39669988.5084 | 100000 | 2.1604 | 13169.5343 | 18362.6649 | 268.4788 | 374.3478
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.8307 | 12.0352 | 0.62736 | 4 | 12211.8828 | 16682.6113 | 248.9557 | 340.0976 | 97.3437 | 0 | 150.0767 | 1981787.677 | 122536.9523 | 2538690.7291 | 2582030.3241 | 0 | 315827.76 | 0 | 2940940.6426 | 7651724.2821 | 5222459.0497 | 23355997.4168 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 30645022.0497 | 41864059.7647 | 133352.1432 | 2.5094 | 12211.8828 | 16682.6113 | 248.9557 | 340.0976
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6723 | 13.2379 | 0.70683 | 4 | 11493.2123 | 15461.2699 | 234.3047 | 315.1989 | 97.3032 | 0 | 164.2549 | 2118943.2498 | 130917.5297 | 2739773.4289 | 2838887.8515 | 0 | 309708.7183 | 0 | 3173910.0034 | 8257862.7705 | 5636161.023 | 25206164.5749 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 32495189.2079 | 43714226.9228 | 177827.941 | 2.8273 | 11493.2123 | 15461.2699 | 234.3047 | 315.1989
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.4392 | 14.27 | 0.77774 | 4 | 10945.495 | 14551.7767 | 223.1387 | 296.6577 | 97.2521 | 0 | 145.4287 | 2233443.8684 | 137891.8464 | 2909481.9724 | 3060042.8844 | 0 | 299727.2468 | 0 | 3369829.2491 | 8767604.4591 | 5984070.1996 | 26762091.7261 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 34051116.359 | 45270154.074 | 237137.3706 | 3.111 | 10945.495 | 14551.7767 | 223.1387 | 296.6577
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.0734 | 15.1249 | 0.83852 | 4 | 10529.7492 | 13874.6561 | 214.6632 | 282.8536 | 97.1989 | 0 | 158.8687 | 2326206.4963 | 143525.9743 | 3048224.8285 | 3243789.4269 | 0 | 287705.2037 | 0 | 3529286.2526 | 9182478.873 | 6267230.5119 | 28028447.5671 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 35317472.2 | 46536509.915 | 316227.766 | 3.3541 | 10529.7492 | 13874.6561 | 214.6632 | 282.8536
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.636 | 15.814 | 0.88895 | 4 | 10215.1083 | 13370.238 | 208.2488 | 272.5704 | 97.149 | 0 | 164.8022 | 2399684.7823 | 147977.8233 | 3158937.6614 | 3392304.1843 | 0 | 275189.4627 | 0 | 3655896.6264 | 9511893.0945 | 6492062.4869 | 29033946.1218 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 36322970.7547 | 47542008.4696 | 421696.5034 | 3.5558 | 10215.1083 | 13370.238 | 208.2488 | 272.5704
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.5 | 16.6951 | 0.94344 | 4 | 9976.8479 | 12949.761 | 203.3915 | 263.9984 | 97.0765 | 0 | 122.5811 | 2492054.6299 | 153559.661 | 3299153.4114 | 3582792.9699 | 0 | 275036.0139 | 0 | 3823012.7076 | 9946694.8574 | 6788823.6243 | 30361127.8755 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 37650152.5084 | 48869190.2234 | 562341.3252 | 3.7738 | 9976.8479 | 12949.761 | 203.3915 | 263.9984
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.0823 | 16.7822 | 0.96219 | 4 | 9798.3355 | 12713.2972 | 199.7523 | 259.1778 | 97.0686 | 0 | 137.9945 | 2501094.5558 | 154104.8835 | 3312944.2367 | 3601679.0588 | 0 | 252616.0712 | 0 | 3830751.1343 | 9966828.6564 | 6802565.3558 | 30422583.9524 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 37711608.5854 | 48930646.3003 | 749894.2093 | 3.8488 | 9798.3355 | 12713.2972 | 199.7523 | 259.1778
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.2741 | 17.11 | 0.98762 | 4 | 9663.4101 | 12503.3403 | 197.0017 | 254.8975 | 97.0388 | 0 | 138.8706 | 2534950.7661 | 156145.7954 | 3364678.4899 | 3672739.5795 | 0 | 243517.9185 | 0 | 3889092.6943 | 10118621.428 | 6906167.0415 | 30885913.7133 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38174938.3463 | 49393976.0612 | 1000000 | 3.9505 | 9663.4101 | 12503.3403 | 197.0017 | 254.8975
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.9527 | 17.3605 | 1.0073 | 4 | 9561.8907 | 12346.3448 | 194.9321 | 251.6969 | 97.0151 | 0 | 152.355 | 2560670.7997 | 157694.6298 | 3404088.5145 | 3727117.4633 | 0 | 235961.575 | 0 | 3933357.8631 | 10233790.3172 | 6984772.1749 | 31237453.3376 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38526477.9705 | 49745515.6854 | 1333521.4322 | 4.0292 | 9561.8907 | 12346.3448 | 194.9321 | 251.6969
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.2218 | 17.5496 | 1.0223 | 4 | 9485.5625 | 12229.027 | 193.376 | 249.3053 | 96.9967 | 0 | 156.4412 | 2579995.6365 | 158857.388 | 3433762.5366 | 3768195.1881 | 0 | 229792.279 | 0 | 3966535.181 | 10320110.8927 | 7043687.7414 | 31500936.8433 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 38789961.4762 | 50008999.1912 | 1778279.41 | 4.0894 | 9485.5625 | 12229.027 | 193.376 | 249.3053
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5 | 18.1821 | 1.0545 | 4 | 9427.9268 | 12087.668 | 192.201 | 246.4235 | 96.9234 | 0 | 163.897 | 2643919.5554 | 162689.5792 | 3532610.6014 | 3906102.7612 | 0 | 241017.8267 | 0 | 4089672.7263 | 10640489.5267 | 7262352.7421 | 32478855.319 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39767879.9519 | 50986917.6669 | 2371373.7057 | 4.2181 | 9427.9268 | 12087.668 | 192.201 | 246.4235
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5 | 18.1821 | 1.0589 | 4 | 9383.3929 | 12032.1639 | 191.2932 | 245.2919 | 96.9234 | 0 | 136.8098 | 2643916.7366 | 162689.3621 | 3532608.0347 | 3906101.1291 | 0 | 233300.7483 | 0 | 4086660.2442 | 10632651.6661 | 7257003.2413 | 32454931.1624 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39743955.7954 | 50962993.5103 | 3162277.6602 | 4.2356 | 9383.3929 | 12032.1639 | 191.2932 | 245.2919
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.5 | 18.182 | 1.0622 | 4 | 9350.1756 | 11990.7796 | 190.616 | 244.4483 | 96.9233 | 0 | 110.5584 | 2643914.6223 | 162689.1993 | 3532606.1096 | 3906099.9048 | 0 | 227427.8763 | 0 | 4084367.7078 | 10626686.9568 | 7252932.2046 | 32436724.5817 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39725749.2146 | 50944786.9296 | 4216965.0343 | 4.2487 | 9350.1756 | 11990.7796 | 190.616 | 244.4483
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118 | 18.108 | 1.0615 | 4 | 9324.9299 | 11967.179 | 190.1013 | 243.9671 | 96.9312 | 0 | 138.65 | 2636451.7804 | 162241.4222 | 3521067.2124 | 3889968.2112 | 0 | 220413.7802 | 0 | 4067755.5385 | 10583465.4999 | 7223432.6721 | 32304796.1171 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39593820.75 | 50812858.4649 | 5623413.2519 | 4.246 | 9324.9299 | 11967.179 | 190.1013 | 243.9671
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.642 | 18.0549 | 1.0611 | 4 | 9306.3032 | 11949.6193 | 189.7216 | 243.6092 | 96.9368 | 0 | 115.1394 | 2631098.1044 | 161920.1183 | 3512794.5235 | 3878413.8443 | 0 | 215230.9052 | 0 | 4055788.4233 | 10552329.521 | 7202181.7267 | 32209757.1668 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39498781.7997 | 50717819.5147 | 7498942.0933 | 4.2443 | 9306.3032 | 11949.6193 | 189.7216 | 243.6092
1 | 2100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.642 | 18.0549 | 1.0624 | 4 | 9292.5325 | 11932.4624 | 189.4408 | 243.2594 | 96.9367 | 0 | 115.1272 | 2631097.2326 | 161920.0511 | 3512793.7302 | 3878413.3406 | 0 | 212696.3673 | 0 | 4054799.0815 | 10549755.4564 | 7200424.8748 | 32201900.1344 | 961560.8286 | 6327463.8043 | 6327463.8043 | 1478867.319 | 3412706.5916 | 0 | 39490924.7673 | 50709962.4823 | 10000000 | 4.2497 | 9292.5325 | 11932.4624 | 189.4408 | 243.2594
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.0096 | [19 empty] | 100 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.105 | [19 empty] | 133.3521 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0337 | [19 empty] | 177.8279 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7877 | [19 empty] | 237.1374 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1807 | [19 empty] | 316.2278 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.194 | [19 empty] | 421.6965 | 0
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.10502 | 0.0010286 | 4 | 2015627.5737 | 4854394.7649 | 41091.2944 | 98963.4033 | 82.4707 | 0 | 58.7656 | 64287.7258 | 3602.8107 | 57843.8456 | 50489.0525 | 0 | 41692.2919 | 0 | 84987.1334 | 221119.0877 | 150918.3209 | 674940.2685 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8293151.3199 | 19973050.0206 | 562.3413 | 0.0041144 | 2015627.5737 | 4854394.7649 | 41091.2944 | 98963.4033
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3208 | 0.16869 | 0.0027777 | 4 | 768939.0491 | 1820164.1888 | 15675.8626 | 37106.5089 | 87.6222 | 0 | 218.1156 | 93329.7695 | 5412.7702 | 84166.2543 | 63854.7279 | 0 | 51977.8349 | 0 | 116509.1291 | 303132.8546 | 206894.402 | 925277.7424 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8543488.7938 | 20223387.4945 | 749.8942 | 0.011111 | 768939.0491 | 1820164.1888 | 15675.8626 | 37106.5089
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.25392 | 0.0054131 | 4 | 408579.0886 | 948011.1096 | 8329.4374 | 19326.4887 | 91.259 | 0 | 317.714 | 127627.4277 | 7584.5046 | 116412.7764 | 81590.8158 | 0 | 63404.1381 | 0 | 154681.6684 | 402449.9716 | 274680.3752 | 1228431.6778 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 8846642.7291 | 20526541.4298 | 1000 | 0.021652 | 408579.0886 | 948011.1096 | 8329.4374 | 19326.4887
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4877 | 0.35944 | 0.0091314 | 4 | 251582.0399 | 571353.7128 | 5128.8402 | 11647.8182 | 93.753 | 0 | 441.9984 | 165607.2283 | 10008.5244 | 153434.0592 | 103411.6543 | 0 | 74765.4783 | 0 | 197818.5083 | 514683.1805 | 351281.8464 | 1571010.4795 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9189221.5309 | 20869120.2316 | 1333.5214 | 0.036526 | 251582.0399 | 571353.7128 | 5128.8402 | 11647.8182
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2734 | 0.48942 | 0.014194 | 4 | 168720.525 | 374441.5623 | 3439.5961 | 7633.4977 | 95.5394 | 0 | 58.0982 | 207976.0703 | 12721.9401 | 196143.8069 | 130119.1087 | 0 | 86170.2939 | 0 | 246921.1758 | 642438.249 | 438477.3057 | 1960967.9507 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 9579179.002 | 21259077.7028 | 1778.2794 | 0.056775 | 168720.525 | 374441.5623 | 3439.5961 | 7633.4977
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3406 | 0.66655 | 0.021067 | 4 | 119603.6856 | 258209.2714 | 2438.2829 | 5263.9453 | 96.9675 | 0 | 79.801 | 260507.6486 | 16089.4595 | 250861.8731 | 166326.4145 | 0 | 100612.4351 | 0 | 309815.154 | 806075.479 | 550163.0776 | 2460451.5416 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10078662.5929 | 21758561.2936 | 2371.3737 | 0.084267 | 119603.6856 | 258209.2714 | 2438.2829 | 5263.9453
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6434 | 0.88315 | 0.030143 | 4 | 88321.1657 | 185191.1608 | 1800.5464 | 3775.3723 | 97.9932 | 0 | 117.3397 | 319201.9649 | 19850.1491 | 313955.7017 | 210464.4399 | 0 | 115114.1541 | 0 | 381648.6998 | 992971.6299 | 677723.5409 | 3030930.2802 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 10649141.3316 | 22329040.0323 | 3162.2777 | 0.12057 | 88321.1657 | 185191.1608 | 1800.5464 | 3775.3723
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2512 | 1.1502 | 0.041976 | 4 | 67376.6423 | 136939.5307 | 1373.564 | 2791.6976 | 98.7234 | 0 | 104.2343 | 385783.3676 | 24110.8646 | 387630.1803 | 265181.3121 | 0 | 130160.0524 | 0 | 465217.653 | 1210400.9039 | 826123.4881 | 3694607.822 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 11312818.8733 | 22992717.5741 | 4216.965 | 0.1679 | 67376.6423 | 136939.5307 | 1373.564 | 2791.6976
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.5144 | 1.5287 | 0.058219 | 4 | 52434.5472 | 102589.2052 | 1068.9492 | 2091.4197 | 99.4261 | 0 | 124.9987 | 472885.7006 | 29689.8637 | 486435.1259 | 342336.3597 | 0 | 151457.8797 | 0 | 578293.9225 | 1504602.162 | 1026921.8921 | 4592622.9062 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 12210833.9576 | 23890732.6583 | 5623.4133 | 0.23288 | 52434.5472 | 102589.2052 | 1068.9492 | 2091.4197
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1675 | 1.9713 | 0.078857 | 4 | 41845.8399 | 78874.5705 | 853.084 | 1607.9648 | 99.8877 | 0 | 123.9635 | 566711.563 | 35683.0963 | 595984.8285 | 432609.9431 | 0 | 170974.3656 | 0 | 702765.8806 | 1828452.6643 | 1247956.5143 | 5581138.8556 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 13199349.907 | 24879248.6077 | 7498.9421 | 0.31543 | 41845.8399 | 78874.5705 | 853.084 | 1607.9648
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.5191 | 2.5306 | 0.10563 | 4 | 34055.9228 | 61698.6325 | 694.2761 | 1257.8101 | 100.247 | 0 | 133.6191 | 676649.2141 | 42693.4647 | 727601.5247 | 546621.1833 | 0 | 192716.1287 | 0 | 852649.791 | 2218419.8538 | 1514117.1342 | 6771468.2944 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 14389679.3458 | 26069578.0465 | 10000 | 0.42253 | 34055.9228 | 61698.6325 | 694.2761 | 1257.8101
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6607 | 3.2219 | 0.13994 | 4 | 28213.8689 | 49079.6522 | 575.1779 | 1000.5551 | 100.5236 | 0 | 110.4971 | 802955.9916 | 50733.0152 | 882487.6864 | 687501.2224 | 0 | 215717.1738 | 0 | 1029364.0849 | 2678194.1972 | 1827922.571 | 8174875.9424 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 15793086.9938 | 27472985.6945 | 13335.2143 | 0.55976 | 28213.8689 | 49079.6522 | 575.1779 | 1000.5551
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7567 | 4.0725 | 0.18353 | 4 | 23764.359 | 39674.7713 | 484.4686 | 808.8239 | 100.7383 | 0 | 136.4886 | 947826.8884 | 59936.7033 | 1064254.445 | 860856.4132 | 0 | 240033.9928 | 0 | 1237434.2927 | 3219550.1969 | 2197409.1645 | 9827302.0968 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 17445513.1481 | 29125411.8488 | 17782.7941 | 0.7341 | 23764.359 | 39674.7713 | 484.4686 | 808.8239
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9176 | 5.1011 | 0.23805 | 4 | 20332.8216 | 32599.0153 | 414.5121 | 664.575 | 100.9048 | 0 | 110.3281 | 1111537.8588 | 70317.069 | 1274186.978 | 1070452.2959 | 0 | 264848.4602 | 0 | 1478623.6382 | 3847075.3991 | 2625708.0094 | 11742749.7085 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 19360960.7599 | 31040859.4606 | 23713.7371 | 0.9522 | 20332.8216 | 32599.0153 | 414.5121 | 664.575
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.2381 | 6.3234 | 0.30503 | 4 | 17661.041 | 27233.7922 | 360.0442 | 555.1977 | 101.034 | 0 | 134.9538 | 1293922.5602 | 81858.439 | 1512941.8083 | 1319495.3558 | 0 | 289433.0636 | 0 | 1754083.9785 | 4563766.6999 | 3114864.5487 | 13930366.4539 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 21548577.5053 | 33228476.206 | 31622.7766 | 1.2201 | 17661.041 | 27233.7922 | 360.0442 | 555.1977
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.6586 | 7.7292 | 0.38493 | 4 | 15568.7557 | 23154.437 | 317.3901 | 472.0345 | 101.1308 | 0 | 154.4639 | 1491299.1297 | 94322.2682 | 1776390.1735 | 1605913.0228 | 0 | 312064.1528 | 0 | 2059195.6113 | 5357604.5816 | 3656675.2147 | 16353464.1545 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 23971675.2059 | 35651573.9066 | 42169.6503 | 1.5397 | 15568.7557 | 23154.437 | 317.3901 | 472.0345
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.9035 | 9.2711 | 0.4763 | 4 | 13928.7535 | 20059.3032 | 283.9565 | 408.936 | 101.1942 | 0 | 128.5927 | 1695939.3663 | 107214.3309 | 2054541.8954 | 1920236.7912 | 0 | 330315.9398 | 0 | 2382216.8462 | 6198039.5739 | 4230289.3662 | 18918794.1098 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 26537005.1612 | 38216903.8619 | 56234.1325 | 1.9052 | 13928.7535 | 20059.3032 | 283.9565 | 408.936
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4749 | 10.8635 | 0.57519 | 4 | 12648.3135 | 17724.8721 | 257.853 | 361.3455 | 101.2203 | 0 | 159.0689 | 1896822.4974 | 119833.8263 | 2332257.0326 | 2245318.372 | 0 | 341723.5243 | 0 | 2705022.5485 | 7037913.7949 | 4803520.7797 | 21482412.3758 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 29100623.4272 | 40780522.1279 | 74989.4209 | 2.3008 | 12648.3135 | 17724.8721 | 257.853 | 361.3455
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.8339 | 12.414 | 0.67618 | 4 | 11655.2372 | 15973.5964 | 237.6078 | 325.6434 | 101.2099 | 0 | 186.9272 | 2083913.0367 | 131547.7086 | 2594980.0886 | 2562623.2959 | 0 | 345321.2645 | 0 | 3010170.3038 | 7831845.6597 | 5345395.5911 | 23905796.9489 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 31524008.0002 | 43203906.701 | 100000 | 2.7047 | 11655.2372 | 15973.5964 | 237.6078 | 325.6434
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.5453 | 13.8494 | 0.77468 | 4 | 10877.5713 | 14646.852 | 221.754 | 298.5959 | 101.1701 | 0 | 171.4772 | 2250642.6669 | 141948.7171 | 2832439.0405 | 2857291.9531 | 0 | 340688.8812 | 0 | 3284974.3909 | 8546829.5243 | 5833386.7701 | 26088201.9443 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 33706412.9956 | 45386311.6963 | 133352.1432 | 3.0987 | 10877.5713 | 14646.852 | 221.754 | 298.5959
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.4038 | 15.1362 | 0.86505 | 4 | 10296.0346 | 13671.5489 | 209.8986 | 278.713 | 101.111 | 0 | 185.2535 | 2395419.027 | 150946.5994 | 3041223.3465 | 3122418.371 | 0 | 332829.2319 | 0 | 3526706.2646 | 9175766.2735 | 6262649.0248 | 28007958.1387 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 35626169.1901 | 47306067.8908 | 177827.941 | 3.4602 | 10296.0346 | 13671.5489 | 209.8986 | 278.713
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.8908 | 16.1919 | 0.94299 | 4 | 9853.1666 | 12949.6662 | 200.8701 | 263.9965 | 101.0467 | 0 | 156.7908 | 2511163.5769 | 158115.0066 | 3209914.9968 | 3340709.5895 | 0 | 320039.5124 | 0 | 3720577.646 | 9680179.8395 | 6606921.6483 | 29547621.816 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 37165832.8673 | 48845731.568 | 237137.3706 | 3.772 | 9853.1666 | 12949.6662 | 200.8701 | 263.9965
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.2233 | 17.0549 | 1.0088 | 4 | 9517.1132 | 12411.6397 | 194.0192 | 253.0281 | 100.9839 | 0 | 176.3762 | 2603882.3007 | 163839.6829 | 3346217.3193 | 3519716.555 | 0 | 305773.3755 | 0 | 3876377.401 | 10085538.8432 | 6883587.4976 | 30784932.9752 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 38403144.0265 | 50083042.7272 | 316227.766 | 4.0352 | 9517.1132 | 12411.6397 | 194.0192 | 253.0281
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.5157 | 17.7462 | 1.0629 | 4 | 9262.8067 | 12010.0933 | 188.8348 | 244.842 | 100.9271 | 0 | 170.3298 | 2676979.2808 | 168340.7843 | 3454433.3055 | 3663468.8186 | 0 | 291659.8703 | 0 | 3999404.0032 | 10405628.8258 | 7102055.4879 | 31761970.3765 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 39380181.4278 | 51060080.1285 | 421696.5034 | 4.2514 | 9262.8067 | 12010.0933 | 188.8348 | 244.842
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.9592 | 17.6566 | 1.0793 | 4 | 9064.9874 | 11770.4562 | 184.802 | 239.9567 | 100.9346 | 0 | 200.4521 | 2667565.1825 | 167761.4617 | 3440466.4271 | 3644840.9048 | 0 | 255040.5275 | 0 | 3968513.0564 | 10325256.9187 | 7047200.0098 | 31516644.4884 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 39134855.5398 | 50814754.2405 | 562341.3252 | 4.3171 | 9064.9874 | 11770.4562 | 184.802 | 239.9567
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.523 | 18.7083 | 1.1404 | 4 | 8925.898 | 11486.332 | 181.9665 | 234.1644 | 100.8389 | 0 | 174.327 | 2777059.9705 | 174485.4633 | 3603698.3511 | 3864171.3546 | 0 | 267130.5838 | 0 | 4167752.8321 | 10843637.9455 | 7401005.7123 | 33098942.2134 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 40717153.2648 | 52397051.9655 | 749894.2093 | 4.5617 | 8925.898 | 11486.332 | 181.9665 | 234.1644
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.5519 | 19.0318 | 1.1671 | 4 | 8816.8002 | 11318.7017 | 179.7424 | 230.747 | 100.8068 | 0 | 178.792 | 2810290.3742 | 176520.8961 | 3653547.2889 | 3931824.55 | 0 | 257480.4524 | 0 | 4223568.789 | 10988859.6159 | 7500122.4864 | 33542214.4529 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41160425.5043 | 52840324.205 | 1000000 | 4.6684 | 8816.8002 | 11318.7017 | 179.7424 | 230.747
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0935 | 19.2771 | 1.1876 | 4 | 8734.7014 | 11193.3853 | 178.0687 | 228.1923 | 100.7817 | 0 | 190.8148 | 2835351.6951 | 178054.3057 | 3691238.3258 | 3983185.9974 | 0 | 249506.7709 | 0 | 4265561.4671 | 11098115.9503 | 7574692.1796 | 33875706.692 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41493917.7434 | 53173816.4441 | 1333521.4322 | 4.7505 | 8734.7014 | 11193.3853 | 178.0687 | 228.1923
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.2534 | 19.4613 | 1.2032 | 4 | 8672.9662 | 11099.7293 | 176.8101 | 226.283 | 100.7624 | 0 | 186.6052 | 2854099.231 | 179200.4537 | 3719488.5225 | 4021800.3394 | 0 | 243035.2078 | 0 | 4296873.2642 | 11179582.8235 | 7630294.9945 | 34124374.8366 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41742585.888 | 53422484.5887 | 1778279.41 | 4.813 | 8672.9662 | 11099.7293 | 176.8101 | 226.283
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.1398 | 19.6019 | 1.2152 | 4 | 8626.5715 | 11029.4596 | 175.8643 | 224.8505 | 100.7474 | 0 | 197.8537 | 2868366.5792 | 180072.1535 | 3741019.24 | 4051297.8875 | 0 | 237966.4747 | 0 | 4320701.7106 | 11241579.5532 | 7672609.0364 | 34313612.6351 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 41931823.6865 | 53611722.3872 | 2371373.7057 | 4.8608 | 8626.5715 | 11029.4596 | 175.8643 | 224.8505
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.8197 | 19.7097 | 1.2243 | 4 | 8591.7219 | 10976.664 | 175.1539 | 223.7741 | 100.7358 | 0 | 181.2697 | 2879274.156 | 180738.2575 | 3757498.2664 | 4073914.1827 | 0 | 234066.4825 | 0 | 4338941.6246 | 11289036.0678 | 7704999.0828 | 34458468.1203 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 42076679.1716 | 53756577.8724 | 3162277.6602 | 4.8974 | 8591.7219 | 10976.664 | 175.1539 | 223.7741
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3191 | 19.7888 | 1.2312 | 4 | 8565.5546 | 10937.2833 | 174.6204 | 222.9713 | 100.7272 | 0 | 195.4536 | 2887264.8662 | 181226.0542 | 3769580.8028 | 4090518.539 | 0 | 230980.2805 | 0 | 4352232.5117 | 11323616.2297 | 7728600.7538 | 34564020.0378 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 42182231.0892 | 53862129.7899 | 4216965.0343 | 4.9246 | 8565.5546 | 10937.2833 | 174.6204 | 222.9713
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.7017 | 19.8494 | 1.2364 | 4 | 8545.9123 | 10907.6722 | 174.22 | 222.3677 | 100.7205 | 0 | 189.8056 | 2893377.0099 | 181599.0708 | 3778828.6519 | 4103239.8415 | 0 | 228648.9157 | 0 | 4362420.461 | 11350123.1841 | 7746692.2949 | 34644929.4298 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 42263140.4812 | 53943039.1819 | 5623413.2519 | 4.9454 | 8545.9123 | 10907.6722 | 174.22 | 222.3677
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.977 | 19.893 | 1.2402 | 4 | 8531.1714 | 10885.6471 | 173.9195 | 221.9186 | 100.7157 | 0 | 203.262 | 2897767.1072 | 181866.9367 | 3785474.1748 | 4112388.1414 | 0 | 226803.1311 | 0 | 4369676.8015 | 11369002.6936 | 7759577.948 | 34702556.9343 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 42320767.9856 | 54000666.6863 | 7498942.0933 | 4.9607 | 8531.1714 | 10885.6471 | 173.9195 | 221.9186
1 | 2200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2035 | 19.9288 | 1.2432 | 4 | 8520.111 | 10868.8648 | 173.694 | 221.5765 | 100.7117 | 0 | 161.0927 | 2901376.9574 | 182087.1622 | 3790940.508 | 4119917.2956 | 0 | 225506.4037 | 0 | 4375733.0475 | 11384759.8033 | 7770332.4991 | 34750653.6767 | 961560.8286 | 6656650.2227 | 6656650.2227 | 1478867.319 | 3544381.159 | 0 | 42368864.7281 | 54048763.4288 | 10000000 | 4.9728 | 8520.111 | 10868.8648 | 173.694 | 221.5765
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 21.5975 | [19 empty] | 100 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.7895 | [19 empty] | 133.3521 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9723 | [19 empty] | 177.8279 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.5231 | [19 empty] | 237.1374 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.4449 | [19 empty] | 316.2278 | 0
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75252 | 0.083446 | 0.00042157 | 4 | 5064675.6923 | 12269236.7327 | 103250.2645 | 250124.9862 | 81.0864 | 0 | 67.1447 | 54176.58 | 3003.484 | 48175.1426 | 45459.6959 | 0 | 38786.482 | 0 | 73944.5399 | 192388.5247 | 131309.1213 | 587243.5702 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8540501.1309 | 20689464.9446 | 421.6965 | 0.0016863 | 5064675.6923 | 12269236.7327 | 103250.2645 | 250124.9862
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1263 | 0.14511 | 0.0019491 | 4 | 1128302.459 | 2686541.9047 | 23001.9718 | 54768.7905 | 88.0458 | 0 | 181.0484 | 84444.4063 | 4900.4398 | 74591.7049 | 58116.2151 | 0 | 50337.314 | 0 | 106232.1313 | 276394.2144 | 188644.7307 | 843661.1566 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 8796918.7172 | 20945882.5309 | 562.3413 | 0.0077966 | 1128302.459 | 2686541.9047 | 23001.9718 | 54768.7905
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5931 | 0.22522 | 0.0044039 | 4 | 516209.1738 | 1205879.872 | 10523.6222 | 24583.4923 | 92.6355 | 0 | 268.4626 | 118811.8159 | 7106.977 | 105652.1998 | 74370.5675 | 0 | 62151.403 | 0 | 143556.2557 | 373503.9299 | 254924.1069 | 1140077.2558 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9093334.8164 | 21242298.6301 | 749.8942 | 0.017616 | 516209.1738 | 1205879.872 | 10523.6222 | 24583.4923
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.32029 | 0.007936 | 4 | 296460.5567 | 679176.2317 | 6043.7494 | 13845.9261 | 95.6548 | 0 | 341.4323 | 155182.194 | 9469.2745 | 139711.4731 | 93387.9863 | 0 | 72864.5042 | 0 | 183540.0185 | 477533.4789 | 325926.4117 | 1457615.3411 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9410872.9018 | 21559836.7155 | 1000 | 0.031744 | 296460.5567 | 679176.2317 | 6043.7494 | 13845.9261
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8861 | 0.45216 | 0.012876 | 4 | 190665.2204 | 426552.2996 | 3886.9684 | 8695.8456 | 98.0525 | 0 | 75.0659 | 200580.1145 | 12433.0562 | 183760.8149 | 119450.4192 | 0 | 86448.601 | 0 | 235042.4723 | 611532.2991 | 417383.3599 | 1866631.1372 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 9819888.6979 | 21968852.5116 | 1333.5214 | 0.051503 | 190665.2204 | 426552.2996 | 3886.9684 | 8695.8456
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 0.61544 | 0.019586 | 4 | 131337.627 | 286412.3772 | 2677.4952 | 5838.9037 | 99.7652 | 0 | 94.9155 | 251565.8456 | 15771.9627 | 234862.2308 | 151773.9872 | 0 | 100267.5981 | 0 | 294154.2335 | 765328.9763 | 522352.7523 | 2336077.5866 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10289335.1472 | 22438298.9609 | 1778.2794 | 0.078343 | 131337.627 | 286412.3772 | 2677.4952 | 5838.9037
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9861 | 0.82499 | 0.028561 | 4 | 94999.3075 | 201340.2125 | 1936.6894 | 4104.5926 | 101.0632 | 0 | 81.1672 | 311259.0342 | 19681.8643 | 296624.8542 | 193032.7642 | 0 | 115708.5438 | 0 | 365159.7537 | 950070.7746 | 648442.8257 | 2899980.4148 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 10853237.9754 | 23002201.7891 | 2371.3737 | 0.11425 | 94999.3075 | 201340.2125 | 1936.6894 | 4104.5926
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4741 | 1.0896 | 0.0404 | 4 | 71301.523 | 146480.0219 | 1453.578 | 2986.1934 | 102.0245 | 0 | 94.8449 | 380311.4958 | 24199.0058 | 370298.7135 | 245047.8979 | 0 | 132512.4715 | 0 | 449424.138 | 1169309.4174 | 798077.7043 | 3569180.8441 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 11522438.4047 | 23671402.2184 | 3162.2777 | 0.1616 | 71301.523 | 146480.0219 | 1453.578 | 2986.1934
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1914 | 1.3933 | 0.055369 | 4 | 55283.2838 | 110137.8661 | 1127.0245 | 2245.3094 | 102.6265 | 0 | 103.0383 | 453377.3844 | 28963.7498 | 450607.1271 | 305120.2308 | 0 | 147240.4985 | 0 | 540270.5063 | 1405673.0327 | 959400.7285 | 4290653.2579 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 12243910.8185 | 24392874.6322 | 4216.965 | 0.22148 | 55283.2838 | 110137.8661 | 1127.0245 | 2245.3094
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.825 | 1.8664 | 0.076885 | 4 | 43335.3266 | 82839.0157 | 883.4492 | 1688.7854 | 103.3938 | 0 | 105.8069 | 559034.4379 | 35882.3055 | 568997.6871 | 397959.6622 | 0 | 173239.8745 | 0 | 676694.4472 | 1760620.1425 | 1201659.4244 | 5374087.9813 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 13327345.5419 | 25476309.3556 | 5623.4133 | 0.30754 | 43335.3266 | 82839.0157 | 883.4492 | 1688.7854
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.8607 | 2.4086 | 0.10372 | 4 | 34937.3158 | 64221.6973 | 712.2444 | 1309.2462 | 103.8388 | 0 | 95.4216 | 670260.1694 | 43132.7167 | 697555.319 | 504671.5595 | 0 | 196216.1222 | 0 | 823615.9958 | 2142879.8742 | 1462559.5459 | 6540891.3025 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 14494148.8632 | 26643112.6769 | 7498.9421 | 0.41486 | 34937.3158 | 64221.6973 | 712.2444 | 1309.2462
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5996 | 3.0764 | 0.13816 | 4 | 28701.3394 | 50685.3108 | 585.1156 | 1033.2886 | 104.1782 | 0 | 120.4537 | 797424.7561 | 51405.8597 | 848195.8902 | 635980.5127 | 0 | 220194.8292 | 0 | 995748.7207 | 2590733.915 | 1768229.1313 | 7907913.6148 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 15861171.1755 | 28010134.9892 | 10000 | 0.55263 | 28701.3394 | 50685.3108 | 585.1156 | 1033.2886
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2406 | 3.9054 | 0.1822 | 4 | 23987.4745 | 40657.2711 | 489.0171 | 828.8535 | 104.4425 | 0 | 114.7291 | 944356.7737 | 60945.667 | 1026376.8846 | 798861.8434 | 0 | 246002.7843 | 0 | 1199852.1417 | 3121769.1491 | 2130671.5902 | 9528836.8341 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 17482094.3947 | 29631058.2084 | 13335.2143 | 0.7288 | 23987.4745 | 40657.2711 | 489.0171 | 828.8535
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.9091 | 4.918 | 0.2378 | 4 | 20371.4113 | 33143.7023 | 415.2988 | 675.6792 | 104.6476 | 0 | 124.7725 | 1111854.3159 | 71798.4693 | 1234085.6296 | 997819.9186 | 0 | 272859.7474 | 0 | 1438483.0515 | 3742637.8267 | 2554427.2202 | 11423966.1793 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 19377223.7399 | 31526187.5536 | 17782.7941 | 0.9512 | 20371.4113 | 33143.7023 | 415.2988 | 675.6792
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.7102 | 6.1332 | 0.30683 | 4 | 17565.6124 | 27464.451 | 358.0988 | 559.9 | 104.8067 | 0 | 121.1816 | 1299966.2785 | 83961.639 | 1472355.3985 | 1236548.21 | 0 | 299843.975 | 0 | 1713143.4454 | 4457247.8308 | 3042163.2318 | 13605230.009 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 21558487.5697 | 33707451.3834 | 23713.7371 | 1.2273 | 17565.6124 | 27464.451 | 358.0988 | 559.9
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.7345 | 7.5669 | 0.3909 | 4 | 15370.6725 | 23140.4433 | 313.352 | 471.7492 | 104.9293 | 0 | 137.9199 | 1508353.7081 | 97407.0456 | 1741653.1896 | 1518214.6688 | 0 | 326268.893 | 0 | 2024840.027 | 5268218.3984 | 3595667.308 | 16080623.2385 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 24033880.7992 | 36182844.6129 | 31622.7766 | 1.5636 | 15370.6725 | 23140.4433 | 313.352 | 471.7492
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.7944 | 9.1848 | 0.48957 | 4 | 13647.1319 | 19851.0181 | 278.2152 | 404.6899 | 105.0164 | 0 | 141.5108 | 1730007.4952 | 111675.1983 | 2033555.5395 | 1836192.7461 | 0 | 349321.2968 | 0 | 2363693.3876 | 6149845.3342 | 4197395.8073 | 18771686.8049 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 26724944.3655 | 38873908.1792 | 42169.6503 | 1.9583 | 13647.1319 | 19851.0181 | 278.2152 | 404.6899
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.4971 | 10.9144 | 0.59986 | 4 | 12295.7742 | 17359.0366 | 250.666 | 353.8874 | 105.0637 | 0 | 152.3769 | 1954467.981 | 126084.2066 | 2334437.8929 | 2176551.7156 | 0 | 366119.2946 | 0 | 2713487.8254 | 7059938.7087 | 4818553.2359 | 21549640.8607 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 29502898.4213 | 41651862.235 | 56234.1325 | 2.3994 | 12295.7742 | 17359.0366 | 250.666 | 353.8874
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.3092 | 12.6568 | 0.71634 | 4 | 11242.2637 | 15482.2304 | 229.1888 | 315.6262 | 105.0684 | 0 | 172.6514 | 2169916.7899 | 139866.9058 | 2628101.1681 | 2520091.4538 | 0 | 374671.7395 | 0 | 3054732.7423 | 7947787.9835 | 5424528.6095 | 24259697.3924 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 32212954.953 | 44361918.7667 | 74989.4209 | 2.8653 | 11242.2637 | 15482.2304 | 229.1888 | 315.6262
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.6681 | 14.3098 | 0.83224 | 4 | 10426.7136 | 14076.1988 | 212.5627 | 286.9624 | 105.0352 | 0 | 177.8989 | 2365878.6708 | 152353.0616 | 2899337.756 | 2846858.7756 | 0 | 374444.2295 | 0 | 3369160.2725 | 8765863.9191 | 5982882.2453 | 26756778.9304 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 34710036.491 | 46859000.3047 | 100000 | 3.329 | 10426.7136 | 14076.1988 | 212.5627 | 286.9624
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.1749 | 15.8025 | 0.94159 | 4 | 9799.5496 | 13025.1982 | 199.7771 | 265.5363 | 104.9752 | 0 | 177.5381 | 2536677.0144 | 163190.576 | 3139000.5255 | 3142990.4296 | 0 | 366876.6087 | 0 | 3646006.7101 | 9486161.5609 | 6474500.1864 | 28955403.6115 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 36908661.1721 | 49057624.9858 | 133352.1432 | 3.7664 | 9799.5496 | 13025.1982 | 199.7771 | 265.5363
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.8749 | 17.1443 | 1.043 | 4 | 9311.5287 | 12223.675 | 189.8281 | 249.1961 | 104.8981 | 0 | 199.0423 | 2685731.5265 | 172610.0513 | 3350667.776 | 3410346.5488 | 0 | 354902.1289 | 0 | 3889960.6323 | 10120879.6245 | 6907708.307 | 30892806.5952 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 38846064.1558 | 50995027.9695 | 177827.941 | 4.1718 | 9311.5287 | 12223.675 | 189.8281 | 249.1961
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0575 | 18.2145 | 1.1275 | 4 | 8949.0343 | 11642.9276 | 182.4382 | 237.3568 | 104.8215 | 0 | 192.58 | 2801798.3612 | 179916.9097 | 3517176.0175 | 3624401.1421 | 0 | 339280.8451 | 0 | 4080403.5775 | 10616373.1029 | 7245892.7873 | 32405242.7434 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 40358500.304 | 52507464.1177 | 237137.3706 | 4.5098 | 8949.0343 | 11642.9276 | 182.4382 | 237.3568
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.1077 | 19.0836 | 1.198 | 4 | 8674.0224 | 11209.2076 | 176.8317 | 228.5149 | 104.7498 | 0 | 159.1323 | 2894319.4307 | 185722.5049 | 3650992.3454 | 3798807.588 | 0 | 322958.901 | 0 | 4232592.3003 | 11012336.9412 | 7516146.2433 | 33613876.2547 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 41567133.8153 | 53716097.629 | 316227.766 | 4.7921 | 8674.0224 | 11209.2076 | 176.8317 | 228.5149
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.1413 | 19.7743 | 1.2555 | 4 | 8465.9031 | 10885.1217 | 172.5889 | 221.9079 | 104.6869 | 0 | 196.6769 | 2966787.2037 | 190257.2883 | 3756495.2614 | 3937807.4936 | 0 | 307337.2524 | 0 | 4351886.9548 | 11322717.1615 | 7727987.1213 | 34561275.737 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 42514533.2976 | 54663497.1113 | 421696.5034 | 5.0219 | 8465.9031 | 10885.1217 | 172.5889 | 221.9079
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.287 | 20.3107 | 1.3011 | 4 | 8308.7062 | 10643.1079 | 169.3842 | 216.9742 | 104.6345 | 0 | 187.3529 | 3022444.2992 | 193732.3043 | 3837945.0515 | 4046020.828 | 0 | 293136.1898 | 0 | 4443378.6824 | 11560759.8693 | 7890456.1607 | 35287873.3853 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 43241130.9459 | 55390094.7596 | 562341.3252 | 5.2043 | 8308.7062 | 10643.1079 | 169.3842 | 216.9742
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.9172 | 20.7577 | 1.3396 | 4 | 8181.9556 | 10449.2838 | 166.8002 | 213.0228 | 104.5886 | 0 | 177.1093 | 3068414.5563 | 196597.253 | 3905498.0994 | 4136367.8772 | 0 | 280127.5859 | 0 | 4518932.095 | 11757334.3509 | 8024622.2835 | 35887894.1013 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 43841151.6619 | 55990115.4756 | 749894.2093 | 5.3583 | 8181.9556 | 10449.2838 | 166.8002 | 213.0228
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.6003 | 21.043 | 1.3647 | 4 | 8100.8361 | 10326.4626 | 165.1465 | 210.5189 | 104.558 | 0 | 198.2319 | 3097559.1261 | 198410.9456 | 3948462.1271 | 4194114.9578 | 0 | 270711.719 | 0 | 4566610.9615 | 11881384.981 | 8109289.3876 | 36266544.2057 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44219801.7663 | 56368765.58 | 1000000 | 5.4587 | 8100.8361 | 10326.4626 | 165.1465 | 210.5189
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.0112 | 21.2817 | 1.3859 | 4 | 8033.6194 | 10225.1795 | 163.7762 | 208.4541 | 104.5319 | 0 | 183.5758 | 3121834.7351 | 199920.1318 | 3984327.21 | 4242487.9706 | 0 | 262312.4386 | 0 | 4606244.1696 | 11984502.4586 | 8179669.1849 | 36581298.2992 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44534555.8598 | 56683519.6735 | 1333521.4322 | 5.5435 | 8033.6194 | 10225.1795 | 163.7762 | 208.4541
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.0977 | 21.4652 | 1.4022 | 4 | 7983.0704 | 10149.1082 | 162.7457 | 206.9033 | 104.5114 | 0 | 188.4718 | 3140429.3083 | 201075.1688 | 4011848.6381 | 4279711.8316 | 0 | 255700.8595 | 0 | 4636618.6644 | 12063530.6636 | 8233607.5586 | 36822522.6928 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44775780.2534 | 56924744.0671 | 1778279.41 | 5.6088 | 7983.0704 | 10149.1082 | 162.7457 | 206.9033
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.9138 | 21.6029 | 1.4146 | 4 | 7945.0794 | 10092.1798 | 161.9712 | 205.7427 | 104.4958 | 0 | 175.0202 | 3154339.7346 | 201938.6847 | 4032465.5318 | 4307656.5377 | 0 | 250467.641 | 0 | 4659278.5707 | 12122487.0914 | 8273846.5321 | 37002480.324 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 44955737.8846 | 57104701.6983 | 2371373.7057 | 5.6583 | 7945.0794 | 10092.1798 | 161.9712 | 205.7427
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.5346 | 21.7075 | 1.424 | 4 | 7916.5408 | 10049.4539 | 161.3894 | 204.8717 | 104.4838 | 0 | 191.3359 | 3164888.9478 | 202593.2275 | 4048116.9601 | 4328904.9632 | 0 | 246426.7401 | 0 | 4676463.0271 | 12167197.5221 | 8304362.3197 | 37138953.7077 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 45092211.2683 | 57241175.0821 | 3162277.6602 | 5.6959 | 7916.5408 | 10049.4539 | 161.3894 | 204.8717
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9996 | 21.7858 | 1.4311 | 4 | 7895.1113 | 10017.4592 | 160.9525 | 204.2195 | 104.4747 | 0 | 202.1031 | 3172774.4085 | 203082.3115 | 4059825.501 | 4344819.7672 | 0 | 243297.2837 | 0 | 4689281.716 | 12200549.1212 | 8327125.4714 | 37240755.5804 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 45194013.1411 | 57342976.9548 | 4216965.0343 | 5.7243 | 7895.1113 | 10017.4592 | 160.9525 | 204.2195
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.346 | 21.8441 | 1.4364 | 4 | 7879.0248 | 9993.517 | 160.6246 | 203.7314 | 104.4679 | 0 | 208.0884 | 3178636.9387 | 203445.8246 | 4068535.4726 | 4356669.4795 | 0 | 240881.1256 | 0 | 4698785.848 | 12225276.923 | 8344002.7043 | 37316234.3164 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 45269491.877 | 57418455.6907 | 5623413.2519 | 5.7456 | 7879.0248 | 9993.517 | 160.6246 | 203.7314
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.6038 | 21.8875 | 1.4404 | 4 | 7866.9522 | 9975.5976 | 160.3785 | 203.366 | 104.4628 | 0 | 219.8744 | 3182995.046 | 203715.9977 | 4075013.1654 | 4365488.1574 | 0 | 239026.3624 | 0 | 4705833.1043 | 12243612.4383 | 8356517.0702 | 37372201.3417 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 45325458.9023 | 57474422.716 | 7498942.0933 | 5.7615 | 7866.9522 | 9975.5976 | 160.3785 | 203.366
1 | 2300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.789 | 21.9187 | 1.4433 | 4 | 7857.8936 | 9962.2627 | 160.1938 | 203.0942 | 104.4592 | 0 | 217.0401 | 3186123.1068 | 203909.8856 | 4079664.0985 | 4371823.0495 | 0 | 237571.6359 | 0 | 4710845.7928 | 12256654.4254 | 8365418.4944 | 37412010.489 | 961560.8286 | 6991696.732 | 6991696.732 | 1478867.319 | 3678399.7627 | 0 | 45365268.0496 | 57514231.8633 | 10000000 | 5.7732 | 7857.8936 | 9962.2627 | 160.1938 | 203.0942
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.6051 | [19 empty] | 100 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2925 | [19 empty] | 133.3521 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3527 | [19 empty] | 177.8279 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.6585 | [19 empty] | 237.1374 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1974 | [19 empty] | 316.2278 | 0
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.91829 | 0.11572 | 0.0010847 | 4 | 2080109.0232 | 4990090.5781 | 42405.836 | 101729.746 | 86.9765 | 0 | 56.0943 | 71611.0652 | 4120.0973 | 62291.1695 | 51589.778 | 0 | 46501.0808 | 0 | 92084.1444 | 239584.0548 | 163521.0403 | 731302.4304 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9025466.5911 | 21651699.645 | 421.6965 | 0.0043389 | 2080109.0232 | 4990090.5781 | 42405.836 | 101729.746
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3402 | 0.19141 | 0.0032609 | 4 | 714623.146 | 1682617.5415 | 14568.5594 | 34302.4345 | 93.1501 | 0 | 225.5703 | 106640.7401 | 6387.0814 | 92724.2981 | 66606.01 | 0 | 59280.5623 | 0 | 129339.0899 | 336513.7807 | 229677.57 | 1027169.1326 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9321333.2934 | 21947566.3472 | 562.3413 | 0.013044 | 714623.146 | 1682617.5415 | 14568.5594 | 34302.4345
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.28459 | 0.0065492 | 4 | 368232.7674 | 850207.0808 | 7506.923 | 17332.6213 | 97.1824 | 0 | 288.5591 | 144645.0933 | 8892.1268 | 126961.1976 | 84669.487 | 0 | 71474.7218 | 0 | 170290.6244 | 443061.2732 | 302398.4229 | 1352392.947 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 9646557.1077 | 22272790.1616 | 749.8942 | 0.026197 | 368232.7674 | 850207.0808 | 7506.923 | 17332.6213
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4877 | 0.40462 | 0.011229 | 4 | 223307.1581 | 504411.6755 | 4552.4185 | 10283.1143 | 100.1044 | 0 | 422.1412 | 188509.2146 | 11810.1006 | 167878.7561 | 107747.0796 | 0 | 84555.7369 | 0 | 218595.3462 | 568740.2509 | 388176.9077 | 1736013.3926 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10030177.5533 | 22656410.6072 | 1000 | 0.044917 | 223307.1581 | 504411.6755 | 4552.4185 | 10283.1143
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3271 | 0.56281 | 0.017682 | 4 | 148439.9036 | 326960.9198 | 3026.1482 | 6665.5406 | 102.3132 | 0 | 82.5612 | 240680.3524 | 15295.2916 | 218246.0947 | 137920.7818 | 0 | 99625.4433 | 0 | 277589.5058 | 722230.9527 | 492937.4656 | 2204525.8879 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 10498690.0486 | 23124923.1025 | 1333.5214 | 0.070727 | 148439.9036 | 326960.9198 | 3026.1482 | 6665.5406
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3749 | 0.76141 | 0.026409 | 4 | 104569.3144 | 224097.2721 | 2131.7869 | 4568.526 | 103.9272 | 0 | 80.7339 | 300254.3882 | 19283.2983 | 277610.9437 | 175885.5701 | 0 | 115470.8503 | 0 | 346516.9697 | 901566.0747 | 615337.3713 | 2751925.4663 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 11046089.627 | 23672322.6809 | 1778.2794 | 0.10563 | 104569.3144 | 224097.2721 | 2131.7869 | 4568.526
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7024 | 1.0134 | 0.037999 | 4 | 76952.3776 | 160021.6779 | 1568.7783 | 3262.2583 | 105.1388 | 0 | 103.5659 | 369341.9683 | 23905.6332 | 348633.463 | 223798.3339 | 0 | 132815.9812 | 0 | 428413.198 | 1114643.2615 | 760766.9296 | 3402318.7686 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 11696482.9293 | 24322715.9832 | 2371.3737 | 0.152 | 76952.3776 | 160021.6779 | 1568.7783 | 3262.2583
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3024 | 1.3167 | 0.053026 | 4 | 58613.4844 | 118142.2751 | 1194.9152 | 2408.4901 | 105.9823 | 0 | 115.9102 | 445843.5458 | 29015.2818 | 429607.3654 | 281738.2434 | 0 | 149795.2069 | 0 | 521039.8609 | 1355638.838 | 925251.3625 | 4137929.7047 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 12432093.8655 | 25058326.9194 | 3162.2777 | 0.2121 | 58613.4844 | 118142.2751 | 1194.9152 | 2408.4901
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.583 | 1.7522 | 0.073723 | 4 | 45578.1078 | 88394.3393 | 929.1714 | 1802.0382 | 106.8087 | 0 | 107.5421 | 547249.1255 | 35794.2401 | 539623.9177 | 364305.235 | 0 | 174670.103 | 0 | 648040.6223 | 1686068.7678 | 1150776.5793 | 5146528.5907 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 13440692.7515 | 26066925.8053 | 4216.965 | 0.29489 | 45578.1078 | 88394.3393 | 929.1714 | 1802.0382
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2749 | 2.2651 | 0.10009 | 4 | 36362.2261 | 67898.3513 | 741.2932 | 1384.1997 | 107.3537 | 0 | 94.322 | 657260.6324 | 43127.6196 | 662427.3665 | 461858.3302 | 0 | 197863.8409 | 0 | 788789.7379 | 2052269.0951 | 1400715.8273 | 6264312.4499 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 14558476.6106 | 27184709.6645 | 5623.4133 | 0.40037 | 36362.2261 | 67898.3513 | 741.2932 | 1384.1997
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.6434 | 2.9074 | 0.13424 | 4 | 29591.1318 | 53104.9791 | 603.2552 | 1082.6168 | 107.7742 | 0 | 133.1648 | 784984.6621 | 51625.8268 | 808590.2572 | 584057.4971 | 0 | 223039.8177 | 0 | 956396.2437 | 2488346.8424 | 1698347.8503 | 7595388.9973 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 15889553.1581 | 28515786.212 | 7498.9421 | 0.53697 | 29591.1318 | 53104.9791 | 603.2552 | 1082.6168
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.8239 | 3.7045 | 0.17806 | 4 | 24519.8051 | 42247.1943 | 499.8694 | 861.2662 | 108.0995 | 0 | 123.9995 | 932347.4618 | 61409.6248 | 981321.4326 | 735620.4847 | 0 | 249965.4941 | 0 | 1154659.1542 | 3004186.266 | 2050418.8564 | 9169928.7745 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 17464092.9353 | 30090325.9892 | 10000 | 0.71224 | 24519.8051 | 42247.1943 | 499.8694 | 861.2662
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.9855 | 4.6886 | 0.23381 | 4 | 20658.9512 | 34159.413 | 421.1607 | 696.3858 | 108.3527 | 0 | 131.3558 | 1101851.6445 | 72637.8945 | 1184632.9883 | 922501.6538 | 0 | 278628.9859 | 0 | 1388498.7351 | 3612588.8886 | 2465666.1477 | 11027006.9384 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 19321171.0992 | 31947404.1531 | 13335.2143 | 0.93524 | 20658.9512 | 34159.413 | 421.1607 | 696.3858
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.2419 | 5.8817 | 0.30372 | 4 | 17678.0763 | 28071.1089 | 360.3915 | 572.2675 | 108.549 | 0 | 109.6689 | 1293851.5908 | 85328.5781 | 1420000.5307 | 1149043.8926 | 0 | 307960.5536 | 0 | 1659912.2069 | 4318751.0675 | 2947636.345 | 13182484.7653 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 21476648.926 | 34102881.9799 | 17782.7941 | 1.2149 | 17678.0763 | 28071.1089 | 360.3915 | 572.2675
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.723 | 7.3084 | 0.39001 | 4 | 15352.7704 | 23446.2383 | 312.987 | 477.9833 | 108.7015 | 0 | 116.0315 | 1509015.3676 | 99518.8839 | 1689272.5956 | 1419942.5607 | 0 | 337361.472 | 0 | 1971493.2431 | 5129421.0097 | 3500935.2382 | 15656960.3707 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 23951124.5314 | 36577357.5853 | 23713.7371 | 1.5601 | 15352.7704 | 23446.2383 | 312.987 | 477.9833
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.3897 | 8.9609 | 0.4936 | 4 | 13526.9804 | 19921.9515 | 275.7658 | 406.1359 | 108.8156 | 0 | 149.2758 | 1743357.6175 | 114937.9938 | 1988334.3187 | 1733748.2326 | 0 | 364730.9164 | 0 | 2318592.5408 | 6032502.1823 | 4117306.695 | 18413510.4969 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 26707674.6577 | 39333907.7116 | 31622.7766 | 1.9744 | 13526.9804 | 19921.9515 | 275.7658 | 406.1359
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.007 | 10.7925 | 0.6131 | 4 | 12091.3366 | 17239.875 | 246.4983 | 351.4582 | 108.8891 | 0 | 159.3609 | 1988630.5932 | 131032.6197 | 2307185.5299 | 2081792.5398 | 0 | 387316.4582 | 0 | 2689423.5189 | 6997328.3197 | 4775820.3589 | 21358529.9384 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 29652694.0992 | 42278927.1531 | 42169.6503 | 2.4524 | 12091.3366 | 17239.875 | 246.4983 | 351.4582
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.0756 | 12.7043 | 0.74368 | 4 | 10966.5286 | 15211.0178 | 223.5675 | 310.0972 | 108.9159 | 0 | 158.2216 | 2231642.929 | 146925.2827 | 2628672.197 | 2445689.4506 | 0 | 401886.7124 | 0 | 3063378.463 | 7970282.3753 | 5439881.4941 | 24328358.9041 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 32622523.0649 | 45248756.1188 | 56234.1325 | 2.9747 | 10966.5286 | 15211.0178 | 223.5675 | 310.0972
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.007 | 14.5806 | 0.87818 | 4 | 10090.9927 | 13685.4127 | 205.7185 | 278.9956 | 108.8962 | 0 | 167.0913 | 2459413.828 | 161760.7347 | 2934963.4057 | 2803850.8665 | 0 | 406740.8645 | 0 | 3419024.5828 | 8895600.6262 | 6071430.2137 | 27152785.1223 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 35446949.2831 | 48073182.337 | 74989.4209 | 3.5127 | 10090.9927 | 13685.4127 | 205.7185 | 278.9956
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.3218 | 16.3289 | 1.0093 | 4 | 9414.2875 | 12541.8153 | 191.923 | 255.6819 | 108.8389 | 0 | 202.5553 | 2663398.7681 | 174986.8092 | 3213399.6393 | 3138815.531 | 0 | 402584.5121 | 0 | 3741342.2512 | 9734205.0829 | 6643794.987 | 29712527.5807 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 38006691.7415 | 50632924.7954 | 100000 | 4.0371 | 9414.2875 | 12541.8153 | 191.923 | 255.6819
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.6239 | 17.8756 | 1.1304 | 4 | 8894.544 | 11687.0575 | 181.3273 | 238.2565 | 108.7585 | 0 | 204.5755 | 2837983.6538 | 186254.1034 | 3454885.7674 | 3436416.5809 | 0 | 391057.1728 | 0 | 4019572.9385 | 10458104.2582 | 7137871.0488 | 31922145.5237 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 40216309.6845 | 52842542.7384 | 133352.1432 | 4.5215 | 8894.544 | 11687.0575 | 181.3273 | 238.2565
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.646 | 18.99 | 1.2291 | 4 | 8490.2416 | 11058.4986 | 173.0851 | 225.4425 | 108.684 | 0 | 322.8108 | 2960619.3039 | 194136.1821 | 3626324.2505 | 3651653.8588 | 0 | 365903.4364 | 0 | 4211468.4424 | 10957376.996 | 7478634.9514 | 33446117.4215 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 41740281.5822 | 54366514.6361 | 177827.941 | 4.9163 | 8490.2416 | 11058.4986 | 173.0851 | 225.4425
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.9567 | 20.3334 | 1.3318 | 4 | 8189.7165 | 10559.7873 | 166.9584 | 215.2755 | 108.5767 | 0 | 173.374 | 3105215.228 | 203392.1215 | 3830433.5021 | 3912174.6843 | 0 | 357423.3402 | 0 | 4449369.1617 | 11576345.8676 | 7901093.9247 | 35335447.8301 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 43629611.9908 | 56255845.0447 | 237137.3706 | 5.3274 | 8189.7165 | 10559.7873 | 166.9584 | 215.2755
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.724 | 21.2034 | 1.4068 | 4 | 7962.2324 | 10206.0123 | 162.3209 | 208.0634 | 108.4971 | 0 | 184.3606 | 3197059.4949 | 209248.3191 | 3961227.6396 | 4081563.8878 | 0 | 339096.7643 | 0 | 4597396.4812 | 11961482.5884 | 8163957.6505 | 36511032.8258 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 44805196.9866 | 57431430.0404 | 316227.766 | 5.6272 | 7962.2324 | 10206.0123 | 162.3209 | 208.0634
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.5017 | 21.8894 | 1.4672 | 4 | 7790.0818 | 9941.4423 | 158.8114 | 202.6697 | 108.4289 | 0 | 190.0872 | 3268515.6164 | 213791.4308 | 4063621.1796 | 4215508.106 | 0 | 321996.8202 | 0 | 4712538.9297 | 12261059.6204 | 8368425.1305 | 37425456.8335 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 45719620.9943 | 58345854.0482 | 421696.5034 | 5.869 | 7790.0818 | 9941.4423 | 158.8114 | 202.6697
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.4371 | 22.4202 | 1.515 | 4 | 7660.0442 | 9743.6368 | 156.1604 | 198.6372 | 108.3729 | 0 | 178.3623 | 3323244.2161 | 217262.9218 | 4142428.689 | 4319400.8131 | 0 | 306781.2028 | 0 | 4800555.9587 | 12490061.8751 | 8524723.8749 | 38124459.5516 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 46418623.7123 | 59044856.7662 | 562341.3252 | 6.0598 | 7660.0442 | 9743.6368 | 156.1604 | 198.6372
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.7003 | 22.8281 | 1.5522 | 4 | 7561.9603 | 9595.5719 | 154.1608 | 195.6187 | 108.328 | 0 | 187.9635 | 3364974.2705 | 219905.0162 | 4202746.5706 | 4399391.5737 | 0 | 293824.076 | 0 | 4867528.1877 | 12664309.8772 | 8643651.7167 | 38656331.2887 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 46950495.4495 | 59576728.5034 | 749894.2093 | 6.2088 | 7561.9603 | 9595.5719 | 154.1608 | 195.6187
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.4271 | 23.1386 | 1.5809 | 4 | 7488.0649 | 9484.7377 | 152.6543 | 193.3592 | 108.2927 | 0 | 193.9533 | 3396545.8263 | 221901.0516 | 4248514.0544 | 4460360.9483 | 0 | 283087.8554 | 0 | 4918059.797 | 12795782.7591 | 8733384.6602 | 39057636.9524 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47351801.1131 | 59978034.167 | 1000000 | 6.3236 | 7488.0649 | 9484.7377 | 152.6543 | 193.3592
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.7501 | 23.3759 | 1.603 | 4 | 7432.4461 | 9401.5991 | 151.5205 | 191.6643 | 108.2651 | 0 | 204.043 | 3420576.8964 | 223418.6606 | 4283428.1769 | 4507031.728 | 0 | 274471.3278 | 0 | 4956481.4479 | 12895748.0134 | 8801613.0003 | 39362769.2512 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47656933.412 | 60283166.4659 | 1333521.4322 | 6.412 | 7432.4461 | 9401.5991 | 151.5205 | 191.6643
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.7512 | 23.5552 | 1.6198 | 4 | 7390.6161 | 9339.3131 | 150.6677 | 190.3945 | 108.2439 | 0 | 191.323 | 3438671.436 | 224560.3818 | 4309761.9996 | 4542324.6792 | 0 | 267621.8343 | 0 | 4985346.7291 | 12970849.5539 | 8852871.3448 | 39592007.9589 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 47886172.1197 | 60512405.1736 | 1778279.41 | 6.4793 | 7390.6161 | 9339.3131 | 150.6677 | 190.3945
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.5017 | 23.6895 | 1.6325 | 4 | 7359.1763 | 9292.6923 | 150.0268 | 189.4441 | 108.2278 | 0 | 194.1333 | 3452185.5888 | 225412.5331 | 4329455.0424 | 4568769.2341 | 0 | 262221.9086 | 0 | 5006837.2797 | 13026763.5582 | 8891033.8017 | 39762678.9463 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48056843.1071 | 60683076.161 | 2371373.7057 | 6.5302 | 7359.1763 | 9292.6923 | 150.0268 | 189.4441
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.0593 | 23.7892 | 1.6421 | 4 | 7335.5579 | 9257.8326 | 149.5453 | 188.7334 | 108.2157 | 0 | 199.4853 | 3462196.7728 | 226043.4887 | 4344057.5336 | 4588406.6215 | 0 | 257987.5534 | 0 | 5022689.8683 | 13068008.7419 | 8919184.4871 | 39888575.0673 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48182739.2281 | 60808972.282 | 3162277.6602 | 6.5684 | 7335.5579 | 9257.8326 | 149.5453 | 188.7334
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.4808 | 23.8645 | 1.6493 | 4 | 7317.8223 | 9231.678 | 149.1837 | 188.2002 | 108.2065 | 0 | 202.4258 | 3469750.7559 | 226519.4033 | 4355083.8158 | 4603250.867 | 0 | 254743.4769 | 0 | 5034645.8443 | 13099115.7391 | 8940415.6518 | 39983525.554 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48277689.7148 | 60903922.7687 | 4216965.0343 | 6.5973 | 7317.8223 | 9231.678 | 149.1837 | 188.2002
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7929 | 23.9202 | 1.6547 | 4 | 7304.5085 | 9212.12 | 148.9123 | 187.8015 | 108.1997 | 0 | 173.8271 | 3475334.5755 | 226871.0955 | 4363238.7333 | 4614238.4766 | 0 | 252235.424 | 0 | 5043448.1389 | 13122017.504 | 8956046.577 | 40053430.5249 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48347594.6857 | 60973827.7396 | 5623413.2519 | 6.6189 | 7304.5085 | 9212.12 | 148.9123 | 187.8015
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.0487 | 23.9659 | 1.659 | 4 | 7294.5166 | 9197.2321 | 148.7086 | 187.498 | 108.194 | 0 | 186.0781 | 3479905.4716 | 227158.9311 | 4369917.004 | 4623242.0683 | 0 | 250453.4354 | 0 | 5050763.995 | 13141051.8609 | 8969037.9167 | 40111530.683 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48405694.8438 | 61031927.8977 | 7498942.0933 | 6.6359 | 7294.5166 | 9197.2321 | 148.7086 | 187.498
1 | 2400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2191 | 23.9963 | 1.662 | 4 | 7287.0191 | 9186.2965 | 148.5557 | 187.2751 | 108.1903 | 0 | 196.0171 | 3482947.7126 | 227350.4707 | 4374363.3327 | 4629239.5084 | 0 | 248973.8419 | 0 | 5055521.1978 | 13153429.1268 | 8977485.655 | 40149310.8459 | 961560.8286 | 7332603.3321 | 7332603.3321 | 1478867.319 | 3814762.4027 | 0 | 48443475.0067 | 61069708.0606 | 10000000 | 6.6479 | 7287.0191 | 9186.2965 | 148.5557 | 187.2751
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.7262 | [19 empty] | 100 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3143 | [19 empty] | 133.3521 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.7365 | [19 empty] | 177.8279 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6975 | [19 empty] | 237.1374 | 0
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.71826 | 0.084839 | 0.00028218 | 4 | 8189075.6126 | 19805676.4269 | 166945.3829 | 403765.5031 | 83.9183 | 0 | 78.0372 | 56302.8076 | 3172.0686 | 48707.226 | 45060.8027 | 0 | 41159.4497 | 0 | 75816.9183 | 197260.0691 | 134634.0505 | 602113.3924 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9243044.2442 | 22354750.6655 | 316.2278 | 0.0011287 | 8189075.6126 | 19805676.4269 | 166945.3829 | 403765.5031
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1069 | 0.15646 | 0.0020661 | 4 | 1154744.1399 | 2741272.4168 | 23541.0212 | 55884.5461 | 92.6275 | 0 | 182.3908 | 92412.1098 | 5506.6871 | 78943.0968 | 59018.062 | 0 | 55454.9767 | 0 | 113620.6236 | 295617.5559 | 201765.0562 | 902338.1681 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9543269.0199 | 22654975.4412 | 421.6965 | 0.0082644 | 1154744.1399 | 2741272.4168 | 23541.0212 | 55884.5461
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5542 | 0.24278 | 0.0050039 | 4 | 492622.3987 | 1147698.9815 | 10042.7739 | 23397.3961 | 97.8953 | 0 | 245.2192 | 130276.2003 | 8028.7802 | 111748.8554 | 75369.7196 | 0 | 68205.3745 | 0 | 153515.2827 | 399415.2753 | 272609.1326 | 1219168.6207 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 9860099.4724 | 22971805.8937 | 562.3413 | 0.020016 | 492622.3987 | 1147698.9815 | 10042.7739 | 23397.3961
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.35791 | 0.0093426 | 4 | 274120.3422 | 624977.7452 | 5588.314 | 12741.0167 | 101.7336 | 0 | 364.9915 | 175131.3825 | 11061.1586 | 152005.3333 | 96875.9253 | 0 | 82505.859 | 0 | 201856.0669 | 525188.0797 | 358451.6559 | 1603075.4612 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10244006.3129 | 23355712.7342 | 749.8942 | 0.03737 | 274120.3422 | 624977.7452 | 5588.314 | 12741.0167
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8667 | 0.50363 | 0.015433 | 4 | 173160.3556 | 385557.8495 | 3530.1081 | 7860.1183 | 104.4721 | 0 | 73.865 | 226122.7193 | 14535.0381 | 199370.1343 | 123964.1382 | 0 | 97429.8983 | 0 | 257954.552 | 671144.8305 | 458070.1374 | 2048591.448 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 10689522.2998 | 23801228.7211 | 1000 | 0.061732 | 173160.3556 | 385557.8495 | 3530.1081 | 7860.1183
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.805 | 0.69239 | 0.02376 | 4 | 118112.7423 | 256075.0234 | 2407.888 | 5220.4357 | 106.5248 | 0 | 91.0157 | 285944.6043 | 18624.1976 | 256803.5554 | 158881.7264 | 0 | 114132.9707 | 0 | 325410.9512 | 846652.544 | 577857.7583 | 2584308.3078 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11225239.1596 | 24336945.5809 | 1333.5214 | 0.095038 | 118112.7423 | 256075.0234 | 2407.888 | 5220.4357
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9667 | 0.92703 | 0.034908 | 4 | 84836.616 | 178739.8019 | 1729.5092 | 3643.8526 | 108.0283 | 0 | 71.3426 | 353784.3114 | 23266.1615 | 323986.1275 | 202257.0863 | 0 | 131432.6835 | 0 | 403543.2844 | 1049936.8478 | 716603.4727 | 3204809.9749 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 11845740.8267 | 24957447.248 | 1778.2794 | 0.13963 | 84836.616 | 178739.8019 | 1729.5092 | 3643.8526
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4601 | 1.2287 | 0.049655 | 4 | 63415.8485 | 129429.7087 | 1292.8178 | 2638.5997 | 109.1679 | 0 | 99.4075 | 433668.8717 | 28724.732 | 405559.0551 | 257789.5624 | 0 | 151117.1084 | 0 | 497975.1386 | 1295629.1618 | 884293.5254 | 3954757.1554 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 12595688.0072 | 25707394.4285 | 2371.3737 | 0.19862 | 63415.8485 | 129429.7087 | 1292.8178 | 2638.5997
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.1673 | 1.572 | 0.068287 | 4 | 49039.2233 | 97041.6524 | 999.7309 | 1978.3253 | 109.8811 | 0 | 88.8718 | 517420.5187 | 34426.8666 | 493678.8072 | 321419.879 | 0 | 167953.2661 | 0 | 598610.7417 | 1557462.3579 | 1063000.0619 | 4753972.4991 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 13394903.3509 | 26506609.7722 | 3162.2777 | 0.27315 | 49039.2233 | 97041.6524 | 999.7309 | 1978.3253
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.8056 | 2.1109 | 0.095148 | 4 | 38374.6059 | 72825.5298 | 782.3182 | 1484.6469 | 110.7773 | 0 | 91.8913 | 639455.1674 | 42774.7395 | 624547.0661 | 420575.3008 | 0 | 198254.6701 | 0 | 750986.7081 | 1953913.366 | 1333586.0212 | 5964093.0391 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 14605023.8909 | 27716730.3122 | 4216.965 | 0.38059 | 38374.6059 | 72825.5298 | 782.3182 | 1484.6469
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.807 | 2.7203 | 0.1285 | 4 | 30908.4744 | 56417.6669 | 630.1111 | 1150.1504 | 111.2972 | 0 | 105.5497 | 766223.1426 | 51402.294 | 764768.7188 | 532927.2935 | 0 | 224171.3754 | 0 | 912402.2015 | 2373883.3688 | 1620224.1777 | 7246002.5723 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 15886933.424 | 28998639.8453 | 5623.4133 | 0.514 | 30908.4744 | 56417.6669 | 630.1111 | 1150.1504
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.5607 | 3.4828 | 0.17155 | 4 | 25375.2163 | 44482.3956 | 517.3081 | 906.8338 | 111.7002 | 0 | 106.4843 | 913424.0039 | 61398.0392 | 931639.9445 | 673391.3101 | 0 | 252339.8925 | 0 | 1104555.3442 | 2873826.4302 | 1961445.5898 | 8772020.5544 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 17412951.4062 | 30524657.8275 | 7498.9421 | 0.68622 | 25375.2163 | 44482.3956 | 517.3081 | 906.8338
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.2017 | 4.4257 | 0.2266 | 4 | 21196.3944 | 35661.9377 | 432.1172 | 727.0168 | 112.012 | 0 | 104.3169 | 1082823.7609 | 72875.436 | 1128222.9738 | 847075.1009 | 0 | 282247.0026 | 0 | 1331165.267 | 3463418.9651 | 2363854.6098 | 10571683.1161 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 19212613.9679 | 32324320.3891 | 10000 | 0.90641 | 21196.3944 | 35661.9377 | 432.1172 | 727.0168
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.8702 | 5.5772 | 0.29614 | 4 | 17992.5445 | 29061.5677 | 366.8024 | 592.4594 | 112.2538 | 0 | 111.0107 | 1275855.1717 | 85923.9431 | 1357285.5587 | 1059037.6403 | 0 | 313253.6342 | 0 | 1595628.8197 | 4151498.8804 | 2833483.2907 | 12671966.9388 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 21312897.7906 | 34424604.2119 | 13335.2143 | 1.1845 | 17992.5445 | 29061.5677 | 366.8024 | 592.4594
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.7567 | 6.9764 | 0.3831 | 4 | 15504.7397 | 24061.1105 | 316.0851 | 490.5183 | 112.4429 | 0 | 133.1153 | 1495269.8363 | 100721.715 | 1623251.2373 | 1316567.0524 | 0 | 345416.017 | 0 | 1903678.0846 | 4952979.8781 | 3380510.5403 | 15118394.3609 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 23759325.2127 | 36871031.634 | 17782.7941 | 1.5324 | 15504.7397 | 24061.1105 | 316.0851 | 490.5183
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.9003 | 8.6311 | 0.48942 | 4 | 13555.334 | 20252.885 | 276.3438 | 412.8825 | 112.5883 | 0 | 121.0197 | 1738710.6329 | 117101.012 | 1924364.4949 | 1621111.0313 | 0 | 376788.6554 | 0 | 2253449.5723 | 5863013.5411 | 4001627.2147 | 17896166.1546 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 26537097.0064 | 39648803.4277 | 23713.7371 | 1.9577 | 13555.334 | 20252.885 | 276.3438 | 412.8825
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.2035 | 10.5202 | 0.61536 | 4 | 12020.7567 | 17347.5795 | 245.0594 | 353.6539 | 112.6916 | 0 | 108.7257 | 2000436.1465 | 134664.4439 | 2254354.0847 | 1968922.2374 | 0 | 404891.4108 | 0 | 2637674.6461 | 6862688.3676 | 4683925.825 | 20947557.1618 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 29588488.0136 | 42700194.4349 | 31622.7766 | 2.4614 | 12020.7567 | 17347.5795 | 245.0594 | 353.6539
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.2734 | 12.5605 | 0.7575 | 4 | 10813.7545 | 15141.0673 | 220.453 | 308.6711 | 112.7466 | 0 | 172.4023 | 2267865.6726 | 152552.9676 | 2597728.9734 | 2345021.3494 | 0 | 425866.1474 | 0 | 3037723.693 | 7903533.9264 | 5394324.3062 | 24124617.036 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 32765547.8877 | 45877254.309 | 42169.6503 | 3.03 | 10813.7545 | 15141.0673 | 220.453 | 308.6711
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.5977 | 14.6434 | 0.90942 | 4 | 9869.3034 | 13473.7085 | 201.1991 | 274.6798 | 112.7487 | 0 | 179.322 | 2527560.4374 | 169853.9388 | 2936980.7333 | 2729852.5999 | 0 | 437269.3817 | 0 | 3432591.6655 | 8930899.3922 | 6095522.3468 | 27260530.4955 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 35901461.3473 | 49013167.7686 | 56234.1325 | 3.6377 | 9869.3034 | 13473.7085 | 201.1991 | 274.6798
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.5661 | 16.6417 | 1.0623 | 4 | 9135.4165 | 12221.0423 | 186.2378 | 249.1425 | 112.7023 | 0 | 145.9548 | 2766031.3827 | 185665.2186 | 3253568.7177 | 3100324.7953 | 0 | 437901.9566 | 0 | 3799961.9076 | 9886721.4043 | 6747890.5103 | 30178065.8931 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 38818996.7449 | 51930703.1662 | 74989.4209 | 4.2493 | 9135.4165 | 12221.0423 | 186.2378 | 249.1425
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.7593 | 18.4705 | 1.2084 | 4 | 8569.0119 | 11281.6736 | 174.6909 | 229.9922 | 112.6205 | 0 | 185.2494 | 2976263.0955 | 199532.2676 | 3536783.9299 | 3440779.2835 | 0 | 429425.696 | 0 | 4127285.8662 | 10738351.2012 | 7329145.3459 | 32777566.6856 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 41418497.5374 | 54530203.9587 | 100000 | 4.8335 | 8569.0119 | 11281.6736 | 174.6909 | 229.9922
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.825 | 20.0618 | 1.3408 | 4 | 8134.4127 | 10579.1378 | 165.831 | 215.67 | 112.5203 | 0 | 179.692 | 3153606.3333 | 211169.7152 | 3778793.9688 | 3738364.4884 | 0 | 413902.6701 | 0 | 4405376.4986 | 11461885.9823 | 7822972.7011 | 34986072.3579 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 43627003.2097 | 56738709.631 | 133352.1432 | 5.3633 | 8134.4127 | 10579.1378 | 165.831 | 215.67
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.6728 | 21.4022 | 1.4562 | 4 | 7802.5205 | 10053.4641 | 159.0649 | 204.9535 | 112.4159 | 0 | 183.4471 | 3299250.0279 | 220680.987 | 3979745.4101 | 3990101.8998 | 0 | 394495.801 | 0 | 4634866.9091 | 12058972.9555 | 8230496.8292 | 36808610.8195 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 45449541.6713 | 58561248.0926 | 177827.941 | 5.825 | 7802.5205 | 10053.4641 | 159.0649 | 204.9535
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.5971 | 22.5533 | 1.5571 | 4 | 7544.8436 | 9649.997 | 153.8118 | 196.7282 | 112.3122 | 0 | 186.7949 | 3421770.5639 | 228647.1964 | 4150383.0207 | 4207166.1166 | 0 | 374378.1119 | 0 | 4829114.5537 | 12564365.4812 | 8575437.6128 | 38351262.6573 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 46992193.5091 | 60103899.9304 | 237137.3706 | 6.2284 | 7544.8436 | 9649.997 | 153.8118 | 196.7282
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.0935 | 23.4214 | 1.6361 | 4 | 7354.8805 | 9358.3816 | 149.9392 | 190.7833 | 112.2255 | 0 | 186.0771 | 3512671.4437 | 234535.226 | 4277956.6475 | 4371439.6608 | 0 | 354154.2665 | 0 | 4972795.3254 | 12938193.376 | 8830582.8324 | 39492328.7782 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 48133259.63 | 61244966.0513 | 316227.766 | 6.5444 | 7354.8805 | 9358.3816 | 149.9392 | 190.7833
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.624 | 24.0994 | 1.6992 | 4 | 7211.1195 | 9140.226 | 147.0084 | 186.3359 | 112.1529 | 0 | 186.3977 | 3582811.7753 | 239064.8438 | 4376976.4125 | 4500122.8108 | 0 | 335616.6509 | 0 | 5083491.0724 | 13226201.0029 | 9027153.9557 | 40371438.5242 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49012369.3759 | 62124075.7972 | 421696.5034 | 6.7968 | 7211.1195 | 9140.226 | 147.0084 | 186.3359
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.3734 | 24.6253 | 1.7489 | 4 | 7102.5172 | 8976.7844 | 144.7944 | 183.0039 | 112.0935 | 0 | 199.5267 | 3636699.7423 | 242536.4669 | 4453404.7264 | 4600153.7949 | 0 | 319511.254 | 0 | 5168399.334 | 13447114.8825 | 9177932.2179 | 41045752.4189 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49686683.2707 | 62798389.692 | 562341.3252 | 6.9956 | 7102.5172 | 8976.7844 | 144.7944 | 183.0039
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.4734 | 25.0256 | 1.7874 | 4 | 7020.5947 | 8854.4992 | 143.1243 | 180.5109 | 112.0467 | 0 | 196.4269 | 3677430.3456 | 245155.4504 | 4511379.0407 | 4676443.9954 | 0 | 305863.9941 | 0 | 5232346.4022 | 13613492.0368 | 9291488.0444 | 41553599.3098 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 50194530.1615 | 63306236.5828 | 749894.2093 | 7.1496 | 7020.5947 | 8854.4992 | 143.1243 | 180.5109
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.7129 | 24.8807 | 1.7942 | 4 | 6954.244 | 8781.2054 | 141.7717 | 179.0168 | 112.0635 | 0 | 195.8268 | 3662704.2513 | 244208.6458 | 4490408.2918 | 4648817.5687 | 0 | 277979.6051 | 0 | 5196406.1614 | 13519982.9026 | 9227666.1389 | 41268173.5656 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 49909104.4174 | 63020810.8387 | 1000000 | 7.1768 | 6954.244 | 8781.2054 | 141.7717 | 179.0168
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.2 | 26.2995 | 1.8794 | 4 | 6910.0794 | 8654.2399 | 140.8713 | 176.4284 | 111.8882 | 0 | 227.9637 | 3805396.449 | 253354.8069 | 4694701.3113 | 4919712.0127 | 0 | 308741.8088 | 0 | 5452943.4916 | 14187440.4125 | 9683219.6043 | 43305509.8971 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51946440.7488 | 65058147.1701 | 1333521.4322 | 7.5175 | 6910.0794 | 8654.2399 | 140.8713 | 176.4284
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.2324 | 25.739 | 1.8571 | 4 | 6877.4503 | 8642.5441 | 140.2061 | 176.19 | 111.9594 | 0 | 184.4213 | 3749392.8369 | 249771.5736 | 4614256.6506 | 4812596.1827 | 0 | 278726.6787 | 0 | 5344850.1298 | 13906203.6581 | 9491269.7406 | 42447067.451 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51087998.3027 | 64199704.724 | 1778279.41 | 7.4283 | 6877.4503 | 8642.5441 | 140.2061 | 176.19
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.9272 | 25.8704 | 1.8701 | 4 | 6851.1784 | 8603.9561 | 139.6705 | 175.4033 | 111.9429 | 0 | 176.1255 | 3762558.8573 | 250614.5372 | 4633142.3161 | 4837687.9612 | 0 | 273189.973 | 0 | 5365305.5215 | 13959424.3914 | 9527593.9846 | 42609517.5424 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51250448.3942 | 64362154.8155 | 2371373.7057 | 7.4805 | 6851.1784 | 8603.9561 | 139.6705 | 175.4033
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.4575 | 25.9706 | 1.8801 | 4 | 6831.4414 | 8574.9585 | 139.2682 | 174.8121 | 111.9301 | 0 | 221.422 | 3772582.7733 | 251255.9988 | 4647533.984 | 4856833.9676 | 0 | 268953.1028 | 0 | 5380892.3323 | 13999978.076 | 9555272.7076 | 42733302.9424 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51374233.7942 | 64485940.2155 | 3162277.6602 | 7.5203 | 6831.4414 | 8574.9585 | 139.2682 | 174.8121
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.8324 | 26.0414 | 1.8873 | 4 | 6816.6199 | 8553.4421 | 138.966 | 174.3735 | 111.921 | 0 | 208.1859 | 3779654.3407 | 251708.3533 | 4657693.8734 | 4870363.4079 | 0 | 265551.3401 | 0 | 5391738.813 | 14028198.3937 | 9574533.6544 | 42819442.1765 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51460373.0283 | 64572079.4496 | 4216965.0343 | 7.5493 | 6816.6199 | 8553.4421 | 138.966 | 174.3735
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.1251 | 26.0966 | 1.8929 | 4 | 6805.4934 | 8537.2065 | 138.7392 | 174.0425 | 111.9139 | 0 | 182.9509 | 3785166.5892 | 252060.8647 | 4665617.3412 | 4880922.1608 | 0 | 263023.9574 | 0 | 5400248.4562 | 14050338.7397 | 9589644.8954 | 42887023.0045 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51527953.8563 | 64639660.2776 | 5623413.2519 | 7.5715 | 6805.4934 | 8537.2065 | 138.7392 | 174.0425
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.364 | 26.1417 | 1.8973 | 4 | 6797.1428 | 8524.855 | 138.5689 | 173.7907 | 111.9081 | 0 | 204.7397 | 3789662.0959 | 252348.2949 | 4672081.7724 | 4889541.3839 | 0 | 261221.8472 | 0 | 5407293.6038 | 14068668.7687 | 9602155.5169 | 42942973.2837 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51583904.1355 | 64695610.5568 | 7498942.0933 | 7.5891 | 6797.1428 | 8524.855 | 138.5689 | 173.7907
1 | 2500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5272 | 26.1725 | 1.9004 | 4 | 6790.8768 | 8515.7438 | 138.4412 | 173.605 | 111.9041 | 0 | 194.0079 | 3792729.2855 | 252544.3657 | 4676493.7331 | 4895426.5872 | 0 | 259755.6597 | 0 | 5412010.3561 | 14080940.7907 | 9610531.4241 | 42980432.2021 | 961560.8286 | 7679370.0231 | 7679370.0231 | 1478867.319 | 3953469.0791 | 0 | 51621363.0539 | 64733069.4752 | 10000000 | 7.6016 | 6790.8768 | 8515.7438 | 138.4412 | 173.605
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 22.4808 | [19 empty] | 100 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.3054 | [19 empty] | 133.3521 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8879 | [19 empty] | 177.8279 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1268 | [19 empty] | 237.1374 | 0
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.86458 | 0.11592 | 0.00092425 | 4 | 2633480.7314 | 6313608.0563 | 53687.0668 | 128711.44 | 89.9782 | 0 | 59.1998 | 73568.4337 | 4304.2936 | 62232.095 | 50719.4431 | 0 | 48867.8081 | 0 | 93479.9087 | 243215.547 | 165999.6084 | 742387.1376 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 9735944.7712 | 23341328.6871 | 316.2278 | 0.003697 | 2633480.7314 | 6313608.0563 | 53687.0668 | 128711.44
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2819 | 0.1991 | 0.0034105 | 4 | 737731.8552 | 1735057.3705 | 15039.6617 | 35371.4913 | 97.5837 | 0 | 196.2388 | 113347.0415 | 6960.3932 | 95374.7571 | 66284.0615 | 0 | 63657.2395 | 0 | 134793.1622 | 350704.1581 | 239362.7941 | 1070483.6071 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10064041.2408 | 23669425.1567 | 421.6965 | 0.013642 | 737731.8552 | 1735057.3705 | 15039.6617 | 35371.4913
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.807 | 0.30768 | 0.0073053 | 4 | 357445.3544 | 823046.6868 | 7287.007 | 16778.92 | 102.6853 | 0 | 301.0066 | 158768.9106 | 10069.542 | 134591.6106 | 86105.6566 | 0 | 79069.577 | 0 | 182756.0658 | 475493.7947 | 324534.2853 | 1451389.4426 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10444947.0763 | 24050330.9922 | 562.3413 | 0.029221 | 357445.3544 | 823046.6868 | 7287.007 | 16778.92
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.44299 | 0.012928 | 4 | 210310.1952 | 473418.4271 | 4287.4578 | 9651.275 | 106.1771 | 0 | 433.1967 | 209222.2442 | 13567.2849 | 179699.364 | 110608.8771 | 0 | 94417.3246 | 0 | 236930.887 | 616445.5667 | 420736.7659 | 1881628.3143 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 10875185.948 | 24480569.8639 | 749.8942 | 0.05171 | 210310.1952 | 473418.4271 | 4287.4578 | 9651.275
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2734 | 0.61849 | 0.020725 | 4 | 137393.9182 | 301511.7273 | 2800.9609 | 6146.7244 | 108.7684 | 0 | 91.408 | 268211.2314 | 17681.0065 | 234254.4971 | 142131.8566 | 0 | 111443.286 | 0 | 301751.5323 | 785095.5893 | 535843.8718 | 2396412.871 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 11389970.5046 | 24995354.4205 | 1000 | 0.0829 | 137393.9182 | 301511.7273 | 2800.9609 | 6146.7244
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3212 | 0.84301 | 0.031337 | 4 | 95753.0045 | 204292.5017 | 1952.0545 | 4164.779 | 110.6952 | 0 | 87.7869 | 336768.7148 | 22475.8372 | 299698.5671 | 182523.7534 | 0 | 130053.3086 | 0 | 378892.8706 | 985801.5278 | 672829.7989 | 3009044.3785 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 12002602.0121 | 25607985.928 | 1333.5214 | 0.12535 | 95753.0045 | 204292.5017 | 1952.0545 | 4164.779
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6272 | 1.1236 | 0.045453 | 4 | 69946.8785 | 144778.4366 | 1425.9617 | 2951.5043 | 112.1183 | 0 | 70.3415 | 415041.5633 | 27949.3172 | 376770.8224 | 232833.8649 | 0 | 149671.4399 | 0 | 468884.133 | 1219940.3326 | 832634.3443 | 3723725.8175 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 12717283.4511 | 26322667.367 | 1778.2794 | 0.18181 | 69946.8785 | 144778.4366 | 1425.9617 | 2951.5043
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.2176 | 1.4647 | 0.063766 | 4 | 53052.0487 | 106393.5019 | 1081.5378 | 2168.9754 | 113.1272 | 0 | 76.6487 | 502439.8635 | 34046.4264 | 465447.7155 | 293871.3441 | 0 | 169366.9497 | 0 | 571417.1967 | 1486710.332 | 1014710.3504 | 4538010.1783 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 13531567.8119 | 27136951.7278 | 2371.3737 | 0.25506 | 53052.0487 | 106393.5019 | 1081.5378 | 2168.9754
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4903 | 1.9561 | 0.089086 | 4 | 41119.2013 | 79299.6517 | 838.2705 | 1616.6307 | 114.0967 | 0 | 103.881 | 618667.7034 | 42167.7959 | 586250.646 | 381709.3793 | 0 | 198317.7901 | 0 | 712574.1928 | 1853971.8805 | 1265373.9038 | 5659033.2918 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 14652590.9254 | 28257974.8413 | 3162.2777 | 0.35634 | 41119.2013 | 79299.6517 | 838.2705 | 1616.6307
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1091 | 2.5211 | 0.12114 | 4 | 32729.8395 | 60807.1818 | 667.242 | 1239.6366 | 114.7306 | 0 | 100.0973 | 741760.2555 | 50741.4198 | 717878.366 | 482786.6033 | 0 | 223725.7283 | 0 | 864588.0254 | 2249480.6907 | 1535316.7936 | 6866277.8826 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 15859835.5163 | 29465219.4322 | 4216.965 | 0.48457 | 32729.8395 | 60807.1818 | 667.242 | 1239.6366
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4413 | 3.2402 | 0.16282 | 4 | 26595.9817 | 47485.619 | 542.1951 | 968.0586 | 115.229 | 0 | 99.9911 | 887047.7186 | 60837.1945 | 877173.1615 | 611296.4757 | 0 | 252594.859 | 0 | 1048690.2696 | 2728476.9657 | 1862241.5937 | 8328358.2383 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 17321915.872 | 30927299.7879 | 5623.4133 | 0.6513 | 26595.9817 | 47485.619 | 542.1951 | 968.0586
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.5829 | 4.1342 | 0.21638 | 4 | 22011.9805 | 37731.3507 | 448.744 | 769.2046 | 115.6147 | 0 | 109.4432 | 1054878.6805 | 72471.1971 | 1065662.7638 | 770899.6541 | 0 | 283541.568 | 0 | 1266507.0068 | 3295191.4354 | 2249035.8641 | 10058188.1699 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 19051745.8035 | 32657129.7194 | 7498.9421 | 0.86552 | 22011.9805 | 37731.3507 | 448.744 | 769.2046
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6908 | 5.237 | 0.2846 | 4 | 18524.5086 | 30475.9243 | 377.6472 | 621.2929 | 115.9142 | 0 | 107.0939 | 1247766.1984 | 85810.3204 | 1287303.086 | 967764.1501 | 0 | 316291.872 | 0 | 1522924.8944 | 3962338.1805 | 2704377.2261 | 12094575.9278 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 21088133.5615 | 34693517.4774 | 10000 | 1.1384 | 18524.5086 | 30475.9243 | 377.6472 | 621.2929
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.9519 | 6.5891 | 0.37072 | 4 | 15832.4492 | 25007.3144 | 322.7659 | 509.8079 | 116.1483 | 0 | 86.72 | 1468670.0218 | 101052.2452 | 1546708.1567 | 1209314.0579 | 0 | 350766.489 | 0 | 1823839.2786 | 4745255.682 | 3238734.5082 | 14484340.4396 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 23477898.0732 | 37083281.9891 | 13335.2143 | 1.4829 | 15832.4492 | 25007.3144 | 322.7659 | 509.8079
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.4498 | 8.2087 | 0.4774 | 4 | 13731.385 | 20856.1731 | 279.9329 | 425.1813 | 116.3296 | 0 | 100.5579 | 1716456.7048 | 118108.4744 | 1843783.7917 | 1498719.4733 | 0 | 385175.5664 | 0 | 2169275.1642 | 5644008.9977 | 3852152.1137 | 17227680.2862 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 26221237.9199 | 39826621.8358 | 17782.7941 | 1.9096 | 13731.385 | 20856.1731 | 279.9329 | 425.1813
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.2387 | 10.1068 | 0.60662 | 4 | 12079.3157 | 17686.3991 | 246.2532 | 360.5612 | 116.4661 | 0 | 165.2386 | 1989273.8196 | 136839.3361 | 2177399.252 | 1837920.3362 | 0 | 418076.297 | 0 | 2558208.5259 | 6655933.8237 | 4542811.6005 | 20316462.9909 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 29310020.6245 | 42915404.5404 | 23713.7371 | 2.4265 | 12079.3157 | 17686.3991 | 246.2532 | 360.5612
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.0996 | 12.2335 | 0.75718 | 4 | 10777.0636 | 15269.1791 | 219.705 | 311.2829 | 116.5544 | 0 | 153.4881 | 2277571.4888 | 156572.8493 | 2536658.6535 | 2218217.8958 | 0 | 445874.697 | 0 | 2977609.2779 | 7747128.5495 | 5287574.4226 | 23647207.8345 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 32640765.4681 | 46246149.384 | 31622.7766 | 3.0287 | 10777.0636 | 15269.1791 | 219.705 | 311.2829
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.5406 | 14.4778 | 0.92352 | 4 | 9753.4976 | 13436.5404 | 198.8382 | 273.9221 | 116.5863 | 0 | 162.7252 | 2565899.3898 | 176231.5508 | 2902500.8544 | 2620142.3192 | 0 | 464396.469 | 0 | 3404376.5275 | 8857489.3908 | 6045418.5124 | 27036455.0139 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 36030012.6475 | 49635396.5634 | 42169.6503 | 3.6941 | 9753.4976 | 13436.5404 | 198.8382 | 273.9221
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.0151 | 16.7162 | 1.0973 | 4 | 8953.913 | 12053.6774 | 182.5376 | 245.7305 | 116.5603 | 0 | 173.3565 | 2840015.7361 | 194830.3265 | 3256332.7851 | 3022078.3702 | 0 | 471754.505 | 0 | 3816154.5719 | 9928851.3952 | 6776645.0947 | 30306662.7848 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 39300220.4184 | 52905604.3343 | 56234.1325 | 4.3892 | 8953.913 | 12053.6774 | 182.5376 | 245.7305
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9614 | 18.8253 | 1.2687 | 4 | 8333.6234 | 11014.6405 | 169.8922 | 224.5483 | 116.4858 | 0 | 187.5391 | 3087741.9162 | 211544.4707 | 3581254.318 | 3402136.5118 | 0 | 467867.2775 | 0 | 4192712.3528 | 10908577.4984 | 7445328.2915 | 33297162.637 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 42290720.2706 | 55896104.1865 | 74989.4209 | 5.0747 | 8333.6234 | 11014.6405 | 169.8922 | 224.5483
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 96.9675 | 20.7182 | 1.4291 | 4 | 7855.4819 | 10235.563 | 160.1446 | 208.6658 | 116.38 | 0 | 203.2942 | 3302353.7408 | 225939.116 | 3866839.0778 | 3744623.5858 | 0 | 454759.1295 | 0 | 4521860.7134 | 11764954.0151 | 8029822.8609 | 35911152.2392 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 44904709.8729 | 58510093.7888 | 100000 | 5.7164 | 7855.4819 | 10235.563 | 160.1446 | 208.6658
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7702 | 22.3435 | 1.5722 | 4 | 7488.8891 | 9652.2781 | 152.6711 | 196.7747 | 116.2612 | 0 | 186.0251 | 3481315.5698 | 237873.6412 | 4108012.8462 | 4039911.2217 | 0 | 435230.6833 | 0 | 4797914.1453 | 12483188.4185 | 8520032.5995 | 38103479.1254 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 47097036.7591 | 60702420.675 | 133352.1432 | 6.2889 | 7488.8891 | 9652.2781 | 152.6711 | 196.7747
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3324 | 23.6988 | 1.6954 | 4 | 7209.044 | 9215.2574 | 146.9661 | 187.8655 | 116.1431 | 0 | 202.0536 | 3627059.7872 | 247541.5895 | 4306542.3557 | 4287122.7223 | 0 | 412649.8999 | 0 | 5023557.3783 | 13070265.825 | 8920724.9927 | 39895464.5506 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 48889022.1842 | 62494406.1001 | 177827.941 | 6.7816 | 7209.044 | 9215.2574 | 146.9661 | 187.8655
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.9816 | 24.8566 | 1.8022 | 4 | 6991.2857 | 8878.6247 | 142.5268 | 181.0028 | 116.0289 | 0 | 207.9807 | 3749178.89 | 255603.8861 | 4474412.7066 | 4499065.2169 | 0 | 390027.6013 | 0 | 5213632.4374 | 13564802.139 | 9258256.1887 | 41404979.0659 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 50398536.6996 | 64003920.6155 | 237137.3706 | 7.2088 | 6991.2857 | 8878.6247 | 142.5268 | 181.0028
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.2398 | 25.7238 | 1.8851 | 4 | 6831.1896 | 8635.5607 | 139.263 | 176.0476 | 115.9355 | 0 | 187.5777 | 3839293.7199 | 261531.5733 | 4599157.4481 | 4658612.4386 | 0 | 368155.1319 | 0 | 5353432.6216 | 13928533.5413 | 9506510.3447 | 42515226.8193 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 51508784.453 | 65114168.3689 | 316227.766 | 7.5402 | 6831.1896 | 8635.5607 | 139.263 | 176.0476
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.5527 | 26.395 | 1.9507 | 4 | 6710.0229 | 8453.6956 | 136.7929 | 172.34 | 115.8587 | 0 | 203.4911 | 3908272.9147 | 266055.5838 | 4695163.3638 | 4782565.2028 | 0 | 348362.5693 | 0 | 5460163.6574 | 14206225.803 | 9696041.0193 | 43362850.1142 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 52356407.7478 | 65961791.6637 | 421696.5034 | 7.8027 | 6710.0229 | 8453.6956 | 136.7929 | 172.34
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.1083 | 26.9106 | 2.002 | 4 | 6618.4835 | 8317.486 | 134.9267 | 169.5632 | 115.797 | 0 | 185.3642 | 3960806.817 | 269492.4104 | 4768601.153 | 4878003.5975 | 0 | 331286.7295 | 0 | 5541194.3759 | 14417051.1107 | 9839933.6239 | 44006369.8178 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 52999927.4515 | 66605311.3674 | 562341.3252 | 8.0079 | 6618.4835 | 8317.486 | 134.9267 | 169.5632
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.0692 | 27.3049 | 2.0417 | 4 | 6549.4257 | 8215.3769 | 133.5189 | 167.4816 | 115.7482 | 0 | 168.4322 | 4000719.3547 | 272098.4 | 4824584.2454 | 4951122.8756 | 0 | 317064.8334 | 0 | 5602579.9865 | 14576763.8778 | 9948940.8691 | 44493874.4424 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53487432.0761 | 67092815.992 | 749894.2093 | 8.1667 | 6549.4257 | 8215.3769 | 133.5189 | 167.4816
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.565 | 27.605 | 2.0722 | 4 | 6497.3897 | 8138.8107 | 132.4581 | 165.9207 | 115.7101 | 0 | 209.3508 | 4030933.8065 | 274068.1601 | 4867074.4802 | 5006830.6853 | 0 | 305506.23 | 0 | 5648921.2113 | 14697334.2386 | 10031232.6179 | 44861901.43 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 53855459.0636 | 67460842.9795 | 1000000 | 8.2888 | 6497.3897 | 8138.8107 | 132.4581 | 165.9207
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 132.1384 | 27.9199 | 2.1004 | 4 | 6458.2474 | 8077.6424 | 131.6601 | 164.6737 | 115.6695 | 0 | 170.1333 | 4062511.3657 | 276124.0804 | 4911581.3922 | 5065375.9862 | 0 | 299147.5483 | 0 | 5699748.7454 | 14829577.0563 | 10121491.0582 | 45265557.2327 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 54259114.8663 | 67864498.7822 | 1333521.4322 | 8.4015 | 6458.2474 | 8077.6424 | 131.6601 | 164.6737
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.3091 | 28.356 | 2.133 | 4 | 6428.3907 | 8022.987 | 131.0514 | 163.5594 | 115.6186 | 0 | 204.3456 | 4106176.3011 | 278973.4189 | 4973038.772 | 5146286.6588 | 0 | 300458.4808 | 0 | 5773924.1163 | 15022566.156 | 10253210.0844 | 45854633.9884 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 54848191.622 | 68453575.5379 | 1778279.41 | 8.5322 | 6428.3907 | 8022.987 | 131.0514 | 163.5594
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.9935 | 28.4935 | 2.1471 | 4 | 6405.9246 | 7990.1138 | 130.5934 | 162.8893 | 115.603 | 0 | 191.1338 | 4119906.3777 | 279869.4073 | 4992377.4287 | 5171797.4856 | 0 | 295022.0444 | 0 | 5794999.37 | 15077399.643 | 10290635.066 | 46022006.8227 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55015564.4564 | 68620948.3723 | 2371373.7057 | 8.5882 | 6405.9246 | 7990.1138 | 130.5934 | 162.8893
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.5077 | 28.5967 | 2.1576 | 4 | 6389.0455 | 7965.4727 | 130.2493 | 162.3869 | 115.5911 | 0 | 187.3095 | 4130197.8247 | 280540.7147 | 5006884.011 | 5190956.8826 | 0 | 290818.8966 | 0 | 5810765.3486 | 15118419.4851 | 10318631.951 | 46147215.1143 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55140772.748 | 68746156.6639 | 3162277.6602 | 8.6305 | 6389.0455 | 7965.4727 | 130.2493 | 162.3869
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.9 | 28.6755 | 2.1657 | 4 | 6376.3695 | 7946.9487 | 129.9909 | 162.0093 | 115.5821 | 0 | 198.1414 | 4138036.9087 | 281051.8922 | 5017940.2194 | 5205572.3682 | 0 | 287634.3753 | 0 | 5822791.9479 | 15149710.2295 | 10339988.5271 | 46242726.4682 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55236284.1019 | 68841668.0178 | 4216965.0343 | 8.6627 | 6376.3695 | 7946.9487 | 129.9909 | 162.0093
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.1922 | 28.7341 | 2.1717 | 4 | 6366.8534 | 7933.079 | 129.7969 | 161.7265 | 115.5753 | 0 | 194.6773 | 4143868.8649 | 281432.0941 | 5026169.2228 | 5216457.9047 | 0 | 285189.4115 | 0 | 5831715.8242 | 15172928.3252 | 10355835.3544 | 46313597.0018 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55307154.6354 | 68912538.5513 | 5623413.2519 | 8.6867 | 6366.8534 | 7933.079 | 129.7969 | 161.7265
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4091 | 28.7776 | 2.1762 | 4 | 6359.7112 | 7922.6996 | 129.6513 | 161.5149 | 115.5703 | 0 | 197.123 | 4148192.665 | 281713.9232 | 5032272.2027 | 5224535.172 | 0 | 283315.8345 | 0 | 5838311.621 | 15190089.2354 | 10367548.0283 | 46365978.682 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55359536.3157 | 68964920.2316 | 7498942.0933 | 8.7047 | 6359.7112 | 7922.6996 | 129.6513 | 161.5149
1 | 2600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.5749 | 28.8108 | 2.1796 | 4 | 6354.352 | 7914.8922 | 129.5421 | 161.3558 | 115.5664 | 0 | 197.0952 | 4151495.1209 | 281929.1515 | 5036934.7021 | 5230708.2921 | 0 | 281916.9227 | 0 | 5843363.8338 | 15203234.0569 | 10376519.639 | 46406101.719 | 961560.8286 | 8031996.805 | 8031996.805 | 1478867.319 | 4094519.7919 | 0 | 55399659.3526 | 69005043.2685 | 10000000 | 8.7184 | 6354.352 | 7914.8922 | 129.5421 | 161.3558
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.968 | [19 empty] | 100 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3087 | [19 empty] | 133.3521 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0393 | [19 empty] | 177.8279 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0838 | [19 empty] | 237.1374 | 0
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0109 | 0.15082 | 0.0018706 | 4 | 1368929.0465 | 3254369.472 | 27907.4702 | 66344.7235 | 95.4271 | 0 | 34.4195 | 92105.8313 | 5572.7291 | 76496.9397 | 56796.1379 | 0 | 56564.7908 | 0 | 112139.2073 | 291763.2144 | 199134.389 | 890573.2395 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10242617.7459 | 24349883.2836 | 316.2278 | 0.0074822 | 1368929.0465 | 3254369.472 | 27907.4702 | 66344.7235
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4958 | 0.25467 | 0.0052099 | 4 | 510179.7627 | 1187118.4392 | 10400.7045 | 24201.0151 | 102.6783 | 0 | 240.6046 | 139296.7599 | 8820.2638 | 115695.6466 | 75421.0952 | 0 | 74035.2312 | 0 | 161174.9087 | 419344.0509 | 286210.9314 | 1279998.8876 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 10632043.394 | 24739308.9317 | 421.6965 | 0.02084 | 510179.7627 | 1187118.4392 | 10400.7045 | 24201.0151
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.38362 | 0.010269 | 4 | 269320.445 | 612749.3421 | 5490.4616 | 12491.7241 | 107.3422 | 0 | 361.4916 | 190790.242 | 12441.1367 | 160025.2327 | 98226.2131 | 0 | 90947.5797 | 0 | 215447.8576 | 560551.1311 | 382587.6652 | 1711017.0582 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11063061.5645 | 25170327.1022 | 562.3413 | 0.041078 | 269320.445 | 612749.3421 | 5490.4616 | 12491.7241
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7989 | 0.54518 | 0.017456 | 4 | 165494.5886 | 367538.4719 | 3373.831 | 7492.7689 | 110.6021 | 0 | 505.5558 | 248566.0276 | 16547.2562 | 211485.8034 | 126619.6567 | 0 | 108136.5296 | 0 | 277428.5567 | 721812.196 | 492651.6555 | 2203247.6817 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 11555292.188 | 25662557.7257 | 749.8942 | 0.069823 | 165494.5886 | 367538.4719 | 3373.831 | 7492.7689
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7 | 0.74919 | 0.027303 | 4 | 111058.4337 | 240229.6471 | 2264.0764 | 4897.4063 | 112.9895 | 0 | 86.7943 | 314582.1864 | 21259.6624 | 272263.6242 | 162225.1863 | 0 | 126288.6675 | 0 | 349681.5375 | 909799.6309 | 620956.9426 | 2777057.4378 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12129101.9442 | 26236367.4819 | 1000 | 0.10921 | 111058.4337 | 240229.6471 | 2264.0764 | 4897.4063
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8548 | 1.0119 | 0.040612 | 4 | 78912.5721 | 165753.7453 | 1608.7395 | 3379.1143 | 114.8028 | 0 | 86.6847 | 392104.54 | 26805.2759 | 345838.8348 | 208093.1363 | 0 | 146610.4145 | 0 | 436586.3586 | 1135908.1489 | 775280.6522 | 3467227.3611 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 12819271.8675 | 26926537.4052 | 1333.5214 | 0.16245 | 78912.5721 | 165753.7453 | 1608.7395 | 3379.1143
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3091 | 1.3432 | 0.058217 | 4 | 58546.3324 | 119126.5496 | 1193.5462 | 2428.5558 | 116.1517 | 0 | 84.7023 | 481531.8749 | 33195.3811 | 433363.1892 | 265678.9263 | 0 | 168614.0226 | 0 | 539129.5237 | 1402704.43 | 957374.5962 | 4281591.9441 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 13633636.4504 | 27740901.9881 | 1778.2794 | 0.23287 | 58546.3324 | 119126.5496 | 1193.5462 | 2428.5558
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.9876 | 1.724 | 0.080567 | 4 | 45022.5763 | 88797.2903 | 917.8461 | 1810.2529 | 117.0244 | 0 | 84.0064 | 576227.2301 | 39938.4187 | 528823.3587 | 332252.9079 | 0 | 187900.8059 | 0 | 649405.6613 | 1689620.3194 | 1153200.5862 | 5157369.2882 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 14509413.7946 | 28616679.3323 | 2371.3737 | 0.32227 | 45022.5763 | 88797.2903 | 917.8461 | 1810.2529
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5498 | 2.3135 | 0.11251 | 4 | 35138.4754 | 66483.8993 | 716.3454 | 1355.3642 | 118.051 | 0 | 74.7673 | 712118.6727 | 49655.8344 | 668616.6401 | 434467.9951 | 0 | 221607.0999 | 0 | 813721.8344 | 2117137.2959 | 1444989.7073 | 6462315.0797 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 15814359.586 | 29921625.1237 | 3162.2777 | 0.45006 | 35138.4754 | 66483.8993 | 716.3454 | 1355.3642
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4929 | 2.9872 | 0.15242 | 4 | 28227.4302 | 51365.7286 | 575.4543 | 1047.1599 | 118.6701 | 0 | 74.4712 | 854805.4287 | 59806.3915 | 819938.8132 | 551460.9926 | 0 | 251084.65 | 0 | 989467.5476 | 2574391.5913 | 1757075.1595 | 7858030.5744 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 17210075.0808 | 31317340.6185 | 4216.965 | 0.60969 | 28227.4302 | 51365.7286 | 575.4543 | 1047.1599
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.1781 | 3.8311 | 0.20404 | 4 | 23123.1611 | 40408.1017 | 471.3969 | 823.7738 | 119.1498 | 0 | 105.8049 | 1020685.4028 | 71579.5724 | 1000215.9346 | 698077.165 | 0 | 283177.6804 | 0 | 1198756.9445 | 3118919.6708 | 2128726.7627 | 9520139.1331 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 18872183.6395 | 32979449.1772 | 5623.4133 | 0.81616 | 23123.1611 | 40408.1017 | 471.3969 | 823.7738
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7413 | 4.8767 | 0.27017 | 4 | 19277.8637 | 32331.6995 | 393.0053 | 659.1254 | 119.521 | 0 | 95.6183 | 1211855.6972 | 85115.9883 | 1212883.6559 | 879831.2108 | 0 | 317314.0109 | 0 | 1445730.2196 | 3761493.4713 | 2567296.5851 | 11481520.8391 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 20833565.3454 | 34940830.8832 | 7498.9421 | 1.0807 | 19277.8637 | 32331.6995 | 393.0053 | 659.1254
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.3413 | 6.1601 | 0.35404 | 4 | 16334.4769 | 26296.2176 | 333.0004 | 536.084 | 119.8092 | 0 | 132.7674 | 1430691.6883 | 100572.3532 | 1461848.6729 | 1102915.688 | 0 | 353054.2311 | 0 | 1735142.2271 | 4514484.1483 | 3081228.1946 | 13779937.2034 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 23131981.7098 | 37239247.2475 | 10000 | 1.4161 | 16334.4769 | 26296.2176 | 333.0004 | 536.084
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.1649 | 7.7243 | 0.45928 | 4 | 14050.9251 | 21729.9197 | 286.4471 | 442.9938 | 120.0344 | 0 | 134.2821 | 1680031.136 | 118138.7434 | 1751652.1921 | 1374759.777 | 0 | 390206.6086 | 0 | 2072767.4983 | 5392915.8474 | 3680775.8792 | 16461247.6819 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 25813292.1882 | 39920557.7259 | 13335.2143 | 1.8371 | 14050.9251 | 21729.9197 | 286.4471 | 442.9938
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.2935 | 9.5873 | 0.58877 | 4 | 12261.0122 | 18251.1796 | 249.9573 | 372.075 | 120.2081 | 0 | 128.0815 | 1958467.6239 | 137705.1315 | 2081925.785 | 1698471.623 | 0 | 426918.0196 | 0 | 2458360.3914 | 6396149.4594 | 4365503.4337 | 19523501.4675 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 28875545.9739 | 42982811.5116 | 17782.7941 | 2.3551 | 12261.0122 | 18251.1796 | 249.9573 | 372.075
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.7017 | 11.7423 | 0.74379 | 4 | 10849.6491 | 15591.3063 | 221.1848 | 317.8499 | 120.3332 | 0 | 138.2745 | 2261428.1446 | 158933.8223 | 2448341.3775 | 2073023.0611 | 0 | 460823.0396 | 0 | 2886994.2836 | 7511366.9219 | 5126662.2673 | 22927572.9178 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 32279617.4241 | 46386882.9618 | 23713.7371 | 2.9752 | 10849.6491 | 15591.3063 | 221.1848 | 317.8499
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.0371 | 14.1042 | 0.92104 | 4 | 9736.5054 | 13565.6851 | 198.4918 | 276.5548 | 120.4017 | 0 | 161.4626 | 2575088.9382 | 180833.1119 | 2834845.6036 | 2483984.609 | 0 | 487247.3463 | 0 | 3339179.8475 | 8687861.0032 | 5929643.6524 | 26518684.1119 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 35870728.6183 | 49977994.156 | 31622.7766 | 3.6841 | 9736.5054 | 13565.6851 | 198.4918 | 276.5548
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.783 | 16.5484 | 1.113 | 4 | 8862.5162 | 12031.1916 | 180.6744 | 245.2721 | 120.4061 | 0 | 164.8269 | 2883261.1655 | 202248.316 | 3221467.8559 | 2910184.8064 | 0 | 502668.3416 | 0 | 3790733.8893 | 9862711.9935 | 6731503.594 | 30104779.9622 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 39456824.4685 | 53564090.0062 | 42169.6503 | 4.4521 | 8862.5162 | 12031.1916 | 180.6744 | 245.2721
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.3212 | 18.9282 | 1.309 | 4 | 8180.8673 | 10875.0817 | 166.778 | 221.7032 | 120.3494 | 0 | 170.5477 | 3169836.8153 | 222048.6621 | 3587179.2726 | 3326542.5041 | 0 | 505282.7125 | 0 | 4216247.0869 | 10969810.049 | 7487120.7655 | 33484067.868 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 42836112.3744 | 56943377.9121 | 56234.1325 | 5.2361 | 8180.8673 | 10875.0817 | 166.778 | 221.7032
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.1696 | 21.1324 | 1.4987 | 4 | 7652.8163 | 10006.0784 | 156.013 | 203.9874 | 120.2465 | 0 | 205.7792 | 3424957.1597 | 239563.1557 | 3917926.4967 | 3713797.7001 | 0 | 496405.9109 | 0 | 4599133.665 | 11966002.3844 | 8167042.5041 | 36524828.9766 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 45876873.4829 | 59984139.0207 | 74989.4209 | 5.9948 | 7652.8163 | 10006.0784 | 156.013 | 203.9874
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.9586 | 23.0806 | 1.6732 | 4 | 7246.1933 | 9354.0593 | 147.7235 | 190.6952 | 120.1172 | 0 | 200.8489 | 3643038.7226 | 254436.8649 | 4204688.0688 | 4057630.6017 | 0 | 478623.2947 | 0 | 4928982.8456 | 12824202.2907 | 8752781.5744 | 39144384.2634 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 48496428.7698 | 62603694.3075 | 100000 | 6.6927 | 7246.1933 | 9354.0593 | 147.7235 | 190.6952
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.5102 | 24.7384 | 1.8269 | 4 | 6934.6314 | 8865.0989 | 141.3718 | 180.727 | 119.9802 | 0 | 197.8177 | 3823592.5283 | 266674.0814 | 4445043.1403 | 4351528.7968 | 0 | 455343.3187 | 0 | 5203450.9275 | 13538311.9389 | 9240176.0828 | 41324120.8146 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 50676165.3209 | 64783430.8586 | 133352.1432 | 7.3077 | 6934.6314 | 8865.0989 | 141.3718 | 180.727
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7829 | 26.1028 | 1.9574 | 4 | 6696.8586 | 8498.625 | 136.5245 | 173.256 | 119.8495 | 0 | 225.1056 | 3968930.7905 | 276469.5845 | 4640523.2912 | 4594254.4919 | 0 | 429646.8445 | 0 | 5424831.751 | 14114299.4302 | 9633299.3809 | 43082255.5648 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 52434300.0711 | 66541565.6088 | 177827.941 | 7.8297 | 6696.8586 | 8498.625 | 136.5245 | 173.256
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.8675 | 27.2001 | 2.0651 | 4 | 6516.003 | 8223.84 | 132.8375 | 167.6541 | 119.7328 | 0 | 193.9756 | 4083786.444 | 284172.613 | 4796332.3228 | 4790170.1462 | 0 | 404119.7132 | 0 | 5599846.6833 | 14569652.3834 | 9944087.1281 | 44472167.4338 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 53824211.9402 | 67931477.4779 | 237137.3706 | 8.2603 | 6516.003 | 8223.84 | 132.8375 | 167.6541
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.1593 | 28.1201 | 2.1558 | 4 | 6375.4717 | 8011.4046 | 129.9726 | 163.3233 | 119.6272 | 0 | 190.1339 | 4178731.5431 | 290513.4758 | 4926046.4163 | 4954934.5215 | 0 | 380905.8609 | 0 | 5745141.4089 | 14947679.4554 | 10202098.3724 | 45626051.0545 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 54978095.5608 | 69085361.0985 | 316227.766 | 8.6234 | 6375.4717 | 8011.4046 | 129.9726 | 163.3233
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.2728 | 28.7838 | 2.2237 | 4 | 6272.5824 | 7858.5659 | 127.8751 | 160.2075 | 119.5466 | 0 | 190.057 | 4246476.1693 | 295021.9422 | 5019126.0949 | 5074103.307 | 0 | 359959.9006 | 0 | 5847928.0915 | 15215109.319 | 10384624.7494 | 46442349.5739 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 55794394.0803 | 69901659.618 | 421696.5034 | 8.895 | 6272.5824 | 7858.5659 | 127.8751 | 160.2075
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.6692 | 29.2925 | 2.2766 | 4 | 6194.8422 | 7744.0003 | 126.2902 | 157.8719 | 119.4824 | 0 | 199.1658 | 4297981.0943 | 298440.5477 | 5090192.4547 | 5165617.4775 | 0 | 342105.6129 | 0 | 5925791.503 | 15417693.9438 | 10522892.9186 | 47060715.5526 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 56412760.059 | 70520025.5967 | 562341.3252 | 9.1064 | 6194.8422 | 7744.0003 | 126.2902 | 157.8719
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.3091 | 30.0646 | 2.3397 | 4 | 6135.8711 | 7643.2279 | 125.088 | 155.8175 | 119.388 | 0 | 204.4411 | 4375666.1256 | 303594.937 | 5197600.4069 | 5304571.8023 | 0 | 339806.6703 | 0 | 6053283.5774 | 15749402.1691 | 10749290.5983 | 48073216.2868 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57425260.7931 | 71532526.3308 | 749894.2093 | 9.3589 | 6135.8711 | 7643.2279 | 125.088 | 155.8175
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8024 | 30.3818 | 2.3727 | 4 | 6090.9955 | 7577.4236 | 124.1732 | 154.476 | 119.3517 | 0 | 207.4907 | 4407443.9564 | 305705.2084 | 5241559.4619 | 5361619.6059 | 0 | 328454.2622 | 0 | 6101465.173 | 15874760.7974 | 10834850.438 | 48455858.9031 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 57807903.4094 | 71915168.9471 | 1000000 | 9.4907 | 6090.9955 | 7577.4236 | 124.1732 | 154.476
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.9233 | 30.6196 | 2.3977 | 4 | 6057.2062 | 7528.1478 | 123.4843 | 153.4715 | 119.3241 | 0 | 190.5752 | 4431177.9929 | 307279.7109 | 5274447.8714 | 5404406.807 | 0 | 319342.9909 | 0 | 6137295.5956 | 15967984.2072 | 10898477.3307 | 48740412.5067 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58092457.0131 | 72199722.5508 | 1333521.4322 | 9.5906 | 6057.2062 | 7528.1478 | 123.4843 | 153.4715
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7735 | 30.7997 | 2.4167 | 4 | 6031.787 | 7491.1634 | 122.9661 | 152.7175 | 119.303 | 0 | 172.9498 | 4449110.2696 | 308468.4129 | 5299328.919 | 5436836.9945 | 0 | 312215.269 | 0 | 6164324.3474 | 16038307.4751 | 10946474.406 | 48955066.0935 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58307110.5999 | 72414376.1376 | 1778279.41 | 9.6666 | 6031.787 | 7491.1634 | 122.9661 | 152.7175
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2411 | 31.3214 | 2.4536 | 4 | 6013.0544 | 7450.4758 | 122.5842 | 151.888 | 119.2412 | 0 | 166.8091 | 4500849.4892 | 311894.2342 | 5371261.2373 | 5530876.901 | 0 | 319256.1269 | 0 | 6253313.8156 | 16269839.8172 | 11104499.987 | 49661791.6085 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 59013836.1149 | 73121101.6526 | 2371373.7057 | 9.8143 | 6013.0544 | 7450.4758 | 122.5842 | 151.888
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.2 | 31.7345 | 2.4831 | 4 | 5997.7084 | 7418.0611 | 122.2714 | 151.2272 | 119.1913 | 0 | 216.8017 | 4541574.6031 | 314586.1133 | 5428044.044 | 5605417.3741 | 0 | 324276.756 | 0 | 6323420.5673 | 16452243.2042 | 11228994.0467 | 50218556.7087 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 59570601.2151 | 73677866.7528 | 3162277.6602 | 9.9322 | 5997.7084 | 7418.0611 | 122.2714 | 151.2272
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.264 | 31.1149 | 2.4501 | 4 | 5987.5395 | 7426.9852 | 122.0641 | 151.4091 | 119.2656 | 0 | 221.9296 | 4480407.8899 | 310541.1729 | 5342821.2127 | 5493650.3399 | 0 | 299188.1959 | 0 | 6211377.4364 | 16160729.9609 | 11030030.2681 | 49328746.4769 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58680790.9832 | 72788056.521 | 4216965.0343 | 9.8005 | 5987.5395 | 7426.9852 | 122.0641 | 151.4091
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5413 | 31.1735 | 2.4563 | 4 | 5979.4453 | 7415.2499 | 121.8991 | 151.1699 | 119.2586 | 0 | 235.5173 | 4486209.7407 | 310925.1468 | 5350893.0273 | 5504211.9271 | 0 | 296737.2968 | 0 | 6220101.0841 | 16183427.1027 | 11045521.5337 | 49398026.8592 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58750071.3656 | 72857336.9033 | 5623413.2519 | 9.8253 | 5979.4453 | 7415.2499 | 121.8991 | 151.1699
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.7413 | 31.2158 | 2.4609 | 4 | 5973.3703 | 7406.5086 | 121.7752 | 150.9917 | 119.2536 | 0 | 210.5484 | 4490391.7536 | 311201.8628 | 5356713.1262 | 5511830.6993 | 0 | 294822.0024 | 0 | 6226334.1833 | 16199644.3482 | 11056590.137 | 49447528.1128 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58799572.6192 | 72906838.1569 | 7498942.0933 | 9.8436 | 5973.3703 | 7406.5086 | 121.7752 | 150.9917
1 | 2700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.8922 | 31.2477 | 2.4643 | 4 | 5968.8118 | 7399.9475 | 121.6823 | 150.8579 | 119.2497 | 0 | 216.6009 | 4493545.4939 | 311410.511 | 5361103.188 | 5517579.3711 | 0 | 293378.7932 | 0 | 6231036.7693 | 16211879.5124 | 11064940.8881 | 49484874.5271 | 961560.8286 | 8390483.6777 | 8390483.6777 | 1478867.319 | 4237914.541 | 0 | 58836919.0335 | 72944184.5712 | 10000000 | 9.8574 | 5968.8118 | 7399.9475 | 121.6823 | 150.8579
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1741 | [19 empty] | 100 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6667 | [19 empty] | 133.3521 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7325 | [19 empty] | 177.8279 | 0
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.77197 | 0.10575 | 0.00052649 | 4 | 4949436.0041 | 11890405.0857 | 100900.9476 | 242401.9906 | 91.051 | 0 | 55.8697 | 69680.7771 | 4096.4619 | 57775.7421 | 48086.7671 | 0 | 48590.1022 | 0 | 89009.6416 | 231584.8291 | 158061.4045 | 706885.7256 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10423277.1955 | 25040628.4823 | 237.1374 | 0.002106 | 4949436.0041 | 11890405.0857 | 100900.9476 | 242401.9906
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2083 | 0.2009 | 0.003182 | 4 | 849248.0514 | 1997675.7865 | 17313.0702 | 40725.323 | 101.3359 | 0 | 60.4791 | 117157.5297 | 7346.9236 | 95795.2951 | 65105.6584 | 0 | 67474.4219 | 0 | 137623.1332 | 358067.1622 | 244388.1958 | 1092958.3199 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 10809349.7899 | 25426701.0766 | 316.2278 | 0.012728 | 849248.0514 | 1997675.7865 | 17313.0702 | 40725.323
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.32054 | 0.0075605 | 4 | 371450.2436 | 854793.9508 | 7572.5156 | 17426.1309 | 107.6203 | 0 | 296.0198 | 168770.9277 | 11008.3622 | 138575.2911 | 85893.2301 | 0 | 85560.7346 | 0 | 191025.3328 | 497008.7313 | 339218.6716 | 1517061.2813 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11233452.7512 | 25850804.0379 | 421.6965 | 0.030242 | 371450.2436 | 854793.9508 | 7572.5156 | 17426.1309
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3515 | 0.46708 | 0.014009 | 4 | 208804.0697 | 469661.2737 | 4256.7534 | 9574.6803 | 111.7919 | 0 | 413.5909 | 224905.6622 | 15060.7165 | 186719.1371 | 111091.1974 | 0 | 102829.1971 | 0 | 249836.305 | 650022.8171 | 443653.9293 | 1984118.9617 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 11700510.4316 | 26317861.7184 | 562.3413 | 0.056036 | 208804.0697 | 469661.2737 | 4256.7534 | 9574.6803
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1295 | 0.65251 | 0.023019 | 4 | 132962.4267 | 291712.2435 | 2710.6189 | 5946.9487 | 114.8225 | 0 | 561.6759 | 288914.9244 | 19720.815 | 243453.2267 | 142715.5631 | 0 | 120921.6473 | 0 | 318133.2088 | 827717.3512 | 564934.1001 | 2526510.8365 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12242902.3064 | 26860253.5932 | 749.8942 | 0.092078 | 132962.4267 | 291712.2435 | 2710.6189 | 5946.9487
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.158 | 0.89951 | 0.035382 | 4 | 91260.8179 | 194544.5387 | 1860.4752 | 3966.0536 | 117.1717 | 0 | 68.0388 | 366237.4252 | 25372.2285 | 314220.6782 | 184690.0541 | 0 | 142460.6434 | 0 | 402862.6015 | 1048165.8505 | 715394.7306 | 3199404.212 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 12915795.682 | 27533146.9687 | 1000 | 0.14153 | 91260.8179 | 194544.5387 | 1860.4752 | 3966.0536
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4421 | 1.209 | 0.051923 | 4 | 65966.5047 | 136346.6816 | 1344.8164 | 2779.6115 | 118.898 | 0 | 73.3442 | 454573.6189 | 31835.0867 | 397610.5018 | 237163.2724 | 0 | 165208.2946 | 0 | 501692.402 | 1305300.7188 | 890894.5619 | 3984278.4572 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 13700669.9271 | 28318021.2139 | 1333.5214 | 0.20769 | 65966.5047 | 136346.6816 | 1344.8164 | 2779.6115
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0085 | 1.5868 | 0.073555 | 4 | 49613.5017 | 99295.5035 | 1011.4383 | 2024.2731 | 120.1294 | 0 | 74.918 | 553490.8296 | 39060.5873 | 493805.4599 | 301366.0647 | 0 | 188126.6563 | 0 | 614581.3432 | 1599014.587 | 1091360.3121 | 4880805.8401 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 14597197.3101 | 29214548.5968 | 1778.2794 | 0.29422 | 49613.5017 | 99295.5035 | 1011.4383 | 2024.2731
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3495 | 2.1549 | 0.10371 | 4 | 38295.1673 | 73532.4248 | 780.6988 | 1499.0579 | 121.3034 | 0 | 104.6838 | 690150.8363 | 49050.9208 | 630256.8158 | 397590.4734 | 0 | 224864.7153 | 0 | 776846.367 | 2021194.8939 | 1379507.0465 | 6169462.0691 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 15885853.539 | 30503204.8257 | 2371.3737 | 0.41483 | 38295.1673 | 73532.4248 | 780.6988 | 1499.0579
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.707 | 2.7269 | 0.14077 | 4 | 30336.1732 | 56295.7122 | 618.4439 | 1147.6642 | 121.9992 | 0 | 99.4845 | 817079.6187 | 58304.889 | 760503.1571 | 494588.6363 | 0 | 247554.3827 | 0 | 927431.9667 | 2412987.7349 | 1646913.711 | 7365364.0965 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 17081755.5664 | 31699106.8531 | 3162.2777 | 0.56308 | 30336.1732 | 56295.7122 | 618.4439 | 1147.6642
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.9519 | 3.513 | 0.18971 | 4 | 24587.496 | 43849.9923 | 501.2494 | 893.9414 | 122.5964 | 0 | 94.2258 | 979001.4127 | 70065.1361 | 930970.9783 | 626753.1061 | 0 | 280230.7877 | 0 | 1125938.3541 | 2929460.6357 | 1999417.0783 | 8941837.4889 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 18658228.9588 | 33275580.2456 | 4216.965 | 0.75885 | 24587.496 | 43849.9923 | 501.2494 | 893.9414
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0151 | 4.4979 | 0.25291 | 4 | 20300.5549 | 34749.5673 | 413.8543 | 708.4169 | 123.0602 | 0 | 95.5288 | 1167427.2038 | 83718.0608 | 1134143.6555 | 792468.9551 | 0 | 315877.8695 | 0 | 1362517.9404 | 3544992.1901 | 2419530.012 | 10820675.8872 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 20537067.3571 | 35154418.6439 | 5623.4133 | 1.0117 | 20300.5549 | 34749.5673 | 413.8543 | 708.4169
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0038 | 5.7083 | 0.3336 | 4 | 17040.7753 | 27994.9989 | 347.3993 | 570.7159 | 123.4173 | 0 | 136.1015 | 1383220.9676 | 99328.6878 | 1372003.8141 | 997097.1358 | 0 | 353001.5054 | 0 | 1639814.3232 | 4266460.4968 | 2911946.9561 | 13022873.8868 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 22739265.3568 | 37356616.6435 | 7498.9421 | 1.3344 | 17040.7753 | 27994.9989 | 347.3993 | 570.7159
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.1212 | 7.1928 | 0.43562 | 4 | 14530.8785 | 22919.6764 | 296.2316 | 467.2486 | 123.6958 | 0 | 115.0945 | 1630290.1348 | 117154.5059 | 1650392.9732 | 1248063.5797 | 0 | 391929.9995 | 0 | 1964754.1653 | 5111887.3116 | 3488968.1289 | 15603440.7988 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 25319832.2687 | 39937183.5555 | 10000 | 1.7425 | 14530.8785 | 22919.6764 | 296.2316 | 467.2486
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.5265 | 8.9903 | 0.5629 | 4 | 12573.8785 | 19065.8287 | 256.3355 | 388.6827 | 123.913 | 0 | 130.9286 | 1910229.669 | 137298.2266 | 1972511.0807 | 1551903.4369 | 0 | 431796.1605 | 0 | 2341458.0438 | 6091993.5308 | 4157910.7627 | 18595100.9111 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 28311492.3811 | 42928843.6678 | 13335.2143 | 2.2516 | 12573.8785 | 19065.8287 | 256.3355 | 388.6827
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2908 | 11.1172 | 0.71839 | 4 | 11034.2917 | 16121.1428 | 224.949 | 328.6513 | 124.0779 | 0 | 134.5676 | 2221109.3823 | 159605.2 | 2337480.4321 | 1911403.275 | 0 | 470648.0798 | 0 | 2769096.084 | 7204619.9909 | 4917301.1839 | 21991263.628 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 31707655.098 | 46325006.3847 | 17782.7941 | 2.8736 | 11034.2917 | 16121.1428 | 224.949 | 328.6513
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.2519 | 13.5315 | 0.90168 | 4 | 9818.3302 | 13871.1603 | 200.1599 | 282.7824 | 124.1874 | 0 | 129.0304 | 2553461.0418 | 183373.5102 | 2735233.5224 | 2319628.1034 | 0 | 504492.9028 | 0 | 3235513.7414 | 8418143.06 | 5745555.614 | 25695401.4958 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 35411792.9657 | 50029144.2525 | 23713.7371 | 3.6067 | 9818.3302 | 13871.1603 | 200.1599 | 282.7824
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.9876 | 16.1244 | 1.1073 | 4 | 8859.635 | 12159.7624 | 180.6156 | 247.8932 | 124.2312 | 0 | 157.1463 | 2891172.0262 | 207420.5662 | 3146971.1929 | 2758734.839 | 0 | 528614.9757 | 0 | 3717836.304 | 9673047.4299 | 6602053.6322 | 29525850.9662 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 39242242.4361 | 53859593.7228 | 31622.7766 | 4.4293 | 8859.635 | 12159.7624 | 180.6156 | 247.8932
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.9297 | 18.7508 | 1.3255 | 4 | 8108.0094 | 10864.9865 | 165.2927 | 221.4974 | 124.2043 | 0 | 171.6139 | 3216532.6111 | 230458.3034 | 3550821.3872 | 3204712.1195 | 0 | 539849.7996 | 0 | 4189525.9461 | 10900287.1219 | 7439669.9392 | 33271857.228 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 42988248.698 | 57605599.9847 | 42169.6503 | 5.3019 | 8108.0094 | 10864.9865 | 165.2927 | 221.4974
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4903 | 21.2637 | 1.544 | 4 | 7522.7192 | 9889.5284 | 153.3608 | 201.6114 | 124.1154 | 0 | 185.024 | 3514429.333 | 251410.7515 | 3926911.9755 | 3633054.1336 | 0 | 537518.301 | 0 | 4626696.5529 | 12037715.3648 | 8215988.0868 | 36743724.4992 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 46460115.9692 | 61077467.2559 | 56234.1325 | 6.176 | 7522.7192 | 9889.5284 | 153.3608 | 201.6114
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.2003 | 23.5509 | 1.7515 | 4 | 7069.8812 | 9156.2822 | 144.1291 | 186.6632 | 123.9839 | 0 | 169.239 | 3775518.9112 | 269641.3954 | 4261727.2397 | 4024641.5493 | 0 | 523499.8663 | 0 | 5013461.2952 | 13043997.8877 | 8902796.5857 | 39815284.7305 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 49531676.2004 | 64149027.4872 | 74989.4209 | 7.006 | 7069.8812 | 9156.2822 | 144.1291 | 186.6632
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.7434 | 25.5419 | 1.9392 | 4 | 6721.4914 | 8605.9207 | 137.0267 | 175.4433 | 123.8323 | 0 | 202.4782 | 3995697.5852 | 284901.5371 | 4548082.9089 | 4366857.6959 | 0 | 500989.2119 | 0 | 5341646.2862 | 13897867.9144 | 9485580.4242 | 42421623.5639 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 52138015.0338 | 66755366.3205 | 100000 | 7.7569 | 6721.4914 | 8605.9207 | 137.0267 | 175.4433
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.0197 | 27.2205 | 2.1027 | 4 | 6454.6854 | 8192.6486 | 131.5875 | 167.0182 | 123.6787 | 0 | 181.8456 | 4176578.7588 | 297351.7919 | 4786193.1009 | 4656616.5289 | 0 | 473921.0239 | 0 | 5612357.8697 | 14602203.924 | 9966304.2234 | 44571527.2214 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 54287918.6914 | 68905269.9781 | 133352.1432 | 8.4106 | 6454.6854 | 8192.6486 | 131.5875 | 167.0182
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9977 | 28.587 | 2.2397 | 4 | 6251.1379 | 7882.736 | 127.4379 | 160.7002 | 123.5367 | 0 | 212.472 | 4320783.1395 | 307216.3852 | 4977964.6349 | 4893412.6181 | 0 | 445163.9033 | 0 | 5828370.8656 | 15164225.429 | 10349895.449 | 46287032.4246 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 56003423.8945 | 70620775.1812 | 177827.941 | 8.9589 | 6251.1379 | 7882.736 | 127.4379 | 160.7002
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.789 | 29.6737 | 2.3516 | 4 | 6096.3317 | 7650.3369 | 124.282 | 155.9625 | 123.4131 | 0 | 232.6468 | 4433579.5407 | 314891.7162 | 5129222.6811 | 5082345.1049 | 0 | 417194.0571 | 0 | 5997120.909 | 15603278.4265 | 10649558.1414 | 47627190.5769 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 57343582.0468 | 71960933.3336 | 237137.3706 | 9.4062 | 6096.3317 | 7650.3369 | 124.282 | 155.9625
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.8723 | 30.5936 | 2.4461 | 4 | 5975.7003 | 7469.6272 | 121.8227 | 152.2785 | 123.3012 | 0 | 207.3179 | 4527806.2687 | 321274.5896 | 5256451.8181 | 5242742.5728 | 0 | 392425.4528 | 0 | 6138873.2738 | 15972089.0023 | 10901278.9377 | 48752941.9158 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 58469333.3857 | 73086684.6725 | 316227.766 | 9.7845 | 5975.7003 | 7469.6272 | 121.8227 | 152.2785
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.7876 | 31.2466 | 2.5159 | 4 | 5887.6634 | 7340.1455 | 120.028 | 149.6388 | 123.2177 | 0 | 208.9377 | 4594013.2754 | 325742.5976 | 5346344.5339 | 5356893.1002 | 0 | 370310.2054 | 0 | 6237388.4479 | 16228405.2771 | 11076220.062 | 49535317.4996 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 59251708.9695 | 73869060.2562 | 421696.5034 | 10.0637 | 5887.6634 | 7340.1455 | 120.028 | 149.6388
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.0265 | 32.1979 | 2.5976 | 4 | 5820.1193 | 7226.9293 | 118.651 | 147.3307 | 123.1057 | 0 | 213.3185 | 4689859.4227 | 332218.5182 | 5476589.4834 | 5523038.1845 | 0 | 366074.019 | 0 | 6391234.0548 | 16628679.9883 | 11349415.7772 | 50757109.4481 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60473500.918 | 75090852.2048 | 562341.3252 | 10.3904 | 5820.1193 | 7226.9293 | 118.651 | 147.3307
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.8707 | 32.6109 | 2.6418 | 4 | 5769.1039 | 7152.3787 | 117.611 | 145.8109 | 123.0574 | 0 | 188.624 | 4731184.4531 | 335006.985 | 5532908.4987 | 5595242.4285 | 0 | 351582.5768 | 0 | 6452910.7274 | 16789150.0386 | 11458939.8839 | 51246925.5919 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 60963317.0618 | 75580668.3486 | 749894.2093 | 10.5672 | 5769.1039 | 7152.3787 | 117.611 | 145.8109
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.2519 | 32.9196 | 2.6753 | 4 | 5730.6489 | 7096.583 | 116.827 | 144.6734 | 123.0207 | 0 | 188.3582 | 4761937.7682 | 337079.2166 | 5574911.317 | 5649253.9608 | 0 | 339754.0905 | 0 | 6498545.1777 | 16907881.5174 | 11539976.5578 | 51609339.6059 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 61325731.0758 | 75943082.3626 | 1000000 | 10.7014 | 5730.6489 | 7096.583 | 116.827 | 144.6734
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.2944 | 33.1523 | 2.7008 | 4 | 5701.6947 | 7054.728 | 116.2368 | 143.8202 | 122.9928 | 0 | 207.6026 | 4785066.7517 | 338637.3587 | 5606527.4392 | 5690137.1866 | 0 | 330360.9499 | 0 | 6532784.5775 | 16996965.4124 | 11600778.1466 | 51881257.8225 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 61597649.2924 | 76215000.5792 | 1333521.4322 | 10.8034 | 5701.6947 | 7054.728 | 116.2368 | 143.8202
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.0714 | 33.3258 | 2.7201 | 4 | 5679.9156 | 7023.3694 | 115.7928 | 143.1809 | 122.9718 | 0 | 190.8141 | 4802303.1302 | 339800.4427 | 5630062.8661 | 5720922.2263 | 0 | 322943.1726 | 0 | 6558252.4168 | 17063227.5059 | 11646003.3871 | 52083515.1477 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 61799906.6176 | 76417257.9044 | 1778279.41 | 10.8804 | 5679.9156 | 7023.3694 | 115.7928 | 143.1809
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.6755 | 33.4606 | 2.7349 | 4 | 5663.5438 | 6999.7195 | 115.459 | 142.6987 | 122.9554 | 0 | 214.4356 | 4815670.5089 | 340701.9564 | 5648331.3895 | 5744853.0222 | 0 | 317334.1304 | 0 | 6578087.4929 | 17114834.3052 | 11681226.088 | 52241038.8934 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 61957430.3633 | 76574781.65 | 2371373.7057 | 10.9397 | 5663.5438 | 6999.7195 | 115.459 | 142.6987
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.119 | 33.5594 | 2.7459 | 4 | 5651.2438 | 6982.0554 | 115.2082 | 142.3386 | 122.9433 | 0 | 197.1497 | 4825461.6877 | 341362.0022 | 5661721.5607 | 5762413.0957 | 0 | 312942.6414 | 0 | 6592521.3852 | 17152388.3322 | 11706857.483 | 52355668.1881 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 62072059.658 | 76689410.9447 | 3162277.6602 | 10.9838 | 5651.2438 | 6982.0554 | 115.2082 | 142.3386
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.4649 | 33.6365 | 2.7557 | 4 | 5638.7279 | 6964.807 | 114.9531 | 141.987 | 122.9339 | 0 | 220.1282 | 4833093.1005 | 341876.3951 | 5672161.3046 | 5776112.7222 | 0 | 307635.4489 | 0 | 6603042.7988 | 17179762.8923 | 11725541.1828 | 52439225.8454 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 62155617.3153 | 76772968.602 | 4216965.0343 | 11.023 | 5638.7279 | 6964.807 | 114.9531 | 141.987
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.689 | 33.6864 | 2.7603 | 4 | 5635.0725 | 6958.9599 | 114.8786 | 141.8678 | 122.9277 | 0 | 226.3053 | 4838024.8916 | 342208.5623 | 5678913.9497 | 5784983.8839 | 0 | 306939.4384 | 0 | 6610917.5831 | 17200251.4656 | 11739525.0551 | 52501764.8296 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 62218156.2996 | 76835507.5863 | 5623413.2519 | 11.0412 | 5635.0725 | 6958.9599 | 114.8786 | 141.8678
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.9 | 34.4003 | 2.807 | 4 | 5628.8044 | 6930.6718 | 114.7508 | 141.2911 | 122.8392 | 0 | 228.3169 | 4908328.2227 | 346939.9283 | 5775328.8915 | 5912033.7679 | 0 | 325491.5085 | 0 | 6734567.7044 | 17521963.717 | 11959100.2772 | 53483754.0174 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 63200145.4874 | 77817496.7741 | 7498942.0933 | 11.228 | 5628.8044 | 6930.6718 | 114.7508 | 141.2911
1 | 2800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.025 | 33.7612 | 2.7686 | 4 | 5625.963 | 6945.8727 | 114.6929 | 141.601 | 122.9185 | 0 | 206.2179 | 4845416.9733 | 342706.493 | 5689035.5665 | 5798284.5428 | 0 | 303593.1552 | 0 | 6621824.325 | 17228628.5708 | 11758893.0125 | 52588382.6391 | 961560.8286 | 8754830.6413 | 8754830.6413 | 1478867.319 | 4383653.3264 | 0 | 62304774.109 | 76922125.3957 | 10000000 | 11.0745 | 5625.963 | 6945.8727 | 114.6929 | 141.601
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0836 | [19 empty] | 100 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.6033 | [19 empty] | 133.3521 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.596 | [19 empty] | 177.8279 | 0
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.93774 | 0.14639 | 0.0013649 | 4 | 2009725.6503 | 4782068.2721 | 40970.9757 | 97488.93 | 97.859 | 0 | 43.2157 | 91872.4315 | 5631.9062 | 74557.2999 | 55017.0389 | 0 | 58827.9117 | 0 | 111503.5694 | 290109.415 | 198005.6369 | 885525.2096 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 10972123.734 | 26107764.8969 | 237.1374 | 0.0054595 | 2009725.6503 | 4782068.2721 | 40970.9757 | 97488.93
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3936 | 0.25355 | 0.004928 | 4 | 577339.0061 | 1345176.8496 | 11769.8365 | 27423.2496 | 106.5168 | 0 | 49.9993 | 142477.554 | 9217.9576 | 114967.0931 | 73445.5685 | 0 | 77656.8423 | 0 | 162928.356 | 423906.1612 | 289324.6654 | 1293924.1981 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11380522.7225 | 26516163.8854 | 316.2278 | 0.019712 | 577339.0061 | 1345176.8496 | 11769.8365 | 27423.2496
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.35927 | 0.01036 | 4 | 283105.5687 | 648359.6402 | 5771.4899 | 13217.6882 | 111.1973 | 0 | 313.0952 | 186806.9482 | 12445.9445 | 151425.1816 | 91335.1192 | 0 | 89076.1362 | 0 | 207124.8386 | 538896.343 | 367807.8273 | 1644918.3387 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 11731516.863 | 26867158.026 | 421.6965 | 0.041439 | 283105.5687 | 648359.6402 | 5771.4899 | 13217.6882
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4293 | 0.50933 | 0.018184 | 4 | 167664.2347 | 375757.3387 | 3418.0622 | 7660.3216 | 115.1726 | 0 | 433.081 | 243723.3336 | 16648.7337 | 199636.0109 | 116424.7422 | 0 | 104315.7343 | 0 | 265491.9363 | 690755.5585 | 471454.8623 | 2108450.9118 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12195049.4362 | 27330690.5991 | 562.3413 | 0.072735 | 167664.2347 | 375757.3387 | 3418.0622 | 7660.3216
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2073 | 0.70532 | 0.029019 | 4 | 109891.7226 | 240287.8641 | 2240.2914 | 4898.5931 | 118.2355 | 0 | 586.9364 | 311083.6299 | 21665.8611 | 258474.672 | 149017.2934 | 0 | 121491.8267 | 0 | 336075.9804 | 874400.7623 | 596796.4874 | 2669006.5132 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 12755605.0376 | 27891246.2006 | 749.8942 | 0.11607 | 109891.7226 | 240287.8641 | 2240.2914 | 4898.5931
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 0.97459 | 0.043957 | 4 | 76643.9199 | 162725.9383 | 1562.49 | 3317.3884 | 120.698 | 0 | 86.8197 | 395102.8139 | 27950.5434 | 334208.3801 | 193701.253 | 0 | 143412.8008 | 0 | 426806.5586 | 1110463.1154 | 757913.894 | 3389559.3592 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 13476157.8836 | 28611799.0466 | 1000 | 0.17583 | 76643.9199 | 162725.9383 | 1562.49 | 3317.3884
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6636 | 1.3303 | 0.064053 | 4 | 56066.0527 | 115141.0433 | 1142.9823 | 2347.3059 | 122.5765 | 0 | 93.9566 | 495955.445 | 35497.7857 | 428116.1173 | 252343.1758 | 0 | 169350.1275 | 0 | 538692.434 | 1401567.2122 | 956598.4217 | 4278120.7192 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 14364719.2436 | 29500360.4065 | 1333.5214 | 0.25621 | 56066.0527 | 115141.0433 | 1142.9823 | 2347.3059
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.5468 | 1.8093 | 0.090879 | 4 | 42611.034 | 84247.7201 | 868.6836 | 1717.5037 | 123.9623 | 0 | 92.2377 | 619527.9677 | 44723.2219 | 547013.7346 | 331464.278 | 0 | 201795.2361 | 0 | 680364.5309 | 1770168.9476 | 1208176.6801 | 5403234.5969 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 15489833.1213 | 30625474.2843 | 1778.2794 | 0.36352 | 42611.034 | 84247.7201 | 868.6836 | 1717.5037
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.048 | 2.4528 | 0.12777 | 4 | 33088.0572 | 62701.9538 | 674.5448 | 1278.2641 | 125.1737 | 0 | 92.1021 | 771692.448 | 56115.5402 | 697189.6223 | 437658.9989 | 0 | 240806.3753 | 0 | 859350.564 | 2235853.8904 | 1526016.2224 | 6824683.6614 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 16911282.1858 | 32046923.3488 | 2371.3737 | 0.5111 | 33088.0572 | 62701.9538 | 674.5448 | 1278.2641
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.006 | 3.212 | 0.17472 | 4 | 26443.9135 | 48100.3684 | 539.0949 | 980.5911 | 125.9497 | 0 | 103.569 | 936362.7845 | 68398.8156 | 864577.6554 | 563644.3033 | 0 | 277477.4887 | 0 | 1057079.8085 | 2750304.8248 | 1877139.556 | 8394985.2367 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 18481583.7611 | 33617224.924 | 3162.2777 | 0.6989 | 26443.9135 | 48100.3684 | 539.0949 | 980.5911
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5332 | 4.1174 | 0.23453 | 4 | 21581.8904 | 37716.1726 | 439.976 | 768.8952 | 126.5167 | 0 | 91.789 | 1118168.6856 | 81920.1267 | 1054155.1693 | 713461.9429 | 0 | 312447.8109 | 0 | 1279259.9568 | 3328371.9954 | 2271682.2781 | 10159467.9657 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 20246066.4901 | 35381707.6531 | 4216.965 | 0.9381 | 21581.8904 | 37716.1726 | 439.976 | 768.8952
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.9519 | 5.252 | 0.31151 | 4 | 17938.291 | 30085.3433 | 365.6963 | 613.3304 | 126.9608 | 0 | 76.2506 | 1330040.8967 | 97634.4961 | 1280355.2935 | 901156.8139 | 0 | 350812.1908 | 0 | 1544399.8795 | 4018211.6865 | 2742512.042 | 12265123.299 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 22351721.8234 | 37487362.9864 | 5623.4133 | 1.246 | 17938.291 | 30085.3433 | 365.6963 | 613.3304
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.3887 | 6.6478 | 0.40933 | 4 | 15159.2462 | 24403.4072 | 309.0417 | 497.4965 | 127.3054 | 0 | 99.0702 | 1572961.6846 | 115600.7887 | 1545646.6533 | 1131767.0211 | 0 | 391117.2976 | 0 | 1855266.4437 | 4827022.719 | 3294542.1911 | 14733924.7992 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 24820523.3236 | 39956164.4866 | 7498.9421 | 1.6373 | 15159.2462 | 24403.4072 | 309.0417 | 497.4965
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.0318 | 8.3536 | 0.5325 | 4 | 13006.9329 | 20112.9264 | 265.1639 | 410.0292 | 127.5746 | 0 | 111.0412 | 1850353.4296 | 136059.9146 | 1855186.6846 | 1413543.2927 | 0 | 433102.3469 | 0 | 2218415.8106 | 5771862.8797 | 3939415.0153 | 17617939.3739 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 27704537.8983 | 42840179.0613 | 10000 | 2.13 | 13006.9329 | 20112.9264 | 265.1639 | 410.0292
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.0561 | 10.4143 | 0.68554 | 4 | 11320.5794 | 16840.1708 | 230.7853 | 343.3097 | 127.7842 | 0 | 131.386 | 2164232.4931 | 159145.5758 | 2212738.9533 | 1753931.44 | 0 | 476049.2841 | 0 | 2638778.1211 | 6865559.3832 | 4685885.3522 | 20956320.6028 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 31042919.1272 | 46178560.2902 | 13335.2143 | 2.7422 | 11320.5794 | 16840.1708 | 230.7853 | 343.3097
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.4176 | 12.8173 | 0.87034 | 4 | 9989.5663 | 14337.1681 | 203.6508 | 292.2826 | 127.9374 | 0 | 137.0109 | 2508096.9761 | 184359.0804 | 2612254.5693 | 2150943.0174 | 0 | 516198.5463 | 0 | 3109022.3539 | 8089038.4166 | 5520934.9324 | 24690847.8923 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 34777446.4167 | 49913087.5796 | 17782.7941 | 3.4814 | 9989.5663 | 14337.1681 | 203.6508 | 292.2826
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.8929 | 15.5002 | 1.085 | 4 | 8937.2296 | 12424.853 | 182.1975 | 253.2974 | 128.0267 | 0 | 128.0268 | 2870204.5003 | 210807.4505 | 3041051.2105 | 2594683.1264 | 0 | 549310.0992 | 0 | 3613761.9909 | 9402267.4159 | 6417240.7086 | 28699326.5024 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 38785925.0268 | 53921566.1897 | 23713.7371 | 4.3398 | 8937.2296 | 12424.853 | 182.1975 | 253.2974
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.9593 | 18.3209 | 1.321 | 4 | 8108.1978 | 10972.5421 | 165.2966 | 223.6901 | 128.0406 | 0 | 151.9271 | 3230929.9643 | 237017.3038 | 3476205.9355 | 3062202.5462 | 0 | 570234.407 | 0 | 4124870.1611 | 10732066.0321 | 7324855.5888 | 32758381.9388 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 42844980.4632 | 57980621.6262 | 31622.7766 | 5.2842 | 8108.1978 | 10972.5421 | 165.2966 | 223.6901
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 83.0117 | 21.1161 | 1.5662 | 4 | 7459.1882 | 9875.1439 | 152.0656 | 201.3182 | 127.9791 | 0 | 173.5202 | 3571568.0196 | 261603.0672 | 3894551.9252 | 3527078.9969 | 0 | 576397.1735 | 0 | 4614167.6811 | 12005117.8103 | 8193739.5861 | 36644224.2598 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 46730822.7842 | 61866463.9472 | 42169.6503 | 6.2649 | 7459.1882 | 9875.1439 | 152.0656 | 201.3182
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.523 | 23.748 | 1.8074 | 4 | 6954.4846 | 9048.0197 | 141.7766 | 184.4561 | 127.857 | 0 | 191.0808 | 3879088.7718 | 283629.3245 | 4278639.1995 | 3966834.3825 | 0 | 568554.8256 | 0 | 5060931.1366 | 13167504.6776 | 8987092.5077 | 40192274.8259 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 50278873.3503 | 65414514.5132 | 56234.1325 | 7.2297 | 6954.4846 | 9048.0197 | 141.7766 | 184.4561
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0381 | 26.1042 | 2.0325 | 4 | 6564.3973 | 8426.1045 | 133.8241 | 171.7775 | 127.6977 | 0 | 206.8067 | 4144679.8241 | 302498.7965 | 4615508.8114 | 4362521.801 | 0 | 549047.9871 | 0 | 5449960.3158 | 14179678.8012 | 9677922.1451 | 43281818.4821 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 53368417.0065 | 68504058.1695 | 74989.4209 | 8.13 | 6564.3973 | 8426.1045 | 133.8241 | 171.7775
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.3324 | 28.1353 | 2.2335 | 4 | 6264.4774 | 7958.6045 | 127.7098 | 162.2469 | 127.5245 | 0 | 205.7487 | 4366877.506 | 318160.1552 | 4901211.1027 | 4705378.4132 | 0 | 521943.4588 | 0 | 5777292.548 | 15031330.1242 | 10259191.6727 | 45881384.9806 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 55967983.505 | 71103624.668 | 100000 | 8.9342 | 6264.4774 | 7958.6045 | 127.7098 | 162.2469
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.3117 | 29.8264 | 2.4063 | 4 | 6034.8953 | 7607.4104 | 123.0295 | 155.0874 | 127.3556 | 0 | 220.1623 | 4547429.9754 | 330792.5981 | 5136106.9164 | 4992268.5607 | 0 | 490993.8749 | 0 | 6044060.851 | 15725406.5269 | 10732913.0794 | 47999972.3827 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 58086570.9071 | 73222212.0701 | 133352.1432 | 9.6251 | 6034.8953 | 7607.4104 | 123.0295 | 155.0874
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9996 | 31.1919 | 2.5498 | 4 | 5859.791 | 7343.8195 | 119.4598 | 149.7137 | 127.2033 | 0 | 226.7748 | 4690390.1972 | 340729.8748 | 5323928.9344 | 5224932.3745 | 0 | 459243.7959 | 0 | 6255297.819 | 16275001.787 | 11108023.1374 | 49677547.9202 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 59764146.4446 | 74899787.6076 | 177827.941 | 10.199 | 5859.791 | 7343.8195 | 119.4598 | 149.7137
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.548 | 32.2752 | 2.6662 | 4 | 5726.6309 | 7145.8561 | 116.7451 | 145.6779 | 127.0725 | 0 | 228.5339 | 4802077.7081 | 348450.5612 | 5471841.4731 | 5410216.6594 | 0 | 429199.7607 | 0 | 6420096.6033 | 16703774.419 | 11400669.2692 | 50986326.4539 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 61072924.9782 | 76208566.1412 | 237137.3706 | 10.6647 | 5726.6309 | 7145.8561 | 116.7451 | 145.6779
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.146 | 32.6538 | 2.7309 | 4 | 5623.192 | 7008.7695 | 114.6364 | 142.8832 | 127.0243 | 0 | 509.489 | 4840738.8211 | 351112.9356 | 5523307.6038 | 5475128.5178 | 0 | 385524.2043 | 0 | 6464566.7122 | 16819476.5203 | 11479638.3308 | 51339493.646 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 61426092.1704 | 76561733.3334 | 316227.766 | 10.9237 | 5623.192 | 7008.7695 | 114.6364 | 142.8832
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.3176 | 34.3504 | 2.8689 | 4 | 5545.3353 | 6864.2917 | 113.0492 | 139.9379 | 126.8206 | 0 | 197.2118 | 5012462.3234 | 362934.5075 | 5752533.8554 | 5765245.4389 | 0 | 395919.885 | 0 | 6742747.444 | 17543245.7216 | 11973625.6826 | 53548714.8584 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 63635313.3828 | 78770954.5457 | 421696.5034 | 11.4755 | 5545.3353 | 6864.2917 | 113.0492 | 139.9379
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.5903 | 34.8863 | 2.9279 | 4 | 5487.1238 | 6779.4849 | 111.8624 | 138.209 | 126.757 | 0 | 229.3775 | 5066112.884 | 366619.7662 | 5824473.1192 | 5856967.3626 | 0 | 377616.2041 | 0 | 6821797.8411 | 17748918.6394 | 12114001.6752 | 54176507.4917 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 64263106.0161 | 79398747.1791 | 562341.3252 | 11.7116 | 5487.1238 | 6779.4849 | 111.8624 | 138.209
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.3077 | 35.2901 | 2.973 | 4 | 5443.1862 | 6715.9267 | 110.9667 | 136.9132 | 126.7081 | 0 | 209.9841 | 5106332.869 | 369377.3421 | 5878549.7834 | 5926167.5488 | 0 | 362518.5794 | 0 | 6880748.9878 | 17902297.4307 | 12218685.8519 | 54644678.3931 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 64731276.9175 | 79866918.0804 | 749894.2093 | 11.8922 | 5443.1862 | 6715.9267 | 110.9667 | 136.9132
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.6159 | 35.5971 | 3.0076 | 4 | 5410.067 | 6668.1916 | 110.2915 | 135.9401 | 126.6705 | 0 | 239.4487 | 5136786.9541 | 371462.3774 | 5919580.1287 | 5978817.6225 | 0 | 350450.7903 | 0 | 6925268.1705 | 18018127.2117 | 12297742.0575 | 54998235.3126 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65084833.837 | 80220475 | 1000000 | 12.0303 | 5410.067 | 6668.1916 | 110.2915 | 135.9401
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.5929 | 35.826 | 3.0336 | 4 | 5385.1297 | 6632.4448 | 109.7832 | 135.2114 | 126.6421 | 0 | 193.428 | 5159429.008 | 373010.8769 | 5950132.9733 | 6018104.3208 | 0 | 340830.585 | 0 | 6958188.0279 | 18103777.9281 | 12356200.4314 | 55259674.1513 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65346272.6757 | 80481913.8387 | 1333521.4322 | 12.1346 | 5385.1297 | 6632.4448 | 109.7832 | 135.2114
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.3286 | 35.9982 | 3.0534 | 4 | 5366.3698 | 6605.6301 | 109.4007 | 134.6647 | 126.6206 | 0 | 213.0081 | 5176419.8879 | 374171.9399 | 5973086.9548 | 6047665.6096 | 0 | 333317.4999 | 0 | 6982818.1379 | 18167860.4218 | 12399938.0501 | 55455278.5019 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65541877.0263 | 80677518.1892 | 1778279.41 | 12.2134 | 5366.3698 | 6605.6301 | 109.4007 | 134.6647
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.8887 | 36.1291 | 3.0683 | 4 | 5352.2671 | 6585.4753 | 109.1132 | 134.2538 | 126.6041 | 0 | 188.6945 | 5189323.0517 | 375053.1272 | 5990533.9163 | 6070160.85 | 0 | 327557.4241 | 0 | 7001525.064 | 18216532.0063 | 12433157.4066 | 55603842.8462 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65690441.3706 | 80826082.5336 | 2371373.7057 | 12.2734 | 5352.2671 | 6585.4753 | 109.1132 | 134.2538
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.3102 | 36.2276 | 3.0796 | 4 | 5341.6714 | 6570.3543 | 108.8972 | 133.9456 | 126.5917 | 0 | 191.6399 | 5199015.2682 | 375714.718 | 6003647.9912 | 6087084.4062 | 0 | 323139.3531 | 0 | 7015554.6773 | 18253034.1823 | 12458070.8917 | 55715261.4881 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65801860.0125 | 80937501.1754 | 3162277.6602 | 12.3186 | 5341.6714 | 6570.3543 | 108.8972 | 133.9456
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.6197 | 36.2999 | 3.088 | 4 | 5333.7142 | 6559.0554 | 108.735 | 133.7152 | 126.5826 | 0 | 195.2131 | 5206120.6557 | 376199.557 | 6013266.808 | 6099505.5588 | 0 | 319713.6401 | 0 | 7025774.4257 | 18279623.8711 | 12476218.9007 | 55796423.4171 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65883021.9415 | 81018663.1044 | 4216965.0343 | 12.3522 | 5333.7142 | 6559.0554 | 108.735 | 133.7152
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.8176 | 35.6441 | 3.0496 | 4 | 5325.7557 | 6566.5434 | 108.5727 | 133.8679 | 126.664 | 0 | 208.4642 | 5141420.3537 | 371777.8716 | 5925855.4743 | 5986899.81 | 0 | 292702.4237 | 0 | 6910275.814 | 17979120.1756 | 12271118.9538 | 54879170.8768 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 64965769.4012 | 80101410.5642 | 5623413.2519 | 12.1984 | 5325.7557 | 6566.5434 | 108.5727 | 133.8679
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.0921 | 35.9427 | 3.0712 | 4 | 5320.7854 | 6552.8554 | 108.4714 | 133.5888 | 126.6271 | 0 | 180.9596 | 5170933.1081 | 373796.1628 | 5965688.4009 | 6038144.668 | 0 | 298793.4373 | 0 | 6960468.7531 | 18109711.9071 | 12360250.494 | 55277786.9313 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65364385.4557 | 80500026.6187 | 7498942.0933 | 12.2847 | 5320.7854 | 6552.8554 | 108.4714 | 133.5888
1 | 2900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.0472 | 36.1661 | 3.0873 | 4 | 5317.1692 | 6542.8137 | 108.3977 | 133.3841 | 126.5993 | 0 | 181.8098 | 5192954.371 | 375300.5447 | 5995454.9976 | 6076516.0269 | 0 | 303351.1605 | 0 | 6997995.0693 | 18207347.6841 | 12426888.9179 | 55575808.7719 | 961560.8286 | 9125037.6958 | 9125037.6958 | 1478867.319 | 4531736.1482 | 0 | 65662407.2963 | 80798048.4593 | 10000000 | 12.3491 | 5317.1692 | 6542.8137 | 108.3977 | 133.3841
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.1521 | [19 empty] | 100 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.3896 | [19 empty] | 133.3521 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.2461 | [19 empty] | 177.8279 | 0
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0887 | 0.18817 | 0.0025412 | 4 | 1133363.4163 | 2674203.8867 | 23105.1462 | 54517.2634 | 103.5337 | 0 | 56.4984 | 113686.9506 | 7213.03 | 90762.2102 | 61725.1245 | 0 | 68076.3734 | 0 | 133170.8386 | 346483.2049 | 236481.9069 | 1057599.6391 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11520265.3088 | 27182400.4752 | 237.1374 | 0.010165 | 1133363.4163 | 2674203.8867 | 23105.1462 | 54517.2634
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.27026 | 0.0068952 | 4 | 428201.7868 | 996066.3609 | 8729.4726 | 20306.16 | 109.3071 | 0 | 58.6582 | 151583.029 | 9968.3466 | 120748.4046 | 75427.2216 | 0 | 77324.2375 | 0 | 169669.9834 | 441446.4926 | 301296.302 | 1347464.0173 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 11810129.687 | 27472264.8534 | 316.2278 | 0.027581 | 428201.7868 | 996066.3609 | 8729.4726 | 20306.16
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.39058 | 0.013446 | 4 | 226925.2118 | 518124.5653 | 4626.1774 | 10562.6701 | 114.4351 | 0 | 320.7216 | 201837.8157 | 13706.7333 | 161522.15 | 95301.3232 | 0 | 90223.836 | 0 | 219410.8247 | 570861.9585 | 389625.0167 | 1742489.6582 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12205155.3279 | 27867290.4943 | 421.6965 | 0.053785 | 226925.2118 | 518124.5653 | 4626.1774 | 10562.6701
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4877 | 0.54889 | 0.022715 | 4 | 139599.8083 | 311978.8602 | 2845.9309 | 6360.111 | 118.4505 | 0 | 436.0406 | 261624.3903 | 18222.6998 | 211459.8731 | 121146.0531 | 0 | 104695.3325 | 0 | 279687.856 | 727690.4296 | 496663.6707 | 2221190.3051 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 12683855.9748 | 28345991.1412 | 562.3413 | 0.090859 | 139599.8083 | 311978.8602 | 2845.9309 | 6360.111
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 0.76107 | 0.035579 | 4 | 93316.5188 | 203366.9275 | 1902.3835 | 4145.9099 | 121.6437 | 0 | 591.4149 | 334331.9966 | 23765.8818 | 274038.9171 | 155700.2741 | 0 | 121981.4278 | 0 | 354829.214 | 923192.8294 | 630098.0758 | 2817938.6166 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 13280604.2863 | 28942739.4527 | 749.8942 | 0.14232 | 93316.5188 | 203366.9275 | 1902.3835 | 4145.9099
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 1.0489 | 0.053172 | 4 | 65990.5053 | 139628.9574 | 1345.3057 | 2846.5252 | 124.1892 | 0 | 83.3783 | 423815.0905 | 30612.9009 | 353581.5685 | 202007.9954 | 0 | 143530.3883 | 0 | 449883.698 | 1170505.0983 | 798893.7811 | 3572830.521 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 14035496.1907 | 29697631.3571 | 1000 | 0.21269 | 65990.5053 | 139628.9574 | 1345.3057 | 2846.5252
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8022 | 1.4375 | 0.077176 | 4 | 48567.2291 | 99302.1951 | 990.1087 | 2024.4096 | 126.1652 | 0 | 77.9026 | 533868.4974 | 39058.9435 | 454364.8003 | 265261.9046 | 0 | 170121.8088 | 0 | 570443.6224 | 1484177.2913 | 1012981.4981 | 4530278.3665 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 14992944.0362 | 30655079.2026 | 1333.5214 | 0.3087 | 48567.2291 | 99302.1951 | 990.1087 | 2024.4096
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7099 | 1.95 | 0.10888 | 4 | 37142.1827 | 73104.2841 | 757.1936 | 1490.3297 | 127.583 | 0 | 99.7002 | 665772.085 | 49146.3201 | 579323.9167 | 348412.5923 | 0 | 202016.748 | 0 | 719421.9482 | 1871788.3356 | 1277534.0004 | 5713415.9464 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 16176081.6161 | 31838216.7825 | 1778.2794 | 0.43552 | 37142.1827 | 73104.2841 | 757.1936 | 1490.3297
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.2721 | 2.6467 | 0.15265 | 4 | 28969.0672 | 54619.2798 | 590.5736 | 1113.4879 | 128.8664 | 0 | 95.6045 | 830182.4842 | 61759.1131 | 739044.0718 | 460769.7903 | 0 | 241271.7841 | 0 | 909880.625 | 2367322.7441 | 1615746.4164 | 7225977.0291 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 17688642.6988 | 33350777.8652 | 2371.3737 | 0.6106 | 28969.0672 | 54619.2798 | 590.5736 | 1113.4879
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.6562 | 3.5636 | 0.21024 | 4 | 23264.9798 | 41889.1887 | 474.2881 | 853.9678 | 129.7497 | 0 | 96.404 | 1027598.9057 | 76830.8504 | 937012.7773 | 608997.052 | 0 | 288342.1877 | 0 | 1146124.8915 | 2981981.8651 | 2035263.8965 | 9102152.426 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 19564818.0957 | 35226953.2621 | 3162.2777 | 0.84096 | 23264.9798 | 41889.1887 | 474.2881 | 853.9678
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1728 | 4.7879 | 0.28706 | 4 | 19101.1555 | 32741.0928 | 389.4029 | 667.4715 | 130.4226 | 0 | 72.2641 | 1269074.4674 | 95210.351 | 1186170.3865 | 806880.8656 | 0 | 346055.9271 | 0 | 1444322.8791 | 3757831.86 | 2564797.4602 | 11470344.197 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 21933009.8667 | 37595145.0331 | 4216.965 | 1.1483 | 19101.1555 | 32741.0928 | 389.4029 | 667.4715
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.9936 | 6.0951 | 0.37998 | 4 | 15982.9071 | 26287.454 | 325.8332 | 535.9053 | 130.8523 | 0 | 85.2323 | 1507438.3416 | 113297.5083 | 1438425.1529 | 1018136.043 | 0 | 387997.3612 | 0 | 1741464.8187 | 4530934.2348 | 3092455.7166 | 13830149.1772 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 24292814.8469 | 39954950.0133 | 5623.4133 | 1.5199 | 15982.9071 | 26287.454 | 325.8332 | 535.9053
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.8908 | 7.6946 | 0.49756 | 4 | 13589.2539 | 21458.6784 | 277.0353 | 437.4642 | 131.1853 | 0 | 92.8979 | 1779507.1497 | 133882.343 | 1732815.768 | 1276561.5501 | 0 | 431450.7766 | 0 | 2088144.8591 | 5432924.586 | 3708082.6654 | 16583369.6979 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 27046035.3676 | 42708170.534 | 7498.9421 | 1.9903 | 13589.2539 | 21458.6784 | 277.0353 | 437.4642
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.1038 | 9.6513 | 0.64532 | 4 | 11726.0752 | 17793.6367 | 239.0519 | 362.7474 | 131.4465 | 0 | 141.3909 | 2090744.0207 | 157362.6724 | 2076807.7547 | 1592648.2871 | 0 | 477048.7062 | 0 | 2493898.462 | 6488612.2293 | 4428611.1741 | 19805733.3065 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 30268398.9762 | 45930534.1426 | 10000 | 2.5813 | 11726.0752 | 17793.6367 | 239.0519 | 362.7474
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.7102 | 11.986 | 0.82724 | 4 | 10260.5328 | 14993.767 | 209.1748 | 305.6682 | 131.6465 | 0 | 113.179 | 2438892.9439 | 183549.5932 | 2469482.9051 | 1969797.4102 | 0 | 522137.9864 | 0 | 2957705.7271 | 7695343.5931 | 5252230.1258 | 23489140.2846 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 33951805.9543 | 49613941.1207 | 13335.2143 | 3.309 | 10260.5328 | 14993.767 | 209.1748 | 305.6682
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.6512 | 14.6798 | 1.0447 | 4 | 9101.3671 | 12849.5425 | 185.5437 | 261.9553 | 131.7847 | 0 | 140.3699 | 2816720.3822 | 211869.721 | 2904029.198 | 2405158.4433 | 0 | 563117.2444 | 0 | 3471349.0457 | 9031738.1452 | 6164346.8678 | 27568329.0475 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 38030994.7172 | 53693129.8836 | 17782.7941 | 4.1786 | 9101.3671 | 12849.5425 | 185.5437 | 261.9553
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.5481 | 17.6226 | 1.2925 | 4 | 8184.8824 | 11214.3836 | 166.8599 | 228.6204 | 131.8483 | 0 | 140.3557 | 3206532.7979 | 240951.6438 | 3360963.0874 | 2881437.668 | 0 | 594107.6729 | 0 | 4010757.2193 | 10435167.5651 | 7122216.2844 | 31852133.9387 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 42314799.6084 | 57976934.7748 | 23713.7371 | 5.1699 | 8184.8824 | 11214.3836 | 166.8599 | 228.6204
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.8554 | 20.6567 | 1.5599 | 4 | 7463.7724 | 9973.8801 | 152.1591 | 203.331 | 131.8281 | 0 | 195.6991 | 3587972.7849 | 269229.823 | 3816469.77 | 3373780.1453 | 0 | 610774.9561 | 0 | 4546708.7169 | 11829603.4233 | 8073947.4104 | 36108487.03 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 46571152.6997 | 62233287.8661 | 31622.7766 | 6.2396 | 7463.7724 | 9973.8801 | 152.1591 | 203.331
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.9808 | 23.614 | 1.8327 | 4 | 6900.0839 | 9036.604 | 140.6675 | 184.2234 | 131.73 | 0 | 192.0672 | 3942860.0414 | 295334.3213 | 4247934.5428 | 3855532.5811 | 0 | 611623.664 | 0 | 5051781.2087 | 13143698.4423 | 8970844.2628 | 40119609.0644 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 50582274.7341 | 66244409.9005 | 42169.6503 | 7.3307 | 6900.0839 | 9036.604 | 140.6675 | 184.2234
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.3855 | 26.3484 | 2.096 | 4 | 6462.2777 | 8330.3646 | 131.7423 | 169.8258 | 131.5746 | 0 | 162.3852 | 4258008.1675 | 318312.6831 | 4637587.8078 | 4303099.2443 | 0 | 597883.3678 | 0 | 5504807.5955 | 14322380.1723 | 9775318.7631 | 43717397.8016 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 54180063.4713 | 69842198.6377 | 56234.1325 | 8.3841 | 6462.2777 | 8330.3646 | 131.7423 | 169.8258
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.7003 | 28.7668 | 2.3382 | 4 | 6124.1865 | 7798.8095 | 124.8498 | 158.9893 | 131.3882 | 0 | 196.0282 | 4527346.5489 | 337773.3027 | 4975734.4092 | 4700976.3467 | 0 | 573046.1473 | 0 | 5894801.9344 | 15337065.443 | 10467862.3101 | 46814606.4422 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 57277272.1119 | 72939407.2783 | 74989.4209 | 9.3526 | 6124.1865 | 7798.8095 | 124.8498 | 158.9893
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.7272 | 30.8261 | 2.5515 | 4 | 5864.384 | 7398.9753 | 119.5534 | 150.8381 | 131.1946 | 0 | 200.8685 | 4750266.5478 | 353739.2757 | 5259401.82 | 5041511.2921 | 0 | 541338.5374 | 0 | 6219040.4145 | 16180667.4579 | 11043638.0195 | 49389603.3648 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 59852269.0345 | 75514404.2009 | 100000 | 10.2061 | 5864.384 | 7398.9753 | 119.5534 | 150.8381
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.4092 | 32.5217 | 2.7326 | 4 | 5665.5675 | 7098.4543 | 115.5003 | 144.7116 | 131.012 | 0 | 224.2847 | 4929623.5005 | 366482.4946 | 5490279.9027 | 5323239.4578 | 0 | 506607.4273 | 0 | 6480330.7853 | 16860491.4049 | 11507631.8323 | 51464686.8054 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 61927352.4751 | 77589487.6415 | 133352.1432 | 10.9305 | 5665.5675 | 7098.4543 | 115.5003 | 144.7116
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.8318 | 33.8843 | 2.8819 | 4 | 5513.9414 | 6872.5985 | 112.4092 | 140.1072 | 130.8501 | 0 | 204.1071 | 5071106.741 | 376463.1834 | 5674179.8487 | 5550405.0866 | 0 | 472119.6896 | 0 | 6686267.0742 | 17396295.3851 | 11873329.0585 | 53100166.067 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 63562831.7367 | 79224966.9031 | 177827.941 | 11.5277 | 5513.9414 | 6872.5985 | 112.4092 | 140.1072
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.8 | 35.372 | 3.0284 | 4 | 5398.58 | 6691.5057 | 110.0574 | 136.4154 | 130.6629 | 0 | 209.812 | 5223115.5498 | 387123.8791 | 5873387.378 | 5799267.212 | 0 | 453528.7791 | 0 | 6917204.8912 | 17997148.213 | 12283423.4598 | 54934199.362 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 65396865.0317 | 81059000.198 | 237137.3706 | 12.1137 | 5398.58 | 6691.5057 | 110.0574 | 136.4154
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.7197 | 36.3498 | 3.1339 | 4 | 5309.56 | 6558.9734 | 108.2426 | 133.7135 | 130.5498 | 0 | 205.0581 | 5322093.5 | 394069.7458 | 6003385.2655 | 5962786.5269 | 0 | 429131.4709 | 0 | 7063471.9385 | 18377705.0668 | 12543161.3321 | 56095804.8465 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 66558470.5162 | 82220605.6826 | 316227.766 | 12.5356 | 5309.56 | 6558.9734 | 108.2426 | 133.7135
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.8324 | 37.1226 | 3.2188 | 4 | 5239.7923 | 6456.2318 | 106.8203 | 131.619 | 130.4574 | 0 | 222.5038 | 5399594.8406 | 399489.6528 | 6105665.8225 | 6092289.5582 | 0 | 406915.1902 | 0 | 7177542.4751 | 18674493.2038 | 12745725.3341 | 57001716.0773 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 67464381.747 | 83126516.9134 | 421696.5034 | 12.8754 | 5239.7923 | 6456.2318 | 106.8203 | 131.619
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.9667 | 37.6505 | 3.2793 | 4 | 5189.3436 | 6383.3569 | 105.7918 | 130.1334 | 130.3926 | 0 | 200.1007 | 5452170.4372 | 403156.3634 | 6175307.0597 | 6180898.7312 | 0 | 387878.8919 | 0 | 7253770.4785 | 18872822.8322 | 12881089.3807 | 57607094.1749 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 68069759.8446 | 83731895.011 | 562341.3252 | 13.1172 | 5189.3436 | 6383.3569 | 105.7918 | 130.1334
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.5797 | 38.0484 | 3.3255 | 4 | 5151.2664 | 6328.7046 | 105.0155 | 129.0192 | 130.3429 | 0 | 226.5666 | 5491608.7999 | 405901.5483 | 6227682.3656 | 6247769.036 | 0 | 372300.8659 | 0 | 7310652.4201 | 19020817.9761 | 12982099.1074 | 58058832.1192 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 68521497.7889 | 84183632.9553 | 749894.2093 | 13.3019 | 5151.2664 | 6328.7046 | 105.0155 | 129.0192
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.7977 | 38.3483 | 3.3606 | 4 | 5122.565 | 6287.7004 | 104.4304 | 128.1833 | 130.305 | 0 | 211.3135 | 5521220.0135 | 407959.6564 | 6267084.1171 | 6298205.4872 | 0 | 359829.1423 | 0 | 7353176.3825 | 19131456.6033 | 13057612.2439 | 58396543.6461 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 68859209.3158 | 84521344.4822 | 1000000 | 13.4423 | 5122.565 | 6287.7004 | 104.4304 | 128.1833
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7056 | 38.5715 | 3.387 | 4 | 5100.9543 | 6256.9915 | 103.9899 | 127.5572 | 130.2765 | 0 | 225.464 | 5543197.097 | 409485.4473 | 6296370.8955 | 6335766.7881 | 0 | 349919.9089 | 0 | 7384548.6533 | 19213080.8168 | 13113322.4468 | 58645692.0536 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69108357.7233 | 84770492.8897 | 1333521.4322 | 13.5481 | 5100.9543 | 6256.9915 | 103.9899 | 127.5572
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.3977 | 38.7414 | 3.4072 | 4 | 5084.6971 | 6233.9024 | 103.6584 | 127.0865 | 130.2547 | 0 | 237.3653 | 5559899.5434 | 410644.0795 | 6318653.085 | 6364385.6781 | 0 | 342272.1659 | 0 | 7408383.2752 | 19275093.6138 | 13155647.455 | 58834978.8958 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69297644.5655 | 84959779.7319 | 1778279.41 | 13.6287 | 5084.6971 | 6233.9024 | 103.6584 | 127.0865
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.9165 | 38.8687 | 3.4223 | 4 | 5072.476 | 6216.5896 | 103.4093 | 126.7336 | 130.2383 | 0 | 231.5913 | 5572388.5338 | 411509.878 | 6335328.1741 | 6385826.2777 | 0 | 336356.3643 | 0 | 7426149.5989 | 19321317.9436 | 13187196.5099 | 58976073.2802 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69438738.9499 | 85100874.1163 | 2371373.7057 | 13.6893 | 5072.476 | 6216.5896 | 103.4093 | 126.7336
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.3038 | 38.9637 | 3.4337 | 4 | 5063.294 | 6203.6159 | 103.2221 | 126.4691 | 130.226 | 0 | 238.7184 | 5581694.8152 | 412154.7228 | 6347761.6224 | 6401826.1236 | 0 | 331802.4673 | 0 | 7439343.503 | 19355645.7756 | 13210625.9606 | 59080854.9904 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69543520.6601 | 85205655.8265 | 3162277.6602 | 13.7348 | 5063.294 | 6203.6159 | 103.2221 | 126.4691
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.5887 | 39.0335 | 3.4422 | 4 | 5056.3985 | 6193.9162 | 103.0815 | 126.2714 | 130.2169 | 0 | 214.0487 | 5588531.1838 | 412628.2494 | 6356899.5493 | 6413592.3417 | 0 | 328284.7035 | 0 | 7448975.0508 | 19380705.0873 | 13227729.4557 | 59157345.6215 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69620011.2912 | 85282146.4576 | 4216965.0343 | 13.7687 | 5056.3985 | 6193.9162 | 103.0815 | 126.2714
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.8056 | 39.0866 | 3.4486 | 4 | 5051.2218 | 6186.6243 | 102.976 | 126.1227 | 130.21 | 0 | 218.0783 | 5593730.5248 | 412988.2918 | 6363851.7093 | 6422548.1279 | 0 | 325637.3133 | 0 | 7456314.8271 | 19399801.6797 | 13240763.2725 | 59215635.7464 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69678301.4161 | 85340436.5825 | 5623413.2519 | 13.7943 | 5051.2218 | 6186.6243 | 102.976 | 126.1227
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.9714 | 39.1272 | 3.4535 | 4 | 5047.3366 | 6181.139 | 102.8968 | 126.0109 | 130.2047 | 0 | 212.3327 | 5597701.5895 | 413263.2249 | 6369162.8909 | 6429392.3308 | 0 | 323656.4992 | 0 | 7461938.8487 | 19414434.2302 | 13250750.2889 | 59260299.9029 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69722965.5726 | 85385100.739 | 7498942.0933 | 13.8138 | 5047.3366 | 6181.139 | 102.8968 | 126.0109
1 | 3000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.0808 | 39.154 | 3.4569 | 4 | 5044.4212 | 6177.1051 | 102.8373 | 125.9286 | 130.2012 | 0 | 234.2734 | 5600321.8407 | 413444.5977 | 6372668.2512 | 6433910.7266 | 0 | 322045.3294 | 0 | 7465532.3908 | 19423783.8895 | 13257131.6234 | 59288838.6492 | 961560.8286 | 9501104.8411 | 9501104.8411 | 1478867.319 | 4682163.0063 | 0 | 69751504.3189 | 85413639.4853 | 10000000 | 13.8275 | 5044.4212 | 6177.1051 | 102.8373 | 125.9286
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.1707 | [19 empty] | 100 | 0
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.473 | [19 empty] | 133.3521 | 0
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79402 | 0.12194 | 0.00059019 | 4 | 4928539.1379 | 11789399.466 | 100474.9367 | 240342.8545 | 96.9708 | 0 | 37.0486 | 80489.5132 | 4899.7467 | 64458.1092 | 50099.0217 | 0 | 55278.7575 | 0 | 99537.8079 | 258976.958 | 176757.0953 | 790497.0096 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11635089.9154 | 27831923.2125 | 177.8279 | 0.0023608 | 4928539.1379 | 11789399.466 | 100474.9367 | 240342.8545
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.20016 | 0.0038963 | 4 | 766304.854 | 1805543.077 | 15622.161 | 36808.4378 | 106.0866 | 0 | 61.5438 | 120668.7151 | 7771.5149 | 95183.0915 | 63208.7979 | 0 | 67834.8595 | 0 | 138320.1218 | 359880.5835 | 245625.893 | 1098493.5772 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 11943086.4831 | 28139919.7802 | 237.1374 | 0.015585 | 766304.854 | 1805543.077 | 15622.161 | 36808.4378
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.29169 | 0.0090758 | 4 | 337784.7687 | 783940.7008 | 6886.1994 | 15981.6915 | 112.2996 | 0 | 69.8826 | 162785.0781 | 10896.7197 | 128072.7082 | 78183.67 | 0 | 77897.6526 | 0 | 178555.9731 | 464566.0152 | 317075.8512 | 1418033.668 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12262626.5739 | 28459459.871 | 316.2278 | 0.036303 | 337784.7687 | 783940.7008 | 6886.1994 | 15981.6915
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.41829 | 0.016738 | 4 | 189244.0997 | 431164.0489 | 3857.9969 | 8789.8623 | 117.5027 | 0 | 337.9664 | 215478.2173 | 14902.5457 | 170259.6558 | 98581.0787 | 0 | 90180.8449 | 0 | 229866.9135 | 598066.5568 | 408192.7141 | 1825528.5268 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 12670121.4327 | 28866954.7297 | 421.6965 | 0.066951 | 189244.0997 | 431164.0489 | 3857.9969 | 8789.8623
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.546 | 0.59057 | 0.027655 | 4 | 119176.8948 | 265593.8762 | 2429.5822 | 5414.4904 | 121.7238 | 0 | 463.0262 | 280371.7544 | 19918.1407 | 223700.1552 | 126159.8975 | 0 | 105005.2784 | 0 | 294510.5382 | 766256.008 | 522985.4704 | 2338907.2427 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13183500.1486 | 29380333.4456 | 562.3413 | 0.11062 | 119176.8948 | 265593.8762 | 2429.5822 | 5414.4904
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3628 | 0.81934 | 0.042662 | 4 | 80958.8989 | 175873.3894 | 1650.4567 | 3585.4169 | 125.0473 | 0 | 622.5017 | 358443.5269 | 26007.207 | 290022.9766 | 162316.8597 | 0 | 122370.9317 | 0 | 374072.9858 | 973261.176 | 664270.7511 | 2970766.4149 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 13815359.3207 | 30012192.6178 | 749.8942 | 0.17065 | 80958.8989 | 175873.3894 | 1650.4567 | 3585.4169
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4721 | 1.1332 | 0.063465 | 4 | 57622.1226 | 121423.876 | 1174.7049 | 2475.3899 | 127.7107 | 0 | 87.0142 | 455876.0527 | 33659.4382 | 375227.7716 | 212397.0421 | 0 | 144395.3593 | 0 | 476406.7089 | 1239512.5321 | 845992.7726 | 3783467.6775 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 14628060.5834 | 30824893.8804 | 1000 | 0.25386 | 57622.1226 | 121423.876 | 1174.7049 | 2475.3899
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9459 | 1.5517 | 0.091476 | 4 | 42744.056 | 87009.5136 | 871.3954 | 1773.8066 | 129.7538 | 0 | 86.9207 | 573864.8241 | 42933.3992 | 481809.0544 | 278759.8162 | 0 | 170958.1777 | 0 | 603846.856 | 1571085.6532 | 1072298.2409 | 4795556.0217 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 15640148.9276 | 31836982.2246 | 1333.5214 | 0.3659 | 42744.056 | 87009.5136 | 871.3954 | 1773.8066
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8951 | 2.1034 | 0.12846 | 4 | 32874.5196 | 64395.7166 | 670.1915 | 1312.7938 | 131.2061 | 0 | 100.5806 | 715351.9113 | 54017.7942 | 613944.5344 | 366409.0338 | 0 | 202855.2516 | 0 | 761505.6249 | 1981281.4298 | 1352265.2871 | 6047630.8673 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 16892223.7732 | 33089057.0702 | 1778.2794 | 0.51384 | 32874.5196 | 64395.7166 | 670.1915 | 1312.7938
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.489 | 2.8474 | 0.1794 | 4 | 25749.948 | 48320.6633 | 524.9475 | 985.0821 | 132.551 | 0 | 98.1561 | 890530.3233 | 67796.3352 | 781561.8309 | 483454.8534 | 0 | 241314.4334 | 0 | 961216.5327 | 2500888.2455 | 1706907.6156 | 7633670.1699 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 18478263.0758 | 34675096.3729 | 2371.3737 | 0.7176 | 25749.948 | 48320.6633 | 524.9475 | 985.0821
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.958 | 3.8382 | 0.2467 | 4 | 20745.7229 | 37159.5035 | 422.9296 | 757.5467 | 133.475 | 0 | 96.5008 | 1103341.1154 | 84442.2132 | 991818.3762 | 639829.441 | 0 | 288782.4217 | 0 | 1212203.2913 | 3153904.307 | 2152604.4957 | 9626925.6615 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 20471518.5674 | 36668351.8645 | 3162.2777 | 0.98678 | 20745.7229 | 37159.5035 | 422.9296 | 757.5467
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.5601 | 5.1544 | 0.33635 | 4 | 17076.6923 | 29115.4624 | 348.1315 | 593.5581 | 134.1746 | 0 | 89.7256 | 1362385.7082 | 104649.043 | 1255038.0972 | 848105.0611 | 0 | 346261.8963 | 0 | 1527411.5243 | 3974011.471 | 2712344.4867 | 12130207.2879 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 22974800.1938 | 39171633.4908 | 4216.965 | 1.3454 | 17076.6923 | 29115.4624 | 348.1315 | 593.5581
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.6574 | 6.8981 | 0.45522 | 4 | 14341.3352 | 23236.4773 | 292.3675 | 473.707 | 134.7039 | 0 | 95.5232 | 1677214.07 | 129118.763 | 1583959.3091 | 1123671.0118 | 0 | 415891.7805 | 0 | 1922643.4244 | 5002323.8019 | 3414188.7823 | 15269010.9429 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 26113603.8488 | 42310437.1458 | 5623.4133 | 1.8209 | 14341.3352 | 23236.4773 | 292.3675 | 473.707
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.5413 | 8.8676 | 0.60041 | 4 | 12261.0345 | 19005.1283 | 249.9578 | 387.4452 | 135.0584 | 0 | 121.8101 | 2005779.3822 | 154569.7696 | 1935955.0824 | 1434907.0848 | 0 | 474723.4208 | 0 | 2342314.5485 | 6094221.9805 | 4159431.7254 | 18601902.9943 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 29446495.9001 | 45643329.1972 | 7498.9421 | 2.4016 | 12261.0345 | 19005.1283 | 249.9578 | 387.4452
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.3124 | 11.091 | 0.77602 | 4 | 10636.0474 | 15853.9628 | 216.8302 | 323.2045 | 135.3107 | 0 | 99.1348 | 2352051.8695 | 181313.6238 | 2315005.3724 | 1786412.4286 | 0 | 523352.5424 | 0 | 2791672.9763 | 7263360.4336 | 4957392.743 | 22170561.9897 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 33015154.8956 | 49211988.1926 | 10000 | 3.1041 | 10636.0474 | 15853.9628 | 216.8302 | 323.2045
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.5157 | 13.7234 | 0.99063 | 4 | 9353.7843 | 13441.3029 | 190.6895 | 274.0191 | 135.4995 | 0 | 118.7377 | 2736763.9257 | 210929.5533 | 2744650.8036 | 2202628.0461 | 0 | 570550.2691 | 0 | 3301553.8131 | 8589965.78 | 5862828.151 | 26219870.342 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 37064463.2478 | 53261296.5449 | 13335.2143 | 3.9625 | 9353.7843 | 13441.3029 | 190.6895 | 274.0191
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.9755 | 16.7095 | 1.2434 | 4 | 8338.382 | 11594.8345 | 169.9892 | 236.3764 | 135.6176 | 0 | 147.315 | 3147680.738 | 242432.1529 | 3212566.2976 | 2675094.5639 | 0 | 611170.9816 | 0 | 3856688.4463 | 10034312.2216 | 6848624.2757 | 30628569.6776 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 41473162.5835 | 57669995.8805 | 17782.7941 | 4.9738 | 8338.382 | 11594.8345 | 169.9892 | 236.3764
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.2271 | 19.9064 | 1.5264 | 4 | 7536.0986 | 10188.961 | 153.6336 | 207.7158 | 135.6502 | 0 | 164.1488 | 3563703.9375 | 274142.7779 | 3695437.2606 | 3181782.5418 | 0 | 639004.5683 | 0 | 4428087.7236 | 11520975.9311 | 7863302.8054 | 35166437.5463 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 46011030.4522 | 62207863.7492 | 23713.7371 | 6.1054 | 7536.0986 | 10188.961 | 153.6336 | 207.7158
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.7035 | 23.1408 | 1.8259 | 4 | 6905.7879 | 9123.4133 | 140.7838 | 185.9931 | 135.5923 | 0 | 144.0151 | 3963797.9797 | 304405.4512 | 4168624.0765 | 3695916.3759 | 0 | 650546.7224 | 0 | 4985483.3362 | 12971204.9776 | 8853113.9288 | 39593092.8483 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 50437685.7542 | 66634519.0512 | 31622.7766 | 7.3037 | 6905.7879 | 9123.4133 | 140.7838 | 185.9931
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.8017 | 26.2348 | 2.1256 | 4 | 6413.7955 | 8318.7534 | 130.7539 | 169.589 | 135.4567 | 0 | 199.8616 | 4329697.347 | 331825.7864 | 4609275.5216 | 4189666.9031 | 0 | 645083.3415 | 0 | 5501164.0708 | 14312900.4684 | 9768848.6704 | 43688462.1093 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 54533055.0152 | 70729888.3122 | 42169.6503 | 8.5025 | 6413.7955 | 8318.7534 | 130.7539 | 169.589
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.0575 | 29.0582 | 2.4105 | 4 | 6032.0993 | 7711.9447 | 122.9725 | 157.2184 | 135.2686 | 0 | 215.5121 | 4650878.5823 | 355651.0288 | 5002682.2061 | 4642334.3765 | 0 | 625233.0625 | 0 | 5957943.9099 | 15501347.9112 | 10579988.4702 | 47316059.5475 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 58160652.4533 | 74357485.7504 | 56234.1325 | 9.6419 | 6032.0993 | 7711.9447 | 122.9725 | 157.2184
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.1413 | 31.5267 | 2.6688 | 4 | 5737.5587 | 7254.8145 | 116.9679 | 147.8992 | 135.0564 | 0 | 228.4243 | 4922602.1107 | 375600.1651 | 5340662.119 | 5040027.574 | 0 | 594985.551 | 0 | 6346812.2327 | 16513103.5194 | 11270532.4623 | 50404325.7343 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 61248918.6402 | 77445751.9372 | 74989.4209 | 10.6751 | 5737.5587 | 7254.8145 | 116.9679 | 147.8992
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 119.9124 | 33.6118 | 2.894 | 4 | 5511.2914 | 6910.4751 | 112.3551 | 140.8794 | 134.8435 | 0 | 200.6853 | 5146046.1324 | 391852.1634 | 5622252.2612 | 5377866.4768 | 0 | 558953.6385 | 0 | 6667818.5622 | 17348296.1413 | 11840568.5883 | 52953653.9643 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 63798246.8702 | 79995080.1672 | 100000 | 11.5759 | 5511.2914 | 6910.4751 | 112.3551 | 140.8794
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.3165 | 35.3108 | 3.083 | 4 | 5338.1735 | 6651.5574 | 108.8259 | 135.601 | 134.6478 | 0 | 232.2915 | 5324162.4841 | 404696.6153 | 5849255.3457 | 5654494.2087 | 0 | 520703.4232 | 0 | 6923791.71 | 18014285.7644 | 12295120.1908 | 54986509.742 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 65831102.6479 | 82027935.9449 | 133352.1432 | 12.3321 | 5338.1735 | 6651.5574 | 108.8259 | 135.601
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.4586 | 36.6617 | 3.2373 | 4 | 5206.1632 | 6456.9536 | 106.1347 | 131.6337 | 134.478 | 0 | 235.2324 | 5463340.4224 | 414657.4196 | 6028308.3732 | 5875353.3535 | 0 | 483381.746 | 0 | 7123366.1127 | 18533537.422 | 12649520.1166 | 56571464.966 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 67416057.8719 | 83612891.1689 | 177827.941 | 12.9493 | 5206.1632 | 6456.9536 | 106.1347 | 131.6337
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.8124 | 38.3279 | 3.4018 | 4 | 5104.2224 | 6294.5214 | 104.0565 | 128.3223 | 134.2795 | 0 | 207.252 | 5632900.6077 | 426777.7135 | 6247369.2086 | 6147993.216 | 0 | 468314.055 | 0 | 7380108.3723 | 19201528.1165 | 13105437.4914 | 58610428.7812 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 69455021.687 | 85651854.9841 | 237137.3706 | 13.6074 | 5104.2224 | 6294.5214 | 104.0565 | 128.3223
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.254 | 39.2263 | 3.5057 | 4 | 5026.6091 | 6181.64 | 102.4742 | 126.0211 | 134.1716 | 0 | 241.4606 | 5723247.9543 | 433213.2817 | 6364727.2785 | 6295292.7087 | 0 | 440202.5439 | 0 | 7510106.6692 | 19539757.0184 | 13336285.6669 | 59642833.1216 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70487426.0274 | 86684259.3245 | 316227.766 | 14.0229 | 5026.6091 | 6181.64 | 102.4742 | 126.0211
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.469 | 39.282 | 3.5448 | 4 | 4966.1985 | 6108.507 | 101.2427 | 124.5302 | 134.1642 | 0 | 600.0656 | 5728802.9288 | 433606.4129 | 6371986.9957 | 6304453.0754 | 0 | 394742.2551 | 0 | 7501100.7505 | 19516325.4654 | 13320293.1505 | 59571311.0343 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 70415903.9402 | 86612737.2372 | 421696.5034 | 14.179 | 4966.1985 | 6108.507 | 101.2427 | 124.5302
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2239 | 40.5161 | 3.6551 | 4 | 4921.5945 | 6029.4203 | 100.3334 | 122.9179 | 134.0108 | 0 | 216.2641 | 5851524.5228 | 442308.6114 | 6532330.9167 | 6507288.7658 | 0 | 397247.8544 | 0 | 7694973.2617 | 20020741.971 | 13664567.7803 | 61110983.6841 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 71955576.5899 | 88152409.887 | 562341.3252 | 14.6204 | 4921.5945 | 6029.4203 | 100.3334 | 122.9179
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.8265 | 40.9293 | 3.7036 | 4 | 4888.3956 | 5981.7077 | 99.6566 | 121.9452 | 133.9576 | 0 | 219.8316 | 5892268.6693 | 445186.0139 | 6585824.6331 | 6575127.0018 | 0 | 381907.6372 | 0 | 7753322.4426 | 20172554.5704 | 13768182.9989 | 61574373.9672 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 72418966.8731 | 88615800.1701 | 749894.2093 | 14.8145 | 4888.3956 | 5981.7077 | 99.6566 | 121.9452
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.9714 | 41.2238 | 3.7393 | 4 | 4863.3682 | 5946.2393 | 99.1463 | 121.2221 | 133.9192 | 0 | 211.6398 | 5921197.5319 | 447225.5765 | 6623882.4824 | 6623462.8923 | 0 | 369127.9961 | 0 | 7794109.6269 | 20278674.4575 | 13840612.0024 | 61898292.5661 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 72742885.472 | 88939718.769 | 1000000 | 14.9573 | 4863.3682 | 5946.2393 | 99.1463 | 121.2221
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.8339 | 41.4454 | 3.7664 | 4 | 4844.5237 | 5919.6204 | 98.7622 | 120.6795 | 133.8901 | 0 | 220.6207 | 5942903.8933 | 448754.1347 | 6652479.4456 | 6659845.1466 | 0 | 359087.5767 | 0 | 7824597.3768 | 20357997.3288 | 13894751.4919 | 62140416.3943 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 72985009.3002 | 89181842.5972 | 1333521.4322 | 15.0655 | 4844.5237 | 5919.6204 | 98.7622 | 120.6795
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4723 | 41.6092 | 3.7866 | 4 | 4830.3471 | 5899.698 | 98.4732 | 120.2733 | 133.8684 | 0 | 235.3499 | 5958920.7091 | 449881.0286 | 6673603.4615 | 6686754.4385 | 0 | 351200.8315 | 0 | 7846940.583 | 20416129.7681 | 13934428.0763 | 62317858.8967 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73162451.8026 | 89359285.0996 | 1778279.41 | 15.1464 | 4830.3471 | 5899.698 | 98.4732 | 120.2733
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.9593 | 41.734 | 3.802 | 4 | 4819.6899 | 5884.7143 | 98.2559 | 119.9679 | 133.8518 | 0 | 204.4866 | 5971109.2769 | 450738.0145 | 6689691.3431 | 6707267.8732 | 0 | 345182.0556 | 0 | 7863955.5396 | 20460399.1951 | 13964642.8698 | 62452986.1677 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73297579.0736 | 89494412.3706 | 2371373.7057 | 15.2079 | 4819.6899 | 5884.7143 | 98.2559 | 119.9679
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.3077 | 41.8232 | 3.8133 | 4 | 4811.6828 | 5873.5587 | 98.0927 | 119.7404 | 133.8399 | 0 | 211.3013 | 5979814.1732 | 451349.7406 | 6701188.1773 | 6721937.8525 | 0 | 340435.2822 | 0 | 7875942.8381 | 20491587.6866 | 13985929.6562 | 62548185.4067 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73392778.3125 | 89589611.6096 | 3162277.6602 | 15.253 | 4811.6828 | 5873.5587 | 98.0927 | 119.7404
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.5855 | 41.8943 | 3.822 | 4 | 4805.6696 | 5865.1099 | 97.9701 | 119.5682 | 133.8304 | 0 | 200.9042 | 5986747.6066 | 451836.8143 | 6710349.2367 | 6733633.4379 | 0 | 336951.3538 | 0 | 7885612.1952 | 20516745.3704 | 14003100.2923 | 62624976.3071 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73469569.2129 | 89666402.51 | 4216965.0343 | 15.2881 | 4805.6696 | 5865.1099 | 97.9701 | 119.5682
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.7876 | 41.9461 | 3.8285 | 4 | 4801.1552 | 5858.8041 | 97.878 | 119.4396 | 133.8235 | 0 | 217.9327 | 5991785.1751 | 452190.5958 | 6717007.6899 | 6742137.5421 | 0 | 334255.7405 | 0 | 7892576.93 | 20534866.1816 | 14015468.1182 | 62680287.9733 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73524880.8791 | 89721714.1762 | 5623413.2519 | 15.314 | 4801.1552 | 5858.8041 | 97.878 | 119.4396
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.9339 | 41.9835 | 3.8333 | 4 | 4797.7671 | 5854.1002 | 97.809 | 119.3438 | 133.8185 | 0 | 202.1107 | 5995430.3192 | 452446.5307 | 6721826.9729 | 6748294.5356 | 0 | 332173.9225 | 0 | 7897567.1896 | 20547849.8135 | 14024329.7138 | 62719918.9977 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73564511.9036 | 89761345.2007 | 7498942.0933 | 15.3331 | 4797.7671 | 5854.1002 | 97.809 | 119.3438
1 | 3100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.0434 | 42.0115 | 3.8368 | 4 | 4795.2247 | 5850.5737 | 97.7571 | 119.2719 | 133.8147 | 0 | 227.7823 | 5998155.5975 | 452637.8497 | 6725430.7565 | 6752899.6358 | 0 | 330599.9604 | 0 | 7901292.282 | 20557541.7398 | 14030944.6526 | 62749502.4743 | 961560.8286 | 9883032.0773 | 9883032.0773 | 1478867.319 | 4834933.9008 | 0 | 73594095.3802 | 89790928.6773 | 10000000 | 15.3474 | 4795.2247 | 5850.5737 | 97.7571 | 119.2719
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.2035 | [19 empty] | 100 | 0
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.6873 | [19 empty] | 133.3521 | 0
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.1484 | 0.0014884 | 4 | 2038462.0891 | 4850191.1055 | 41556.8069 | 98877.7061 | 101.8791 | 0 | 55.1308 | 95424.6514 | 5983.2466 | 75151.2184 | 54216.5819 | 0 | 60992.8813 | 0 | 113789.746 | 296057.5777 | 202065.3801 | 903681.2834 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12136061.5163 | 28875797.0712 | 177.8279 | 0.0059535 | 2038462.0891 | 4850191.1055 | 41556.8069 | 98877.7061
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.21655 | 0.0054033 | 4 | 573202.1419 | 1347711.6033 | 11685.501 | 27474.9239 | 108.966 | 0 | 46.8985 | 129776.6854 | 8501.2811 | 101161.1097 | 65335.9971 | 0 | 68598.2854 | 0 | 145615.6099 | 378861.9471 | 258581.0637 | 1156431.9795 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12388812.2124 | 29128547.7673 | 237.1374 | 0.021613 | 573202.1419 | 1347711.6033 | 11685.501 | 27474.9239
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.31826 | 0.011554 | 4 | 275638.0274 | 637859.4576 | 5619.254 | 13003.6278 | 115.4998 | 0 | 57.7961 | 176233.4863 | 12024.4571 | 137014.5797 | 81624.0843 | 0 | 79334.719 | 0 | 189630.2173 | 493378.927 | 336741.2556 | 1505981.7264 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 12738361.9593 | 29478097.5142 | 316.2278 | 0.046214 | 275638.0274 | 637859.4576 | 5619.254 | 13003.6278
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.45291 | 0.020456 | 4 | 160868.3159 | 365448.7918 | 3279.5182 | 7450.1679 | 120.736 | 0 | 340.3893 | 231887.6575 | 16353.5961 | 181032.9944 | 102883.5511 | 0 | 91175.4173 | 0 | 243099.9544 | 632496.2147 | 431691.6631 | 1930621.0487 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13163001.2816 | 29902736.8365 | 421.6965 | 0.081825 | 160868.3159 | 365448.7918 | 3279.5182 | 7450.1679
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6044 | 0.63403 | 0.032966 | 4 | 103833.3092 | 230781.9066 | 2116.7825 | 4704.8013 | 124.9928 | 0 | 457.8618 | 299758.7538 | 21720.1787 | 236244.8745 | 131079.8716 | 0 | 105228.8103 | 0 | 309672.6707 | 805704.7666 | 549910.0588 | 2459319.9851 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 13691700.218 | 30431435.7729 | 562.3413 | 0.13186 | 103833.3092 | 230781.9066 | 2116.7825 | 4704.8013
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4601 | 0.88692 | 0.050661 | 4 | 70973.0952 | 153579.1397 | 1446.8825 | 3130.9185 | 128.508 | 0 | 613.6264 | 385849.4394 | 28612.1987 | 308258.3934 | 170731.6105 | 0 | 123575.6877 | 0 | 396640.6586 | 1031977.6314 | 704345.9385 | 3149991.5582 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 14382371.7911 | 31122107.346 | 749.8942 | 0.20265 | 70973.0952 | 153579.1397 | 1446.8825 | 3130.9185
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5842 | 1.2217 | 0.07462 | 4 | 51035.9035 | 107119.1054 | 1040.4359 | 2183.7679 | 131.2277 | 0 | 87.5577 | 489270.8699 | 36937.7261 | 397513.8044 | 222882.7112 | 0 | 145131.4656 | 0 | 503777.2651 | 1310725.105 | 894596.8169 | 4000835.7643 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 15233215.9972 | 31972951.5521 | 1000 | 0.29848 | 51035.9035 | 107119.1054 | 1040.4359 | 2183.7679
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0728 | 1.6662 | 0.10675 | 4 | 38147.7073 | 77351.2017 | 777.6926 | 1576.9089 | 133.319 | 0 | 68.6573 | 614171.3837 | 46999.1947 | 508820.0103 | 291585.9919 | 0 | 171011.2302 | 0 | 636709.2462 | 1656586.8516 | 1130654.5657 | 5056538.4744 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 16288918.7073 | 33028654.2622 | 1333.5214 | 0.427 | 38147.7073 | 77351.2017 | 777.6926 | 1576.9089
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0756 | 2.2628 | 0.14959 | 4 | 29452.0284 | 57428.5427 | 600.4194 | 1170.7585 | 134.8177 | 0 | 65.6375 | 766726.956 | 59251.5881 | 649292.6121 | 384552.2352 | 0 | 203368.5051 | 0 | 804644.8396 | 2093520.8174 | 1428870.9754 | 6390228.529 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 17622608.7619 | 34362344.3168 | 1778.2794 | 0.59835 | 29452.0284 | 57428.5427 | 600.4194 | 1170.7585
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7326 | 3.0671 | 0.20883 | 4 | 23120.8686 | 43161.2469 | 471.3502 | 879.9004 | 136.2397 | 0 | 104.4174 | 955843.8162 | 74542.238 | 827324.8961 | 509167.8114 | 0 | 242042.2646 | 0 | 1017479.2002 | 2647272.1653 | 1806817.6488 | 8080490.0404 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 19312870.2733 | 36052605.8282 | 2371.3737 | 0.8353 | 23120.8686 | 43161.2469 | 471.3502 | 879.9004
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.2675 | 4.13 | 0.28652 | 4 | 18686.9174 | 33293.1888 | 380.9581 | 678.7267 | 137.1965 | 0 | 92.1739 | 1183591.5799 | 92822.5427 | 1048994.7195 | 673426.595 | 0 | 289252.0384 | 0 | 1282354.1154 | 3336422.3614 | 2277176.8183 | 10184040.7705 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 21416421.0034 | 38156156.5583 | 3162.2777 | 1.1461 | 18686.9174 | 33293.1888 | 380.9581 | 678.7267
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.9622 | 5.5384 | 0.38927 | 4 | 15439.2712 | 26190.0182 | 314.7504 | 533.9189 | 137.9228 | 0 | 81.9923 | 1459690.7615 | 114863.915 | 1325925.8202 | 888225.4351 | 0 | 346488.5946 | 0 | 1612725.8653 | 4195981.8859 | 2863843.8559 | 12807746.1334 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 24040126.3664 | 40779861.9212 | 4216.965 | 1.5571 | 15439.2712 | 26190.0182 | 314.7504 | 533.9189
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.1884 | 7.4096 | 0.52595 | 4 | 12997.8399 | 20954.7014 | 264.9785 | 427.1899 | 138.4733 | 0 | 116.7246 | 1796510.7877 | 141671.8489 | 1672998.8329 | 1174950.1841 | 0 | 416097.5322 | 0 | 2028869.3825 | 5278701.9549 | 3602822.5507 | 16112623.0738 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 27345003.3067 | 44084738.8616 | 5623.4133 | 2.1038 | 12997.8399 | 20954.7014 | 264.9785 | 427.1899
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.4005 | 9.8791 | 0.70641 | 4 | 11141.7509 | 17065.9733 | 227.1397 | 347.9129 | 138.8894 | 0 | 97.8351 | 2204998.3905 | 174063.9307 | 2105313.489 | 1553533.7605 | 0 | 500213.8916 | 0 | 2549868.1503 | 6634233.8772 | 4528000.9411 | 20250226.431 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 31482606.6639 | 48222342.2188 | 7498.9421 | 2.8256 | 11141.7509 | 17065.9733 | 227.1397 | 347.9129
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.6452 | 12.6614 | 0.92403 | 4 | 9708.7183 | 14237.7012 | 197.9254 | 290.2548 | 139.1664 | 0 | 84.3076 | 2631184.0245 | 207768.1283 | 2567110.5309 | 1981856.9746 | 0 | 571506.4353 | 0 | 3104176.1765 | 8076429.6571 | 5512329.195 | 24652361.122 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 35884741.355 | 52624476.9098 | 10000 | 3.6961 | 9708.7183 | 14237.7012 | 197.9254 | 290.2548
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.4233 | 15.6029 | 1.1745 | 4 | 8577.3951 | 12140.6489 | 174.8618 | 247.5035 | 139.3409 | 0 | 141.7248 | 3052964.5137 | 241011.3932 | 3033659.008 | 2435730.4249 | 0 | 620169.0946 | 0 | 3659578.4294 | 9521472.3906 | 6498600.5533 | 29063185.8077 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 40295566.0406 | 57035301.5955 | 13335.2143 | 4.6979 | 8577.3951 | 12140.6489 | 174.8618 | 247.5035
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.3413 | 18.8771 | 1.4648 | 4 | 7681.5888 | 10538.6782 | 156.5996 | 214.8452 | 139.4337 | 0 | 123.2932 | 3495497.4113 | 275712.1769 | 3532827.8343 | 2941209.9385 | 0 | 659309.4923 | 0 | 4252777.1728 | 11064853.8391 | 7551990.1052 | 33774177.9706 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 45006558.2035 | 61746293.7583 | 17782.7941 | 5.859 | 7681.5888 | 10538.6782 | 156.5996 | 214.8452
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.883 | 22.3158 | 1.7836 | 4 | 6974.8319 | 9321.1173 | 142.1914 | 190.0236 | 139.4306 | 0 | 155.8988 | 3935516.5426 | 309965.0717 | 4038917.4637 | 3472623.8804 | 0 | 683043.7398 | 0 | 4851626.0123 | 12622935.6786 | 8615412.9761 | 38530041.3652 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 49762421.5981 | 66502157.153 | 23713.7371 | 7.1346 | 6974.8319 | 9321.1173 | 142.1914 | 190.0236
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 86.4487 | 25.727 | 2.1147 | 4 | 6420.5336 | 8399.5265 | 130.8913 | 171.2357 | 139.3327 | 0 | 179.5087 | 4350955.2836 | 341996.7687 | 4526023.7994 | 4000633.9048 | 0 | 688543.8834 | 0 | 5424179.9195 | 14112603.4983 | 9632141.8726 | 43077078.9302 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 54309459.1631 | 71049194.718 | 31622.7766 | 8.4587 | 6420.5336 | 8399.5265 | 130.8913 | 171.2357
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.5035 | 28.946 | 2.4405 | 4 | 5988.464 | 7703.2631 | 122.0829 | 157.0414 | 139.1591 | 0 | 155.0325 | 4726229.153 | 370607.193 | 4974298.8879 | 4499944.921 | 0 | 676795.1708 | 0 | 5946671.377 | 15472019.093 | 10559970.9491 | 47226536.7448 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 58458916.9777 | 75198652.5326 | 42169.6503 | 9.7619 | 5988.464 | 7703.2631 | 122.0829 | 157.0414
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 107.6466 | 31.8596 | 2.7465 | 4 | 5653.5265 | 7177.2465 | 115.2548 | 146.3179 | 138.9378 | 0 | 209.6871 | 5053505.1532 | 395280.6125 | 5371830.6691 | 4954653.0712 | 0 | 651480.4326 | 0 | 6406432.4761 | 16668223.1628 | 11376404.8063 | 50877810.3839 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 62110190.6168 | 78849926.1717 | 56234.1325 | 10.9861 | 5653.5265 | 7177.2465 | 115.2548 | 146.3179
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.4823 | 34.3677 | 3.0206 | 4 | 5395.1007 | 6780.569 | 109.9864 | 138.2311 | 138.7009 | 0 | 212.2567 | 5327068.9782 | 415734.5994 | 5708423.5664 | 5352618.4109 | 0 | 615846.2573 | 0 | 6793679.8068 | 17675761.2819 | 12064070.2755 | 53953203.1764 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 65185583.4093 | 81925318.9642 | 74989.4209 | 12.0824 | 5395.1007 | 6780.569 | 109.9864 | 138.2311
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9265 | 36.4545 | 3.2562 | 4 | 5196.7776 | 6481.993 | 105.9433 | 132.1442 | 138.472 | 0 | 233.6096 | 5548981.8198 | 432162.4417 | 5984960.608 | 5686319.9203 | 0 | 574968.6353 | 0 | 7108683.4358 | 18495336.1084 | 12623446.9352 | 56454859.9045 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 67687240.1374 | 84426975.6923 | 100000 | 13.0248 | 5196.7776 | 6481.993 | 105.9433 | 132.1442
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.0165 | 38.143 | 3.4523 | 4 | 5045.1469 | 6257.3459 | 102.8521 | 127.5645 | 138.2658 | 0 | 240.0276 | 5724897.8204 | 445070.2953 | 6206541.2696 | 5958202.3011 | 0 | 532988.0423 | 0 | 7358402.8942 | 19145054.9147 | 13066893.3708 | 58438050.9083 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 69670431.1413 | 86410166.6961 | 133352.1432 | 13.8094 | 5045.1469 | 6257.3459 | 102.8521 | 127.5645
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.1667 | 40.1148 | 3.6554 | 4 | 4928.3785 | 6073.2321 | 100.4717 | 123.8111 | 138.0261 | 0 | 201.4448 | 5927040.0762 | 459840.4249 | 6462922.3392 | 6276828.0951 | 0 | 513033.0594 | 0 | 7659468.958 | 19928367.0556 | 13601520.0024 | 60829020.0108 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 72061400.2437 | 88801135.7986 | 177827.941 | 14.6217 | 4928.3785 | 6073.2321 | 100.4717 | 123.8111
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 141.2345 | 41.2353 | 3.7895 | 4 | 4838.8473 | 5943.2084 | 98.6464 | 121.1603 | 137.892 | 0 | 230.9419 | 6040582.7569 | 468126.945 | 6607501.1468 | 6460062.6921 | 0 | 478305.8709 | 0 | 7821285.9706 | 20349381.7292 | 13888871.1681 | 62114118.2798 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 73346498.5127 | 90086234.0676 | 237137.3706 | 15.1578 | 4838.8473 | 5943.2084 | 98.6464 | 121.1603
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.4601 | 42.1201 | 3.8962 | 4 | 4770.9061 | 5845.0263 | 97.2614 | 119.1588 | 137.7825 | 0 | 236.5732 | 6129422.603 | 474587.9354 | 6721140.3051 | 6605686.8363 | 0 | 448601.0299 | 0 | 7947981.0968 | 20679016.4588 | 14113853.6445 | 63120289.9099 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 74352670.1428 | 91092405.6977 | 316227.766 | 15.5846 | 4770.9061 | 5845.0263 | 97.2614 | 119.1588
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.9102 | 42.7896 | 3.9784 | 4 | 4719.455 | 5771.3664 | 96.2125 | 117.6571 | 137.6975 | 0 | 236.3681 | 6196160.0096 | 479426.2598 | 6806833.5534 | 6716258.3808 | 0 | 423241.9573 | 0 | 8042548.8628 | 20925062.3874 | 14281785.0464 | 63871316.4576 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 75103696.6905 | 91843432.2454 | 421696.5034 | 15.9136 | 4719.455 | 5771.3664 | 96.2125 | 117.6571
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.1003 | 43.3862 | 4.0491 | 4 | 4678.8542 | 5712.4016 | 95.3848 | 116.455 | 137.6205 | 0 | 243.9326 | 6255286.7849 | 483702.2059 | 6882984.8641 | 6815059.3038 | 0 | 403418.8566 | 0 | 8127776.286 | 21146806.66 | 14433130.0689 | 64548165.0302 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 75780545.2631 | 92520280.818 | 562341.3252 | 16.1964 | 4678.8542 | 5712.4016 | 95.3848 | 116.455
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4964 | 43.7656 | 4.0968 | 4 | 4649.8428 | 5671.3591 | 94.7933 | 115.6183 | 137.5706 | 0 | 241.342 | 6292707.5773 | 486402.4828 | 6931302.6184 | 6878029.151 | 0 | 386680.8336 | 0 | 8180297.8386 | 21283456.9663 | 14526396.7108 | 64965274.1788 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 76197654.4117 | 92937389.9666 | 749894.2093 | 16.3871 | 4649.8428 | 5671.3591 | 94.7933 | 115.6183
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.5318 | 44.0464 | 4.1326 | 4 | 4627.9779 | 5640.6326 | 94.3476 | 114.9919 | 137.5332 | 0 | 211.9995 | 6320326.4621 | 488392.6439 | 6967023.2259 | 6924719.2483 | 0 | 373248.9846 | 0 | 8218747.1203 | 21383494.1102 | 14594674.1171 | 65270625.9124 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 76503006.1453 | 93242741.7002 | 1000000 | 16.5305 | 4627.9779 | 5640.6326 | 94.3476 | 114.9919
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.3212 | 44.2603 | 4.16 | 4 | 4611.5163 | 5617.5216 | 94.012 | 114.5208 | 137.5046 | 0 | 219.2039 | 6341308.815 | 489902.9995 | 6994194.0408 | 6960312.1165 | 0 | 362812.7567 | 0 | 8247926.9841 | 21459414.1303 | 14646491.0908 | 65502362.9338 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 76734743.1667 | 93474478.7216 | 1333521.4322 | 16.6398 | 4611.5163 | 5617.5216 | 94.012 | 114.5208
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.9083 | 44.4192 | 4.1804 | 4 | 4599.1332 | 5600.2074 | 93.7596 | 114.1678 | 137.4832 | 0 | 213.0923 | 6356873.404 | 491022.4648 | 7014368.1701 | 6986783.6893 | 0 | 354667.1717 | 0 | 8269448.811 | 21515409.5089 | 14684709.0873 | 65673282.3071 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 76905662.54 | 93645398.0949 | 1778279.41 | 16.7218 | 4599.1332 | 5600.2074 | 93.7596 | 114.1678
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3493 | 44.5384 | 4.1959 | 4 | 4589.8246 | 5587.2156 | 93.5698 | 113.9029 | 137.4671 | 0 | 216.0353 | 6368540.2792 | 491861.0854 | 7029500.8482 | 7006664.7731 | 0 | 348400.4614 | 0 | 8285537.3044 | 21557268.4687 | 14713278.6875 | 65801051.908 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77033432.1409 | 93773167.6958 | 2371373.7057 | 16.7835 | 4589.8246 | 5587.2156 | 93.5698 | 113.9029
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.6823 | 44.6284 | 4.2075 | 4 | 4582.831 | 5577.4598 | 93.4272 | 113.7041 | 137.4549 | 0 | 270.2584 | 6377334.4938 | 492492.9321 | 7040913.4929 | 7021672.5075 | 0 | 343623.9018 | 0 | 8297654.5579 | 21588795.0768 | 14734796.2453 | 65897283.2081 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77129663.441 | 93869398.9959 | 3162277.6602 | 16.8301 | 4582.831 | 5577.4598 | 93.4272 | 113.7041
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.9212 | 44.6929 | 4.2161 | 4 | 4577.579 | 5570.1915 | 93.3201 | 113.5559 | 137.4461 | 0 | 249.2716 | 6383638.7119 | 492945.712 | 7049098.1212 | 7032443.084 | 0 | 339898.2144 | 0 | 8306229.2989 | 21611104.7939 | 14750023.0857 | 65965381.0219 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77197761.2549 | 93937496.8097 | 4216965.0343 | 16.8643 | 4577.579 | 5570.1915 | 93.3201 | 113.5559
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1038 | 44.7423 | 4.2226 | 4 | 4573.6362 | 5564.7239 | 93.2398 | 113.4444 | 137.4393 | 0 | 266.7987 | 6388453.1838 | 493291.4136 | 7055350.3888 | 7040674.8685 | 0 | 337101.1703 | 0 | 8312799.6997 | 21628199.629 | 14761690.6618 | 66017561.0155 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77249941.2484 | 93989676.8033 | 5623413.2519 | 16.8903 | 4573.6362 | 5564.7239 | 93.2398 | 113.4444
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.2501 | 44.7818 | 4.2276 | 4 | 4570.6771 | 5560.5799 | 93.1794 | 113.3599 | 137.434 | 0 | 247.2065 | 6392308.5931 | 493568.2067 | 7060358.1616 | 7047270.5304 | 0 | 335063.1768 | 0 | 8318141.7807 | 21642098.628 | 14771177.0143 | 66059986.0916 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77292366.3245 | 94032101.8794 | 7498942.0933 | 16.9105 | 4570.6771 | 5560.5799 | 93.1794 | 113.3599
1 | 3200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.3427 | 44.8068 | 4.2311 | 4 | 4568.4567 | 5557.5505 | 93.1342 | 113.2982 | 137.4305 | 0 | 244.3497 | 6394747.1618 | 493743.2383 | 7063526.3492 | 7051444.8732 | 0 | 333383.0864 | 0 | 8321369.4365 | 21650496.3261 | 14776908.6158 | 66085619.0872 | 961560.8286 | 10270819.4043 | 10270819.4043 | 1478867.319 | 4990048.8316 | 0 | 77317999.3201 | 94057734.875 | 10000000 | 16.9243 | 4568.4567 | 5557.5505 | 93.1342 | 113.2982
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.5853 | [19 empty] | 100 | 0
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.9348 | [19 empty] | 133.3521 | 0
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.15826 | 0.0024832 | 4 | 1265085.1994 | 3005869.7776 | 25790.4729 | 61278.7212 | 104.3003 | 0 | 58.8404 | 101410.7137 | 6450.3957 | 78980.1329 | 55517.6347 | 0 | 61069.2366 | 0 | 118336.9643 | 307888.5069 | 210140.2324 | 939793.8173 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12565821.4681 | 29856663.408 | 177.8279 | 0.0099328 | 1265085.1994 | 3005869.7776 | 25790.4729 | 61278.7212
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1813 | 0.23524 | 0.0071105 | 4 | 451737.6556 | 1059670.0834 | 9209.2831 | 21602.808 | 111.9482 | 0 | 55.4956 | 139985.3292 | 9335.2041 | 107853.5437 | 67844.6317 | 0 | 69626.2212 | 0 | 153911.5226 | 400446.2103 | 273312.7669 | 1222315.4296 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 12848343.0804 | 30139185.0204 | 237.1374 | 0.028442 | 451737.6556 | 1059670.0834 | 9209.2831 | 21602.808
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.34201 | 0.014181 | 4 | 232843.3484 | 537668.2877 | 4746.8266 | 10961.0953 | 118.4898 | 0 | 65.5774 | 188457.5668 | 13091.8179 | 144831.6861 | 84542.7894 | 0 | 79767.884 | 0 | 199169.7802 | 518198.9128 | 353681.4059 | 1581741.843 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13207769.4938 | 30498611.4338 | 316.2278 | 0.056724 | 232843.3484 | 537668.2877 | 4746.8266 | 10961.0953
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0404 | 0.48921 | 0.024508 | 4 | 139389.1486 | 315766.4784 | 2841.6363 | 6437.3268 | 123.9674 | 0 | 353.4115 | 248947.6928 | 17903.8349 | 192124.4134 | 107187.3449 | 0 | 92078.8619 | 0 | 256714.4377 | 667918.3075 | 455867.9692 | 2038742.8624 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 13664770.5132 | 30955612.4531 | 421.6965 | 0.098033 | 139389.1486 | 315766.4784 | 2841.6363 | 6437.3268
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6822 | 0.68606 | 0.039038 | 4 | 91139.8969 | 201870.1272 | 1858.0101 | 4115.3956 | 128.3622 | 0 | 477.3094 | 322414.9676 | 23865.3134 | 251040.6067 | 137621.2528 | 0 | 106360.532 | 0 | 328108.0423 | 853669.8217 | 582647.1945 | 2605727.7309 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14231755.3817 | 31522597.3217 | 562.3413 | 0.15615 | 91139.8969 | 201870.1272 | 1858.0101 | 4115.3956
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5379 | 0.95191 | 0.059111 | 4 | 63204.1998 | 136332.9612 | 1288.5031 | 2779.3318 | 131.9034 | 0 | 630.9395 | 412494.2887 | 31258.5397 | 325436.2314 | 178370.8974 | 0 | 123780.5568 | 0 | 417822.8005 | 1087089.2196 | 741960.7298 | 3318213.2638 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 14944240.9146 | 32235082.8546 | 749.8942 | 0.23644 | 63204.1998 | 136332.9612 | 1288.5031 | 2779.3318
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.689 | 1.3122 | 0.086596 | 4 | 45746.2002 | 95664.0439 | 932.5982 | 1950.2409 | 134.7268 | 0 | 85.5689 | 523438.7487 | 40420.0203 | 419910.5077 | 233224.412 | 0 | 145444.1085 | 0 | 531350.7409 | 1382465.6328 | 943561.2012 | 4219815.3721 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 15845843.0229 | 33136684.9629 | 1000 | 0.34639 | 45746.2002 | 95664.0439 | 932.5982 | 1950.2409
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2238 | 1.7949 | 0.12376 | 4 | 34295.0166 | 69222.1648 | 699.1503 | 1411.1875 | 136.9038 | 0 | 80.287 | 658777.4829 | 51631.7149 | 538668.2003 | 307005.1372 | 0 | 171859.5053 | 0 | 673897.3959 | 1753342.7886 | 1196692.4808 | 5351874.706 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 16977902.3568 | 34268744.2967 | 1333.5214 | 0.49505 | 34295.0166 | 69222.1648 | 699.1503 | 1411.1875
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2506 | 2.4253 | 0.17196 | 4 | 26685.8337 | 51823.1349 | 544.0268 | 1056.4847 | 138.4179 | 0 | 83.5299 | 819016.5406 | 64788.6325 | 684679.4844 | 400942.8319 | 0 | 203459.3608 | 0 | 847425.8716 | 2204828.287 | 1504840.6106 | 6729981.6195 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 18356009.2703 | 35646851.2103 | 1778.2794 | 0.68786 | 26685.8337 | 51823.1349 | 544.0268 | 1056.4847
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9689 | 3.2916 | 0.23999 | 4 | 20989.3463 | 39001.4954 | 427.8962 | 795.0982 | 139.9205 | 0 | 107.943 | 1022346.3732 | 81683.2349 | 873256.3685 | 532189.3811 | 0 | 242248.8608 | 0 | 1073172.4452 | 2792174.5645 | 1905716.5137 | 8522787.7419 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 20148815.3927 | 37439657.3327 | 2371.3737 | 0.95995 | 20989.3463 | 39001.4954 | 427.8962 | 795.0982
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.5648 | 4.4269 | 0.32857 | 4 | 17011.7977 | 30168.1024 | 346.8085 | 615.0176 | 140.9099 | 0 | 92.825 | 1265058.6707 | 101682.6019 | 1106124.5214 | 703102.2832 | 0 | 289019.515 | 0 | 1351345.1609 | 3515922.9097 | 2399689.6309 | 10731945.2937 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 22357972.9445 | 39648814.8844 | 3162.2777 | 1.3143 | 17011.7977 | 30168.1024 | 346.8085 | 615.0176
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.3689 | 5.9477 | 0.44722 | 4 | 14064.5394 | 23730.2085 | 286.7247 | 483.7724 | 141.6659 | 0 | 99.8888 | 1563176.4593 | 126183.1626 | 1400150.5973 | 933475.1928 | 0 | 346666.5043 | 0 | 1704164.2474 | 4433885.7995 | 3026218.1654 | 13533920.1287 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 25159947.7795 | 42450789.7195 | 4216.965 | 1.7889 | 14064.5394 | 23730.2085 | 286.7247 | 483.7724
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.7322 | 7.9634 | 0.60467 | 4 | 11856.2681 | 19005.1826 | 241.7061 | 387.4464 | 142.2378 | 0 | 92.921 | 1925761.3085 | 155882.3444 | 1767636.6658 | 1239171.4685 | 0 | 416532.9732 | 0 | 2146944.0565 | 5585908.0363 | 3812497.0137 | 17050333.8668 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 28676361.5176 | 45967203.4575 | 5623.4133 | 2.4187 | 11856.2681 | 19005.1826 | 241.7061 | 387.4464
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.1043 | 10.6158 | 0.81215 | 4 | 10178.4646 | 15501.0085 | 207.5018 | 316.009 | 142.6692 | 0 | 91.7591 | 2364307.8412 | 191676.4334 | 2224025.7238 | 1641634.5397 | 0 | 500546.6691 | 0 | 2699654.5708 | 7023947.418 | 4793988.4404 | 21439781.6364 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 33065809.2872 | 50356651.2272 | 7498.9421 | 3.2486 | 10178.4646 | 15501.0085 | 207.5018 | 316.009
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.0789 | 14.0931 | 1.0838 | 4 | 8889.2706 | 12877.7548 | 181.2198 | 262.5305 | 142.9911 | 0 | 102.9328 | 2893410.2352 | 234679.0108 | 2789215.1964 | 2169300.4418 | 0 | 601950.9262 | 0 | 3388536.7661 | 8816277.5808 | 6017290.6053 | 26910660.7625 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 38536688.4133 | 55827530.3533 | 10000 | 4.3352 | 8889.2706 | 12877.7548 | 181.2198 | 262.5305
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.4017 | 17.6735 | 1.3889 | 4 | 7890.49 | 11002.7338 | 160.8583 | 224.3056 | 143.1686 | 0 | 104.5263 | 3399165.7411 | 275561.9482 | 3342584.3329 | 2711570.5711 | 0 | 671152.3459 | 0 | 4056013.6263 | 10552915.4529 | 7202581.6373 | 32211545.6557 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 43837573.3065 | 61128415.2465 | 13335.2143 | 5.5557 | 7890.49 | 11002.7338 | 160.8583 | 224.3056
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.7387 | 21.243 | 1.7202 | 4 | 7100.5972 | 9613.5191 | 144.7553 | 195.9846 | 143.2307 | 0 | 142.1104 | 3873532.7898 | 313665.3087 | 3872384.7995 | 3253188.2619 | 0 | 708059.2484 | 0 | 4688123.8592 | 12197536.6152 | 8325069.3742 | 37231560.2569 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 48857587.9077 | 66148429.8476 | 17782.7941 | 6.8808 | 7100.5972 | 9613.5191 | 144.7553 | 195.9846
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.524 | 24.9249 | 2.0779 | 4 | 6477.8852 | 8558.2473 | 132.0605 | 174.4714 | 143.1873 | 0 | 160.3523 | 4337496.0966 | 350617.4454 | 4400734.2884 | 3813824.9849 | 0 | 727028.3699 | 0 | 5315583.4622 | 13830057.7926 | 9439298.6227 | 42214641.0627 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 53840668.7135 | 71131510.6535 | 23713.7371 | 8.3115 | 6477.8852 | 8558.2473 | 132.0605 | 174.4714
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.1628 | 28.5209 | 2.4432 | 4 | 5990.0851 | 7759.3655 | 122.116 | 158.1852 | 143.0465 | 0 | 168.7977 | 4769530.6278 | 384658.0185 | 4902203.8151 | 4364170.433 | 0 | 726384.9589 | 0 | 5907309.6628 | 15369607.9868 | 10490073.2648 | 46913938.7677 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 58539966.4185 | 75830808.3584 | 31622.7766 | 9.7728 | 5990.0851 | 7759.3655 | 122.116 | 158.1852
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.0829 | 31.847 | 2.7958 | 4 | 5610.3537 | 7156.4823 | 114.3746 | 145.8946 | 142.835 | 0 | 208.3146 | 5152546.4823 | 414439.3674 | 5355261.9839 | 4874143.5379 | 0 | 707364.8786 | 0 | 6436464.9375 | 16746361.467 | 11429735.8045 | 51116318.4592 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 62742346.11 | 80033188.05 | 42169.6503 | 11.1833 | 5610.3537 | 7156.4823 | 114.3746 | 145.8946
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.9586 | 34.8097 | 3.1214 | 4 | 5316.3004 | 6701.1772 | 108.38 | 136.6126 | 142.5841 | 0 | 204.4218 | 5481542.2635 | 439668.7073 | 5751306.1027 | 5329593.0645 | 0 | 675000.3999 | 0 | 6894073.1098 | 17936964.0628 | 12242346.5406 | 54750494.251 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 66376521.9018 | 83667363.8418 | 56234.1325 | 12.4855 | 5316.3004 | 6701.1772 | 108.38 | 136.6126
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.5165 | 37.34 | 3.4088 | 4 | 5089.6413 | 6357.7459 | 103.7592 | 129.6112 | 142.3249 | 0 | 216.9862 | 5754063.1418 | 460289.2743 | 6084538.5184 | 5720008.3595 | 0 | 633811.9964 | 0 | 7274557.4033 | 18926906.1464 | 12918002.354 | 57772177.1941 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 69398204.8449 | 86689046.7849 | 74989.4209 | 13.6352 | 5089.6413 | 6357.7459 | 103.7592 | 129.6112
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.7003 | 39.4357 | 3.6537 | 4 | 4915.6451 | 6098.7416 | 100.2121 | 124.3311 | 142.0796 | 0 | 205.3805 | 5974174.5698 | 476738.1763 | 6357381.0666 | 6044528.2576 | 0 | 588806.5796 | 0 | 7582235.1734 | 19727420.591 | 13464369.9113 | 60215654.3255 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 71841681.9763 | 89132523.9162 | 100000 | 14.6149 | 4915.6451 | 6098.7416 | 100.2121 | 124.3311
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 135.8755 | 41.7936 | 3.9029 | 4 | 4781.8899 | 5889.4469 | 97.4853 | 120.0643 | 141.7874 | 0 | 225.9013 | 6216810.6796 | 494736.3184 | 6661075.8097 | 6411293.8159 | 0 | 565522.7759 | 0 | 7936281.3658 | 20648576.1586 | 14093077.5141 | 63027374.438 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 74653402.0888 | 91944244.0287 | 133352.1432 | 15.6117 | 4781.8899 | 5889.4469 | 97.4853 | 120.0643
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.9593 | 43.254 | 4.0777 | 4 | 4678.2783 | 5738.3557 | 95.373 | 116.9841 | 141.6133 | 0 | 217.0369 | 6364969.3772 | 505703.3689 | 6847483.9768 | 6638876.5316 | 0 | 526310.1946 | 0 | 8144503.9451 | 21190328.5978 | 14462834.6857 | 64681010.6778 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 76307038.3286 | 93597880.2685 | 177827.941 | 16.3109 | 4678.2783 | 5738.3557 | 95.373 | 116.9841
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.9593 | 44.3951 | 4.2168 | 4 | 4599.3922 | 5624.5132 | 93.7648 | 114.6633 | 141.4713 | 0 | 234.3608 | 6479322.8537 | 514116.3784 | 6992326.7521 | 6817090.33 | 0 | 491004.8158 | 0 | 8304605.8407 | 21606880.8886 | 14747140.1835 | 65952488.0427 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 77578515.6935 | 94869357.6335 | 237137.3706 | 16.8671 | 4599.3922 | 5624.5132 | 93.7648 | 114.6633
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.048 | 45.2714 | 4.3254 | 4 | 4539.4946 | 5538.8751 | 92.5437 | 112.9175 | 141.3587 | 0 | 258.8168 | 6566313.0621 | 520484.8775 | 7103092.3023 | 6954189.5561 | 0 | 460320.066 | 0 | 8425715.9469 | 21921984.542 | 14962204.9016 | 66914305.2545 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 78540332.9053 | 95831174.8452 | 316227.766 | 17.3016 | 4539.4946 | 5538.8751 | 92.5437 | 112.9175
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.4038 | 45.9368 | 4.4091 | 4 | 4494.119 | 5474.5183 | 91.6187 | 111.6055 | 141.271 | 0 | 269.3299 | 6631890.8429 | 525266.8704 | 7186938.7753 | 7058441.978 | 0 | 434432.846 | 0 | 8516418.8119 | 22157974.7909 | 15123273.0956 | 67634638.011 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 79260665.6619 | 96551507.6018 | 421696.5034 | 17.6365 | 4494.119 | 5474.5183 | 91.6187 | 111.6055
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.5574 | 45.9798 | 4.4409 | 4 | 4458.3865 | 5431.7682 | 90.8902 | 110.7339 | 141.2647 | 0 | 232.5511 | 6636094.0302 | 525570.6709 | 7192348.8771 | 7065194.031 | 0 | 397323.0034 | 0 | 8508446.9389 | 22137233.6126 | 15109116.8152 | 67571327.9792 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 79197355.63 | 96488197.57 | 562341.3252 | 17.7637 | 4458.3865 | 5431.7682 | 90.8902 | 110.7339
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.8681 | 46.9108 | 4.5298 | 4 | 4432.5389 | 5386.8174 | 90.3633 | 109.8176 | 141.1396 | 0 | 217.2847 | 6727152.1179 | 532184.4321 | 7309269.8082 | 7211271.9949 | 0 | 397317.7902 | 0 | 8649106.4958 | 22503200.9265 | 15358897.0269 | 68688400.5924 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 80314428.2432 | 97605270.1831 | 749894.2093 | 18.1193 | 4432.5389 | 5386.8174 | 90.3633 | 109.8176
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.8614 | 47.189 | 4.5661 | 4 | 4413.2474 | 5359.9402 | 89.97 | 109.2696 | 141.1012 | 0 | 262.2793 | 6754198.9712 | 534141.6879 | 7344124.1898 | 7254976.4717 | 0 | 383772.3539 | 0 | 8685773.3331 | 22598600.5156 | 15424009.2067 | 68979596.7299 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 80605624.3807 | 97896466.3207 | 1000000 | 18.2645 | 4413.2474 | 5359.9402 | 89.97 | 109.2696
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.6191 | 47.4009 | 4.5938 | 4 | 4398.7211 | 5339.7168 | 89.6739 | 108.8573 | 141.0718 | 0 | 251.2615 | 6774756.4387 | 535627.3983 | 7370651.1835 | 7288286.2861 | 0 | 373276.0445 | 0 | 8713612.9669 | 22671033.5321 | 15473446.2288 | 69200690.079 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 80826717.7298 | 98117559.6697 | 1333521.4322 | 18.375 | 4398.7211 | 5339.7168 | 89.6739 | 108.8573
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.1797 | 47.5575 | 4.6144 | 4 | 4387.7927 | 5324.5738 | 89.4511 | 108.5486 | 141.05 | 0 | 258.7564 | 6789923.9577 | 536722.4643 | 7390243.0463 | 7312914.0351 | 0 | 365073.4823 | 0 | 8734002.0244 | 22724081.6774 | 15509652.678 | 69362613.3656 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 80988641.0164 | 98279482.9563 | 1778279.41 | 18.4577 | 4387.7927 | 5324.5738 | 89.4511 | 108.5486
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5935 | 47.673 | 4.6298 | 4 | 4379.577 | 5313.2394 | 89.2836 | 108.3176 | 141.0338 | 0 | 237.5007 | 6801095.0902 | 537528.3892 | 7404683.736 | 7331080.921 | 0 | 358709.3138 | 0 | 8748908.0056 | 22762863.9828 | 15536122.3983 | 69480991.8369 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81107019.4877 | 98397861.4277 | 2371373.7057 | 18.5194 | 4379.577 | 5313.2394 | 89.2836 | 108.3176
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.9102 | 47.7614 | 4.6416 | 4 | 4373.4041 | 5304.709 | 89.1578 | 108.1437 | 141.0214 | 0 | 231.1 | 6809632.6654 | 538143.988 | 7415726.1487 | 7344980.7896 | 0 | 353901.2115 | 0 | 8760330.0733 | 22792581.8598 | 15556405.4601 | 69571702.1964 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81197729.8472 | 98488571.7872 | 3162277.6602 | 18.5663 | 4373.4041 | 5304.709 | 89.1578 | 108.1437
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.1466 | 47.8273 | 4.6503 | 4 | 4368.7683 | 5298.3146 | 89.0633 | 108.0133 | 141.0121 | 0 | 235.8146 | 6815995.5917 | 538602.5883 | 7423959.4251 | 7355349.2335 | 0 | 350233.15 | 0 | 8768814.5955 | 22814656.8464 | 15571472.092 | 69639083.5224 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81265111.1732 | 98555953.1132 | 4216965.0343 | 18.6014 | 4368.7683 | 5298.3146 | 89.0633 | 108.0133
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.3272 | 47.8776 | 4.657 | 4 | 4365.2879 | 5293.5042 | 88.9923 | 107.9152 | 141.005 | 0 | 229.5282 | 6820853.5347 | 538952.6128 | 7430247.2836 | 7363270.3752 | 0 | 347481.353 | 0 | 8775314.0121 | 22831566.9952 | 15583013.616 | 69690699.7826 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81316727.4334 | 98607569.3733 | 5623413.2519 | 18.628 | 4365.2879 | 5293.5042 | 88.9923 | 107.9152
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.4439 | 47.9101 | 4.6616 | 4 | 4362.6758 | 5289.9729 | 88.939 | 107.8433 | 141.0004 | 0 | 230.5545 | 6823989.7831 | 539178.5014 | 7434308.005 | 7368387.2797 | 0 | 345239.7627 | 0 | 8779330.2994 | 22842016.5509 | 15590145.6525 | 69722595.8346 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81348623.4854 | 98639465.4254 | 7498942.0933 | 18.6465 | 4362.6758 | 5289.9729 | 88.939 | 107.8433
1 | 3300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.4561 | 47.9135 | 4.6635 | 4 | 4360.7164 | 5287.6333 | 88.8991 | 107.7956 | 140.9999 | 0 | 237.1585 | 6824315.2696 | 539201.8194 | 7434730.9743 | 7368923.917 | 0 | 342902.4644 | 0 | 8778929.0335 | 22840972.5391 | 15589433.093 | 69719409.1103 | 961560.8286 | 10664466.8222 | 10664466.8222 | 1478867.319 | 5147507.7987 | 0 | 81345436.7611 | 98636278.701 | 10000000 | 18.6541 | 4360.7164 | 5287.6333 | 88.8991 | 107.7956
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.8168 | [19 empty] | 100 | 0
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.7719 | [19 empty] | 133.3521 | 0
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.16849 | 0.0035514 | 4 | 915290.4367 | 2171847.9552 | 18659.4336 | 44276.0582 | 106.7185 | 0 | 63.7131 | 107582.7413 | 6941.4187 | 82894.3141 | 56822.0144 | 0 | 61107.8949 | 0 | 122985.8696 | 319984.0048 | 218395.6583 | 976713.9161 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13002249.0757 | 30852401.5279 | 177.8279 | 0.014206 | 915290.4367 | 2171847.9552 | 18659.4336 | 44276.0582
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2202 | 0.25485 | 0.0089943 | 4 | 370115.1082 | 866267.9886 | 7545.2971 | 17660.0447 | 114.9295 | 0 | 63.4156 | 150612.0783 | 10224.8786 | 114747.0115 | 70376.077 | 0 | 70583.5182 | 0 | 162451.9898 | 422666.754 | 288478.7445 | 1290141.0518 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13315676.2114 | 31165828.6636 | 237.1374 | 0.035977 | 370115.1082 | 866267.9886 | 7545.2971 | 17660.0447
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5834 | 0.36555 | 0.016989 | 4 | 201323.2304 | 463998.6508 | 4104.2464 | 9459.2401 | 121.4117 | 0 | 52.1605 | 200605.5315 | 14185.8488 | 152440.5711 | 87393.4721 | 0 | 79854.1806 | 0 | 208447.0456 | 542336.4543 | 370155.774 | 1655418.8781 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 13680954.0377 | 31531106.4899 | 316.2278 | 0.067955 | 201323.2304 | 463998.6508 | 4104.2464 | 9459.2401
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.5217 | 0.028746 | 4 | 123140.6691 | 278381.1146 | 2510.3891 | 5675.1756 | 127.0249 | 0 | 360.24 | 264647.325 | 19403.8941 | 201830.3139 | 111165.9176 | 0 | 91840.1779 | 0 | 268666.1751 | 699014.2766 | 477091.6071 | 2133659.6873 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14159194.8469 | 32009347.2991 | 421.6965 | 0.11498 | 123140.6691 | 278381.1146 | 2510.3891 | 5675.1756
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7405 | 0.73445 | 0.045355 | 4 | 81377.6526 | 179768.269 | 1658.9935 | 3664.8193 | 131.6243 | 0 | 482.6739 | 343807.4267 | 25986.2956 | 264510.0425 | 143317.5665 | 0 | 106421.0542 | 0 | 344776.5304 | 897037.8086 | 612246.7366 | 2738103.4611 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 14763638.6207 | 32613791.0729 | 562.3413 | 0.18142 | 81377.6526 | 179768.269 | 1658.9935 | 3664.8193
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 1.0262 | 0.068526 | 4 | 56676.6644 | 121798.3098 | 1155.4305 | 2483.0233 | 135.3573 | 0 | 650.1752 | 442277.2753 | 34281.2928 | 344789.311 | 187103.023 | 0 | 124749.1337 | 0 | 441948.014 | 1149858.0764 | 784801.7644 | 3509807.8906 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 15535343.0501 | 33385495.5024 | 749.8942 | 0.2741 | 56676.6644 | 121798.3098 | 1155.4305 | 2483.0233
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8011 | 1.4079 | 0.099456 | 4 | 41405.4047 | 86274.7582 | 844.1052 | 1758.8276 | 138.235 | 0 | 88.6972 | 559222.4579 | 44187.3207 | 443191.1229 | 243170.0052 | 0 | 145878.9747 | 0 | 559903.4538 | 1456753.9347 | 994264.4938 | 4446571.7637 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 16472106.9233 | 34322259.3755 | 1000 | 0.39783 | 41405.4047 | 86274.7582 | 844.1052 | 1758.8276
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3675 | 1.9246 | 0.14162 | 4 | 31183.2641 | 62694.153 | 635.713 | 1278.1051 | 140.4752 | 0 | 84.7042 | 703599.1572 | 56470.4635 | 568228.1267 | 320153.0389 | 0 | 172202.7603 | 0 | 710054.8832 | 1847417.1537 | 1260900.168 | 5639025.7514 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 17664560.9109 | 35514713.3632 | 1333.5214 | 0.56648 | 31183.2641 | 62694.153 | 635.713 | 1278.1051
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4358 | 2.6029 | 0.19687 | 4 | 24297.5551 | 46964.9167 | 495.3385 | 957.4434 | 142.0155 | 0 | 82.3282 | 875948.6011 | 71059.2105 | 722684.3595 | 421527.7675 | 0 | 203834.6807 | 0 | 895071.3015 | 2328791.9222 | 1589448.3388 | 7108366.1819 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 19133901.3415 | 36984053.7937 | 1778.2794 | 0.78748 | 24297.5551 | 46964.9167 | 495.3385 | 957.4434
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.2079 | 3.5315 | 0.27444 | 4 | 19156.887 | 35417.5594 | 390.5391 | 722.0349 | 143.5969 | 0 | 93.9775 | 1093730.9533 | 89719.0742 | 921440.2526 | 559758.9076 | 0 | 242422.0414 | 0 | 1133757.7793 | 2949805.1762 | 2013302.6452 | 9003936.8298 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 21029471.9893 | 38879624.4416 | 2371.3737 | 1.0977 | 19156.887 | 35417.5594 | 390.5391 | 722.0349
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.8937 | 4.7578 | 0.37607 | 4 | 15548.6788 | 27415.019 | 316.9808 | 558.8922 | 144.6245 | 0 | 93.8488 | 1355641.5166 | 111971.417 | 1168687.8218 | 743063.0606 | 0 | 289641.5774 | 0 | 1430912.1034 | 3722939.7727 | 2540982.8936 | 11363840.1632 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 23389375.3227 | 41239527.7749 | 3162.2777 | 1.5043 | 15548.6788 | 27415.019 | 316.9808 | 558.8922
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.7905 | 6.387 | 0.51115 | 4 | 12887.2217 | 21617.6928 | 262.7234 | 440.7059 | 145.4053 | 0 | 101.1666 | 1674400.6161 | 138943.6586 | 1478344.3248 | 985827.168 | 0 | 347042.3307 | 0 | 1803577.6583 | 4692539.1023 | 3202754.3593 | 14323429.2181 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 26348964.3776 | 44199116.8299 | 4216.965 | 2.0446 | 12887.2217 | 21617.6928 | 262.7234 | 440.7059
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2775 | 8.5443 | 0.68986 | 4 | 10890.8225 | 17359.5654 | 222.0241 | 353.8982 | 145.9968 | 0 | 79.299 | 2061450.8204 | 171530.4007 | 1865114.9837 | 1305602.9873 | 0 | 416654.4348 | 0 | 2269937.9145 | 5905912.8252 | 4030906.8576 | 18027111.2242 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 30052646.3837 | 47902798.836 | 5623.4133 | 2.7594 | 10890.8225 | 17359.5654 | 222.0241 | 353.8982
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.8205 | 11.3894 | 0.92636 | 4 | 9364.7931 | 14182.0822 | 190.914 | 289.1209 | 146.4437 | 0 | 107.3754 | 2531526.9922 | 211066.668 | 2346460.0864 | 1731286.9247 | 0 | 500693.2306 | 0 | 2855203.2217 | 7428653.1003 | 5070208.3845 | 22675098.6084 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 34700633.768 | 52550786.2202 | 7498.9421 | 3.7054 | 9364.7931 | 14182.0822 | 190.914 | 289.1209
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.9996 | 15.1129 | 1.2355 | 4 | 8191.4993 | 11803.3303 | 166.9948 | 240.6269 | 146.7757 | 0 | 94.2836 | 3097720.908 | 258473.1718 | 2941553.5306 | 2288473.0739 | 0 | 601903.4457 | 0 | 3583368.4106 | 9323189.5545 | 6363268.4434 | 28457950.5384 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 40483485.698 | 58333638.1502 | 10000 | 4.9421 | 8191.4993 | 11803.3303 | 166.9948 | 240.6269
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.3944 | 19.8968 | 1.6313 | 4 | 7288.9812 | 10024.5409 | 148.5957 | 204.3638 | 146.9803 | 0 | 96.1298 | 3767946.0624 | 314233.9221 | 3664847.1393 | 3004529.0304 | 0 | 722071.3695 | 0 | 4474714.7342 | 11642289.8483 | 7946102.0466 | 35536734.1528 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 47562269.3124 | 65412421.7646 | 13335.2143 | 6.5252 | 7288.9812 | 10024.5409 | 148.5957 | 204.3638
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.1823 | 23.7886 | 2.0079 | 4 | 6589.8405 | 8812.2982 | 134.3428 | 179.6506 | 147.0065 | 0 | 114.3919 | 4277316.8117 | 356219.6671 | 4227811.9409 | 3587324.3455 | 0 | 757286.2043 | 0 | 5150323.9981 | 13400086.5663 | 9145834.4257 | 40902203.9594 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 52927739.119 | 70777891.5712 | 17782.7941 | 8.0317 | 6589.8405 | 8812.2982 | 134.3428 | 179.6506
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.0787 | 27.6769 | 2.4039 | 4 | 6039.6828 | 7896.0495 | 123.1271 | 160.9716 | 146.9196 | 0 | 142.8816 | 4760162.9437 | 395568.7696 | 4772483.5514 | 4170256.8503 | 0 | 769498.5024 | 0 | 5798508.5408 | 15086529.7856 | 10296866.5759 | 46049875.5199 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 58075410.6795 | 75925563.1317 | 23713.7371 | 9.6156 | 6039.6828 | 7896.0495 | 123.1271 | 160.9716
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.6787 | 31.418 | 2.8012 | 4 | 5609.3609 | 7202.4233 | 114.3544 | 146.8311 | 146.7362 | 0 | 170.0298 | 5203384.8176 | 431179.6459 | 5282685.2774 | 4731725.2439 | 0 | 761357.2541 | 0 | 6400029.5732 | 16651564.1228 | 11365034.6692 | 50826960.604 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 62852495.7635 | 80702648.2158 | 31622.7766 | 11.2049 | 5609.3609 | 7202.4233 | 114.3544 | 146.8311
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.4681 | 34.8447 | 3.1796 | 4 | 5274.6164 | 6678.0877 | 107.5302 | 136.1418 | 146.4871 | 0 | 191.1556 | 5592930.6989 | 461983.4165 | 5739929.7691 | 5246812.4949 | 0 | 735402.7374 | 0 | 6933053.0555 | 18038381.8857 | 12311566.2887 | 55060060.3467 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 67085595.5062 | 84935747.9584 | 42169.6503 | 12.7186 | 5274.6164 | 6678.0877 | 107.5302 | 136.1418
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.0996 | 37.8558 | 3.5238 | 4 | 5015.5135 | 6281.9074 | 102.248 | 128.0652 | 146.2073 | 0 | 222.0487 | 5923257.2365 | 487676.0708 | 6134772.8569 | 5700205.1089 | 0 | 696494.8678 | 0 | 7387538.3949 | 19220859.511 | 13118631.5654 | 58669435.6121 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 70694970.7717 | 88545123.2239 | 56234.1325 | 14.0953 | 5015.5135 | 6281.9074 | 102.248 | 128.0652
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.4601 | 40.4316 | 3.8265 | 4 | 4815.8395 | 5982.0497 | 98.1774 | 121.9522 | 145.9239 | 0 | 239.8123 | 6197839.4466 | 508742.8978 | 6467886.2503 | 6091175.4881 | 0 | 650798.554 | 0 | 7767412.6283 | 20209214.3435 | 13793204.0473 | 61686273.6559 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 73711808.8155 | 91561961.2677 | 74989.4209 | 15.3061 | 4815.8395 | 5982.0497 | 98.1774 | 121.9522
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.3077 | 42.5168 | 4.0811 | 4 | 4662.5355 | 5756.001 | 95.0521 | 117.3439 | 145.6657 | 0 | 222.7023 | 6415773.7514 | 525363.759 | 6734552.638 | 6415026.2482 | 0 | 600998.1454 | 0 | 8069768.6714 | 20995882.7458 | 14330121.3962 | 64087487.3553 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 76113022.5149 | 93963174.9671 | 100000 | 16.3244 | 4662.5355 | 5756.001 | 95.0521 | 117.3439
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.4512 | 44.9848 | 4.3493 | 4 | 4543.3947 | 5569.4364 | 92.6232 | 113.5405 | 145.3688 | 0 | 232.0567 | 6669247.487 | 544612.4574 | 7046922.1023 | 6799486.9545 | 0 | 577083.1534 | 0 | 8438567.3403 | 21955421.2313 | 14985026.1291 | 67016366.8552 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 79041902.0148 | 96892054.467 | 133352.1432 | 17.3971 | 4543.3947 | 5569.4364 | 92.6232 | 113.5405
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 144.3091 | 46.4468 | 4.5306 | 4 | 4452.1004 | 5437.0858 | 90.7621 | 110.8423 | 145.1891 | 0 | 228.3645 | 6816986.5506 | 555757.9832 | 7230427.3743 | 7028193.4058 | 0 | 535548.5114 | 0 | 8645096.3919 | 22492767.4585 | 15351775.9706 | 68656553.6463 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 80682088.8059 | 98532241.2581 | 177827.941 | 18.1223 | 4452.1004 | 5437.0858 | 90.7621 | 110.8423
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.0675 | 47.5708 | 4.6731 | 4 | 4382.623 | 5337.5692 | 89.3457 | 108.8136 | 145.0457 | 0 | 261.5941 | 6929279.8692 | 564177.8414 | 7370779.8971 | 7204685.4206 | 0 | 498108.2146 | 0 | 8801142.1847 | 22898766.6022 | 15628878.7286 | 69895818.7585 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 81921353.918 | 99771506.3702 | 237137.3706 | 18.6923 | 4382.623 | 5337.5692 | 89.3457 | 108.8136
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.2734 | 48.52 | 4.7902 | 4 | 4329.8155 | 5261.413 | 88.2691 | 107.261 | 144.9205 | 0 | 243.7487 | 7022998.9365 | 571135.2323 | 7488882.7438 | 7351525.8879 | 0 | 468713.7098 | 0 | 8932270.039 | 23239934.381 | 15861732.748 | 70937193.6784 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 82962728.8379 | 100812881.2901 | 316227.766 | 19.1608 | 4329.8155 | 5261.413 | 88.2691 | 107.261
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.4996 | 49.1744 | 4.8752 | 4 | 4289.7767 | 5205.1253 | 87.4529 | 106.1135 | 144.8318 | 0 | 267.9434 | 7087025.1908 | 575852.8842 | 7570065.9654 | 7451787.9233 | 0 | 441925.6276 | 0 | 9019396.4606 | 23466619.4578 | 16016449.9708 | 71629123.4805 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 83654658.6401 | 101504811.0923 | 421696.5034 | 19.5009 | 4289.7767 | 5205.1253 | 87.4529 | 106.1135
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.1781 | 49.6661 | 4.94 | 4 | 4259.4999 | 5162.8468 | 86.8357 | 105.2516 | 144.7641 | 0 | 254.061 | 7134886.6642 | 579367.6984 | 7630942.6278 | 7527180.4765 | 0 | 419958.5632 | 0 | 9084011.0517 | 23634733.3697 | 16131191.17 | 72142271.6215 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 84167806.7811 | 102017959.2333 | 562341.3252 | 19.76 | 4259.4999 | 5162.8468 | 86.8357 | 105.2516
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.7787 | 50.1338 | 4.9978 | 4 | 4235.311 | 5128.2089 | 86.3425 | 104.5455 | 144.699 | 0 | 230.403 | 7180226.5367 | 582689.0386 | 7688751.5621 | 7598937.4787 | 0 | 403613.4187 | 0 | 9147145.0336 | 23798995.04 | 16243303.1352 | 72643661.2436 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 84669196.4032 | 102519348.8554 | 749894.2093 | 19.9913 | 4235.311 | 5128.2089 | 86.3425 | 104.5455
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7191 | 50.4079 | 5.0346 | 4 | 4218.2932 | 5104.6686 | 85.9956 | 104.0656 | 144.6604 | 0 | 245.1084 | 7206699.1821 | 584623.1929 | 7722582.2492 | 7641007.3382 | 0 | 389817.4313 | 0 | 9182444.4636 | 23890836.9159 | 16305987.1027 | 72923997.8759 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 84949533.0355 | 102799685.4877 | 1000000 | 20.1384 | 4218.2932 | 5104.6686 | 85.9956 | 104.0656
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.4307 | 50.615 | 5.0625 | 4 | 4205.4786 | 5086.9746 | 85.7344 | 103.7049 | 144.6309 | 0 | 242.0397 | 7226659.8 | 586079.4423 | 7748124.9925 | 7672807.4824 | 0 | 379096.4817 | 0 | 9208979.5976 | 23959875.8915 | 16353107.6222 | 73134731.3104 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85160266.47 | 103010418.9222 | 1333521.4322 | 20.2498 | 4205.4786 | 5086.9746 | 85.7344 | 103.7049
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 158.9519 | 50.7665 | 5.0832 | 4 | 4195.8377 | 5073.7424 | 85.5378 | 103.4351 | 144.6093 | 0 | 215.5539 | 7241240.0498 | 587141.9619 | 7766801.7775 | 7696079.7203 | 0 | 370690.4318 | 0 | 9228162.0371 | 24009784.6641 | 16387171.385 | 73287072.0274 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85312607.1869 | 103162759.6391 | 1778279.41 | 20.3327 | 4195.8377 | 5073.7424 | 85.5378 | 103.4351
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.3392 | 50.879 | 5.0987 | 4 | 4188.5898 | 5063.826 | 85.3901 | 103.2329 | 144.5932 | 0 | 227.7511 | 7252051.8995 | 587929.2132 | 7780661.7468 | 7713360.8972 | 0 | 364204.7146 | 0 | 9242301.3038 | 24046572.1358 | 16412279.5903 | 73399361.5011 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85424896.6607 | 103275049.1129 | 2371373.7057 | 20.3947 | 4188.5898 | 5063.826 | 85.3901 | 103.2329
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6339 | 50.9646 | 5.1104 | 4 | 4183.144 | 5056.3692 | 85.279 | 103.0809 | 144.5809 | 0 | 241.7486 | 7260266.221 | 588526.9724 | 7791197.6391 | 7726503.683 | 0 | 359291.5131 | 0 | 9253056.5512 | 24074555.0832 | 16431378.5269 | 73484776.1899 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85510311.3495 | 103360463.8017 | 3162277.6602 | 20.4416 | 4183.144 | 5056.3692 | 85.279 | 103.0809
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.8534 | 51.0283 | 5.1192 | 4 | 4179.0542 | 5050.7804 | 85.1957 | 102.967 | 144.5717 | 0 | 219.7166 | 7266377.5493 | 588971.4863 | 7799039.5192 | 7736289.3764 | 0 | 355543.4861 | 0 | 9261026.3527 | 24095290.8721 | 16445531.1289 | 73548069.7711 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85573604.9307 | 103423757.3829 | 4216965.0343 | 20.4768 | 4179.0542 | 5050.7804 | 85.1957 | 102.967
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.0165 | 51.0756 | 5.1258 | 4 | 4175.9837 | 5046.5931 | 85.1331 | 102.8816 | 144.5649 | 0 | 234.1835 | 7270916.9302 | 589301.5453 | 7804866.1865 | 7743562.2711 | 0 | 352691.3128 | 0 | 9266921.9159 | 24110629.9181 | 16456000.343 | 73594890.4228 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85620425.5824 | 103470578.0346 | 5623413.2519 | 20.5031 | 4175.9837 | 5046.5931 | 85.1331 | 102.8816
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.146 | 51.1132 | 5.1309 | 4 | 4173.6792 | 5043.4255 | 85.0861 | 102.8171 | 144.5595 | 0 | 234.6501 | 7274517.025 | 589563.2573 | 7809488.1145 | 7749332.5329 | 0 | 350599.2855 | 0 | 9271665.0839 | 24122970.6683 | 16464423.1586 | 73632559.1259 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85658094.2855 | 103508246.7377 | 7498942.0933 | 20.5234 | 4173.6792 | 5043.4255 | 85.0861 | 102.8171
1 | 3400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.2212 | 51.135 | 5.1342 | 4 | 4171.9499 | 5041.1316 | 85.0508 | 102.7703 | 144.5563 | 0 | 236.3518 | 7276605.6937 | 589715.0145 | 7812170.6451 | 7752682.1305 | 0 | 348826.2247 | 0 | 9274199.8863 | 24129565.7042 | 16468924.4061 | 73652689.7053 | 961560.8286 | 11063974.3309 | 11063974.3309 | 1478867.319 | 5307310.8022 | 0 | 85678224.8648 | 103528377.317 | 10000000 | 20.5367 | 4171.9499 | 5041.1316 | 85.0508 | 102.7703
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 24.9883 | [19 empty] | 100 | 0
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.74031 | 0.12183 | 0.00099865 | 4 | 3310792.1295 | 7921435.3142 | 67494.9757 | 161489.1734 | 100.7606 | 0 | 45.0724 | 82665.5368 | 5139.71 | 64231.9937 | 49103.8254 | 0 | 55338.2913 | 0 | 100026.9493 | 260249.6037 | 177625.7021 | 794381.6121 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13225284.3713 | 31642951.463 | 133.3521 | 0.0039946 | 3310792.1295 | 7921435.3142 | 67494.9757 | 161489.1734
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.18351 | 0.0048095 | 4 | 699857.6097 | 1657209.7795 | 14267.544 | 33784.4629 | 109.6423 | 0 | 50.6778 | 116249.4707 | 7632.779 | 88566.3695 | 58851.3977 | 0 | 62237.4384 | 0 | 130079.6075 | 338440.4557 | 230992.5653 | 1033050.0837 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13463952.8429 | 31881619.9346 | 177.8279 | 0.019238 | 699857.6097 | 1657209.7795 | 14267.544 | 33784.4629
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2545 | 0.27406 | 0.011022 | 4 | 312686.6557 | 730430.6352 | 6374.5404 | 14890.8165 | 117.8076 | 0 | 49.1511 | 161035.4244 | 11123.9055 | 121371.8409 | 72781.6482 | 0 | 71156.7364 | 0 | 170613.1266 | 443900.3579 | 302971.1155 | 1354954.1555 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 13785856.9147 | 32203524.0064 | 237.1374 | 0.044088 | 312686.6557 | 730430.6352 | 6374.5404 | 14890.8165
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.39461 | 0.020187 | 4 | 175579.6238 | 403670.2415 | 3579.4281 | 8229.3639 | 124.5362 | 0 | 272.536 | 215105.6809 | 15504.0724 | 161714.3952 | 90869.9665 | 0 | 80741.3911 | 0 | 219934.8474 | 572225.3582 | 390555.565 | 1746651.2768 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14177554.036 | 32595221.1277 | 316.2278 | 0.080747 | 175579.6238 | 403670.2415 | 3579.4281 | 8229.3639
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.56182 | 0.033566 | 4 | 109352.6011 | 246527.8542 | 2229.3007 | 5025.8038 | 130.2523 | 0 | 367.7043 | 283337.3952 | 21205.5951 | 213680.2967 | 116024.6638 | 0 | 92586.3312 | 0 | 283465.37 | 737518.7459 | 503371.6986 | 2251190.0964 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 14682092.8556 | 33099759.9473 | 421.6965 | 0.13426 | 109352.6011 | 246527.8542 | 2229.3007 | 5025.8038
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8183 | 0.79157 | 0.052485 | 4 | 72997.4793 | 160725.9608 | 1488.1524 | 3276.6161 | 134.9885 | 0 | 494.9739 | 368358.3476 | 28460.9286 | 280198.8965 | 150061.7698 | 0 | 107343.4415 | 0 | 364425.1197 | 948159.4076 | 647138.2784 | 2894146.1896 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 15325048.9488 | 33742716.0405 | 562.3413 | 0.20994 | 72997.4793 | 160725.9608 | 1488.1524 | 3276.6161
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.717 | 1.0975 | 0.078239 | 4 | 51501.9664 | 110352.414 | 1049.9372 | 2249.6832 | 138.7583 | 0 | 62.6201 | 471042.3493 | 37331.2184 | 363002.4254 | 194165.8247 | 0 | 124869.1839 | 0 | 464260.2906 | 1207910.0434 | 824423.4247 | 3687004.7604 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 16117907.5196 | 34535574.6112 | 749.8942 | 0.31296 | 51501.9664 | 110352.414 | 1049.9372 | 2249.6832
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9131 | 1.5102 | 0.11364 | 4 | 37666.4779 | 78183.1486 | 767.8821 | 1593.8692 | 141.7388 | 0 | 91.0825 | 597447.6628 | 48380.1263 | 467629.8444 | 254922.1662 | 0 | 146236.8629 | 0 | 590700.4984 | 1536881.5274 | 1048953.2222 | 4691151.9105 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 17122054.6697 | 35539721.7614 | 1000 | 0.45457 | 37666.4779 | 78183.1486 | 767.8821 | 1593.8692
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.5138 | 2.0645 | 0.16148 | 4 | 28464.5891 | 56978.8201 | 580.2891 | 1161.5903 | 144.0434 | 0 | 73.618 | 752055.3728 | 61944.7298 | 599529.3813 | 336473.5357 | 0 | 172571.2323 | 0 | 749803.9583 | 1950836.0935 | 1331485.7195 | 5954700.0232 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 18385602.7824 | 36803269.874 | 1333.5214 | 0.64591 | 28464.5891 | 56978.8201 | 580.2891 | 1161.5903
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 2.7938 | 0.22422 | 4 | 22239.7046 | 42774.8118 | 453.3865 | 872.0224 | 145.6208 | 0 | 75.13 | 937010.3999 | 78086.489 | 762837.3698 | 444158.2493 | 0 | 204442.7942 | 0 | 946348.7678 | 2462205.3711 | 1680505.759 | 7515595.2001 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 19946497.9592 | 38364165.0509 | 1778.2794 | 0.89689 | 22239.7046 | 42774.8118 | 453.3865 | 872.0224
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.4636 | 3.7911 | 0.3125 | 4 | 17568.1016 | 32302.374 | 358.1495 | 658.5276 | 147.2743 | 0 | 103.5975 | 1170882.0977 | 98831.1357 | 972635.3198 | 591310.3849 | 0 | 242943.3726 | 0 | 1199874.9012 | 3121828.3647 | 2130712.006 | 9529017.5825 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 21959920.3417 | 40377587.4334 | 2371.3737 | 1.25 | 17568.1016 | 32302.374 | 358.1495 | 658.5276
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.2226 | 5.1042 | 0.42766 | 4 | 14295.9905 | 25062.5092 | 291.4431 | 510.9332 | 148.3336 | 0 | 95.5186 | 1451001.6197 | 123413.1409 | 1232946.8928 | 784934.5463 | 0 | 289991.5301 | 0 | 1514092.2146 | 3939357.3595 | 2688692.3435 | 12024429.6475 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 24455332.4067 | 42872999.4984 | 3162.2777 | 1.7106 | 14295.9905 | 25062.5092 | 291.4431 | 510.9332
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2138 | 6.8494 | 0.58107 | 4 | 11871.2982 | 19795.2936 | 242.0125 | 403.5538 | 149.1392 | 0 | 89.6078 | 1792520.9091 | 153318.9149 | 1559040.4549 | 1043057.1669 | 0 | 347187.2363 | 0 | 1909098.626 | 4967083.015 | 3390136.2211 | 15161442.5442 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 27592345.3034 | 46010012.395 | 4216.965 | 2.3243 | 11871.2982 | 19795.2936 | 242.0125 | 403.5538
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.8474 | 9.1693 | 0.78482 | 4 | 10046.5805 | 15913.4438 | 204.8131 | 324.4171 | 149.7518 | 0 | 108.4398 | 2209067.8282 | 189639.8538 | 1967895.3022 | 1385610.8893 | 0 | 417130.5533 | 0 | 2406044.3265 | 6260033.79 | 4272601.6925 | 19108024.236 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 31538926.9952 | 49956594.0868 | 5623.4133 | 3.1393 | 10046.5805 | 15913.4438 | 204.8131 | 324.4171
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.5588 | 12.2151 | 1.0524 | 4 | 8658.2634 | 13033.4809 | 176.5104 | 265.7051 | 150.2133 | 0 | 110.5926 | 2711463.498 | 233222.3724 | 2474607.1283 | 1833800.919 | 0 | 501011.6346 | 0 | 3024101.1654 | 7868090.9039 | 5370133.715 | 24016431.3366 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 36447334.0958 | 54865001.1874 | 7498.9421 | 4.2095 | 8658.2634 | 13033.4809 | 176.5104 | 265.7051
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.94 | 16.1914 | 1.4011 | 4 | 7588.9838 | 10875.1593 | 154.7117 | 221.7048 | 150.5546 | 0 | 114.0168 | 3315066.2141 | 285305.6584 | 3099661.4626 | 2417168.6445 | 0 | 601809.3095 | 0 | 3790414.4028 | 9861880.7551 | 6730936.2568 | 30102242.7038 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 42533145.463 | 60950812.5547 | 10000 | 5.6046 | 7588.9838 | 10875.1593 | 154.7117 | 221.7048
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.5757 | 21.2926 | 1.8469 | 4 | 6764.8945 | 9257.9864 | 137.9115 | 188.7366 | 150.7584 | 0 | 123.5702 | 4028813.1064 | 346485.5017 | 3858406.6179 | 3166672.7539 | 0 | 721529.4992 | 0 | 4727543.9168 | 12300099.519 | 8395070.6635 | 37544621.5784 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 49975524.3376 | 68393191.4293 | 13335.2143 | 7.3875 | 6764.8945 | 9257.9864 | 137.9115 | 188.7366
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.6038 | 26.4895 | 2.328 | 4 | 6138.5138 | 8116.3634 | 125.1419 | 165.463 | 150.7592 | 0 | 138.3497 | 4703903.1334 | 403720.7543 | 4594983.3953 | 3933668.409 | 0 | 805784.8099 | 0 | 5632403.5958 | 14654358.7913 | 10001900.992 | 44730723.8811 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 57161626.6403 | 75579293.732 | 17782.7941 | 9.312 | 6138.5138 | 8116.3634 | 125.1419 | 165.463
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.642 | 30.6023 | 2.7656 | 4 | 5650.6665 | 7315.5713 | 115.1965 | 149.1378 | 150.6252 | 0 | 148.9491 | 5208228.3202 | 445887.3343 | 5157846.3572 | 4544872.9716 | 0 | 811822.5892 | 0 | 6305776.4533 | 16406336.8388 | 11197662.009 | 50078432.8735 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 62509335.6326 | 80927002.7243 | 23713.7371 | 11.0623 | 5650.6665 | 7315.5713 | 115.1965 | 149.1378
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.1929 | 34.4946 | 3.1979 | 4 | 5269.5783 | 6709.4226 | 107.4275 | 136.7807 | 150.3972 | 0 | 189.5736 | 5664584.8268 | 483476.1081 | 5677196.561 | 5127987.7297 | 0 | 796202.1868 | 0 | 6922284.4908 | 18010364.2893 | 12292443.7034 | 54974539.8959 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 67405442.6551 | 85823109.7467 | 31622.7766 | 12.7914 | 5269.5783 | 6709.4226 | 107.4275 | 136.7807
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 110.8332 | 38.026 | 3.6051 | 4 | 4973.5585 | 6250.7665 | 101.3927 | 127.4303 | 150.1099 | 0 | 212.9251 | 6062768.1446 | 515741.0416 | 6138801.2223 | 5661925.2415 | 0 | 763235.3648 | 0 | 7465563.6958 | 19423865.3388 | 13257187.2143 | 59289087.2637 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 71719990.0229 | 90137657.1146 | 42169.6503 | 14.4203 | 4973.5585 | 6250.7665 | 101.3927 | 127.4303
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.1681 | 41.069 | 3.9687 | 4 | 4744.6548 | 5904.8329 | 96.7262 | 120.378 | 149.8031 | 0 | 208.7381 | 6394142.7918 | 542074.775 | 6530204.4836 | 6121393.2716 | 0 | 717216.6759 | 0 | 7918962.4792 | 20603515.9682 | 14062323.0082 | 62889833.4535 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 75320736.2127 | 93738403.3044 | 56234.1325 | 15.8749 | 4744.6548 | 5904.8329 | 96.7262 | 120.378
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.1413 | 43.6244 | 4.2827 | 4 | 4568.4052 | 5643.5301 | 93.1331 | 115.051 | 149.5036 | 0 | 209.7633 | 6664399.0722 | 563150.1953 | 6854836.4606 | 6506652.211 | 0 | 665010.3731 | 0 | 8289078.8417 | 21566482.8223 | 14719567.6731 | 65829177.6493 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 78260080.4085 | 96677747.5002 | 74989.4209 | 17.1307 | 4568.4052 | 5643.5301 | 93.1331 | 115.051
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 137.223 | 46.5033 | 4.6045 | 4 | 4432.1984 | 5432.1863 | 90.3564 | 110.7425 | 149.1481 | 0 | 219.5702 | 6961605.1461 | 586041.91 | 7216341.9235 | 6942097.3454 | 0 | 636560.2241 | 0 | 8713632.1542 | 22671083.4534 | 15473480.3011 | 69200842.4579 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 81631745.2171 | 100049412.3088 | 100000 | 18.4179 | 4432.1984 | 5432.1863 | 90.3564 | 110.7425
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.1519 | 48.3707 | 4.8373 | 4 | 4326.4324 | 5278.2958 | 88.2002 | 107.6052 | 148.9214 | 0 | 209.1169 | 7150981.1997 | 600539.8886 | 7448531.5675 | 7224550.4852 | 0 | 589825.993 | 0 | 8975627.3623 | 23352741.2423 | 15938725.7487 | 71281523.4872 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 83712426.2464 | 102130093.3381 | 133352.1432 | 19.3491 | 4326.4324 | 5278.2958 | 88.2002 | 107.6052
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.7728 | 49.8114 | 5.0217 | 4 | 4245.6252 | 5162.5301 | 86.5528 | 105.2452 | 148.7375 | 0 | 241.3598 | 7294924.7237 | 611452.581 | 7626556.7627 | 7442116.1776 | 0 | 545798.258 | 0 | 9173130.9162 | 23866604.976 | 16289448.3058 | 72850032.7011 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 85280935.4603 | 103698602.552 | 177827.941 | 20.0868 | 4245.6252 | 5162.5301 | 86.5528 | 105.2452
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.366 | 50.9241 | 5.1667 | 4 | 4184.1051 | 5075.2817 | 85.2986 | 103.4665 | 148.5902 | 0 | 240.8138 | 7404845.7634 | 619721.539 | 7763428.4294 | 7610422.8517 | 0 | 506850.6977 | 0 | 9323055.0197 | 24256676.7397 | 16555680.2997 | 74040681.3402 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 86471584.0994 | 104889251.1911 | 237137.3706 | 20.6667 | 4184.1051 | 5075.2817 | 85.2986 | 103.4665
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.1233 | 51.7735 | 5.2791 | 4 | 4137.391 | 5009.5949 | 84.3463 | 102.1274 | 148.4747 | 0 | 294.0144 | 7488017.7593 | 625939.7593 | 7867543.0747 | 7739052.18 | 0 | 473539.0319 | 0 | 9435695.804 | 24549744.9547 | 16755705.3784 | 74935237.9423 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 87366140.7015 | 105783807.7932 | 316227.766 | 21.1162 | 4137.391 | 5009.5949 | 84.3463 | 102.1274
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.2233 | 52.4178 | 5.3654 | 4 | 4101.9982 | 4960.1673 | 83.6248 | 101.1197 | 148.3853 | 0 | 291.379 | 7550687.4802 | 630602.5915 | 7946314.7423 | 7836717.917 | 0 | 445841.6133 | 0 | 9519964.0943 | 24768993.7603 | 16905347.1933 | 75604469.3923 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 88035372.1515 | 106453039.2432 | 421696.5034 | 21.4616 | 4101.9982 | 4960.1673 | 83.6248 | 101.1197
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.7922 | 52.8977 | 5.4308 | 4 | 4075.2331 | 4923.074 | 83.0791 | 100.3635 | 148.3177 | 0 | 255.1359 | 7597135.1181 | 634045.8576 | 8004876.4658 | 7909519.531 | 0 | 423117.0317 | 0 | 9581790.6616 | 24929853.806 | 17015137.4799 | 76095475.9518 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 88526378.7109 | 106944045.8026 | 562341.3252 | 21.723 | 4075.2331 | 4923.074 | 83.0791 | 100.3635
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.605 | 52.8401 | 5.449 | 4 | 4053.9075 | 4898.9152 | 82.6444 | 99.871 | 148.3253 | 0 | 407.15 | 7591548.2812 | 633628.7754 | 7997858.2995 | 7900792.9005 | 0 | 390628.3368 | 0 | 9560638.0714 | 24874819.1054 | 16977575.1658 | 75927488.936 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 88358391.6952 | 106776058.7869 | 749894.2093 | 21.7959 | 4053.9075 | 4898.9152 | 82.6444 | 99.871
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.1823 | 53.6264 | 5.5266 | 4 | 4038.7127 | 4871.8561 | 82.3346 | 99.3194 | 148.2138 | 0 | 232.9409 | 7667297.8362 | 639227.662 | 8093622.8219 | 8020157.764 | 0 | 391949.2865 | 0 | 9676779.5945 | 25176995.5245 | 17183816.781 | 76849847.2706 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89280750.0297 | 107698417.1214 | 1000000 | 22.1062 | 4038.7127 | 4871.8561 | 82.3346 | 99.3194
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8324 | 53.8241 | 5.5543 | 4 | 4027.3877 | 4856.375 | 82.1037 | 99.0038 | 148.1851 | 0 | 232.3095 | 7686245.5134 | 640622.0782 | 8117657.011 | 8050187.2011 | 0 | 380823.3543 | 0 | 9701458.7116 | 25241205.5248 | 17227641.4256 | 77045840.8198 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89476743.579 | 107894410.6707 | 1333521.4322 | 22.2171 | 4027.3877 | 4856.375 | 82.1037 | 99.0038
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.307 | 53.9682 | 5.5748 | 4 | 4018.8671 | 4844.799 | 81.93 | 98.7678 | 148.1641 | 0 | 273.4938 | 7700042.5139 | 641636.1939 | 8135175.3105 | 8072093.0878 | 0 | 372112.1775 | 0 | 9719213.1206 | 25287398.855 | 17259169.3227 | 77186840.5819 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89617743.3411 | 108035410.4327 | 1778279.41 | 22.2993 | 4018.8671 | 4844.799 | 81.93 | 98.7678
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.6749 | 54.0799 | 5.5905 | 4 | 4012.4611 | 4836.0684 | 81.7994 | 98.5898 | 148.1478 | 0 | 276.1938 | 7710716.2815 | 642420.0854 | 8148737.497 | 8089062.1496 | 0 | 365542.3732 | 0 | 9733026.5708 | 25323338.619 | 17283698.95 | 77296542.5264 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89727445.2856 | 108145112.3773 | 2371373.7057 | 22.3622 | 4012.4611 | 4836.0684 | 81.7994 | 98.5898
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.9527 | 54.1641 | 5.6024 | 4 | 4007.6478 | 4829.5098 | 81.7013 | 98.4561 | 148.1355 | 0 | 265.693 | 7718766.7513 | 643010.921 | 8158972.174 | 8101873.7052 | 0 | 360548.7741 | 0 | 9743437.207 | 25350424.9588 | 17302185.9335 | 77379220.425 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89810123.1842 | 108227790.2759 | 3162277.6602 | 22.4097 | 4007.6478 | 4829.5098 | 81.7013 | 98.4561
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.1501 | 54.224 | 5.6111 | 4 | 4004.0329 | 4824.6269 | 81.6276 | 98.3565 | 148.1267 | 0 | 265.3373 | 7724481.003 | 643430.0493 | 8166240.1511 | 8110974.7647 | 0 | 356654.9062 | 0 | 9750694.541 | 25369307.0531 | 17315073.3509 | 77436855.8193 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89867758.5785 | 108285425.6702 | 4216965.0343 | 22.4443 | 4004.0329 | 4824.6269 | 81.6276 | 98.3565
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.3035 | 54.2705 | 5.6177 | 4 | 4001.3189 | 4820.945 | 81.5723 | 98.2815 | 148.1199 | 0 | 231.591 | 7728917.0859 | 643755.3239 | 8171883.9597 | 8118043.7468 | 0 | 353755.5183 | 0 | 9756378.6975 | 25384096.0624 | 17325167.1536 | 77481997.5482 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89912900.3074 | 108330567.3991 | 5623413.2519 | 22.4708 | 4001.3189 | 4820.945 | 81.5723 | 98.2815
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.4083 | 54.3022 | 5.6224 | 4 | 3999.2819 | 4818.2184 | 81.5308 | 98.2259 | 148.1152 | 0 | 253.3462 | 7731946.4837 | 643977.3571 | 8175739.327 | 8122873.63 | 0 | 351471.573 | 0 | 9760143.2646 | 25393890.6939 | 17331852.1908 | 77511894.5202 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89942797.2794 | 108360464.371 | 7498942.0933 | 22.4897 | 3999.2819 | 4818.2184 | 81.5308 | 98.2259
1 | 3500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.501 | 54.3303 | 5.6263 | 4 | 3997.7533 | 4816.1246 | 81.4996 | 98.1832 | 148.1111 | 0 | 245.7857 | 7734622.5878 | 644173.5081 | 8179145.1385 | 8127140.8163 | 0 | 349878.2196 | 0 | 9763634.5054 | 25402974.1863 | 17338051.8611 | 77539620.8231 | 961560.8286 | 11469341.9306 | 11469341.9306 | 1478867.319 | 5469457.8421 | 0 | 89970523.5823 | 108388190.674 | 10000000 | 22.5053 | 3997.7533 | 4816.1246 | 81.4996 | 98.1832
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.0278 | [19 empty] | 100 | 0
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75975 | 0.13036 | 0.0017598 | 4 | 1941992.7596 | 4640292.2288 | 39590.1491 | 94598.6335 | 103.1179 | 0 | 48.3001 | 88022.0478 | 5549.8583 | 67686.4467 | 50254.9823 | 0 | 55690.1039 | 0 | 104209.3412 | 271131.3295 | 185052.7036 | 827596.8133 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13669727.263 | 32663113.1214 | 133.3521 | 0.007039 | 1941992.7596 | 4640292.2288 | 39590.1491 | 94598.6335
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.19484 | 0.0060806 | 4 | 572109.3661 | 1353012.3423 | 11663.2233 | 27582.9867 | 112.0612 | 0 | 53.4369 | 122980.552 | 8192.4478 | 92753.7723 | 60293.209 | 0 | 62185.8556 | 0 | 135098.2763 | 351498.0025 | 239904.6093 | 1072906.7248 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 13915037.1745 | 32908423.0329 | 177.8279 | 0.024322 | 572109.3661 | 1353012.3423 | 11663.2233 | 27582.9867
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.28942 | 0.013035 | 4 | 273223.4699 | 637491.024 | 5570.03 | 12996.1168 | 120.3537 | 0 | 51.9985 | 169636.0368 | 11900.3396 | 126556.0351 | 74570.9571 | 0 | 70673.094 | 0 | 176801.2204 | 460000.5086 | 313959.7992 | 1404097.9908 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14246228.4405 | 33239614.2988 | 237.1374 | 0.052141 | 273223.4699 | 637491.024 | 5570.03 | 12996.1168
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6709 | 0.42223 | 0.023578 | 4 | 155592.8677 | 356980.3597 | 3171.9711 | 7277.5275 | 127.5214 | 0 | 276.9033 | 229081.8612 | 16828.3027 | 170350.6984 | 94331.6527 | 0 | 80977.8817 | 0 | 230712.4547 | 600266.4815 | 409694.2079 | 1832243.5407 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 14674373.9904 | 33667759.8488 | 316.2278 | 0.094313 | 155592.8677 | 356980.3597 | 3171.9711 | 7277.5275
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.60388 | 0.038786 | 4 | 98067.3263 | 220490.8461 | 1999.2351 | 4495.0041 | 133.4779 | 0 | 375.1981 | 302790.1691 | 23139.191 | 225884.7797 | 120953.8163 | 0 | 93238.408 | 0 | 298742.482 | 777266.6577 | 530500.4651 | 2372515.9689 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15214646.4185 | 34208032.2769 | 421.6965 | 0.15514 | 98067.3263 | 220490.8461 | 1999.2351 | 4495.0041
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8961 | 0.85056 | 0.060098 | 4 | 66115.4681 | 145125.7137 | 1347.8532 | 2958.584 | 138.3501 | 0 | 501.8383 | 393569.6885 | 31091.0464 | 296114.7009 | 156316.3075 | 0 | 108123.4904 | 0 | 384233.9411 | 999697.8976 | 682314.3569 | 3051461.4294 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 15893591.879 | 34886977.7374 | 562.3413 | 0.24039 | 66115.4681 | 145125.7137 | 1347.8532 | 2958.584
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 1.1773 | 0.089251 | 4 | 46868.8256 | 100070.7331 | 955.4844 | 2040.0772 | 142.1818 | 0 | 76.4359 | 503110.0158 | 40863.6102 | 383034.1712 | 203745.9629 | 0 | 125297.3651 | 0 | 489859.9388 | 1274515.0767 | 869882.7285 | 3890308.8693 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 16732439.319 | 35725825.1773 | 749.8942 | 0.35701 | 46868.8256 | 100070.7331 | 955.4844 | 2040.0772
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.04 | 1.6237 | 0.12951 | 4 | 34373.0054 | 71036.5695 | 700.7402 | 1448.1766 | 145.2666 | 0 | 73.8164 | 639555.3857 | 53183.5437 | 494299.618 | 268806.738 | 0 | 147072.3072 | 0 | 625137.8611 | 1626480.4812 | 1110106.3492 | 4964642.2841 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 17806772.7338 | 36800158.5921 | 1000 | 0.51805 | 34373.0054 | 71036.5695 | 700.7402 | 1448.1766
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6648 | 2.2137 | 0.18333 | 4 | 26096.1172 | 51997.2922 | 532.0046 | 1060.0351 | 147.6104 | 0 | 82.6261 | 803935.1448 | 68112.0339 | 632317.2206 | 354849.4356 | 0 | 172975.8746 | 0 | 792553.9867 | 2062062.8983 | 1407400.2993 | 6294206.8939 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 19136337.3436 | 38129723.2019 | 1333.5214 | 0.7333 | 26096.1172 | 51997.2922 | 532.0046 | 1060.0351
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.8185 | 2.9922 | 0.25424 | 4 | 20439.284 | 39116.2107 | 416.6825 | 797.4369 | 149.2454 | 0 | 71.6867 | 1001461.4765 | 85993.5487 | 803695.0143 | 469073.6397 | 0 | 204459.3968 | 0 | 1000226.3997 | 2602383.9173 | 1776180.4972 | 7943473.8902 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 20785604.3398 | 39778990.1982 | 1778.2794 | 1.0169 | 20439.284 | 39116.2107 | 416.6825 | 797.4369
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7265 | 4.0644 | 0.35367 | 4 | 16200.2011 | 29626.0436 | 330.263 | 603.967 | 150.949 | 0 | 89.3251 | 1252132.773 | 108959.4533 | 1025573.9175 | 623163.0181 | 0 | 243410.7007 | 0 | 1268763.5464 | 3301062.4885 | 2253042.9785 | 10076108.8759 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 22918239.3256 | 41911625.1839 | 2371.3737 | 1.4147 | 16200.2011 | 29626.0436 | 330.263 | 603.967
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.571 | 5.4743 | 0.48477 | 4 | 13193.6364 | 22988.7085 | 268.9701 | 468.6559 | 152.0413 | 0 | 99.3649 | 1554103.9257 | 136644.6051 | 1300217.5637 | 832186.9836 | 0 | 290597.4763 | 0 | 1604362.7162 | 4174222.6876 | 2848992.756 | 12741328.7144 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 25583459.1641 | 44576845.0224 | 3162.2777 | 1.9391 | 13193.6364 | 22988.7085 | 268.9701 | 468.6559
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6548 | 7.3342 | 0.65676 | 4 | 10991.5583 | 18221.5549 | 224.0778 | 371.471 | 152.8695 | 0 | 91.9872 | 1917242.945 | 169507.9326 | 1642047.0005 | 1100388.3348 | 0 | 347327.005 | 0 | 2018840.155 | 5252607.9623 | 3585012.8645 | 16032974.1998 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 28875104.6495 | 47868490.5078 | 4216.965 | 2.627 | 10991.5583 | 18221.5549 | 224.0778 | 371.471
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.4152 | 9.8094 | 0.88587 | 4 | 9321.7047 | 14681.8013 | 190.0356 | 299.3084 | 153.5008 | 0 | 94.3154 | 2361586.6155 | 209656.9339 | 2071144.9681 | 1459097.8177 | 0 | 416910.2097 | 0 | 2542174.6525 | 6614216.974 | 4514338.9933 | 20189127.1646 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 33031257.6143 | 52024643.4726 | 5623.4133 | 3.5435 | 9321.7047 | 14681.8013 | 190.0356 | 299.3084
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.2969 | 13.0637 | 1.1874 | 4 | 8046.2824 | 12045.3167 | 164.0344 | 245.5601 | 153.9769 | 0 | 87.7077 | 2898771.1611 | 258001.2239 | 2603692.0211 | 1931244.1001 | 0 | 500592.1788 | 0 | 3194997.2671 | 8312727.505 | 5673607.3317 | 25373632.7888 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 38215763.2385 | 57209149.0968 | 7498.9421 | 4.7495 | 8046.2824 | 12045.3167 | 164.0344 | 245.5601
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.9022 | 17.3115 | 1.5806 | 4 | 7062.0584 | 10066.1295 | 143.9696 | 205.2117 | 154.3275 | 0 | 94.8299 | 3544695.1117 | 315895.4833 | 3260496.2149 | 2547336.1306 | 0 | 601345.4735 | 0 | 4005209.6815 | 10420734.0097 | 7112365.0863 | 31808077.1915 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 44650207.6412 | 63643593.4996 | 10000 | 6.3225 | 7062.0584 | 10066.1295 | 143.9696 | 205.2117
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.7742 | 22.7401 | 2.0813 | 4 | 6304.5726 | 8586.0159 | 128.5272 | 175.0375 | 154.529 | 0 | 109.0221 | 4305388.138 | 383537.4651 | 4054904.957 | 3335594.4338 | 0 | 720450.7496 | 0 | 4991951.54 | 12988033.9169 | 8864600.0257 | 39644461.2261 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 52486591.6758 | 71479977.5341 | 13335.2143 | 8.3252 | 6304.5726 | 8586.0159 | 128.5272 | 175.0375
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.0226 | 29.3361 | 2.6851 | 4 | 5733.9491 | 7502.3654 | 116.8943 | 152.9459 | 154.4872 | 0 | 133.6017 | 5157262.447 | 458095.5016 | 4971449.6093 | 4296929.8841 | 0 | 853562.7135 | 0 | 6137547.0607 | 15968638.4678 | 10898923.877 | 48742409.561 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 61584540.0107 | 80577925.8691 | 17782.7941 | 10.7403 | 5733.9491 | 7502.3654 | 116.8943 | 152.9459
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.0512 | 33.6195 | 3.1617 | 4 | 5301.1638 | 6802.999 | 108.0714 | 138.6883 | 154.3059 | 0 | 138.0606 | 5676047.9317 | 502549.0224 | 5544932.6825 | 4924807.889 | 0 | 851213.8789 | 0 | 6824825.0478 | 17756794.8102 | 12119377.3236 | 54200548.5862 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 67042679.0359 | 86036064.8942 | 23713.7371 | 12.6468 | 5301.1638 | 6802.999 | 108.0714 | 138.6883
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.466 | 37.6249 | 3.6253 | 4 | 4963.5809 | 6273.3692 | 101.1893 | 127.8911 | 154.0356 | 0 | 174.5271 | 6139933.0682 | 541492.8862 | 6068719.4889 | 5515486.0513 | 0 | 827189.1504 | 0 | 7446200.0515 | 19373485.1085 | 13222801.6718 | 59135307.4769 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 71977437.9265 | 90970823.7849 | 31622.7766 | 14.5011 | 4963.5809 | 6273.3692 | 101.1893 | 127.8911
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.8692 | 41.2092 | 4.0553 | 4 | 4701.3776 | 5872.288 | 95.8439 | 119.7145 | 153.7149 | 0 | 201.1115 | 6539591.8476 | 574396.7633 | 6528588.6639 | 6046939.9406 | 0 | 786398.8774 | 0 | 7985607.2762 | 20776912.0594 | 14180669.4034 | 63419104.8318 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 76261235.2815 | 95254621.1398 | 42169.6503 | 16.221 | 4701.3776 | 5872.288 | 95.8439 | 119.7145
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9265 | 44.2786 | 4.4361 | 4 | 4498.7772 | 5569.175 | 91.7137 | 113.5352 | 153.3829 | 0 | 235.2515 | 6870740.5901 | 601098.8568 | 6916543.9951 | 6504950.5015 | 0 | 733958.6524 | 0 | 8434644.1124 | 21945213.7971 | 14978059.3456 | 66985209.851 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 79827340.3007 | 98820726.1591 | 56234.1325 | 17.7442 | 4498.7772 | 5569.175 | 91.7137 | 113.5352
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.5512 | 46.8247 | 4.7613 | 4 | 4342.8699 | 5340.1537 | 88.5353 | 108.8663 | 153.0683 | 0 | 226.9726 | 7137951.7743 | 622219.875 | 7234678.2908 | 6887316.7246 | 0 | 675990.2582 | 0 | 8797681.1999 | 22889761.8296 | 15622732.7863 | 69868332.7387 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 82710463.1884 | 101703849.0468 | 74989.4209 | 19.0451 | 4342.8699 | 5340.1537 | 88.5353 | 108.8663
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 140.7741 | 49.8836 | 5.111 | 4 | 4220.9346 | 5149.9747 | 86.0495 | 104.9892 | 152.6987 | 0 | 223.244 | 7453746.3985 | 647213.0109 | 7612346.5929 | 7353311.3193 | 0 | 648286.0779 | 0 | 9248812.3258 | 24063512.4795 | 16423841.723 | 73451069.9279 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 86293200.3776 | 105286586.2359 | 100000 | 20.4441 | 4220.9346 | 5149.9747 | 86.0495 | 104.9892
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2964 | 51.6986 | 5.3486 | 4 | 4127.2688 | 5015.0447 | 84.14 | 102.2385 | 152.4713 | 0 | 267.6209 | 7637735.6832 | 661648.6779 | 7834359.8797 | 7632183.4106 | 0 | 596974.929 | 0 | 9501532.0064 | 24721037.2484 | 16872615.8885 | 75458087.7237 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 88300218.1734 | 107293604.0317 | 133352.1432 | 21.3943 | 4127.2688 | 5015.0447 | 84.14 | 102.2385
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7035 | 53.1362 | 5.5394 | 4 | 4055.7849 | 4912.9809 | 82.6827 | 100.1578 | 152.2833 | 0 | 205.3299 | 7781519.3368 | 672826.049 | 8009203.9516 | 7854234.9608 | 0 | 550774.7766 | 0 | 9698738.0392 | 25234126.8932 | 17222810.114 | 77024234.1211 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 89866364.5708 | 108859750.4291 | 177827.941 | 22.1576 | 4055.7849 | 4912.9809 | 82.6827 | 100.1578
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.0332 | 54.2161 | 5.6867 | 4 | 4001.3831 | 4836.3732 | 81.5736 | 98.596 | 152.1379 | 0 | 263.476 | 7888427.7175 | 681077.3457 | 8139983.0783 | 8021732.6637 | 0 | 509426.42 | 0 | 9843852.4178 | 25611684.7393 | 17480501.1021 | 78176685.4843 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 91018815.934 | 110012201.7923 | 237137.3706 | 22.7468 | 4001.3831 | 4836.3732 | 81.5736 | 98.596
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.5741 | 55.0364 | 5.8004 | 4 | 3960.0999 | 4778.7228 | 80.732 | 97.4207 | 152.0248 | 0 | 242.1803 | 7968997.8101 | 687259.6557 | 8239006.2853 | 8149385.412 | 0 | 474297.0909 | 0 | 9952389.039 | 25894074.7638 | 17673238.0964 | 79038648.1532 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 91880778.6028 | 110874164.4612 | 316227.766 | 23.2016 | 3960.0999 | 4778.7228 | 80.732 | 97.4207
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.1734 | 55.8645 | 5.9029 | 4 | 3928.7129 | 4733.1226 | 80.0921 | 96.4911 | 151.9074 | 0 | 256.1418 | 8048776.7143 | 693184.6274 | 8338871.2935 | 8271381.6422 | 0 | 451610.1228 | 0 | 10063491.516 | 26183140.6188 | 17870531.4821 | 79920988.017 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 92763118.4666 | 111756504.325 | 421696.5034 | 23.6116 | 3928.7129 | 4733.1226 | 80.0921 | 96.4911
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.6498 | 56.3319 | 5.9682 | 4 | 3904.9587 | 4700.5605 | 79.6079 | 95.8273 | 151.8398 | 0 | 222.7804 | 8093364.3917 | 696450.1154 | 8395144.9382 | 8339105.3151 | 0 | 428238.5595 | 0 | 10121398.2948 | 26333802.1787 | 17973361.0925 | 80380864.8859 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 93222995.3356 | 112216381.1939 | 562341.3252 | 23.873 | 3904.9587 | 4700.5605 | 79.6079 | 95.8273
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 161.7675 | 56.6849 | 6.0179 | 4 | 3887.0204 | 4676.0572 | 79.2422 | 95.3278 | 151.7881 | 0 | 289.1225 | 8126912.3982 | 698898.0294 | 8437596.2578 | 8390242.6832 | 0 | 409667.3718 | 0 | 10164693.5288 | 26446447.4966 | 18050243.8366 | 80724701.6026 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 93566832.0523 | 112560217.9106 | 749894.2093 | 24.0716 | 3887.0204 | 4676.0572 | 79.2422 | 95.3278
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.942 | 57.0553 | 6.0651 | 4 | 3872.4511 | 4655.3532 | 78.9452 | 94.9057 | 151.7337 | 0 | 261.3879 | 8162008.94 | 701452.9768 | 8482088.9308 | 8443891.9109 | 0 | 396472.6571 | 0 | 10212507.0121 | 26570848.3722 | 18135149.9904 | 81104420.7903 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 93946551.24 | 112939937.0983 | 1000000 | 24.2602 | 3872.4511 | 4655.3532 | 78.9452 | 94.9057
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.5534 | 57.2477 | 6.0927 | 4 | 3862.3986 | 4641.75 | 78.7402 | 94.6284 | 151.7051 | 0 | 250.0618 | 8180181.0318 | 702770.9278 | 8505181.0722 | 8471748.9994 | 0 | 385127.5906 | 0 | 10235553.7525 | 26630811.2633 | 18176075.8957 | 81287450.5335 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94129580.9831 | 113122966.8415 | 1333521.4322 | 24.3708 | 3862.3986 | 4641.75 | 78.7402 | 94.6284
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.0092 | 57.391 | 6.1134 | 4 | 3854.8346 | 4631.5441 | 78.586 | 94.4203 | 151.6837 | 0 | 257.2431 | 8193694.1884 | 703749.4284 | 8522371.8565 | 8492494.7749 | 0 | 376352.2977 | 0 | 10252578.3929 | 26675105.8854 | 18206307.8854 | 81422654.7096 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94264785.1592 | 113258171.0176 | 1778279.41 | 24.4537 | 3854.8346 | 4631.5441 | 78.586 | 94.4203
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.3427 | 57.4958 | 6.1288 | 4 | 3849.1473 | 4623.9086 | 78.4701 | 94.2646 | 151.668 | 0 | 262.0088 | 8203564.022 | 704463.2319 | 8534938.3922 | 8507664.0736 | 0 | 369551.4365 | 0 | 10264870.6509 | 26707087.8192 | 18228136.2124 | 81520275.8386 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94362406.2883 | 113355792.1467 | 2371373.7057 | 24.5151 | 3849.1473 | 4623.9086 | 78.4701 | 94.2646
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.601 | 57.5768 | 6.1405 | 4 | 3844.8738 | 4618.1523 | 78.383 | 94.1473 | 151.6558 | 0 | 248.55 | 8211193.7755 | 705014.5885 | 8544658.3462 | 8519399.7923 | 0 | 364444.9161 | 0 | 10274437.4532 | 26731978.6764 | 18245124.7339 | 81596252.282 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94438382.7317 | 113431768.5901 | 3162277.6602 | 24.5622 | 3844.8738 | 4618.1523 | 78.383 | 94.1473
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.7908 | 57.6364 | 6.1493 | 4 | 3841.6641 | 4613.8447 | 78.3175 | 94.0595 | 151.6468 | 0 | 242.7952 | 8216797.3622 | 705419.2352 | 8551800.5445 | 8528024.4475 | 0 | 360531.9938 | 0 | 10281403.6975 | 26750103.4149 | 18257495.2403 | 81651575.936 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94493706.3857 | 113487092.244 | 4216965.0343 | 24.5971 | 3841.6641 | 4613.8447 | 78.3175 | 94.0595
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.9345 | 57.6815 | 6.1559 | 4 | 3839.2542 | 4610.6085 | 78.2684 | 93.9935 | 151.64 | 0 | 251.1865 | 8221036.1507 | 705725.182 | 8557205.0044 | 8534551.4572 | 0 | 357583.0941 | 0 | 10286679.3465 | 26763829.5716 | 18266863.6243 | 81693473.431 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94535603.8807 | 113528989.739 | 5623413.2519 | 24.6234 | 3839.2542 | 4610.6085 | 78.2684 | 93.9935
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.042 | 57.7152 | 6.1608 | 4 | 3837.4455 | 4608.1817 | 78.2315 | 93.944 | 151.6349 | 0 | 252.6738 | 8224202.5832 | 705953.6407 | 8561243.2767 | 8539428.9303 | 0 | 355352.7542 | 0 | 10290610.6622 | 26774058.0486 | 18273844.77 | 81724694.6659 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94566825.1156 | 113560210.9739 | 7498942.0933 | 24.6432 | 3837.4455 | 4608.1817 | 78.2315 | 93.944
1 | 3600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.1197 | 57.7396 | 6.1644 | 4 | 3836.0881 | 4606.3701 | 78.2038 | 93.9071 | 151.6313 | 0 | 243.6806 | 8226494.2874 | 706118.9262 | 8564166.6702 | 8542960.0143 | 0 | 353645.0679 | 0 | 10293420.1368 | 26781367.7251 | 18278833.7745 | 81747006.6025 | 961560.8286 | 11880569.6211 | 11880569.6211 | 1478867.319 | 5633948.9183 | 0 | 94589137.0521 | 113582522.9105 | 10000000 | 24.6577 | 3836.0881 | 4606.3701 | 78.2038 | 93.9071
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.712 | [19 empty] | 100 | 0
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.78939 | 0.14232 | 0.0026595 | 4 | 1328690.817 | 3168998.2663 | 27087.1595 | 64604.316 | 105.9753 | 0 | 37.0991 | 95304.193 | 6112.684 | 72459.3546 | 51928.6609 | 0 | 56858.4167 | 0 | 110238.6906 | 286818.4598 | 195759.4924 | 875479.952 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14134698.183 | 33712006.9352 | 133.3521 | 0.010638 | 1328690.817 | 3168998.2663 | 27087.1595 | 64604.316
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.21281 | 0.0076634 | 4 | 469699.8868 | 1108358.5234 | 9575.4675 | 22595.3877 | 115.1421 | 0 | 62.6 | 133129.4876 | 9035.0053 | 99322.5787 | 62672.5588 | 0 | 63541.682 | 0 | 143403.5119 | 373106.5217 | 254652.8677 | 1138864.2137 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14398082.4447 | 33975391.197 | 177.8279 | 0.030654 | 469699.8868 | 1108358.5234 | 9575.4675 | 22595.3877
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.325 | 0.316 | 0.015655 | 4 | 235588.7514 | 548222.2992 | 4802.7954 | 11176.2531 | 123.608 | 0 | 61.1926 | 183475.8255 | 13129.9926 | 135469.4618 | 77878.5132 | 0 | 72246.6536 | 0 | 188058.1742 | 489288.7932 | 333949.6553 | 1493497.0694 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 14752715.3004 | 34330024.0527 | 237.1374 | 0.062621 | 235588.7514 | 548222.2992 | 4802.7954 | 11176.2531
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.45793 | 0.027593 | 4 | 137736.5233 | 315109.2948 | 2807.9453 | 6423.9292 | 130.7836 | 0 | 292.5655 | 246478.5539 | 18490.4932 | 181368.0743 | 98790.6738 | 0 | 82294.7585 | 0 | 244694.7959 | 636645.6653 | 434523.7483 | 1943286.7632 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15202504.9942 | 34779813.7465 | 316.2278 | 0.11037 | 137736.5233 | 315109.2948 | 2807.9453 | 6423.9292
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.64832 | 0.044507 | 4 | 88523.3621 | 198491.0394 | 1804.6685 | 4046.5083 | 136.7017 | 0 | 392.4038 | 323309.7875 | 25252.908 | 238553.0578 | 126375.4611 | 0 | 93806.3433 | 0 | 314846.0476 | 819164.8319 | 559096.8299 | 2500405.2672 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 15759623.4983 | 35336932.2505 | 421.6965 | 0.17803 | 88523.3621 | 198491.0394 | 1804.6685 | 4046.5083
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9544 | 0.90646 | 0.068076 | 4 | 60445.4214 | 132340.5315 | 1232.2617 | 2697.9407 | 141.6033 | 0 | 521.8731 | 418000.1119 | 33788.4593 | 310878.9938 | 162706.2936 | 0 | 107895.4946 | 0 | 402975.0478 | 1048458.4128 | 715594.4104 | 3200297.2242 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 16459515.4552 | 36036824.2074 | 562.3413 | 0.2723 | 60445.4214 | 132340.5315 | 1232.2617 | 2697.9407
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 1.2618 | 0.10123 | 4 | 42882.4756 | 91231.9589 | 874.2173 | 1859.8869 | 145.6104 | 0 | 77.0239 | 536998.807 | 44758.7797 | 403896.1525 | 213816.0748 | 0 | 125714.1737 | 0 | 516821.7552 | 1344664.1922 | 917760.9413 | 4104430.8763 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 17363649.1073 | 36940957.8596 | 749.8942 | 0.40491 | 42882.4756 | 91231.9589 | 874.2173 | 1859.8869
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1495 | 1.7362 | 0.14636 | 4 | 31589.5771 | 65028.781 | 643.9963 | 1325.6997 | 148.7567 | 0 | 94.7198 | 682048.8448 | 58354.2256 | 520169.1157 | 282629.1031 | 0 | 147073.1124 | 0 | 659207.0166 | 1715121.4352 | 1170605.6217 | 5235208.4749 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 18494426.7059 | 38071735.4582 | 1000 | 0.58546 | 31589.5771 | 65028.781 | 643.9963 | 1325.6997
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8085 | 2.3663 | 0.20666 | 4 | 24070.2458 | 47753.266 | 490.7045 | 973.5149 | 151.1633 | 0 | 90.1952 | 857413.6489 | 74865.93 | 665186.6136 | 372855.2921 | 0 | 172927.7545 | 0 | 835867.2033 | 2174755.0029 | 1484314.9763 | 6638186.4216 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 19897404.6526 | 39474713.4049 | 1333.5214 | 0.82664 | 24070.2458 | 47753.266 | 490.7045 | 973.5149
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.04 | 3.2152 | 0.28823 | 4 | 18803.6489 | 35784.4185 | 383.3378 | 729.5138 | 153.0032 | 0 | 95.9347 | 1073543.7813 | 95332.9735 | 848843.8693 | 495479.3818 | 0 | 205242.9829 | 0 | 1060192.7656 | 2758404.1008 | 1882667.4783 | 8419707.3335 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 21678925.5646 | 41256234.3168 | 1778.2794 | 1.1529 | 18803.6489 | 35784.4185 | 383.3378 | 729.5138
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9849 | 4.3461 | 0.39854 | 4 | 14996.1504 | 27276.6662 | 305.7168 | 556.0717 | 154.6167 | 0 | 83.2787 | 1337982.5272 | 120588.0487 | 1078929.6026 | 656724.232 | 0 | 243431.2159 | 0 | 1340685.6943 | 3488189.1641 | 2380760.7796 | 10647291.2645 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 23906509.4955 | 43483818.2478 | 2371.3737 | 1.5942 | 14996.1504 | 27276.6662 | 305.7168 | 556.0717
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.907 | 5.9075 | 0.54468 | 4 | 12280.9031 | 21266.5833 | 250.3628 | 433.5481 | 155.7409 | 0 | 83.8424 | 1661085.1385 | 149564.1647 | 1379203.7683 | 876291.338 | 0 | 291738.6074 | 0 | 1699574.3766 | 4421943.8972 | 3018067.5717 | 13497468.8624 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 26756687.0934 | 46333995.8456 | 3162.2777 | 2.1787 | 12280.9031 | 21266.5833 | 250.3628 | 433.5481
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.1152 | 7.9719 | 0.73818 | 4 | 10265.245 | 16895.5202 | 209.2709 | 344.438 | 156.5966 | 0 | 102.6946 | 2052840.0097 | 184687.7099 | 1752787.6851 | 1164687.8666 | 0 | 350234.5641 | 0 | 2147042.7558 | 5586164.8316 | 3812672.2818 | 17051117.7045 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 30310335.9356 | 49887644.6878 | 4216.965 | 2.9527 | 10265.245 | 16895.5202 | 209.2709 | 344.438
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.007 | 10.6919 | 0.99379 | 4 | 8739.3342 | 13664.2533 | 178.1631 | 278.5643 | 157.2457 | 0 | 86.1202 | 2527577.1708 | 227287.1798 | 2216550.3667 | 1543215.6887 | 0 | 420861.1862 | 0 | 2704841.7209 | 7037443.3186 | 4803199.6699 | 21480976.3016 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 34740194.5327 | 54317503.2849 | 5623.4133 | 3.9752 | 8739.3342 | 13664.2533 | 178.1631 | 278.5643
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.0669 | 14.2757 | 1.3293 | 4 | 7571.7358 | 11253.5227 | 154.3601 | 229.4183 | 157.7358 | 0 | 94.9819 | 3100972.5725 | 278262.7726 | 2793264.6307 | 2039578.7724 | 0 | 506053.8022 | 0 | 3400071.6946 | 8846289.0988 | 6037774.083 | 27002267.4268 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 40261485.6578 | 59838794.4101 | 7498.9421 | 5.3173 | 7571.7358 | 11253.5227 | 154.3601 | 229.4183
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.889 | 18.9495 | 1.7665 | 4 | 6666.7357 | 9437.3908 | 135.9104 | 192.394 | 158.0944 | 0 | 101.5523 | 3789765.3504 | 339278.0069 | 3503585.8849 | 2687210.8493 | 0 | 608421.9947 | 0 | 4262022.2136 | 11088907.5388 | 7568407.2495 | 33847599.0879 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 47106817.3189 | 66684126.0712 | 10000 | 7.0659 | 6666.7357 | 9437.3908 | 135.9104 | 192.394
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.0117 | 24.8972 | 2.322 | 4 | 5966.8096 | 8074.6556 | 121.6415 | 164.6128 | 158.2903 | 0 | 103.2395 | 4599230.2322 | 410716.0576 | 4358668.9198 | 3514326.7078 | 0 | 728948.2701 | 0 | 5308637.1731 | 13811984.9733 | 9426963.5522 | 42159475.8861 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 55418694.1171 | 74996002.8694 | 13335.2143 | 9.2878 | 5966.8096 | 8074.6556 | 121.6415 | 164.6128
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.8474 | 32.1801 | 2.9989 | 4 | 5435.224 | 7067.2678 | 110.8044 | 144.0758 | 158.2144 | 0 | 112.5082 | 5518355.6472 | 491527.5438 | 5351848.3414 | 4539667.5124 | 0 | 868115.2738 | 0 | 6540110.5842 | 17016026.1791 | 11613787.5116 | 51939438.5935 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 65198656.8245 | 84775965.5767 | 17782.7941 | 11.9956 | 5435.224 | 7067.2678 | 110.8044 | 144.0758
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.5996 | 37.7262 | 3.5857 | 4 | 5036.9744 | 6401.9281 | 102.6855 | 130.512 | 157.9398 | 0 | 140.1871 | 6178568.3887 | 549397.3888 | 6077823.2005 | 5336551.2794 | 0 | 902044.8777 | 0 | 7427310.2027 | 19324337.5966 | 13189257.4851 | 58985290.4196 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 72244508.6506 | 91821817.4028 | 23713.7371 | 14.3428 | 5036.9744 | 6401.9281 | 102.6855 | 130.512
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.5692 | 42.0946 | 4.1028 | 4 | 4726.2637 | 5919.1822 | 96.3513 | 120.6705 | 157.5976 | 0 | 162.3561 | 6679221.6258 | 593191.0868 | 6634594.4007 | 5977719.9873 | 0 | 877144.4132 | 0 | 8097129.8904 | 21067071.0252 | 14378708.8597 | 64304781.2892 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 77563999.5202 | 97141308.2725 | 31622.7766 | 16.4113 | 4726.2637 | 5919.1822 | 96.3513 | 120.6705
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.3728 | 45.9231 | 4.5782 | 4 | 4484.7426 | 5553.7988 | 91.4275 | 113.2217 | 157.2093 | 0 | 205.6582 | 7105959.9704 | 630461.5884 | 7113100.8543 | 6552084.7047 | 0 | 833752.6066 | 0 | 8671790.2925 | 22562219.5122 | 15399178.4244 | 68868547.9534 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 82127766.1844 | 101705074.9366 | 42169.6503 | 18.3127 | 4484.7426 | 5553.7988 | 91.4275 | 113.2217
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.825 | 48.8466 | 4.9713 | 4 | 4298.7915 | 5283.3145 | 87.6367 | 107.7075 | 156.857 | 0 | 240.3029 | 7423162.0147 | 657815.469 | 7473382.1893 | 6996013.1058 | 0 | 767881.7798 | 0 | 9094119.2778 | 23661032.9005 | 16149141.1402 | 72222547.8771 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 85481766.1082 | 105059074.8604 | 56234.1325 | 19.8851 | 4298.7915 | 5283.3145 | 87.6367 | 107.7075
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1003 | 52.3596 | 5.3911 | 4 | 4154.9322 | 5062.791 | 84.7039 | 103.2118 | 156.4159 | 0 | 260.0849 | 7793365.8935 | 689036.1708 | 7901277.025 | 7528433.4718 | 0 | 735158.5526 | 0 | 9612435.7344 | 25009585.9992 | 17069556.3401 | 76338849.1875 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 89598067.4185 | 109175376.1708 | 74989.4209 | 21.5643 | 4154.9322 | 5062.791 | 84.7039 | 103.2118
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.7982 | 54.9618 | 5.7234 | 4 | 4042.8927 | 4898.0403 | 82.4198 | 99.8532 | 156.0917 | 0 | 237.4645 | 8062636.3518 | 711656.0106 | 8214597.4886 | 7925876.0743 | 0 | 687492.1014 | 0 | 9984880.6304 | 25978611.2197 | 17730935.9645 | 79296685.8413 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 92555904.0723 | 112133212.8245 | 100000 | 22.8935 | 4042.8927 | 4898.0403 | 82.4198 | 99.8532
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9681 | 57.8511 | 6.0673 | 4 | 3955.0311 | 4761.6979 | 80.6287 | 97.0737 | 155.6924 | 0 | 229.8868 | 8367404.1289 | 738952.3204 | 8557498.9141 | 8373619.8242 | 0 | 672306.9586 | 0 | 10416815.037 | 27102415.9437 | 18497955.7806 | 82726968.9075 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 95986187.1385 | 115563495.8907 | 133352.1432 | 24.2694 | 3955.0311 | 4761.6979 | 80.6287 | 97.0737
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.4575 | 59.2061 | 6.2678 | 4 | 3888.017 | 4668.8844 | 79.2625 | 95.1815 | 155.4895 | 0 | 262.2721 | 8510882.7736 | 752137.3165 | 8716806.3881 | 8586275.6137 | 0 | 625136.5587 | 0 | 10604583.0737 | 27590949.8588 | 18831390.216 | 84218161.7991 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 97477380.0301 | 117054688.7824 | 177827.941 | 25.0712 | 3888.017 | 4668.8844 | 79.2625 | 95.1815
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.3345 | 60.0557 | 6.4083 | 4 | 3837.2424 | 4600.9908 | 78.2274 | 93.7974 | 155.3535 | 0 | 242.9814 | 8600644.3276 | 760429.2786 | 8816283.2786 | 8720863.8933 | 0 | 578234.1227 | 0 | 10715817.4113 | 27880358.7878 | 19028917.7568 | 85101548.8566 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 98360767.0876 | 117938075.8399 | 237137.3706 | 25.6332 | 3837.2424 | 4600.9908 | 78.2274 | 93.7974
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0413 | 60.8389 | 6.5288 | 4 | 3798.7927 | 4548.4425 | 77.4435 | 92.7262 | 155.22 | 0 | 225.6194 | 8683314.5033 | 768104.7878 | 8907703.4864 | 8846033.8311 | 0 | 544361.1788 | 0 | 10822311.9371 | 28157435.6989 | 19218028.442 | 85947293.8654 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 99206512.0964 | 118783820.8487 | 316227.766 | 26.1153 | 3798.7927 | 4548.4425 | 77.4435 | 92.7262
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.1017 | 61.428 | 6.621 | 4 | 3769.6623 | 4508.8742 | 76.8497 | 91.9195 | 155.1169 | 0 | 267.4566 | 8745384.4992 | 773883.5989 | 8976283.0919 | 8940659.8106 | 0 | 516495.3253 | 0 | 10901555.4671 | 28363611.1089 | 19358747.3957 | 86576620.2976 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 99835838.5286 | 119413147.2809 | 421696.5034 | 26.484 | 3769.6623 | 4508.8742 | 76.8497 | 91.9195
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.6487 | 61.866 | 6.6908 | 4 | 3747.6366 | 4479.1394 | 76.4006 | 91.3133 | 155.0386 | 0 | 253.5691 | 8791494.6458 | 778185.7634 | 9027192.6486 | 9011323.8047 | 0 | 493892.1723 | 0 | 10959814.7236 | 28515189.7436 | 19462202.9286 | 87039296.4305 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100298514.6615 | 119875823.4138 | 562341.3252 | 26.7631 | 3747.6366 | 4479.1394 | 76.4006 | 91.3133
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.4018 | 62.0776 | 6.7333 | 4 | 3731.0185 | 4457.9066 | 76.0619 | 90.8805 | 155.0001 | 0 | 249.7954 | 8813754.9884 | 780266.7367 | 9051749.5345 | 9045570.5599 | 0 | 471825.9373 | 0 | 10983635.4252 | 28577166.3228 | 19504503.2174 | 87228472.7222 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100487690.9532 | 120064999.7054 | 749894.2093 | 26.933 | 3731.0185 | 4457.9066 | 76.0619 | 90.8805
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.387 | 62.0726 | 6.7507 | 4 | 3718.5533 | 4443.5677 | 75.8077 | 90.5881 | 155.0003 | 0 | 243.2097 | 8813241.6198 | 780221.2288 | 9051164.154 | 9044819.5142 | 0 | 448889.5888 | 0 | 10973951.0812 | 28551969.6463 | 19487305.9679 | 87151562.801 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100410781.032 | 119988089.7842 | 1000000 | 27.0026 | 3718.5533 | 4443.5677 | 75.8077 | 90.5881
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 168.487 | 61.5339 | 6.7165 | 4 | 3708.7408 | 4437.4465 | 75.6077 | 90.4633 | 155.0953 | 0 | 511.7292 | 8756604.4479 | 774939.6038 | 8988598.1212 | 8957980.1614 | 0 | 410877.6821 | 0 | 10876710.0064 | 28298968.3167 | 19314627.3618 | 86379305.7012 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 99638523.9323 | 119215832.6845 | 1333521.4322 | 26.8659 | 3708.7408 | 4437.4465 | 75.6077 | 90.4633
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.387 | 62.0719 | 6.7753 | 4 | 3701.3073 | 4423.6878 | 75.4562 | 90.1829 | 154.9997 | 0 | 232.2779 | 8813164.5159 | 780213.2831 | 9051084.7204 | 9044756.6353 | 0 | 416417.8635 | 0 | 10961198.4371 | 28518789.8824 | 19464660.0973 | 87050285.435 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100309503.666 | 119886812.4182 | 1778279.41 | 27.1011 | 3701.3073 | 4423.6878 | 75.4562 | 90.1829
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3675 | 62.0657 | 6.7821 | 4 | 3696.1368 | 4417.7865 | 75.3507 | 90.0626 | 155.0005 | 0 | 229.2959 | 8812549.3852 | 780160.3798 | 9050370.8935 | 9043814.9543 | 0 | 406255.8228 | 0 | 10956329.0599 | 28506120.7616 | 19456013.162 | 87011614.419 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100270832.65 | 119848141.4023 | 2371373.7057 | 27.1286 | 3696.1368 | 4417.7865 | 75.3507 | 90.0626
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3675 | 62.0655 | 6.7877 | 4 | 3692.2579 | 4413.3204 | 75.2717 | 89.9715 | 155.0003 | 0 | 230.6838 | 8812524.7902 | 780158.8866 | 9050337.6004 | 9043789.8354 | 0 | 398702.4626 | 0 | 10953350.2943 | 28498370.6248 | 19450723.5344 | 86987958.0286 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100247176.2597 | 119824485.0119 | 3162277.6602 | 27.1506 | 3692.2579 | 4413.3204 | 75.2717 | 89.9715
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3675 | 62.0653 | 6.7918 | 4 | 3689.3485 | 4409.9712 | 75.2124 | 89.9032 | 155.0002 | 0 | 228.9611 | 8812506.3416 | 780157.7666 | 9050312.6276 | 9043770.994 | 0 | 392993.4982 | 0 | 10951099.0789 | 28492513.4241 | 19446725.8746 | 86970079.6057 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100229297.8367 | 119806606.5889 | 4216965.0343 | 27.1672 | 3689.3485 | 4409.9712 | 75.2124 | 89.9032
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3649 | 62.0644 | 6.7948 | 4 | 3687.1671 | 4407.4676 | 75.1679 | 89.8522 | 155.0002 | 0 | 253.7592 | 8812415.4219 | 780149.7284 | 9050208.7913 | 9043638.3271 | 0 | 388660.8486 | 0 | 10949278.5157 | 28487776.6921 | 19443492.9576 | 86955621.2827 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100214839.5138 | 119792148.266 | 5623413.2519 | 27.1794 | 3687.1671 | 4407.4676 | 75.1679 | 89.8522
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3649 | 62.0642 | 6.7972 | 4 | 3685.5303 | 4405.5842 | 75.1345 | 89.8138 | 155.0001 | 0 | 256.773 | 8812405.0443 | 780149.0984 | 9050194.7438 | 9043627.7286 | 0 | 385416.0841 | 0 | 10947999.1527 | 28484448.0519 | 19441221.0923 | 86945460.9961 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100204679.2271 | 119781987.9794 | 7498942.0933 | 27.1887 | 3685.5303 | 4405.5842 | 75.1345 | 89.8138
1 | 3700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.3649 | 62.0642 | 6.7989 | 4 | 3684.3027 | 4404.1717 | 75.1095 | 89.785 | 155.0001 | 0 | 252.1261 | 8812397.2614 | 780148.6259 | 9050184.2085 | 9043619.78 | 0 | 382974.3093 | 0 | 10947036.4322 | 28481943.2506 | 19439511.514 | 86937815.3819 | 961560.8286 | 12297657.4024 | 12297657.4024 | 1478867.319 | 5800784.0308 | 0 | 100197033.6129 | 119774342.3652 | 10000000 | 27.1957 | 3684.3027 | 4404.1717 | 75.1095 | 89.785
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 26.0503 | [19 empty] | 100 | 0
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.79402 | 0.14715 | 0.0034559 | 4 | 1054212.4059 | 2513273.3436 | 21491.5458 | 51236.4766 | 107.6043 | 0 | 42.3575 | 98552.1159 | 6381.8199 | 74333.4936 | 52457.9424 | 0 | 55889.5425 | 0 | 112169.8166 | 291842.8535 | 199188.7443 | 890816.3285 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14572982.4318 | 34742418.2051 | 133.3521 | 0.013824 | 1054212.4059 | 2513273.3436 | 21491.5458 | 51236.4766
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0498 | 0.23025 | 0.0093662 | 4 | 397261.5536 | 935619.3839 | 8098.7141 | 19073.8667 | 118.0625 | 0 | 48.5346 | 142962.6994 | 9876.0818 | 105566.1838 | 64918.2356 | 0 | 64483.0944 | 0 | 151244.455 | 393507.0475 | 268576.6457 | 1201134.4433 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 14883300.5465 | 35052736.3199 | 177.8279 | 0.037465 | 397261.5536 | 935619.3839 | 8098.7141 | 19073.8667
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3639 | 0.34002 | 0.018383 | 4 | 207456.4519 | 481749.5271 | 4229.2804 | 9821.1157 | 126.5877 | 0 | 69.208 | 196168.1053 | 14307.5868 | 143347.9333 | 80984.2126 | 0 | 72935.6942 | 0 | 198019.9776 | 515207.3622 | 351639.6111 | 1572610.4832 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15254776.5864 | 35424212.3598 | 237.1374 | 0.073532 | 207456.4519 | 481749.5271 | 4229.2804 | 9821.1157
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.48822 | 0.031545 | 4 | 124555.1471 | 284402.3841 | 2539.2251 | 5797.9273 | 133.7675 | 0 | 301.3663 | 261568.1123 | 20007.1815 | 190516.865 | 102291.2158 | 0 | 82370.5061 | 0 | 256134.0135 | 666408.1627 | 454837.2644 | 2034133.3212 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 15716299.4244 | 35885735.1977 | 316.2278 | 0.12618 | 124555.1471 | 284402.3841 | 2539.2251 | 5797.9273
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 0.69402 | 0.050548 | 4 | 80667.8854 | 180422.6563 | 1644.524 | 3678.1599 | 139.9238 | 0 | 402.0192 | 344215.2869 | 27474.3274 | 251369.9918 | 131209.8659 | 0 | 94252.8164 | 0 | 330923.6925 | 860995.5661 | 587647.1656 | 2628088.7126 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 16310254.8159 | 36479690.5892 | 421.6965 | 0.20219 | 80667.8854 | 180422.6563 | 1644.524 | 3678.1599
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0322 | 0.97309 | 0.0773 | 4 | 55182.2709 | 120413.2879 | 1124.9652 | 2454.7877 | 144.9599 | 0 | 538.982 | 446551.6908 | 37027.4789 | 328239.7148 | 171020.0493 | 0 | 108513.9256 | 0 | 425627.6151 | 1107395.7464 | 755820.3516 | 3380196.5725 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 17062362.6757 | 37231798.449 | 562.3413 | 0.3092 | 55182.2709 | 120413.2879 | 1124.9652 | 2454.7877
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9922 | 1.351 | 0.11438 | 4 | 39374.0254 | 83457.4526 | 802.6928 | 1701.3931 | 149.0356 | 0 | 75.4646 | 573066.3761 | 49144.2818 | 425488.2137 | 225126.7208 | 0 | 126021.0817 | 0 | 545550.2029 | 1419409.7203 | 968776.3 | 4332582.8973 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 18014749.0006 | 38184184.7739 | 749.8942 | 0.45753 | 39374.0254 | 83457.4526 | 802.6928 | 1701.3931
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.281 | 1.862 | 0.16532 | 4 | 29068.916 | 59570.1375 | 592.6092 | 1214.4178 | 152.2848 | 0 | 99.7888 | 729439.3819 | 64436.3255 | 548615.7389 | 298464.9954 | 0 | 147768.2602 | 0 | 697602.6338 | 1815018.9551 | 1238787.7317 | 5540134.0225 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 19222300.1258 | 39391735.8991 | 1000 | 0.66127 | 29068.916 | 59570.1375 | 592.6092 | 1214.4178
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.9742 | 2.5326 | 0.23258 | 4 | 22248.7486 | 43929.3115 | 453.5708 | 895.5584 | 154.7331 | 0 | 82.6214 | 916054.8501 | 82776.367 | 700368.7514 | 392550.997 | 0 | 173434.2281 | 0 | 883422.2255 | 2298483.416 | 1568762.1606 | 7015852.9959 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 20698019.0991 | 40867454.8724 | 1333.5214 | 0.9303 | 22248.7486 | 43929.3115 | 453.5708 | 895.5584
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.24 | 3.4962 | 0.32405 | 4 | 17460.0891 | 33020.5246 | 355.9475 | 673.1681 | 156.7294 | 0 | 72.8308 | 1149034.7378 | 103789.2234 | 906437.2451 | 523681.8114 | 0 | 206584.8366 | 0 | 1126915.8632 | 2932003.9138 | 2001152.9178 | 8949600.5492 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 22631766.6524 | 42801202.4258 | 1778.2794 | 1.2962 | 17460.0891 | 33020.5246 | 355.9475 | 673.1681
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.2601 | 4.7681 | 0.44499 | 4 | 14055.7717 | 25387.2901 | 286.5459 | 517.5542 | 158.2855 | 0 | 92.4464 | 1429958.0594 | 129145.6111 | 1161747.0027 | 692544.6701 | 0 | 246711.9195 | 0 | 1427441.8325 | 3713910.8396 | 2534820.4613 | 11336280.3963 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 25018446.4996 | 45187882.2729 | 2371.3737 | 1.7799 | 14055.7717 | 25387.2901 | 286.5459 | 517.5542
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.258 | 6.4513 | 0.60474 | 4 | 11570.6345 | 19908.6591 | 235.883 | 405.8649 | 159.4381 | 0 | 71.97 | 1769390.3979 | 159584.3505 | 1479627.1848 | 915514.8765 | 0 | 295090.9123 | 0 | 1801491.0116 | 4687110.0755 | 3199048.937 | 14306857.7459 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 27989023.8492 | 48158459.6225 | 3162.2777 | 2.419 | 11570.6345 | 19908.6591 | 235.883 | 405.8649
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.5757 | 8.6907 | 0.81715 | 4 | 9704.6203 | 15875.2856 | 197.8418 | 323.6392 | 160.318 | 0 | 110.2745 | 2183357.3828 | 196595.5063 | 1877915.548 | 1211961.0614 | 0 | 354154.2531 | 0 | 2271353.6631 | 5909596.3128 | 4033420.9135 | 18038354.641 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 31720520.7442 | 51889956.5176 | 4216.965 | 3.2686 | 9704.6203 | 15875.2856 | 197.8418 | 323.6392
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.6138 | 11.6553 | 1.0983 | 4 | 8284.4755 | 12875.674 | 168.8902 | 262.488 | 160.9857 | 0 | 80.4341 | 2686524.185 | 241435.79 | 2374930.9467 | 1604289.7701 | 0 | 425792.4543 | 0 | 2859859.5269 | 7440767.8512 | 5078476.9509 | 22712077.4749 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 36394243.5782 | 56563679.3515 | 5623.4133 | 4.3931 | 8284.4755 | 12875.674 | 168.8902 | 262.488
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.8562 | 15.5486 | 1.4675 | 4 | 7191.3726 | 10627.4365 | 146.6059 | 216.6547 | 161.4894 | 0 | 102.8587 | 3294243.0385 | 295406.0723 | 2990787.6568 | 2119263.2585 | 0 | 511895.7506 | 0 | 3592522.3529 | 9347006.2346 | 6379523.8169 | 28530648.1811 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 42212814.2843 | 62382250.0577 | 7498.9421 | 5.8699 | 7191.3726 | 10627.4365 | 146.6059 | 216.6547
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.8831 | 20.6112 | 1.9473 | 4 | 6342.6154 | 8931.9615 | 129.3028 | 182.0901 | 161.8547 | 0 | 111.1527 | 4022435.548 | 359839.8111 | 3747285.3935 | 2789345.3518 | 0 | 614848.2631 | 0 | 4498164.2034 | 11703300.5568 | 7987743.1088 | 35722962.2365 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 49405128.3398 | 69574564.1131 | 10000 | 7.7894 | 6342.6154 | 8931.9615 | 129.3028 | 182.0901
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.2615 | 27.0485 | 2.5564 | 4 | 5684.9498 | 7657.3636 | 115.8954 | 156.1057 | 162.0434 | 0 | 124.3557 | 4877877.3428 | 435247.5897 | 4657445.8635 | 3644848.5568 | 0 | 736257.3295 | 0 | 5597153.906 | 14562646.3294 | 9939305.3523 | 44450782.2699 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 58132948.3731 | 78302384.1465 | 13335.2143 | 10.2258 | 5684.9498 | 7657.3636 | 115.8954 | 156.1057
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.3601 | 34.9019 | 3.2962 | 4 | 5185.2516 | 6715.0058 | 105.7084 | 136.8945 | 161.934 | 0 | 117.359 | 5846099.7689 | 520272.9197 | 5711015.7057 | 4702228.974 | 0 | 876060.4209 | 0 | 6885714.3378 | 17915216.2528 | 12227503.2134 | 54684111.5933 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 68366277.6965 | 88535713.4698 | 17782.7941 | 13.1848 | 5185.2516 | 6715.0058 | 105.7084 | 136.8945
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 101.2077 | 41.6204 | 3.9835 | 4 | 4815.2262 | 6081.0314 | 98.1649 | 123.9701 | 161.5652 | 0 | 120.3567 | 6625615.3194 | 588505.5309 | 6574735.7149 | 5627358.4721 | 0 | 938597.288 | 0 | 7938376.8069 | 20654028.0665 | 14096798.5532 | 63044015.752 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 76726181.8552 | 96895617.6286 | 23713.7371 | 15.9341 | 4815.2262 | 6081.0314 | 98.1649 | 123.9701
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 113.2286 | 46.2603 | 4.5376 | 4 | 4528.7382 | 5639.9692 | 92.3245 | 114.9784 | 161.1677 | 0 | 178.7767 | 7143050.004 | 633698.5456 | 7154853.9086 | 6282088.2267 | 0 | 908115.8139 | 0 | 8627504.5345 | 22446997.0544 | 15320536.7293 | 68516844.817 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 82199010.9202 | 102368446.6936 | 31622.7766 | 18.1505 | 4528.7382 | 5639.9692 | 92.3245 | 114.9784
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 124.0346 | 50.3065 | 5.0437 | 4 | 4306.0527 | 5305.7955 | 87.7847 | 108.1658 | 160.7286 | 0 | 197.075 | 7582319.1058 | 672006.4429 | 7651261.2205 | 6865796.1878 | 0 | 859498.0822 | 0 | 9216043.6053 | 23978254.9905 | 16365651.7349 | 73190831.3698 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 86872997.4731 | 107042433.2464 | 42169.6503 | 20.1746 | 4306.0527 | 5305.7955 | 87.7847 | 108.1658
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.3001 | 53.674 | 5.4844 | 4 | 4133.9828 | 5053.3853 | 84.2768 | 103.0201 | 160.2968 | 0 | 224.468 | 7940302.5188 | 703187.9063 | 8058328.7166 | 7362424.1188 | 0 | 798840.5579 | 0 | 9696602.6892 | 25228571.1506 | 17219018.2056 | 77007275.864 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 90689441.9672 | 110858877.7405 | 56234.1325 | 21.9375 | 4133.9828 | 5053.3853 | 84.2768 | 103.0201
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 143.8876 | 57.4759 | 5.9442 | 4 | 3998.8872 | 4847.1756 | 81.5227 | 98.8162 | 159.8252 | 0 | 234.2089 | 8336892.6606 | 737694.2199 | 8511813.669 | 7928091.6489 | 0 | 766171.8019 | 0 | 10249458.9601 | 26666989.7612 | 18200768.4638 | 81397881.1855 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 95080047.2887 | 115249483.0621 | 74989.4209 | 23.7766 | 3998.8872 | 4847.1756 | 81.5227 | 98.8162
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.7398 | 59.8834 | 6.2728 | 4 | 3895.1763 | 4699.025 | 79.4084 | 95.796 | 159.5048 | 0 | 245.0199 | 8584183.0571 | 759190.8095 | 8795868.9374 | 8291845.9398 | 0 | 706514.6178 | 0 | 10583665.311 | 27536526.1309 | 18794244.9034 | 84052039.7068 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 97734205.81 | 117903641.5834 | 100000 | 25.0911 | 3895.1763 | 4699.025 | 79.4084 | 95.796
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.1797 | 61.763 | 6.5369 | 4 | 3815.8991 | 4587.2725 | 77.7923 | 93.5178 | 159.2405 | 0 | 272.4193 | 8775292.2277 | 775793.6392 | 9016047.7636 | 8579569.6092 | 0 | 650120.9784 | 0 | 10840761.4451 | 28205437.5342 | 19250790.6809 | 86093813.8785 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 99775979.9817 | 119945415.7551 | 133352.1432 | 26.1474 | 3815.8991 | 4587.2725 | 77.7923 | 93.5178
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.3797 | 63.1946 | 6.7439 | 4 | 3755.5014 | 4503.1951 | 76.561 | 91.8037 | 159.0309 | 0 | 265.9632 | 8919756.1056 | 788338.4166 | 9182858.4721 | 8801082.2313 | 0 | 598995.5946 | 0 | 11033502.0199 | 28706908.9732 | 19593055.2422 | 87624497.0555 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 101306663.1587 | 121476098.9321 | 177827.941 | 26.9755 | 3755.5014 | 4503.1951 | 76.561 | 91.8037
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6434 | 64.294 | 6.9056 | 4 | 3709.5989 | 4439.7864 | 75.6252 | 90.5111 | 158.8646 | 0 | 303.9471 | 9030057.1778 | 797913.3526 | 9310434.2822 | 8972286.4825 | 0 | 555146.3511 | 0 | 11179676.682 | 29087225.4595 | 19852629.0588 | 88785368.8463 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 102467534.9495 | 122636970.7229 | 237137.3706 | 27.6223 | 3709.5989 | 4439.7864 | 75.6252 | 90.5111
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0749 | 65.1059 | 7.0283 | 4 | 3674.7991 | 4392.2401 | 74.9158 | 89.5418 | 158.7389 | 0 | 275.8913 | 9111175.2306 | 804953.2101 | 9404372.6352 | 9099510.1086 | 0 | 517738.4687 | 0 | 11285722.3647 | 29363134.5731 | 20040942.6982 | 89627549.2892 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 103309715.3924 | 123479151.1657 | 316227.766 | 28.113 | 3674.7991 | 4392.2401 | 74.9158 | 89.5418
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.8776 | 65.7039 | 7.1208 | 4 | 3648.4683 | 4356.588 | 74.379 | 88.8149 | 158.6447 | 0 | 279.9739 | 9170745.2772 | 810122.0629 | 9473419.5213 | 9193700.6118 | 0 | 486690.5063 | 0 | 11362524.412 | 29562957.7458 | 20177326.1195 | 90237486.2569 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 103919652.3601 | 124089088.1334 | 421696.5034 | 28.4831 | 3648.4683 | 4356.588 | 74.379 | 88.8149
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.2413 | 66.1542 | 7.1911 | 4 | 3628.5772 | 4329.7687 | 73.9735 | 88.2682 | 158.5728 | 0 | 313.431 | 9215488.092 | 814003.8387 | 9525314.7117 | 9264877.4877 | 0 | 461779.4302 | 0 | 11419770.7885 | 29711901.0745 | 20278983.0019 | 90692118.425 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 104374284.5283 | 124543720.3016 | 562341.3252 | 28.7645 | 3628.5772 | 4329.7687 | 73.9735 | 88.2682
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.2398 | 66.4826 | 7.2436 | 4 | 3613.5714 | 4309.6881 | 73.6675 | 87.8588 | 158.5199 | 0 | 319.0791 | 9248073.9851 | 816830.626 | 9563128.0973 | 9316954.1283 | 0 | 441769.2159 | 0 | 11460834.8605 | 29818741.3667 | 20351903.6966 | 91018235.9765 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 104700402.0797 | 124869837.8531 | 749894.2093 | 28.9742 | 3613.5714 | 4309.6881 | 73.6675 | 87.8588
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.9781 | 66.7248 | 7.2828 | 4 | 3602.2642 | 4294.6328 | 73.437 | 87.5519 | 158.4806 | 0 | 312.7258 | 9272071.6728 | 818912.2441 | 9590985.4571 | 9355436.1062 | 0 | 425995.816 | 0 | 11490726.5055 | 29896513.2953 | 20404984.636 | 91255625.7331 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 104937791.8363 | 125107227.6096 | 1000000 | 29.1311 | 3602.2642 | 4294.6328 | 73.437 | 87.5519
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.528 | 66.5765 | 7.2842 | 4 | 3592.9479 | 4285.1776 | 73.2471 | 87.3591 | 158.5039 | 0 | 409.6726 | 9257378.676 | 817637.753 | 9573928.3127 | 9331949.1804 | 0 | 401666.4721 | 0 | 11459198.5537 | 29814484.032 | 20348997.9782 | 91005240.9582 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 104687407.0614 | 124856842.8347 | 1333521.4322 | 29.1369 | 3592.9479 | 4285.1776 | 73.2471 | 87.3591
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3157 | 67.1626 | 7.3465 | 4 | 3586.5627 | 4272.924 | 73.1169 | 87.1093 | 158.4094 | 0 | 293.3269 | 9315393.3562 | 822669.746 | 9641296.0172 | 9425130.3464 | 0 | 406479.1404 | 0 | 11548277.7564 | 30046249.8447 | 20507182.9077 | 91712679.1151 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105394845.2184 | 125564280.9917 | 1778279.41 | 29.386 | 3586.5627 | 4272.924 | 73.1169 | 87.1093
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.5982 | 67.2546 | 7.3623 | 4 | 3581.8196 | 4266.7133 | 73.0202 | 86.9827 | 158.3942 | 0 | 288.0982 | 9324494.7891 | 823459.1045 | 9651869.2038 | 9439834.2828 | 0 | 399131.3921 | 0 | 11559127.6212 | 30074478.9673 | 20526449.8639 | 91798845.2247 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105481011.3279 | 125650447.1013 | 2371373.7057 | 29.449 | 3581.8196 | 4266.7133 | 73.0202 | 86.9827
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.8345 | 67.3316 | 7.3748 | 4 | 3578.2565 | 4261.9855 | 72.9476 | 86.8863 | 158.3815 | 0 | 293.2084 | 9332103.8392 | 824119.0159 | 9660709.6019 | 9452136.0163 | 0 | 393795.8667 | 0 | 11568517.0926 | 30098908.4459 | 20543123.485 | 91873413.3637 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105555579.4669 | 125725015.2403 | 3162277.6602 | 29.4992 | 3578.2565 | 4261.9855 | 72.9476 | 86.8863
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0003 | 67.3856 | 7.3839 | 4 | 3575.5809 | 4258.469 | 72.8931 | 86.8147 | 158.3725 | 0 | 283.0375 | 9337435.3048 | 824581.3911 | 9666904.3409 | 9460763.4119 | 0 | 389632.2078 | 0 | 11574933.4961 | 30115602.6114 | 20554517.5961 | 91924370.3602 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105606536.4634 | 125775972.2367 | 4216965.0343 | 29.5355 | 3575.5809 | 4258.469 | 72.8931 | 86.8147
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.1124 | 67.4221 | 7.3903 | 4 | 3573.5724 | 4255.8637 | 72.8521 | 86.7615 | 158.3665 | 0 | 284.3454 | 9341035.78 | 824893.6414 | 9671088.0394 | 9466594.3372 | 0 | 386357.7693 | 0 | 11579088.1313 | 30126412.12 | 20561895.3077 | 91957365.1263 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105639531.2295 | 125808967.0028 | 5623413.2519 | 29.5613 | 3573.5724 | 4255.8637 | 72.8521 | 86.7615
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2024 | 67.4514 | 7.3954 | 4 | 3572.065 | 4253.8931 | 72.8214 | 86.7214 | 158.3616 | 0 | 302.7601 | 9343927.096 | 825144.3879 | 9674447.8412 | 9471277.8435 | 0 | 383949.1104 | 0 | 11582511.0488 | 30135317.8493 | 20567973.651 | 91984548.8281 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105666714.9313 | 125836150.7046 | 7498942.0933 | 29.5814 | 3572.065 | 4253.8931 | 72.8214 | 86.7214
1 | 3800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2755 | 67.4752 | 7.3993 | 4 | 3570.934 | 4252.3997 | 72.7983 | 86.6909 | 158.3577 | 0 | 296.8797 | 9346276.9665 | 825348.1767 | 9677178.555 | 9475084.7963 | 0 | 382192.9654 | 0 | 11585371.7694 | 30142760.8574 | 20573053.657 | 92007267.7437 | 961560.8286 | 12720605.2746 | 12720605.2746 | 1478867.319 | 5969963.1797 | 0 | 105689433.847 | 125858869.6203 | 10000000 | 29.5971 | 3570.934 | 4252.3997 | 72.7983 | 86.6909
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0 | 0 | 0 | 0 |  |  |  |  | 15 |  | 25.8421 | [19 empty] | 100 | 0
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.83292 | 0.1631 | 0.0046397 | 4 | 811753.0004 | 1930884.1952 | 16548.6829 | 39363.686 | 110.9215 | 0 | 48.8216 | 108028.423 | 7137.2035 | 80520.7947 | 54678.7091 | 0 | 57718.4043 | 0 | 120152.5785 | 312612.3625 | 213364.3609 | 954212.8363 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15065186.9026 | 35834953.8243 | 133.3521 | 0.018559 | 811753.0004 | 1930884.1952 | 16548.6829 | 39363.686
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.24341 | 0.010996 | 4 | 349133.2669 | 821340.738 | 7117.5539 | 16744.1419 | 120.4875 | 0 | 52.4107 | 150595.4761 | 10558.4985 | 110178.6588 | 66504.7419 | 0 | 64275.846 | 0 | 156824.1563 | 408024.2856 | 278484.959 | 1245446.622 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15356420.6883 | 36126187.6099 | 177.8279 | 0.043984 | 349133.2669 | 821340.738 | 7117.5539 | 16744.1419
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3982 | 0.36337 | 0.021228 | 4 | 185588.0536 | 430193.9065 | 3783.4635 | 8770.0847 | 129.4652 | 0 | 55.5434 | 208505.487 | 15489.5286 | 150869.6004 | 83818.9054 | 0 | 73246.7704 | 0 | 207452.8138 | 539749.6671 | 368390.2385 | 1647523.0113 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 15758497.0776 | 36528263.9992 | 237.1374 | 0.084911 | 185588.0536 | 430193.9065 | 3783.4635 | 8770.0847
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.5276 | 0.036323 | 4 | 111945.6835 | 254895.6513 | 2282.1642 | 5196.3926 | 137.0266 | 0 | 315.791 | 280585.3094 | 21944.2172 | 202256.3562 | 107179.8908 | 0 | 83507.6653 | 0 | 271234.6411 | 705696.8983 | 481652.6337 | 2154057.6119 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16265031.6782 | 37034798.5999 | 316.2278 | 0.14529 | 111945.6835 | 254895.6513 | 2282.1642 | 5196.3926
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.371 | 0.74272 | 0.05724 | 4 | 73710.6817 | 164424.0174 | 1502.6919 | 3352.006 | 143.1442 | 0 | 408.5636 | 366602.0183 | 29960.0629 | 264782.9216 | 137033.2284 | 0 | 94624.9778 | 0 | 348271.2515 | 906130.3562 | 618452.5872 | 2765857.404 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 16876831.4703 | 37646598.3919 | 421.6965 | 0.22896 | 73710.6817 | 164424.0174 | 1502.6919 | 3352.006
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.11 | 1.0425 | 0.087266 | 4 | 50641.8957 | 110142.9198 | 1032.4035 | 2245.4124 | 148.3138 | 0 | 543.444 | 476383.9871 | 40584.1455 | 346003.4812 | 179489.4893 | 0 | 109002.5516 | 0 | 449070.8253 | 1168390.1704 | 797450.2993 | 3566374.9496 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 17677349.0159 | 38447115.9376 | 562.3413 | 0.34907 | 50641.8957 | 110142.9198 | 1032.4035 | 2245.4124
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1043 | 1.4513 | 0.12918 | 4 | 36189.7216 | 76385.7278 | 737.7764 | 1557.2264 | 152.5212 | 0 | 76.7132 | 613322.5982 | 54287.0578 | 449367.7775 | 237572.9717 | 0 | 126986.8785 | 0 | 577799.5407 | 1503315.8819 | 1026043.9794 | 4588696.6858 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 18699670.7521 | 39469437.6737 | 749.8942 | 0.51671 | 36189.7216 | 76385.7278 | 737.7764 | 1557.2264
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4079 | 2.0114 | 0.18535 | 4 | 26947.0738 | 54961.0576 | 549.3525 | 1120.4555 | 155.7997 | 0 | 83.171 | 778919.7952 | 70324.0342 | 582517.9722 | 314070.6827 | 0 | 148677.6084 | 0 | 738858.9362 | 1922359.3911 | 1312049.7849 | 5867778.2048 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 19978752.2711 | 40748519.1928 | 1000 | 0.74141 | 26947.0738 | 54961.0576 | 549.3525 | 1120.4555
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.14 | 2.7773 | 0.25923 | 4 | 20805.587 | 40835.8282 | 424.15 | 832.4936 | 158.2948 | 0 | 72.6884 | 977952.2129 | 88465.4977 | 753934.4484 | 413396.5977 | 0 | 175729.3646 | 0 | 939696.4673 | 2444897.4497 | 1668692.747 | 7462764.7853 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 21573738.8516 | 42343505.7733 | 1333.5214 | 1.0369 | 20805.587 | 40835.8282 | 424.15 | 832.4936
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4615 | 3.8162 | 0.35891 | 4 | 16429.9277 | 30897.3181 | 334.9463 | 629.8836 | 160.3969 | 0 | 91.5752 | 1222573.5457 | 110503.2985 | 972154.055 | 545182.8561 | 0 | 209155.8601 | 0 | 1193232.15 | 3104545.2887 | 2118915.9516 | 9476263.0056 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 23587237.0719 | 44357003.9935 | 1778.2794 | 1.4356 | 16429.9277 | 30897.3181 | 334.9463 | 629.8836
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.5379 | 5.1886 | 0.4906 | 4 | 13293.3872 | 23877.3476 | 271.0037 | 486.772 | 161.9499 | 0 | 84.2772 | 1517630.5526 | 137016.1464 | 1243008.0961 | 719411.0086 | 0 | 249495.6313 | 0 | 1507958.9597 | 3923399.8881 | 2677801.0415 | 11975721.3243 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 26086695.3906 | 46856462.3123 | 2371.3737 | 1.9624 | 13293.3872 | 23877.3476 | 271.0037 | 486.772
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.6259 | 7.0124 | 0.66559 | 4 | 10973.5663 | 18774.8604 | 223.711 | 382.7509 | 163.1333 | 0 | 80.1376 | 1876566.4771 | 169177.7534 | 1581710.8926 | 950766.283 | 0 | 298514.7772 | 0 | 1901927.1115 | 4948424.2052 | 3377401.2 | 15104488.7 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 29215462.7663 | 49985229.6879 | 3162.2777 | 2.6623 | 10973.5663 | 18774.8604 | 223.711 | 382.7509
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.058 | 9.4366 | 0.89809 | 4 | 9225.7418 | 15007.407 | 188.0792 | 305.9463 | 164.0361 | 0 | 77.9066 | 2314091.6219 | 208260.664 | 2005792.2887 | 1258123.4932 | 0 | 358247.26 | 0 | 2396360.9779 | 6234839.7032 | 4255406.2106 | 19031122.2195 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 33142096.2858 | 53911863.2075 | 4216.965 | 3.5924 | 9225.7418 | 15007.407 | 188.0792 | 305.9463
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.24 | 12.6418 | 1.2055 | 4 | 7891.82 | 12199.2494 | 160.8854 | 248.6982 | 164.721 | 0 | 80.2611 | 2845417.0244 | 255565.4906 | 2534429.4045 | 1664173.7482 | 0 | 430545.5314 | 0 | 3014751.1676 | 7843764.1276 | 5353530.1903 | 23942176.6844 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 38053150.7507 | 58822917.6724 | 5623.4133 | 4.8218 | 7891.82 | 12199.2494 | 160.8854 | 248.6982
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.6721 | 16.852 | 1.6092 | 4 | 6861.9958 | 10088.7118 | 139.8911 | 205.672 | 165.2378 | 0 | 96.1749 | 3487512.8049 | 312531.125 | 3189743.0646 | 2197525.0497 | 0 | 517546.929 | 0 | 3784894.9996 | 9847520.4002 | 6721135.0194 | 30058409.3924 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 44169383.4588 | 64939150.3804 | 7498.9421 | 6.4368 | 6861.9958 | 10088.7118 | 139.8911 | 205.672
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.928 | 22.3178 | 2.1331 | 4 | 6061.0659 | 8495.2391 | 123.563 | 173.1869 | 165.6091 | 0 | 111.0772 | 4255864.2133 | 380445.612 | 3993511.1975 | 2890388.1285 | 0 | 621363.265 | 0 | 4735213.2424 | 12320053.5308 | 8408689.6866 | 37605528.876 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 51716502.9423 | 72486269.8639 | 10000 | 8.5326 | 6061.0659 | 8495.2391 | 123.563 | 173.1869
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.5527 | 29.2437 | 2.7961 | 4 | 5440.0426 | 7297.0603 | 110.9026 | 148.7604 | 165.788 | 0 | 104.4392 | 5155761.766 | 459683.5107 | 4957460.9515 | 3772368.556 | 0 | 743267.6602 | 0 | 5884531.5534 | 15310344.0184 | 10449624.3887 | 46733042.405 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 60844016.4713 | 81613783.393 | 13335.2143 | 11.1845 | 5440.0426 | 7297.0603 | 110.9026 | 148.7604
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.8948 | 37.6597 | 3.5983 | 4 | 4968.0261 | 6411.0437 | 101.2799 | 130.6978 | 165.6419 | 0 | 107.4517 | 6170827.9973 | 548719.7183 | 6069256.1023 | 4858990.608 | 0 | 883220.0733 | 0 | 7227095.6547 | 18803420.4124 | 12833720.8031 | 57395251.3695 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 71506225.4358 | 92275992.3575 | 17782.7941 | 14.3933 | 4968.0261 | 6411.0437 | 101.2799 | 130.6978
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 104.7233 | 45.5854 | 4.3908 | 4 | 4621.1018 | 5803.6703 | 94.2074 | 118.3157 | 165.1662 | 0 | 125.0137 | 7068731.2847 | 627212.1478 | 7071217.5702 | 5908136.0919 | 0 | 973133.2997 | 0 | 8442887.8538 | 21966662.3211 | 14992698.4039 | 67050678.9731 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 81161653.0394 | 101931419.961 | 23713.7371 | 17.5633 | 4621.1018 | 5803.6703 | 94.2074 | 118.3157
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.7855 | 50.485 | 4.9807 | 4 | 4355.4236 | 5397.943 | 88.7912 | 110.0444 | 164.7124 | 0 | 144.6644 | 7601464.5885 | 673674.916 | 7672975.6137 | 6574456.5786 | 0 | 937141.6491 | 0 | 9149288.2049 | 23804571.132 | 16247108.9326 | 72660681.6153 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 86771655.6816 | 107541422.6033 | 31622.7766 | 19.9227 | 4355.4236 | 5397.943 | 88.7912 | 110.0444
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 127.5151 | 54.7119 | 5.5141 | 4 | 4148.9973 | 5090.6596 | 84.5829 | 103.78 | 164.2256 | 0 | 200.7124 | 8049340.8613 | 712678.9706 | 8182750.7634 | 7163018.5376 | 0 | 882530.7371 | 0 | 9746224.7493 | 25357677.5722 | 17307135.9912 | 77401358.1828 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 91512332.2491 | 112282099.1707 | 42169.6503 | 22.0565 | 4148.9973 | 5090.6596 | 84.5829 | 103.78
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.1493 | 59.176 | 6.0527 | 4 | 3988.4378 | 4846.31 | 81.3097 | 98.7986 | 163.6562 | 0 | 235.4278 | 8511824.0938 | 752902.2759 | 8712652.0449 | 7796600.7045 | 0 | 847113.3374 | 0 | 10382226.0581 | 27012422.5157 | 18436533.4167 | 82452274.447 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 96563248.5133 | 117333015.435 | 56234.1325 | 24.2108 | 3988.4378 | 4846.31 | 81.3097 | 98.7986
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.4903 | 62.3254 | 6.4709 | 4 | 3863.0589 | 4665.4881 | 78.7537 | 95.1123 | 163.2524 | 0 | 248.6602 | 8832152.4005 | 780731.7734 | 9081665.5963 | 8248841.5538 | 0 | 784060.68 | 0 | 10813706.2816 | 28135045.5486 | 19202746.7043 | 85878950.5385 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 99989924.6048 | 120759691.5264 | 74989.4209 | 25.8836 | 3863.0589 | 4665.4881 | 78.7537 | 95.1123
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.287 | 64.8406 | 6.8152 | 4 | 3766.8173 | 4528.7096 | 76.7917 | 92.3239 | 162.9067 | 0 | 271.4222 | 9084703.1182 | 802655.9839 | 9373705.9892 | 8615586.0857 | 0 | 721380.5079 | 0 | 11153232.3572 | 29018422.7508 | 19805669.7964 | 88575356.5894 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 102686330.6557 | 123456097.5774 | 100000 | 27.2608 | 3766.8173 | 4528.7096 | 76.7917 | 92.3239
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.6 | 66.7729 | 7.0887 | 4 | 3693.2391 | 4425.7312 | 75.2917 | 90.2245 | 162.6264 | 0 | 250.5882 | 9276840.8621 | 819325.9198 | 9596522.6997 | 8900685.1281 | 0 | 661763.1662 | 0 | 11409503.7326 | 29685188.3012 | 20260750.9852 | 90610580.795 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 104721554.8613 | 125491321.7829 | 133352.1432 | 28.3549 | 3693.2391 | 4425.7312 | 75.2917 | 90.2245
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.7165 | 68.2501 | 7.3033 | 4 | 3637.1853 | 4348.1554 | 74.1489 | 88.643 | 162.4035 | 0 | 270.4337 | 9422663.0162 | 831971.9679 | 9765987.8565 | 9120980.8368 | 0 | 608342.976 | 0 | 11602479.1948 | 30187270.8692 | 20603432.6546 | 92143129.3719 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 106254103.4382 | 127023870.3598 | 177827.941 | 29.2133 | 3637.1853 | 4348.1554 | 74.1489 | 88.643
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.8519 | 69.3633 | 7.4689 | 4 | 3594.5952 | 4289.7994 | 73.2807 | 87.4534 | 162.2305 | 0 | 233.2451 | 9531968.8732 | 841448.1445 | 9893216.4204 | 9288424.4057 | 0 | 562064.3612 | 0 | 11745677.6599 | 30559843.9014 | 20857721.4047 | 93280365.171 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 107391339.2373 | 128161106.1589 | 237137.3706 | 29.8758 | 3594.5952 | 4289.7994 | 73.2807 | 87.4534
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.1876 | 70.1859 | 7.5946 | 4 | 3562.3057 | 4246.0109 | 72.6224 | 86.5607 | 162.0997 | 0 | 291.7119 | 9612415.8272 | 848420.748 | 9986962.5695 | 9412967.8764 | 0 | 522807.8201 | 0 | 11849594.188 | 30830213.3912 | 21042254.137 | 94105636.5573 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 108216610.6236 | 128986377.5453 | 316227.766 | 30.3782 | 3562.3057 | 4246.0109 | 72.6224 | 86.5607
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 171.0124 | 70.8245 | 7.6921 | 4 | 3537.8715 | 4212.907 | 72.1243 | 85.8858 | 161.9966 | 0 | 272.9794 | 9674690.0366 | 853817.2908 | 10059594.3401 | 9510146.8409 | 0 | 491332.3249 | 0 | 11929936.525 | 31039247.6716 | 21184924.3286 | 94743689.3586 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 108854663.4249 | 129624430.3465 | 421696.5034 | 30.7684 | 3537.8715 | 4212.907 | 72.1243 | 85.8858
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.3157 | 71.2779 | 7.7638 | 4 | 3519.4036 | 4188.204 | 71.7478 | 85.3822 | 161.9223 | 0 | 282.2398 | 9718804.7284 | 857639.6618 | 10111079.1348 | 9579273.3233 | 0 | 465270.3255 | 0 | 11985506.1978 | 31183828.5612 | 21283603.7566 | 95185005.6893 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 109295979.7556 | 130065746.6772 | 562341.3252 | 31.0553 | 3519.4036 | 4188.204 | 71.7478 | 85.3822
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2755 | 71.6106 | 7.8174 | 4 | 3505.4696 | 4169.6853 | 71.4637 | 85.0047 | 161.8673 | 0 | 282.7654 | 9751123.5191 | 860439.6959 | 10148814.5455 | 9630141.21 | 0 | 444441.3812 | 0 | 12025634.5371 | 31288234.2688 | 21354862.7974 | 95503691.955 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 109614666.0213 | 130384432.943 | 749894.2093 | 31.2696 | 3505.4696 | 4169.6853 | 71.4637 | 85.0047
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.9944 | 71.8591 | 7.8578 | 4 | 3494.9687 | 4155.773 | 71.2497 | 84.7211 | 161.8259 | 0 | 268.6545 | 9775236.8392 | 862528.6781 | 10176978.7071 | 9668218.7016 | 0 | 428140.2873 | 0 | 12055330.2531 | 31365496.4304 | 21407595.8103 | 95739525.7071 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 109850499.7734 | 130620266.695 | 1000000 | 31.431 | 3494.9687 | 4155.773 | 71.2497 | 84.7211
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.513 | 72.038 | 7.8875 | 4 | 3487.0629 | 4145.3751 | 71.0885 | 84.5091 | 161.796 | 0 | 264.5483 | 9792583.1683 | 864031.3459 | 10197244.064 | 9695679.4152 | 0 | 415294.3566 | 0 | 12076284.6165 | 31420015.3855 | 21444806.1174 | 95905938.4693 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110016912.5356 | 130786679.4573 | 1333521.4322 | 31.55 | 3487.0629 | 4145.3751 | 71.0885 | 84.5091
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2977 | 72.3087 | 7.9234 | 4 | 3480.3856 | 4135.7157 | 70.9524 | 84.3122 | 161.751 | 0 | 263.9678 | 9818808.0295 | 866303.0154 | 10227889.9305 | 9737236.0212 | 0 | 407905.1907 | 0 | 12112675.4531 | 31514696.8775 | 21509428.1812 | 96194942.6992 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110305916.7655 | 131075683.6871 | 1778279.41 | 31.6936 | 3480.3856 | 4135.7157 | 70.9524 | 84.3122
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5756 | 72.4041 | 7.9397 | 4 | 3475.9813 | 4129.968 | 70.8626 | 84.195 | 161.7348 | 0 | 256.1372 | 9828048.6895 | 867103.4317 | 10238690.6507 | 9751935.5516 | 0 | 400360.0667 | 0 | 12123593.9722 | 31543104.6246 | 21528817.0522 | 96281654.0392 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110392628.1055 | 131162395.0272 | 2371373.7057 | 31.7587 | 3475.9813 | 4129.968 | 70.8626 | 84.195
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.7776 | 72.4735 | 7.9517 | 4 | 3472.6724 | 4125.6698 | 70.7951 | 84.1074 | 161.7231 | 0 | 259.4901 | 9834761.4 | 867684.8681 | 10246537.3773 | 9762624.7094 | 0 | 394555.3237 | 0 | 12131403.8346 | 31563424.2846 | 21542685.6377 | 96343677.4354 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110454651.5017 | 131224418.4233 | 3162277.6602 | 31.8068 | 3472.6724 | 4125.6698 | 70.7951 | 84.1074
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.946 | 72.5313 | 7.9613 | 4 | 3470.1877 | 4122.4015 | 70.7445 | 84.0407 | 161.7133 | 0 | 266.5368 | 9840352.0703 | 868169.1092 | 10253072.9852 | 9771531.2839 | 0 | 390335.4263 | 0 | 12138149.7413 | 31580975.7499 | 21554664.8735 | 96397251.2396 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110508225.3059 | 131277992.2276 | 4216965.0343 | 31.845 | 3470.1877 | 4122.4015 | 70.7445 | 84.0407
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0601 | 72.5704 | 7.9681 | 4 | 3468.3223 | 4119.9801 | 70.7064 | 83.9914 | 161.7066 | 0 | 268.0353 | 9844136.4942 | 868496.8968 | 10257497.2985 | 9777565.2036 | 0 | 387014.8663 | 0 | 12142537.1961 | 31592391.0075 | 21562456.0213 | 96432094.9843 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110543069.0507 | 131312835.9723 | 5623413.2519 | 31.8722 | 3468.3223 | 4119.9801 | 70.7064 | 83.9914
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.1519 | 72.6019 | 7.9733 | 4 | 3466.9224 | 4118.1478 | 70.6779 | 83.954 | 161.7013 | 0 | 305.0167 | 9847180.2645 | 868760.5305 | 10261055.8679 | 9782419.3108 | 0 | 384576.0261 | 0 | 12146156.8799 | 31601808.6822 | 21568883.7779 | 96460841.3398 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110571815.4061 | 131341582.3278 | 7498942.0933 | 31.8934 | 3466.9224 | 4118.1478 | 70.6779 | 83.954
1 | 3900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.2056 | 72.6203 | 7.9768 | 4 | 3465.8719 | 4116.8114 | 70.6565 | 83.9268 | 161.6981 | 0 | 303.8375 | 9848959.3953 | 868914.6276 | 10263135.9658 | 9785259.4164 | 0 | 382577.2831 | 0 | 12148050.2084 | 31606734.7346 | 21572245.9098 | 96475877.541 | 961560.8286 | 13149413.2377 | 13149413.2377 | 1478867.319 | 6141486.3649 | 0 | 110586851.6073 | 131356618.5289 | 10000000 | 31.9074 | 3465.8719 | 4116.8114 | 70.6565 | 83.9268
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.66714 | 0.11359 | 0.0013735 | 4 | 2785517.6147 | 6676698.2772 | 56786.5443 | 136113.5253 | 102.6797 | 0 | 53.8466 | 79821.7194 | 5012.2545 | 60645.0888 | 46976.9501 | 0 | 52310.2113 | 0 | 95458.8274 | 248364.2875 | 169513.7296 | 758103.0685 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15303745.1888 | 36682047.3859 | 100 | 0.005494 | 2785517.6147 | 6676698.2772 | 56786.5443 | 136113.5253
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85236 | 0.17341 | 0.0057301 | 4 | 677890.6831 | 1610606.3458 | 13819.7185 | 32834.3889 | 113.284 | 0 | 52.5107 | 114308.7909 | 7659.5482 | 84427.1143 | 55980.015 | 0 | 57890.8754 | 0 | 124903.8741 | 324974.2591 | 221801.6094 | 991946.0865 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15537588.2067 | 36915890.4039 | 133.3521 | 0.02292 | 677890.6831 | 1610606.3458 | 13819.7185 | 32834.3889
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.2641 | 0.013088 | 4 | 303019.0459 | 711386.169 | 6177.4531 | 14502.5693 | 123.5629 | 0 | 61.9001 | 161998.995 | 11574.2299 | 117359.5531 | 69054.3287 | 0 | 65426.929 | 0 | 165911.4739 | 431667.6221 | 294622.022 | 1317615.1537 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 15863257.274 | 37241559.4711 | 177.8279 | 0.052351 | 303019.0459 | 711386.169 | 6177.4531 | 14502.5693
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4371 | 0.38955 | 0.024404 | 4 | 166743.5097 | 385749.0204 | 3399.292 | 7864.0155 | 132.4444 | 0 | 62.1755 | 222144.0609 | 16825.686 | 159179.1004 | 86974.0258 | 0 | 73787.1025 | 0 | 217974.8905 | 567125.9522 | 387075.1156 | 1731085.9338 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16276728.0541 | 37655030.2512 | 237.1374 | 0.097615 | 166743.5097 | 385749.0204 | 3399.292 | 7864.0155
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 0.56045 | 0.040865 | 4 | 102748.6178 | 233536.2385 | 2094.6696 | 4760.9521 | 140.0094 | 0 | 312.5403 | 296764.7004 | 23681.4338 | 211847.236 | 110572.5493 | 0 | 83408.6788 | 0 | 283247.0933 | 736950.8349 | 502984.0877 | 2249456.6142 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 16795098.7345 | 38173400.9316 | 316.2278 | 0.16346 | 102748.6178 | 233536.2385 | 2094.6696 | 4760.9521
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 0.80195 | 0.065107 | 4 | 67118.3702 | 149208.106 | 1368.2988 | 3041.8091 | 146.5351 | 0 | 411.4307 | 393178.801 | 32985.4718 | 280864.9105 | 144270.4411 | 0 | 95903.1215 | 0 | 369409.0709 | 961126.6263 | 655988.6716 | 2933727.1147 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 17479369.235 | 38857671.4321 | 421.6965 | 0.26043 | 67118.3702 | 149208.106 | 1368.2988 | 3041.8091
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2073 | 1.1236 | 0.098852 | 4 | 46361.401 | 100427.569 | 945.1399 | 2047.3518 | 151.7709 | 0 | 547.9772 | 510942.9656 | 44904.4061 | 366387.2686 | 189903.3357 | 0 | 110273.4877 | 0 | 476740.4708 | 1240380.9121 | 846585.4598 | 3786118.3063 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 18331760.4266 | 39710062.6237 | 562.3413 | 0.39541 | 46361.401 | 100427.569 | 945.1399 | 2047.3518
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1969 | 1.5666 | 0.1444 | 4 | 33583.2712 | 70594.6566 | 684.6404 | 1439.1676 | 155.9396 | 0 | 74.746 | 653615.8054 | 58976.3762 | 476974.6522 | 249631.1803 | 0 | 127523.0874 | 0 | 611021.2296 | 1589751.9017 | 1085038.339 | 4852532.5718 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 19398174.692 | 40776476.8892 | 749.8942 | 0.57761 | 33583.2712 | 70594.6566 | 684.6404 | 1439.1676
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5394 | 2.1936 | 0.2055 | 4 | 25254.1501 | 51262.1872 | 514.84 | 1045.049 | 159.3188 | 0 | 89.2939 | 828750.1622 | 74996.4544 | 624241.7267 | 327633.4817 | 0 | 150340.4283 | 0 | 782325.2788 | 2035449.8985 | 1389236.3801 | 6212973.8108 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 20758615.931 | 42136918.1282 | 1000 | 0.82199 | 25254.1501 | 51262.1872 | 514.84 | 1045.049
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3226 | 3.0262 | 0.286 | 4 | 19614.3816 | 38301.9296 | 399.8657 | 780.8366 | 161.8665 | 0 | 87.089 | 1038703.6175 | 93943.659 | 807522.7812 | 430028.6104 | 0 | 178170.3694 | 0 | 993863.9246 | 2585830.0624 | 1764882.1511 | 7892945.1756 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 22438587.2958 | 43816889.493 | 1333.5214 | 1.144 | 19614.3816 | 38301.9296 | 399.8657 | 780.8366
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.681 | 4.1411 | 0.3942 | 4 | 15563.2323 | 29121.355 | 317.2775 | 593.6782 | 164.0282 | 0 | 74.8023 | 1294897.4377 | 117008.7689 | 1037832.5427 | 565670.4994 | 0 | 211415.6971 | 0 | 1258461.7289 | 3274259.2726 | 2234749.2328 | 9994295.1802 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 24539937.3005 | 45918239.4976 | 1778.2794 | 1.5768 | 15563.2323 | 29121.355 | 317.2775 | 593.6782
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.8326 | 5.624 | 0.53781 | 4 | 12629.6377 | 22567.3364 | 257.4722 | 460.0657 | 165.6152 | 0 | 100.8512 | 1606272.1777 | 144967.5784 | 1325784.5979 | 746333.2526 | 0 | 252397.5725 | 0 | 1589544.5199 | 4135668.7803 | 2822678.922 | 12623647.4013 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 27169289.5216 | 48547591.7187 | 2371.3737 | 2.1512 | 12629.6377 | 22567.3364 | 257.4722 | 460.0657
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.0131 | 7.5921 | 0.72847 | 4 | 10452.1156 | 17788.8267 | 213.0805 | 362.6493 | 166.827 | 0 | 93.1513 | 1984715.0769 | 178850.1094 | 1685475.6569 | 985956.8573 | 0 | 301997.7523 | 0 | 2003428.2266 | 5212509.2859 | 3557644.694 | 15910577.6592 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 30456219.7795 | 51834521.9766 | 3162.2777 | 2.9139 | 10452.1156 | 17788.8267 | 213.0805 | 362.6493
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.5574 | 10.2026 | 0.98138 | 4 | 8807.1728 | 14253.1731 | 179.5461 | 290.5702 | 167.7503 | 0 | 92.7996 | 2445276.6874 | 219955.5094 | 2135026.2041 | 1303596.9305 | 0 | 362183.0558 | 0 | 2521754.971 | 6561089.1515 | 4478078.1628 | 20026960.6725 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 34572602.7927 | 55950904.9899 | 4216.965 | 3.9255 | 8807.1728 | 14253.1731 | 179.5461 | 290.5702
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.8831 | 13.6527 | 1.3156 | 4 | 7547.7549 | 11610.1859 | 153.8712 | 236.6893 | 168.4512 | 0 | 102.8515 | 3004580.8385 | 269705.6898 | 2695313.1222 | 1723238.2143 | 0 | 434998.3861 | 0 | 3169856.1378 | 8247315.4438 | 5628962.2558 | 25173970.0883 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 39719612.2085 | 61097914.4057 | 5623.4133 | 5.2624 | 7547.7549 | 11610.1859 | 153.8712 | 236.6893
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.4958 | 18.1807 | 1.7543 | 4 | 6573.0925 | 9619.6992 | 134.0014 | 196.1106 | 168.9799 | 0 | 91.6252 | 3680140.0444 | 329581.8476 | 3389389.0818 | 2273936.2401 | 0 | 522539.1199 | 0 | 3976278.6702 | 10345461.4529 | 7060990.0196 | 31578316.4765 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 46123958.5967 | 67502260.7938 | 7498.9421 | 7.0171 | 6573.0925 | 9619.6992 | 134.0014 | 196.1106
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.9654 | 24.0475 | 2.3225 | 4 | 5813.832 | 8115.0239 | 118.5228 | 165.4357 | 169.3561 | 0 | 91.9736 | 4487295.097 | 400853.1858 | 4239254.4972 | 2987918.8191 | 0 | 626753.2206 | 0 | 4969409.1797 | 12929383.3196 | 8824569.7879 | 39465437.1071 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 54011079.2273 | 75389381.4245 | 10000 | 9.2901 | 5813.832 | 8115.0239 | 118.5228 | 165.4357
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.8562 | 31.4749 | 3.0407 | 4 | 5224.3743 | 6982.0472 | 106.5059 | 142.3385 | 169.5235 | 0 | 113.4149 | 5432163.3503 | 483961.972 | 5257808.9545 | 3896403.0477 | 0 | 749359.1242 | 0 | 6169681.615 | 16052245.9864 | 10955987.7264 | 48997611.7765 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 63543253.8967 | 84921556.0939 | 13335.2143 | 12.1628 | 5224.3743 | 6982.0472 | 106.5059 | 142.3385
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.4541 | 40.4598 | 3.9061 | 4 | 4776.5902 | 6144.8606 | 97.3773 | 125.2713 | 169.3377 | 0 | 123.8558 | 6493683.7047 | 576970.2243 | 6427661.3683 | 5011713.1288 | 0 | 889532.0168 | 0 | 7565828.5727 | 19684733.9815 | 13435235.4232 | 60085358.4203 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 74631000.5406 | 96009302.7377 | 17782.7941 | 15.6243 | 4776.5902 | 6144.8606 | 97.3773 | 125.2713
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.1675 | 49.6239 | 4.8079 | 4 | 4449.0556 | 5560.6753 | 90.7 | 113.3619 | 168.7423 | 0 | 119.8792 | 7508937.3338 | 665610.5405 | 7568093.0382 | 6180677.188 | 0 | 1005744.9858 | 0 | 8942334.6037 | 23266120.3137 | 15879605.1851 | 71017123.1889 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 85562765.3091 | 106941067.5062 | 23713.7371 | 19.2317 | 4449.0556 | 5560.6753 | 90.7 | 113.3619
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.213 | 54.7515 | 5.4308 | 4 | 4201.5682 | 5185.6985 | 85.6547 | 105.7175 | 168.2337 | 0 | 161.3975 | 8053485.0295 | 713039.6339 | 8187483.5287 | 6854382.2844 | 0 | 963618.5622 | 0 | 9661083.5251 | 25136157.5716 | 17155944.039 | 76725194.1744 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 91270836.2946 | 112649138.4918 | 31622.7766 | 21.723 | 4201.5682 | 5185.6985 | 85.6547 | 105.7175
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 130.9233 | 59.1701 | 5.9919 | 4 | 4009.3186 | 4901.2889 | 81.7354 | 99.9194 | 167.6966 | 0 | 230.3216 | 8511215.223 | 752849.3552 | 8711952.1587 | 7449002.5106 | 0 | 904021.6734 | 0 | 10268325.9591 | 26716077.8223 | 18234272.0743 | 81547716.7765 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 96093358.8968 | 117471661.0939 | 42169.6503 | 23.9675 | 4009.3186 | 4901.2889 | 81.7354 | 99.9194
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.7233 | 63.9381 | 6.5663 | 4 | 3858.7819 | 4672.7209 | 78.6665 | 95.2597 | 167.0916 | 0 | 229.1208 | 8994406.9299 | 794818.9577 | 9269180.7219 | 8101058.3987 | 0 | 867360.287 | 0 | 10930461.8651 | 28438819.6269 | 19410078.7547 | 86806185.5418 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 101351827.6621 | 122730129.8592 | 56234.1325 | 26.2652 | 3858.7819 | 4672.7209 | 78.6665 | 95.2597
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.9982 | 67.2143 | 7.0033 | 4 | 3741.9015 | 4505.057 | 76.2837 | 91.8417 | 166.6576 | 0 | 224.8766 | 9320511.3296 | 823113.6252 | 9647241.4483 | 8555766.7586 | 0 | 800604.899 | 0 | 11367422.8437 | 29575702.4602 | 20186024.649 | 90276388.0137 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 104822030.1339 | 126200332.3311 | 74989.4209 | 28.013 | 3741.9015 | 4505.057 | 76.2837 | 91.8417
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.6413 | 69.7926 | 7.3591 | 4 | 3652.2092 | 4378.4626 | 74.4552 | 89.2609 | 166.2922 | 0 | 234.8768 | 9573984.4266 | 845089.9479 | 9942166.4173 | 8919228.0953 | 0 | 733969.8647 | 0 | 11705631.1132 | 30455651.0014 | 20786607.6095 | 92962328.476 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 107507970.5962 | 128886272.7934 | 100000 | 29.4364 | 3652.2092 | 4378.4626 | 74.4552 | 89.2609
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.9271 | 71.8106 | 7.6446 | 4 | 3583.6558 | 4282.789 | 73.0577 | 87.3104 | 165.9914 | 0 | 258.4053 | 9770537.9514 | 862121.6144 | 10171489.8115 | 9207547.6103 | 0 | 672405.9638 | 0 | 11966800.151 | 31135159.2648 | 21250385.9617 | 95036448.3289 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 109582090.4491 | 130960392.6463 | 133352.1432 | 30.5783 | 3583.6558 | 4282.789 | 73.0577 | 87.3104
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.9419 | 73.3212 | 7.8654 | 4 | 3531.4075 | 4210.9089 | 71.9925 | 85.8451 | 165.7571 | 0 | 257.9696 | 9916646.5596 | 874776.7603 | 10342305.7394 | 9425225.1429 | 0 | 616602.8834 | 0 | 12158467.2634 | 31633837.7748 | 21590744.2917 | 96558606.4155 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 111104248.5357 | 132482550.7328 | 177827.941 | 31.4617 | 3531.4075 | 4210.9089 | 71.9925 | 85.8451
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.9964 | 74.4585 | 8.0356 | 4 | 3491.7068 | 4156.8159 | 71.1832 | 84.7423 | 165.5755 | 0 | 307.5304 | 10026090.9728 | 884253.2754 | 10470448.9578 | 9590515.9465 | 0 | 568476.2217 | 0 | 12300516.2959 | 32003420.2191 | 21842991.9041 | 97686713.7933 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 112232355.9135 | 133610658.1107 | 237137.3706 | 32.1425 | 3491.7068 | 4156.8159 | 71.1832 | 84.7423
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.2887 | 75.3052 | 8.1652 | 4 | 3461.6053 | 4116.163 | 70.5695 | 83.9135 | 165.4374 | 0 | 272.2343 | 10107256.053 | 891279.5241 | 10565586.068 | 9714378.9559 | 0 | 527989.7934 | 0 | 12404531.2538 | 32274045.8031 | 22027699.426 | 98512766.8772 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 113058408.9974 | 134436711.1946 | 316227.766 | 32.6607 | 3461.6053 | 4116.163 | 70.5695 | 83.9135
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.9749 | 75.9242 | 8.2623 | 4 | 3438.8237 | 4085.6857 | 70.1051 | 83.2922 | 165.3348 | 0 | 269.4644 | 10166431.2875 | 896401.2999 | 10635003.7514 | 9805394.0325 | 0 | 494437.8852 | 0 | 12479090.6201 | 32468033.98 | 22160100.3427 | 99104893.1995 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 113650535.3197 | 135028837.5168 | 421696.5034 | 33.0492 | 3438.8237 | 4085.6857 | 70.1051 | 83.2922
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2318 | 76.3834 | 8.3355 | 4 | 3421.609 | 4062.7901 | 69.7541 | 82.8255 | 165.2578 | 0 | 266.4397 | 10210250.2585 | 900193.4797 | 10686437.3714 | 9873182.7035 | 0 | 467402.091 | 0 | 12533611.7026 | 32609886.6529 | 22256917.7067 | 99537881.9662 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 114083524.0865 | 135461826.2836 | 562341.3252 | 33.3421 | 3421.609 | 4062.7901 | 69.7541 | 82.8255
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.1667 | 76.7239 | 8.3905 | 4 | 3408.6187 | 4045.5972 | 69.4893 | 82.475 | 165.2002 | 0 | 300.6232 | 10242683.8048 | 903000.0858 | 10724523.5247 | 9923574.9047 | 0 | 445929.3485 | 0 | 12573487.5507 | 32713635.43 | 22327728.379 | 99854563.0282 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 114400205.1485 | 135778507.3456 | 749894.2093 | 33.562 | 3408.6187 | 4045.5972 | 69.4893 | 82.475
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.8318 | 76.9654 | 8.4308 | 4 | 3398.8276 | 4032.7642 | 69.2897 | 82.2134 | 165.159 | 0 | 303.5104 | 10265672.1905 | 904989.232 | 10751526.8438 | 9959409.6907 | 0 | 428751.0312 | 0 | 12601036.1054 | 32785311.1184 | 22376648.5091 | 100073344.7211 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 114618986.8413 | 135997289.0385 | 1000000 | 33.7231 | 3398.8276 | 4032.7642 | 69.2897 | 82.2134
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.3534 | 76.4257 | 8.3974 | 4 | 3390.8914 | 4027.3487 | 69.1279 | 82.103 | 165.2485 | 0 | 293.7579 | 10214280.7263 | 900542.2643 | 10691169.5192 | 9879672.1127 | 0 | 392046.5733 | 0 | 12510307.3664 | 32549253.5505 | 22215534.3685 | 99352806.4813 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 113898448.6015 | 135276750.7987 | 1333521.4322 | 33.5895 | 3390.8914 | 4027.3487 | 69.1279 | 82.103
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1159 | 77.431 | 8.4986 | 4 | 3385.2334 | 4014.1111 | 69.0126 | 81.8331 | 165.0797 | 0 | 298.148 | 10309920.9976 | 908817.6993 | 10803523.4117 | 10028578.7072 | 0 | 407997.8287 | 0 | 12658947.0714 | 32935983.5726 | 22479485.5551 | 100533254.8437 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115078896.9639 | 136457199.1611 | 1778279.41 | 33.9944 | 3385.2334 | 4014.1111 | 69.0126 | 81.8331
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.3787 | 77.5259 | 8.515 | 4 | 3381.1274 | 4008.7915 | 68.9289 | 81.7246 | 165.0633 | 0 | 290.8887 | 10318930.9663 | 909597.2047 | 10814114.1514 | 10042725.6256 | 0 | 400154.4164 | 0 | 12669353.7221 | 32963059.5432 | 22497965.4614 | 100615901.0911 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115161543.2114 | 136539845.4085 | 2371373.7057 | 34.0601 | 3381.1274 | 4008.7915 | 68.9289 | 81.7246
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.5808 | 77.5988 | 8.5275 | 4 | 3378.0425 | 4004.7863 | 68.866 | 81.643 | 165.0507 | 0 | 303.2822 | 10325851.038 | 910195.8895 | 10822249.0546 | 10053600.4532 | 0 | 394245.0083 | 0 | 12677395.163 | 32983981.7227 | 22512245.2788 | 100679763.608 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115225405.7283 | 136603707.9254 | 3162277.6602 | 34.1101 | 3378.0425 | 4004.7863 | 68.866 | 81.643
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.7271 | 77.6515 | 8.5367 | 4 | 3375.7257 | 4001.7929 | 68.8187 | 81.582 | 165.0415 | 0 | 290.0622 | 10330857.5225 | 910629.0155 | 10828134.8299 | 10061474.3894 | 0 | 389709.0235 | 0 | 12683113.8645 | 32998860.6111 | 22522400.4258 | 100725179.6822 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115270821.8025 | 136649123.9996 | 4216965.0343 | 34.147 | 3375.7257 | 4001.7929 | 68.8187 | 81.582
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8392 | 77.6919 | 8.5437 | 4 | 3373.9864 | 3999.5412 | 68.7833 | 81.5361 | 165.0345 | 0 | 289.3328 | 10334689.6555 | 910960.5414 | 10832640.2249 | 10067504.1194 | 0 | 386305.8064 | 0 | 12687519.1356 | 33010322.2228 | 22530223.2114 | 100760164.9175 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115305807.0377 | 136684109.2349 | 5623413.2519 | 34.1749 | 3373.9864 | 3999.5412 | 68.7833 | 81.5361
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.9272 | 77.7236 | 8.5491 | 4 | 3372.681 | 3997.8424 | 68.7567 | 81.5014 | 165.029 | 0 | 281.3255 | 10337697.4893 | 911220.7533 | 10836176.636 | 10072238.1228 | 0 | 383781.6139 | 0 | 12691034.7 | 33019469.0002 | 22536466.0749 | 100788084.3905 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115333726.5107 | 136712028.7079 | 7498942.0933 | 34.1965 | 3372.681 | 3997.8424 | 68.7567 | 81.5014
1 | 4000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.9855 | 77.7446 | 8.5529 | 4 | 3371.7015 | 3996.5863 | 68.7367 | 81.4758 | 165.0253 | 0 | 274.6234 | 10339690.5741 | 911393.1769 | 10838520.0383 | 10075377.0854 | 0 | 381795.8519 | 0 | 12693242.9234 | 33025214.3444 | 22540387.3904 | 100805621.3848 | 961560.8286 | 13584081.2916 | 13584081.2916 | 1478867.319 | 6315353.5865 | 0 | 115351263.505 | 136729565.7022 | 10000000 | 34.2116 | 3371.7015 | 3996.5863 | 68.7367 | 81.4758
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.68659 | 0.12185 | 0.0020703 | 4 | 1905200.5149 | 4561170.9403 | 38840.0895 | 92985.6391 | 105.0594 | 0 | 56.3219 | 85118.0826 | 5421.337 | 64037.421 | 48107.7541 | 0 | 52856.9674 | 0 | 99661.2092 | 259298.023 | 176976.2288 | 791477.023 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 15777647.2881 | 37772688.8879 | 100 | 0.0082814 | 1905200.5149 | 4561170.9403 | 38840.0895 | 92985.6391
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.18846 | 0.0070954 | 4 | 564971.461 | 1339942.5173 | 11517.7074 | 27316.5406 | 116.2366 | 0 | 55.6273 | 123183.2462 | 8403.5616 | 90050.7908 | 57954.6463 | 0 | 59002.3967 | 0 | 132051.9102 | 343571.9828 | 234494.9379 | 1048713.4725 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16034883.7375 | 38029925.3374 | 133.3521 | 0.028382 | 564971.461 | 1339942.5173 | 11517.7074 | 27316.5406
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.28436 | 0.015331 | 4 | 266998.4068 | 625663.9957 | 5443.1237 | 12755.0068 | 126.4814 | 0 | 46.9609 | 173214.3926 | 12608.9926 | 124252.7566 | 71697.1193 | 0 | 66176.3358 | 0 | 174700.3428 | 454534.456 | 310229.106 | 1387413.5018 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16373583.7668 | 38368625.3667 | 177.8279 | 0.061325 | 266998.4068 | 625663.9957 | 5443.1237 | 12755.0068
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.476 | 0.41706 | 0.027855 | 4 | 150818.1735 | 348223.48 | 3074.6325 | 7099.0066 | 135.4233 | 0 | 69.9414 | 236408.3242 | 18266.9694 | 167765.252 | 90309.8616 | 0 | 74253.3102 | 0 | 228931.4498 | 595632.672 | 406531.5377 | 1818099.3769 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 16804269.6419 | 38799311.2418 | 237.1374 | 0.11142 | 150818.1735 | 348223.48 | 3074.6325 | 7099.0066
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9237 | 0.60354 | 0.046473 | 4 | 93410.8046 | 211732.2789 | 1904.3056 | 4316.4489 | 143.2656 | 0 | 323.2242 | 317463.8125 | 25947.2976 | 224265.5122 | 115802.0231 | 0 | 84353.7392 | 0 | 299454.63 | 779119.5206 | 531765.0821 | 2378171.6172 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 17364341.8822 | 39359383.4821 | 316.2278 | 0.18589 | 93410.8046 | 211732.2789 | 1904.3056 | 4316.4489
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 0.85628 | 0.073132 | 4 | 61785.2186 | 136974.5728 | 1259.5753 | 2792.4119 | 149.752 | 0 | 423.2666 | 418296.7051 | 36068.197 | 295272.4448 | 151223.5403 | 0 | 96079.5724 | 0 | 388806.7792 | 1011595.4844 | 690434.7043 | 3087777.4275 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 18073947.6926 | 40068989.2924 | 421.6965 | 0.29253 | 61785.2186 | 136974.5728 | 1259.5753 | 2792.4119
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2851 | 1.2005 | 0.11047 | 4 | 42935.1551 | 92709.2495 | 875.2912 | 1890.0035 | 155.1195 | 0 | 565.4777 | 543708.3069 | 49245.6172 | 385387.2994 | 198332.8852 | 0 | 110518.5309 | 0 | 502005.1294 | 1306114.3714 | 891449.8964 | 3986762.0367 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 18972932.3018 | 40967973.9016 | 562.3413 | 0.4419 | 42935.1551 | 92709.2495 | 875.2912 | 1890.0035
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3166 | 1.713 | 0.16047 | 4 | 31369.65 | 65636.9396 | 639.5127 | 1338.0978 | 159.4428 | 0 | 72.1306 | 696906.0603 | 63075.9938 | 512196.5467 | 260762.1222 | 0 | 129490.8518 | 0 | 648348.3142 | 1686869.3189 | 1151322.9719 | 5148972.1798 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 20135142.4448 | 42130184.0447 | 749.8942 | 0.64187 | 31369.65 | 65636.9396 | 639.5127 | 1338.0978
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6831 | 2.3865 | 0.22629 | 4 | 23808.7113 | 48108.8345 | 485.3728 | 980.7637 | 162.8565 | 0 | 94.766 | 879213.0708 | 79554.3623 | 667784.7988 | 340472.1412 | 0 | 152296.5165 | 0 | 826535.1469 | 2150474.9067 | 1467743.3116 | 6564074.2548 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 21550244.5198 | 43545286.1197 | 1000 | 0.90514 | 23808.7113 | 48108.8345 | 485.3728 | 980.7637
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4884 | 3.2719 | 0.31281 | 4 | 18613.0977 | 36191.4518 | 379.4532 | 737.8117 | 165.4125 | 0 | 78.4559 | 1097234.8615 | 99218.3845 | 859545.1683 | 445219.2799 | 0 | 179738.6197 | 0 | 1045572.9624 | 2720366.3717 | 1856705.9466 | 8303601.5947 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 23289771.8597 | 45284813.4596 | 1333.5214 | 1.2513 | 18613.0977 | 36191.4518 | 379.4532 | 737.8117
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.9025 | 4.4724 | 0.43034 | 4 | 14811.2035 | 27588.8177 | 301.9464 | 562.4354 | 167.6504 | 0 | 98.2841 | 1366948.3534 | 123485.2921 | 1103739.312 | 585577.6235 | 0 | 213396.5673 | 0 | 1323327.3878 | 3443026.4113 | 2349936.2729 | 10509437.2203 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 25495607.4853 | 47490649.0852 | 1778.2794 | 1.7214 | 14811.2035 | 27588.8177 | 301.9464 | 562.4354
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1226 | 6.0656 | 0.58602 | 4 | 12051.7488 | 21435.0531 | 245.6912 | 436.9825 | 169.2731 | 0 | 97.2592 | 1694134.2635 | 152843.2032 | 1408414.1963 | 772320.6727 | 0 | 254749.1988 | 0 | 1670159.9985 | 4345413.7192 | 2965834.1526 | 13263869.4049 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 28250039.6699 | 50245081.2698 | 2371.3737 | 2.3441 | 12051.7488 | 21435.0531 | 245.6912 | 436.9825
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.3958 | 8.1805 | 0.79273 | 4 | 9995.3838 | 16931.8933 | 203.7694 | 345.1795 | 170.5137 | 0 | 88.4111 | 2092072.144 | 188443.8855 | 1789192.8703 | 1019992.3881 | 0 | 304847.0193 | 0 | 2103873.8398 | 5473848.1673 | 3736013.8505 | 16708284.1647 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 31694454.4297 | 53689496.0296 | 3162.2777 | 3.1709 | 9995.3838 | 16931.8933 | 203.7694 | 345.1795
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0495 | 10.9794 | 1.0664 | 4 | 8439.0028 | 13595.3093 | 172.0405 | 277.1588 | 171.4575 | 0 | 108.0551 | 2575429.7631 | 231548.2764 | 2264105.1376 | 1347580.1648 | 0 | 365324.87 | 0 | 2645755.4027 | 6883712.8387 | 4698275.4585 | 21011731.9118 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 35997902.1769 | 57992943.7767 | 4216.965 | 4.2657 | 8439.0028 | 13595.3093 | 172.0405 | 277.1588
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.5279 | 14.6826 | 1.4284 | 4 | 7243.2685 | 11092.8215 | 147.6638 | 226.1422 | 172.1753 | 0 | 114.5166 | 3163278.1796 | 283791.379 | 2856779.7369 | 1780901.4507 | 0 | 438739.8466 | 0 | 3324161.3312 | 8648785.9045 | 5902974.0946 | 26399411.9229 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 41385582.188 | 63380623.7879 | 5623.4133 | 5.7137 | 7243.2685 | 11092.8215 | 147.6638 | 226.1422
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.3453 | 19.5444 | 1.9036 | 4 | 6315.8865 | 9204.5193 | 128.7579 | 187.6466 | 172.7166 | 0 | 103.6145 | 3873710.8693 | 346699.2424 | 3591305.9694 | 2349682.0728 | 0 | 527154.2356 | 0 | 4168535.4319 | 10845674.1096 | 7402395.4361 | 33105157.3671 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 48091327.6322 | 70086369.2321 | 7498.9421 | 7.6143 | 6315.8865 | 9204.5193 | 128.7579 | 187.6466
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.0495 | 25.8279 | 2.5177 | 4 | 5593.1273 | 7777.129 | 114.0235 | 158.5473 | 173.0965 | 0 | 120.2033 | 4720591.0976 | 421404.016 | 4488536.1221 | 3085496.6368 | 0 | 631962.8096 | 0 | 5205716.366 | 13544206.1452 | 9244198.9997 | 41342112.1931 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 56328282.4581 | 78323324.058 | 10000 | 10.071 | 5593.1273 | 7777.129 | 114.0235 | 158.5473
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 69.1863 | 33.7518 | 3.2912 | 4 | 5032.0128 | 6702.765 | 102.5844 | 136.6449 | 173.2496 | 0 | 110.7871 | 5708534.4743 | 508211.8039 | 5559960.0439 | 4018453.5473 | 0 | 754676.2905 | 0 | 6454436.1024 | 16793118.7515 | 11461648.612 | 51259039.6257 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 66245209.8908 | 88240251.4907 | 13335.2143 | 13.1648 | 5032.0128 | 6702.765 | 102.5844 | 136.6449
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.04 | 43.3074 | 4.2201 | 4 | 4605.827 | 5908.806 | 93.896 | 120.459 | 173.0208 | 0 | 127.9537 | 6815556.6035 | 605103.9451 | 6787086.2684 | 5161377.4091 | 0 | 894911.4642 | 0 | 7902973.9192 | 20561917.0149 | 14033930.8678 | 62762857.4922 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 77749027.7572 | 99744069.3571 | 17782.7941 | 16.8806 | 4605.827 | 5908.806 | 93.896 | 120.459
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.5218 | 53.7226 | 5.234 | 4 | 4294.93 | 5345.5094 | 87.558 | 108.9754 | 172.2946 | 0 | 146.7779 | 7945415.5269 | 703633.0269 | 8064158.6398 | 6444237.1754 | 0 | 1035906.7231 | 0 | 9435406.9259 | 24548993.3531 | 16755192.3948 | 74932943.7658 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 89919114.0308 | 111914155.6307 | 23713.7371 | 20.9361 | 4294.93 | 5345.5094 | 87.558 | 108.9754
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.5823 | 59.0833 | 5.8898 | 4 | 4063.5654 | 4997.1793 | 82.8413 | 101.8743 | 171.729 | 0 | 184.3718 | 8502315.6388 | 752075.827 | 8701722.9132 | 7126201.8181 | 0 | 988363.5083 | 0 | 10167565.0851 | 26453918.697 | 18055343.0844 | 80747506.5718 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 95733676.8368 | 117728718.4367 | 31622.7766 | 23.559 | 4063.5654 | 4997.1793 | 82.8413 | 101.8743
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.1829 | 63.6481 | 6.4745 | 4 | 3883.9191 | 4733.2082 | 79.1789 | 96.4929 | 171.1463 | 0 | 212.6836 | 8965321.2983 | 792294.1466 | 9235537.6748 | 7721516.7857 | 0 | 922804.079 | 0 | 10778614.8539 | 28043744.8519 | 19140432.1027 | 85600265.7928 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 100586436.0579 | 122581477.6577 | 42169.6503 | 25.8982 | 3883.9191 | 4733.2082 | 79.1789 | 96.4929
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.2038 | 68.7452 | 7.0866 | 4 | 3742.1795 | 4518.1214 | 76.2894 | 92.108 | 170.5051 | 0 | 267.5709 | 9471334.8578 | 836191.8563 | 9822619.2811 | 8394064.175 | 0 | 885902.322 | 0 | 11469943.8719 | 29842441.1458 | 20368079.2829 | 91090576.7928 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 106076747.0578 | 128071788.6577 | 56234.1325 | 28.3462 | 3742.1795 | 4518.1214 | 76.2894 | 92.108
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.3692 | 72.1247 | 7.5399 | 4 | 3632.8772 | 4362.1645 | 74.0611 | 88.9286 | 170.0435 | 0 | 244.1752 | 9800990.7709 | 864759.6516 | 10207067.9908 | 8848793.8371 | 0 | 815149.833 | 0 | 11909337.2125 | 30985652.486 | 21148344.5132 | 94580096.2952 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 109566266.5602 | 131561308.1601 | 74989.4209 | 30.1596 | 3632.8772 | 4362.1645 | 74.0611 | 88.9286
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.9586 | 74.7964 | 7.9094 | 4 | 3548.9846 | 4244.203 | 72.3509 | 86.5238 | 169.6539 | 0 | 270.5582 | 10058514.9599 | 887060.301 | 10508443.8601 | 9213455.4233 | 0 | 745898.8084 | 0 | 12251215.6076 | 31875149.941 | 21755444.8036 | 97295183.7049 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 112281353.97 | 134276395.5698 | 100000 | 31.6376 | 3548.9846 | 4244.203 | 72.3509 | 86.5238
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.0749 | 76.8369 | 8.2011 | 4 | 3484.8707 | 4155.3639 | 71.0438 | 84.7127 | 169.3414 | 0 | 250.9073 | 10253447.8636 | 903931.4953 | 10737166.6599 | 9495682.7922 | 0 | 680920.7312 | 0 | 12507748.3214 | 32542595.4404 | 22210990.0715 | 99332483.3755 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 114318653.6405 | 136313695.2404 | 133352.1432 | 32.8043 | 3484.8707 | 4155.3639 | 71.0438 | 84.7127
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.0159 | 78.3883 | 8.4286 | 4 | 3436.0269 | 4088.422 | 70.0481 | 83.348 | 169.0948 | 0 | 310.1079 | 10400674.6687 | 916668.5713 | 10910248.3016 | 9712611.252 | 0 | 623180.2577 | 0 | 12699719.39 | 33042064.782 | 22551888.1603 | 100857055.3835 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 115843225.6485 | 137838267.2484 | 177827.941 | 33.7143 | 3436.0269 | 4088.422 | 70.0481 | 83.348
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0586 | 79.5732 | 8.6052 | 4 | 3398.9024 | 4037.9078 | 69.2912 | 82.3182 | 168.9011 | 0 | 276.3075 | 10512569.0024 | 926345.9519 | 11041982.4757 | 9879554.4686 | 0 | 574074.8277 | 0 | 12844465.4233 | 33418664.2692 | 22808925.0486 | 102006581.4674 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 116992751.7325 | 138987793.3323 | 237137.3706 | 34.4207 | 3398.9024 | 4037.9078 | 69.2912 | 82.3182
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.2855 | 80.4329 | 8.7375 | 4 | 3370.746 | 4000.0734 | 68.7172 | 81.5469 | 168.7575 | 0 | 249.7842 | 10593459.8227 | 933340.3568 | 11137317.0038 | 10001375.1637 | 0 | 532198.0369 | 0 | 12947099.2497 | 33685696.4326 | 22991179.9871 | 102821666.0534 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 117807836.3185 | 139802877.9183 | 316227.766 | 34.9501 | 3370.746 | 4000.0734 | 68.7172 | 81.5469
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.9218 | 81.0608 | 8.8366 | 4 | 3349.4339 | 3971.7015 | 68.2827 | 80.9685 | 168.6509 | 0 | 327.3455 | 10652385.1759 | 938434.6385 | 11206816.9476 | 10090798.8829 | 0 | 497564.8825 | 0 | 13020540.2057 | 33876774.7351 | 23121594.8548 | 103404910.3229 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 118391080.5879 | 140386122.1878 | 421696.5034 | 35.3466 | 3349.4339 | 3971.7015 | 68.2827 | 80.9685
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1398 | 81.5261 | 8.9113 | 4 | 3333.3275 | 3950.3846 | 67.9544 | 80.5339 | 168.571 | 0 | 311.2645 | 10695967.1218 | 942201.9863 | 11258248.5777 | 10157314.3779 | 0 | 469681.9165 | 0 | 13074131.4523 | 34016208.1658 | 23216761.0363 | 103830514.6346 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 118816684.8996 | 140811726.4995 | 562341.3252 | 35.6451 | 3333.3275 | 3950.3846 | 67.9544 | 80.5339
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.0218 | 81.8618 | 8.9665 | 4 | 3321.1718 | 3934.4288 | 67.7066 | 80.2087 | 168.5128 | 0 | 318.264 | 10727374.6115 | 944916.7039 | 11295327.9801 | 10205454.2078 | 0 | 447291.4095 | 0 | 13111942.316 | 34114584.2771 | 23283904.7537 | 104130796.2596 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119116966.5246 | 141112008.1245 | 749894.2093 | 35.8659 | 3321.1718 | 3934.4288 | 67.7066 | 80.2087
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.6823 | 82.1127 | 9.0081 | 4 | 3312.0088 | 3922.4361 | 67.5198 | 79.9642 | 168.4691 | 0 | 299.9482 | 10750812.5559 | 946942.4429 | 11323006.7766 | 10241489.7707 | 0 | 429794.7249 | 0 | 13139898.0457 | 34187319.3512 | 23333547.9363 | 104352811.6041 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119338981.8692 | 141334023.469 | 1000000 | 36.0322 | 3312.0088 | 3922.4361 | 67.5198 | 79.9642
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.1498 | 82.2898 | 9.0384 | 4 | 3305.1086 | 3913.4879 | 67.3791 | 79.7817 | 168.4381 | 0 | 280.537 | 10767356.6651 | 948372.2826 | 11342548.5645 | 10266988.1846 | 0 | 415939.6763 | 0 | 13159070.0955 | 34237201.092 | 23367593.2495 | 104505069.8101 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119491240.0751 | 141486281.675 | 1333521.4322 | 36.1535 | 3305.1086 | 3913.4879 | 67.3791 | 79.7817
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.9127 | 82.5791 | 9.0766 | 4 | 3299.2907 | 3905.1061 | 67.2605 | 79.6109 | 168.3879 | 0 | 307.4258 | 10794348.4562 | 950704.9559 | 11374438.5197 | 10308606.3494 | 0 | 408186.6476 | 0 | 13196151.1222 | 34333678.3172 | 23433440.938 | 104799555.3063 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119785725.5713 | 141780767.1712 | 1778279.41 | 36.3065 | 3299.2907 | 3905.1061 | 67.2605 | 79.6109
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.1755 | 82.6784 | 9.0936 | 4 | 3295.4485 | 3900.1308 | 67.1822 | 79.5094 | 168.3703 | 0 | 291.9976 | 10803601.3557 | 951504.5729 | 11385372.6496 | 10322933.4922 | 0 | 400223.136 | 0 | 13206817.7305 | 34361430.6439 | 23452382.4713 | 104884266.0521 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119870436.3171 | 141865477.917 | 2371373.7057 | 36.3745 | 3295.4485 | 3900.1308 | 67.1822 | 79.5094
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.3607 | 82.7483 | 9.106 | 4 | 3292.5616 | 3896.4228 | 67.1233 | 79.4338 | 168.3579 | 0 | 282.9048 | 10810113.5548 | 952067.3338 | 11393068.7483 | 10333028.0816 | 0 | 394033.4849 | 0 | 13214101.3693 | 34380381.1781 | 23465316.6003 | 104942110.3512 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119928280.6162 | 141923322.2161 | 3162277.6602 | 36.424 | 3292.5616 | 3896.4228 | 67.1233 | 79.4338
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.5117 | 82.8052 | 9.1157 | 4 | 3290.3934 | 3893.6123 | 67.0791 | 79.3766 | 168.3478 | 0 | 290.668 | 10815418.7069 | 952525.7799 | 11399338.7576 | 10341255.0454 | 0 | 389479.5343 | 0 | 13220226.9514 | 34396318.6861 | 23476194.277 | 104990757.7386 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 119976928.0036 | 141971969.6035 | 4216965.0343 | 36.4628 | 3290.3934 | 3893.6123 | 67.0791 | 79.3766
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.6165 | 82.8447 | 9.1227 | 4 | 3288.7657 | 3891.5223 | 67.0459 | 79.3339 | 168.3408 | 0 | 292.4434 | 10819099.4468 | 952843.8487 | 11403689.1284 | 10346967.2951 | 0 | 385941.918 | 0 | 13224331.2384 | 34406997.199 | 23483482.5814 | 105023352.6557 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 120009522.9207 | 142004564.5206 | 5623413.2519 | 36.4907 | 3288.7657 | 3891.5223 | 67.0459 | 79.3339
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.6897 | 82.8722 | 9.1277 | 4 | 3287.5439 | 3889.9666 | 67.021 | 79.3022 | 168.3359 | 0 | 288.5137 | 10821666.5443 | 953065.6812 | 11406723.3549 | 10350953.6668 | 0 | 383211.2699 | 0 | 13227092.0017 | 34414180.1388 | 23488385.0854 | 105045277.743 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 120031448.0081 | 142026489.6079 | 7498942.0933 | 36.511 | 3287.5439 | 3889.9666 | 67.021 | 79.3022
1 | 4100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.746 | 82.8934 | 9.1316 | 4 | 3286.6271 | 3888.7962 | 67.0023 | 79.2784 | 168.3321 | 0 | 297.5924 | 10823642.1883 | 953236.4031 | 11409058.5591 | 10354022.1133 | 0 | 381170.8229 | 0 | 13229240.7338 | 34419770.6991 | 23492200.7577 | 105062342.2774 | 961560.8286 | 14024609.4364 | 14024609.4364 | 1478867.319 | 6491564.8444 | 0 | 120048512.5424 | 142043554.1423 | 10000000 | 36.5264 | 3286.6271 | 3888.7962 | 67.0023 | 79.2784
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.70141 | 0.12895 | 0.0027881 | 4 | 1457220.015 | 3485490.1775 | 29707.401 | 71056.4317 | 107.1309 | 0 | 43.0866 | 89706.6436 | 5784.8285 | 66905.1576 | 49043.8482 | 0 | 52946.565 | 0 | 103110.9467 | 268273.5324 | 183102.1983 | 818873.7202 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16251432.2209 | 38871417.3507 | 100 | 0.011152 | 1457220.015 | 3485490.1775 | 29707.401 | 71056.4317
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.19981 | 0.0083899 | 4 | 492310.5914 | 1166334.3403 | 10036.4173 | 23777.3031 | 118.6029 | 0 | 60.2057 | 130010.2167 | 8998.4513 | 94209.0189 | 59372.0336 | 0 | 59076.9839 | 0 | 137150.0147 | 356836.205 | 243548.0421 | 1089200.9663 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16521759.4669 | 39141744.5967 | 133.3521 | 0.03356 | 492310.5914 | 1166334.3403 | 10036.4173 | 23777.3031
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1619 | 0.29957 | 0.017383 | 4 | 242617.6729 | 567939.509 | 4946.0894 | 11578.2151 | 128.9128 | 0 | 51.2528 | 181864.794 | 13445.563 | 129325.4154 | 73489.6783 | 0 | 65806.5911 | 0 | 180933.4963 | 470751.8429 | 321297.8057 | 1436915.1868 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 16869473.6875 | 39489458.8173 | 177.8279 | 0.069531 | 242617.6729 | 567939.509 | 4946.0894 | 11578.2151
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.44327 | 0.031348 | 4 | 138212.9944 | 318607.4948 | 2817.6588 | 6495.2447 | 138.301 | 0 | 56.1358 | 250014.1037 | 19691.1546 | 175808.3587 | 93019.3524 | 0 | 74336.7847 | 0 | 239019.2041 | 621878.9395 | 424445.1545 | 1898213.0522 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17330771.5529 | 39950756.6827 | 237.1374 | 0.12539 | 138212.9944 | 318607.4948 | 2817.6588 | 6495.2447
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.982 | 0.64895 | 0.052597 | 4 | 85297.0517 | 192812.8591 | 1738.8958 | 3930.7509 | 146.5187 | 0 | 335.9351 | 339234.4332 | 28436.0275 | 237112.6931 | 121341.5326 | 0 | 85199.7352 | 0 | 316416.5244 | 823250.8906 | 561885.649 | 2512877.4857 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 17945435.9864 | 40565421.1161 | 316.2278 | 0.21039 | 85297.0517 | 192812.8591 | 1738.8958 | 3930.7509
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5655 | 0.91205 | 0.081671 | 4 | 57170.6954 | 126411.7034 | 1165.502 | 2577.0736 | 152.9672 | 0 | 437.7547 | 444252.0911 | 39446.1762 | 309803.6472 | 157830.8929 | 0 | 96123.8546 | 0 | 408508.0981 | 1062854.2748 | 725419.882 | 3244238.9167 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 18676797.4174 | 41296782.5472 | 421.6965 | 0.32668 | 57170.6954 | 126411.7034 | 1165.502 | 2577.0736
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3628 | 1.312 | 0.12252 | 4 | 40107.5166 | 86263.4647 | 817.646 | 1758.5974 | 158.4654 | 0 | 577.242 | 578275.9668 | 52335.0356 | 413793.2619 | 207595.043 | 0 | 111540.0818 | 0 | 531780.3618 | 1383583.4182 | 944324.1127 | 4223227.2818 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 19655785.7825 | 42275770.9123 | 562.3413 | 0.49008 | 40107.5166 | 86263.4647 | 817.646 | 1758.5974
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4138 | 1.8538 | 0.17592 | 4 | 29629.2387 | 61774.0924 | 604.0321 | 1259.3484 | 162.8694 | 0 | 73.7642 | 736561.7168 | 66663.2478 | 545620.6267 | 269820.7595 | 0 | 130372.0815 | 0 | 682124.9886 | 1774749.2973 | 1211302.8628 | 5417215.5811 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 20849774.0818 | 43469759.2116 | 749.8942 | 0.70369 | 29629.2387 | 61774.0924 | 604.0321 | 1259.3484
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.817 | 2.5784 | 0.24724 | 4 | 22584.692 | 45457.2435 | 460.4195 | 926.7074 | 166.3706 | 0 | 62.8555 | 928243.1195 | 83980.4624 | 710411.4818 | 352404.6749 | 0 | 153626.8749 | 0 | 869179.9792 | 2261428.0126 | 1543471.0863 | 6902745.6916 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 22335304.1923 | 44955289.3221 | 1000 | 0.98896 | 22584.692 | 45457.2435 | 460.4195 | 926.7074
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.671 | 3.5305 | 0.34093 | 4 | 17717.2496 | 34304.1707 | 361.1901 | 699.3369 | 168.9668 | 0 | 93.4287 | 1157487.1128 | 104644.9575 | 913479.0553 | 461033.2285 | 0 | 181621.1774 | 0 | 1099123.5573 | 2859694.0349 | 1951799.9396 | 8728883.0633 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 24161441.564 | 46781426.6938 | 1333.5214 | 1.3637 | 17717.2496 | 34304.1707 | 361.1901 | 699.3369
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.1406 | 4.8187 | 0.46807 | 4 | 14138.2713 | 26219.7881 | 288.2278 | 534.5258 | 171.2775 | 0 | 91.387 | 1440610.3302 | 130102.2134 | 1171586.7621 | 606030.6867 | 0 | 215552.3117 | 0 | 1389914.0986 | 3616271.3738 | 2468179.5196 | 11038247.296 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 26470805.7967 | 49090790.9265 | 1778.2794 | 1.8723 | 14138.2713 | 26219.7881 | 288.2278 | 534.5258
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4199 | 6.5192 | 0.63572 | 4 | 11538.2104 | 20433.6332 | 235.222 | 416.5673 | 172.928 | 0 | 98.1993 | 1782500.7045 | 160758.3007 | 1492073.2274 | 798141.3415 | 0 | 256864.5847 | 0 | 1751231.8819 | 4556346.1297 | 3109799.8571 | 13907716.0276 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 29340274.5283 | 51960259.6581 | 2371.3737 | 2.5429 | 11538.2104 | 20433.6332 | 235.222 | 416.5673
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.7831 | 8.7825 | 0.85878 | 4 | 9588.8662 | 16173.7495 | 195.482 | 329.7238 | 174.1954 | 0 | 103.6663 | 2199631.364 | 198048.1856 | 1893782.4757 | 1053542.2624 | 0 | 307268.7726 | 0 | 2204386.4935 | 5735361.4742 | 3914502.0561 | 17506523.084 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 32939081.5847 | 55559066.7145 | 3162.2777 | 3.4351 | 9588.8662 | 16173.7495 | 195.482 | 329.7238
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5636 | 11.782 | 1.1544 | 4 | 8108.3262 | 13006.8094 | 165.2992 | 265.1614 | 175.1611 | 0 | 108.5724 | 2707153.7522 | 243271.0784 | 2395574.3293 | 1391859.2198 | 0 | 368336.6184 | 0 | 2771416.0493 | 7210656.0646 | 4921420.9282 | 22009688.0402 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 37442246.5409 | 60062231.6707 | 4216.965 | 4.6178 | 8108.3262 | 13006.8094 | 165.2992 | 265.1614
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.2079 | 15.7493 | 1.5454 | 4 | 6968.8055 | 10628.1242 | 142.0685 | 216.6687 | 175.8953 | 0 | 107.1685 | 3324306.5656 | 298071.0869 | 3021643.4529 | 1839162.6325 | 0 | 442445.094 | 0 | 3480995.2445 | 9056835.5758 | 6181476.3799 | 27644936.0322 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 43077494.5329 | 65697479.6627 | 5623.4133 | 6.1815 | 6968.8055 | 10628.1242 | 142.0685 | 216.6687
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.2079 | 20.9394 | 2.057 | 4 | 6084.7465 | 8833.8939 | 124.0458 | 180.0909 | 176.4469 | 0 | 109.6775 | 4067738.2279 | 363840.6575 | 3794938.9223 | 2424206.0328 | 0 | 531032.7789 | 0 | 4360885.0816 | 11346128.4417 | 7743965.8011 | 34632735.9438 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 50065294.4445 | 72685279.5743 | 7498.9421 | 8.228 | 6084.7465 | 8833.8939 | 124.0458 | 180.0909
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.158 | 27.6507 | 2.7184 | 4 | 5394.2642 | 7474.5363 | 109.9694 | 152.3785 | 176.8296 | 0 | 91.4558 | 4954738.1234 | 442009.1783 | 4740227.0527 | 3181650.4863 | 0 | 636432.6139 | 0 | 5442472.4073 | 14160196.7992 | 9664625.2784 | 43222351.9394 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 58654910.4401 | 81274895.5699 | 10000 | 10.8736 | 5394.2642 | 7474.5363 | 109.9694 | 152.3785
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.5622 | 36.0867 | 3.5487 | 4 | 4858.4023 | 6451.9372 | 99.0451 | 131.5315 | 176.9658 | 0 | 117.2393 | 5986467.6283 | 532573.4831 | 5865586.3395 | 4139556.2899 | 0 | 759425.5012 | 0 | 6740607.6044 | 17537678.2978 | 11969825.8015 | 53531720.9456 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 68964279.4463 | 91584264.5761 | 13335.2143 | 14.1948 | 4858.4023 | 6451.9372 | 99.0451 | 131.5315
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 90.6502 | 46.2025 | 4.5408 | 4 | 4451.8485 | 5697.2365 | 90.757 | 116.1459 | 176.6907 | 0 | 117.7792 | 7136693.6487 | 633143.8346 | 7147696.6017 | 5307309.6496 | 0 | 899152.517 | 0 | 8238358.5381 | 21434518.9965 | 14629499.6504 | 65426373.4367 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 80858931.9374 | 103478917.0672 | 17782.7941 | 18.163 | 4451.8485 | 5697.2365 | 90.757 | 116.1459
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 114.0849 | 57.5451 | 5.645 | 4 | 4155.5933 | 5157.3657 | 84.7174 | 105.1399 | 175.8554 | 0 | 121.5265 | 8344042.4208 | 738315.9459 | 8520012.7057 | 6658657.5319 | 0 | 1051909.7645 | 0 | 9872045.9638 | 25685038.5628 | 17530566.5939 | 78400589.4893 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 93833147.99 | 116453133.1198 | 23713.7371 | 22.58 | 4155.5933 | 5157.3657 | 84.7174 | 105.1399
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8567 | 63.4611 | 6.3564 | 4 | 3938.6653 | 4828.3211 | 80.295 | 98.4319 | 175.2005 | 0 | 161.9835 | 8946541.4967 | 790663.8412 | 9213822.0278 | 7388405.8212 | 0 | 1010655.6492 | 0 | 10666534.646 | 27752135.1419 | 18941402.4837 | 84710161.1077 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 100142719.6084 | 122762704.7382 | 31622.7766 | 25.4255 | 3938.6653 | 4828.3211 | 80.295 | 98.4319
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 139.823 | 69.2855 | 7.052 | 4 | 3769.4346 | 4571.3315 | 76.845 | 93.1928 | 174.4552 | 0 | 196.6997 | 9524340.3563 | 840786.8822 | 9884331.5419 | 8124292.1585 | 0 | 973547.4429 | 0 | 11445446.3689 | 29778703.668 | 20324577.1446 | 90896025.5632 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 106328584.0639 | 128948569.1937 | 42169.6503 | 28.2081 | 3769.4346 | 4571.3315 | 76.845 | 93.1928
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 149.6487 | 73.6197 | 7.6154 | 4 | 3636.4453 | 4379.0192 | 74.1339 | 89.2722 | 173.8937 | 0 | 235.0969 | 9945416.8062 | 877268.1489 | 10375975.6389 | 8679909.7744 | 0 | 903332.4421 | 0 | 12004942.0961 | 31234396.7817 | 21318117.6062 | 95339359.2944 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 110771917.7951 | 133391902.9249 | 56234.1325 | 30.4616 | 3636.4453 | 4379.0192 | 74.1339 | 89.2722
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.6996 | 77.0892 | 8.0835 | 4 | 3533.9233 | 4233.4924 | 72.0438 | 86.3055 | 173.4056 | 0 | 256.6117 | 10277441.1236 | 906007.5356 | 10765353.9361 | 9132688.9121 | 0 | 828689.7348 | 0 | 12444970.6845 | 32379260.9065 | 22099510.896 | 98833923.7292 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 114266482.2299 | 136886467.3597 | 74989.4209 | 32.3342 | 3533.9233 | 4233.4924 | 72.0438 | 86.3055
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.1964 | 79.8347 | 8.4647 | 4 | 3455.2815 | 4123.3477 | 70.4406 | 84.06 | 172.9946 | 0 | 287.3326 | 10537200.126 | 928475.8769 | 11071002.741 | 9496937.3016 | 0 | 756556.7532 | 0 | 12788167.3915 | 33272188.3389 | 22708952.2164 | 101559480.7456 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 116992039.2463 | 139612024.3761 | 100000 | 33.8589 | 3455.2815 | 4123.3477 | 70.4406 | 84.06
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.2265 | 81.9237 | 8.7645 | 4 | 3395.1558 | 4040.374 | 69.2148 | 82.3685 | 172.6663 | 0 | 300.0255 | 10733154.337 | 945416.2551 | 11302152.8389 | 9777210.7087 | 0 | 689255.0193 | 0 | 13044403.772 | 33938862.8397 | 23163971.262 | 103594427.0328 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 119026985.5335 | 141646970.6633 | 133352.1432 | 35.0579 | 3395.1558 | 4040.374 | 69.2148 | 82.3685
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.0781 | 83.5026 | 8.9972 | 4 | 3349.3507 | 3977.8786 | 68.281 | 81.0944 | 172.409 | 0 | 284.7516 | 10880329.5343 | 958134.6148 | 11476083.7137 | 9991382.8704 | 0 | 629512.5484 | 0 | 13234822.8798 | 34434294.2978 | 23502113.4122 | 105106673.8714 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 120539232.3721 | 143159217.5018 | 177827.941 | 35.9888 | 3349.3507 | 3977.8786 | 68.281 | 81.0944
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.9692 | 84.6759 | 9.1749 | 4 | 3314.5418 | 3930.8989 | 67.5714 | 80.1367 | 172.2126 | 0 | 307.5234 | 10989181.0917 | 967538.4318 | 11604898.8213 | 10151903.6608 | 0 | 577954.775 | 0 | 13373675.9444 | 34795561.4892 | 23748685.6937 | 106209399.9078 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 121641958.4085 | 144261943.5383 | 237137.3706 | 36.6995 | 3314.5418 | 3930.8989 | 67.5714 | 80.1367
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.1398 | 85.5499 | 9.3099 | 4 | 3288.1436 | 3895.558 | 67.0333 | 79.4162 | 172.0634 | 0 | 318.3533 | 11069995.6988 | 974518.6034 | 11700630.2328 | 10272281.3074 | 0 | 534869.5901 | 0 | 13475395.2187 | 35060214.1753 | 23929316.59 | 107017221.4165 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 122449779.9172 | 145069765.047 | 316227.766 | 37.2398 | 3288.1436 | 3895.558 | 67.0333 | 79.4162
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.8092 | 86.2179 | 9.4137 | 4 | 3268.1559 | 3868.8753 | 66.6258 | 78.8723 | 171.9476 | 0 | 310.9349 | 11131599.4024 | 979838.6254 | 11773658.9293 | 10364652.4369 | 0 | 500162.4294 | 0 | 13552465.6111 | 35260735.5272 | 24066176.533 | 107629289.4946 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 123061847.9953 | 145681833.1251 | 421696.5034 | 37.6548 | 3268.1559 | 3868.8753 | 66.6258 | 78.8723
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.9781 | 86.6831 | 9.4891 | 4 | 3253.0452 | 3848.9915 | 66.3177 | 78.4669 | 171.8659 | 0 | 308.3888 | 11174426.6823 | 983536.7051 | 11824456.395 | 10429171.4224 | 0 | 471364.0071 | 0 | 13604352.5327 | 35395734.6536 | 24158316.2107 | 108041358.6089 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 123473917.1096 | 146093902.2394 | 562341.3252 | 37.9564 | 3253.0452 | 3848.9915 | 66.3177 | 78.4669
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.8406 | 87.0253 | 9.5455 | 4 | 3241.6395 | 3834.0671 | 66.0852 | 78.1626 | 171.8053 | 0 | 303.5418 | 11205883.6088 | 986252.7443 | 11861781.769 | 10476756.5691 | 0 | 448464.0544 | 0 | 13641864.1108 | 35493332.0851 | 24224928.4631 | 108339263.4045 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 123771821.9052 | 146391807.035 | 749894.2093 | 38.1819 | 3241.6395 | 3834.0671 | 66.0852 | 78.1626
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.4667 | 87.273 | 9.5872 | 4 | 3233.0407 | 3822.8912 | 65.9099 | 77.9348 | 171.7611 | 0 | 281.548 | 11228636.1209 | 988217.1122 | 11888786.3998 | 10511281.0039 | 0 | 430347.1752 | 0 | 13668434.4466 | 35562462.6487 | 24272111.4933 | 108550276.4005 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 123982834.9012 | 146602820.031 | 1000000 | 38.3487 | 3233.0407 | 3822.8912 | 65.9099 | 77.9348
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.087 | 86.3248 | 9.5166 | 4 | 3226.2294 | 3820.4525 | 65.7711 | 77.8851 | 171.9249 | 0 | 757.8721 | 11141448.8152 | 980689.1408 | 11785339.3343 | 10379882.6646 | 0 | 381631.1581 | 0 | 13520906.5341 | 35178625.2823 | 24010134.6037 | 107378657.533 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 122811216.0337 | 145431201.1635 | 1333521.4322 | 38.0665 | 3226.2294 | 3820.4525 | 65.7711 | 77.8851
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.6506 | 87.7408 | 9.6564 | 4 | 3221.1127 | 3806.7313 | 65.6667 | 77.6054 | 171.6779 | 0 | 292.478 | 11271554.5327 | 991922.259 | 11939742.7935 | 10576562.0296 | 0 | 408003.7622 | 0 | 13723236.297 | 35705045.822 | 24369427.4388 | 108985494.9348 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124418053.4355 | 147038038.5653 | 1778279.41 | 38.6258 | 3221.1127 | 3806.7313 | 65.6667 | 77.6054
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.9204 | 87.847 | 9.6743 | 4 | 3217.5076 | 3802.0486 | 65.5932 | 77.5099 | 171.6587 | 0 | 331.4323 | 11281286.0708 | 992762.3336 | 11951300.0147 | 10591427.0889 | 0 | 400020.1768 | 0 | 13734550.3171 | 35734482.5814 | 24389518.632 | 109075347.2154 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124507905.716 | 147127890.8458 | 2371373.7057 | 38.697 | 3217.5076 | 3802.0486 | 65.5932 | 77.5099
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.101 | 87.918 | 9.6868 | 4 | 3214.7987 | 3798.5801 | 65.538 | 77.4392 | 171.6458 | 0 | 320.818 | 11287790.8496 | 993323.8483 | 11959025.7612 | 10601376.1358 | 0 | 393696.6079 | 0 | 13741733.1491 | 35753170.8369 | 24402273.7504 | 109132390.9393 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124564949.44 | 147184934.5698 | 3162277.6602 | 38.7474 | 3214.7987 | 3798.5801 | 65.538 | 77.4392
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.2371 | 87.9715 | 9.6963 | 4 | 3212.7641 | 3795.9751 | 65.4965 | 77.3861 | 171.6361 | 0 | 322.819 | 11292691.033 | 993746.8435 | 11964846.0631 | 10608875.6571 | 0 | 388913.131 | 0 | 13747138.3638 | 35767234.0968 | 24411872.2142 | 109175317.4025 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124607875.9032 | 147227861.033 | 4216965.0343 | 38.7853 | 3212.7641 | 3795.9751 | 65.4965 | 77.3861
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.3251 | 88.006 | 9.7029 | 4 | 3211.2366 | 3794.0506 | 65.4654 | 77.3469 | 171.6298 | 0 | 299.5904 | 11295853.9346 | 994019.87 | 11968603.0242 | 10613721.3372 | 0 | 385132.9924 | 0 | 13750359.1518 | 35775613.9264 | 24417591.6201 | 109200895.8566 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124633454.3573 | 147253439.4871 | 5623413.2519 | 38.8117 | 3211.2366 | 3794.0506 | 65.4654 | 77.3469
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.4151 | 88.0414 | 9.7087 | 4 | 3210.09 | 3792.5548 | 65.442 | 77.3164 | 171.6234 | 0 | 319.1206 | 11299092.9357 | 994299.4636 | 11972450.5035 | 10618679.9047 | 0 | 382561.9409 | 0 | 13754163.0519 | 35785510.8943 | 24424346.5041 | 109231105.1989 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124663663.6996 | 147283648.8294 | 7498942.0933 | 38.8349 | 3210.09 | 3792.5548 | 65.442 | 77.3164
1 | 4200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.454 | 88.0566 | 9.7121 | 4 | 3209.2296 | 3791.4942 | 65.4245 | 77.2947 | 171.6206 | 0 | 325.8246 | 11300488.3141 | 994419.9134 | 11974108.0565 | 10620821.4463 | 0 | 380290.8718 | 0 | 13755350.1548 | 35788599.4925 | 24426454.5358 | 109240532.7852 | 961560.8286 | 14470997.6721 | 14470997.6721 | 1478867.319 | 6670120.1387 | 0 | 124673091.2859 | 147293076.4157 | 10000000 | 38.8483 | 3209.2296 | 3791.4942 | 65.4245 | 77.2947
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.72086 | 0.1379 | 0.0036156 | 4 | 1157390.939 | 2765204.2031 | 23594.9798 | 56372.4279 | 109.5136 | 0 | 46.4845 | 95382.2812 | 6239.534 | 70476.3377 | 50235.8083 | 0 | 53412.1694 | 0 | 107540.991 | 279799.5988 | 190968.9755 | 854055.6959 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 16738862.5231 | 39991995.3101 | 100 | 0.014463 | 1157390.939 | 2765204.2031 | 23594.9798 | 56372.4279
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.21165 | 0.0097778 | 4 | 435060.4605 | 1029598.7828 | 8869.296 | 20989.7638 | 120.9705 | 0 | 62.701 | 137082.2085 | 9627.2799 | 98484.3884 | 60843.5114 | 0 | 59108.2229 | 0 | 142406.7883 | 370513.2515 | 252882.9075 | 1130948.5584 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17015755.3856 | 40268888.1725 | 133.3521 | 0.039111 | 435060.4605 | 1029598.7828 | 8869.296 | 20989.7638
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2008 | 0.32345 | 0.020107 | 4 | 216369.2211 | 505482.8626 | 4410.9792 | 10304.9519 | 131.9845 | 0 | 56.8756 | 194826.694 | 14696.6329 | 137218.0944 | 76479.9714 | 0 | 66748.8252 | 0 | 191088.385 | 497172.7801 | 339330.6383 | 1517562.0212 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17402368.8485 | 40655501.6354 | 177.8279 | 0.080429 | 216369.2211 | 505482.8626 | 4410.9792 | 10304.9519
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5686 | 0.48189 | 0.03602 | 4 | 124269.1265 | 285657.6259 | 2533.3942 | 5823.5171 | 141.6984 | 0 | 66.5061 | 269358.7724 | 21736.604 | 187518.112 | 97748.3285 | 0 | 75862.0816 | 0 | 254367.3204 | 661811.5898 | 451700.0089 | 2020102.8177 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 17904909.6449 | 41158042.4319 | 237.1374 | 0.14408 | 124269.1265 | 285657.6259 | 2533.3942 | 5823.5171
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0209 | 0.68798 | 0.058577 | 4 | 79011.5599 | 178253.1084 | 1610.7575 | 3633.9307 | 149.5007 | 0 | 334.6267 | 358666.8864 | 30838.9141 | 247898.7928 | 126311.3933 | 0 | 84864.4515 | 0 | 330946.3709 | 861054.5705 | 587687.4373 | 2628268.8168 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 18513075.644 | 41766208.4309 | 316.2278 | 0.23431 | 79011.5599 | 178253.1084 | 1610.7575 | 3633.9307
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 0.99389 | 0.091736 | 4 | 52693.982 | 116063.9201 | 1074.2381 | 2366.12 | 156.3505 | 0 | 447.6079 | 475761.3309 | 42947.4837 | 331420.5927 | 166613.8189 | 0 | 97425.2598 | 0 | 434525.7095 | 1130546.7626 | 771621.3959 | 3450862.3539 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 19335669.1811 | 42588801.968 | 421.6965 | 0.36694 | 52693.982 | 116063.9201 | 1074.2381 | 2366.12
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4601 | 1.431 | 0.13527 | 4 | 37617.1342 | 80593.5161 | 766.8762 | 1643.0078 | 161.9127 | 0 | 597.0783 | 614482.6933 | 55614.7924 | 443559.9492 | 215936.3563 | 0 | 113171.5039 | 0 | 562678.4651 | 1463973.9449 | 999192.2991 | 4468610.0042 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 20353416.8315 | 43606549.6184 | 562.3413 | 0.54107 | 37617.1342 | 80593.5161 | 766.8762 | 1643.0078
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5259 | 2.0052 | 0.19238 | 4 | 28051.9681 | 58270.2418 | 571.8773 | 1187.9177 | 166.3404 | 0 | 77.0735 | 778193.166 | 70427.5079 | 580971.21 | 279500.1655 | 0 | 131681.1899 | 0 | 717901.5634 | 1867832.6061 | 1274834.1338 | 5701341.5428 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 21586148.37 | 44839281.1569 | 749.8942 | 0.76951 | 28051.9681 | 58270.2418 | 571.8773 | 1187.9177
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9459 | 2.7714 | 0.26852 | 4 | 21524.8189 | 43174.3004 | 438.8125 | 880.1665 | 169.87 | 0 | 86.2779 | 976484.8702 | 88333.1395 | 752645.4389 | 363787.2868 | 0 | 154505.4047 | 0 | 910944.8946 | 2370091.7553 | 1617636.3235 | 7234429.1135 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 23119235.9407 | 46372368.7276 | 1000 | 1.0741 | 21524.8189 | 43174.3004 | 438.8125 | 880.1665
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.8562 | 3.7956 | 0.36988 | 4 | 16924.1962 | 32640.6685 | 345.0226 | 665.4242 | 172.5139 | 0 | 89.4823 | 1217933.8072 | 110085.8045 | 967957.5803 | 476650.392 | 0 | 183281.6798 | 0 | 1152804.6129 | 2999361.13 | 2047125.6019 | 9155200.6087 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 25040007.4359 | 48293140.2228 | 1333.5214 | 1.4795 | 16924.1962 | 32640.6685 | 345.0226 | 665.4242
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3842 | 5.1752 | 0.50706 | 4 | 13536.7846 | 25001.3816 | 275.9657 | 509.687 | 174.9027 | 0 | 101.5889 | 1514864.0321 | 136767.883 | 1240434.4396 | 626418.5903 | 0 | 217486.7912 | 0 | 1457028.9771 | 3790890.5208 | 2587360.6754 | 11571251.9096 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 27456058.7368 | 50709191.5237 | 1778.2794 | 2.0283 | 13536.7846 | 25001.3816 | 275.9657 | 509.687
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.7365 | 6.992 | 0.68752 | 4 | 11072.8219 | 19528.2011 | 225.7345 | 398.1088 | 176.5845 | 0 | 76.1274 | 1872711.482 | 168832.8303 | 1578025.9154 | 824436.7887 | 0 | 259047.8325 | 0 | 1834191.391 | 4772189.7551 | 3257117.5666 | 14566553.5616 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 30451360.3888 | 53704493.1757 | 2371.3737 | 2.7501 | 11072.8219 | 19528.2011 | 225.7345 | 398.1088
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.1922 | 9.4079 | 0.9271 | 4 | 9224.1885 | 15494.5627 | 188.0476 | 315.8776 | 177.8757 | 0 | 47.4304 | 2309126.6164 | 207817.8403 | 2000918.8494 | 1087555.6292 | 0 | 310237.3712 | 0 | 2307105.9595 | 6002616.4542 | 4096909.0714 | 18322287.7917 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 34207094.6189 | 57460227.4058 | 3162.2777 | 3.7084 | 9224.1885 | 15494.5627 | 188.0476 | 315.8776
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.0849 | 12.6039 | 1.2452 | 4 | 7808.8598 | 12477.5009 | 159.1942 | 254.3707 | 178.8591 | 0 | 51.9654 | 2839385.4537 | 255029.3781 | 2528354.2024 | 1435462.0444 | 0 | 370555.2815 | 0 | 2897226.6805 | 7537989.5197 | 5144832.7374 | 23008835.2978 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 38893642.125 | 62146774.912 | 4216.965 | 4.9807 | 7808.8598 | 12477.5009 | 159.1942 | 254.3707
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.8922 | 16.8391 | 1.6664 | 4 | 6716.7438 | 10205.3142 | 136.9299 | 208.0491 | 179.609 | 0 | 57.8698 | 3485611.5167 | 312362.7438 | 3187779.1111 | 1896271.158 | 0 | 444231.0633 | 0 | 3637239.6812 | 9463351.5501 | 6458931.8854 | 28885778.7096 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 44770585.5368 | 68023718.3238 | 5623.4133 | 6.6655 | 6716.7438 | 10205.3142 | 136.9299 | 208.0491
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.0969 | 22.375 | 2.2172 | 4 | 5869.1779 | 8491.0869 | 119.6511 | 173.1023 | 180.1712 | 0 | 56.9958 | 4263600.301 | 381128.1272 | 4001700.0347 | 2498628.2861 | 0 | 532269.0213 | 0 | 4554157.0504 | 11848982.4591 | 8087174.0006 | 36167639.2803 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 52052446.1076 | 75305578.8945 | 7498.9421 | 8.8688 | 5869.1779 | 8491.0869 | 119.6511 | 173.1023
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.0058 | 29.3664 | 2.9127 | 4 | 5218.4192 | 7214.2532 | 106.3845 | 147.0723 | 180.5497 | 0 | 113.2156 | 5171117.1271 | 461032.9875 | 4974096.9439 | 3260394.4695 | 0 | 634636.9726 | 0 | 5655498.6152 | 14714447.2945 | 10042912.6302 | 44914137.0405 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 60798943.8677 | 84052076.6546 | 10000 | 11.6508 | 5218.4192 | 7214.2532 | 106.3845 | 147.0723
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 71.5757 | 38.2679 | 3.7968 | 4 | 4703.8807 | 6234.9652 | 95.895 | 127.1082 | 180.6729 | 0 | 136.5005 | 6241517.7584 | 554907.9161 | 6147543.0959 | 4236575.7276 | 0 | 756227.4865 | 0 | 6995341.074 | 18200442.5327 | 12422176.0103 | 55554731.6015 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 71439538.4287 | 94692671.2157 | 13335.2143 | 15.1874 | 4703.8807 | 6234.9652 | 95.895 | 127.1082
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 91.9117 | 48.9588 | 4.8538 | 4 | 4313.1565 | 5510.8317 | 87.9295 | 112.3458 | 180.3567 | 0 | 124.0916 | 7437158.0567 | 659352.9298 | 7486833.5211 | 5429258.6929 | 0 | 895870.8736 | 0 | 8544304.8889 | 22230528.643 | 15172792.5906 | 67856100.1967 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 83740907.0239 | 106994039.8108 | 17782.7941 | 19.4152 | 4313.1565 | 5510.8317 | 87.9295 | 112.3458
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 115.8754 | 61.057 | 6.0397 | 4 | 4026.9928 | 4989.5068 | 82.0957 | 101.7178 | 179.4361 | 0 | 77.0729 | 8703703.9837 | 769575.3385 | 8933503.9813 | 6823647.5044 | 0 | 1051658.1041 | 0 | 10250014.6757 | 26668435.619 | 18201755.2915 | 81402294.4982 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 97287101.3254 | 120540234.1123 | 23713.7371 | 24.1587 | 4026.9928 | 4989.5068 | 82.0957 | 101.7178
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.3823 | 67.5686 | 6.8068 | 4 | 3824.5919 | 4678.63 | 77.9695 | 95.3802 | 178.6883 | 0 | 114.1601 | 9355497.1606 | 826147.7717 | 9687893.8364 | 7602681.7675 | 0 | 1020256.1799 | 0 | 11112065.9192 | 28911316.1237 | 19732567.3226 | 88248426.0815 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 104133232.9087 | 127386365.6956 | 31622.7766 | 27.2273 | 3824.5919 | 4678.63 | 77.9695 | 95.3802
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.364 | 73.6465 | 7.5324 | 4 | 3665.9608 | 4437.7275 | 74.7356 | 90.4691 | 177.9029 | 0 | 127.9686 | 9947995.0473 | 877491.4057 | 10378993.5133 | 8346944.2395 | 0 | 981966.2803 | 0 | 11908022.2896 | 30982231.3262 | 21146009.5013 | 94569653.6033 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 110454460.4305 | 133707593.2174 | 42169.6503 | 30.1297 | 3665.9608 | 4437.7275 | 74.7356 | 90.4691
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9 | 79.8414 | 8.2553 | 4 | 3540.2116 | 4244.4013 | 72.172 | 86.5279 | 177.0794 | 0 | 205.9097 | 10537832.4133 | 928530.5511 | 11071747.8019 | 9119409.8864 | 0 | 957484.819 | 0 | 12719852.1339 | 33094446.052 | 22587639.4534 | 101016943.1109 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 116901749.9381 | 140154882.725 | 56234.1325 | 33.0211 | 3540.2116 | 4244.4013 | 72.172 | 86.5279
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.9586 | 82.0937 | 8.6332 | 4 | 3443.4494 | 4116.8166 | 70.1994 | 83.9269 | 176.7462 | 0 | 256.355 | 10749043.6795 | 946789.5629 | 11320917.5972 | 9406370.4353 | 0 | 840710.6255 | 0 | 12972894.4412 | 33752810.2294 | 23036986.5325 | 103026523.1036 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 118911329.9308 | 142164462.7177 | 74989.4209 | 34.5326 | 3443.4494 | 4116.8166 | 70.1994 | 83.9269
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.2929 | 84.8735 | 9.0222 | 4 | 3369.5503 | 4013.8805 | 68.6928 | 81.8284 | 176.3191 | 0 | 231.8719 | 11007476.2826 | 969118.7474 | 11626563.8645 | 9764747.6774 | 0 | 765037.5461 | 0 | 13311848.206 | 34634698.3965 | 23638893.3275 | 105718384.048 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 121603190.8752 | 144856323.6621 | 100000 | 36.0888 | 3369.5503 | 4013.8805 | 68.6928 | 81.8284
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.2887 | 87.0309 | 9.3314 | 4 | 3313.0832 | 3936.0624 | 67.5417 | 80.242 | 175.9721 | 0 | 258.6438 | 11206399.5347 | 986297.2885 | 11862394.0442 | 10046713.019 | 0 | 696229.0087 | 0 | 13571232.8291 | 35309563.9787 | 24099502.9544 | 107778332.6574 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 123663139.4846 | 146916272.2715 | 133352.1432 | 37.3257 | 3313.0832 | 3936.0624 | 67.5417 | 80.242
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.0398 | 88.6285 | 9.5683 | 4 | 3270.0464 | 3877.5998 | 66.6643 | 79.0501 | 175.7057 | 0 | 310.3201 | 11352811.4047 | 998936.1999 | 12036279.0029 | 10257442.1019 | 0 | 634488.6054 | 0 | 13759183.3528 | 35798572.6873 | 24433261.4462 | 109270974.801 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 125155781.6282 | 148408914.4151 | 177827.941 | 38.2734 | 3270.0464 | 3877.5998 | 66.6643 | 79.0501
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.8781 | 89.8253 | 9.7499 | 4 | 3237.3392 | 3833.579 | 65.9975 | 78.1527 | 175.5008 | 0 | 298.8366 | 11462005.7606 | 1008359.6737 | 12166131.1751 | 10416672.3343 | 0 | 581701.4163 | 0 | 13897599.4403 | 36158702.9541 | 24679057.7532 | 110370230.5075 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 126255037.3347 | 149508170.1216 | 237137.3706 | 38.9996 | 3237.3392 | 3833.579 | 65.9975 | 78.1527
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 180.9781 | 90.704 | 9.8867 | 4 | 3212.5326 | 3800.5219 | 65.4918 | 77.4788 | 175.3474 | 0 | 292.8999 | 11541916.8941 | 1015254.5766 | 12261250.5049 | 10534365.1681 | 0 | 537326.2463 | 0 | 13997144.2221 | 36417698.0569 | 24855827.2327 | 111160782.9019 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 127045589.7291 | 150298722.5161 | 316227.766 | 39.5469 | 3212.5326 | 3800.5219 | 65.4918 | 77.4788
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.525 | 91.3475 | 9.9893 | 4 | 3193.7512 | 3775.705 | 65.1089 | 76.9729 | 175.2333 | 0 | 285.8017 | 11600304.044 | 1020291.5856 | 12330797.4633 | 10620998.2065 | 0 | 500838.1775 | 0 | 14068559.496 | 36603505.9502 | 24982644.9378 | 111727939.8608 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 127612746.688 | 150865879.475 | 421696.5034 | 39.957 | 3193.7512 | 3775.705 | 65.1089 | 76.9729
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.6575 | 91.8166 | 10.0657 | 4 | 3179.5534 | 3757.0889 | 64.8195 | 76.5933 | 175.1493 | 0 | 346.3719 | 11642789.9804 | 1023956.4096 | 12381429.247 | 10684386.5558 | 0 | 471312.1568 | 0 | 14119510.9964 | 36736071.3026 | 25073123.5148 | 112132580.1634 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 128017386.9906 | 151270519.7775 | 562341.3252 | 40.2627 | 3179.5534 | 3757.0889 | 64.8195 | 76.5933
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.4734 | 92.1535 | 10.122 | 4 | 3168.8353 | 3743.1541 | 64.601 | 76.3093 | 175.0884 | 0 | 336.3114 | 11673260.712 | 1026584.5983 | 12417755.2286 | 10730035.6073 | 0 | 447621.5601 | 0 | 14155150.5055 | 36828797.9946 | 25136411.3874 | 112415617.5939 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 128300424.4211 | 151553557.208 | 749894.2093 | 40.4882 | 3168.8353 | 3743.1541 | 64.601 | 76.3093
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.0802 | 92.4034 | 10.1643 | 4 | 3160.7536 | 3732.6844 | 64.4362 | 76.0958 | 175.043 | 0 | 328.715 | 11695849.536 | 1028532.8381 | 12444691.7525 | 10763975.0087 | 0 | 429079.9065 | 0 | 14181230.3263 | 36896652.3387 | 25182723.3716 | 112622735.0784 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 128507541.9056 | 151760674.6926 | 1000000 | 40.6572 | 3160.7536 | 3732.6844 | 64.4362 | 76.0958
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.905 | 91.5012 | 10.0979 | 4 | 3154.3264 | 3730.0211 | 64.3052 | 76.0415 | 175.2017 | 0 | 751.339 | 11614223.9174 | 1021492.3468 | 12347383.8562 | 10642173.3951 | 0 | 381774.0702 | 0 | 14042748.5584 | 36536351.1852 | 24936810.4309 | 111522957.7602 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 127407764.5874 | 150660897.3744 | 1333521.4322 | 40.3914 | 3154.3264 | 3730.0211 | 64.3052 | 76.0415
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.2789 | 92.8963 | 10.2364 | 4 | 3149.5509 | 3717.4563 | 64.2079 | 75.7854 | 174.9537 | 0 | 316.8735 | 11740342.5225 | 1032369.99 | 12497765.8362 | 10830877.3687 | 0 | 406766.8752 | 0 | 14238167.8111 | 37044791.9947 | 25283831.7307 | 113074914.1291 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 128959720.9563 | 152212853.7432 | 1778279.41 | 40.9454 | 3149.5509 | 3717.4563 | 64.2079 | 75.7854
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.6077 | 93.0309 | 10.2569 | 4 | 3146.1613 | 3712.9299 | 64.1388 | 75.6931 | 174.929 | 0 | 301.2848 | 11752482.8063 | 1033416.9252 | 12512251.5612 | 10849179.6027 | 0 | 399404.2657 | 0 | 14253226.7128 | 37083972.168 | 25310573.0041 | 113194507.046 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129079313.8732 | 152332446.6601 | 2371373.7057 | 41.0276 | 3146.1613 | 3712.9299 | 64.1388 | 75.6931
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.7781 | 93.1005 | 10.2695 | 4 | 3143.6143 | 3709.6894 | 64.0868 | 75.627 | 174.9161 | 0 | 316.0231 | 11758758.4686 | 1033958.1055 | 12519740.3237 | 10858661.9127 | 0 | 392892.6839 | 0 | 14259964.4828 | 37101502.4634 | 25322537.7909 | 113248016.2314 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129132823.0586 | 152385955.8456 | 3162277.6602 | 41.0778 | 3143.6143 | 3709.6894 | 64.0868 | 75.627
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.9024 | 93.1512 | 10.2788 | 4 | 3141.7013 | 3707.2642 | 64.0478 | 75.5776 | 174.9066 | 0 | 316.655 | 11763331.5605 | 1034352.4605 | 12525197.6942 | 10865576.6775 | 0 | 387916.8618 | 0 | 14264786.3492 | 37114047.9707 | 25331100.3574 | 113286309.9319 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129171116.7591 | 152424249.546 | 4216965.0343 | 41.115 | 3141.7013 | 3707.2642 | 64.0478 | 75.5776
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.995 | 93.189 | 10.2857 | 4 | 3140.2649 | 3705.4453 | 64.0185 | 75.5405 | 174.8996 | 0 | 312.7244 | 11766737.6711 | 1034646.1797 | 12529262.5877 | 10870729.3412 | 0 | 384149.1177 | 0 | 14268354.71 | 37123332.1133 | 25337436.9755 | 113314648.6962 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129199455.5234 | 152452588.3103 | 5623413.2519 | 41.1429 | 3140.2649 | 3705.4453 | 64.0185 | 75.5405
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.0681 | 93.2189 | 10.2911 | 4 | 3139.1868 | 3704.0728 | 63.9966 | 75.5125 | 174.8941 | 0 | 306.4647 | 11769428.1853 | 1034878.1894 | 12532473.5753 | 10874799.9991 | 0 | 381351.326 | 0 | 14271243.1973 | 37130847.3648 | 25342566.2891 | 113337588.1263 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129222394.9535 | 152475527.7405 | 7498942.0933 | 41.1643 | 3139.1868 | 3704.0728 | 63.9966 | 75.5125
1 | 4300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.107 | 93.2347 | 10.2945 | 4 | 3138.3777 | 3703.0759 | 63.9801 | 75.4922 | 174.8911 | 0 | 310.2841 | 11770855.3301 | 1035001.255 | 12534176.8321 | 10876963.2522 | 0 | 379052.2283 | 0 | 14272459.0702 | 37134010.8167 | 25344725.41 | 113347244.1947 | 961560.8286 | 14923245.9986 | 14923245.9986 | 1478867.319 | 6851019.4693 | 0 | 129232051.0219 | 152485183.8088 | 10000000 | 41.178 | 3138.3777 | 3703.0759 | 63.9801 | 75.4922
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.74031 | 0.1473 | 0.0045223 | 4 | 952697.1838 | 2273631.5489 | 19422.0207 | 46351.0544 | 111.8971 | 0 | 49.1421 | 101295.7636 | 6722.7134 | 74165.13 | 51494.0945 | 0 | 53834.5271 | 0 | 112129.7691 | 291738.6583 | 199117.6289 | 890498.2848 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17233413.5294 | 41127898.1006 | 100 | 0.018089 | 952697.1838 | 2273631.5489 | 19422.0207 | 46351.0544
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.22977 | 0.011595 | 4 | 378157.8628 | 893330.2163 | 7709.2595 | 18211.7448 | 124.0445 | 0 | 49.4766 | 147505.7007 | 10558.0218 | 104951.4984 | 63091.8691 | 0 | 60243.878 | 0 | 150676.8774 | 392030.327 | 267568.7536 | 1196626.9259 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17539542.1705 | 41434026.7418 | 133.3521 | 0.046382 | 378157.8628 | 893330.2163 | 7709.2595 | 18211.7448
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.235 | 0.34646 | 0.022923 | 4 | 195618.0001 | 456215.9066 | 3987.9375 | 9300.5783 | 134.9024 | 0 | 43.9814 | 207319.493 | 15945.3324 | 144685.616 | 79245.12 | 0 | 67291.2874 | 0 | 200649.871 | 522049.8055 | 356309.7193 | 1593496.2447 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 17936411.4893 | 41830896.0605 | 177.8279 | 0.091691 | 195618.0001 | 456215.9066 | 3987.9375 | 9300.5783
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6125 | 0.51622 | 0.040656 | 4 | 113575.5964 | 260508.1732 | 2315.3922 | 5310.8115 | 144.7817 | 0 | 261.1554 | 286877.8625 | 23702.7401 | 197694.7901 | 102060.4809 | 0 | 76397.3758 | 0 | 267825.9673 | 696828.2281 | 475599.5841 | 2126987.0288 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 18469902.2734 | 42364386.8447 | 237.1374 | 0.16262 | 113575.5964 | 260508.1732 | 2315.3922 | 5310.8115
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0793 | 0.73726 | 0.065765 | 4 | 72672.7956 | 163505.9808 | 1481.5332 | 3333.2906 | 152.7512 | 0 | 344.4583 | 382621.9598 | 33892.9241 | 261357.1721 | 132360.7726 | 0 | 85501.335 | 0 | 349336.3238 | 908901.4557 | 620343.9196 | 2774315.8625 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19117231.1071 | 43011715.6784 | 316.2278 | 0.26306 | 72672.7956 | 163505.9808 | 1481.5332 | 3333.2906
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7211 | 1.0852 | 0.1017 | 4 | 49157.0858 | 107893.1373 | 1002.1337 | 2199.5475 | 159.7297 | 0 | 461.1798 | 506426.5695 | 45822.6259 | 355489.0388 | 173481.3991 | 0 | 98773.7015 | 0 | 460197.4006 | 1197339.2369 | 817208.632 | 3654738.6043 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 19997653.8489 | 43892138.4202 | 421.6965 | 0.40681 | 49157.0858 | 107893.1373 | 1002.1337 | 2199.5475
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5379 | 1.542 | 0.14753 | 4 | 35637.968 | 76128.5479 | 726.5282 | 1551.9834 | 165.253 | 0 | 606.8716 | 647461.6572 | 58600.9854 | 470881.7581 | 222924.009 | 0 | 113706.0505 | 0 | 590294.0395 | 1535824.0048 | 1048231.4413 | 4687923.9457 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 21030839.1903 | 44925323.7615 | 562.3413 | 0.59012 | 35637.968 | 76128.5479 | 726.5282 | 1551.9834
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6379 | 2.1598 | 0.20929 | 4 | 26670.2867 | 55212.0156 | 543.7099 | 1125.5716 | 169.8075 | 0 | 79.0097 | 819797.075 | 74187.5307 | 616552.6211 | 289000.1849 | 0 | 132768.2396 | 0 | 753599.204 | 1960710.5444 | 1338225.2351 | 5984840.6349 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 22327755.8795 | 46222240.4508 | 749.8942 | 0.83718 | 26670.2867 | 55212.0156 | 543.7099 | 1125.5716
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.0922 | 2.9778 | 0.29112 | 4 | 20547.9966 | 41067.7056 | 418.8987 | 837.2207 | 173.3971 | 0 | 75.5073 | 1026995.8803 | 92888.2008 | 797162.5248 | 375952.0818 | 0 | 155786.6582 | 0 | 955026.2849 | 2484782.4904 | 1695915.1069 | 7584509.2281 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 23927424.4727 | 47821909.044 | 1000 | 1.1645 | 20547.9966 | 41067.7056 | 418.8987 | 837.2207
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0265 | 4.0578 | 0.39894 | 4 | 16235.2026 | 31208.8352 | 330.9766 | 636.2343 | 176.0368 | 0 | 81.6212 | 1276522.5829 | 115356.3901 | 1021099.6755 | 491084.6992 | 0 | 184074.3557 | 0 | 1204373.7044 | 3133533.3277 | 2138700.8838 | 9564745.6194 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 25907660.864 | 49802145.4352 | 1333.5214 | 1.5958 | 16235.2026 | 31208.8352 | 330.9766 | 636.2343
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.6205 | 5.5351 | 0.54677 | 4 | 13003.1497 | 23928.459 | 265.0868 | 487.814 | 178.5175 | 0 | 70.689 | 1588328.6508 | 143358.4744 | 1308979.8271 | 645913.4758 | 0 | 218803.6762 | 0 | 1523099.8007 | 3962793.2507 | 2704687.8208 | 12095964.9766 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 28438880.2212 | 52333364.7924 | 1778.2794 | 2.1871 | 13003.1497 | 23928.459 | 265.0868 | 487.814
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.0117 | 7.4516 | 0.73945 | 4 | 10658.5427 | 18737.0037 | 217.2888 | 381.9792 | 180.2191 | 0 | 54.4171 | 1958728.6761 | 176526.7232 | 1660475.5459 | 847810.2752 | 0 | 258523.9129 | 0 | 1911805.402 | 4974125.4907 | 3394942.8555 | 15182938.8814 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 31525854.126 | 55420338.6973 | 2371.3737 | 2.9578 | 10658.5427 | 18737.0037 | 217.2888 | 381.9792
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.4675 | 9.9711 | 0.99189 | 4 | 8911.8873 | 14934.346 | 181.6809 | 304.4568 | 181.5199 | 0 | 96.5527 | 2405934.7373 | 216449.3519 | 2096175.8757 | 1113081.0897 | 0 | 307849.5461 | 0 | 2394401.3343 | 6229741.1126 | 4251926.3177 | 19015559.3654 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 35358474.61 | 59252959.1812 | 3162.2777 | 3.9676 | 8911.8873 | 14934.346 | 181.6809 | 304.4568
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.399 | 13.3258 | 1.3285 | 4 | 7560.9082 | 12057.4753 | 154.1393 | 245.8079 | 182.524 | 0 | 112.3214 | 2953487.1334 | 265167.9504 | 2643549.3581 | 1466039.7433 | 0 | 367377.5661 | 0 | 3001292.483 | 7808747.3911 | 5329630.5481 | 23835292.1736 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 40178207.4182 | 64072691.9894 | 4216.965 | 5.3139 | 7560.9082 | 12057.4753 | 154.1393 | 245.8079
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.2064 | 17.7425 | 1.7718 | 4 | 6516.3496 | 9887.7744 | 132.8446 | 201.5757 | 183.2884 | 0 | 122.3381 | 3617071.406 | 324001.0935 | 3323877.9931 | 1930616.4091 | 0 | 439022.8269 | 0 | 3757489.9942 | 9776218.1977 | 6672469.8011 | 29840767.7216 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 46183682.9662 | 70078167.5374 | 5623.4133 | 7.0874 | 6516.3496 | 9887.7744 | 132.8446 | 201.5757
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.4259 | 23.5239 | 2.3522 | 4 | 5700.8231 | 8240.3812 | 116.219 | 167.9913 | 183.8647 | 0 | 99.6854 | 4417751.5032 | 394723.0708 | 4165244.9114 | 2538718.3972 | 0 | 525081.9878 | 0 | 4696192.7495 | 12218530.2125 | 8339397.9357 | 37295640.7681 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 53638556.0127 | 77533040.5839 | 7498.9421 | 9.4089 | 5700.8231 | 8240.3812 | 116.219 | 167.9913
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 55.6442 | 30.9881 | 3.1013 | 4 | 5061.6562 | 6987.8527 | 103.1887 | 142.4568 | 184.2577 | 0 | 120.5374 | 5372353.5744 | 478710.6577 | 5192658.7566 | 3324879.5788 | 0 | 627579.1145 | 0 | 5848510.856 | 15216625.5527 | 10385659.6101 | 46446977.7009 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 62789892.9455 | 86684377.5167 | 10000 | 12.405 | 5061.6562 | 6987.8527 | 103.1887 | 142.4568
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 72.3721 | 40.3547 | 4.0396 | 4 | 4564.7257 | 6043.4845 | 93.0581 | 123.2046 | 184.3714 | 0 | 124.2602 | 6481674.9555 | 575919.9964 | 6414291.7624 | 4318170.372 | 0 | 747682.7192 | 0 | 7229718.5241 | 18810244.5806 | 12838378.4381 | 57416081.3483 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 73758996.5929 | 97653481.1642 | 13335.2143 | 16.1585 | 4564.7257 | 6043.4845 | 93.0581 | 123.2046
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 92.8131 | 51.5522 | 5.1568 | 4 | 4187.8318 | 5346.2338 | 85.3746 | 108.9902 | 184.0214 | 0 | 138.7956 | 7715506.2329 | 683611.3261 | 7802451.9171 | 5527125.3524 | 0 | 884869.38 | 0 | 8819290.0413 | 22945983.6024 | 15661105.3014 | 70039943.1537 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 86382858.3983 | 110277342.9695 | 17782.7941 | 20.6271 | 4187.8318 | 5346.2338 | 85.3746 | 108.9902
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 116.6648 | 64.0955 | 6.3974 | 4 | 3913.6103 | 4847.3648 | 79.7842 | 98.8201 | 183.0458 | 0 | 133.6524 | 9010180.0607 | 796188.0808 | 9287430.6426 | 6926822.9669 | 0 | 1037264.0289 | 0 | 10552575.4541 | 27455636.7008 | 18739036.2052 | 83805134.14 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 100148049.3846 | 124042533.9558 | 23713.7371 | 25.5897 | 3913.6103 | 4847.3648 | 79.7842 | 98.8201
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.2487 | 72.3975 | 7.3164 | 4 | 3719.9569 | 4536.432 | 75.8364 | 92.4813 | 182.0667 | 0 | 151.3583 | 9827409.1257 | 867048.0339 | 10237943.0742 | 7891243.2031 | 0 | 1049003.8718 | 0 | 11650332.4504 | 30311775.2241 | 20688409.4352 | 92523164.4184 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 108866079.663 | 132760564.2343 | 31622.7766 | 29.2654 | 3719.9569 | 4536.432 | 75.8364 | 92.4813
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 146.6346 | 78.9134 | 8.0918 | 4 | 3568.6039 | 4306.8395 | 72.7508 | 87.8007 | 181.2362 | 0 | 169.3223 | 10450322.4837 | 920962.7655 | 10968678.9939 | 8665516.604 | 0 | 1010675.9194 | 0 | 12486301.1389 | 32486794.2709 | 22172904.6268 | 99162156.8031 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 115505072.0477 | 139399556.619 | 42169.6503 | 32.367 | 3568.6039 | 4306.8395 | 72.7508 | 87.8007
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.3165 | 83.5077 | 8.6941 | 4 | 3450.8859 | 4137.9712 | 70.351 | 84.3581 | 180.6045 | 0 | 200.7621 | 10880798.511 | 958175.1352 | 11476638.3838 | 9222345.9224 | 0 | 932705.6621 | 0 | 13053558.8096 | 33962682.3696 | 23180228.5806 | 103667133.3743 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 120010048.6189 | 143904533.1902 | 56234.1325 | 34.7766 | 3450.8859 | 4137.9712 | 70.351 | 84.3581
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.6387 | 86.9224 | 9.1734 | 4 | 3358.9043 | 4010.0911 | 68.4758 | 81.7511 | 180.1187 | 0 | 195.2917 | 11196427.5084 | 985436.3101 | 11850560.3155 | 9641927.4476 | 0 | 842641.1984 | 0 | 13461627.1842 | 35024392.5738 | 23904867.6109 | 106907880.149 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 123250795.3936 | 147145279.9648 | 74989.4209 | 36.6938 | 3358.9043 | 4010.0911 | 68.4758 | 81.7511
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8844 | 89.7621 | 9.5706 | 4 | 3289.9512 | 3914.1173 | 67.0701 | 79.7946 | 179.6686 | 0 | 217.8156 | 11456249.3281 | 1007862.9499 | 12159282.152 | 9998323.81 | 0 | 765706.7284 | 0 | 13801095.7377 | 35907620.1154 | 24507688.5566 | 109603829.378 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 125946744.6226 | 149841229.1938 | 100000 | 38.2823 | 3289.9512 | 3914.1173 | 67.0701 | 79.7946
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 174.7519 | 91.939 | 9.8837 | 4 | 3237.1626 | 3841.5552 | 65.9939 | 78.3153 | 179.3067 | 0 | 189.8976 | 11653859.8179 | 1024911.2351 | 12394625.0002 | 10275457.0202 | 0 | 695133.06 | 0 | 14057154.5921 | 36573832.7297 | 24962392.3551 | 111637365.8103 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 127980281.0549 | 151874765.6262 | 133352.1432 | 39.5347 | 3237.1626 | 3841.5552 | 65.9939 | 78.3153
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.4908 | 93.5892 | 10.1269 | 4 | 3196.877 | 3786.756 | 65.1727 | 77.1981 | 179.0222 | 0 | 229.076 | 11802779.4428 | 1037754.0395 | 12572283.5483 | 10488000.3177 | 0 | 632961.4644 | 0 | 14248173.7369 | 37070825.3611 | 25301600.0383 | 113154377.9489 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 129497293.1935 | 153391777.7648 | 177827.941 | 40.5074 | 3196.877 | 3786.756 | 65.1727 | 77.1981
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.3996 | 94.858 | 10.316 | 4 | 3166.1985 | 3745.2614 | 64.5472 | 76.3522 | 178.7971 | 0 | 231.4214 | 11916780.606 | 1047582.7149 | 12708459.2393 | 10652521.565 | 0 | 580674.4153 | 0 | 14393347.2308 | 37448537.013 | 25559396.0018 | 114307298.786 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 130650214.0306 | 154544698.6018 | 237137.3706 | 41.2641 | 3166.1985 | 3745.2614 | 64.5472 | 76.3522
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 183.4996 | 95.7663 | 10.4564 | 4 | 3142.8994 | 3714.1869 | 64.0723 | 75.7187 | 178.6323 | 0 | 229.2722 | 11998124.7743 | 1054594.3938 | 12805717.3276 | 10771119.3992 | 0 | 535938.1074 | 0 | 14494542.6608 | 37711826.764 | 25739096.667 | 115110960.094 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 131453875.3386 | 155348359.9099 | 316227.766 | 41.8257 | 3142.8994 | 3714.1869 | 64.0723 | 75.7187
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.0607 | 96.4374 | 10.5622 | 4 | 3125.2405 | 3690.809 | 63.7123 | 75.2421 | 178.5086 | 0 | 271.9769 | 12058085.7915 | 1059762.1233 | 12877457.4221 | 10859216.8144 | 0 | 499271.5404 | 0 | 14567979.5398 | 37902894.4591 | 25869504.2949 | 115694171.9855 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 132037087.2301 | 155931571.8014 | 421696.5034 | 42.2486 | 3125.2405 | 3690.809 | 63.7123 | 75.2421
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.1861 | 96.9189 | 10.6403 | 4 | 3111.8799 | 3673.2973 | 63.4399 | 74.8851 | 178.4188 | 0 | 269.9116 | 12101036.9964 | 1063463.4645 | 12928871.3779 | 10922689.7659 | 0 | 469346.6296 | 0 | 14619309.2114 | 38036443.7354 | 25960654.4201 | 116101815.6012 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 132444730.8458 | 156339215.4171 | 562341.3252 | 42.561 | 3111.8799 | 3673.2973 | 63.4399 | 74.8851
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.0144 | 97.2722 | 10.6985 | 4 | 3101.7869 | 3660.1463 | 63.2341 | 74.617 | 178.3524 | 0 | 277.5051 | 12132503.4166 | 1066174.8871 | 12966550.9729 | 10969387.0681 | 0 | 445528.5441 | 0 | 14656256.5067 | 38132573.0188 | 26026264.6313 | 116395239.0457 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 132738154.2903 | 156632638.8615 | 749894.2093 | 42.7941 | 3101.7869 | 3660.1463 | 63.2341 | 74.617
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.6212 | 97.5302 | 10.7418 | 4 | 3094.1724 | 3650.2802 | 63.0789 | 74.4159 | 178.3035 | 0 | 273.2426 | 12155475.2363 | 1068154.2277 | 12994065.7535 | 11003585.5312 | 0 | 426757.2968 | 0 | 14682734.8378 | 38201464.2048 | 26073284.2814 | 116605521.3696 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 132948436.6142 | 156842921.1854 | 1000000 | 42.9674 | 3094.1724 | 3650.2802 | 63.0789 | 74.4159
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.0498 | 97.7122 | 10.7734 | 4 | 3088.4346 | 3642.9134 | 62.9619 | 74.2657 | 178.2688 | 0 | 259.2497 | 12171658.4096 | 1069548.5753 | 13013452.9301 | 11027736.5432 | 0 | 411911.4697 | 0 | 14700780.0919 | 38248414.2544 | 26105328.655 | 116748830.9291 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133091746.1737 | 156986230.745 | 1333521.4322 | 43.0936 | 3088.4346 | 3642.9134 | 62.9619 | 74.2657
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.8003 | 98.0311 | 10.8151 | 4 | 3083.6346 | 3635.977 | 62.8641 | 74.1243 | 178.2088 | 0 | 256.0551 | 12200010.9064 | 1071991.3223 | 13047425.8807 | 11070039.135 | 0 | 404003.613 | 0 | 14739453.6344 | 38349034.879 | 26174004.2988 | 117055963.6694 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133398878.914 | 157293363.4853 | 1778279.41 | 43.2603 | 3083.6346 | 3635.977 | 62.8641 | 74.1243
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.0413 | 98.133 | 10.8327 | 4 | 3080.4406 | 3631.8815 | 62.7989 | 74.0408 | 178.1892 | 0 | 269.0478 | 12209060.892 | 1072771.0054 | 13058271.7961 | 11083610.4916 | 0 | 395484.0169 | 0 | 14749487.2988 | 38375140.4156 | 26191821.8639 | 117135647.7804 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133478563.025 | 157373047.5963 | 2371373.7057 | 43.331 | 3080.4406 | 3631.8815 | 62.7989 | 74.0408
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.207 | 98.203 | 10.8454 | 4 | 3078.0399 | 3628.8353 | 62.75 | 73.9787 | 178.1757 | 0 | 260.6709 | 12215278.1226 | 1073306.6298 | 13065723.3429 | 11092945.5596 | 0 | 388823.7708 | 0 | 14756070.196 | 38392267.7639 | 26203511.6311 | 117187927.0168 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133530842.2614 | 157425326.8327 | 3162277.6602 | 43.3818 | 3078.0399 | 3628.8353 | 62.75 | 73.9787
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.3339 | 98.2566 | 10.8551 | 4 | 3076.2365 | 3626.5433 | 62.7132 | 73.932 | 178.1653 | 0 | 253.2658 | 12220033.7873 | 1073716.3332 | 13071423.4504 | 11100090.0038 | 0 | 383807.4224 | 0 | 14761137.6889 | 38405452.3407 | 26212510.3757 | 117228171.4023 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133571086.6469 | 157465571.2182 | 4216965.0343 | 43.4203 | 3076.2365 | 3626.5433 | 62.7132 | 73.932
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.4239 | 98.2945 | 10.8621 | 4 | 3074.8822 | 3624.8331 | 62.6856 | 73.8971 | 178.158 | 0 | 265.3015 | 12223404.7826 | 1074006.7441 | 13075464.0566 | 11105157.9363 | 0 | 379952.617 | 0 | 14764614.5932 | 38414498.5327 | 26218684.5876 | 117255783.8501 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133598699.0947 | 157493183.6659 | 5623413.2519 | 43.4484 | 3074.8822 | 3624.8331 | 62.6856 | 73.8971
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.4971 | 98.3254 | 10.8676 | 4 | 3073.8657 | 3623.5386 | 62.6649 | 73.8707 | 178.152 | 0 | 261.3527 | 12226144.9952 | 1074242.8116 | 13078748.6762 | 11109277.5145 | 0 | 377113.4047 | 0 | 14767555.6869 | 38422150.6551 | 26223907.3184 | 117279141.0626 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133622056.3072 | 157516540.8785 | 7498942.0933 | 43.4704 | 3073.8657 | 3623.5386 | 62.6649 | 73.8707
1 | 4400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.5554 | 98.35 | 10.8718 | 4 | 3073.1027 | 3622.5605 | 62.6494 | 73.8508 | 178.1472 | 0 | 266.1768 | 12228330.2314 | 1074431.0673 | 13081368.121 | 11112562.8383 | 0 | 375016.8552 | 0 | 14769966.5541 | 38428423.2371 | 26228188.4844 | 117298287.3888 | 961560.8286 | 15381354.416 | 15381354.416 | 1478867.319 | 7034262.8363 | 0 | 133641202.6334 | 157535687.2046 | 10000000 | 43.4874 | 3073.1027 | 3622.5605 | 62.6494 | 73.8508
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.75975 | 0.15706 | 0.0055015 | 4 | 805894.3813 | 1921222.5374 | 16429.247 | 39166.7201 | 114.2817 | 0 | 53.5169 | 107395.4385 | 7230.9668 | 77940.1468 | 52751.1331 | 0 | 54212.6048 | 0 | 116816.8131 | 303933.3852 | 207440.7806 | 927721.2687 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 17734605.0216 | 42278645.5044 | 100 | 0.022006 | 805894.3813 | 1921222.5374 | 16429.247 | 39166.7201
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.24286 | 0.013236 | 4 | 340907.6869 | 804496.7917 | 6949.8643 | 16400.7553 | 126.4167 | 0 | 53.6165 | 155245.3096 | 11282.502 | 109527.9299 | 64763.8563 | 0 | 60171.2174 | 0 | 156386.4179 | 406885.3801 | 277707.6326 | 1241970.2457 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18048853.9985 | 42592894.4814 | 133.3521 | 0.052944 | 340907.6869 | 804496.7917 | 6949.8643 | 16400.7553
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.37228 | 0.02608 | 4 | 177190.886 | 412467.7233 | 3612.2759 | 8408.7124 | 137.9671 | 0 | 54.3454 | 221149.5652 | 17363.1987 | 152932.4268 | 82137.17 | 0 | 68071.6928 | 0 | 211245.0809 | 549616.3681 | 375124.4647 | 1677639.9672 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 18484523.72 | 43028564.2028 | 177.8279 | 0.10432 | 177190.886 | 412467.7233 | 3612.2759 | 8408.7124
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6514 | 0.54959 | 0.045445 | 4 | 104723.291 | 239744.3571 | 2134.9259 | 4887.513 | 147.7581 | 0 | 273.2662 | 304062.5616 | 25732.6871 | 207404.2123 | 106146.604 | 0 | 76532.7086 | 0 | 280752.7218 | 730460.9917 | 498554.6363 | 2229647.1235 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19036530.8764 | 43580571.3592 | 237.1374 | 0.18178 | 104723.291 | 239744.3571 | 2134.9259 | 4887.513
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1376 | 0.79909 | 0.073571 | 4 | 67097.3463 | 150499.6904 | 1367.8702 | 3068.1398 | 155.9988 | 0 | 357.3144 | 408340.1219 | 36799.8852 | 278372.1732 | 139065.174 | 0 | 86277.4771 | 0 | 370053.3842 | 962802.9974 | 657132.8294 | 2938844.0424 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 19745727.7953 | 44289768.2781 | 316.2278 | 0.29428 | 67097.3463 | 150499.6904 | 1367.8702 | 3068.1398
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7794 | 1.1687 | 0.111 | 4 | 46478.6888 | 101756.0693 | 947.5309 | 2074.4351 | 162.9394 | 0 | 469.0287 | 533355.6783 | 48264.0906 | 377216.7435 | 178870.8263 | 0 | 99000.2286 | 0 | 482315.9512 | 1254887.1685 | 856486.2778 | 3830396.9647 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 20637280.7176 | 45181321.2004 | 421.6965 | 0.44402 | 46478.6888 | 101756.0693 | 947.5309 | 2074.4351
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 1.6665 | 0.16103 | 4 | 33750.6753 | 71856.1008 | 688.0532 | 1464.8838 | 168.6934 | 0 | 624.6345 | 683615.9971 | 61873.4127 | 501051.4518 | 230943.0629 | 0 | 114966.7837 | 0 | 621055.7762 | 1615859.7336 | 1102857.4708 | 4932223.6888 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 21739107.4417 | 46283147.9245 | 562.3413 | 0.64411 | 33750.6753 | 71856.1008 | 688.0532 | 1464.8838
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7622 | 2.325 | 0.22727 | 4 | 25399.007 | 52397.5704 | 517.7931 | 1068.1953 | 173.3094 | 0 | 82.1944 | 863271.5838 | 78114.7676 | 653992.3919 | 299062.2153 | 0 | 134137.1796 | 0 | 791145.4739 | 2058398.2369 | 1404899.0926 | 6283020.9417 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 23089904.6946 | 47633945.1774 | 749.8942 | 0.90909 | 25399.007 | 52397.5704 | 517.7931 | 1068.1953
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.258 | 3.2 | 0.31528 | 4 | 19635.9821 | 39097.9366 | 400.3061 | 797.0643 | 176.9542 | 0 | 68.1447 | 1080249.9783 | 97688.0619 | 844410.5789 | 389059.4123 | 0 | 157522.0649 | 0 | 1001882.7376 | 2606693.3687 | 1779121.7864 | 7956627.989 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 24763511.7418 | 49307552.2246 | 1000 | 1.2611 | 19635.9821 | 39097.9366 | 400.3061 | 797.0643
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2311 | 4.3446 | 0.43052 | 4 | 15571.639 | 29824.359 | 317.4489 | 608.0099 | 179.5813 | 0 | 49.5662 | 1339346.1482 | 121004.692 | 1078436.2689 | 507244.5921 | 0 | 185351.8357 | 0 | 1260239.5794 | 3278884.8749 | 2237906.3015 | 10008414.2927 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 26815298.0455 | 51359338.5283 | 1333.5214 | 1.7221 | 15571.639 | 29824.359 | 317.4489 | 608.0099
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7863 | 5.8614 | 0.58422 | 4 | 12561.8389 | 23064.7184 | 256.0901 | 470.2055 | 182.08 | 0 | 93.2628 | 1653738.7749 | 149223.0207 | 1370354.4164 | 660931.6686 | 0 | 217313.0692 | 0 | 1580108.7704 | 4111118.8958 | 2805923.1214 | 12548711.7374 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 29355595.4902 | 53899635.973 | 1778.2794 | 2.3369 | 12561.8389 | 23064.7184 | 256.0901 | 470.2055
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.1969 | 7.8672 | 0.78715 | 4 | 10330.067 | 18125.2755 | 210.5924 | 369.5083 | 183.8127 | 0 | 87.6462 | 2035196.9345 | 183362.2836 | 1734159.789 | 865452.3131 | 0 | 256785.2708 | 0 | 1979233.0705 | 5149558.4529 | 3514679.4569 | 15718427.5713 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 32525311.3241 | 57069351.8069 | 2371.3737 | 3.1486 | 10330.067 | 18125.2755 | 210.5924 | 369.5083
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.7259 | 10.5319 | 1.0567 | 4 | 8634.531 | 14441.0689 | 176.0266 | 294.4007 | 185.1535 | 0 | 87.6794 | 2500790.751 | 224901.3691 | 2189979.6139 | 1136940.7614 | 0 | 304951.8696 | 0 | 2479450.1024 | 6451020.5612 | 4402954.0882 | 19690989.1168 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 36497872.8697 | 61041913.3525 | 3162.2777 | 4.227 | 8634.531 | 14441.0689 | 176.0266 | 294.4007
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 24.7279 | 14.0647 | 1.4141 | 4 | 7332.1777 | 11671.2699 | 149.4764 | 237.9346 | 186.1835 | 0 | 118.5426 | 3068455.4181 | 275376.6254 | 2760178.6072 | 1496718.0552 | 0 | 363592.0408 | 0 | 3106085.0912 | 8081396.2616 | 5515719.0046 | 24667521.1041 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 41474404.8569 | 66018445.3397 | 4216.965 | 5.6565 | 7332.1777 | 11671.2699 | 149.4764 | 237.9346
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 32.6279 | 18.7158 | 1.8848 | 4 | 6323.5785 | 9579.0641 | 128.9147 | 195.2822 | 186.9683 | 0 | 125.0907 | 3756569.6549 | 336342.473 | 3468962.7053 | 1970290.0862 | 0 | 434209.8398 | 0 | 3886886.1561 | 10112880.4682 | 6902248.7185 | 30868390.1021 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 47675273.8549 | 72219314.3377 | 5623.4133 | 7.5393 | 6323.5785 | 9579.0641 | 128.9147 | 195.2822
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 42.9789 | 24.8098 | 2.5014 | 4 | 5534.8104 | 7987.8033 | 112.8346 | 162.8422 | 187.5601 | 0 | 108.9335 | 4587763.6879 | 409705.9358 | 4346419.8946 | 2590749.7115 | 0 | 519316.5921 | 0 | 4857042.7706 | 12637028.9725 | 8625031.9387 | 38573059.5037 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 55379943.2566 | 79923983.7394 | 7498.9421 | 10.0058 | 5534.8104 | 7987.8033 | 112.8346 | 162.8422
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 56.3358 | 32.6584 | 3.2955 | 4 | 4916.9141 | 6778.8677 | 100.2379 | 138.1964 | 187.9586 | 0 | 108.326 | 5576505.1565 | 496630.2353 | 5415391.4079 | 3391173.4793 | 0 | 620245.4741 | 0 | 6044978.8437 | 15727794.9556 | 10734543.2311 | 48007262.7835 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 64814146.5364 | 89358187.0192 | 10000 | 13.1819 | 4916.9141 | 6778.8677 | 100.2379 | 138.1964
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 73.1958 | 42.4782 | 4.2875 | 4 | 4436.7191 | 5867.8705 | 90.4485 | 119.6245 | 188.0606 | 0 | 123.426 | 6722471.0174 | 596970.7697 | 6682929.6908 | 4399738.7197 | 0 | 738139.1339 | 0 | 7464697.2393 | 19421610.9967 | 13255648.5795 | 59282206.1471 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 76089089.8999 | 100633130.3827 | 13335.2143 | 17.1499 | 4436.7191 | 5867.8705 | 90.4485 | 119.6245
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 93.7948 | 54.2088 | 5.4672 | 4 | 4072.3986 | 5194.7396 | 83.0214 | 105.9018 | 187.6731 | 0 | 120.6796 | 7996554.6012 | 708084.6515 | 8122492.2941 | 5626732.9939 | 0 | 873519.1822 | 0 | 9097679.6519 | 23670296.2636 | 16155463.5759 | 72250823.2143 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 89057706.9671 | 113601747.45 | 17782.7941 | 21.8686 | 4072.3986 | 5194.7396 | 83.0214 | 105.9018
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 117.7294 | 67.2881 | 6.7716 | 4 | 3807.6313 | 4713.7713 | 77.6237 | 96.0966 | 186.6337 | 0 | 159.8218 | 9327799.0501 | 823745.6753 | 9655708.0796 | 7041643.4151 | 0 | 1023542.8824 | 0 | 10870251.2499 | 28282163.9572 | 19303158.0412 | 86328012.3507 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 103134896.1036 | 127678936.5864 | 23713.7371 | 27.0864 | 3807.6313 | 4713.7713 | 77.6237 | 96.0966
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.6667 | 78.1334 | 7.901 | 4 | 3622.8483 | 4399.4556 | 73.8567 | 89.6889 | 185.3215 | 0 | 133.5695 | 10376539.4755 | 914580.8612 | 10881855.1426 | 8267703.0832 | 0 | 1100258.015 | 0 | 12300965.2653 | 32004588.3453 | 21843789.1742 | 97690279.3624 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 114497163.1153 | 139041203.5981 | 31622.7766 | 31.6042 | 3622.8483 | 4399.4556 | 73.8567 | 89.6889
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150 | 83.8412 | 8.6269 | 4 | 3479.5623 | 4190.8245 | 70.9356 | 85.4356 | 184.5888 | 0 | 175.3736 | 10911786.7265 | 960852.4786 | 11513295.0039 | 8928077.0993 | 0 | 1026783.3432 | 0 | 13002909.9141 | 33830904.3329 | 23090287.3627 | 103264896.2612 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 120071780.014 | 144615820.4968 | 42169.6503 | 34.5077 | 3479.5623 | 4190.8245 | 70.9356 | 85.4356
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.5614 | 88.5323 | 9.2454 | 4 | 3368.6328 | 4032.316 | 68.6741 | 82.2042 | 183.9257 | 0 | 229.7148 | 11344018.0576 | 998177.2355 | 12025828.3289 | 9482780.3293 | 0 | 944669.6698 | 0 | 13570234.7122 | 35306967.0832 | 24097730.5199 | 107770405.9363 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 124577289.6891 | 149121330.1719 | 56234.1325 | 36.9816 | 3368.6328 | 4032.316 | 68.6741 | 82.2042
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 167.2929 | 92.2372 | 9.7521 | 4 | 3283.1837 | 3912.3803 | 66.9321 | 79.7592 | 183.3614 | 0 | 226.8877 | 11680827.5368 | 1027237.232 | 12426777.7832 | 9928950.6463 | 0 | 860072.3972 | 0 | 14010307.5823 | 36451946.4199 | 24879202.4442 | 111265322.042 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 128072205.7948 | 152616246.2776 | 74989.4209 | 39.0085 | 3283.1837 | 3912.3803 | 66.9321 | 79.7592
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.4756 | 95.1426 | 10.1605 | 4 | 3217.6713 | 3821.5785 | 65.5966 | 77.908 | 182.8928 | 0 | 245.6453 | 11942294.3351 | 1049782.0692 | 12738956.2181 | 10284720.3976 | 0 | 780050.57 | 0 | 14350363.4001 | 37336701.9027 | 25483066.2411 | 113965935.1339 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 130772818.8868 | 155316859.3696 | 100000 | 40.6421 | 3217.6713 | 3821.5785 | 65.5966 | 77.908
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.213 | 97.3326 | 10.4786 | 4 | 3167.6061 | 3753.179 | 64.5759 | 76.5136 | 182.5236 | 0 | 256.4688 | 12137883.4319 | 1066638.4585 | 12972994.4173 | 10556330.6751 | 0 | 706418.0141 | 0 | 14601703.3488 | 37990636.8924 | 25929390.3086 | 115961995.5467 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 132768879.2995 | 157312919.7823 | 133352.1432 | 41.9146 | 3167.6061 | 3753.179 | 64.5759 | 76.5136
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.8212 | 98.9797 | 10.7242 | 4 | 3129.4647 | 3701.6308 | 63.7984 | 75.4627 | 182.2366 | 0 | 255.5375 | 12284175.1432 | 1079241.755 | 13148327.654 | 10762907.2997 | 0 | 641798.9325 | 0 | 14787415.8059 | 38473822.6109 | 26259174.4899 | 117436863.6911 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 134243747.444 | 158787787.9268 | 177827.941 | 42.8967 | 3129.4647 | 3701.6308 | 63.7984 | 75.4627
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.5077 | 100.1941 | 10.9103 | 4 | 3100.4742 | 3662.879 | 63.2074 | 74.6727 | 182.0197 | 0 | 277.3963 | 12391597.3245 | 1088493.9365 | 13277227.7014 | 10916554.0353 | 0 | 586360.8351 | 0 | 14921491.1948 | 38822659.2702 | 26497262.6778 | 118501646.9756 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 135308530.7284 | 159852571.2112 | 237137.3706 | 43.6412 | 3100.4742 | 3662.879 | 63.2074 | 74.6727
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.5929 | 101.1289 | 11.0542 | 4 | 3078.4738 | 3633.556 | 62.7589 | 74.075 | 181.8495 | 0 | 297.1606 | 12474039.0965 | 1095593.1887 | 13376239.7036 | 11035402.3209 | 0 | 541194.1045 | 0 | 15023762.6815 | 39088748.6998 | 26678874.1811 | 119313853.9766 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 136120737.7295 | 160664778.2123 | 316227.766 | 44.217 | 3078.4738 | 3633.556 | 62.7589 | 74.075
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.0427 | 101.775 | 11.1585 | 4 | 3061.8123 | 3611.707 | 62.4192 | 73.6295 | 181.7301 | 0 | 291.5026 | 12530890.4751 | 1100488.0946 | 13444561.5204 | 11117955.5158 | 0 | 503051.7818 | 0 | 15091809.4812 | 39265792.5143 | 26799710.2223 | 119854259.6055 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 136661143.3583 | 161205183.8411 | 421696.5034 | 44.6341 | 3061.8123 | 3611.707 | 62.4192 | 73.6295
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.1 | 102.2442 | 11.236 | 4 | 3049.2139 | 3595.3153 | 62.1623 | 73.2954 | 181.6424 | 0 | 293.8972 | 12572109.2063 | 1104036.6738 | 13494118.8253 | 11178125.9956 | 0 | 472227.9124 | 0 | 15140041.2592 | 39391281.7071 | 26885359.175 | 120237300.7547 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 137044184.5075 | 161588224.9903 | 562341.3252 | 44.9441 | 3049.2139 | 3595.3153 | 62.1623 | 73.2954
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.8649 | 102.5825 | 11.2933 | 4 | 3039.7008 | 3583.032 | 61.9684 | 73.045 | 181.5787 | 0 | 295.3338 | 12601803.3921 | 1106592.9042 | 13529831.6937 | 11221643.6041 | 0 | 447598.2792 | 0 | 15173913.2506 | 39479409.6805 | 26945508.3277 | 120506301.1322 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 137313184.885 | 161857225.3678 | 749894.2093 | 45.1733 | 3039.7008 | 3583.032 | 61.9684 | 73.045
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.423 | 102.8288 | 11.3358 | 4 | 3032.526 | 3573.8204 | 61.8221 | 72.8572 | 181.532 | 0 | 274.4062 | 12623401.0273 | 1108452.0444 | 13555812.9828 | 11253386.5552 | 0 | 428207.3049 | 0 | 15198011.3667 | 39542108.0354 | 26988301.2432 | 120697680.5599 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 137504564.3128 | 162048604.7956 | 1000000 | 45.3432 | 3032.526 | 3573.8204 | 61.8221 | 72.8572
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.8271 | 103.0069 | 11.3672 | 4 | 3027.1207 | 3566.9209 | 61.712 | 72.7165 | 181.4981 | 0 | 272.7265 | 12639003.9103 | 1109795.1013 | 13574585.936 | 11276368.3886 | 0 | 413040.5422 | 0 | 15214989.6126 | 39586281.9485 | 27018450.8466 | 120832516.2861 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 137639400.039 | 162183440.5218 | 1333521.4322 | 45.4688 | 3027.1207 | 3566.9209 | 61.712 | 72.7165
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.5628 | 103.3315 | 11.4095 | 4 | 3022.6106 | 3560.4081 | 61.62 | 72.5837 | 181.4373 | 0 | 286.3767 | 12667438.1679 | 1112242.5415 | 13608804.0596 | 11318221.1477 | 0 | 405117.4146 | 0 | 15253611.0992 | 39686767.1343 | 27087034.0507 | 121139235.6156 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 137946119.3684 | 162490159.8512 | 1778279.41 | 45.6381 | 3022.6106 | 3560.4081 | 61.62 | 72.5837
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.7823 | 103.4278 | 11.4268 | 4 | 3019.604 | 3556.5893 | 61.5587 | 72.5059 | 181.4188 | 0 | 257.514 | 12675867.9794 | 1112968.0991 | 13618950.2851 | 11330697.2652 | 0 | 396333.8393 | 0 | 15262578.8126 | 39710099.2849 | 27102958.7229 | 121210454.2884 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138017338.0412 | 162561378.524 | 2371373.7057 | 45.7071 | 3019.604 | 3556.5893 | 61.5587 | 72.5059
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.9324 | 103.4936 | 11.4391 | 4 | 3017.3443 | 3553.7489 | 61.5126 | 72.448 | 181.4061 | 0 | 312.6588 | 12681626.0479 | 1113463.6915 | 13625881.2115 | 11339229.4773 | 0 | 389476.3574 | 0 | 15268373.9464 | 39725177.0343 | 27113249.5967 | 121256477.363 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138063361.1158 | 162607401.5986 | 3162277.6602 | 45.7566 | 3017.3443 | 3553.7489 | 61.5126 | 72.448
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.0445 | 103.5427 | 11.4484 | 4 | 3015.6469 | 3551.6174 | 61.478 | 72.4045 | 181.3966 | 0 | 314.3326 | 12685921.3621 | 1113833.382 | 13631051.6704 | 11345597.9096 | 0 | 384274.4071 | 0 | 15272664.7052 | 39736340.7086 | 27120869.0337 | 121290553.1787 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138097436.9315 | 162641477.4143 | 4216965.0343 | 45.7936 | 3015.6469 | 3551.6174 | 61.478 | 72.4045
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.1176 | 103.5747 | 11.4549 | 4 | 3014.3723 | 3550.0382 | 61.4521 | 72.3723 | 181.3903 | 0 | 307.0959 | 12688721.9482 | 1114074.422 | 13634422.9672 | 11349755.0582 | 0 | 380206.3946 | 0 | 15275200.5082 | 39742938.3477 | 27125372.0581 | 121310691.7041 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138117575.4569 | 162661615.9397 | 5623413.2519 | 45.8197 | 3014.3723 | 3550.0382 | 61.4521 | 72.3723
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.1714 | 103.5982 | 11.4598 | 4 | 3013.4155 | 3548.8553 | 61.4326 | 72.3482 | 181.3858 | 0 | 295.8027 | 12690777.1545 | 1114251.3081 | 13636897.0428 | 11352806.9999 | 0 | 377123.4267 | 0 | 15277023.8135 | 39747682.2141 | 27128609.8443 | 121325171.8038 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138132055.5567 | 162676096.0395 | 7498942.0933 | 45.839 | 3013.4155 | 3548.8553 | 61.4326 | 72.3482
1 | 4500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.2297 | 103.6238 | 11.4641 | 4 | 3012.6975 | 3547.9335 | 61.4179 | 72.3294 | 181.3808 | 0 | 303.4753 | 12693014.0284 | 1114443.8289 | 13639589.8637 | 11356123.1923 | 0 | 375028.6142 | 0 | 15279497.8157 | 39754119.0606 | 27133003.1243 | 121344819.5281 | 961560.8286 | 15845322.9242 | 15845322.9242 | 1478867.319 | 7219850.2396 | 0 | 138151703.281 | 162695743.7638 | 10000000 | 45.8565 | 3012.6975 | 3547.9335 | 61.4179 | 72.3294
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.78939 | 0.17119 | 0.0067665 | 4 | 674629.628 | 1605753.8263 | 13753.2375 | 32735.4637 | 117.3313 | 0 | 37.502 | 116008.4159 | 7957.9212 | 83323.6827 | 54608.0024 | 0 | 55417.9602 | 0 | 123753.2332 | 321980.5274 | 219758.326 | 982808.0691 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18259520.4211 | 43461320.9426 | 100 | 0.027066 | 674629.628 | 1605753.8263 | 13753.2375 | 32735.4637
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.26481 | 0.015546 | 4 | 299065.9873 | 704345.4255 | 6096.8647 | 14359.0342 | 129.6979 | 0 | 61.1831 | 167653.1308 | 12445.3005 | 117109.8985 | 67554.8619 | 0 | 61529.3533 | 0 | 166254.0925 | 432559.0453 | 295230.4366 | 1320336.1194 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 18597048.4714 | 43798848.9929 | 133.3521 | 0.062184 | 299065.9873 | 704345.4255 | 6096.8647 | 14359.0342
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3128 | 0.39964 | 0.029547 | 4 | 161123.8144 | 374357.2955 | 3284.7269 | 7631.7798 | 141.0279 | 0 | 60.531 | 235743.8356 | 18912.377 | 161519.0359 | 85332.339 | 0 | 68775.4958 | 0 | 222410.4025 | 578666.2447 | 394951.6024 | 1766311.333 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19043023.685 | 44244824.2065 | 177.8279 | 0.11819 | 161123.8144 | 374357.2955 | 3284.7269 | 7631.7798
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.58433 | 0.050589 | 4 | 96921.4181 | 221462.8012 | 1975.8742 | 4514.8188 | 150.7345 | 0 | 277.1221 | 321996.3097 | 27954.7363 | 217349.7822 | 110333.2598 | 0 | 76582.2814 | 0 | 294144.3841 | 765303.3501 | 522335.2618 | 2335999.3655 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 19612711.7174 | 44814512.239 | 237.1374 | 0.20236 | 96921.4181 | 221462.8012 | 1975.8742 | 4514.8188
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.196 | 0.86846 | 0.08134 | 4 | 62635.1249 | 140093.3778 | 1276.9017 | 2855.993 | 159.2436 | 0 | 366.6905 | 433495.4052 | 39206.8693 | 297464.0132 | 144372.9801 | 0 | 87070.1601 | 0 | 390627.6769 | 1016333.0866 | 693668.2151 | 3102238.4066 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 20378950.7586 | 45580751.2801 | 316.2278 | 0.32536 | 62635.1249 | 140093.3778 | 1276.9017 | 2855.993
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8572 | 1.2654 | 0.12148 | 4 | 43853.9564 | 95716.9129 | 894.0222 | 1951.3187 | 166.313 | 0 | 479.8998 | 563821.7105 | 51025.3307 | 401979.8958 | 185310.7877 | 0 | 100070.631 | 0 | 507861.2587 | 1321350.8185 | 901849.0847 | 4033269.5176 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 21309981.8695 | 46511782.3911 | 421.6965 | 0.48593 | 43853.9564 | 95716.9129 | 894.0222 | 1951.3187
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.7365 | 1.7965 | 0.17514 | 4 | 32057.6659 | 68030.6672 | 653.5389 | 1386.8972 | 172.1512 | 0 | 67.4435 | 720531.3492 | 65213.3332 | 532079.362 | 239088.3327 | 0 | 116215.1849 | 0 | 652519.7492 | 1697722.5372 | 1158730.5164 | 5182100.3649 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 22458812.7168 | 47660613.2384 | 562.3413 | 0.70058 | 32057.6659 | 68030.6672 | 653.5389 | 1386.8972
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8742 | 2.4867 | 0.24518 | 4 | 24311.2443 | 50008.3927 | 495.6176 | 1019.4887 | 176.7681 | 0 | 83.3529 | 904958.2428 | 81878.7529 | 690129.3459 | 308213.8736 | 0 | 134729.9322 | 0 | 826764.9575 | 2151072.8266 | 1468151.4043 | 6565899.3358 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 23842611.6877 | 49044412.2093 | 749.8942 | 0.98072 | 24311.2443 | 50008.3927 | 495.6176 | 1019.4887
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.3869 | 3.4053 | 0.33835 | 4 | 18888.079 | 37509.4347 | 385.059 | 764.6806 | 180.4369 | 0 | 77.521 | 1128502.1057 | 102034.8516 | 887486.4185 | 399754.8477 | 0 | 157516.621 | 0 | 1043364.9893 | 2714621.6787 | 1852785.0756 | 8286066.5881 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 25562778.94 | 50764579.4616 | 1000 | 1.3534 | 18888.079 | 37509.4347 | 385.059 | 764.6806
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.3534 | 4.5891 | 0.45859 | 4 | 15069.372 | 28808.0828 | 307.2095 | 587.2917 | 183.0412 | 0 | 59.3184 | 1391954.8493 | 125732.0751 | 1126720.1309 | 518320.3596 | 0 | 184110.4521 | 0 | 1305266.7681 | 3396036.3837 | 2317864.6134 | 10366005.6323 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 27642717.9843 | 52844518.5058 | 1333.5214 | 1.8344 | 15069.372 | 28808.0828 | 307.2095 | 587.2917
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.9495 | 6.1907 | 0.62227 | 4 | 12162.3846 | 22287.296 | 247.9467 | 454.3567 | 185.6345 | 0 | 110.6888 | 1718703.9143 | 155044.5093 | 1431620.2535 | 675429.2866 | 0 | 215351.6333 | 0 | 1636498.3428 | 4257832.996 | 2906058.5095 | 12996539.4454 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 30273251.7973 | 55475052.3189 | 1778.2794 | 2.4891 | 12162.3846 | 22287.296 | 247.9467 | 454.3567
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.4138 | 8.3073 | 0.83794 | 4 | 10011.2424 | 17530.2212 | 204.0927 | 357.3773 | 187.4119 | 0 | 89.3142 | 2114907.6186 | 190483.5599 | 1811342.2983 | 884601.8733 | 0 | 254467.2195 | 0 | 2049763.0022 | 5333062.8674 | 3639924.9905 | 16278553.4298 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 33555265.7817 | 58757066.3033 | 2371.3737 | 3.3518 | 10011.2424 | 17530.2212 | 204.0927 | 357.3773
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.0011 | 11.1114 | 1.1238 | 4 | 8377.138 | 13983.545 | 170.7793 | 285.0735 | 188.7839 | 0 | 100.8922 | 2597277.2133 | 233493.2738 | 2285853.4661 | 1161538.838 | 0 | 301866.1521 | 0 | 2566211.2879 | 6676755.3687 | 4557022.7328 | 20380018.3326 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 37656730.6846 | 62858531.2062 | 3162.2777 | 4.4952 | 8377.138 | 13983.545 | 170.7793 | 285.0735
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.0789 | 14.8277 | 1.5026 | 4 | 7119.7135 | 11312.6725 | 145.145 | 230.6241 | 189.8387 | 0 | 98.6817 | 3185373.4777 | 285751.5084 | 2879341.2406 | 1528348.1301 | 0 | 359568.4617 | 0 | 3212969.2992 | 8359487.046 | 5705521.6792 | 25516360.8429 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 42793073.1949 | 67994873.7164 | 4216.965 | 6.0105 | 7119.7135 | 11312.6725 | 145.145 | 230.6241
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.0884 | 19.7264 | 2.002 | 4 | 6143.8353 | 9290.842 | 125.2504 | 189.4064 | 190.6437 | 0 | 130.3185 | 3899240.3924 | 348955.5799 | 3618029.6938 | 2011732.4179 | 0 | 429313.5222 | 0 | 4019835.9264 | 10458788.4989 | 7138338.0571 | 31924234.0887 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 49200946.4406 | 74402746.9622 | 5623.4133 | 8.0082 | 6143.8353 | 9290.842 | 125.2504 | 189.4064
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 43.5636 | 26.1329 | 2.6552 | 4 | 5380.6398 | 7753.4986 | 109.6916 | 158.0656 | 191.2491 | 0 | 122.5237 | 4760089.3481 | 424881.3289 | 4530890.379 | 2643880.2477 | 0 | 513053.0597 | 0 | 5020389.8017 | 13062024.4405 | 8915100.0784 | 39870308.6839 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 57147021.0359 | 82348821.5574 | 7498.9421 | 10.6209 | 5380.6398 | 7753.4986 | 109.6916 | 158.0656
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.0669 | 34.3735 | 3.4953 | 4 | 4782.5029 | 6585.0759 | 97.4978 | 134.2457 | 191.6518 | 0 | 106.9148 | 5783059.1568 | 514746.5596 | 5641739.7348 | 3458344.1476 | 0 | 612272.1096 | 0 | 6243963.0662 | 16245511.0854 | 11087895.1276 | 49587530.9875 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 66864243.3395 | 92066043.861 | 10000 | 13.981 | 4782.5029 | 6585.0759 | 97.4978 | 134.2457
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 74.1043 | 44.6757 | 4.5437 | 4 | 4317.5794 | 5704.2256 | 88.0197 | 116.2884 | 191.7398 | 0 | 113.7443 | 6968068.7393 | 618424.0615 | 6958100.1781 | 4484349.8089 | 0 | 728481.9344 | 0 | 7705395.6417 | 20047858.8657 | 13683075.6182 | 61193754.8479 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 78470467.1999 | 103672267.7214 | 13335.2143 | 18.1746 | 4317.5794 | 5704.2256 | 88.0197 | 116.2884
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 94.84 | 56.9288 | 5.7853 | 4 | 3965.4055 | 5054.4481 | 80.8402 | 103.0418 | 191.3118 | 0 | 143.6966 | 8280293.5741 | 732772.0582 | 8446937.3615 | 5728123.7286 | 0 | 861471.6859 | 0 | 9379343.3793 | 24403127.505 | 16655635.9563 | 74487705.2489 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 91764417.6008 | 116966218.1224 | 17782.7941 | 23.1412 | 3965.4055 | 5054.4481 | 80.8402 | 103.0418
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 118.8379 | 70.53 | 7.1525 | 4 | 3709.6996 | 4590.5753 | 75.6272 | 93.5851 | 190.2068 | 0 | 122.7318 | 9645990.8185 | 851330.3859 | 10026115.0516 | 7157026.6544 | 0 | 1008687.7952 | 0 | 11188768.7752 | 29110881.2209 | 19868774.6021 | 88857575.3038 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 106134287.6557 | 131336088.1773 | 23713.7371 | 28.6099 | 3709.6996 | 4590.5753 | 75.6272 | 93.5851
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 142.0897 | 83.0077 | 8.4262 | 4 | 3532.0139 | 4279.7385 | 72.0049 | 87.2483 | 188.6889 | 0 | 140.3478 | 10834285.9042 | 954156.1484 | 11421640.2386 | 8528411.3141 | 0 | 1119197.8656 | 0 | 12814499.6736 | 33340699.5355 | 22755712.5159 | 101768603.1959 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 119045315.5479 | 144247116.0694 | 31622.7766 | 33.7047 | 3532.0139 | 4279.7385 | 72.0049 | 87.2483
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 153.3406 | 88.8524 | 9.1733 | 4 | 3396.7915 | 4083.6138 | 69.2482 | 83.25 | 187.9156 | 0 | 191.6354 | 11373275.2567 | 1000702.4028 | 12060603.387 | 9188168.4935 | 0 | 1041154.7188 | 0 | 13518922.661 | 35173463.6515 | 24006611.6845 | 107362902.2559 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 124639614.6079 | 149841415.1294 | 42169.6503 | 36.6933 | 3396.7915 | 4083.6138 | 69.2482 | 83.25
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.7823 | 93.6278 | 9.8062 | 4 | 3292.1253 | 3934.6231 | 67.1144 | 80.2126 | 187.2218 | 0 | 210.9316 | 11806253.8488 | 1038053.6227 | 12576431.5423 | 9738721.6109 | 0 | 955117.8779 | 0 | 14084685.616 | 36645462.8067 | 25011281.3545 | 111856008.2799 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 129132720.6319 | 154334521.1535 | 56234.1325 | 39.2247 | 3292.1253 | 3934.6231 | 67.1144 | 80.2126
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 170.4575 | 97.4204 | 10.3256 | 4 | 3211.5487 | 3821.7293 | 65.4718 | 77.9111 | 186.6295 | 0 | 260.3015 | 12145699.4708 | 1067311.9216 | 12982355.9802 | 10184555.6384 | 0 | 868341.5166 | 0 | 14526823.1658 | 37795814.0162 | 25796419.6923 | 115367321.4019 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 132644033.7538 | 157845834.2754 | 74989.4209 | 41.3022 | 3211.5487 | 3821.7293 | 65.4718 | 77.9111
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.4808 | 100.339 | 10.7387 | 4 | 3149.7792 | 3736.4818 | 64.2125 | 76.1732 | 186.1474 | 0 | 309.3917 | 12404387.5705 | 1089595.413 | 13292583.7672 | 10533424.6288 | 0 | 785381.003 | 0 | 14861095.2292 | 38665521.3566 | 26390012.8229 | 118022001.7914 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 135298714.1433 | 160500514.6649 | 100000 | 42.955 | 3149.7792 | 3736.4818 | 64.2125 | 76.1732
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 181.1903 | 102.5843 | 11.0642 | 4 | 3102.5824 | 3672.0281 | 63.2503 | 74.8593 | 185.7604 | 0 | 296.2002 | 12601954.7042 | 1106605.9295 | 13530013.6997 | 10805358.8898 | 0 | 710860.6166 | 0 | 15114369.5975 | 39324489.3092 | 26839771.991 | 120033424.7375 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 137310137.0894 | 162511937.611 | 133352.1432 | 44.2567 | 3102.5824 | 3672.0281 | 63.2503 | 74.8593
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.7124 | 104.2419 | 11.3124 | 4 | 3066.62 | 3623.5723 | 62.5172 | 73.8714 | 185.4651 | 0 | 300.56 | 12747029.997 | 1119092.5532 | 13704632.4926 | 11008270.9932 | 0 | 644835.0186 | 0 | 15297305.8113 | 39800451.8121 | 27164626.1793 | 121486244.8572 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 138762957.2092 | 163964757.7307 | 177827.941 | 45.2495 | 3066.62 | 3623.5723 | 62.5172 | 73.8714
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.3434 | 105.4682 | 11.5007 | 4 | 3039.2842 | 3587.114 | 61.9599 | 73.1282 | 185.2412 | 0 | 322.4404 | 12853940.2557 | 1128291.98 | 13833459.952 | 11159700.0118 | 0 | 588496.9659 | 0 | 15429916.7745 | 40145478.3361 | 27400113.8715 | 122539398.1475 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 139816110.4994 | 165017911.021 | 237137.3706 | 46.003 | 3039.2842 | 3587.114 | 61.9599 | 73.1282
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.2996 | 106.3733 | 11.6429 | 4 | 3018.5455 | 3559.6885 | 61.5371 | 72.5691 | 185.0729 | 0 | 304.942 | 12932623.6218 | 1135061.2796 | 13928352.204 | 11272214.0307 | 0 | 541614.9146 | 0 | 15525847.7598 | 40395071.0816 | 27570466.0489 | 123301250.941 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 140577963.2929 | 165779763.8145 | 316227.766 | 46.5714 | 3018.5455 | 3559.6885 | 61.5371 | 72.5691
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.7734 | 107.0511 | 11.7506 | 4 | 3002.8363 | 3539.0192 | 61.2169 | 72.1477 | 184.9452 | 0 | 304.5623 | 12991425.9443 | 1140119.4783 | 13999311.011 | 11356836.6095 | 0 | 503656.8228 | 0 | 15596626.4477 | 40579222.709 | 27696153.3185 | 123863352.3412 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 141140064.6931 | 166341865.2147 | 421696.5034 | 47.0023 | 3002.8363 | 3539.0192 | 61.2169 | 72.1477
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.8017 | 107.5218 | 11.8286 | 4 | 2990.9542 | 3523.5994 | 60.9746 | 71.8333 | 184.8554 | 0 | 293.7821 | 13032191.2175 | 1143625.777 | 14048525.4405 | 11415764.2552 | 0 | 472386.3073 | 0 | 15643872.269 | 40702146.6446 | 27780051.4304 | 124238563.3416 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 141515275.6936 | 166717076.2151 | 562341.3252 | 47.3144 | 2990.9542 | 3523.5994 | 60.9746 | 71.8333
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.5392 | 107.8582 | 11.886 | 4 | 2981.9809 | 3512.0539 | 60.7917 | 71.598 | 184.7907 | 0 | 313.4217 | 13061303.5561 | 1146129.6116 | 14083682.4774 | 11458009.7616 | 0 | 447340.942 | 0 | 15676621.876 | 40787354.4041 | 27838207.4771 | 124498650.1059 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 141775362.4578 | 166977162.9794 | 749894.2093 | 47.544 | 2981.9809 | 3512.0539 | 60.7917 | 71.598
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.0728 | 108.1011 | 11.9284 | 4 | 2975.2126 | 3503.4019 | 60.6537 | 71.4216 | 184.7437 | 0 | 312.8441 | 13082304.2544 | 1147935.7075 | 14109049.1853 | 11488570.8644 | 0 | 427581.8623 | 0 | 15699622.3308 | 40847196.8694 | 27879051.1894 | 124681312.2635 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 141958024.6155 | 167159825.137 | 1000000 | 47.7136 | 2975.2126 | 3503.4019 | 60.6537 | 71.4216
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.687 | 107.4654 | 11.8863 | 4 | 2969.7706 | 3499.83 | 60.5428 | 71.3488 | 184.8621 | 0 | 576.6088 | 13027313.1428 | 1143206.2194 | 14042635.391 | 11409110.7743 | 0 | 387939.4208 | 0 | 15603979.9298 | 40598354.961 | 27709211.4737 | 123921751.3129 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 141198463.6648 | 166400264.1864 | 1333521.4322 | 47.5452 | 2969.7706 | 3499.83 | 60.5428 | 71.3488
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.1982 | 108.6132 | 12.0032 | 4 | 2965.8759 | 3490.7728 | 60.4634 | 71.1641 | 184.6454 | 0 | 294.2616 | 13126538.1128 | 1151739.6505 | 14162494.3984 | 11553032.6724 | 0 | 404395.0873 | 0 | 15755297.9694 | 40992053.4603 | 27977918.7891 | 125123470.1402 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142400182.4921 | 167601983.0137 | 1778279.41 | 48.0129 | 2965.8759 | 3490.7728 | 60.4634 | 71.1641
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.4003 | 108.7046 | 12.0201 | 4 | 2963.0402 | 3487.1999 | 60.4056 | 71.0913 | 184.6274 | 0 | 307.5348 | 13134429.0336 | 1152418.2048 | 14172030.7061 | 11564598.0972 | 0 | 395366.0111 | 0 | 15763348.4006 | 41012999.0309 | 27992214.5715 | 125187404.0558 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142464116.4077 | 167665916.9293 | 2371373.7057 | 48.0804 | 2963.0402 | 3487.1999 | 60.4056 | 71.0913
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.542 | 108.7687 | 12.0324 | 4 | 2960.9089 | 3484.5344 | 60.3621 | 71.0369 | 184.6147 | 0 | 294.544 | 13139955.7046 | 1152893.4468 | 14178710.1686 | 11572707.0617 | 0 | 388378.2968 | 0 | 15768731.4246 | 41027004.5553 | 28001773.6296 | 125230154.288 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142506866.6399 | 167708667.1615 | 3162277.6602 | 48.1294 | 2960.9089 | 3484.5344 | 60.3621 | 71.0369
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.6392 | 108.8126 | 12.0412 | 4 | 2959.3078 | 3482.5496 | 60.3295 | 70.9965 | 184.606 | 0 | 286.239 | 13143743.9895 | 1153219.2008 | 14183288.8255 | 11578271.2601 | 0 | 382969.1292 | 0 | 15772182.038 | 41035982.3435 | 28007901.1545 | 125257557.9411 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142534270.293 | 167736070.8146 | 4216965.0343 | 48.1647 | 2959.3078 | 3482.5496 | 60.3295 | 70.9965
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.7272 | 108.8523 | 12.0484 | 4 | 2958.1055 | 3481.0323 | 60.305 | 70.9656 | 184.5982 | 0 | 284.8951 | 13147174.4512 | 1153514.1836 | 14187435.1347 | 11583306.4071 | 0 | 379074.5141 | 0 | 15775696.8294 | 41045127.1097 | 28014142.6454 | 125285471.2751 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142562183.6271 | 167763984.1486 | 5623413.2519 | 48.1937 | 2958.1055 | 3481.0323 | 60.305 | 70.9656
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.7855 | 108.8787 | 12.0536 | 4 | 2957.203 | 3479.9076 | 60.2866 | 70.9426 | 184.593 | 0 | 275.4568 | 13149446.7538 | 1153709.5761 | 14190181.6754 | 11586644.9952 | 0 | 376038.4102 | 0 | 15777848.3501 | 41050724.9254 | 28017963.2696 | 125302557.9558 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142579270.3077 | 167781070.8293 | 7498942.0933 | 48.2142 | 2957.203 | 3479.9076 | 60.2866 | 70.9426
1 | 4600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.8218 | 108.895 | 12.0571 | 4 | 2956.5257 | 3479.0773 | 60.2728 | 70.9257 | 184.5897 | 0 | 305.3154 | 13150857.9116 | 1153830.9194 | 14191887.3744 | 11588721.3261 | 0 | 373655.5302 | 0 | 15778991.6941 | 41053699.6717 | 28019993.5951 | 125311638.0226 | 961560.8286 | 16315151.5233 | 16315151.5233 | 1478867.319 | 7407781.6792 | 0 | 142588350.3745 | 167790150.8961 | 10000000 | 48.2283 | 2956.5257 | 3479.0773 | 60.2728 | 70.9257
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.81347 | 0.18385 | 0.0080465 | 4 | 583575.5345 | 1387273.4206 | 11896.9766 | 28281.4451 | 120.0127 | 0 | 44.5617 | 123718.7611 | 8628.0979 | 88053.7695 | 56231.1928 | 0 | 56089.0233 | 0 | 129761.1294 | 337611.8411 | 230427.0188 | 1030520.834 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 18782921.8759 | 44650686.5634 | 100 | 0.032186 | 583575.5345 | 1387273.4206 | 11896.9766 | 28281.4451
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0498 | 0.28577 | 0.017927 | 4 | 266995.7847 | 627734.0909 | 5443.0702 | 12797.2085 | 132.7527 | 0 | 46.7461 | 179473.2344 | 13591.7732 | 124211.2024 | 70112.1539 | 0 | 62458.5365 | 0 | 175440.2912 | 456459.6498 | 311543.0903 | 1393289.9317 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19145690.9736 | 45013455.6611 | 133.3521 | 0.071708 | 266995.7847 | 627734.0909 | 5443.0702 | 12797.2085
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.42509 | 0.033059 | 4 | 148222.4676 | 343839.5383 | 3021.7155 | 7009.6341 | 143.8599 | 0 | 62.912 | 249496.4671 | 20445.8519 | 169356.7723 | 88459.5713 | 0 | 68916.9257 | 0 | 232703.4794 | 605446.7194 | 413229.8267 | 1848055.6138 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 19600456.6557 | 45468221.3432 | 177.8279 | 0.13224 | 148222.4676 | 343839.5383 | 3021.7155 | 7009.6341
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7487 | 0.63037 | 0.057137 | 4 | 88522.8042 | 201706.489 | 1804.6571 | 4112.0596 | 154.1132 | 0 | 276.4234 | 345389.1234 | 30973.8271 | 230338.2551 | 116047.3716 | 0 | 77702.2602 | 0 | 312175.8266 | 812217.4648 | 554355.1091 | 2479199.238 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 20231600.2799 | 46099364.9674 | 237.1374 | 0.22855 | 88522.8042 | 201706.489 | 1804.6571 | 4112.0596
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2543 | 0.94102 | 0.08926 | 4 | 58866.6065 | 131317.209 | 1200.0754 | 2677.0789 | 162.4859 | 0 | 365.3047 | 458460.2196 | 41472.07 | 317185.0965 | 149381.2433 | 0 | 87768.7396 | 0 | 411164.2739 | 1069765.0993 | 730136.6617 | 3265333.4038 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 21017734.4457 | 46885499.1333 | 316.2278 | 0.35704 | 58866.6065 | 131317.209 | 1200.0754 | 2677.0789
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.935 | 1.3644 | 0.13229 | 4 | 41554.5137 | 90440.0383 | 847.145 | 1843.7425 | 169.6827 | 0 | 485.839 | 594333.6453 | 53789.7745 | 426964.3775 | 191656.2446 | 0 | 100971.1551 | 0 | 533408.9268 | 1387820.6104 | 947216.0834 | 4236160.8176 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 21988561.8595 | 47856326.547 | 421.6965 | 0.52915 | 41554.5137 | 90440.0383 | 847.145 | 1843.7425
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8265 | 1.9226 | 0.18911 | 4 | 30629.1596 | 64825.9229 | 624.4168 | 1321.5641 | 175.546 | 0 | 81.8554 | 755596.4871 | 68384.5646 | 561751.2622 | 246417.6554 | 0 | 116718.4958 | 0 | 682058.7014 | 1774576.8315 | 1211185.1514 | 5416689.1495 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 23169090.1914 | 49036854.8789 | 562.3413 | 0.75644 | 30629.1596 | 64825.9229 | 624.4168 | 1321.5641
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9863 | 2.6519 | 0.2636 | 4 | 23332.2397 | 47865.7638 | 475.6593 | 975.8083 | 180.2225 | 0 | 65.1353 | 946737.8108 | 85649.4339 | 726569.3913 | 317219.2919 | 0 | 135056.6883 | 0 | 862380.7203 | 2243737.7356 | 1531397.1088 | 6848748.1808 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 24601149.2227 | 50468913.9103 | 749.8942 | 1.0544 | 23332.2397 | 47865.7638 | 475.6593 | 975.8083
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.499 | 3.6042 | 0.36112 | 4 | 18240.3655 | 36148.4067 | 371.8545 | 736.9342 | 183.8827 | 0 | 92.1522 | 1174431.7053 | 106170.4756 | 928713.9595 | 409296.2868 | 0 | 156555.397 | 0 | 1082315.4515 | 2815962.7913 | 1921952.4673 | 8595398.5344 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 26347799.5763 | 52215564.2638 | 1000 | 1.4445 | 18240.3655 | 36148.4067 | 371.8545 | 736.9342
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.4869 | 4.8439 | 0.48799 | 4 | 14593.211 | 27845.3609 | 297.5023 | 567.6653 | 186.5039 | 0 | 93.4355 | 1445920.4165 | 130579.0392 | 1176495.333 | 529829.1764 | 0 | 182527.1304 | 0 | 1351486.9272 | 3516291.7566 | 2399941.3764 | 10733071.1557 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 28485472.1977 | 54353236.8852 | 1333.5214 | 1.952 | 14593.211 | 27845.3609 | 297.5023 | 567.6653
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.1347 | 6.5396 | 0.66237 | 4 | 11783.3291 | 21546.6863 | 240.2191 | 439.2583 | 189.1976 | 0 | 107.2731 | 1786420.1022 | 161109.2356 | 1495796.3121 | 691155.8065 | 0 | 213637.5028 | 0 | 1695766.3941 | 4412036.3078 | 3011305.4384 | 13467227.0994 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 31219628.1413 | 57087392.8288 | 1778.2794 | 2.6495 | 11783.3291 | 21546.6863 | 240.2191 | 439.2583
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.6574 | 8.7717 | 0.89133 | 4 | 9709.3376 | 16964.687 | 197.938 | 345.8481 | 191.015 | 0 | 92.9439 | 2197712.927 | 197876.9471 | 1891911.2521 | 905179.9943 | 0 | 252355.2335 | 0 | 2123564.178 | 5525078.3884 | 3770979.5291 | 16864658.4495 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 34617059.4914 | 60484824.1789 | 2371.3737 | 3.5653 | 9709.3376 | 16964.687 | 197.938 | 345.8481
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.2984 | 11.7138 | 1.1935 | 4 | 8135.7953 | 13554.3107 | 165.8592 | 276.323 | 192.4124 | 0 | 91.4119 | 2696057.4626 | 242283.9377 | 2384468.1639 | 1186994.5784 | 0 | 298661.2688 | 0 | 2655301.5105 | 6908549.853 | 4715227.2312 | 21087544.0062 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 38839945.0481 | 64707709.7356 | 3162.2777 | 4.774 | 8135.7953 | 13554.3107 | 165.8592 | 276.323
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.4662 | 15.6254 | 1.595 | 4 | 6919.6288 | 10974.1592 | 141.066 | 223.7231 | 193.4914 | 0 | 113.8931 | 3305764.973 | 296427.4988 | 3002609.1507 | 1561569.3749 | 0 | 355563.501 | 0 | 3323554.4543 | 8647206.9353 | 5901896.4157 | 26394592.3036 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 44146993.3455 | 70014758.033 | 4216.965 | 6.38 | 6919.6288 | 10974.1592 | 141.066 | 223.7231
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 33.5636 | 20.7623 | 2.1226 | 4 | 5976.438 | 9023.1486 | 121.8378 | 183.9491 | 194.3126 | 0 | 117.815 | 4043310.8075 | 361683.4896 | 3769235.8409 | 2053380.2794 | 0 | 423727.5202 | 0 | 4154021.7956 | 10807912.6052 | 7376622.4334 | 32989894.7718 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 50742295.8137 | 76610060.5012 | 5623.4133 | 8.4904 | 5976.438 | 9023.1486 | 121.8378 | 183.9491
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.1775 | 27.4951 | 2.8139 | 4 | 5236.6191 | 7534.8585 | 106.7556 | 153.6083 | 194.9314 | 0 | 94.0439 | 4934925.5183 | 440266.4325 | 4718873.4378 | 2698069.2574 | 0 | 506164.9922 | 0 | 5186336.8588 | 13493784.6427 | 9209785.2882 | 41188206.4278 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 58940607.4698 | 84808372.1573 | 7498.9421 | 11.2555 | 5236.6191 | 7534.8585 | 106.7556 | 153.6083
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 57.8368 | 36.1395 | 3.7013 | 4 | 4656.9272 | 6404.1219 | 94.9378 | 130.5567 | 195.3371 | 0 | 114.9115 | 5992697.5545 | 533119.2722 | 5872456.7156 | 3527236.5788 | 0 | 603605.8258 | 0 | 6446355.2193 | 16772093.9513 | 11447298.7539 | 51194863.8714 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 68947264.9133 | 94815029.6008 | 10000 | 14.8053 | 4656.9272 | 6404.1219 | 94.9378 | 130.5567
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 75.04 | 46.9218 | 4.8064 | 4 | 4206.5517 | 5552.0402 | 85.7562 | 113.1858 | 195.4087 | 0 | 109.1725 | 7215585.2189 | 640027.8147 | 7236582.1986 | 4569775.9169 | 0 | 717662.4492 | 0 | 7948057.1033 | 20679214.2122 | 14113988.6152 | 63120893.5291 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 80873294.571 | 106741059.2585 | 13335.2143 | 19.2256 | 4206.5517 | 5552.0402 | 85.7562 | 113.1858
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 95.9265 | 59.7062 | 6.111 | 4 | 3865.7311 | 4923.9718 | 78.8082 | 100.3818 | 194.9375 | 0 | 127.0737 | 8566081.3305 | 757617.7519 | 8775043.2159 | 5830419.2578 | 0 | 848274.6847 | 0 | 9663200.1339 | 25141664.5536 | 17159702.6674 | 76742003.5958 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 94494404.6377 | 120362169.3252 | 17782.7941 | 24.4441 | 3865.7311 | 4923.9718 | 78.8082 | 100.3818
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 120.0358 | 73.8493 | 7.5426 | 4 | 3618.5292 | 4475.9204 | 73.7686 | 91.2477 | 193.7618 | 0 | 138.74 | 9967522.0101 | 879182.2522 | 10401853.0918 | 7274559.8085 | 0 | 993278.965 | 0 | 11511394.4898 | 29950287.1507 | 20441686.3972 | 91419764.1653 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 109172165.2072 | 135039929.8947 | 23713.7371 | 30.1703 | 3618.5292 | 4475.9204 | 73.7686 | 91.2477
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 145.466 | 87.9575 | 8.9627 | 4 | 3447.0575 | 4168.5987 | 70.2729 | 84.9825 | 192.0317 | 0 | 138.9711 | 11291414.5596 | 993636.6558 | 11963329.8753 | 8784112.985 | 0 | 1135539.5396 | 0 | 13325533.11 | 34670303.7094 | 23663194.6852 | 105827065.1198 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 123579466.1617 | 149447230.8492 | 31622.7766 | 35.8507 | 3447.0575 | 4168.5987 | 70.2729 | 84.9825
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 156.6346 | 93.932 | 9.7299 | 4 | 3319.4073 | 3984.0521 | 67.6706 | 81.2203 | 191.218 | 0 | 167.6514 | 11833624.1164 | 1040413.5664 | 12609113.0213 | 9443166.0624 | 0 | 1053260.1472 | 0 | 14032034.9963 | 36508476.6943 | 24917785.518 | 111437874.1222 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 129190275.1642 | 155058039.8517 | 42169.6503 | 38.9197 | 3319.4073 | 3984.0521 | 67.6706 | 81.2203
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 165.9929 | 98.8055 | 10.3777 | 4 | 3220.6613 | 3843.8172 | 65.6575 | 78.3614 | 190.4913 | 0 | 217.4899 | 12268738.3261 | 1077912.0261 | 13129815.0039 | 9992611.8761 | 0 | 964142.4403 | 0 | 14598955.6723 | 37983488.0017 | 25924511.0438 | 115940174.3904 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 133692575.4323 | 159560340.1199 | 56234.1325 | 41.5109 | 3220.6613 | 3843.8172 | 65.6575 | 78.3614
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.5392 | 102.6444 | 10.9058 | 4 | 3144.6604 | 3737.644 | 64.1082 | 76.1969 | 189.8769 | 0 | 233.8615 | 12607230.8136 | 1107060.1083 | 13536360.2354 | 10433975.8354 | 0 | 874480.195 | 0 | 15038051.8032 | 39125926.0634 | 26704248.4956 | 119427333.5499 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 137179734.5919 | 163047499.2794 | 74989.4209 | 43.6231 | 3144.6604 | 3737.644 | 64.1082 | 76.1969
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.4823 | 105.6085 | 11.3261 | 4 | 3086.4006 | 3657.3792 | 62.9205 | 74.5606 | 189.376 | 0 | 307.4834 | 12866146.7346 | 1129342.1993 | 13848176.6416 | 10780362.8631 | 0 | 789825.1748 | 0 | 15371402.9092 | 39993237.2616 | 27296206.2099 | 122074699.9941 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 139827101.0361 | 165694865.7236 | 100000 | 45.3043 | 3086.4006 | 3657.3792 | 62.9205 | 74.5606
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.1233 | 107.8867 | 11.6566 | 4 | 3041.8968 | 3596.6866 | 62.0132 | 73.3233 | 188.9745 | 0 | 303.8282 | 13063764.3228 | 1146341.2456 | 14086654.5925 | 11050384.3656 | 0 | 714098.4257 | 0 | 15623884.7513 | 40650143.2234 | 27744558.0269 | 124079828.9537 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 141832229.9956 | 167699994.6831 | 133352.1432 | 46.6262 | 3041.8968 | 3596.6866 | 62.0132 | 73.3233
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.6017 | 109.5712 | 11.9086 | 4 | 3007.9765 | 3551.0256 | 61.3217 | 72.3925 | 188.6678 | 0 | 314.55 | 13209131.4086 | 1158841.4743 | 14262342.1236 | 11251932.6737 | 0 | 647354.1108 | 0 | 15806544.6985 | 41125386.9373 | 28068921.6269 | 125530455.0536 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 143282856.0955 | 169150620.783 | 177827.941 | 47.6343 | 3007.9765 | 3551.0256 | 61.3217 | 72.3925
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.1692 | 110.8026 | 12.0984 | 4 | 2982.1906 | 3516.7199 | 60.796 | 71.6931 | 188.4381 | 0 | 291.9219 | 13314993.9993 | 1167942.4432 | 14390424.5105 | 11400554.1073 | 0 | 590142.0398 | 0 | 15936982.2691 | 41464758.7395 | 28300549.8553 | 126566347.9641 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 144318749.006 | 170186513.6935 | 237137.3706 | 48.3935 | 2982.1906 | 3516.7199 | 60.796 | 71.6931
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.0723 | 111.7086 | 12.2412 | 4 | 2962.6264 | 3490.9174 | 60.3971 | 71.1671 | 188.266 | 0 | 316.5669 | 13392676.6935 | 1174619.6053 | 14484486.2596 | 11510639.3779 | 0 | 542563.7622 | 0 | 16030944.4224 | 41709228.9882 | 28467405.8234 | 127312564.9325 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 145064965.9744 | 170932730.6619 | 316227.766 | 48.965 | 2962.6264 | 3490.9174 | 60.3971 | 71.1671
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.4406 | 112.3564 | 12.3467 | 4 | 2947.8076 | 3471.5866 | 60.095 | 70.773 | 188.1413 | 0 | 361.6966 | 13448108.6187 | 1179383.6044 | 14551643.853 | 11589748.4461 | 0 | 503273.7344 | 0 | 16096141.7201 | 41878858.9831 | 28583181.7805 | 127830340.7405 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 145582741.7824 | 171450506.4699 | 421696.5034 | 49.3868 | 2947.8076 | 3471.5866 | 60.095 | 70.773
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.4493 | 112.8321 | 12.4255 | 4 | 2936.6 | 3457.0573 | 59.8666 | 70.4768 | 188.0488 | 0 | 347.5463 | 13488749.897 | 1182876.124 | 14600902.1671 | 11648046.2701 | 0 | 471739.5924 | 0 | 16143002.4797 | 42000781.0671 | 28666396.1081 | 128202493.7056 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 145954894.7475 | 171822659.435 | 562341.3252 | 49.702 | 2936.6 | 3457.0573 | 59.8666 | 70.4768
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.2628 | 113.2144 | 12.4873 | 4 | 2928.134 | 3446.0154 | 59.694 | 70.2517 | 187.974 | 0 | 369.2879 | 13521385.421 | 1185680.4693 | 14640469.5516 | 11694981.6678 | 0 | 447648.9857 | 0 | 16181164.7772 | 42100071.537 | 28734163.894 | 128505566.3037 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 146257967.3456 | 172125732.0331 | 749894.2093 | 49.9492 | 2928.134 | 3446.0154 | 59.694 | 70.2517
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.777 | 113.4551 | 12.5296 | 4 | 2921.7456 | 3437.877 | 59.5637 | 70.0858 | 187.9265 | 0 | 364.1003 | 13541912.7415 | 1187444.276 | 14665362.5041 | 11724554.5406 | 0 | 427630.9807 | 0 | 16203292.9668 | 42157644.5471 | 28773458.6564 | 128681301.2131 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 146433702.2551 | 172301466.9426 | 1000000 | 50.1186 | 2921.7456 | 3437.877 | 59.5637 | 70.0858
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.9365 | 113.0584 | 12.5096 | 4 | 2916.5771 | 3433.5362 | 59.4584 | 69.9973 | 188.0016 | 0 | 331.7021 | 13508070.0908 | 1184536.3145 | 14624324.6978 | 11676142.8282 | 0 | 394635.1648 | 0 | 16141206.5475 | 41996108.4198 | 28663206.9303 | 128188230.9936 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 145940632.0356 | 171808396.7231 | 1333521.4322 | 50.0383 | 2916.5771 | 3433.5362 | 59.4584 | 69.9973
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.8977 | 113.9797 | 12.6058 | 4 | 2912.9515 | 3425.965 | 59.3845 | 69.8429 | 187.8236 | 0 | 350.3614 | 13586616.6611 | 1191285.2132 | 14719588.6763 | 11789028.5107 | 0 | 404553.0674 | 0 | 16259518.1302 | 42303930.8891 | 28873302.0907 | 129127823.2389 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 146880224.2808 | 172747988.9683 | 1778279.41 | 50.4232 | 2912.9515 | 3425.965 | 59.3845 | 69.8429
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.083 | 114.0659 | 12.6222 | 4 | 2910.2756 | 3422.6206 | 59.3299 | 69.7747 | 187.8062 | 0 | 335.4 | 13593951.8255 | 1191915.4153 | 14728488.2275 | 11799674.076 | 0 | 395305.2794 | 0 | 16266640.5812 | 42322462.0456 | 28885949.9857 | 129184387.4363 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 146936788.4782 | 172804553.1657 | 2371373.7057 | 50.489 | 2910.2756 | 3422.6206 | 59.3299 | 69.7747
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.2191 | 114.1291 | 12.6345 | 4 | 2908.2643 | 3420.1134 | 59.2889 | 69.7236 | 187.7935 | 0 | 337.9575 | 13599338.5784 | 1192378.2136 | 14735024.1739 | 11807498.0032 | 0 | 388242.3403 | 0 | 16271767.7107 | 42335801.7847 | 28895054.6318 | 129225105.4365 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 146977506.4784 | 172845271.1659 | 3162277.6602 | 50.5379 | 2908.2643 | 3420.1134 | 59.2889 | 69.7236
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.3265 | 114.1791 | 12.6439 | 4 | 2906.7534 | 3418.2216 | 59.2581 | 69.6851 | 187.7834 | 0 | 316.7322 | 13603588.5384 | 1192743.3419 | 14740181.0158 | 11813672.1045 | 0 | 382961.647 | 0 | 16275927.1926 | 42346623.9033 | 28902440.9501 | 129258138.6936 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 147010539.7355 | 172878304.423 | 4216965.0343 | 50.5755 | 2906.7534 | 3418.2216 | 59.2581 | 69.6851
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.3971 | 114.2118 | 12.6505 | 4 | 2905.6188 | 3416.819 | 59.235 | 69.6565 | 187.7768 | 0 | 333.7071 | 13606375.9448 | 1192982.8157 | 14743563.3153 | 11817726.5464 | 0 | 378840.0247 | 0 | 16278400.5723 | 42353059.1301 | 28906833.1246 | 129277781.474 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 147030182.5159 | 172897947.2035 | 5623413.2519 | 50.602 | 2905.6188 | 3416.819 | 59.235 | 69.6565
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.4554 | 114.2389 | 12.6557 | 4 | 2904.767 | 3415.757 | 59.2176 | 69.6348 | 187.7713 | 0 | 342.5579 | 13608681.8638 | 1193180.9227 | 14746361.4273 | 11821079.4057 | 0 | 375802.2833 | 0 | 16280591.3021 | 42358758.9595 | 28910723.3753 | 129295179.5395 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 147047580.5814 | 172915345.2689 | 7498942.0933 | 50.6228 | 2904.767 | 3415.757 | 59.2176 | 69.6348
1 | 4700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.4897 | 114.2548 | 12.6592 | 4 | 2904.1278 | 3414.9766 | 59.2046 | 69.6189 | 187.7681 | 0 | 329.7605 | 13610033.0175 | 1193297.0031 | 14748001.0067 | 11823047.852 | 0 | 373389.6965 | 0 | 16281629.7446 | 42361460.7739 | 28912567.4192 | 129303426.5135 | 961560.8286 | 16790840.2133 | 16790840.2133 | 1478867.319 | 7598057.1552 | 0 | 147055827.5555 | 172923592.243 | 10000000 | 50.6368 | 2904.1278 | 3414.9766 | 59.2046 | 69.6189
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.83292 | 0.19513 | 0.0093194 | 4 | 517885.8301 | 1229893.7635 | 10557.8031 | 25073.0479 | 122.3977 | 0 | 48.7261 | 130603.1097 | 9243.438 | 92197.1514 | 57617.3424 | 0 | 56316.713 | 0 | 134931.3242 | 351063.6275 | 239608.1394 | 1071580.8455 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19305530.6683 | 45847463.649 | 100 | 0.037278 | 517885.8301 | 1229893.7635 | 10557.8031 | 25073.0479
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.30093 | 0.020002 | 4 | 245951.6374 | 577700.6995 | 5014.0568 | 11777.2102 | 135.1342 | 0 | 51.4822 | 188241.4632 | 14486.7197 | 129239.7244 | 71935.9835 | 0 | 62209.0092 | 0 | 181784.031 | 472964.7596 | 322808.1669 | 1443669.8575 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 19677619.6802 | 46219552.6609 | 133.3521 | 0.080006 | 245951.6374 | 577700.6995 | 5014.0568 | 11777.2102
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3936 | 0.46059 | 0.037673 | 4 | 134033.816 | 310166.6998 | 2732.4606 | 6323.1677 | 147.2293 | 0 | 51.3983 | 268228.8574 | 22585.3613 | 180137.3627 | 93004.4404 | 0 | 70142.0725 | 0 | 247298.2568 | 643419.3363 | 439146.9179 | 1963962.6052 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20197912.428 | 46739845.4087 | 177.8279 | 0.15069 | 134033.816 | 310166.6998 | 2732.4606 | 6323.1677
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7875 | 0.68047 | 0.063152 | 4 | 82509.4179 | 187580.7614 | 1682.0661 | 3824.0875 | 157.0881 | 0 | 284.0763 | 365698.8741 | 33052.4283 | 244726.7972 | 120960.7306 | 0 | 77805.7304 | 0 | 328475.3786 | 854625.5556 | 583299.5025 | 2608644.9973 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 20842594.82 | 47384527.8007 | 237.1374 | 0.25261 | 82509.4179 | 187580.7614 | 1682.0661 | 3824.0875
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3126 | 1.0152 | 0.097411 | 4 | 55594.4123 | 123712.7816 | 1133.3673 | 2522.0524 | 165.7257 | 0 | 371.1267 | 483412.3813 | 43735.5196 | 337045.3119 | 154295.3721 | 0 | 88329.0627 | 0 | 431658.8826 | 1123087.8671 | 766530.5464 | 3428094.9438 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 21662044.7665 | 48203977.7472 | 316.2278 | 0.38964 | 55594.4123 | 123712.7816 | 1133.3673 | 2522.0524
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0128 | 1.4659 | 0.14343 | 4 | 39520.6021 | 85784.6868 | 805.6809 | 1748.8369 | 173.0487 | 0 | 497.0284 | 624919.0929 | 56559.9135 | 452185.081 | 197917.5902 | 0 | 101692.6306 | 0 | 558976.9802 | 1454343.4405 | 992619.2819 | 4439214.0108 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 22673163.8336 | 49215096.8142 | 421.6965 | 0.5737 | 39520.6021 | 85784.6868 | 805.6809 | 1748.8369
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.9191 | 2.0532 | 0.20364 | 4 | 29326.8088 | 61910.8851 | 597.8667 | 1262.1371 | 178.9507 | 0 | 54.5116 | 791200.458 | 71603.2504 | 592068.8742 | 253790.9244 | 0 | 117056.7329 | 0 | 712030.8935 | 1852558.3273 | 1264409.1247 | 5654718.5854 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 23888668.4081 | 50430601.3888 | 562.3413 | 0.81457 | 29326.8088 | 61910.8851 | 597.8667 | 1262.1371
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.0789 | 2.8081 | 0.28146 | 4 | 22508.2554 | 46083.3423 | 458.8612 | 939.4713 | 183.6116 | 0 | 78.1609 | 985559.4732 | 89151.6602 | 760621.2526 | 324945.1762 | 0 | 134301.8677 | 0 | 894885.9776 | 2328309.7474 | 1589119.2446 | 7106894.3993 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 25340844.222 | 51882777.2027 | 749.8942 | 1.1258 | 22508.2554 | 46083.3423 | 458.8612 | 939.4713
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.6259 | 3.8162 | 0.38526 | 4 | 17622.0941 | 34845.5903 | 359.2502 | 710.3745 | 187.3497 | 0 | 72.7725 | 1222586.7022 | 110504.4823 | 972165.9576 | 419600.9793 | 0 | 155834.2332 | 0 | 1123470.0183 | 2923038.5322 | 1995033.8607 | 8922234.7658 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 27156184.5886 | 53698117.5693 | 1000 | 1.541 | 17622.0941 | 34845.5903 | 359.2502 | 710.3745
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.6332 | 5.1115 | 0.51879 | 4 | 14142.8101 | 26933.091 | 288.3203 | 549.0675 | 189.9737 | 0 | 80.0484 | 1501712.5811 | 135587.6097 | 1228208.1185 | 542045.8367 | 0 | 181013.1673 | 0 | 1399541.2522 | 3641319.2529 | 2485275.2117 | 11114703.0301 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 29348652.8529 | 55890585.8335 | 1333.5214 | 2.0752 | 14142.8101 | 26933.091 | 288.3203 | 549.0675
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.3199 | 6.8947 | 0.70343 | 4 | 11433.7973 | 20866.8484 | 233.0934 | 425.3989 | 192.7544 | 0 | 103.2642 | 1854288.614 | 167184.3134 | 1560428.9115 | 706624.9876 | 0 | 211432.6745 | 0 | 1754984.2054 | 4566108.9057 | 3116463.1523 | 13937515.7645 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 32171465.5872 | 58713398.5679 | 1778.2794 | 2.8137 | 11433.7973 | 20866.8484 | 233.0934 | 425.3989
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 14.8937 | 9.2401 | 0.94564 | 4 | 9432.1614 | 16449.1195 | 192.2874 | 335.3376 | 194.6085 | 0 | 100.8783 | 2279949.6403 | 205215.2691 | 1972306.6556 | 925042.8011 | 0 | 249439.2484 | 0 | 2196461.9096 | 5714743.3326 | 3900429.7507 | 17443588.6074 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 35677538.4302 | 62219471.4108 | 2371.3737 | 3.7825 | 9432.1614 | 16449.1195 | 192.2874 | 335.3376
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.6079 | 12.3358 | 1.2656 | 4 | 7909.6228 | 13152.5018 | 161.2484 | 268.1315 | 196.0365 | 0 | 94.8884 | 2796523.9514 | 251219.0945 | 2485228.9906 | 1213135.106 | 0 | 295066.8822 | 0 | 2746057.8697 | 7144679.2829 | 4876390.4191 | 21808301.5965 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 40042251.4193 | 66584184.3999 | 3162.2777 | 5.0625 | 7909.6228 | 13152.5018 | 161.2484 | 268.1315
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 25.8559 | 16.4402 | 1.6898 | 4 | 6733.2316 | 10659.9895 | 137.266 | 217.3183 | 197.1369 | 0 | 82.6961 | 3426935.0565 | 307165.426 | 3127233.6933 | 1594939.6688 | 0 | 350766.0451 | 0 | 3434745.5569 | 8936503.376 | 6099347.1809 | 27277636.0033 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 45511585.8261 | 72053518.8068 | 4216.965 | 6.7592 | 6733.2316 | 10659.9895 | 137.266 | 217.3183
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.0849 | 21.8474 | 2.2487 | 4 | 5817.9143 | 8768.7329 | 118.6061 | 178.7625 | 197.9775 | 0 | 92.7112 | 4192042.558 | 374814.0244 | 3926023.6386 | 2097763.0116 | 0 | 418093.0673 | 0 | 4293407.157 | 11170564.7236 | 7624139.956 | 34096848.1365 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 52330797.9592 | 78872730.9399 | 5623.4133 | 8.9948 | 5817.9143 | 8768.7329 | 118.6061 | 178.7625
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 44.8205 | 28.9006 | 2.9779 | 4 | 5101.3154 | 7329.5652 | 103.9972 | 149.4231 | 198.6069 | 0 | 120.7754 | 5112729.5363 | 455901.2606 | 4910871.6016 | 2753646.2805 | 0 | 498591.1054 | 0 | 5355378.5159 | 13933596.3593 | 9509965.822 | 42530680.4816 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 60764630.3044 | 87306563.2851 | 7498.9421 | 11.9116 | 5101.3154 | 7329.5652 | 103.9972 | 149.4231
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 58.6527 | 37.9655 | 3.9147 | 4 | 4538.8179 | 6233.8513 | 92.5299 | 127.0855 | 199.0143 | 0 | 107.4808 | 6206403.3388 | 551834.1836 | 6108641.5785 | 3598408.7894 | 0 | 594280.006 | 0 | 6653231.4796 | 17310343.5444 | 11814665.1611 | 52837808.0814 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 71071757.9042 | 97613690.8848 | 10000 | 15.6586 | 4538.8179 | 6233.8513 | 92.5299 | 127.0855
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 76.0385 | 49.2435 | 5.0782 | 4 | 4102.1842 | 5408.857 | 83.6286 | 110.2669 | 199.0667 | 0 | 121.856 | 7467913.9812 | 662034.3535 | 7521640.2819 | 4658295.9066 | 0 | 706189.8599 | 0 | 8196269.0094 | 21325010.6765 | 14554757.9718 | 65092112.0407 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 83326061.8635 | 109867994.8442 | 13335.2143 | 20.3126 | 4102.1842 | 5408.857 | 83.6286 | 110.2669
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 97.0863 | 62.5671 | 6.4468 | 4 | 3772.2294 | 4801.5015 | 76.902 | 97.8851 | 198.5483 | 0 | 124.1699 | 8856550.8766 | 782850.476 | 9109837.0792 | 5936069.6275 | 0 | 834358.9907 | 0 | 9952670.1496 | 25894806.1558 | 17673737.2864 | 79040880.6418 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 97274830.4646 | 123816763.4453 | 17782.7941 | 25.7871 | 3772.2294 | 4801.5015 | 76.902 | 97.8851
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 121.281 | 77.2361 | 7.9415 | 4 | 3533.3394 | 4368.8855 | 72.0319 | 89.0656 | 197.3001 | 0 | 134.5492 | 10291404.6369 | 907215.6876 | 10781761.7744 | 7394386.8096 | 0 | 976640.8406 | 0 | 11837049.8021 | 30797575.4724 | 21019978.0868 | 94006013.1105 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 112239962.9332 | 138781895.9139 | 23713.7371 | 31.766 | 3533.3394 | 4368.8855 | 72.0319 | 89.0656
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 147.3615 | 92.1839 | 9.4481 | 4 | 3367.4268 | 4069.7368 | 68.6495 | 82.9671 | 195.4534 | 0 | 158.6571 | 11676011.2554 | 1026821.8321 | 12421034.8525 | 8951465.807 | 0 | 1126484.2274 | 0 | 13728709.01 | 35719284.6986 | 24379145.7647 | 109028957.4477 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 127262907.2704 | 153804840.2511 | 31622.7766 | 37.7923 | 3367.4268 | 4069.7368 | 68.6495 | 82.9671
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.987 | 99.1383 | 10.3016 | 4 | 3246.7667 | 3890.887 | 66.1897 | 79.321 | 194.4878 | 0 | 189.1354 | 12298227.0031 | 1080452.1466 | 13165181.7085 | 9700103.8542 | 0 | 1064537.2659 | 0 | 14550315.7715 | 37856936.9573 | 25838137.3556 | 115553892.0627 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 133787841.8854 | 160329774.8661 | 42169.6503 | 41.2065 | 3246.7667 | 3890.887 | 66.1897 | 79.321
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.2092 | 104.0718 | 10.9607 | 4 | 3153.5702 | 3758.9599 | 64.2898 | 76.6315 | 193.7325 | 0 | 202.7565 | 12732176.1183 | 1117814.2485 | 13686743.238 | 10244229.5772 | 0 | 971808.1748 | 0 | 15113580.8292 | 39322437.0958 | 26838371.3132 | 120027160.595 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 138261110.4177 | 164803043.3984 | 56234.1325 | 43.8427 | 3153.5702 | 3758.9599 | 64.2898 | 76.6315
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.6138 | 107.9416 | 11.4955 | 4 | 3081.87 | 3659.092 | 62.8281 | 74.5955 | 193.098 | 0 | 231.2708 | 13068516.2262 | 1146749.922 | 14092394.1244 | 10679685.4681 | 0 | 879327.5175 | 0 | 15548002.5707 | 40452713.3551 | 27609808.085 | 123477197.2689 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 141711147.0917 | 168253080.0723 | 74989.4209 | 45.9822 | 3081.87 | 3659.092 | 62.8281 | 74.5955
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.501 | 110.9579 | 11.9231 | 4 | 3026.919 | 3583.4423 | 61.7078 | 73.0533 | 192.5764 | 0 | 267.5582 | 13328324.5043 | 1169088.329 | 14406561.2532 | 11024724.0176 | 0 | 793535.7879 | 0 | 15881671.2179 | 41320850.7303 | 28202329.682 | 126127085.5222 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 144361035.345 | 170902968.3257 | 100000 | 47.6924 | 3026.919 | 3583.4423 | 61.7078 | 73.0533
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.9903 | 113.2217 | 12.2541 | 4 | 2984.9428 | 3526.4315 | 60.8521 | 71.8911 | 192.1685 | 0 | 311.6235 | 13522008.4308 | 1185734.0023 | 14641224.9962 | 11287353.5078 | 0 | 715730.2812 | 0 | 16127299.9752 | 41959926.3713 | 28638511.9387 | 128077789.5037 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 146311739.3264 | 172853672.3071 | 133352.1432 | 49.0166 | 2984.9428 | 3526.4315 | 60.8521 | 71.8911
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 190.423 | 114.9307 | 12.5095 | 4 | 2952.9592 | 3483.3952 | 60.2001 | 71.0137 | 191.8508 | 0 | 298.6705 | 13667500.5217 | 1198233.8782 | 14817753.0386 | 11487744.0691 | 0 | 648424.8427 | 0 | 16309665.9766 | 42434405.2986 | 28962353.5561 | 129526081.1814 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 147760031.0042 | 174301963.9849 | 177827.941 | 50.038 | 2952.9592 | 3483.3952 | 60.2001 | 71.0137
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.9607 | 116.1814 | 12.7018 | 4 | 2928.6403 | 3451.0461 | 59.7043 | 70.3542 | 191.6126 | 0 | 344.6098 | 13773596.3494 | 1207346.862 | 14946616.1626 | 11635594.0564 | 0 | 590909.4738 | 0 | 16440084.5327 | 42773727.6289 | 29193948.019 | 130561823.0848 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 148795772.9075 | 175337705.8882 | 237137.3706 | 50.8071 | 2928.6403 | 3451.0461 | 59.7043 | 70.3542
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.8024 | 117.0823 | 12.8447 | 4 | 2910.1877 | 3426.7816 | 59.3281 | 69.8596 | 191.4379 | 0 | 354.8454 | 13849823.2065 | 1213893.1546 | 15039270.5704 | 11742819.1387 | 0 | 542641.9685 | 0 | 16531494.7351 | 43011558.2249 | 29356272.2876 | 131287773.2863 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 149521723.109 | 176063656.0897 | 316227.766 | 51.3787 | 2910.1877 | 3426.7816 | 59.3281 | 69.8596
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.1519 | 117.7389 | 12.9513 | 4 | 2896.2097 | 3408.5527 | 59.0432 | 69.488 | 191.3089 | 0 | 346.7112 | 13905272.0452 | 1218654.4596 | 15106705.636 | 11821356.336 | 0 | 503194.079 | 0 | 16596521.1967 | 43180743.7392 | 29471744.8776 | 131804192.3692 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 150038142.192 | 176580075.1727 | 421696.5034 | 51.805 | 2896.2097 | 3408.5527 | 59.0432 | 69.488
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.1265 | 118.2112 | 13.03 | 4 | 2885.6371 | 3394.8852 | 58.8276 | 69.2093 | 191.2152 | 0 | 350.4548 | 13945097.5332 | 1222073.9062 | 15155158.9986 | 11878056.5347 | 0 | 471293.439 | 0 | 16641955.3606 | 43298954.1138 | 29552425.8872 | 132165015.7734 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 150398965.5961 | 176940898.5768 | 562341.3252 | 52.1198 | 2885.6371 | 3394.8852 | 58.8276 | 69.2093
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.8038 | 118.5383 | 13.0869 | 4 | 2877.6512 | 3384.6851 | 58.6648 | 69.0014 | 191.1497 | 0 | 362.4615 | 13972658.6478 | 1224440.1751 | 15188700.2374 | 11917450.9237 | 0 | 445508.2917 | 0 | 16672015.7275 | 43377165.0223 | 29605806.4393 | 132403745.4648 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 150637695.2876 | 177179628.2683 | 749894.2093 | 52.3474 | 2877.6512 | 3384.6851 | 58.6648 | 69.0014
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.301 | 118.7779 | 13.1292 | 4 | 2871.6265 | 3377.0258 | 58.542 | 68.8452 | 191.1015 | 0 | 327.7131 | 13992830.4032 | 1226171.9508 | 15213253.5719 | 11946360.2992 | 0 | 425295.8934 | 0 | 16693525.7262 | 43433129.6266 | 29644003.4317 | 132574570.9029 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 150808520.7256 | 177350453.7063 | 1000000 | 52.5168 | 2871.6265 | 3377.0258 | 58.542 | 68.8452
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.987 | 118.6248 | 13.1315 | 4 | 2866.742 | 3372.0518 | 58.4424 | 68.7438 | 191.1305 | 0 | 367.7396 | 13979945.3783 | 1225065.7595 | 15197569.2795 | 11928073.8072 | 0 | 399041.3103 | 0 | 16664581.2585 | 43357822.0591 | 29592604.4695 | 132344703.3219 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 150578653.1446 | 177120586.1253 | 1333521.4322 | 52.5261 | 2866.742 | 3372.0518 | 58.4424 | 68.7438
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.5165 | 119.3638 | 13.2111 | 4 | 2863.3569 | 3365.6234 | 58.3734 | 68.6128 | 190.9847 | 0 | 333.4831 | 14042115.642 | 1230402.8889 | 15273261.1727 | 12017023.2899 | 0 | 403710.7132 | 0 | 16756940.3456 | 43598121.4582 | 29756613.747 | 133078189.2576 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151312139.0803 | 177854072.061 | 1778279.41 | 52.8443 | 2863.3569 | 3365.6234 | 58.3734 | 68.6128
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.7017 | 119.4523 | 13.2278 | 4 | 2860.8328 | 3362.4654 | 58.3219 | 68.5484 | 190.9666 | 0 | 319.3144 | 14049556.1178 | 1231041.5898 | 15282322.4631 | 12027738.0536 | 0 | 394480.7153 | 0 | 16764204.1865 | 43617020.4821 | 29769512.7192 | 133135876.3274 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151369826.1502 | 177911759.1309 | 2371373.7057 | 52.9111 | 2860.8328 | 3362.4654 | 58.3219 | 68.5484
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.8332 | 119.5151 | 13.24 | 4 | 2858.9356 | 3360.1058 | 58.2833 | 68.5003 | 190.9536 | 0 | 322.9332 | 14054832.8354 | 1231494.5453 | 15288748.9787 | 12035344.6805 | 0 | 387369.6481 | 0 | 16769138.3683 | 43629858.2111 | 29778274.733 | 133175062.0004 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151409011.8232 | 177950944.8039 | 3162277.6602 | 52.9599 | 2858.9356 | 3360.1058 | 58.2833 | 68.5003
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.9186 | 119.5558 | 13.2486 | 4 | 2857.5103 | 3358.3563 | 58.2542 | 68.4646 | 190.9452 | 0 | 324.1057 | 14058252.4558 | 1231788.0845 | 15292913.8818 | 12040281.9601 | 0 | 381807.4055 | 0 | 16771967.0772 | 43637217.9314 | 29783297.8933 | 133197526.6896 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151431476.5123 | 177973409.493 | 4216965.0343 | 52.9942 | 2857.5103 | 3358.3563 | 58.2542 | 68.4646
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.9964 | 119.593 | 13.2556 | 4 | 2856.44 | 3357.0199 | 58.2324 | 68.4374 | 190.9375 | 0 | 335.983 | 14061372.3721 | 1232055.8956 | 15296713.8629 | 12044781.6636 | 0 | 377787.642 | 0 | 16774957.4601 | 43644998.2944 | 29788608.1509 | 133221275.3417 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151455225.1645 | 177997158.1452 | 5623413.2519 | 53.0224 | 2856.44 | 3357.0199 | 58.2324 | 68.4374
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.0501 | 119.6186 | 13.2607 | 4 | 2855.6365 | 3356.0247 | 58.216 | 68.4171 | 190.9322 | 0 | 325.4598 | 14063524.462 | 1232240.6283 | 15299335.1112 | 12047888.2078 | 0 | 374693.8743 | 0 | 16776896.0906 | 43650042.2132 | 29792050.7292 | 133236671.3168 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151470621.1395 | 178012554.1202 | 7498942.0933 | 53.0427 | 2855.6365 | 3356.0247 | 58.216 | 68.4171
1 | 4800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.087 | 119.6361 | 13.2643 | 4 | 2855.0335 | 3355.2837 | 58.2037 | 68.402 | 190.9286 | 0 | 333.8079 | 14065000.0976 | 1232367.2946 | 15301132.4638 | 12050020.1555 | 0 | 372318.0543 | 0 | 16778126.8457 | 43653244.3853 | 29794236.2775 | 133246445.5742 | 961560.8286 | 17272388.9941 | 17272388.9941 | 1478867.319 | 7790676.6675 | 0 | 151480395.397 | 178022328.3777 | 10000000 | 53.0573 | 2855.0335 | 3355.2837 | 58.2037 | 68.402
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.85236 | 0.20686 | 0.010684 | 4 | 464127.4301 | 1101156.6795 | 9461.8654 | 22448.5683 | 124.7845 | 0 | 52.9217 | 137720.494 | 9893.2252 | 96446.7615 | 59035.5949 | 0 | 56497.9591 | 0 | 140241.6735 | 364880.067 | 249038.1433 | 1113753.9185 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 19835112.613 | 47059418.0141 | 100 | 0.042736 | 464127.4301 | 1101156.6795 | 9461.8654 | 22448.5683
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1081 | 0.32563 | 0.022904 | 4 | 221019.8548 | 518177.2821 | 4505.7887 | 10563.7448 | 138.391 | 0 | 58.8748 | 201924.1721 | 15883.335 | 137360.4516 | 74687.1407 | 0 | 63338.181 | 0 | 192345.3794 | 500443.2217 | 341562.7819 | 1527544.6634 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20248903.3578 | 47473208.7589 | 133.3521 | 0.091616 | 221019.8548 | 518177.2821 | 4505.7887 | 10563.7448
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.48466 | 0.041447 | 4 | 125230.3046 | 289443.42 | 2552.9891 | 5900.6956 | 149.8289 | 0 | 58.9335 | 281530.7598 | 24241.4546 | 187264.7605 | 96026.4839 | 0 | 69625.2134 | 0 | 256888.5822 | 668371.3957 | 456177.2112 | 2040125.8612 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 20761484.5557 | 47985789.9568 | 177.8279 | 0.16579 | 125230.3046 | 289443.42 | 2552.9891 | 5900.6956
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8459 | 0.74525 | 0.070058 | 4 | 76674.1064 | 173822.804 | 1563.1054 | 3543.613 | 160.4555 | 0 | 297.3721 | 389622.4005 | 35224.6189 | 263192.4626 | 125768.9879 | 0 | 79009.3968 | 0 | 348198.968 | 905942.2894 | 618324.2278 | 2765283.3519 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 21486642.0464 | 48710947.4474 | 237.1374 | 0.28023 | 76674.1064 | 173822.804 | 1563.1054 | 3543.613
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 1.104 | 0.10689 | 4 | 52260.5772 | 115936.5375 | 1065.4026 | 2363.5231 | 169.2153 | 0 | 393.711 | 512560.0274 | 46378.7661 | 360424.1563 | 160352.4322 | 0 | 89824.8334 | 0 | 456120.684 | 1186732.4566 | 809969.2866 | 3622362.6427 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 22343721.3372 | 49568026.7383 | 316.2278 | 0.42754 | 52260.5772 | 115936.5375 | 1065.4026 | 2363.5231
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0906 | 1.5697 | 0.1549 | 4 | 37707.9674 | 81646.8672 | 768.7279 | 1664.4818 | 176.4109 | 0 | 518.2412 | 655578.5285 | 59335.7829 | 477635.6475 | 204068.9585 | 0 | 102223.3335 | 0 | 584548.4779 | 1520875.232 | 1038028.5967 | 4642294.5576 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 23363653.252 | 50587958.6531 | 421.6965 | 0.61959 | 37707.9674 | 81646.8672 | 768.7279 | 1664.4818
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0117 | 2.1867 | 0.21856 | 4 | 28156.2109 | 59297.2412 | 574.0024 | 1208.8545 | 182.3517 | 0 | 79.2022 | 826944.8426 | 74833.3478 | 622690.3822 | 261076.8378 | 0 | 117282.0559 | 0 | 742102.7119 | 1930799.0301 | 1317810.012 | 5893539.2204 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 24614897.9148 | 51839203.3159 | 562.3413 | 0.87423 | 28156.2109 | 59297.2412 | 574.0024 | 1208.8545
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.1884 | 2.9787 | 0.30076 | 4 | 21702.3384 | 44332.1647 | 442.4315 | 903.7711 | 187.0493 | 0 | 101.7183 | 1027220.7515 | 92908.4743 | 797361.3689 | 333607.1244 | 0 | 133967.9282 | 0 | 930175.6025 | 2420126.1124 | 1651785.8003 | 7387153.1625 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 26108511.857 | 53332817.258 | 749.8942 | 1.203 | 21702.3384 | 44332.1647 | 442.4315 | 903.7711
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.7379 | 4.0227 | 0.40918 | 4 | 17078.7346 | 33712.2266 | 348.1731 | 687.2693 | 190.7833 | 0 | 80.4792 | 1268749.0756 | 114657.2627 | 1014030.2133 | 428937.891 | 0 | 154228.2911 | 0 | 1162435.0661 | 3024417.5939 | 2064227.1534 | 9231682.5472 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 27953041.2416 | 55177346.6427 | 1000 | 1.6367 | 17078.7346 | 33712.2266 | 348.1731 | 687.2693
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.799 | 5.3977 | 0.55156 | 4 | 13706.9903 | 26046.7287 | 279.4355 | 530.9978 | 193.469 | 0 | 75.1083 | 1560444.8862 | 140857.4816 | 1282914.107 | 555286.89 | 0 | 179733.3191 | 0 | 1450502.3067 | 3773909.4631 | 2575770.7547 | 11519419.2084 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 30240777.9029 | 57465083.304 | 1333.5214 | 2.2062 | 13706.9903 | 26046.7287 | 279.4355 | 530.9978
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.5368 | 7.2785 | 0.74746 | 4 | 11092.628 | 20198.2333 | 226.1382 | 411.7683 | 196.3265 | 0 | 107.3389 | 1926516.5454 | 173646.0722 | 1629544.4203 | 724027.9368 | 0 | 209695.5107 | 0 | 1818737.8893 | 4731982.9136 | 3229675.5711 | 14443826.8595 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 33165185.554 | 60389490.955 | 1778.2794 | 2.9898 | 11092.628 | 20198.2333 | 226.1382 | 411.7683
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.1495 | 9.7312 | 1.0025 | 4 | 9168.4048 | 15957.4208 | 186.9103 | 325.3136 | 198.2028 | 0 | 110.8476 | 2364886.6123 | 212790.1523 | 2055725.535 | 946083.4121 | 0 | 246456.0133 | 0 | 2272117.2727 | 5911583.0683 | 4034776.915 | 18044418.9809 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 36765777.6754 | 63990083.0764 | 2371.3737 | 4.0101 | 9168.4048 | 15957.4208 | 186.9103 | 325.3136
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 19.9368 | 12.9832 | 1.3408 | 4 | 7695.4036 | 12771.6676 | 156.8812 | 260.3677 | 199.6578 | 0 | 97.2865 | 2899571.3655 | 260378.094 | 2589046.7603 | 1240296.7336 | 0 | 291204.7186 | 0 | 2839394.0921 | 7387520.9877 | 5042134.8725 | 22549547.6242 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 41270906.3187 | 68495211.7197 | 3162.2777 | 5.3631 | 7695.4036 | 12771.6676 | 156.8812 | 260.3677
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.2775 | 17.2924 | 1.7889 | 4 | 6555.9964 | 10360.55 | 133.6529 | 211.2138 | 200.7792 | 0 | 81.908 | 3551821.56 | 318225.4207 | 3256248.373 | 1630018.1718 | 0 | 345779.2985 | 0 | 3549816.2014 | 9235893.5885 | 6303687.1528 | 28191489.7667 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 46912848.4612 | 74137153.8622 | 4216.965 | 7.1557 | 6555.9964 | 10360.55 | 133.6529 | 211.2138
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 34.6185 | 22.9623 | 2.3788 | 4 | 5668.8085 | 8530.005 | 115.5663 | 173.8957 | 201.6354 | 0 | 93.6795 | 4342679.0291 | 388103.4487 | 4085509.7061 | 2142633.8377 | 0 | 411597.1659 | 0 | 4434504.0431 | 11537669.8782 | 7874696.7673 | 35217393.876 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 53938752.5705 | 81163057.9715 | 5623.4133 | 9.515 | 5668.8085 | 8530.005 | 115.5663 | 173.8957
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 45.5005 | 30.3584 | 3.1483 | 4 | 4973.3289 | 7135.1874 | 101.388 | 145.4604 | 202.2758 | 0 | 106.1311 | 5294583.6572 | 471880.6044 | 5108074.7814 | 2811424.5537 | 0 | 490409.4076 | 0 | 5528785.4717 | 14384765.6875 | 9817898.1591 | 43907822.3225 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 62629181.0169 | 89853486.418 | 7498.9421 | 12.593 | 4973.3289 | 7135.1874 | 101.388 | 145.4604
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 59.5152 | 39.8576 | 4.136 | 4 | 4427.1674 | 6072.7295 | 90.2538 | 123.8008 | 202.6831 | 0 | 111.0461 | 6424799.8026 | 570945.3838 | 6351011.3841 | 3672371.2876 | 0 | 584221.3912 | 0 | 6865306.2072 | 17862118.4832 | 12191262.8946 | 54522036.8343 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 73243395.5287 | 100467700.9298 | 10000 | 16.5441 | 4427.1674 | 6072.7295 | 90.2538 | 123.8008
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 77.0863 | 51.6393 | 5.3591 | 4 | 4003.7314 | 5273.7371 | 81.6215 | 107.5123 | 202.7133 | 0 | 118.6556 | 7724791.8972 | 684420.2338 | 7813004.2741 | 4749713.9333 | 0 | 693743.2299 | 0 | 8449612.6917 | 21984158.9698 | 15004640.2262 | 67104085.456 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 85825444.1505 | 113049749.5515 | 13335.2143 | 21.4364 | 4003.7314 | 5273.7371 | 81.6215 | 107.5123
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 98.3043 | 65.5106 | 6.7928 | 4 | 3684.1754 | 4686.1363 | 75.1069 | 95.5332 | 202.1441 | 0 | 113.9244 | 9151502.9576 | 808452.5078 | 9451110.267 | 6044910.3344 | 0 | 819389.79 | 0 | 10247392.6842 | 26661613.735 | 18197099.2155 | 81381471.4915 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 100102830.186 | 127327135.587 | 17782.7941 | 27.171 | 3684.1754 | 4686.1363 | 75.1069 | 95.5332
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 122.589 | 80.7026 | 8.3505 | 4 | 3453.2856 | 4268.3386 | 70.3999 | 87.0159 | 200.82 | 0 | 148.0099 | 10618789.556 | 935530.2773 | 11167186.8886 | 7516579.0042 | 0 | 958872.9697 | 0 | 12166813.8914 | 31655553.9886 | 21605566.0538 | 96624892.6295 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 115346251.324 | 142570556.725 | 23713.7371 | 33.4019 | 3453.2856 | 4268.3386 | 70.3999 | 87.0159
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 148.6721 | 96.1317 | 9.9156 | 4 | 3292.7539 | 3979.1525 | 67.1272 | 81.1204 | 198.9012 | 0 | 144.2416 | 12030785.8042 | 1057409.3598 | 12844789.3849 | 9082563.9471 | 0 | 1105997.5266 | 0 | 14087402.9488 | 36652532.7491 | 25016106.7355 | 111877588.456 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 130598947.1505 | 157823252.5515 | 31622.7766 | 39.6625 | 3292.7539 | 3979.1525 | 67.1272 | 81.1204
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 163.2681 | 104.4074 | 10.8836 | 4 | 3178.3435 | 3803.6924 | 64.7948 | 77.5434 | 197.7343 | 0 | 168.9849 | 12761484.4464 | 1120336.4467 | 13722042.9843 | 9953068.7213 | 0 | 1072942.1974 | 0 | 15065651.1705 | 39197733.9556 | 26753258.8576 | 119646518.7799 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 138367877.4744 | 165592182.8754 | 42169.6503 | 43.5346 | 3178.3435 | 3803.6924 | 64.7948 | 77.5434
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 172.4003 | 109.4198 | 11.5548 | 4 | 3090.4194 | 3679.443 | 63.0024 | 75.0104 | 196.9473 | 0 | 186.2105 | 13196086.6274 | 1157719.889 | 14246567.426 | 10494906.0629 | 0 | 977613.2182 | 0 | 15628428.3571 | 40661964.7538 | 27752626.4643 | 124115912.7985 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 142837271.493 | 170061576.8941 | 56234.1325 | 46.2194 | 3090.4194 | 3679.443 | 63.0024 | 75.0104
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.7413 | 113.3534 | 12.0988 | 4 | 3022.7822 | 3585.3257 | 61.6235 | 73.0917 | 196.2864 | 0 | 235.4488 | 13533245.6579 | 1186699.5667 | 14654851.63 | 10928454.8003 | 0 | 883642.4507 | 0 | 16062888.7012 | 41792341.449 | 28524131.7857 | 127566256.0415 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 146287614.7359 | 173511920.137 | 74989.4209 | 48.395 | 3022.7822 | 3585.3257 | 61.6235 | 73.0917
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.5265 | 116.3927 | 12.5306 | 4 | 2970.959 | 3514.1137 | 60.567 | 71.64 | 195.7485 | 0 | 276.503 | 13791488.7993 | 1208883.5338 | 14968359.357 | 11269193.5166 | 0 | 796321.2825 | 0 | 16393356.1307 | 42652149.9125 | 29110968.7293 | 130190721.2616 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 148912079.956 | 176136385.3571 | 100000 | 50.1226 | 2970.959 | 3514.1137 | 60.567 | 71.64
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.9381 | 118.6732 | 12.8646 | 4 | 2931.3709 | 3460.4251 | 59.76 | 70.5454 | 195.3282 | 0 | 311.4353 | 13984016.6364 | 1225415.2836 | 15202524.8393 | 11528403.6146 | 0 | 717569.6514 | 0 | 16636592.7099 | 43285001.5967 | 29542903.0076 | 132122427.3395 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 150843786.034 | 178068091.435 | 133352.1432 | 51.4584 | 2931.3709 | 3460.4251 | 59.76 | 70.5454
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 193.2554 | 120.3668 | 13.1195 | 4 | 2901.2115 | 3419.9871 | 59.1451 | 69.7211 | 195.0063 | 0 | 363.5712 | 14126324.4173 | 1237630.9735 | 15375845.6154 | 11723110.2327 | 0 | 648968.8943 | 0 | 16813633.2519 | 43745624.7711 | 29857287.789 | 133528425.9452 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 152249784.6396 | 179474090.0407 | 177827.941 | 52.478 | 2901.2115 | 3419.9871 | 59.1451 | 69.7211
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.8307 | 121.6674 | 13.3168 | 4 | 2878.2716 | 3389.3616 | 58.6775 | 69.0967 | 194.7533 | 0 | 347.3189 | 14235227.7964 | 1246977.0553 | 15508616.5644 | 11873566.2537 | 0 | 592165.4238 | 0 | 16948055.7065 | 44095364.424 | 30095992.2885 | 134595965.5125 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 153317324.207 | 180541629.608 | 237137.3706 | 53.2671 | 2878.2716 | 3389.3616 | 58.6775 | 69.0967
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.6601 | 122.5843 | 13.4615 | 4 | 2860.8632 | 3366.4601 | 58.3226 | 68.6298 | 194.5716 | 0 | 348.7159 | 14311803.4879 | 1253547.6541 | 15602044.0526 | 11980359.7784 | 0 | 543958.5941 | 0 | 17039768.2912 | 44333981.7565 | 30258853.5211 | 135324317.1359 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154045675.8303 | 181269981.2314 | 316227.766 | 53.8459 | 2860.8632 | 3366.4601 | 58.3226 | 68.6298
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.9707 | 123.2375 | 13.5679 | 4 | 2847.6757 | 3349.3049 | 58.0537 | 68.2801 | 194.4404 | 0 | 334.957 | 14366256.9248 | 1258219.4853 | 15668515.511 | 12056829.0109 | 0 | 504204.2133 | 0 | 17103069.8067 | 44498679.3149 | 30371262.9889 | 135827037.2558 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154548395.9502 | 181772701.3513 | 421696.5034 | 54.2718 | 2847.6757 | 3349.3049 | 58.0537 | 68.2801
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.9233 | 123.7102 | 13.6468 | 4 | 2837.7005 | 3336.4297 | 57.8504 | 68.0176 | 194.3445 | 0 | 359.3603 | 14405620.9961 | 1261596.4351 | 15716585.1858 | 12112387.2008 | 0 | 472181.5867 | 0 | 17147664.8477 | 44614706.4641 | 30450453.9023 | 136181196.6185 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 154902555.3129 | 182126860.714 | 562341.3252 | 54.5874 | 2837.7005 | 3336.4297 | 57.8504 | 68.0176
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.5829 | 124.0366 | 13.7037 | 4 | 2830.1656 | 3326.8237 | 57.6968 | 67.8218 | 194.2777 | 0 | 400.4071 | 14432765.6513 | 1263924.969 | 15749741.7474 | 12150849.7833 | 0 | 446293.3843 | 0 | 17176994.4588 | 44691016.0957 | 30502536.7939 | 136414122.8838 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155135481.5783 | 182359786.9793 | 749894.2093 | 54.815 | 2830.1656 | 3326.8237 | 57.6968 | 67.8218
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.0628 | 124.2734 | 13.7459 | 4 | 2824.481 | 3319.6168 | 57.5809 | 67.6749 | 194.229 | 0 | 404.4174 | 14452456.8698 | 1265614.0572 | 15773798.5469 | 12178825.6566 | 0 | 425956.45 | 0 | 17197694.1164 | 44744872.3589 | 30539294.8001 | 136578512.856 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155299871.5505 | 182524176.9516 | 1000000 | 54.9835 | 2824.481 | 3319.6168 | 57.5809 | 67.6749
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.6574 | 124.5674 | 13.7895 | 4 | 2819.8658 | 3313.4356 | 57.4868 | 67.5489 | 194.1694 | 0 | 384.6214 | 14476883.8607 | 1267709.29 | 15803646.2251 | 12213499.4925 | 0 | 411812.5964 | 0 | 17227685.0712 | 44822902.6712 | 30592552.0917 | 136816691.2988 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155538049.9933 | 182762355.3943 | 1333521.4322 | 55.158 | 2819.8658 | 3313.4356 | 57.4868 | 67.5489
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.1325 | 124.8017 | 13.8225 | 4 | 2816.7008 | 3309.0932 | 57.4223 | 67.4603 | 194.1214 | 0 | 355.3738 | 14496335.8443 | 1269377.7235 | 15827418.9671 | 12241198.2069 | 0 | 402797.7685 | 0 | 17252480.119 | 44887414.2994 | 30636582.6035 | 137013605.5322 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155734964.2267 | 182959269.6277 | 1778279.41 | 55.2899 | 2816.7008 | 3309.0932 | 57.4223 | 67.4603
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.3151 | 124.8913 | 13.8393 | 4 | 2814.3211 | 3306.1159 | 57.3737 | 67.3996 | 194.1026 | 0 | 364.4158 | 14503770.9231 | 1270015.4287 | 15836506.5154 | 12251837.8755 | 0 | 393578.4023 | 0 | 17259726.5665 | 44906268.0694 | 30649450.6889 | 137071154.4697 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155792513.1641 | 183016818.5652 | 2371373.7057 | 55.357 | 2814.3211 | 3306.1159 | 57.3737 | 67.3996
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.4419 | 124.9535 | 13.8514 | 4 | 2812.5324 | 3303.8958 | 57.3373 | 67.3544 | 194.0896 | 0 | 370.6569 | 14508929.5392 | 1270457.8771 | 15842811.9611 | 12259228.9037 | 0 | 386438.5337 | 0 | 17264468.0577 | 44918604.4569 | 30657870.5268 | 137108809.8562 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155830168.5506 | 183054473.9517 | 3162277.6602 | 55.4056 | 2812.5324 | 3303.8958 | 57.3373 | 67.3544
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.5346 | 124.9988 | 13.8604 | 4 | 2811.1886 | 3302.2329 | 57.3099 | 67.3205 | 194.08 | 0 | 366.3073 | 14512692.0498 | 1270780.5806 | 15847411.089 | 12264623.4527 | 0 | 380996.5249 | 0 | 17267836.4419 | 44927368.3014 | 30663852.0308 | 137135560.4712 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155856919.1657 | 183081224.5667 | 4216965.0343 | 55.4416 | 2811.1886 | 3302.2329 | 57.3099 | 67.3205
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.5929 | 125.0273 | 13.8667 | 4 | 2810.1794 | 3301.0026 | 57.2893 | 67.2954 | 194.074 | 0 | 349.715 | 14515057.3601 | 1270983.4477 | 15850302.4099 | 12268021.0743 | 0 | 376734.382 | 0 | 17269628.4829 | 44932030.8246 | 30667034.2987 | 137149792.2801 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155871150.9746 | 183095456.3757 | 5623413.2519 | 55.4666 | 2810.1794 | 3301.0026 | 57.2893 | 67.2954
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.6512 | 125.0559 | 13.872 | 4 | 2809.4218 | 3300.0556 | 57.2739 | 67.2761 | 194.0679 | 0 | 365.5686 | 14517428.6073 | 1271186.8231 | 15853201.0417 | 12271420.0016 | 0 | 373717.3632 | 0 | 17271911.9965 | 44937972.0585 | 30671089.3129 | 137167927.2049 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155889285.8993 | 183113591.3004 | 7498942.0933 | 55.488 | 2809.4218 | 3300.0556 | 57.2739 | 67.2761
1 | 4900 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.6855 | 125.0726 | 13.8756 | 4 | 2808.8532 | 3299.3604 | 57.2623 | 67.2619 | 194.0644 | 0 | 351.3378 | 14518817.7178 | 1271305.963 | 15854899.1266 | 12273415.5062 | 0 | 371316.2987 | 0 | 17273004.2987 | 44940814.0049 | 30673028.9998 | 137176601.9156 | 961560.8286 | 17759797.8658 | 17759797.8658 | 1478867.319 | 7985640.2162 | 0 | 155897960.61 | 183122266.0111 | 10000000 | 55.5024 | 2808.8532 | 3299.3604 | 57.2623 | 67.2619
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.88403 | 0.22474 | 0.012557 | 4 | 406049.3079 | 961820.6066 | 8277.8644 | 19608.014 | 127.9387 | 0 | 55.2257 | 148312.2355 | 10874.1437 | 102832.0634 | 61370.1318 | 0 | 57634.6607 | 0 | 148599.0617 | 386624.2766 | 263879.0131 | 1180125.5864 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20394753.2434 | 48309635.1921 | 100 | 0.050227 | 406049.3079 | 961820.6066 | 8277.8644 | 19608.014
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1424 | 0.34968 | 0.025944 | 4 | 200656.134 | 469648.3426 | 4090.6467 | 9574.4167 | 141.4317 | 0 | 46.9343 | 215306.0808 | 17309.7884 | 145113.3294 | 77591.4217 | 0 | 64050.2844 | 0 | 202554.6529 | 527005.6571 | 359692.1898 | 1608623.4045 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 20823251.0615 | 48738133.0101 | 133.3521 | 0.10378 | 200656.134 | 469648.3426 | 4090.6467 | 9574.4167
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.51727 | 0.046232 | 4 | 115501.2602 | 266452.4711 | 2354.6494 | 5431.994 | 152.8816 | 0 | 66.6974 | 299133.5763 | 26491.8804 | 196821.6618 | 99981.1142 | 0 | 69997.5734 | 0 | 270046.0644 | 702604.4655 | 479541.9848 | 2144618.3208 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 21359245.9779 | 49274127.9265 | 177.8279 | 0.18493 | 115501.2602 | 266452.4711 | 2354.6494 | 5431.994
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8848 | 0.79869 | 0.076092 | 4 | 72616.3811 | 164331.2112 | 1480.3831 | 3350.114 | 163.4295 | 0 | 303.686 | 408897.4239 | 36974.3817 | 278186.3826 | 129257.9995 | 0 | 78907.9343 | 0 | 363567.4076 | 945927.8165 | 645615.1716 | 2887334.5177 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22101962.1747 | 50016844.1233 | 237.1374 | 0.30437 | 72616.3811 | 164331.2112 | 1480.3831 | 3350.114
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.4488 | 1.182 | 0.11556 | 4 | 49755.8209 | 110144.4097 | 1014.3397 | 2245.4428 | 172.448 | 0 | 402.6232 | 537609.2808 | 48649.6661 | 380662.7447 | 165115.4831 | 0 | 90081.7218 | 0 | 476626.3696 | 1240084.0443 | 846382.8414 | 3785212.1518 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 22999839.8088 | 50914721.7575 | 316.2278 | 0.46225 | 49755.8209 | 110144.4097 | 1014.3397 | 2245.4428
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.1684 | 1.6761 | 0.16678 | 4 | 36065.9149 | 77910.5283 | 735.2525 | 1588.3115 | 179.7695 | 0 | 498.8016 | 686356.4566 | 62121.4041 | 503347.2363 | 210142.4139 | 0 | 102398.2481 | 0 | 610102.646 | 1587361.9357 | 1083407.1382 | 4845237.479 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 24059865.136 | 51974747.0846 | 421.6965 | 0.66711 | 36065.9149 | 77910.5283 | 735.2525 | 1588.3115
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.0849 | 2.3099 | 0.23276 | 4 | 27194.6914 | 57176.761 | 554.4006 | 1165.6256 | 185.6505 | 0 | 71.4936 | 859347.4625 | 77760.3619 | 650602.4573 | 267081.3285 | 0 | 116328.4534 | 0 | 768736.8248 | 2000095.5286 | 1365106.2961 | 6105058.7132 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 25319686.3702 | 53234568.3189 | 562.3413 | 0.93105 | 27194.6914 | 57176.761 | 554.4006 | 1165.6256
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.2958 | 3.1518 | 0.32049 | 4 | 20968.1156 | 42743.1833 | 427.4634 | 871.3776 | 190.4762 | 0 | 81.3526 | 1068789.2016 | 96655.3076 | 834215.9347 | 342102.1134 | 0 | 133259.0529 | 0 | 965258.428 | 2511404.428 | 1714085.1263 | 7665769.5926 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 26880397.2496 | 54795279.1983 | 749.8942 | 1.282 | 20968.1156 | 42743.1833 | 427.4634 | 871.3776
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.8816 | 4.2551 | 0.43563 | 4 | 16525.2585 | 32545.2367 | 336.8897 | 663.4787 | 194.268 | 0 | 88.1849 | 1319862.6828 | 119253.3392 | 1060616.3064 | 440117.6741 | 0 | 153441.247 | 0 | 1206383.5873 | 3138762.6308 | 2142269.9907 | 9580707.4583 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 28795335.1153 | 56710217.0639 | 1000 | 1.7425 | 16525.2585 | 32545.2367 | 336.8897 | 663.4787
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.9622 | 5.6909 | 0.58539 | 4 | 13299.1327 | 25220.5855 | 271.1208 | 514.1557 | 196.9966 | 0 | 85.7625 | 1619693.8246 | 146171.0186 | 1338370.2399 | 568447.5825 | 0 | 177884.8564 | 0 | 1501721.3336 | 3907170.8646 | 2666724.3994 | 11926184.1196 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 31140811.7766 | 59055693.7253 | 1333.5214 | 2.3416 | 13299.1327 | 25220.5855 | 271.1208 | 514.1557
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.7459 | 7.6656 | 0.79227 | 4 | 10778.6884 | 19587.1771 | 219.7381 | 399.3111 | 199.8869 | 0 | 104.4015 | 1998260.1317 | 180060.9621 | 1698523.1206 | 740893.8513 | 0 | 207179.0012 | 0 | 1881717.6561 | 4895843.3478 | 3341513.6844 | 14943991.7551 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 34158619.4121 | 62073501.3608 | 1778.2794 | 3.1691 | 10778.6884 | 19587.1771 | 219.7381 | 399.3111
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.4079 | 10.2347 | 1.0611 | 4 | 8921.1293 | 15497.9413 | 181.8693 | 315.9465 | 201.7913 | 0 | 98.0301 | 2450699.3724 | 220438.7074 | 2140387.2992 | 967229.7105 | 0 | 242891.8162 | 0 | 2348442.2932 | 6110165.1152 | 4170313.2425 | 18650567.5567 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 37865195.2137 | 65780077.1623 | 2371.3737 | 4.2444 | 8921.1293 | 15497.9413 | 181.8693 | 315.9465
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.2721 | 13.6496 | 1.4184 | 4 | 7493.6079 | 12413.719 | 152.7673 | 253.0705 | 203.2733 | 0 | 107.8841 | 3004091.3103 | 269662.2203 | 2694816.6539 | 1267933.9715 | 0 | 286715.2988 | 0 | 2934055.5873 | 7633810.7807 | 5210232.7169 | 23301318.5397 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 42515946.1967 | 70430828.1453 | 3162.2777 | 5.6736 | 7493.6079 | 12413.719 | 152.7673 | 253.0705
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 26.7185 | 18.177 | 1.892 | 4 | 6387.785 | 10076.2885 | 130.2236 | 205.4188 | 204.4163 | 0 | 86.0192 | 3679610.0857 | 329534.9607 | 3388838.0234 | 1666408.4237 | 0 | 340271.5234 | 0 | 3667818.5766 | 9542911.5633 | 6513233.2292 | 29128626.3859 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 48343254.0429 | 76258135.9916 | 4216.965 | 7.5681 | 6387.785 | 10076.2885 | 130.2236 | 205.4188
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.1884 | 24.1271 | 2.5147 | 4 | 5526.6731 | 8301.8706 | 112.6687 | 169.2449 | 205.2881 | 0 | 129.7032 | 4497835.5125 | 401782.1346 | 4250483.9793 | 2189971.5912 | 0 | 404694.5436 | 0 | 4580459.4269 | 11917415.8474 | 8133881.1943 | 36376524.23 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 55591151.887 | 83506033.8356 | 5623.4133 | 10.0587 | 5526.6731 | 8301.8706 | 112.6687 | 169.2449
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.2238 | 31.8776 | 3.3259 | 4 | 4851.513 | 6949.8012 | 98.9047 | 141.6811 | 205.938 | 0 | 102.0229 | 5481453.3929 | 488288.7371 | 5311564.7595 | 2872005.5128 | 0 | 481647.522 | 0 | 5707634.3704 | 14850093.8351 | 10135494.1814 | 45328182.3111 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 64542809.9681 | 92457691.9168 | 7498.9421 | 13.3036 | 4851.513 | 6949.8012 | 98.9047 | 141.6811
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 60.2916 | 41.7885 | 4.3632 | 4 | 4324.5553 | 5924.0025 | 88.1619 | 120.7688 | 206.3409 | 0 | 129.4746 | 6644643.5296 | 590168.8218 | 6595976.741 | 3761677.7219 | 0 | 572370.8624 | 0 | 7084286.6939 | 18431860.7904 | 12580123.7263 | 56261108.8871 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 75475736.5441 | 103390618.4928 | 10000 | 17.4528 | 4324.5553 | 5924.0025 | 88.1619 | 120.7688
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 78.0265 | 54.0868 | 5.6476 | 4 | 3913.4568 | 5149.1546 | 79.7811 | 104.9725 | 206.3495 | 0 | 118.7023 | 7983739.1245 | 706969.1343 | 8107869.733 | 4861847.4276 | 0 | 679316.6209 | 0 | 8712499.3957 | 22668136.2482 | 15471468.773 | 69191846.4572 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 88406474.1142 | 116321356.0629 | 13335.2143 | 22.5904 | 3913.4568 | 5149.1546 | 79.7811 | 104.9725
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 99.5736 | 68.5391 | 7.1495 | 4 | 3600.9321 | 4577.0496 | 73.4099 | 93.3093 | 205.7242 | 0 | 137.8963 | 9451094.0537 | 834437.0256 | 9799064.2655 | 6156981.1163 | 0 | 803143.545 | 0 | 10547440.8024 | 27442277.3902 | 18729918.2012 | 83764356.3998 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 102978984.0568 | 130893866.0054 | 17782.7941 | 28.5979 | 3600.9321 | 4577.0496 | 73.4099 | 93.3093
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 123.9682 | 84.2641 | 8.7711 | 4 | 3377.7489 | 4173.397 | 68.86 | 85.0803 | 204.3198 | 0 | 120.963 | 10951027.4291 | 964242.5556 | 11559730.8923 | 7643001.8395 | 0 | 940032.3394 | 0 | 12502633.6718 | 32529288.1712 | 22201907.5869 | 99291864.4858 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 118506492.1428 | 146421374.0914 | 23713.7371 | 35.0845 | 3377.7489 | 4173.397 | 68.86 | 85.0803
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 150.046 | 100.1617 | 10.3937 | 4 | 3222.4612 | 3893.8993 | 65.6942 | 79.3824 | 202.3295 | 0 | 151.6274 | 12388739.0802 | 1088247.7848 | 13273796.3199 | 9216649.3269 | 0 | 1084244.5596 | 0 | 14450154.0579 | 37596336.7245 | 25660272.3419 | 114758440.1958 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 133973067.8528 | 161887949.8015 | 31622.7766 | 41.5748 | 3222.4612 | 3893.8993 | 65.6942 | 79.3824
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 166.5667 | 109.7865 | 11.48 | 4 | 3113.6287 | 3721.5301 | 63.4755 | 75.8684 | 200.9501 | 0 | 148.1146 | 13227665.3143 | 1160434.9632 | 14284757.728 | 10206633.5541 | 0 | 1079601.896 | 0 | 15584046.4477 | 40546492.1294 | 27673814.0254 | 123763446.0581 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 142978073.7151 | 170892955.6637 | 42169.6503 | 45.9201 | 3113.6287 | 3721.5301 | 63.4755 | 75.8684
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 175.5861 | 114.8555 | 12.1608 | 4 | 3030.6991 | 3604.5683 | 61.7849 | 73.484 | 200.1337 | 0 | 193.137 | 13661112.0959 | 1197685.0928 | 14809997.3382 | 10743822.4494 | 0 | 981647.1136 | 0 | 16143762.995 | 42002759.772 | 28667746.6148 | 128208533.4716 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 147423161.1287 | 175338043.0773 | 56234.1325 | 48.6433 | 3030.6991 | 3604.5683 | 61.7849 | 73.484
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.8398 | 118.8355 | 12.7117 | 4 | 2966.9341 | 3515.932 | 60.485 | 71.677 | 199.4489 | 0 | 239.7726 | 13997680.0003 | 1226588.2863 | 15219157.1684 | 11174191.4071 | 0 | 886166.5953 | 0 | 16576475.5484 | 43128589.0742 | 29436148.247 | 131644996.3269 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 150859623.9839 | 178774505.9325 | 74989.4209 | 50.847 | 2966.9341 | 3515.932 | 60.485 | 71.677
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.5233 | 121.8926 | 13.147 | 4 | 2918.0871 | 3448.9076 | 59.4892 | 70.3106 | 198.8952 | 0 | 258.2919 | 14254051.699 | 1248592.3313 | 15531577.7044 | 11510551.8091 | 0 | 797579.165 | 0 | 16903517.5564 | 43979485.2936 | 30016902.4009 | 134242257.9598 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 153456885.6168 | 181371767.5654 | 100000 | 52.5882 | 2918.0871 | 3448.9076 | 59.4892 | 70.3106
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.8734 | 124.1946 | 13.484 | 4 | 2880.7755 | 3398.3319 | 58.7285 | 69.2796 | 198.4613 | 0 | 295.6969 | 14445908.2866 | 1265052.3346 | 15765797.7165 | 11767303.4995 | 0 | 718322.1205 | 0 | 17145329.7435 | 44608631.0019 | 30446307.2745 | 136162651.9776 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 155377279.6346 | 183292161.5833 | 133352.1432 | 53.9359 | 2880.7755 | 3398.3319 | 58.7285 | 69.2796
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 196.1324 | 125.8978 | 13.7403 | 4 | 2852.3504 | 3360.2509 | 58.149 | 68.5033 | 198.1305 | 0 | 334.57 | 14587211.3719 | 1277171.5105 | 15938528.1097 | 11959455.3824 | 0 | 649337.8712 | 0 | 17320564.6558 | 45064556.2981 | 30757485.6575 | 137554310.8571 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 156768938.5141 | 184683820.4627 | 177827.941 | 54.9613 | 2852.3504 | 3360.2509 | 58.149 | 68.5033
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.6345 | 127.1924 | 13.9374 | 4 | 2830.7367 | 3331.4543 | 57.7084 | 67.9162 | 197.8733 | 0 | 324.8273 | 14694253.2653 | 1286350.1393 | 16069503.9429 | 12106659.7647 | 0 | 591981.5111 | 0 | 17452011.9631 | 45406555.228 | 30990906.9545 | 138598222.7688 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 157812850.4258 | 185727732.3745 | 237137.3706 | 55.7497 | 2830.7367 | 3331.4543 | 57.7084 | 67.9162
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.423 | 128.1102 | 14.0824 | 4 | 2814.332 | 3309.8962 | 57.374 | 67.4767 | 197.6876 | 0 | 317.3509 | 14769960.9016 | 1292840.853 | 16162204.8421 | 12211655.1551 | 0 | 543592.8734 | 0 | 17542299.3038 | 45641464.3682 | 31151237.2696 | 139315255.5669 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 158529883.2239 | 186444765.1725 | 316227.766 | 56.3295 | 2814.332 | 3309.8962 | 57.374 | 67.4767
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.7085 | 128.7662 | 14.1892 | 4 | 2801.9035 | 3293.7373 | 57.1206 | 67.1473 | 197.553 | 0 | 400.328 | 14823981.6987 | 1297471.7315 | 16228384.0952 | 12287086.5806 | 0 | 503805.6414 | 0 | 17604884.6015 | 45804298.4747 | 31262374.8932 | 139812287.7167 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159026915.3737 | 186941797.3224 | 421696.5034 | 56.7567 | 2801.9035 | 3293.7373 | 57.1206 | 67.1473
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.6318 | 129.2355 | 14.2678 | 4 | 2792.5022 | 3281.6264 | 56.9289 | 66.9004 | 197.4558 | 0 | 367.5915 | 14862574.1482 | 1300779.7574 | 16275679.3147 | 12341248.4137 | 0 | 471641.3366 | 0 | 17648249.9585 | 45917126.2383 | 31339382.1602 | 140156681.3277 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159371308.9847 | 187286190.9333 | 562341.3252 | 57.0711 | 2792.5022 | 3281.6264 | 56.9289 | 66.9004
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.2897 | 129.5688 | 14.3253 | 4 | 2785.4003 | 3272.5595 | 56.7842 | 66.7156 | 197.3862 | 0 | 373.8847 | 14889960.9845 | 1303127.1349 | 16309250.4621 | 12379829.4894 | 0 | 445920.5307 | 0 | 17677954.5546 | 45994411.5041 | 31392130.9422 | 140392585.6025 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 159607213.2595 | 187522095.2081 | 749894.2093 | 57.3014 | 2785.4003 | 3272.5595 | 56.7842 | 66.7156
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.246 | 128.5224 | 14.2495 | 4 | 2779.8707 | 3269.6229 | 56.6714 | 66.6557 | 197.5949 | 0 | 787.0645 | 14803911.2481 | 1295751.2644 | 16203793.1889 | 12259816.8466 | 0 | 390220.6679 | 0 | 17531862.3542 | 45614309.5663 | 31132703.5593 | 139232368.6959 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 158446996.3529 | 186361878.3015 | 1000000 | 56.998 | 2779.8707 | 3269.6229 | 56.6714 | 66.6557
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.5855 | 130.2248 | 14.4226 | 4 | 2775.7157 | 3259.5901 | 56.5867 | 66.4512 | 197.2501 | 0 | 370.1824 | 14943810.6126 | 1307742.3556 | 16375280.474 | 12455830.8974 | 0 | 414858.2345 | 0 | 17744033.8039 | 46166336.1559 | 31509473.0498 | 140917365.5837 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160131993.2407 | 188046875.1893 | 1333521.4322 | 57.6903 | 2775.7157 | 3259.5901 | 56.5867 | 66.4512
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.8413 | 130.3535 | 14.4458 | 4 | 2772.7348 | 3255.8321 | 56.5259 | 66.3745 | 197.2227 | 0 | 373.7654 | 14954359.8618 | 1308646.4349 | 16388219.0502 | 12470821.7454 | 0 | 403034.0127 | 0 | 17754781.631 | 46194299.7973 | 31528558.8096 | 141002721.3428 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160217348.9998 | 188132230.9484 | 1778279.41 | 57.7831 | 2772.7348 | 3255.8321 | 56.5259 | 66.3745
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9876 | 130.4268 | 14.4611 | 4 | 2770.4927 | 3253.0795 | 56.4802 | 66.3184 | 197.2068 | 0 | 355.8135 | 14960372.8798 | 1309161.7479 | 16395594.4357 | 12479393.9277 | 0 | 393398.9963 | 0 | 17759789.5751 | 46207329.4407 | 31537451.8089 | 141042492.8122 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160257120.4692 | 188172002.4178 | 2371373.7057 | 57.8443 | 2770.4927 | 3253.0795 | 56.4802 | 66.3184
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.1191 | 130.4928 | 14.4736 | 4 | 2768.8073 | 3250.9776 | 56.4459 | 66.2756 | 197.1927 | 0 | 360.2847 | 14965783.5915 | 1309625.4389 | 16402231.3379 | 12487099.7677 | 0 | 386378.024 | 0 | 17764936.0824 | 46220719.5969 | 31546590.8657 | 141083364.705 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160297992.362 | 188212874.3106 | 3162277.6602 | 57.8942 | 2768.8073 | 3250.9776 | 56.4459 | 66.2756
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.1922 | 130.5294 | 14.4817 | 4 | 2767.5411 | 3249.4392 | 56.4201 | 66.2442 | 197.1847 | 0 | 352.5963 | 14968782.5993 | 1309882.4481 | 16405910.1064 | 12491384.8004 | 0 | 380712.9299 | 0 | 17767102.4248 | 46226355.9755 | 31550437.8099 | 141100569.0942 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160315196.7512 | 188230078.6998 | 4216965.0343 | 57.9269 | 2767.5411 | 3249.4392 | 56.4201 | 66.2442
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.2628 | 130.5648 | 14.4886 | 4 | 2766.5902 | 3248.2597 | 56.4007 | 66.2202 | 197.1771 | 0 | 369.3939 | 14971682.0044 | 1310130.9202 | 16409466.7757 | 12495518.9458 | 0 | 376647.8838 | 0 | 17769744.1467 | 46233229.1939 | 31555128.9227 | 141121548.7931 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160336176.4501 | 188251058.3988 | 5623413.2519 | 57.9544 | 2766.5902 | 3248.2597 | 56.4007 | 66.2202
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.3165 | 130.5917 | 14.4938 | 4 | 2765.8764 | 3247.3732 | 56.3861 | 66.2021 | 197.1713 | 0 | 355.9081 | 14973888.8378 | 1310320.0397 | 16412173.927 | 12498666.0757 | 0 | 373592.9446 | 0 | 17771770.3116 | 46238500.8595 | 31558726.9428 | 141137639.9387 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160352267.5957 | 188267149.5443 | 7498942.0933 | 57.9752 | 2765.8764 | 3247.3732 | 56.3861 | 66.2021
1 | 5000 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.3554 | 130.6112 | 14.4976 | 4 | 2765.3406 | 3246.7103 | 56.3752 | 66.1886 | 197.1672 | 0 | 361.2146 | 14975485.9882 | 1310456.9106 | 16414133.2005 | 12500944.8972 | 0 | 371273.0507 | 0 | 17773194.6784 | 46242206.7696 | 31561256.3026 | 141148951.7977 | 961560.8286 | 18253066.8284 | 18253066.8284 | 1478867.319 | 8182947.8012 | 0 | 160363579.4547 | 188278461.4033 | 10000000 | 57.9905 | 2765.3406 | 3246.7103 | 56.3752 | 66.1886
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.90348 | 0.23771 | 0.014172 | 4 | 369371.7251 | 874114.8051 | 7530.1422 | 17820.0126 | 130.327 | 0 | 58.7885 | 156088.0875 | 11623.5546 | 107374.3184 | 62963.6236 | 0 | 57708.6128 | 0 | 154345.6968 | 401575.8423 | 274083.764 | 1225763.4999 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 20939520.2103 | 49553182.8338 | 100 | 0.05669 | 369371.7251 | 874114.8051 | 7530.1422 | 17820.0126
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1619 | 0.36717 | 0.028549 | 4 | 187214.4097 | 437779.3742 | 3816.619 | 8924.7247 | 143.8232 | 0 | 48.1997 | 225334.3571 | 18445.4971 | 150635.4905 | 79699.6694 | 0 | 63615.9177 | 0 | 209715.0634 | 545635.5766 | 372407.4927 | 1665489.0645 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 21379245.775 | 49992908.3984 | 133.3521 | 0.1142 | 187214.4097 | 437779.3742 | 3816.619 | 8924.7247
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5102 | 0.56807 | 0.052336 | 4 | 105117.1863 | 241800.9192 | 2142.956 | 4929.4388 | 156.3715 | 0 | 55.9331 | 322145.4131 | 29035.2173 | 211847.7303 | 105528.4344 | 0 | 71356.1702 | 0 | 288566.0565 | 750789.6859 | 512429.3878 | 2291698.0954 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22005454.8059 | 50619117.4293 | 177.8279 | 0.20934 | 105117.1863 | 241800.9192 | 2142.956 | 4929.4388
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.9431 | 0.86661 | 0.083425 | 4 | 68197.3874 | 153943.7606 | 1390.296 | 3138.3518 | 166.7872 | 0 | 306.5683 | 432850.5538 | 39148.3504 | 296956.6558 | 133920.6253 | 0 | 79861.9772 | 0 | 383267.8834 | 997184.4135 | 680598.8523 | 3043789.3117 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 22757546.0222 | 51371208.6456 | 237.1374 | 0.3337 | 68197.3874 | 153943.7606 | 1390.296 | 3138.3518
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5071 | 1.2618 | 0.12449 | 4 | 47518.5116 | 104981.4603 | 968.7291 | 2140.1891 | 175.6784 | 0 | 406.124 | 562712.6968 | 50924.8337 | 401075.2006 | 169808.1006 | 0 | 90181.2701 | 0 | 497133.8197 | 1293440.2227 | 882799.5296 | 3948075.6739 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 23661832.3843 | 52275495.0077 | 316.2278 | 0.49795 | 47518.5116 | 104981.4603 | 968.7291 | 2140.1891
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.2462 | 1.785 | 0.17891 | 4 | 34603.8149 | 74587.5289 | 705.4456 | 1520.5677 | 183.1243 | 0 | 503.0676 | 717299.5906 | 64920.9953 | 529354.2909 | 216175.158 | 0 | 102685.6628 | 0 | 635869.9221 | 1654403.1024 | 1129164.112 | 5049872.8342 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 24763629.5446 | 53377292.168 | 421.6965 | 0.71563 | 34603.8149 | 74587.5289 | 705.4456 | 1520.5677
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.1775 | 2.4496 | 0.24857 | 4 | 26209.2023 | 54987.8505 | 534.31 | 1121.0017 | 189.0446 | 0 | 71.6493 | 895461.7645 | 81021.4431 | 681877.272 | 274279.4589 | 0 | 116010.6777 | 0 | 798973.7403 | 2078765.7803 | 1418800.3594 | 6345190.4962 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 26058947.2067 | 54672609.8301 | 562.3413 | 0.99427 | 26209.2023 | 54987.8505 | 534.31 | 1121.0017
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.4079 | 3.3321 | 0.34108 | 4 | 20277.5394 | 41250.1829 | 413.3851 | 840.9408 | 193.9127 | 0 | 84.3542 | 1111381.414 | 100492.7762 | 872174.1473 | 350814.3152 | 0 | 132428.8147 | 0 | 1001243.6723 | 2605030.6519 | 1777986.948 | 7951552.7395 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 27665309.4499 | 56278972.0733 | 749.8942 | 1.3643 | 20277.5394 | 41250.1829 | 413.3851 | 840.9408
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.0131 | 4.4843 | 0.46209 | 4 | 16030.4483 | 31510.8695 | 326.8024 | 642.3917 | 197.7234 | 0 | 94.9339 | 1369512.2109 | 123715.6731 | 1106092.9938 | 450566.8016 | 0 | 151840.3401 | 0 | 1248673.9276 | 3248793.4214 | 2217368.2661 | 9916563.6347 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 29630320.3451 | 58243982.9685 | 1000 | 1.8484 | 16030.4483 | 31510.8695 | 326.8024 | 642.3917
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.1326 | 6.0014 | 0.62136 | 4 | 12900.7264 | 24413.3148 | 262.9988 | 497.6984 | 200.6277 | 0 | 98.2935 | 1681487.9361 | 151709.9885 | 1396486.4642 | 582074.9772 | 0 | 175649.7873 | 0 | 1555089.5698 | 4046024.0679 | 2761494.5638 | 12350017.3549 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 32063774.0653 | 60677436.6887 | 1333.5214 | 2.4854 | 12900.7264 | 24413.3148 | 262.9988 | 497.6984
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 11.9608 | 8.0659 | 0.83876 | 4 | 10481.9928 | 19010.5557 | 213.6896 | 387.5559 | 203.4447 | 0 | 76.0782 | 2071350.6102 | 186592.7348 | 1769120.2934 | 758160.8644 | 0 | 204273.2393 | 0 | 1945904.1194 | 5062843.3589 | 3455494.6235 | 15453739.8439 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 35167496.5543 | 63781159.1777 | 1778.2794 | 3.355 | 10481.9928 | 19010.5557 | 213.6896 | 387.5559
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.6831 | 10.762 | 1.1225 | 4 | 8684.3033 | 15057.0973 | 177.0413 | 306.9593 | 205.3793 | 0 | 110.9778 | 2539272.7394 | 228328.749 | 2228162.8395 | 989524.0403 | 0 | 239102.3587 | 0 | 2427512.3835 | 6315889.2706 | 4310724.2057 | 19278516.5868 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 38992273.2972 | 67605935.9206 | 2371.3737 | 4.49 | 8684.3033 | 15057.0973 | 177.0413 | 306.9593
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 20.6205 | 14.3466 | 1.4997 | 4 | 7301.1564 | 12071.1188 | 148.8439 | 246.0861 | 206.8843 | 0 | 114.7917 | 3111868.975 | 279229.7919 | 2804361.2769 | 1298509.2156 | 0 | 281896.3593 | 0 | 3032587.5913 | 7890170.8433 | 5385203.7274 | 24083827.7807 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 43797584.4911 | 72411247.1146 | 3162.2777 | 5.9987 | 7301.1564 | 12071.1188 | 148.8439 | 246.0861
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.1595 | 19.0852 | 1.9984 | 4 | 6229.1716 | 9808.8204 | 126.9901 | 199.9661 | 208.0455 | 0 | 91.078 | 3808967.5398 | 340975.8565 | 3523630.7531 | 1703994.1738 | 0 | 333833.6016 | 0 | 3787446.7507 | 9854159.5331 | 6725666.3641 | 30078674.5726 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 49792431.283 | 78406093.9064 | 4216.965 | 7.9934 | 6229.1716 | 9808.8204 | 126.9901 | 199.9661
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 35.7562 | 25.3216 | 2.6547 | 4 | 5392.6325 | 8087.2167 | 109.9361 | 164.8689 | 208.9324 | 0 | 113.3409 | 4654729.6405 | 415604.4523 | 4418007.6456 | 2238794.2561 | 0 | 396621.9679 | 0 | 4728265.6053 | 12301977.2045 | 8396352.2224 | 37550352.9946 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 57264109.705 | 85877772.3284 | 5623.4133 | 10.619 | 5392.6325 | 8087.2167 | 109.9361 | 164.8689
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 46.9548 | 33.4432 | 3.5097 | 4 | 4736.2552 | 6774.4612 | 96.555 | 138.1066 | 209.5918 | 0 | 104.1217 | 5671385.6487 | 504953.7021 | 5519242.2506 | 2935424.7817 | 0 | 471689.1051 | 0 | 5890051.2404 | 15324705.1118 | 10459426.13 | 46776877.9704 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 66490634.6808 | 95104297.3042 | 7498.9421 | 14.0387 | 4736.2552 | 6774.4612 | 96.555 | 138.1066
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 61.3394 | 43.8406 | 4.6036 | 4 | 4220.932 | 5774.8185 | 86.0494 | 117.7275 | 209.993 | 0 | 125.8441 | 6875150.8998 | 610309.5811 | 6853856.8672 | 3829756.6595 | 0 | 560927.7152 | 0 | 7304700.6719 | 19005332.7482 | 12971530.1212 | 58011565.2641 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 77725321.9745 | 106338984.5979 | 10000 | 18.4143 | 4220.932 | 5774.8185 | 86.0494 | 117.7275
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 79.2984 | 56.6652 | 5.9504 | 4 | 3822.2137 | 5024.3824 | 77.921 | 102.4288 | 209.9703 | 0 | 114.1172 | 8252965.8045 | 730395.2069 | 8415631.6475 | 4943806.9088 | 0 | 665145.7025 | 0 | 8973098.6554 | 23346162.0657 | 15934235.3255 | 71261441.3169 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 90975198.0274 | 119588860.6508 | 13335.2143 | 23.8017 | 3822.2137 | 5024.3824 | 77.921 | 102.4288
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 100.8595 | 71.648 | 7.5168 | 4 | 3522.3124 | 4473.9741 | 71.8071 | 91.208 | 209.2894 | 0 | 128.1755 | 9754753.4923 | 860754.1753 | 10153053.8086 | 6274714.6363 | 0 | 785181.2981 | 0 | 10853098.3901 | 28237535.7345 | 19272698.3622 | 86191789.8974 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 105905546.6078 | 134519209.2313 | 17782.7941 | 30.0671 | 3522.3124 | 4473.9741 | 71.8071 | 91.208
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 125.3541 | 87.8998 | 9.202 | 4 | 3306.5291 | 4083.9019 | 67.4081 | 83.2559 | 207.8028 | 0 | 153.5424 | 11286129.4273 | 993180.4295 | 11957052.4359 | 7774716.8023 | 0 | 919222.6622 | 0 | 12842817.6853 | 33414377.193 | 22805999.031 | 101993495.6665 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 121707252.3769 | 150320915.0004 | 23713.7371 | 36.8082 | 3306.5291 | 4083.9019 | 67.4081 | 83.2559
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 151.4442 | 104.2582 | 10.8813 | 4 | 3156.0596 | 3813.4661 | 64.3405 | 77.7427 | 205.7405 | 0 | 163.5913 | 12748456.6381 | 1119215.3259 | 13706350.792 | 9352009.2126 | 0 | 1060510.1891 | 0 | 14814751.4415 | 38544944.3275 | 26307716.5229 | 117653954.4498 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 137367711.1602 | 165981373.7837 | 31622.7766 | 43.5251 | 3156.0596 | 3813.4661 | 64.3405 | 77.7427
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 169.8823 | 115.2801 | 12.0914 | 4 | 3052.2451 | 3643.856 | 62.2241 | 74.2849 | 204.1344 | 0 | 182.7711 | 13697174.0549 | 1200782.8383 | 14853782.8254 | 10461810.2148 | 0 | 1084378.6571 | 0 | 16106192.1503 | 41905008.1407 | 28601029.1179 | 127910157.9993 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 147623914.7097 | 176237577.3332 | 42169.6503 | 48.3657 | 3052.2451 | 3643.856 | 62.2241 | 74.2849
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 178.7922 | 120.4005 | 12.7807 | 4 | 2974.0885 | 3533.7909 | 60.6308 | 72.0411 | 203.2884 | 0 | 201.4119 | 14129147.311 | 1237873.2578 | 15379285.7164 | 10994656.442 | 0 | 984168.3945 | 0 | 16662801.1375 | 43353190.5492 | 29589443.3688 | 132330566.1771 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 152044322.8875 | 180657985.5109 | 56234.1325 | 51.123 | 2974.0885 | 3533.7909 | 60.6308 | 72.0411
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.983 | 124.4334 | 13.3387 | 4 | 2914.0135 | 3450.3043 | 59.4061 | 70.3391 | 202.5775 | 0 | 231.3931 | 14465752.681 | 1266754.5211 | 15790044.1723 | 11422897.1424 | 0 | 887804.1729 | 0 | 17094968.549 | 44477601.5044 | 30356876.9501 | 135762699.6933 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 155476456.4038 | 184090119.0272 | 74989.4209 | 53.3547 | 2914.0135 | 3450.3043 | 59.4061 | 70.3391
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.5512 | 127.4939 | 13.7757 | 4 | 2867.9965 | 3387.2751 | 58.468 | 69.0542 | 202.01 | 0 | 247.2551 | 14719146.7459 | 1288484.4525 | 16099979.0205 | 11753508.8052 | 0 | 798004.7711 | 0 | 17417058.2801 | 45315612.915 | 30928836.9572 | 138320631.9475 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 158034388.6579 | 186648051.2814 | 100000 | 55.1027 | 2867.9965 | 3387.2751 | 58.468 | 69.0542
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.8307 | 129.8082 | 14.1144 | 4 | 2832.8543 | 3339.671 | 57.7516 | 68.0837 | 201.5638 | 0 | 324.6941 | 14909621.7838 | 1304812.2287 | 16333355.2525 | 12007033.4649 | 0 | 718337.4885 | 0 | 17656532.4852 | 45938675.6737 | 31354090.0927 | 140222458.4701 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 159936215.1805 | 188549877.8039 | 133352.1432 | 56.4576 | 2832.8543 | 3339.671 | 57.7516 | 68.0837
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 199.0561 | 131.5306 | 14.3728 | 4 | 2806.0833 | 3303.7885 | 57.2058 | 67.3522 | 201.2218 | 0 | 324.6669 | 15050766.1221 | 1316907.7502 | 16506508.5 | 12197912.6292 | 0 | 649483.0616 | 0 | 17831415.4446 | 46393685.2606 | 31664643.4853 | 141611322.2535 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 161325078.9639 | 189938741.5873 | 177827.941 | 57.4912 | 2806.0833 | 3303.7885 | 57.2058 | 67.3522
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.5038 | 132.825 | 14.57 | 4 | 2785.7304 | 3276.6984 | 56.7909 | 66.7999 | 200.959 | 0 | 407.4928 | 15156487.4892 | 1325965.6911 | 16636326.2855 | 12342590.6417 | 0 | 591970.5868 | 0 | 17960802.8708 | 46730324.8025 | 31894406.8899 | 142638875.2574 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 162352631.9679 | 190966294.5913 | 237137.3706 | 58.2801 | 2785.7304 | 3276.6984 | 56.7909 | 66.7999
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.2554 | 133.7433 | 14.715 | 4 | 2770.2799 | 3256.4104 | 56.4759 | 66.3863 | 200.7689 | 0 | 393.6466 | 15231322.8477 | 1332376.3829 | 16728280.5197 | 12445773.4858 | 0 | 543586.8976 | 0 | 18049722.6522 | 46961675.8338 | 32052308.7225 | 143345047.3422 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 163058804.0526 | 191672466.6761 | 316227.766 | 58.86 | 2770.2799 | 3256.4104 | 56.4759 | 66.3863
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.5419 | 134.4141 | 14.8231 | 4 | 2758.5747 | 3241.1595 | 56.2373 | 66.0754 | 200.6284 | 0 | 370.4673 | 15285892.7525 | 1337050.5286 | 16795365.8053 | 12521525.146 | 0 | 504229.9791 | 0 | 18113185.0425 | 47126791.9553 | 32165003.8683 | 143849045.0775 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 163562801.7879 | 192176464.4114 | 421696.5034 | 59.2925 | 2758.5747 | 3241.1595 | 56.2373 | 66.0754
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.446 | 134.8834 | 14.9017 | 4 | 2749.72 | 3229.761 | 56.0568 | 65.843 | 200.529 | 0 | 380.8212 | 15324028.4948 | 1340316.7547 | 16842263.9397 | 12574736.8866 | 0 | 472153.2832 | 0 | 18155864.75 | 47237835.7996 | 32240793.5737 | 144187993.4824 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 163901750.1928 | 192515412.8163 | 562341.3252 | 59.6067 | 2749.72 | 3229.761 | 56.0568 | 65.843
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 206.0935 | 135.2185 | 14.9593 | 4 | 2743.0311 | 3221.2219 | 55.9204 | 65.669 | 200.4574 | 0 | 360.7802 | 15351233.8439 | 1342646.6893 | 16875728.3053 | 12612839.5435 | 0 | 446571.2637 | 0 | 18185317.6619 | 47314466.2346 | 32293095.4202 | 144421898.9624 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164135655.6728 | 192749318.2963 | 749894.2093 | 59.8373 | 2743.0311 | 3221.2219 | 55.9204 | 65.669
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9754 | 134.6335 | 14.9262 | 4 | 2737.7524 | 3217.0045 | 55.8128 | 65.583 | 200.5761 | 0 | 359.5543 | 15303726.2381 | 1338577.9467 | 16817295.2159 | 12546943.4906 | 0 | 403376.7793 | 0 | 18099868.6715 | 47092145.4898 | 32141356.9436 | 143743290.7756 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 163457047.486 | 192070710.1094 | 1000000 | 59.7048 | 2737.7524 | 3217.0045 | 55.8128 | 65.583
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.3628 | 135.875 | 15.0565 | 4 | 2733.9346 | 3209.0406 | 55.735 | 65.4206 | 200.3182 | 0 | 376.659 | 15404481.1537 | 1347206.6054 | 16941245.4284 | 12687541.3609 | 0 | 415757.6416 | 0 | 18250530.5541 | 47484136.8032 | 32408899.0696 | 144939798.6169 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164653555.3273 | 193267217.9508 | 1333521.4322 | 60.2259 | 2733.9346 | 3209.0406 | 55.735 | 65.4206
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.6017 | 135.9977 | 15.0791 | 4 | 2731.1283 | 3205.5221 | 55.6777 | 65.3489 | 200.2915 | 0 | 350.3732 | 15414421.6478 | 1348057.8286 | 16953479.3616 | 12701591.2576 | 0 | 403845.4445 | 0 | 18260344.2606 | 47509670.0545 | 32426326.0383 | 145017735.8936 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164731492.604 | 193345155.2275 | 1778279.41 | 60.3163 | 2731.1283 | 3205.5221 | 55.6777 | 65.3489
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.7649 | 136.0813 | 15.0953 | 4 | 2729.0176 | 3202.9022 | 55.6347 | 65.2955 | 200.2732 | 0 | 363.0507 | 15421197.3962 | 1348638.0403 | 16961818.9014 | 12711184.3324 | 0 | 394544.6861 | 0 | 18266579.509 | 47525892.8918 | 32437398.4581 | 145067254.2154 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164781010.9259 | 193394673.5493 | 2371373.7057 | 60.3811 | 2729.0176 | 3202.9022 | 55.6347 | 65.2955
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.8964 | 136.1487 | 15.1079 | 4 | 2727.4309 | 3200.9204 | 55.6024 | 65.2551 | 200.2584 | 0 | 368.3376 | 15426658.3806 | 1349105.6629 | 16968540.5415 | 12718916.3122 | 0 | 387607.337 | 0 | 18271823.0113 | 47539535.4092 | 32446709.7566 | 145108896.4113 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164822653.1218 | 193436315.7452 | 3162277.6602 | 60.4315 | 2727.4309 | 3200.9204 | 55.6024 | 65.2551
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.9696 | 136.1861 | 15.1161 | 4 | 2726.239 | 3199.4707 | 55.5781 | 65.2255 | 200.2501 | 0 | 360.6582 | 15429684.6161 | 1349364.7968 | 16972265.4928 | 12723215.7413 | 0 | 382002.7271 | 0 | 18274048.0159 | 47545324.4147 | 32450660.8718 | 145126566.6765 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164840323.3869 | 193453986.0103 | 4216965.0343 | 60.4644 | 2726.239 | 3199.4707 | 55.5781 | 65.2255
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.0427 | 136.2235 | 15.1231 | 4 | 2725.3438 | 3198.3549 | 55.5598 | 65.2028 | 200.2419 | 0 | 352.5182 | 15432719.8502 | 1349624.6998 | 16976001.6033 | 12727517.0676 | 0 | 378022.1352 | 0 | 18276915.2889 | 47552784.471 | 32455752.5134 | 145149337.6296 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164863094.34 | 193476756.9635 | 5623413.2519 | 60.4926 | 2725.3438 | 3198.3549 | 55.5598 | 65.2028
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.0887 | 136.247 | 15.128 | 4 | 2724.6718 | 3197.5309 | 55.5461 | 65.186 | 200.2367 | 0 | 338.8042 | 15434622.0937 | 1349787.5857 | 16978343.1428 | 12730218.0395 | 0 | 374896.6913 | 0 | 18278468.3457 | 47556825.2061 | 32458510.3982 | 145161671.503 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164875428.2134 | 193489090.8368 | 7498942.0933 | 60.512 | 2724.6718 | 3197.5309 | 55.5461 | 65.186
1 | 5100 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.1204 | 136.2632 | 15.1315 | 4 | 2724.1675 | 3196.9168 | 55.5358 | 65.1735 | 200.2331 | 0 | 348.6822 | 15435931.1583 | 1349899.6784 | 16979954.5362 | 12732078.7932 | 0 | 372504.1502 | 0 | 18279443.6434 | 47559362.7306 | 32460242.3108 | 145169417.0011 | 961560.8286 | 18752195.8818 | 18752195.8818 | 1478867.319 | 8382599.4226 | 0 | 164883173.7116 | 193496836.335 | 10000000 | 60.5261 | 2724.1675 | 3196.9168 | 55.5358 | 65.1735
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.92292 | 0.25111 | 0.015884 | 4 | 338250.2673 | 799732.5606 | 6895.6892 | 16303.63 | 132.7177 | 0 | 63.5951 | 164076.1899 | 12410.9083 | 112008.7668 | 64539.6042 | 0 | 57733.6124 | 0 | 160199.9418 | 416807.387 | 284479.6061 | 1272256.0164 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21491001.8711 | 50811649.2965 | 100 | 0.063536 | 338250.2673 | 799732.5606 | 6895.6892 | 16303.63
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2008 | 0.396 | 0.032354 | 4 | 169850.1559 | 396409.9495 | 3462.6252 | 8081.353 | 147.0613 | 0 | 57.945 | 241305.9103 | 20274.7659 | 159647.9113 | 83380.1989 | 0 | 64515.0169 | 0 | 221958.2833 | 577489.9231 | 394148.7388 | 1762720.7484 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 21981466.6031 | 51302114.0285 | 133.3521 | 0.12942 | 169850.1559 | 396409.9495 | 3462.6252 | 8081.353
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.5491 | 0.61446 | 0.057554 | 4 | 98287.4706 | 225649.4125 | 2003.723 | 4600.1685 | 159.4143 | 0 | 64.5846 | 340609.7847 | 30773.9177 | 225543.0407 | 109008.1142 | 0 | 71695.3897 | 0 | 303275.7963 | 789061.4116 | 538550.627 | 2408518.082 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 22627263.9367 | 51947911.3621 | 177.8279 | 0.23022 | 98287.4706 | 225649.4125 | 2003.723 | 4600.1685
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0015 | 0.93634 | 0.091002 | 4 | 64336.8891 | 144886.1051 | 1311.5945 | 2953.6992 | 170.1368 | 0 | 324.4859 | 456867.5032 | 41327.5715 | 315922.3855 | 138527.1143 | 0 | 80679.6174 | 0 | 402996.4349 | 1048514.0576 | 715632.3891 | 3200467.0737 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 23419212.9284 | 52739860.3538 | 237.1374 | 0.36401 | 64336.8891 | 144886.1051 | 1311.5945 | 2953.6992
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.5849 | 1.3574 | 0.13491 | 4 | 45144.2944 | 99476.8522 | 920.3275 | 2027.9702 | 179.149 | 0 | 410.4777 | 592197.6823 | 53596.2831 | 425209.553 | 175660.1862 | 0 | 91115.4266 | 0 | 521733.8611 | 1357444.4843 | 926483.7532 | 4143441.2298 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 24362187.0845 | 53682834.5099 | 316.2278 | 0.53965 | 45144.2944 | 99476.8522 | 920.3275 | 2027.9702
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3045 | 1.8823 | 0.19021 | 4 | 33441.3726 | 71979.3402 | 681.7476 | 1467.3962 | 186.3209 | 0 | 527.1006 | 744470.8837 | 67378.5196 | 552316.3736 | 220926.2549 | 0 | 101655.5283 | 0 | 657831.5484 | 1711542.7492 | 1168163.095 | 5224284.9526 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 25443030.8073 | 54763678.2328 | 421.6965 | 0.76082 | 33441.3726 | 71979.3402 | 681.7476 | 1467.3962
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.2675 | 2.5905 | 0.26467 | 4 | 25315.963 | 53011.8793 | 516.1001 | 1080.7189 | 192.4218 | 0 | 86.8365 | 931313.6136 | 84257.5683 | 713091.0924 | 281238.9884 | 0 | 115314.6208 | 0 | 828834.1945 | 2156456.5569 | 1471825.9108 | 6582332.5457 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 26801078.4004 | 56121725.8259 | 562.3413 | 1.0587 | 25315.963 | 53011.8793 | 516.1001 | 1080.7189
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.5199 | 3.5168 | 0.3623 | 4 | 19636.8472 | 39868.9774 | 400.3237 | 812.783 | 197.3443 | 0 | 86.9196 | 1154329.6651 | 104360.665 | 910643.4012 | 359549.3342 | 0 | 131283.364 | 0 | 1037464.9075 | 2699270.8761 | 1842307.8374 | 8239210.0506 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 28457955.9053 | 57778603.3307 | 749.8942 | 1.4492 | 19636.8472 | 39868.9774 | 400.3237 | 812.783
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.14 | 4.7154 | 0.489 | 4 | 15576.1325 | 30566.22 | 317.5405 | 623.1337 | 201.1633 | 0 | 78.0309 | 1418804.61 | 128143.9038 | 1151454.4408 | 460705.8564 | 0 | 149695.7906 | 0 | 1290433.7946 | 3357444.0292 | 2291524.5385 | 10248206.9639 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 30466952.8187 | 59787600.2441 | 1000 | 1.956 | 15576.1325 | 30566.22 | 317.5405 | 623.1337
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.3178 | 6.3358 | 0.66008 | 4 | 12505.8457 | 23610.7724 | 254.9486 | 481.3375 | 204.3591 | 0 | 93.5154 | 1746990.4882 | 157578.2852 | 1458389.4849 | 596773.0535 | 0 | 173216.3274 | 0 | 1611849.5792 | 4193701.9694 | 2862287.7661 | 12800786.9538 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 33019532.8085 | 62340180.2339 | 1333.5214 | 2.6403 | 12505.8457 | 23610.7724 | 254.9486 | 481.3375
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.1869 | 8.4857 | 0.88753 | 4 | 10197.323 | 18456.3608 | 207.8862 | 376.2579 | 207.0033 | 0 | 109.6189 | 2146868.9107 | 193337.7893 | 1842394.0745 | 776650.8971 | 0 | 201146.9514 | 0 | 2012555.4629 | 5236256.4827 | 3573852.6437 | 15983063.2122 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 36201809.0669 | 65522456.4923 | 1778.2794 | 3.5501 | 10197.323 | 18456.3608 | 207.8862 | 376.2579
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 15.9802 | 11.3203 | 1.1874 | 4 | 8454.9478 | 14628.2372 | 172.3655 | 298.2164 | 208.9688 | 0 | 85.9131 | 2631708.413 | 236558.004 | 2320174.7609 | 1013936.4317 | 0 | 235217.19 | 0 | 2510661.9718 | 6532227.443 | 4458379.4537 | 19938863.6679 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 40157609.5226 | 69478256.9481 | 2371.3737 | 4.7496 | 8454.9478 | 14628.2372 | 172.3655 | 298.2164
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.0032 | 15.0767 | 1.5849 | 4 | 7115.0796 | 11740.2085 | 145.0505 | 239.34 | 210.4954 | 0 | 107.6742 | 3223142.6914 | 289101.5479 | 2917952.0407 | 1328198.5403 | 0 | 276708.2519 | 0 | 3133690.1982 | 8153219.0874 | 5564739.5591 | 24886751.917 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 45105497.7717 | 74426145.1971 | 3162.2777 | 6.3394 | 7115.0796 | 11740.2085 | 145.0505 | 239.34
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 27.6394 | 20.0416 | 2.1103 | 4 | 6075.8353 | 9549.3869 | 123.8641 | 194.6772 | 211.6719 | 0 | 103.5106 | 3943305.5123 | 352849.4584 | 3664206.2181 | 1743399.4849 | 0 | 327086.4627 | 0 | 3912030.3832 | 10178300.5892 | 6946899.2953 | 31068077.4041 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 51286823.2588 | 80607470.6842 | 4216.965 | 8.4411 | 6075.8353 | 9549.3869 | 123.8641 | 194.6772
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.3675 | 26.5735 | 2.8016 | 4 | 5263.5021 | 7879.9361 | 107.3036 | 160.6432 | 212.5717 | 0 | 112.6576 | 4816912.5777 | 429882.8588 | 4591896.6556 | 2289503.4552 | 0 | 388004.9776 | 0 | 4881318.2047 | 12700188.6725 | 8668139.7318 | 38765847.1338 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 58984592.9885 | 88305240.414 | 5623.4133 | 11.2063 | 5263.5021 | 7879.9361 | 107.3036 | 160.6432
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 47.7442 | 35.0844 | 3.7023 | 4 | 4625.2078 | 6605.0801 | 94.2911 | 134.6535 | 213.239 | 0 | 118.474 | 5867799.9025 | 522174.9331 | 5734882.8759 | 3001295.8281 | 0 | 461085.8521 | 0 | 6079023.3628 | 15816371.8109 | 10794998.7549 | 48277633.3203 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 68496379.175 | 97817026.6005 | 7498.9421 | 14.8094 | 4625.2078 | 6605.0801 | 94.2911 | 134.6535
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 62.3138 | 45.9436 | 4.8512 | 4 | 4124.7358 | 5635.7324 | 84.0883 | 114.892 | 213.6336 | 0 | 114.5039 | 7108214.4902 | 630658.3579 | 7115638.0835 | 3912204.5094 | 0 | 547522.593 | 0 | 7532552.8333 | 19598157.3331 | 13376145.0817 | 59821093.2821 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 80039839.1368 | 109360486.5622 | 10000 | 19.4048 | 4124.7358 | 5635.7324 | 84.0883 | 114.892
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 80.489 | 59.3169 | 6.2632 | 4 | 3737.6067 | 4907.961 | 76.1962 | 100.0554 | 213.5792 | 0 | 139.7856 | 8526252.5842 | 754156.3194 | 8729239.0487 | 5045837.512 | 0 | 648981.777 | 0 | 9244742.2241 | 24052922.9098 | 16416614.1241 | 73418746.4993 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 93637492.354 | 122958139.7795 | 13335.2143 | 25.0528 | 3737.6067 | 4907.961 | 76.1962 | 100.0554
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 102.2212 | 74.8605 | 7.8969 | 4 | 3447.1732 | 4375.4107 | 70.2753 | 89.1987 | 212.8365 | 0 | 135.1202 | 10064662.0184 | 887592.4423 | 10515648.6744 | 6394367.9391 | 0 | 765876.0534 | 0 | 11164977.3798 | 29048980.8904 | 19826526.3546 | 88668631.7524 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 108887377.6071 | 138208025.0325 | 17782.7941 | 31.5874 | 3447.1732 | 4375.4107 | 70.2753 | 89.1987
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 126.8279 | 91.6433 | 9.6462 | 4 | 3238.643 | 3998.547 | 66.0241 | 81.5158 | 211.2631 | 0 | 155.1132 | 11627097.5226 | 1022602.8222 | 12362725.5897 | 7908511.7745 | 0 | 897161.7643 | 0 | 13189058.7946 | 34315225.5357 | 23420846.5355 | 104743230.3391 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 124961976.1938 | 154282623.6193 | 23713.7371 | 38.5847 | 3238.643 | 3998.547 | 66.0241 | 81.5158
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 152.8863 | 108.4571 | 11.3818 | 4 | 3093.3429 | 3737.3672 | 63.062 | 76.1913 | 209.131 | 0 | 155.4271 | 13113064.5487 | 1150581.0105 | 14146212.8882 | 9496682.5908 | 0 | 1035255.0677 | 0 | 15187300.4813 | 39514240.5086 | 26969281.0836 | 120612618.1793 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 140831364.034 | 170152011.4594 | 31622.7766 | 45.5272 | 3093.3429 | 3737.3672 | 63.062 | 76.1913
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 173.2151 | 120.9085 | 12.7201 | 4 | 2994.0375 | 3570.3026 | 61.0375 | 72.7854 | 207.2851 | 0 | 148.799 | 14171720.5934 | 1241527.0993 | 15431176.8443 | 10725208.448 | 0 | 1087297.6349 | 0 | 16636202.9418 | 43283987.5 | 29542210.8658 | 132119331.9274 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 152338077.7821 | 181658725.2076 | 42169.6503 | 50.8805 | 2994.0375 | 3570.3026 | 61.0375 | 72.7854
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.1406 | 124.4809 | 13.2834 | 4 | 2921.2606 | 3473.0875 | 59.5538 | 70.8036 | 206.6936 | 0 | 212.8341 | 14469694.9476 | 1267092.6684 | 15794861.398 | 11111053.5969 | 0 | 943938.7586 | 0 | 16998790.1341 | 44227364.9977 | 30186085.3924 | 134998881.8938 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 155217627.7485 | 184538275.1739 | 56234.1325 | 53.1338 | 2921.2606 | 3473.0875 | 59.5538 | 70.8036
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.323 | 130.2367 | 13.9875 | 4 | 2863.7014 | 3387.751 | 58.3804 | 69.0639 | 205.6558 | 0 | 226.702 | 14944782.1108 | 1307825.6145 | 16376471.966 | 11683588.594 | 0 | 890522.8979 | 0 | 17629244.5614 | 45867678.0936 | 31305632.7854 | 140005746.6235 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 160224492.4782 | 189545139.9037 | 74989.4209 | 55.9501 | 2863.7014 | 3387.751 | 58.3804 | 69.0639
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 194.5519 | 133.1696 | 14.4144 | 4 | 2820.4141 | 3328.9436 | 57.498 | 67.865 | 205.098 | 0 | 271.718 | 15184588.4262 | 1328373.0264 | 16670849.3993 | 11995673.0086 | 0 | 796685.2312 | 0 | 17930705.9458 | 46652018.7775 | 31840961.4187 | 142399855.2338 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 162618601.0885 | 191939248.514 | 100000 | 57.6577 | 2820.4141 | 3328.9436 | 57.498 | 67.865
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.8346 | 135.5328 | 14.7578 | 4 | 2787.3518 | 3284.0496 | 56.8239 | 66.9498 | 204.6319 | 0 | 296.0811 | 15376735.835 | 1344830.6444 | 16907103.5306 | 12250214.2937 | 0 | 717842.2649 | 0 | 18172723.3618 | 47281698.4493 | 32270730.7334 | 144321879.1131 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 164540624.9678 | 193861272.3933 | 133352.1432 | 59.0312 | 2787.3518 | 3284.0496 | 56.8239 | 66.9498
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 202.023 | 137.2693 | 15.0175 | 4 | 2762.1612 | 3250.2697 | 56.3104 | 66.2611 | 204.279 | 0 | 350.5931 | 15517329.4906 | 1356869.1633 | 17080182.1883 | 12439360.2543 | 0 | 649269.5878 | 0 | 18346774.1669 | 47734542.9414 | 32579806.4043 | 145704134.1968 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 165922880.0515 | 195243527.4769 | 177827.941 | 60.0699 | 2762.1612 | 3250.2697 | 56.3104 | 66.2611
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.3614 | 138.5304 | 15.2116 | 4 | 2743.012 | 3224.8916 | 55.92 | 65.7438 | 204.017 | 0 | 364.1986 | 15619111.7137 | 1365582.587 | 17205592.7468 | 12577966.9005 | 0 | 591030.6063 | 0 | 18470120.9762 | 48055466.0373 | 32798843.0115 | 146683714.5794 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 166902460.4341 | 196223107.8595 | 237137.3706 | 60.8464 | 2743.012 | 3224.8916 | 55.92 | 65.7438
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 206.1324 | 139.478 | 15.3591 | 4 | 2728.4781 | 3205.7302 | 55.6237 | 65.3531 | 203.8167 | 0 | 356.0696 | 15695427.539 | 1372114.8764 | 17299685.7203 | 12682717.5138 | 0 | 543536.4169 | 0 | 18561458.0058 | 48293106.2526 | 32961037.3415 | 147409083.6663 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 167627829.521 | 196948476.9464 | 316227.766 | 61.4364 | 2728.4781 | 3205.7302 | 55.6237 | 65.3531
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.3823 | 140.1428 | 15.4665 | 4 | 2717.4674 | 3191.4056 | 55.3992 | 65.0611 | 203.6742 | 0 | 375.7741 | 15748875.8651 | 1376689.3061 | 17365615.2468 | 12756592.6823 | 0 | 504225.8594 | 0 | 18623279.5943 | 48453953.3443 | 33070818.7867 | 147900050.6849 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168118796.5396 | 197439443.965 | 421696.5034 | 61.866 | 2717.4674 | 3191.4056 | 55.3992 | 65.0611
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.2667 | 140.6111 | 15.5448 | 4 | 2709.1386 | 3180.6894 | 55.2295 | 64.8427 | 203.5728 | 0 | 337.0177 | 15786490.1247 | 1379908.3123 | 17412028.3356 | 12808850.4939 | 0 | 472323.3944 | 0 | 18665244.2577 | 48563136.7905 | 33145338.7322 | 148233320.4413 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168452066.296 | 197772713.7214 | 562341.3252 | 62.1792 | 2709.1386 | 3180.6894 | 55.2295 | 64.8427
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.9124 | 140.952 | 15.6029 | 4 | 2702.8471 | 3172.6432 | 55.1012 | 64.6786 | 203.4985 | 0 | 332.8294 | 15813844.982 | 1382249.196 | 17445789.9752 | 12846991.8664 | 0 | 447070.6335 | 0 | 18695019.1947 | 48640605.0689 | 33198212.424 | 148469783.3408 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168688529.1955 | 198009176.6209 | 749894.2093 | 62.4114 | 2702.8471 | 3172.6432 | 55.1012 | 64.6786
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.705 | 140.84 | 15.6135 | 4 | 2697.8501 | 3167.3265 | 54.9993 | 64.5702 | 203.5204 | 0 | 441.984 | 15804862.672 | 1381480.5495 | 17434703.189 | 12834703.2644 | 0 | 416538.9664 | 0 | 18670192.5701 | 48576011.2843 | 33154125.8388 | 148272618.3345 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168491364.1892 | 197812011.6146 | 1000000 | 62.4539 | 2697.8501 | 3167.3265 | 54.9993 | 64.5702
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.1808 | 141.6214 | 15.7009 | 4 | 2694.3179 | 3161.1799 | 54.9273 | 64.4449 | 203.3535 | 0 | 421.4244 | 15867509.399 | 1386841.1981 | 17512042.3217 | 12921936.8122 | 0 | 416967.7748 | 0 | 18761066.0273 | 48812445.3791 | 33315496.9667 | 148994305.8789 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169213051.7336 | 198533699.1591 | 1333521.4322 | 62.8037 | 2694.3179 | 3161.1799 | 54.9273 | 64.4449
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.4197 | 141.7465 | 15.7237 | 4 | 2691.6796 | 3157.8658 | 54.8735 | 64.3774 | 203.3256 | 0 | 394.0687 | 15877531.3714 | 1387698.7206 | 17524417.9346 | 12936041.301 | 0 | 405234.3628 | 0 | 18771060.2393 | 48838448.2687 | 33333244.4731 | 149073676.6716 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169292422.5263 | 198613069.9517 | 1778279.41 | 62.8947 | 2691.6796 | 3157.8658 | 54.8735 | 64.3774
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.5855 | 141.8332 | 15.7401 | 4 | 2689.6953 | 3155.395 | 54.8331 | 64.327 | 203.3062 | 0 | 386.4657 | 15884472.2573 | 1388292.6038 | 17532989.3916 | 12945825.3863 | 0 | 396106.758 | 0 | 18777597.6948 | 48855457.387 | 33344853.5459 | 149125595.0247 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169344340.8794 | 198664988.3048 | 2371373.7057 | 62.9604 | 2689.6953 | 3155.395 | 54.8331 | 64.327
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.7 | 141.893 | 15.7519 | 4 | 2688.2037 | 3153.5533 | 54.8027 | 64.2894 | 203.2927 | 0 | 409.7017 | 15889257.9223 | 1388702.0757 | 17538899.5643 | 12952581.3536 | 0 | 389040.2585 | 0 | 18781807.658 | 48866410.8477 | 33352329.5079 | 149159029.188 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169377775.0427 | 198698422.4681 | 3162277.6602 | 63.0078 | 2688.2037 | 3153.5533 | 54.8027 | 64.2894
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.7876 | 141.9387 | 15.7609 | 4 | 2687.0832 | 3152.1679 | 54.7798 | 64.2612 | 203.2824 | 0 | 410.143 | 15892917.9465 | 1389015.2331 | 17543419.7357 | 12957749.6333 | 0 | 383714.7762 | 0 | 18785058.7567 | 48874869.5396 | 33358102.7389 | 149184848.3601 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 169403594.2148 | 198724241.6402 | 4216965.0343 | 63.0437 | 2687.0832 | 3152.1679 | 54.7798 | 64.2612
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.6 | 140.779 | 15.6564 | 4 | 2686.1387 | 3154.3275 | 54.7606 | 64.3052 | 203.528 | 0 | 370.1662 | 15799963.3706 | 1381061.2948 | 17428656.3247 | 12828412.1678 | 0 | 346997.7371 | 0 | 18636185.449 | 48487531.7311 | 33093736.7256 | 148002544.8006 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168221290.6553 | 197541938.0807 | 5623413.2519 | 62.6257 | 2686.1387 | 3154.3275 | 54.7606 | 64.3052
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.482 | 141.2471 | 15.7025 | 4 | 2685.58 | 3152.3939 | 54.7492 | 64.2658 | 203.4288 | 0 | 358.1402 | 15837510.4686 | 1384274.2757 | 17475003.4871 | 12880559.3162 | 0 | 356380.7274 | 0 | 18694154.0272 | 48638354.0806 | 33196676.0782 | 148462912.461 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168681658.3157 | 198002305.7411 | 7498942.0933 | 62.8101 | 2685.58 | 3152.3939 | 54.7492 | 64.2658
1 | 5200 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 209.8083 | 141.4202 | 15.7216 | 4 | 2684.8844 | 3151.1321 | 54.735 | 64.2401 | 203.3922 | 0 | 396.666 | 15851383.4398 | 1385461.3622 | 17492131.0687 | 12899854.514 | 0 | 356911.7463 | 0 | 18714439.4311 | 48691132.5403 | 33232698.4615 | 148624012.5638 | 961560.8286 | 19257185.0261 | 19257185.0261 | 1478867.319 | 8584595.0803 | 0 | 168842758.4185 | 198163405.8439 | 10000000 | 62.8864 | 2684.8844 | 3151.1321 | 54.735 | 64.2401
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.95719 | 0.2727 | 0.018355 | 4 | 300730.6882 | 709833.4253 | 6130.8018 | 14470.9145 | 136.0137 | 0 | 49.5079 | 176595.9832 | 13661.7848 | 119372.651 | 67256.2532 | 0 | 58884.6638 | 0 | 169950.821 | 442177.1746 | 301795.0075 | 1349694.3391 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22079289.4289 | 52115125.7835 | 100 | 0.073419 | 300730.6882 | 709833.4253 | 6130.8018 | 14470.9145
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.235 | 0.42363 | 0.036238 | 4 | 155807.5315 | 363021.2902 | 3176.3473 | 7400.68 | 150.0918 | 0 | 44.7404 | 256719.2367 | 22139.5614 | 168118.9456 | 86894.2895 | 0 | 64999.9882 | 0 | 233560.0883 | 607675.4401 | 414750.9743 | 1854858.5242 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 22584453.614 | 52620289.9686 | 133.3521 | 0.14495 | 155807.5315 | 363021.2902 | 3176.3473 | 7400.68
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6 | 0.67125 | 0.063632 | 4 | 91456.5891 | 209462.3018 | 1864.4663 | 4270.1723 | 162.7979 | 0 | 254.8548 | 362237.4673 | 32738.1033 | 242068.8084 | 113131.3757 | 0 | 72723.7051 | 0 | 320930.7893 | 834996.0818 | 569901.9833 | 2548728.3142 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 23278323.4041 | 53314159.7587 | 177.8279 | 0.25453 | 91456.5891 | 209462.3018 | 1864.4663 | 4270.1723
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.0598 | 1.0079 | 0.098826 | 4 | 60933.1279 | 136915.105 | 1242.2042 | 2791.1996 | 173.4788 | 0 | 328.8608 | 480961.4367 | 43513.2177 | 335088.13 | 143075.7599 | 0 | 81353.8548 | 0 | 422757.0357 | 1099927.0875 | 750722.8384 | 3357399.3608 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 24086994.4506 | 54122830.8053 | 237.1374 | 0.3953 | 60933.1279 | 136915.105 | 1242.2042 | 2791.1996
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.6433 | 1.4412 | 0.14438 | 4 | 43351.0891 | 95357.9646 | 883.7706 | 1944.0011 | 182.373 | 0 | 405.7856 | 617526.7681 | 55890.4757 | 446073.675 | 180240.9679 | 0 | 90924.0447 | 0 | 542355.8133 | 1411098.5736 | 963103.7717 | 4307214.09 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 25036809.1798 | 55072645.5345 | 316.2278 | 0.57754 | 43351.0891 | 95357.9646 | 883.7706 | 1944.0011
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.3823 | 1.9963 | 0.20311 | 4 | 32199.3301 | 69169.9953 | 656.4269 | 1410.1239 | 189.67 | 0 | 541.8259 | 775767.1422 | 70208.1983 | 578904.0918 | 226887.3544 | 0 | 101365.9262 | 0 | 683721.758 | 1778903.7638 | 1214138.3716 | 5429896.6063 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 26159491.6962 | 56195328.0508 | 421.6965 | 0.81242 | 32199.3301 | 69169.9953 | 656.4269 | 1410.1239
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.3601 | 2.7369 | 0.28143 | 4 | 24476.7669 | 51157.7685 | 498.992 | 1042.9203 | 195.808 | 0 | 86.3819 | 967952.8588 | 87563.4888 | 745155.4477 | 288377.3148 | 0 | 114467.2591 | 0 | 859371.384 | 2235908.0598 | 1526053.1942 | 6824849.0072 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 27554444.097 | 57590280.4517 | 562.3413 | 1.1257 | 24476.7669 | 51157.7685 | 498.992 | 1042.9203
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.6294 | 3.7039 | 0.38398 | 4 | 19047.1254 | 38602.9144 | 388.3014 | 786.9726 | 200.7627 | 0 | 111.1991 | 1197185.7586 | 108218.6201 | 949217.3413 | 368105.5232 | 0 | 129705.4837 | 0 | 1073448.7635 | 2792893.488 | 1906207.1938 | 8524982.1723 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 29254577.2622 | 59290413.6168 | 749.8942 | 1.5359 | 19047.1254 | 38602.9144 | 388.3014 | 786.9726
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.3032 | 4.9793 | 0.51921 | 4 | 15099.2289 | 29561.597 | 307.8182 | 602.6531 | 204.6589 | 0 | 90.407 | 1474264.7494 | 133123.8732 | 1202735.6427 | 473162.2061 | 0 | 148428.2667 | 0 | 1338368.7478 | 3482160.9447 | 2376646.396 | 10628890.8265 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 31358485.9164 | 61394322.271 | 1000 | 2.0768 | 15099.2289 | 29561.597 | 307.8182 | 602.6531
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.4958 | 6.6684 | 0.69887 | 4 | 12152.2681 | 22896.6236 | 247.7404 | 466.7786 | 207.9715 | 0 | 88.4412 | 1811173.4206 | 163325.3441 | 1519333.7844 | 611361.024 | 0 | 170226.3155 | 0 | 1667413.7565 | 4338268.5609 | 2960957.4353 | 13242059.6414 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 33971654.7313 | 64007491.0859 | 1333.5214 | 2.7955 | 12152.2681 | 22896.6236 | 247.7404 | 466.7786
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.4064 | 8.9099 | 0.93723 | 4 | 9932.5465 | 17944.3748 | 202.4884 | 365.8204 | 210.5505 | 0 | 85.581 | 2222105.085 | 200054.0025 | 1915718.3846 | 794477.746 | 0 | 197170.1209 | 0 | 2078514.8823 | 5407869.3616 | 3690981.9599 | 16506891.543 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 37236486.6328 | 67272322.9875 | 1778.2794 | 3.7489 | 9932.5465 | 17944.3748 | 202.4884 | 365.8204
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.2775 | 11.8917 | 1.2542 | 4 | 8238.5408 | 14225.5113 | 167.9538 | 290.0063 | 212.5509 | 0 | 78.7772 | 2724953.2522 | 244854.403 | 2413401.5053 | 1038010.5794 | 0 | 230502.3451 | 0 | 2594171.6132 | 6749502.3997 | 4606674.0762 | 20602070.174 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 41331665.2639 | 71367501.6185 | 2371.3737 | 5.0169 | 8238.5408 | 14225.5113 | 167.9538 | 290.0063
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.3905 | 15.8332 | 1.6734 | 4 | 6937.8782 | 11425.0611 | 141.438 | 232.9153 | 214.0997 | 0 | 125.5717 | 3336833.5478 | 299181.426 | 3034510.7206 | 1359738.121 | 0 | 270783.4787 | 0 | 3237408.4447 | 8423072.6893 | 5748920.1873 | 25710448.6152 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 46440043.7051 | 76475880.0597 | 3162.2777 | 6.6937 | 6937.8782 | 11425.0611 | 141.438 | 232.9153
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.1385 | 21.0377 | 2.2271 | 4 | 5928.7397 | 9300.3719 | 120.8654 | 189.6007 | 215.2925 | 0 | 102.1758 | 4081266.1293 | 365035.1889 | 3809181.3757 | 1784425.519 | 0 | 319582.0864 | 0 | 4040201.2167 | 10511774.8068 | 7174502.301 | 32085968.6238 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 52815563.7137 | 82851400.0683 | 4216.965 | 8.9084 | 5928.7397 | 9300.3719 | 120.8654 | 189.6007
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 36.9937 | 27.8689 | 2.9541 | 4 | 5140.1111 | 7682.0229 | 104.7881 | 156.6084 | 216.2034 | 0 | 108.7533 | 4982460.9794 | 444447.4819 | 4770123.4187 | 2341687.6546 | 0 | 378267.4199 | 0 | 5037624.9122 | 13106866.6626 | 8945705.8164 | 40007184.3457 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 60736779.4355 | 90772615.7902 | 5623.4133 | 11.8162 | 5140.1111 | 7682.0229 | 104.7881 | 156.6084
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 48.5406 | 36.7727 | 3.9014 | 4 | 4519.4212 | 6444.0828 | 92.1345 | 131.3713 | 216.8772 | 0 | 104.3253 | 6067139.7148 | 539640.0299 | 5954617.2768 | 3068294.1144 | 0 | 448900.1466 | 0 | 6270650.6001 | 16314946.5743 | 11135286.2756 | 49799474.7324 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 70529069.8223 | 100564906.1769 | 7498.9421 | 15.6058 | 4519.4212 | 6444.0828 | 92.1345 | 131.3713
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 63.3273 | 48.1283 | 5.109 | 4 | 4032.5544 | 5502.2939 | 82.2091 | 112.1717 | 217.2639 | 0 | 126.1972 | 7347142.0951 | 651503.5263 | 7385059.2217 | 3998067.8711 | 0 | 532755.2742 | 0 | 7766665.9155 | 20207271.5499 | 13791878.0507 | 61680343.5045 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 82409938.5944 | 112445774.949 | 10000 | 20.4362 | 4032.5544 | 5502.2939 | 82.2091 | 112.1717
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 81.707 | 62.051 | 6.5867 | 4 | 3656.8261 | 4796.8374 | 74.5493 | 97.79 | 217.1747 | 0 | 124.9387 | 8804427.4825 | 778324.0425 | 9049664.2835 | 5150729.7588 | 0 | 630956.8284 | 0 | 9521499.9343 | 24772989.7008 | 16908074.5048 | 75616666.5356 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 96346261.6254 | 126382097.9801 | 13335.2143 | 26.347 | 3656.8261 | 4796.8374 | 74.5493 | 97.79
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 103.6368 | 78.1792 | 8.2903 | 4 | 3375.3865 | 4281.1403 | 68.8118 | 87.2768 | 216.3656 | 0 | 141.6598 | 10380878.6031 | 914956.2074 | 10886959.223 | 6518424.6913 | 0 | 744898.01 | 0 | 11483985.5266 | 29878974.6508 | 20393014.1507 | 91202091.0629 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 111931686.1527 | 141967522.5074 | 17782.7941 | 33.1611 | 3375.3865 | 4281.1403 | 68.8118 | 87.2768
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 128.3238 | 95.4691 | 10.1016 | 4 | 3174.0275 | 3917.369 | 64.7068 | 79.8609 | 214.7041 | 0 | 127.935 | 11971531.9387 | 1052302.2858 | 12773913.6008 | 8044572.8139 | 0 | 872878.4535 | 0 | 13538927.6461 | 35225512.5192 | 24042136.1063 | 107521775.3642 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 128251370.4541 | 158287206.8087 | 23713.7371 | 40.4065 | 3174.0275 | 3917.369 | 64.7068 | 79.8609
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 154.4092 | 112.7556 | 11.895 | 4 | 3033.4836 | 3664.7539 | 61.8417 | 74.711 | 212.4986 | 0 | 136.6018 | 13482216.8555 | 1182314.7237 | 14592982.8032 | 9641532.326 | 0 | 1008411.9546 | 0 | 15563908.8786 | 40494098.3054 | 27638054.1639 | 123603520.0109 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 144333115.1007 | 174368951.4554 | 31622.7766 | 47.58 | 3033.4836 | 3664.7539 | 61.8417 | 74.711
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 176.5519 | 126.6347 | 13.3629 | 4 | 2938.3393 | 3500.2654 | 59.902 | 71.3576 | 210.4047 | 0 | 162.5016 | 14648184.0613 | 1282400.0137 | 16013120.6066 | 10984898.5707 | 0 | 1087575.6209 | 0 | 17166309.7605 | 44663216.7026 | 30483563.1368 | 136329268.4731 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 157058863.5629 | 187094699.9176 | 42169.6503 | 53.4516 | 2938.3393 | 3500.2654 | 59.902 | 71.3576
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 185.2749 | 131.8525 | 14.0667 | 4 | 2869.1145 | 3402.9254 | 58.4908 | 69.3732 | 209.4975 | 0 | 208.962 | 15077080.3642 | 1319162.4455 | 16538810.7485 | 11509998.6296 | 0 | 984330.8381 | 0 | 17717459.3801 | 46097194.9564 | 31462282.7603 | 140706320.1227 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 161435915.2125 | 191471751.5672 | 56234.1325 | 56.2668 | 2869.1145 | 3402.9254 | 58.4908 | 69.3732
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 192.2339 | 135.9133 | 14.6303 | 4 | 2815.9525 | 3329.2008 | 57.407 | 67.8703 | 208.7457 | 0 | 232.5299 | 15407580.8649 | 1347472.0411 | 16945060.1992 | 11927383.4854 | 0 | 885621.0974 | 0 | 18140115.8983 | 47196860.5179 | 32212827.102 | 144062921.2061 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 164792516.296 | 194828352.6506 | 74989.4209 | 58.5211 | 2815.9525 | 3329.2008 | 57.407 | 67.8703
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 197.6607 | 139.0157 | 15.0723 | 4 | 2775.2562 | 3273.4538 | 56.5774 | 66.7338 | 208.1426 | 0 | 251.2481 | 15658215.0162 | 1368929.7589 | 17253798.3603 | 12251958.9318 | 0 | 795428.3601 | 0 | 18458048.8666 | 48024056.8845 | 32777405.6194 | 146587841.7977 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 167317436.8876 | 197353273.2422 | 100000 | 60.289 | 2775.2562 | 3273.4538 | 56.5774 | 66.7338
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.8601 | 141.3763 | 15.4154 | 4 | 2744.1824 | 3231.2899 | 55.9439 | 65.8742 | 207.6658 | 0 | 309.4038 | 15847867.9191 | 1385160.5477 | 17487790.6435 | 12502348.1194 | 0 | 716440.5153 | 0 | 18696447.0205 | 48644319.9788 | 33200747.9264 | 148481122.6707 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 169210717.7605 | 199246554.1151 | 133352.1432 | 61.6616 | 2744.1824 | 3231.2899 | 55.9439 | 65.8742
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9876 | 143.1114 | 15.6747 | 4 | 2720.5113 | 3199.5597 | 55.4613 | 65.2274 | 207.3049 | 0 | 351.3668 | 15986697.2475 | 1397038.4799 | 17659278.3133 | 12688485.5036 | 0 | 648013.6169 | 0 | 18868010.1329 | 49090692.0047 | 33505406.0061 | 149843621.305 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 170573216.3949 | 200609052.7495 | 177827.941 | 62.699 | 2720.5113 | 3199.5597 | 55.4613 | 65.2274
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.3117 | 144.388 | 15.87 | 4 | 2702.5181 | 3175.6736 | 55.0945 | 64.7404 | 207.0334 | 0 | 355.579 | 16088545.8594 | 1405750.6647 | 17785193.0827 | 12826697.1552 | 0 | 590456.3952 | 0 | 18991690.8313 | 49412483.8116 | 33725035.5264 | 150825853.3265 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 171555448.4163 | 201591284.7709 | 237137.3706 | 63.4799 | 2702.5181 | 3175.6736 | 55.0945 | 64.7404
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.548 | 144.5115 | 15.9415 | 4 | 2688.9126 | 3159.9451 | 54.8171 | 64.4198 | 207.0012 | 0 | 361.4661 | 16098382.5136 | 1406592.0189 | 17797358.8544 | 12840657.9168 | 0 | 523181.5419 | 0 | 18979807.4098 | 49381565.5864 | 33703933.2024 | 150731479.0441 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 171461074.1339 | 201496910.4885 | 316227.766 | 63.766 | 2688.9126 | 3159.9451 | 54.8171 | 64.4198
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.5233 | 144.4929 | 15.9848 | 4 | 2678.6811 | 3148.4383 | 54.6085 | 64.1852 | 207.0001 | 0 | 416.746 | 16096900.3143 | 1406465.2434 | 17795525.6469 | 12839109.1939 | 0 | 467243.187 | 0 | 18956044.9983 | 49319740.6662 | 33661736.424 | 150542765.6739 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 171272360.7638 | 201308197.1184 | 421696.5034 | 63.9391 | 2678.6811 | 3148.4383 | 54.6085 | 64.1852
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.4915 | 144.4716 | 16.0164 | 4 | 2670.9749 | 3139.8046 | 54.4514 | 64.0092 | 207.0008 | 0 | 382.5275 | 16095205.5198 | 1406320.284 | 17793429.5219 | 12837156.8822 | 0 | 423131.3152 | 0 | 18936544.974 | 49269005.6029 | 33627108.7008 | 150387902.8009 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 171117497.8907 | 201153334.2454 | 562341.3252 | 64.0656 | 2670.9749 | 3139.8046 | 54.4514 | 64.0092
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9498 | 149.0094 | 16.4618 | 4 | 2665.0833 | 3121.2266 | 54.3313 | 63.6304 | 206.0001 | 0 | 378.2579 | 16455137.125 | 1437096.8874 | 18239149.6138 | 13330429.9878 | 0 | 504755.5284 | 0 | 19486961.9655 | 50701077.7087 | 34604527.3391 | 154759136.1556 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175488731.2454 | 205524567.6 | 749894.2093 | 65.8474 | 2665.0833 | 3121.2266 | 54.3313 | 63.6304
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9472 | 149.0055 | 16.4822 | 4 | 2660.5343 | 3116.1135 | 54.2386 | 63.5262 | 205.9986 | 0 | 404.9799 | 16454830.7535 | 1437070.6983 | 18238769.7479 | 13330212.5842 | 0 | 479007.3367 | 0 | 19476557.5371 | 50674007.5202 | 34586051.3792 | 154676507.5572 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175406102.647 | 205441939.0017 | 1000000 | 65.9289 | 2660.5343 | 3116.1135 | 54.2386 | 63.5262
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9233 | 148.9917 | 16.4975 | 4 | 2656.8899 | 3112.0475 | 54.1643 | 63.4433 | 206.0004 | 0 | 389.0734 | 16453739.0562 | 1436977.3783 | 18237416.1734 | 13328867.6802 | 0 | 457712.5235 | 0 | 19466737.9965 | 50648459.0899 | 34568614.0506 | 154598523.9485 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175328119.0384 | 205363955.393 | 1333521.4322 | 65.99 | 2656.8899 | 3112.0475 | 54.1643 | 63.4433
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9231 | 148.9899 | 16.5087 | 4 | 2654.3779 | 3109.2268 | 54.1131 | 63.3858 | 205.9993 | 0 | 400.6004 | 16453594.9777 | 1436965.0622 | 18237237.534 | 13328743.9071 | 0 | 443014.8675 | 0 | 19460826.9759 | 50633079.8269 | 34558117.3876 | 154551580.5389 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175281175.6288 | 205317011.9834 | 1778279.41 | 66.0347 | 2654.3779 | 3109.2268 | 54.1131 | 63.3858
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.9811 | 16.5164 | 4 | 2652.4918 | 3107.1285 | 54.0746 | 63.343 | 206.0003 | 0 | 390.3604 | 16452904.4858 | 1436906.0378 | 18236381.4124 | 13327917.0953 | 0 | 431647.3384 | 0 | 19455444.9842 | 50619076.9883 | 34548560.1625 | 154508838.5046 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175238433.5944 | 205274269.9491 | 2371373.7057 | 66.0656 | 2652.4918 | 3107.1285 | 54.0746 | 63.343
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.9801 | 16.5227 | 4 | 2651.0746 | 3105.5384 | 54.0457 | 63.3106 | 205.9997 | 0 | 388.2549 | 16452823.9065 | 1436899.1497 | 18236281.5047 | 13327838.0317 | 0 | 423190.4786 | 0 | 19452042.8978 | 50610225.4574 | 34542518.8108 | 154481820.2371 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175211415.327 | 205247251.6816 | 3162277.6602 | 66.0907 | 2651.0746 | 3105.5384 | 54.0457 | 63.3106
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.9795 | 16.5274 | 4 | 2650.0117 | 3104.3456 | 54.0241 | 63.2863 | 205.9992 | 0 | 385.1554 | 16452774.9493 | 1436894.9648 | 18236220.8043 | 13327828.4288 | 0 | 416798.7899 | 0 | 19449501.9955 | 50603614.5508 | 34538006.7312 | 154461641.2146 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175191236.3045 | 205227072.6591 | 4216965.0343 | 66.1096 | 2650.0117 | 3104.3456 | 54.0241 | 63.2863
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.979 | 16.5309 | 4 | 2649.2138 | 3103.4504 | 54.0078 | 63.268 | 205.9989 | 0 | 390.2071 | 16452738.2246 | 1436891.8255 | 18236175.2704 | 13327821.2255 | 0 | 411976.6944 | 0 | 19447585.2638 | 50598627.6081 | 34534603.0403 | 154446419.1527 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175176014.2425 | 205211850.5971 | 5623413.2519 | 66.1238 | 2649.2138 | 3103.4504 | 54.0078 | 63.268
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.9787 | 16.5336 | 4 | 2648.6151 | 3102.7787 | 53.9956 | 63.2543 | 205.9986 | 0 | 388.1912 | 16452710.6781 | 1436889.4708 | 18236141.1165 | 13327815.8225 | 0 | 408343.9134 | 0 | 19446141.3905 | 50594870.946 | 34532039.0413 | 154434952.3792 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175164547.469 | 205200383.8237 | 7498942.0933 | 66.1344 | 2648.6151 | 3102.7787 | 53.9956 | 63.2543
1 | 5300 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.9083 | 148.9784 | 16.5356 | 4 | 2648.1658 | 3102.2748 | 53.9864 | 63.2441 | 205.9984 | 0 | 385.4076 | 16452690.0174 | 1436887.7047 | 18236115.4999 | 13327811.7701 | 0 | 405610.1309 | 0 | 19445054.8979 | 50592044.1152 | 34530109.6712 | 154426323.8073 | 961560.8286 | 19768034.2612 | 19768034.2612 | 1478867.319 | 8788934.7744 | 0 | 175155918.8971 | 205191755.2518 | 10000000 | 66.1424 | 2648.1658 | 3102.2748 | 53.9864 | 63.2441
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 0.97664 | 0.28705 | 0.020295 | 4 | 278932.7057 | 657832.0753 | 5686.4205 | 13410.7966 | 138.4068 | 0 | 54.1435 | 185035.2871 | 14543.7546 | 124176.4578 | 68684.8097 | 0 | 58793.0364 | 0 | 175981.0048 | 457866.4758 | 312503.2779 | 1397584.104 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 22643888.5199 | 53403117.9309 | 100 | 0.08118 | 278932.7057 | 657832.0753 | 5686.4205 | 13410.7966
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.2739 | 0.45477 | 0.040679 | 4 | 142608.6112 | 331644.4095 | 2907.2694 | 6761.0199 | 153.3105 | 0 | 52.556 | 274086.4542 | 24355.7934 | 177496.369 | 90660.8994 | 0 | 65721.6687 | 0 | 246605.262 | 641616.3061 | 437916.3128 | 1958459.0655 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23204763.4814 | 53963992.8924 | 133.3521 | 0.16272 | 142608.6112 | 331644.4095 | 2907.2694 | 6761.0199
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.632 | 0.71547 | 0.06869 | 4 | 86976.158 | 198925.2089 | 1773.1266 | 4055.3595 | 165.6375 | 0 | 255.9335 | 378705.5996 | 34233.4624 | 254745.8918 | 115936.7525 | 0 | 72410.4894 | 0 | 333852.5563 | 868615.869 | 592848.1789 | 2651348.8 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 23897653.2159 | 54656882.6269 | 177.8279 | 0.27476 | 86976.158 | 198925.2089 | 1773.1266 | 4055.3595
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1182 | 1.0812 | 0.1069 | 4 | 57907.1202 | 129842.1114 | 1180.515 | 2647.0071 | 176.8137 | 0 | 341.1296 | 505147.6455 | 45706.657 | 354461.0198 | 147567.2476 | 0 | 81877.9368 | 0 | 442556.5976 | 1151441.4862 | 785882.4741 | 3514641.0647 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 24760945.4805 | 55520174.8916 | 237.1374 | 0.4276 | 57907.1202 | 129842.1114 | 1180.515 | 2647.0071
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.7016 | 1.5268 | 0.15414 | 4 | 41710.9255 | 91598.9284 | 850.3336 | 1867.3681 | 185.5949 | 0 | 424.2788 | 642977.2775 | 58194.998 | 467155.3014 | 184774.8579 | 0 | 90505.5224 | 0 | 563007.1033 | 1464828.9942 | 999775.8877 | 4471219.9424 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 25717524.3582 | 56476753.7693 | 316.2278 | 0.61657 | 41710.9255 | 91598.9284 | 850.3336 | 1867.3681
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.4601 | 2.113 | 0.2164 | 4 | 31057.0487 | 66592.5145 | 633.1399 | 1357.5785 | 193.0153 | 0 | 550.159 | 807284.6842 | 73056.885 | 605825.514 | 232804.4165 | 0 | 100847.5562 | 0 | 709729.4318 | 1846570.3961 | 1260322.2385 | 5636441.1224 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 26882745.5383 | 57641974.9493 | 421.6965 | 0.86559 | 31057.0487 | 66592.5145 | 633.1399 | 1357.5785
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.4527 | 2.887 | 0.29871 | 4 | 23697.5372 | 49440.5641 | 483.1063 | 1007.9128 | 199.1901 | 0 | 85.346 | 1004904.0637 | 90896.2649 | 777655.8266 | 295502.783 | 0 | 113339.7619 | 0 | 890096.493 | 2315848.491 | 1580614.181 | 7068857.8651 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 28315162.281 | 59074391.692 | 562.3413 | 1.1949 | 23697.5372 | 49440.5641 | 483.1063 | 1007.9128
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.7562 | 3.9094 | 0.40757 | 4 | 18452.9811 | 37320.3954 | 376.189 | 760.8267 | 204.2286 | 0 | 93.7538 | 1243512.6267 | 112387.2116 | 991118.435 | 377798.3592 | 0 | 128447.1165 | 0 | 1112772.8621 | 2895206.726 | 1976038.0811 | 8837281.4181 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 30083585.8339 | 60842815.245 | 749.8942 | 1.6303 | 18452.9811 | 37320.3954 | 376.189 | 760.8267
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.4541 | 5.2417 | 0.5496 | 4 | 14667.7034 | 28659.3864 | 299.021 | 584.2604 | 208.1239 | 0 | 101.2226 | 1528547.4423 | 137995.7534 | 1253169.818 | 485199.4914 | 0 | 146325.2972 | 0 | 1384982.7429 | 3603440.998 | 2459422.5244 | 10999084.0676 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 32245388.4835 | 63004617.8945 | 1000 | 2.1984 | 14667.7034 | 28659.3864 | 299.021 | 584.2604
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.681 | 7.0107 | 0.73884 | 4 | 11821.2051 | 22229.1194 | 240.9913 | 453.1707 | 211.52 | 0 | 82.0887 | 1876247.2838 | 169149.1942 | 1581405.7401 | 626148.6256 | 0 | 167004.0983 | 0 | 1723782.4274 | 4484928.2798 | 3061055.707 | 13689721.3564 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 34936025.7723 | 65695255.1833 | 1333.5214 | 2.9554 | 11821.2051 | 22229.1194 | 240.9913 | 453.1707
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.6622 | 9.3737 | 0.99119 | 4 | 9666.1646 | 17424.3031 | 197.0578 | 355.218 | 214.1149 | 0 | 97.3515 | 2303193.1456 | 207288.6202 | 1995096.5327 | 814746.6442 | 0 | 193530.5118 | 0 | 2150403.6272 | 5594909.1296 | 3818640.4448 | 17077808.656 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 38324113.0719 | 69083342.4829 | 1778.2794 | 3.9648 | 9666.1646 | 17424.3031 | 197.0578 | 355.218
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.5916 | 12.4917 | 1.3244 | 4 | 8029.2174 | 13835.2879 | 163.6865 | 282.0511 | 216.1318 | 0 | 101.6024 | 2821484.5189 | 253438.1491 | 2510333.2233 | 1063406.164 | 0 | 225378.8386 | 0 | 2680875.9486 | 6975089.2951 | 4760641.7677 | 21290647.9054 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 42536952.3213 | 73296181.7323 | 2371.3737 | 5.2978 | 8029.2174 | 13835.2879 | 163.6865 | 282.0511
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 21.7802 | 16.612 | 1.765 | 4 | 6769.275 | 11126.0268 | 138.0008 | 226.8191 | 217.6963 | 0 | 93.3006 | 3452255.8662 | 309408.4374 | 3153345.5299 | 1391801.1806 | 0 | 263895.1582 | 0 | 3342575.4072 | 8696695.553 | 5935673.4142 | 26545650.5466 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 47791954.9625 | 78551184.3735 | 3162.2777 | 7.0601 | 6769.275 | 11126.0268 | 138.0008 | 226.8191
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 28.6527 | 22.0721 | 2.3488 | 4 | 5787.5953 | 9061.5285 | 117.988 | 184.7315 | 218.9066 | 0 | 97.2586 | 4222585.4715 | 377509.3219 | 3958305.4794 | 1826809.1701 | 0 | 311125.1104 | 0 | 4171570.4758 | 10853570.6713 | 7407785.0017 | 33129260.7022 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 54375565.1181 | 85134794.5291 | 4216.965 | 9.3952 | 5787.5953 | 9061.5285 | 117.988 | 184.7315
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 37.669 | 29.2374 | 3.1151 | 4 | 5020.204 | 7488.7826 | 102.3436 | 152.669 | 219.83 | 0 | 115.6288 | 5154970.7152 | 459613.9885 | 4956604.0883 | 2397524.675 | 0 | 367922.0191 | 0 | 5201287.8395 | 13532684.0276 | 9236334.9177 | 41306942.2709 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 62553246.6867 | 93312476.0978 | 5623.4133 | 12.4603 | 5020.204 | 7488.7826 | 102.3436 | 152.669
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 49.3884 | 38.5455 | 4.1106 | 4 | 4417.1044 | 6287.8106 | 90.0486 | 128.1855 | 220.5079 | 0 | 126.6542 | 6273673.515 | 557722.332 | 6183189.6834 | 3139278.2163 | 0 | 435760.3544 | 0 | 6469953.3994 | 16833491.5754 | 11489203.8939 | 51382272.9699 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 72628577.3858 | 103387806.7968 | 7498.9421 | 16.4426 | 4417.1044 | 6287.8106 | 90.0486 | 128.1855
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 64.3795 | 50.3989 | 5.3776 | 4 | 3943.9638 | 5373.9207 | 80.403 | 109.5546 | 220.8834 | 0 | 124.6911 | 7592225.3646 | 672869.7565 | 7662495.8815 | 4087304.4329 | 0 | 516428.2373 | 0 | 8007216.2324 | 20833134.1308 | 14219042.1224 | 63590716.1584 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 84837020.5743 | 115596249.9853 | 10000 | 21.5106 | 3943.9638 | 5373.9207 | 80.403 | 109.5546
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 82.9789 | 64.8918 | 6.9235 | 4 | 3579.2176 | 4689.8935 | 72.9672 | 95.6098 | 220.7555 | 0 | 124.6634 | 9089815.3152 | 803099.6282 | 9379627.4094 | 5260098.0025 | 0 | 611279.5758 | 0 | 9806128.7731 | 25513535.5541 | 17413512.2664 | 77877096.5248 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 99123400.9407 | 129882630.3517 | 13335.2143 | 27.6942 | 3579.2176 | 4689.8935 | 72.9672 | 95.6098
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 105.0789 | 81.59 | 8.696 | 4 | 3306.7481 | 4191.0408 | 67.4125 | 85.44 | 219.8772 | 0 | 128.3274 | 10701949.8909 | 942719.1243 | 11265310.8136 | 6645387.2169 | 0 | 721645.6056 | 0 | 11808034.934 | 30722084.7374 | 20968454.109 | 93775586.4318 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 115021890.8476 | 145781120.2587 | 17782.7941 | 34.784 | 3306.7481 | 4191.0408 | 67.4125 | 85.44
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 129.8831 | 99.4114 | 10.5717 | 4 | 3112.251 | 3839.6469 | 63.4474 | 78.2764 | 218.1219 | 0 | 148.6157 | 12322405.9637 | 1082534.7785 | 13194187.5552 | 8185866.0585 | 0 | 846817.1123 | 0 | 13896406.4726 | 36155599.0968 | 24676939.3069 | 110360756.3445 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 131607060.7604 | 162366290.1714 | 23713.7371 | 42.2868 | 3112.251 | 3839.6469 | 63.4474 | 78.2764
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 155.9459 | 117.1332 | 12.4195 | 4 | 2976.4234 | 3595.5934 | 60.6784 | 73.301 | 215.8473 | 0 | 151.9449 | 13854117.3448 | 1214261.9032 | 15044491.8643 | 9788498.2126 | 0 | 979023.1149 | 0 | 15943353.0516 | 41481334.2088 | 28311862.9537 | 126616942.6539 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 147863247.0698 | 178622476.4808 | 31622.7766 | 49.6782 | 2976.4234 | 3595.5934 | 60.6784 | 73.301
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 179.8971 | 132.4776 | 14.0218 | 4 | 2885.0476 | 3433.4644 | 58.8156 | 69.9958 | 213.4911 | 0 | 158.3954 | 15128138.9076 | 1323537.0207 | 16601506.2821 | 11246422.9057 | 0 | 1085214.565 | 0 | 17700079.6757 | 46051976.5305 | 31431420.2555 | 140568296.1428 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 161814600.5587 | 192573829.9697 | 42169.6503 | 56.0873 | 2885.0476 | 3433.4644 | 58.8156 | 69.9958
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 188.5151 | 137.7268 | 14.7302 | 4 | 2820.0479 | 3342.0902 | 57.4905 | 68.133 | 212.5547 | 0 | 176.0778 | 15554279.232 | 1360032.551 | 17125698.9292 | 11766867.7037 | 0 | 980903.558 | 0 | 18247234.9698 | 47475562.3688 | 32403046.842 | 144913626.1543 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 166159930.5702 | 196919159.9812 | 56234.1325 | 58.921 | 2820.0479 | 3342.0902 | 57.4905 | 68.133
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.4035 | 141.8183 | 15.2971 | 4 | 2770.1531 | 3272.8511 | 56.4733 | 66.7215 | 211.7784 | 0 | 179.3374 | 15883280.3588 | 1388190.6219 | 17531517.4591 | 12181285.0182 | 0 | 882200.6284 | 0 | 18667924.8937 | 48570111.2554 | 33150098.9478 | 148254609.1833 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 169500913.5992 | 200260143.0102 | 74989.4209 | 61.1883 | 2770.1531 | 3272.8511 | 56.4733 | 66.7215
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 200.7593 | 144.9339 | 15.7401 | 4 | 2731.9701 | 3220.5189 | 55.6949 | 65.6546 | 211.1578 | 0 | 256.9477 | 16132014.1576 | 1409468.5152 | 17838960.124 | 12502558.4148 | 0 | 792260.4058 | 0 | 18983352.0308 | 49390787.9633 | 33710227.6642 | 150759629.2759 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 172005933.6917 | 202765163.1028 | 100000 | 62.9604 | 2731.9701 | 3220.5189 | 55.6949 | 65.6546
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 204.9151 | 147.3104 | 16.0842 | 4 | 2702.8197 | 3180.9159 | 55.1006 | 64.8473 | 210.6662 | 0 | 275.8036 | 16320737.4967 | 1425606.943 | 18072586.1469 | 12751020.927 | 0 | 713958.4594 | 0 | 19220724.8895 | 50008383.4498 | 34131749.274 | 152644767.5864 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 173891072.0023 | 204650301.4133 | 133352.1432 | 64.3369 | 2702.8197 | 3180.9159 | 55.1006 | 64.8473
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.0233 | 149.0641 | 16.3447 | 4 | 2680.6162 | 3151.0939 | 54.648 | 64.2393 | 210.2927 | 0 | 330.794 | 16459454.7314 | 1437465.9615 | 18244503.0415 | 12936467.2562 | 0 | 646474.1725 | 0 | 19392502.4136 | 50455313.331 | 34436788.1014 | 154008969.0091 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 175255273.425 | 206014502.836 | 177827.941 | 65.3787 | 2680.6162 | 3151.0939 | 54.648 | 64.2393
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.3083 | 150.3403 | 16.5393 | 4 | 2663.7403 | 3128.6814 | 54.3039 | 63.7824 | 210.0147 | 0 | 330.4352 | 16560118.5846 | 1446070.0869 | 18369361.6454 | 13072685.255 | 0 | 589468.5837 | 0 | 19514704.6207 | 50773258.4068 | 34653792.1488 | 154979459.332 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 176225763.7479 | 206984993.1589 | 237137.3706 | 66.1573 | 2663.7403 | 3128.6814 | 54.3039 | 63.7824
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 212.0445 | 151.3021 | 16.6873 | 4 | 2650.9329 | 3111.7508 | 54.0429 | 63.4372 | 209.8018 | 0 | 400.3847 | 16635822.2677 | 1452539.8413 | 18463317.3276 | 13175911.036 | 0 | 543204.4536 | 0 | 19605610.0212 | 51009775.6116 | 34815220.001 | 155701400.5599 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 176947704.9758 | 207706934.3868 | 316227.766 | 66.7492 | 2650.9329 | 3111.7508 | 54.0429 | 63.4372
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.2749 | 151.9796 | 16.7952 | 4 | 2641.2318 | 3099.0902 | 53.8451 | 63.1791 | 209.6497 | 0 | 415.4768 | 16689060.7239 | 1457089.2063 | 18529420.3738 | 13249016.3727 | 0 | 505057.3281 | 0 | 19667561.1618 | 51170959.7716 | 34925231.5022 | 156193396.4403 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 177439700.8562 | 208198930.2672 | 421696.5034 | 67.1807 | 2641.2318 | 3099.0902 | 53.8451 | 63.1791
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.1593 | 152.4643 | 16.8744 | 4 | 2633.8948 | 3089.6033 | 53.6955 | 62.9857 | 209.5398 | 0 | 375.7166 | 16727117.7941 | 1460341.042 | 18576688.1763 | 13301545.8573 | 0 | 474330.2005 | 0 | 19710608.9974 | 51282961.4093 | 35001674.9214 | 156535268.3983 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 177781572.8142 | 208540802.2252 | 562341.3252 | 67.4976 | 2633.8948 | 3089.6033 | 53.6955 | 62.9857
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.7829 | 152.805 | 16.932 | 4 | 2628.3533 | 3082.5126 | 53.5825 | 62.8412 | 209.4619 | 0 | 398.5379 | 16753838.1414 | 1462624.0772 | 18609882.7451 | 13338573.4508 | 0 | 449730.467 | 0 | 19739713.0638 | 51358684.22 | 35053357.2956 | 156766403.4608 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178012707.8767 | 208771937.2877 | 749894.2093 | 67.7278 | 2628.3533 | 3082.5126 | 53.5825 | 62.8412
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.7233 | 153.3199 | 17.0003 | 4 | 2623.9794 | 3076.3117 | 53.4934 | 62.7148 | 209.3462 | 0 | 408.0924 | 16794200.8353 | 1466072.5528 | 18660036.4603 | 13394439.2541 | 0 | 436006.0411 | 0 | 19792794.506 | 51496791.2442 | 35147618.1774 | 157187959.0712 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178434263.487 | 209193492.8981 | 1000000 | 68.0014 | 2623.9794 | 3076.3117 | 53.4934 | 62.7148
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.0593 | 153.5022 | 17.0318 | 4 | 2620.8957 | 3072.3931 | 53.4305 | 62.6349 | 209.3038 | 0 | 385.9265 | 16808481.0814 | 1467292.5634 | 18677784.0088 | 13414377.79 | 0 | 421529.3486 | 0 | 19807891.269 | 51536069.9247 | 35174426.684 | 157307852.67 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178554157.0858 | 209313386.4969 | 1333521.4322 | 68.1271 | 2620.8957 | 3072.3931 | 53.4305 | 62.6349
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.2787 | 153.621 | 17.0537 | 4 | 2618.5749 | 3069.4915 | 53.3832 | 62.5757 | 209.276 | 0 | 362.4962 | 16817781.4921 | 1468087.1144 | 18689343.5119 | 13427398.2143 | 0 | 410003.0955 | 0 | 19816919.237 | 51559558.8456 | 35190458.3551 | 157379549.866 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178625854.2819 | 209385083.6929 | 1778279.41 | 68.2149 | 2618.5749 | 3069.4915 | 53.3832 | 62.5757
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.4567 | 153.7173 | 17.0709 | 4 | 2616.8296 | 3067.293 | 53.3476 | 62.5309 | 209.2534 | 0 | 377.3911 | 16825323.071 | 1468731.3965 | 18698717.4879 | 13437957.6807 | 0 | 401413.7253 | 0 | 19824535.9109 | 51579375.8687 | 35203983.8806 | 157440039.0216 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178686343.4375 | 209445572.8485 | 2371373.7057 | 68.2835 | 2616.8296 | 3067.293 | 53.3476 | 62.5309
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.5734 | 153.7803 | 17.0829 | 4 | 2615.5178 | 3065.6645 | 53.3209 | 62.4977 | 209.2386 | 0 | 377.1507 | 16830255.2702 | 1469152.7533 | 18704848.3326 | 13444878.489 | 0 | 394660.9414 | 0 | 19829080.3568 | 51591199.5846 | 35212053.8097 | 157476129.5376 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178722433.9535 | 209481663.3645 | 3162277.6602 | 68.3316 | 2615.5178 | 3065.6645 | 53.3209 | 62.4977
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.8272 | 153.9188 | 17.1013 | 4 | 2614.3507 | 3064.0131 | 53.2971 | 62.4641 | 209.2074 | 0 | 338.0592 | 16841093.0692 | 1470078.6127 | 18718320.6946 | 13459952.0543 | 0 | 390734.1219 | 0 | 19843269.6355 | 51628117.1772 | 35237250.8252 | 157588816.1904 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178835120.6063 | 209594350.0173 | 4216965.0343 | 68.4052 | 2614.3507 | 3064.0131 | 53.2971 | 62.4641
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.7346 | 153.8673 | 17.0991 | 4 | 2613.7925 | 3063.5132 | 53.2857 | 62.4539 | 209.2181 | 0 | 369.779 | 16837066.1461 | 1469734.5997 | 18713314.7517 | 13454436.3113 | 0 | 385806.1965 | 0 | 19835539.6221 | 51608005.268 | 35223524.0338 | 157527426.9292 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178773731.345 | 209532960.7561 | 5623413.2519 | 68.3963 | 2613.7925 | 3063.5132 | 53.2857 | 62.4539
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.7781 | 153.8907 | 17.1039 | 4 | 2613.2371 | 3062.8321 | 53.2744 | 62.44 | 209.2125 | 0 | 380.4428 | 16838900.4135 | 1469891.2982 | 18715594.9468 | 13457017.0478 | 0 | 382818.2745 | 0 | 19837046.5725 | 51611926.0439 | 35226200.044 | 157539394.6411 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 178785699.057 | 209544928.468 | 7498942.0933 | 68.4154 | 2613.2371 | 3062.8321 | 53.2744 | 62.44
1 | 5400 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.1 | 155.1543 | 17.2245 | 4 | 2612.7863 | 3059.2328 | 53.2652 | 62.3666 | 208.9278 | 0 | 369.7264 | 16937681.8189 | 1478329.3554 | 18838432.3367 | 13594878.5942 | 0 | 411965.0573 | 0 | 19991901.9934 | 52014828.0838 | 35501188.965 | 158769206.2048 | 961560.8286 | 20284743.5872 | 20284743.5872 | 1478867.319 | 8995618.5048 | 0 | 180015510.6206 | 210774740.0317 | 10000000 | 68.8979 | 2612.7863 | 3059.2328 | 53.2652 | 62.3666
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0155 | 0.31309 | 0.023412 | 4 | 248356.3925 | 584621.2408 | 5063.081 | 11918.2948 | 141.9556 | 0 | 60.5164 | 199924.607 | 16123.1395 | 132781.4413 | 71894.9926 | 0 | 60161.3009 | 0 | 187545.3377 | 487954.4979 | 333038.9713 | 1489424.2883 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23258298.121 | 54749124.7157 | 100 | 0.093649 | 248356.3925 | 584621.2408 | 5063.081 | 11918.2948
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3128 | 0.49501 | 0.045556 | 4 | 130854.9924 | 303668.3355 | 2667.656 | 6190.6898 | 156.5187 | 0 | 60.5833 | 292795.1157 | 26387.5385 | 189747.548 | 94953.7964 | 0 | 66423.6961 | 0 | 261420.001 | 680161.2179 | 464224.0071 | 2076112.9207 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 23844986.7534 | 55335813.3481 | 133.3521 | 0.18222 | 130854.9924 | 303668.3355 | 2667.656 | 6190.6898
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.6903 | 0.78067 | 0.075638 | 4 | 81226.9717 | 185311.2195 | 1655.9217 | 3777.8199 | 169.2156 | 0 | 266.5703 | 402441.2249 | 36388.3325 | 273152.9209 | 120439.0856 | 0 | 73688.8398 | 0 | 353383.0574 | 919430.2266 | 627530.022 | 2806453.7096 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 24575327.5423 | 56066154.137 | 177.8279 | 0.30255 | 81226.9717 | 185311.2195 | 1655.9217 | 3777.8199
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.1571 | 1.1413 | 0.11391 | 4 | 55757.4353 | 124871.6362 | 1136.6907 | 2545.6772 | 179.7853 | 0 | 330.1778 | 524593.6803 | 47469.7853 | 370130.2239 | 150757.4821 | 0 | 81039.6215 | 0 | 457856.4093 | 1191248.4577 | 813051.5501 | 3636147.21 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 25405021.0428 | 56895847.6374 | 237.1374 | 0.45563 | 55757.4353 | 124871.6362 | 1136.6907 | 2545.6772
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.76 | 1.6145 | 0.16419 | 4 | 40205.9012 | 88155.942 | 819.6517 | 1797.1781 | 188.8147 | 0 | 428.9035 | 668599.8894 | 60514.4278 | 488494.084 | 189306.1084 | 0 | 89910.8254 | 0 | 583761.8806 | 1518828.6674 | 1036631.7743 | 4636047.6574 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 26404921.4901 | 57895748.0847 | 316.2278 | 0.65674 | 40205.9012 | 88155.942 | 819.6517 | 1797.1781
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.5379 | 2.2327 | 0.23011 | 4 | 30000.241 | 64213.156 | 611.5955 | 1309.072 | 196.3568 | 0 | 557.1298 | 839085.3902 | 75930.1573 | 633131.6372 | 238735.0932 | 0 | 100096.7542 | 0 | 735921.8225 | 1914717.624 | 1306834.1219 | 5844452.6005 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 27613326.4333 | 59104153.0279 | 421.6965 | 0.92044 | 30000.241 | 64213.156 | 611.5955 | 1309.072
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.5648 | 3.0565 | 0.31798 | 4 | 22888.7947 | 47647.0671 | 466.619 | 971.3499 | 202.6625 | 0 | 86.0704 | 1045981.832 | 94599.7295 | 813971.0914 | 303887.8373 | 0 | 112726.4068 | 0 | 924755.0898 | 2406023.0503 | 1642160.1707 | 7344105.2077 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 29112979.0404 | 60603805.635 | 562.3413 | 1.2719 | 22888.7947 | 47647.0671 | 466.619 | 971.3499
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.8754 | 4.1149 | 0.43142 | 4 | 17913.001 | 36161.4437 | 365.1808 | 737.1999 | 207.6649 | 0 | 77.1598 | 1289122.87 | 116489.5155 | 1032570.6454 | 387270.6515 | 0 | 126545.6366 | 0 | 1151279.7344 | 2995393.709 | 2044417.7556 | 9143090.5179 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 30911964.3507 | 62402790.9453 | 749.8942 | 1.7257 | 17913.001 | 36161.4437 | 365.1808 | 737.1999
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.6005 | 5.5065 | 0.58053 | 4 | 14268.7016 | 27829.9055 | 290.8868 | 567.3503 | 211.5718 | 0 | 87.6982 | 1582540.4871 | 142839.3626 | 1303564.1851 | 496795.025 | 0 | 143592.8636 | 0 | 1431039.4501 | 3723271.1027 | 2541209.0332 | 11364851.5095 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 33133725.3423 | 64624551.9369 | 1000 | 2.3221 | 14268.7016 | 27829.9055 | 290.8868 | 567.3503
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 9.8831 | 7.3746 | 0.78124 | 4 | 11497.937 | 21575.1564 | 234.401 | 439.8387 | 215.0585 | 0 | 104.6605 | 1944433.4364 | 175248.4227 | 1646740.7631 | 642142.4311 | 0 | 163752.4756 | 0 | 1783203.8362 | 4639530.5965 | 3166574.9649 | 14161626.9265 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 35930500.7592 | 67421327.3539 | 1333.5214 | 3.125 | 11497.937 | 21575.1564 | 234.401 | 439.8387
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 12.9058 | 9.8407 | 1.046 | 4 | 9418.9853 | 16945.3318 | 192.0188 | 345.4535 | 217.6637 | 0 | 103.1067 | 2383668.1091 | 214464.5384 | 2074222.6785 | 834473.1287 | 0 | 188831.3472 | 0 | 2221307.3228 | 5779386.0011 | 3944549.7002 | 17640902.826 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 39409776.6587 | 70900603.2534 | 1778.2794 | 4.1841 | 9418.9853 | 16945.3318 | 192.0188 | 345.4535
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 16.9011 | 13.1045 | 1.3966 | 4 | 7831.5245 | 13468.5081 | 159.6562 | 274.5738 | 219.7029 | 0 | 105.2858 | 2918698.0303 | 262077.4752 | 2608367.3436 | 1088764.986 | 0 | 219245.5661 | 0 | 2767889.8265 | 7201481.5563 | 4915159.1378 | 21981683.9218 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 43750557.7545 | 75241384.3492 | 2371.3737 | 5.5865 | 7831.5245 | 13468.5081 | 159.6562 | 274.5738
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.1869 | 17.4258 | 1.8609 | 4 | 6606.4013 | 10836.8875 | 134.6804 | 220.9246 | 221.2884 | 0 | 113.9523 | 3571218.8615 | 319942.6018 | 3276337.3489 | 1425270.2002 | 0 | 256280.8926 | 0 | 3451129.463 | 8979130.9387 | 6128441.3684 | 27407751.6752 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 49176625.5079 | 80667452.1026 | 3162.2777 | 7.4438 | 6606.4013 | 10836.8875 | 134.6804 | 220.9246
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.1669 | 23.1351 | 2.4745 | 4 | 5653.0384 | 8834.5934 | 115.2448 | 180.1051 | 222.5117 | 0 | 92.6527 | 4365830.289 | 390145.0834 | 4110081.2047 | 1869678.6061 | 0 | 301312.8466 | 0 | 4304448.7316 | 11199292.6358 | 7643747.3464 | 34184536.7437 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 55953410.5764 | 87444237.1711 | 4216.965 | 9.8979 | 5653.0384 | 8834.5934 | 115.2448 | 180.1051
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 38.3432 | 30.643 | 3.2813 | 4 | 4905.7921 | 7305.0333 | 100.0112 | 148.923 | 223.4472 | 0 | 99.3813 | 5329780.3697 | 474971.9732 | 5146337.0469 | 2454004.8609 | 0 | 355889.0089 | 0 | 5366783.4713 | 13963269.7135 | 9530218.496 | 42621254.9404 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 64390128.7731 | 95880955.3678 | 5623.4133 | 13.1253 | 4905.7921 | 7305.0333 | 100.0112 | 148.923
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 50.2527 | 40.3804 | 4.328 | 4 | 4318.8633 | 6137.8945 | 88.0459 | 125.1293 | 224.1292 | 0 | 115.795 | 6484610.6984 | 576176.7464 | 6417559.9188 | 3212278.5591 | 0 | 420894.3063 | 0 | 6673492.8893 | 17363059.5764 | 11850644.9361 | 52998717.6308 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 74767591.4636 | 106258418.0582 | 7498.9421 | 17.3119 | 4318.8633 | 6137.8945 | 88.0459 | 125.1293
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 65.4468 | 52.7416 | 5.6559 | 4 | 3859 | 5250.9486 | 78.6709 | 107.0477 | 224.4914 | 0 | 124.1768 | 7841832.7683 | 694614.1772 | 7946138.3483 | 4178646.2702 | 0 | 497975.0401 | 0 | 8252090.5756 | 21470246.9411 | 14653884.7068 | 65535428.8275 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 87304302.6603 | 118795129.2549 | 10000 | 22.6236 | 3859 | 5250.9486 | 78.6709 | 107.0477
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 84.2869 | 67.8323 | 7.2731 | 4 | 3504.6326 | 4587.0671 | 71.4467 | 93.5136 | 224.3214 | 0 | 136.2741 | 9381512.8546 | 828403.8062 | 9718134.6846 | 5373162.6426 | 0 | 589460.2375 | 0 | 10097362.9479 | 26271267.1366 | 17930679.6413 | 80189983.9514 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 101958857.7841 | 133449684.3788 | 13335.2143 | 29.0926 | 3504.6326 | 4587.0671 | 71.4467 | 93.5136
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 106.5721 | 85.1167 | 9.1164 | 4 | 3240.8231 | 4104.3978 | 66.0686 | 83.6737 | 223.3693 | 0 | 129.7831 | 11029971.2955 | 971061.7488 | 11653207.9983 | 6777034.5361 | 0 | 696265.6297 | 0 | 12139741.0713 | 31585116.0642 | 21557490.7231 | 96409889.0671 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 118178762.8998 | 149669589.4945 | 17782.7941 | 36.4657 | 3240.8231 | 4104.3978 | 66.0686 | 83.6737
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 131.4831 | 103.4593 | 11.0556 | 4 | 3053.0723 | 3765.1713 | 62.241 | 76.7581 | 221.5173 | 0 | 160.3954 | 12678622.3302 | 1113205.1646 | 13622265.6232 | 8330759.7875 | 0 | 818419.7211 | 0 | 14259676.3244 | 37100752.7342 | 25322026.0854 | 113245727.7706 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 135014601.6033 | 166505428.198 | 23713.7371 | 44.2225 | 3053.0723 | 3765.1713 | 62.241 | 76.7581
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 157.5468 | 121.6273 | 12.9589 | 4 | 2921.8237 | 3529.3362 | 59.5653 | 71.9503 | 219.172 | 0 | 148.631 | 14231878.2471 | 1246689.6252 | 15504531.1915 | 9940504.519 | 0 | 947639.7532 | 0 | 16329784.901 | 42486750.613 | 28998080.3088 | 129685859.1589 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 151454732.9917 | 182945559.5863 | 31622.7766 | 51.8357 | 2921.8237 | 3529.3362 | 59.5653 | 71.9503
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 182.9789 | 138.2689 | 14.6832 | 4 | 2833.9517 | 3370.1239 | 57.7739 | 68.7045 | 216.5727 | 0 | 152.9736 | 15598028.0853 | 1363777.7738 | 17179607.0208 | 11494057.8266 | 0 | 1075815.1542 | 0 | 18217401.4857 | 47397941.7629 | 32350069.1835 | 144676698.2928 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 166445572.1255 | 197936398.7202 | 42169.6503 | 58.7327 | 2833.9517 | 3370.1239 | 57.7739 | 68.7045
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 191.7749 | 143.7205 | 15.4097 | 4 | 2773.0239 | 3283.9161 | 56.5318 | 66.9471 | 215.5769 | 0 | 168.6635 | 16035321.017 | 1401197.9682 | 17719380.2839 | 12026808.7578 | 0 | 975191.9669 | 0 | 18781580.9976 | 48865821.1237 | 33351927.0091 | 149157229.1242 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 170926102.9569 | 202416929.5516 | 56234.1325 | 61.6389 | 2773.0239 | 3283.9161 | 56.5318 | 66.9471
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.6265 | 147.8567 | 15.9804 | 4 | 2726.2807 | 3218.9294 | 55.5789 | 65.6222 | 214.7721 | 0 | 215.8671 | 16364002.0404 | 1429305.9445 | 18126187.7008 | 12440002.8041 | 0 | 877343.1179 | 0 | 19202368.227 | 49960623.1794 | 34099151.9081 | 152498984.9222 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 174267858.7549 | 205758685.3495 | 74989.4209 | 63.9215 | 2726.2807 | 3218.9294 | 55.5789 | 65.6222
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 203.9413 | 150.9965 | 16.4249 | 4 | 2690.5138 | 3169.8293 | 54.8498 | 64.6213 | 214.1307 | 0 | 228.8178 | 16611778.6551 | 1450485.1231 | 18433471.6118 | 12759170.7952 | 0 | 788373.2914 | 0 | 19516878.9958 | 50778915.6848 | 34657653.3573 | 154996727.5144 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 176765601.3471 | 208256427.9418 | 100000 | 65.6996 | 2690.5138 | 3169.8293 | 54.8498 | 64.6213
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.0091 | 153.359 | 16.7669 | 4 | 2663.2195 | 3132.7569 | 54.2933 | 63.8655 | 213.6297 | 0 | 282.6105 | 16797265.2433 | 1466334.3581 | 18663844.7758 | 13002921.9316 | 0 | 710408.2117 | 0 | 19749902.063 | 51385193.9059 | 35071450.701 | 156847321.1904 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 178616195.0231 | 210107021.6178 | 133352.1432 | 67.0678 | 2663.2195 | 3132.7569 | 54.2933 | 63.8655
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.0707 | 155.1136 | 17.0266 | 4 | 2642.4372 | 3104.814 | 53.8697 | 63.2958 | 213.2469 | 0 | 321.7901 | 16934500.22 | 1478057.5992 | 18834474.6698 | 13186122.7494 | 0 | 643725.1085 | 0 | 19919983.3353 | 51827710.488 | 35373477.361 | 158198051.5313 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 179966925.3641 | 211457751.9587 | 177827.941 | 68.1064 | 2642.4372 | 3104.814 | 53.8697 | 63.2958
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.4017 | 156.4358 | 17.2246 | 4 | 2626.6434 | 3083.7043 | 53.5477 | 62.8655 | 212.9521 | 0 | 382.1458 | 17037634.1419 | 1486866.0776 | 18962808.0134 | 13325443.802 | 0 | 588606.8758 | 0 | 20046529.9752 | 52156958.8868 | 35598196.1585 | 159203043.9313 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 180971917.764 | 212462744.3587 | 237137.3706 | 68.8985 | 2626.6434 | 3083.7043 | 53.5477 | 62.8655
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.0607 | 157.3686 | 17.3693 | 4 | 2614.6589 | 3067.9131 | 53.3034 | 62.5436 | 212.7403 | 0 | 383.7443 | 17110244.6518 | 1493066.74 | 19053212.5079 | 13424336.8628 | 0 | 542390.8972 | 0 | 20133068.1472 | 52382113.459 | 35751868.7806 | 159890302.0464 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 181659175.8792 | 213150002.4738 | 316227.766 | 69.4772 | 2614.6589 | 3067.9131 | 53.3034 | 62.5436
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.2787 | 158.0495 | 17.4769 | 4 | 2605.5825 | 3056.0457 | 53.1183 | 62.3016 | 212.5837 | 0 | 371.4539 | 17163165.5382 | 1497585.5332 | 19119129.4723 | 13496906.3737 | 0 | 504985.4508 | 0 | 20194891.2236 | 52542964.4219 | 35861652.8679 | 160381280.8815 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 182150154.7143 | 213640981.3089 | 421696.5034 | 69.9077 | 2605.5825 | 3056.0457 | 53.1183 | 62.3016
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.1607 | 158.5403 | 17.5563 | 4 | 2598.7188 | 3047.1463 | 52.9784 | 62.1202 | 212.4697 | 0 | 377.9557 | 17201275.276 | 1500839.402 | 19166612.2177 | 13549436.8904 | 0 | 474972.6659 | 0 | 20238323.2163 | 52655965.5579 | 35938778.4652 | 160726203.6915 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 182495077.5243 | 213985904.1189 | 562341.3252 | 70.225 | 2598.7188 | 3047.1463 | 52.9784 | 62.1202
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 215.887 | 157.8213 | 17.5153 | 4 | 2593.4107 | 3042.8869 | 52.8702 | 62.0334 | 212.627 | 0 | 674.6249 | 17145440.3124 | 1496072.0589 | 19097048.81 | 13473419.038 | 0 | 423607.1612 | 0 | 20137879.0785 | 52394630.5152 | 35760411.9286 | 159928508.9029 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 181697382.7357 | 213188209.3303 | 749894.2093 | 70.0612 | 2593.4107 | 3042.8869 | 52.8702 | 62.0334
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.7419 | 159.4185 | 17.6836 | 4 | 2589.4719 | 3034.6702 | 52.7899 | 61.8659 | 212.2663 | 0 | 372.8086 | 17269385.9977 | 1506654.3142 | 19251504.123 | 13643617.4935 | 0 | 438181.9398 | 0 | 20322644.1086 | 52875351.2231 | 36088513.6896 | 161395852.8896 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183164726.7223 | 214655553.317 | 1000000 | 70.7344 | 2589.4719 | 3034.6702 | 52.7899 | 61.8659
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.0554 | 159.591 | 17.7139 | 4 | 2586.5893 | 3031.0259 | 52.7311 | 61.7916 | 212.2251 | 0 | 456.2979 | 17282748.4946 | 1507795.0562 | 19268163.3139 | 13662267.8443 | 0 | 423776.0152 | 0 | 20336452.7825 | 52911278.5599 | 36113034.8352 | 161505516.9018 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183274390.7346 | 214765217.3292 | 1333521.4322 | 70.8556 | 2586.5893 | 3031.0259 | 52.7311 | 61.7916
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220 | 160.1143 | 17.7735 | 4 | 2584.4293 | 3027.3747 | 52.6871 | 61.7171 | 212.1042 | 0 | 397.2573 | 17323271.2289 | 1511254.2919 | 19318692.3744 | 13718533.6095 | 0 | 422628.6018 | 0 | 20394808.2415 | 53063107.4941 | 36216661.2025 | 161968957.0446 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183737830.8774 | 215228657.472 | 1778279.41 | 71.0942 | 2584.4293 | 3027.3747 | 52.6871 | 61.7171
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.6 | 159.3348 | 17.7094 | 4 | 2582.6034 | 3027.1535 | 52.6499 | 61.7126 | 212.2808 | 0 | 412.3681 | 17262898.5014 | 1506100.475 | 19243416.6043 | 13635085.4002 | 0 | 390970.7489 | 0 | 20295003.9746 | 52803437.2642 | 36039430.935 | 161176343.9036 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 182945217.7363 | 214436044.331 | 2371373.7057 | 70.8375 | 2582.6034 | 3027.1535 | 52.6499 | 61.7126
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.6085 | 159.8948 | 17.767 | 4 | 2581.563 | 3024.6705 | 52.6287 | 61.662 | 212.1523 | 0 | 459.9762 | 17306277.7057 | 1509803.6614 | 19297500.9985 | 13695169.8534 | 0 | 398156.3806 | 0 | 20360694.3538 | 52974350.156 | 36156082.4955 | 161698035.6048 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183466909.4375 | 214957736.0322 | 3162277.6602 | 71.0682 | 2581.563 | 3024.6705 | 52.6287 | 61.662
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.6841 | 159.9361 | 17.7754 | 4 | 2580.6422 | 3023.5407 | 52.6099 | 61.639 | 212.1422 | 0 | 413.1782 | 17309474.9125 | 1510076.5898 | 19301487.8216 | 13699663.6476 | 0 | 393016.3766 | 0 | 20363350.5458 | 52981261.0226 | 36160799.304 | 161719130.2206 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183488004.0533 | 214978830.648 | 4216965.0343 | 71.1017 | 2580.6422 | 3023.5407 | 52.6099 | 61.639
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.7593 | 159.9773 | 17.7827 | 4 | 2579.9508 | 3022.6686 | 52.5958 | 61.6212 | 212.1323 | 0 | 452.175 | 17312667.1459 | 1510349.0924 | 19305468.5258 | 13704136.2372 | 0 | 389396.7121 | 0 | 20366586.9082 | 52989681.3737 | 36166546.3666 | 161744832.3619 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183513706.1946 | 215004532.7893 | 5623413.2519 | 71.1307 | 2579.9508 | 3022.6686 | 52.5958 | 61.6212
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.8083 | 160.0042 | 17.7877 | 4 | 2579.4318 | 3022.0236 | 52.5852 | 61.608 | 212.1257 | 0 | 438.9399 | 17314746.4031 | 1510526.5858 | 19308061.3969 | 13707055.0468 | 0 | 386565.74 | 0 | 20368512.5173 | 52994691.4137 | 36169965.8219 | 161760124.9256 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183528998.7583 | 215019825.3529 | 7498942.0933 | 71.1509 | 2579.4318 | 3022.0236 | 52.5852 | 61.608
1 | 5500 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.8519 | 160.028 | 17.7919 | 4 | 2579.0423 | 3021.531 | 52.5773 | 61.598 | 212.12 | 0 | 447.0113 | 17316593.975 | 1510684.3012 | 19310365.3816 | 13709644.2134 | 0 | 384529.3755 | 0 | 20370408.7262 | 52999624.9602 | 36173333.0687 | 161775184.0019 | 961560.8286 | 20807313.0041 | 20807313.0041 | 1478867.319 | 9204646.2715 | 0 | 183544057.8346 | 215034884.4293 | 10000000 | 71.1675 | 2579.0423 | 3021.531 | 52.5773 | 61.598
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0452 | 0.33534 | 0.026355 | 4 | 226367.0905 | 532100.4906 | 4614.7993 | 10847.5882 | 144.9431 | 0 | 47.0508 | 212776.2176 | 17561.3155 | 139976.9772 | 74716.6071 | 0 | 60730.8099 | 0 | 197247.1516 | 513196.6276 | 350267.2435 | 1566472.9501 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 23863776.2906 | 56094404.196 | 100 | 0.10542 | 226367.0905 | 532100.4906 | 4614.7993 | 10847.5882
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3445 | 0.5334 | 0.049903 | 4 | 122598.9146 | 284063.6842 | 2499.3447 | 5791.0224 | 159.4268 | 0 | 62.7229 | 308665.6088 | 27872.208 | 201406.5221 | 97791.6602 | 0 | 66549.386 | 0 | 273891.3002 | 712608.9802 | 486370.2716 | 2175155.937 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 24472459.2775 | 56703087.183 | 133.3521 | 0.19961 | 122598.9146 | 284063.6842 | 2499.3447 | 5791.0224
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7292 | 0.83245 | 0.081482 | 4 | 77380.0206 | 176269.3536 | 1577.4964 | 3593.4892 | 172.2455 | 0 | 267.8016 | 420877.0215 | 38061.7072 | 287555.318 | 123610.4135 | 0 | 73594.624 | 0 | 368042.6428 | 957571.4607 | 653562.198 | 2922875.3856 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 25220178.7261 | 57450806.6316 | 177.8279 | 0.32593 | 77380.0206 | 176269.3536 | 1577.4964 | 3593.4892
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2154 | 1.2181 | 0.12244 | 4 | 53276.7351 | 119088.2973 | 1086.1183 | 2427.776 | 183.113 | 0 | 338.6673 | 549006.6068 | 49682.7062 | 389914.4952 | 155175.2946 | 0 | 81339.9539 | 0 | 477796.4321 | 1243128.3068 | 848460.6132 | 3794504.4088 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 26091807.7493 | 58322435.6548 | 237.1374 | 0.48974 | 53276.7351 | 119088.2973 | 1086.1183 | 2427.776
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8377 | 1.7199 | 0.17595 | 4 | 38550.5597 | 84344.6281 | 785.9053 | 1719.4793 | 192.2639 | 0 | 443.7727 | 698872.7591 | 63253.9395 | 513848.2783 | 195035.4246 | 0 | 90121.8653 | 0 | 608841.584 | 1584080.9111 | 1081167.7714 | 4835222.5333 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 27132525.8738 | 59363153.7793 | 316.2278 | 0.70382 | 38550.5597 | 84344.6281 | 785.9053 | 1719.4793
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.6351 | 2.3714 | 0.24573 | 4 | 28876.5088 | 61667.7777 | 588.6867 | 1257.1811 | 199.843 | 0 | 568.7735 | 875311.1543 | 79202.0231 | 664405.8015 | 245900.6972 | 0 | 99984.3064 | 0 | 766273.5532 | 1993686.601 | 1360732.0713 | 6085496.2079 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 28382799.5484 | 60613427.4539 | 421.6965 | 0.9829 | 28876.5088 | 61667.7777 | 588.6867 | 1257.1811
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.6574 | 3.2152 | 0.33645 | 4 | 22210.1975 | 46158.9543 | 452.7849 | 941.0127 | 206.0353 | 0 | 84.1136 | 1083840.5208 | 98011.5885 | 847607.3876 | 311232.6144 | 0 | 111009.9807 | 0 | 956163.8159 | 2487742.1127 | 1697935.1099 | 7593543.1305 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 29890846.4709 | 62121474.3764 | 562.3413 | 1.3458 | 22210.1975 | 46158.9543 | 452.7849 | 941.0127
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 5.9996 | 4.3295 | 0.45638 | 4 | 17395.0905 | 35050.6355 | 354.6224 | 714.5546 | 211.1103 | 0 | 82.1445 | 1336077.164 | 120710.8678 | 1075444.0287 | 396966.4278 | 0 | 124428.9442 | 0 | 1190914.6987 | 3098515.7557 | 2114800.6714 | 9457858.5583 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 31755161.8988 | 63985789.8042 | 749.8942 | 1.8255 | 17395.0905 | 35050.6355 | 354.6224 | 714.5546
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.7636 | 5.7921 | 0.61376 | 4 | 13871.1259 | 26999.5508 | 282.7817 | 550.4224 | 215.0375 | 0 | 100.3798 | 1639943.3753 | 147986.4196 | 1357383.7924 | 509581.624 | 0 | 140943.4685 | 0 | 1480377.0852 | 3851637.5085 | 2628821.7428 | 11756675.0164 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 34053978.3568 | 66284606.2623 | 1000 | 2.455 | 13871.1259 | 26999.5508 | 282.7817 | 550.4224
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.0869 | 7.7499 | 0.82516 | 4 | 11191.0848 | 20955.9998 | 228.1454 | 427.2164 | 218.5866 | 0 | 109.0294 | 2013746.9019 | 181445.2427 | 1713454.7044 | 658391.8495 | 0 | 159929.9653 | 0 | 1843517.7789 | 4796455.1031 | 3273679.1652 | 14640620.711 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 36937924.0514 | 69168551.9569 | 1333.5214 | 3.3007 | 11191.0848 | 20955.9998 | 228.1454 | 427.2164
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.1615 | 10.3309 | 1.1036 | 4 | 9179.1481 | 16480.0947 | 187.1293 | 335.969 | 221.2129 | 0 | 112.424 | 2466960.6841 | 221887.5962 | 2156472.8147 | 855182.261 | 0 | 183677.1726 | 0 | 2294830.4062 | 5970677.9824 | 4075110.4082 | 18224799.3254 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 40522102.6659 | 72752730.5713 | 1778.2794 | 4.4146 | 9179.1481 | 16480.0947 | 187.1293 | 335.969
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.23 | 13.7507 | 1.4728 | 4 | 7638.6638 | 13109.7489 | 155.7245 | 267.26 | 223.2735 | 0 | 105.814 | 3019817.0376 | 271058.5863 | 2710770.3275 | 1115691.771 | 0 | 212612.7124 | 0 | 2858680.6696 | 7437700.7063 | 5076383.5615 | 22702715.3724 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 45000018.7128 | 77230646.6183 | 2371.3737 | 5.8911 | 7638.6638 | 13109.7489 | 155.7245 | 267.26
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 22.6279 | 18.2916 | 1.9629 | 4 | 6446.3382 | 10551.3089 | 131.4173 | 215.1027 | 224.8797 | 0 | 116.1382 | 3696041.8531 | 330988.667 | 3405928.5162 | 1461406.4503 | 0 | 248195.1317 | 0 | 3565598.6411 | 9276956.2593 | 6331713.2694 | 28316828.788 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 50614132.1285 | 82844760.034 | 3162.2777 | 7.8516 | 6446.3382 | 10551.3089 | 131.4173 | 215.1027
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 29.7199 | 24.2608 | 2.6076 | 4 | 5521.3667 | 8611.4725 | 112.5605 | 175.5565 | 226.1131 | 0 | 97.5892 | 4515499.369 | 403338.79 | 4269309.7258 | 1915681.6581 | 0 | 290789.8419 | 0 | 4443901.5601 | 11562120.2897 | 7891384.6755 | 35292025.9101 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 57589329.2505 | 89819957.156 | 4216.965 | 10.4303 | 5521.3667 | 8611.4725 | 112.5605 | 175.5565
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.0548 | 32.1196 | 3.4562 | 4 | 4794.5812 | 7125.9365 | 97.744 | 145.2719 | 227.0579 | 0 | 95.8319 | 5510975.2112 | 490879.8204 | 5343789.0552 | 2513606.2129 | 0 | 342701.3988 | 0 | 5538761.1624 | 14410720.3884 | 9835612.7758 | 43987046.0251 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 66284349.3656 | 98514977.2711 | 5623.4133 | 13.8248 | 4794.5812 | 7125.9365 | 97.744 | 145.2719
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 51.1541 | 42.2975 | 4.5555 | 4 | 4223.7442 | 5992.5137 | 86.1067 | 122.1655 | 227.7416 | 0 | 128.8804 | 6702111.6569 | 595191.5769 | 6660171.5774 | 3288578.6645 | 0 | 404430.8762 | 0 | 6883688.8972 | 17909946.4718 | 12223906.4796 | 54668026.2004 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 76965329.5409 | 109195957.4464 | 7498.9421 | 18.2221 | 4223.7442 | 5992.5137 | 86.1067 | 122.1655
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 66.5721 | 55.1961 | 5.9478 | 4 | 3776.6203 | 5131.3548 | 76.9915 | 104.6096 | 228.0878 | 0 | 118.0582 | 8100000.6223 | 717087.5497 | 8240625.2925 | 4274968.9877 | 0 | 477822.2696 | 0 | 8506096.8415 | 22131119.1412 | 15104943.5629 | 67552664.2673 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 89849967.6078 | 122080595.5132 | 10000 | 23.7911 | 3776.6203 | 5131.3548 | 76.9915 | 104.6096
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 85.6294 | 70.8762 | 7.6361 | 4 | 3432.7932 | 4487.9931 | 69.9821 | 91.4938 | 227.8716 | 0 | 156.0208 | 9679727.4829 | 854253.7878 | 10065472.0012 | 5489880.4571 | 0 | 565211.4576 | 0 | 10395272.6228 | 27046367.0008 | 18459701.2253 | 82555886.0355 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 104853189.376 | 137083817.2815 | 13335.2143 | 30.5446 | 3432.7932 | 4487.9931 | 69.9821 | 91.4938
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 108.0996 | 88.7523 | 9.5511 | 4 | 3177.4312 | 4021.0655 | 64.7762 | 81.9749 | 226.8419 | 0 | 118.2732 | 11364132.4354 | 999913.3102 | 12049735.1377 | 6912406.8979 | 0 | 668245.957 | 0 | 12477829.1579 | 32464751.914 | 22157860.2653 | 99094875.0753 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 121392178.4158 | 153622806.3212 | 17782.7941 | 38.2045 | 3177.4312 | 4021.0655 | 64.7762 | 81.9749
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 133.1032 | 107.6058 | 11.553 | 4 | 2996.3212 | 3693.7697 | 61.0841 | 75.3025 | 224.8912 | 0 | 147.1633 | 13039468.0673 | 1144251.6429 | 14057312.3682 | 8478971.9881 | 0 | 787180.9966 | 0 | 14627802.1746 | 38058540.6836 | 25975736.0414 | 116169263.9627 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 138466567.3032 | 170697195.2086 | 23713.7371 | 46.2122 | 2996.3212 | 3693.7697 | 61.0841 | 75.3025
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 159.1669 | 126.2143 | 13.5113 | 4 | 2869.4966 | 3465.8609 | 58.4986 | 70.6563 | 222.4758 | 0 | 134.1957 | 14613406.7327 | 1279417.8739 | 15970570.5432 | 10095151.4264 | 0 | 913378.382 | 0 | 16720050.7337 | 43502142.2552 | 29691105.9688 | 132785223.9161 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 155082527.2566 | 187313155.1621 | 31622.7766 | 54.0452 | 2869.4966 | 3465.8609 | 58.4986 | 70.6563
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 184.4916 | 143.1594 | 15.2746 | 4 | 2784.9686 | 3312.4884 | 56.7754 | 67.5296 | 219.7986 | 0 | 164.7152 | 15990530.3763 | 1397366.3946 | 17664015.5468 | 11647938.3913 | 0 | 1039179.651 | 0 | 18618221.8404 | 48440794.1063 | 33061837.3364 | 147859883.6432 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 170157186.9836 | 202387814.8891 | 42169.6503 | 61.0984 | 2784.9686 | 3312.4884 | 56.7754 | 67.5296
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 195.0781 | 149.8494 | 16.1068 | 4 | 2727.8392 | 3228.103 | 55.6107 | 65.8092 | 218.5603 | 0 | 173.9088 | 16521426.8754 | 1442763.1255 | 18321360.1455 | 12291030.0802 | 0 | 967277.9626 | 0 | 19322104.6938 | 50272152.9046 | 34311777.3468 | 153449893.1344 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 175747196.4748 | 207977824.3803 | 56234.1325 | 64.4273 | 2727.8392 | 3228.103 | 55.6107 | 65.8092
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.8519 | 153.9999 | 16.678 | 4 | 2684.1452 | 3167.2775 | 54.7199 | 64.5692 | 217.7318 | 0 | 207.1619 | 16847445.7032 | 1470621.3026 | 18726218.0464 | 12700436.1915 | 0 | 870086.4388 | 0 | 19739774.9962 | 51358845.3555 | 35053467.2739 | 156766895.3081 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 179064198.6485 | 211294826.554 | 74989.4209 | 66.7118 | 2684.1452 | 3167.2775 | 54.7199 | 64.5692
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 207.1083 | 157.1508 | 17.1223 | 4 | 2650.7272 | 3121.3223 | 54.0387 | 63.6324 | 217.0717 | 0 | 230.3482 | 17093297.0354 | 1491619.5417 | 19032107.8221 | 13016839.3452 | 0 | 782195.4923 | 0 | 20052263.1023 | 52171875.3075 | 35608376.9222 | 159248574.5688 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 181545877.9093 | 213776505.8148 | 100000 | 68.4891 | 2650.7272 | 3121.3223 | 54.0387 | 63.6324
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.1445 | 159.5286 | 17.4644 | 4 | 2625.2332 | 3086.6091 | 53.5189 | 62.9247 | 216.5547 | 0 | 241.7033 | 17277912.9672 | 1507382.2552 | 19262134.6343 | 13259237.882 | 0 | 705624.978 | 0 | 20284794.1595 | 52776873.4196 | 36021300.5652 | 161095260.8608 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 183392564.2013 | 215623192.1068 | 133352.1432 | 69.8576 | 2625.2332 | 3086.6091 | 53.5189 | 62.9247
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.1723 | 161.2883 | 17.7233 | 4 | 2605.8267 | 3060.4622 | 53.1233 | 62.3917 | 216.161 | 0 | 331.0929 | 17414042.7457 | 1519002.2325 | 19431926.4628 | 13440842.9069 | 0 | 640149.8696 | 0 | 20453926.0449 | 53216919.8917 | 36321641.3244 | 162438451.4787 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 184735754.8191 | 216966382.7246 | 177827.941 | 70.8933 | 2605.8267 | 3060.4622 | 53.1233 | 62.3917
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.4808 | 162.6157 | 17.9208 | 4 | 2591.0801 | 3040.706 | 52.8227 | 61.9889 | 215.8576 | 0 | 377.524 | 17516459.742 | 1527742.8711 | 19559767.6295 | 13579059.1361 | 0 | 586188.3586 | 0 | 20579994.9175 | 53544925.238 | 36545511.7131 | 163439649.606 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 185736952.9464 | 217967580.8519 | 237137.3706 | 71.6832 | 2591.0801 | 3040.706 | 52.8227 | 61.9889
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 218.1398 | 163.5615 | 18.0658 | 4 | 2579.8938 | 3025.9111 | 52.5946 | 61.6873 | 215.6375 | 0 | 381.0566 | 17589287.092 | 1533957.3741 | 19650724.9794 | 13678215.5104 | 0 | 541217.027 | 0 | 20667426.7733 | 53772404.992 | 36700771.3195 | 164134005.0677 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 186431308.4082 | 218661936.3137 | 316227.766 | 72.2632 | 2579.8938 | 3025.9111 | 52.5946 | 61.6873
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.3534 | 164.2492 | 18.1733 | 4 | 2571.4233 | 3014.8013 | 52.4219 | 61.4608 | 215.4754 | 0 | 365.062 | 17642163.5544 | 1538468.9883 | 19716791.3334 | 13750711.2176 | 0 | 504790.3742 | 0 | 20729640.9325 | 53934273.4723 | 36811249.8833 | 164628089.756 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 186925393.0965 | 219156021.0019 | 421696.5034 | 72.6934 | 2571.4233 | 3014.8013 | 52.4219 | 61.4608
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.2493 | 164.7546 | 18.2535 | 4 | 2565.0189 | 3006.4499 | 52.2914 | 61.2905 | 215.3551 | 0 | 439.3226 | 17680990.423 | 1541781.6045 | 19765317.6483 | 13804217.5774 | 0 | 475821.9046 | 0 | 20774570.3716 | 54051170.6565 | 36891034.6136 | 164984904.7995 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187282208.14 | 219512836.0455 | 562341.3252 | 73.014 | 2565.0189 | 3006.4499 | 52.2914 | 61.2905
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.469 | 164.8762 | 18.2907 | 4 | 2560.004 | 3000.5368 | 52.1891 | 61.17 | 215.3241 | 0 | 434.6488 | 17690324.7199 | 1542577.9549 | 19776985.5597 | 13817301.241 | 0 | 445763.0765 | 0 | 20776451.4953 | 54056064.9546 | 36894375.0726 | 164999844.0745 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187297147.4149 | 219527775.3204 | 749894.2093 | 73.1628 | 2560.004 | 3000.5368 | 52.1891 | 61.17
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.8157 | 165.6364 | 18.3803 | 4 | 2556.4204 | 2994.8057 | 52.1161 | 61.0532 | 215.1457 | 0 | 433.3802 | 17748644.2946 | 1547553.1979 | 19849900.944 | 13897763.1476 | 0 | 440267.4733 | 0 | 20858810.3324 | 54270345.7546 | 37040626.1216 | 165653911.2661 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187951214.6066 | 220181842.5121 | 1000000 | 73.5212 | 2556.4204 | 2994.8057 | 52.1161 | 61.0532
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.1519 | 165.824 | 18.4118 | 4 | 2553.733 | 2991.369 | 52.0613 | 60.9831 | 215.0999 | 0 | 407.8021 | 17763020.7625 | 1548779.5858 | 19867879.5958 | 13917819.2418 | 0 | 426606.3124 | 0 | 20874401.1443 | 54310909.8491 | 37068311.9496 | 165777728.4414 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188075031.7819 | 220305659.6874 | 1333521.4322 | 73.6471 | 2553.733 | 2991.369 | 52.0613 | 60.9831
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.2699 | 165.3239 | 18.376 | 4 | 2551.5493 | 2990.0367 | 52.0168 | 60.9559 | 215.2146 | 0 | 397.4144 | 17724680.3 | 1545508.8836 | 19819936.1447 | 13865081.1679 | 0 | 399170.1665 | 0 | 20808206.8984 | 54138685.9996 | 36950765.6335 | 165252035.1942 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 187549338.5347 | 219779966.4401 | 1778279.41 | 73.5041 | 2551.5493 | 2990.0367 | 52.0168 | 60.9559
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.5586 | 166.0503 | 18.4513 | 4 | 2550.1904 | 2986.8892 | 51.9891 | 60.8918 | 215.0442 | 0 | 427.609 | 17780363.0217 | 1550258.9351 | 19889569.3281 | 13942078.5945 | 0 | 407745.5978 | 0 | 20892306.0361 | 54357494.7047 | 37100107.0708 | 165919923.2887 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188217226.6291 | 220447854.5346 | 2371373.7057 | 73.8052 | 2550.1904 | 2986.8892 | 51.9891 | 60.8918
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.6977 | 166.1277 | 18.4644 | 4 | 2549.0479 | 2985.4356 | 51.9658 | 60.8621 | 215.0252 | 0 | 441.6686 | 17786290.0221 | 1550764.5178 | 19896982.694 | 13950374.8843 | 0 | 401683.8751 | 0 | 20898577.4374 | 54373811.6045 | 37111243.6902 | 165969728.7255 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188267032.066 | 220497659.9715 | 3162277.6602 | 73.8578 | 2549.0479 | 2985.4356 | 51.9658 | 60.8621
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.7903 | 166.1791 | 18.4737 | 4 | 2548.1897 | 2984.3589 | 51.9483 | 60.8402 | 215.0125 | 0 | 429.5494 | 17790227.4771 | 1551100.3865 | 19901907.7324 | 13955897.2509 | 0 | 396935.6978 | 0 | 20902466.7325 | 54383930.7524 | 37118150.2166 | 166000616.2463 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188297919.5868 | 220528547.4922 | 4216965.0343 | 73.8948 | 2548.1897 | 2984.3589 | 51.9483 | 60.8402
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.9756 | 166.2827 | 18.4868 | 4 | 2547.5453 | 2983.4061 | 51.9352 | 60.8208 | 214.9877 | 0 | 429.821 | 17798164.1647 | 1551777.3875 | 19911835.4543 | 13966934.7178 | 0 | 394974.547 | 0 | 20913237.6458 | 54411954.4594 | 37137276.9724 | 166086155.3489 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188383458.6894 | 220614086.5948 | 5623413.2519 | 73.9471 | 2547.5453 | 2983.4061 | 51.9352 | 60.8208
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.0339 | 166.315 | 18.4923 | 4 | 2547.0614 | 2982.7919 | 51.9253 | 60.8082 | 214.9797 | 0 | 419.5624 | 17800642.1665 | 1551988.7599 | 19914935.2012 | 13970400.575 | 0 | 392364.1887 | 0 | 20915829.0476 | 54418696.7555 | 37141878.728 | 166106735.4226 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188404038.763 | 220634666.6685 | 7498942.0933 | 73.9692 | 2547.0614 | 2982.7919 | 51.9253 | 60.8082
1 | 5600 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.0339 | 166.3147 | 18.4941 | 4 | 2546.6983 | 2982.3856 | 51.9179 | 60.8 | 214.9795 | 0 | 420.801 | 17800618.0397 | 1551986.7019 | 19914905.0206 | 13970395.4211 | 0 | 389785.1087 | 0 | 20914799.2139 | 54416017.3394 | 37140049.9715 | 166098556.8169 | 961560.8286 | 21335742.5118 | 21335742.5118 | 1478867.319 | 9416018.0746 | 0 | 188395860.1573 | 220626488.0628 | 10000000 | 73.9765 | 2546.6983 | 2982.3856 | 51.9179 | 60.8
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0692 | 0.35514 | 0.029185 | 4 | 209570.3982 | 492066.5046 | 4272.376 | 10031.4413 | 147.6069 | 0 | 52.6947 | 224326.5039 | 18918.961 | 146270.2946 | 77142.3107 | 0 | 60803.8844 | 0 | 205710.1623 | 535215.6453 | 365295.6755 | 1633683.4375 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 24465276.3766 | 57443909.7201 | 100 | 0.11674 | 209570.3982 | 492066.5046 | 4272.376 | 10031.4413
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.3834 | 0.57873 | 0.054845 | 4 | 114511.5117 | 264838.8608 | 2334.4721 | 5399.0984 | 162.6221 | 0 | 71.7615 | 326695.1977 | 29510.0417 | 214988.1955 | 101015.8232 | 0 | 67092.4887 | 0 | 288327.6813 | 750169.4825 | 512006.0862 | 2289804.9968 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25121397.9359 | 58100031.2794 | 133.3521 | 0.21938 | 114511.5117 | 264838.8608 | 2334.4721 | 5399.0984
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.7681 | 0.88534 | 0.087482 | 4 | 73932.0535 | 168176.0318 | 1507.2049 | 3428.4959 | 175.2745 | 0 | 276.1207 | 439354.355 | 39738.5387 | 302078.5137 | 126739.5245 | 0 | 73385.3534 | 0 | 382705.5513 | 995721.3407 | 679600.275 | 3039323.4522 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 25870916.3913 | 58849549.7348 | 177.8279 | 0.34993 | 73932.0535 | 168176.0318 | 1507.2049 | 3428.4959
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.2738 | 1.2968 | 0.13126 | 4 | 51015.8106 | 113828.6389 | 1040.0263 | 2320.5508 | 186.4344 | 0 | 350.9705 | 573570.9359 | 51908.7348 | 409943.3959 | 159555.3177 | 0 | 81394.2094 | 0 | 497785.3116 | 1295135.2709 | 883956.4347 | 3953249.6109 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 26784842.5499 | 59763475.8935 | 237.1374 | 0.52503 | 51015.8106 | 113828.6389 | 1040.0263 | 2320.5508
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.8961 | 1.8121 | 0.18664 | 4 | 37282.6991 | 81457.1701 | 760.0583 | 1660.6146 | 195.4776 | 0 | 450.8496 | 724910.9178 | 65609.4825 | 535774.9104 | 199533.8695 | 0 | 89136.9808 | 0 | 629836.8027 | 1638706.1634 | 1118450.6286 | 5001959.7557 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 27833552.6947 | 60812186.0382 | 316.2278 | 0.74655 | 37282.6991 | 81457.1701 | 760.0583 | 1660.6146
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.717 | 2.5012 | 0.26069 | 4 | 27940.621 | 59566.9912 | 569.6074 | 1214.3537 | 203.2062 | 0 | 66.0113 | 908663.2847 | 82213.2077 | 693352.0115 | 252122.1862 | 0 | 98903.4003 | 0 | 793749.0953 | 2065172.3255 | 1409522.5472 | 6303698.0584 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 29135290.9975 | 62113924.341 | 421.6965 | 1.0428 | 27940.621 | 59566.9912 | 569.6074 | 1214.3537
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.7622 | 3.388 | 0.35645 | 4 | 21527.9375 | 44657.7169 | 438.8761 | 910.408 | 209.4617 | 0 | 85.1862 | 1124462.0185 | 101670.9813 | 883870.3134 | 319287.4231 | 0 | 109448.9994 | 0 | 990108.4969 | 2576059.2099 | 1758213.3435 | 7863120.7861 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 30694713.7251 | 63673347.0686 | 562.3413 | 1.4258 | 21527.9375 | 44657.7169 | 438.8761 | 910.408
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.1311 | 4.5563 | 0.48275 | 4 | 16891.6335 | 33970.1043 | 344.3588 | 692.5265 | 214.57 | 0 | 89.0676 | 1384934.7637 | 125101.3863 | 1120263.2741 | 407203.2676 | 0 | 122153.4768 | 0 | 1232265.9057 | 3206103.1141 | 2188231.2542 | 9786256.4425 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 32617849.3816 | 65596482.7251 | 749.8942 | 1.931 | 16891.6335 | 33970.1043 | 344.3588 | 692.5265
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 7.917 | 6.0773 | 0.64727 | 4 | 13507.0742 | 26244.6307 | 275.36 | 535.0323 | 218.4765 | 0 | 63.9615 | 1696442.2556 | 153050.0055 | 1410592.275 | 521852.0167 | 0 | 137467.4443 | 0 | 1528567.5589 | 3977019.236 | 2714397.3481 | 12139388.1402 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 34970981.0793 | 67949614.4228 | 1000 | 2.5891 | 13507.0742 | 26244.6307 | 275.36 | 535.0323
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.3064 | 8.1495 | 0.8719 | 4 | 10889.1097 | 20345.0821 | 221.9892 | 414.762 | 222.1236 | 0 | 87.1288 | 2086478.2375 | 187944.1835 | 1783771.6663 | 675834.579 | 0 | 155867.166 | 0 | 1907059.3746 | 4961777.3009 | 3386514.9622 | 15145247.4699 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 37976840.4089 | 70955473.7524 | 1333.5214 | 3.4876 | 10889.1097 | 20345.0821 | 221.9892 | 414.762
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.4394 | 10.8543 | 1.1651 | 4 | 8942.0915 | 16018.3787 | 182.2966 | 326.5563 | 224.7686 | 0 | 104.5035 | 2554653.9841 | 229698.4322 | 2243444.9774 | 877592.8169 | 0 | 178230.0775 | 0 | 2372611.9123 | 6173049.5063 | 4213233.1315 | 18842514.8382 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 41674107.7772 | 74652741.1207 | 1778.2794 | 4.6604 | 8942.0915 | 16018.3787 | 182.2966 | 326.5563
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.581 | 14.4347 | 1.5534 | 4 | 7449.6305 | 12757.0904 | 151.8708 | 260.0705 | 226.844 | 0 | 87.8833 | 3125371.6543 | 280428.0262 | 2818118.7553 | 1144379.5289 | 0 | 205416.2263 | 0 | 2953748.5345 | 7685047.7897 | 5245203.0284 | 23457713.5436 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 46289306.4827 | 79267939.8262 | 2371.3737 | 6.2136 | 7449.6305 | 12757.0904 | 151.8708 | 260.0705
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.0689 | 19.183 | 2.0684 | 4 | 6293.3707 | 10279.3473 | 128.2989 | 209.5584 | 228.4619 | 0 | 122.4525 | 3822796.6149 | 342198.517 | 3538074.3616 | 1498018.825 | 0 | 238772.846 | 0 | 3681545.8541 | 9578627.1236 | 6537609.833 | 29237643.9752 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 52069236.9142 | 85047870.2577 | 3162.2777 | 8.2737 | 6293.3707 | 10279.3473 | 128.2989 | 209.5584
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.3018 | 25.4443 | 2.7477 | 4 | 5393.0792 | 8393.6373 | 109.9452 | 171.1157 | 229.7088 | 0 | 94.7473 | 4670731.7055 | 417013.6977 | 4435132.6205 | 1964144.0577 | 0 | 279157.2632 | 0 | 4588809.9444 | 11939142.1809 | 8148709.8633 | 36442841.3332 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 59274434.2723 | 92253067.6158 | 4216.965 | 10.9908 | 5393.0792 | 8393.6373 | 109.9452 | 171.1157
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 39.771 | 33.6438 | 3.6375 | 4 | 4687.7536 | 6954.2976 | 95.5662 | 141.7728 | 230.659 | 0 | 117.4301 | 5695541.9606 | 507072.3596 | 5545715.7018 | 2574494.0746 | 0 | 327601.9139 | 0 | 5713666.1441 | 14865787.2729 | 10146205.2751 | 45376084.7026 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 68207677.6416 | 101186310.9851 | 5623.4133 | 14.5502 | 4687.7536 | 6954.2976 | 95.5662 | 141.7728
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 52.0775 | 44.2894 | 4.7927 | 4 | 4131.868 | 5852.1133 | 84.2337 | 119.3032 | 231.3442 | 0 | 102.5913 | 6925151.2543 | 614676.3964 | 6909931.0639 | 3367567.6044 | 0 | 385894.4065 | 0 | 7099256.083 | 18470808.0702 | 12606706.045 | 56379990.9237 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 79211583.8628 | 112190217.2063 | 7498.9421 | 19.1709 | 4131.868 | 5852.1133 | 84.2337 | 119.3032
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 67.7294 | 57.7471 | 6.252 | 4 | 3696.9918 | 5015.7048 | 75.3682 | 102.2519 | 231.6716 | 0 | 145.3863 | 8364895.6865 | 740129.2247 | 8543931.0237 | 4374876.6794 | 0 | 455277.2186 | 0 | 8766852.8348 | 22809552.7474 | 15567988.4395 | 69623503.8545 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 92455096.7936 | 125433730.1371 | 10000 | 25.0082 | 3696.9918 | 5015.7048 | 75.3682 | 102.2519
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 87.0131 | 74.0356 | 8.0139 | 4 | 3363.3863 | 4392.1803 | 68.5672 | 89.5405 | 231.4052 | 0 | 133.1498 | 9985449.9937 | 880734.5714 | 10422845.3677 | 5611093.8497 | 0 | 538331.8388 | 0 | 10700997.6923 | 27841800.9189 | 19002601.219 | 84983855.4515 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 107815448.3906 | 140794081.7341 | 13335.2143 | 32.0556 | 3363.3863 | 4392.1803 | 68.5672 | 89.5405
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 109.681 | 92.5192 | 10.0025 | 4 | 3116.2453 | 3940.5055 | 63.5289 | 80.3325 | 230.2929 | 0 | 119.4396 | 11706307.1078 | 1029434.7502 | 12457164.1317 | 7053275.6228 | 0 | 637568.4849 | 0 | 12824662.538 | 33367141.2239 | 22773759.5115 | 101849313.3709 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 124680906.31 | 157659539.6535 | 17782.7941 | 40.01 | 3116.2453 | 3940.5055 | 63.5289 | 80.3325
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 134.7816 | 111.8826 | 12.0671 | 4 | 2941.6549 | 3624.8905 | 59.9696 | 73.8983 | 228.2393 | 0 | 141.167 | 13407568.0259 | 1175899.4647 | 14502524.487 | 8632534.2973 | 0 | 753343.2902 | 0 | 15004029.1304 | 39037406.0478 | 26643831.7661 | 119157136.5094 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 141988729.4484 | 174967362.7919 | 23713.7371 | 48.2683 | 2941.6549 | 3624.8905 | 59.9696 | 73.8983
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 160.8252 | 130.9136 | 14.0787 | 4 | 2819.2177 | 3404.8301 | 57.4736 | 69.4121 | 225.7564 | 0 | 161.5913 | 15000265.1189 | 1312580.3568 | 16444533.5562 | 10254284.8755 | 0 | 876262.6776 | 0 | 17116291.3681 | 44533079.1057 | 30394741.5529 | 135932038.6116 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 158763631.5506 | 191742264.8941 | 31622.7766 | 56.3148 | 2819.2177 | 3404.8301 | 57.4736 | 69.4121
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 186.0191 | 148.1341 | 15.8783 | 4 | 2737.9829 | 3257.2238 | 55.8175 | 66.4029 | 223.0034 | 0 | 149.1268 | 16385953.631 | 1431182.6455 | 18153390.2127 | 11804302.8134 | 0 | 999471.2545 | 0 | 19021977.2172 | 49491282.7752 | 33778817.4383 | 151066377.9878 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 173897970.9268 | 206876604.2703 | 42169.6503 | 63.5132 | 2737.9829 | 3257.2238 | 55.8175 | 66.4029
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 198.4085 | 156.1059 | 16.8212 | 4 | 2684.3205 | 3174.4553 | 54.7235 | 64.7156 | 221.5057 | 0 | 180.4548 | 17011923.587 | 1484670.322 | 18930807.208 | 12558662.8567 | 0 | 956631.0707 | 0 | 19867651.0673 | 51691552.6615 | 35280546.8467 | 157782445.6198 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 180614038.5589 | 213592671.9024 | 56234.1325 | 67.2848 | 2684.3205 | 3174.4553 | 54.7235 | 64.7156
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.0922 | 160.257 | 17.3909 | 4 | 2643.5828 | 3117.6612 | 53.893 | 63.5577 | 220.655 | 0 | 191.7067 | 17334316.5055 | 1512197.1372 | 19332467.3835 | 12963435.0829 | 0 | 860334.9216 | 0 | 20281072.902 | 52767191.4708 | 36014692.4362 | 161065707.8396 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 183897300.7786 | 216875934.1221 | 74989.4209 | 69.5637 | 2643.5828 | 3117.6612 | 53.893 | 63.5577
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 210.3339 | 163.4412 | 17.8364 | 4 | 2612.4466 | 3074.6831 | 53.2583 | 62.6816 | 219.9707 | 0 | 211.5996 | 17580029.2217 | 1533167.4205 | 19639160.0547 | 13279779.3138 | 0 | 774483.8896 | 0 | 20594581.7611 | 53582877.2129 | 36571414.7158 | 163555493.5903 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 186387086.5293 | 219365719.8728 | 100000 | 71.3458 | 2612.4466 | 3074.6831 | 53.2583 | 62.6816
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 214.3091 | 165.8129 | 18.1763 | 4 | 2588.7 | 3042.2936 | 52.7742 | 62.0213 | 219.4415 | 0 | 258.2653 | 17762172.2134 | 1548707.2009 | 19866818.3878 | 13518958.8444 | 0 | 699201.163 | 0 | 20824384.5457 | 54180776.9193 | 36979493.5511 | 165380512.8256 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 188212105.7647 | 221190739.1082 | 133352.1432 | 72.7053 | 2588.7 | 3042.2936 | 52.7742 | 62.0213
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.3318 | 167.5918 | 18.4354 | 4 | 2570.6288 | 3017.8465 | 52.4057 | 61.5229 | 219.0332 | 0 | 291.9169 | 17898308.2333 | 1560318.9884 | 20037144.8245 | 13700607.0904 | 0 | 635565.3478 | 0 | 20994458.349 | 54623274.0685 | 37281506.9478 | 166731183.8497 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 189562776.7888 | 222541410.1323 | 177827.941 | 73.7418 | 2570.6288 | 3017.8465 | 52.4057 | 61.5229
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 219.6239 | 168.9258 | 18.6322 | 4 | 2556.8986 | 2999.3932 | 52.1258 | 61.1467 | 218.7203 | 0 | 381.5149 | 18000132.5069 | 1569002.5588 | 20164637.4462 | 13838005.0634 | 0 | 583043.2337 | 0 | 21120380.1155 | 54950896.6749 | 37505116.1086 | 167731213.708 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 190562806.6471 | 223541439.9906 | 237137.3706 | 74.5289 | 2556.8986 | 2999.3932 | 52.1258 | 61.1467
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 221.2823 | 169.8827 | 18.7772 | 4 | 2546.4871 | 2985.5657 | 51.9136 | 60.8648 | 218.4918 | 0 | 437.2567 | 18073036.5437 | 1575218.9858 | 20255969.3053 | 13937318.7368 | 0 | 539470.4597 | 0 | 21208595.4722 | 55180414.9374 | 37661767.0389 | 168431791.4797 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 191263384.4187 | 224242017.7622 | 316227.766 | 75.1087 | 2546.4871 | 2985.5657 | 51.9136 | 60.8648
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.5197 | 170.5925 | 18.8859 | 4 | 2538.605 | 2975.1552 | 51.7529 | 60.6526 | 218.3203 | 0 | 445.1395 | 18127033.0542 | 1579822.7509 | 20323641.1124 | 14011389.8805 | 0 | 504539.2402 | 0 | 21273106.1549 | 55348258.5008 | 37776323.7198 | 168944114.4136 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 191775707.3527 | 224754340.6962 | 421696.5034 | 75.5437 | 2538.605 | 2975.1552 | 51.7529 | 60.6526
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.4017 | 171.0958 | 18.9652 | 4 | 2532.6467 | 2967.3715 | 51.6314 | 60.4939 | 218.1974 | 0 | 464.2088 | 18165291.0619 | 1583084.417 | 20371602.1539 | 14064162.5872 | 0 | 476338.2319 | 0 | 21317586.5962 | 55463987.4851 | 37855311.1296 | 169297363.6629 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 192128956.6019 | 225107589.9454 | 562341.3252 | 75.8609 | 2532.6467 | 2967.3715 | 51.6314 | 60.4939
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 224.5077 | 171.7276 | 19.0496 | 4 | 2527.9945 | 2960.7942 | 51.5366 | 60.3598 | 218.0449 | 0 | 445.2982 | 18213267.2821 | 1587174.3379 | 20431762.184 | 14130364.0475 | 0 | 459369.5604 | 0 | 21380555.5906 | 55627819.8918 | 37967130.1136 | 169797443.0079 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 192629035.9469 | 225607669.2904 | 749894.2093 | 76.1984 | 2527.9945 | 2960.7942 | 51.5366 | 60.3598
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.0607 | 172.0408 | 19.097 | 4 | 2524.6761 | 2956.4019 | 51.4689 | 60.2703 | 217.9673 | 0 | 437.8219 | 18237029.213 | 1589199.9073 | 20461565.1741 | 14163385.9906 | 0 | 443631.8989 | 0 | 21408976.7517 | 55701765.9229 | 38017599.7992 | 170023154.6576 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 192854747.5967 | 225833380.9402 | 1000000 | 76.3879 | 2524.6761 | 2956.4019 | 51.4689 | 60.2703
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.3894 | 171.0797 | 19.0206 | 4 | 2522.0783 | 2955.5372 | 51.416 | 60.2526 | 218.1926 | 0 | 418.1466 | 18164065.535 | 1582979.9383 | 20370065.6316 | 14063281.6257 | 0 | 401641.0657 | 0 | 21286993.1805 | 55384389.6931 | 37800984.0009 | 169054400.6708 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 191885993.6099 | 224864626.9534 | 1333521.4322 | 76.0825 | 2522.0783 | 2955.5372 | 51.416 | 60.2526
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.6675 | 172.3826 | 19.1528 | 4 | 2520.2964 | 2950.7632 | 51.3797 | 60.1553 | 217.8815 | 0 | 421.735 | 18262946.2116 | 1591409.1014 | 20494076.0926 | 14199517.2923 | 0 | 420648.0889 | 0 | 21437752.7468 | 55776635.1595 | 38068699.5916 | 170251684.2847 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193083277.2238 | 226061910.5673 | 1778279.41 | 76.6113 | 2520.2964 | 2950.7632 | 51.3797 | 60.1553
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.8501 | 172.4852 | 19.1701 | 4 | 2518.8828 | 2948.961 | 51.3508 | 60.1186 | 217.8556 | 0 | 427.626 | 18270722.9757 | 1592071.9847 | 20503832.467 | 14210388.547 | 0 | 412907.9515 | 0 | 21446070.3311 | 55798275.8077 | 38083469.7786 | 170317739.8433 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193149332.7824 | 226127966.1259 | 2371373.7057 | 76.6806 | 2518.8828 | 2948.961 | 51.3508 | 60.1186
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.9887 | 172.563 | 19.1832 | 4 | 2517.8207 | 2947.6058 | 51.3292 | 60.0909 | 217.8359 | 0 | 408.1185 | 18276619.6251 | 1592574.6038 | 20511230.4459 | 14218637.0091 | 0 | 407063.9828 | 0 | 21452389.01 | 55814715.7139 | 38094690.3525 | 170367920.743 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193199513.682 | 226178147.0255 | 3162277.6602 | 76.7328 | 2517.8207 | 2947.6058 | 51.3292 | 60.0909
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.0741 | 172.6107 | 19.192 | 4 | 2517.023 | 2946.6109 | 51.3129 | 60.0706 | 217.8236 | 0 | 409.4063 | 18280239.5757 | 1592883.1592 | 20515772.1948 | 14223716.7792 | 0 | 402387.8219 | 0 | 21455849.817 | 55823720.0239 | 38100835.9791 | 170395405.3508 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193226998.2899 | 226205631.6334 | 4216965.0343 | 76.7681 | 2517.023 | 2946.6109 | 51.3129 | 60.0706
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.1667 | 172.6628 | 19.2002 | 4 | 2516.4241 | 2945.8298 | 51.3007 | 60.0547 | 217.8105 | 0 | 405.5129 | 18284184.9213 | 1593219.4486 | 20520722.3136 | 14229231.0993 | 0 | 399258.3047 | 0 | 21460380.2741 | 55835507.3439 | 38108881.0672 | 170431384.7727 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193262977.7118 | 226241611.0553 | 5623413.2519 | 76.8006 | 2516.4241 | 2945.8298 | 51.3007 | 60.0547
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.2056 | 172.6844 | 19.2046 | 4 | 2515.9746 | 2945.2804 | 51.2915 | 60.0435 | 217.8049 | 0 | 413.7133 | 18285826.3204 | 1593359.356 | 20522781.768 | 14231543.8353 | 0 | 396473.9356 | 0 | 21461694.2339 | 55838925.9979 | 38111214.3687 | 170441819.8158 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193273412.7548 | 226252046.0983 | 7498942.0933 | 76.8185 | 2515.9746 | 2945.2804 | 51.2915 | 60.0435
1 | 5700 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.2593 | 172.7146 | 19.2093 | 4 | 2515.6373 | 2944.8388 | 51.2847 | 60.0345 | 217.7973 | 0 | 407.9143 | 18288114.2538 | 1593554.3712 | 20525652.4603 | 14234742.2263 | 0 | 394721.5811 | 0 | 21464346.1082 | 55845825.6307 | 38115923.5099 | 170462880.1415 | 961560.8286 | 21870032.1104 | 21870032.1104 | 1478867.319 | 9629733.914 | 0 | 193294473.0806 | 226273106.4241 | 10000000 | 76.8372 | 2515.6373 | 2944.8388 | 51.2847 | 60.0345
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.0887 | 0.37306 | 0.031946 | 4 | 196157.5211 | 460156.9933 | 3998.9364 | 9380.9227 | 150.0075 | 0 | 55.8016 | 234936.4209 | 20233.0966 | 151871.702 | 79429.0255 | 0 | 60466.3272 | 0 | 213305.2631 | 554976.5398 | 378782.892 | 1694001.2671 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25065743.8956 | 58800586.8044 | 100 | 0.12778 | 196157.5211 | 460156.9933 | 3998.9364 | 9380.9227
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4176 | 0.62142 | 0.059604 | 4 | 108070.3289 | 249565.167 | 2203.1598 | 5087.7235 | 165.6281 | 0 | 57.5026 | 343290.9112 | 31017.4315 | 227583.8717 | 103869.9013 | 0 | 67217.2091 | 0 | 301461.9367 | 784342.1208 | 535329.6141 | 2394112.9964 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 25765855.6249 | 59500698.5336 | 133.3521 | 0.23842 | 108070.3289 | 249565.167 | 2203.1598 | 5087.7235
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8264 | 0.95536 | 0.095091 | 4 | 69846.5207 | 158537.8814 | 1423.9158 | 3232.0092 | 178.8206 | 0 | 275.272 | 463325.3387 | 41913.4403 | 321045.9312 | 131097.2525 | 0 | 74253.0049 | 0 | 402337.6374 | 1046800.0017 | 714462.5108 | 3195235.1176 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 26566977.7461 | 60301820.6549 | 177.8279 | 0.38036 | 69846.5207 | 158537.8814 | 1423.9158 | 3232.0092
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3321 | 1.3776 | 0.14037 | 4 | 48951.2654 | 109034.17 | 997.9378 | 2222.809 | 189.7499 | 0 | 358.3024 | 598332.9569 | 54152.0491 | 430252.3655 | 163936.1343 | 0 | 81277.5748 | 0 | 517900.9214 | 1347471.9615 | 919677.3015 | 4113001.265 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 27484743.8935 | 61219586.8022 | 237.1374 | 0.56147 | 48951.2654 | 109034.17 | 997.9378 | 2222.809
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.9739 | 1.9232 | 0.19918 | 4 | 35865.928 | 78207.0229 | 731.1755 | 1594.3559 | 198.9146 | 0 | 457.8122 | 755752.654 | 68398.6852 | 561883.8305 | 205277.6477 | 0 | 88909.9292 | 0 | 655286.8712 | 1704922.021 | 1163644.312 | 5204075.9508 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 28575818.5793 | 62310661.488 | 316.2278 | 0.79674 | 35865.928 | 78207.0229 | 731.1755 | 1594.3559
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.807 | 2.6442 | 0.27707 | 4 | 26992.9952 | 57431.5047 | 550.2887 | 1170.8189 | 206.6249 | 0 | 79.24 | 944819.9845 | 85476.3834 | 724891.9217 | 259811.3937 | 0 | 97986.6919 | 0 | 824064.6864 | 2144047.275 | 1463356.321 | 6544454.6577 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 29916197.2862 | 63651040.195 | 421.6965 | 1.1083 | 26992.9952 | 57431.5047 | 550.2887 | 1170.8189
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.8742 | 3.572 | 0.37773 | 4 | 20860.6303 | 43188.1702 | 425.2722 | 880.4493 | 212.9162 | 0 | 84.6636 | 1167047.3057 | 105505.6909 | 922071.0773 | 327872.3545 | 0 | 107813.1561 | 0 | 1025820.738 | 2668975.1355 | 1821630.3719 | 8146735.8299 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 31518478.4584 | 65253321.3672 | 562.3413 | 1.5109 | 20860.6303 | 43188.1702 | 425.2722 | 880.4493
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.2775 | 4.8025 | 0.51128 | 4 | 16386.2098 | 32881.4935 | 334.055 | 670.3337 | 218.0645 | 0 | 73.0471 | 1437198.933 | 129795.8708 | 1168434.5457 | 418515.3431 | 0 | 119933.4167 | 0 | 1276812.4626 | 3322004.1175 | 2267336.0705 | 10140030.7599 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 33511773.3884 | 67246616.2972 | 749.8942 | 2.0451 | 16386.2098 | 32881.4935 | 334.055 | 670.3337
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.0996 | 6.3956 | 0.68433 | 4 | 13128.7062 | 25452.6888 | 267.6464 | 518.8875 | 221.9495 | 0 | 83.3283 | 1758601.7735 | 158618.2005 | 1469394.0114 | 536140.5497 | 0 | 134354.8274 | 0 | 1582272.6514 | 4116748.8702 | 2809765.6946 | 12565896.5787 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 35937639.2072 | 69672482.116 | 1000 | 2.7373 | 13128.7062 | 25452.6888 | 267.6464 | 518.8875
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.5279 | 8.563 | 0.92048 | 4 | 10600.696 | 19763.0148 | 216.1095 | 402.8958 | 225.6549 | 0 | 111.9999 | 2160655.6575 | 194568.78 | 1855806.5705 | 693654.1923 | 0 | 151109.0676 | 0 | 1971759.7644 | 5130114.4435 | 3501408.521 | 15659076.9967 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 39030819.6253 | 72765662.534 | 1333.5214 | 3.6819 | 10600.696 | 19763.0148 | 216.1095 | 402.8958
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.717 | 11.3933 | 1.2287 | 4 | 8716.1788 | 15579.8653 | 177.6911 | 317.6166 | 228.3157 | 0 | 71.1247 | 2643699.3555 | 237625.1633 | 2332140.6234 | 900287.7358 | 0 | 171832.8359 | 0 | 2451378.4285 | 6377983.824 | 4353105.0143 | 19468052.9807 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 42839795.6093 | 76574638.518 | 1778.2794 | 4.915 | 8716.1788 | 15579.8653 | 177.6911 | 317.6166
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 17.9365 | 15.1434 | 1.6373 | 4 | 7267.9813 | 12418.9202 | 148.1676 | 253.1765 | 230.4073 | 0 | 71.2214 | 3233239.8086 | 289997.0186 | 2928283.6279 | 1173805.5515 | 0 | 197140.7902 | 0 | 3050762.0508 | 7937457.0588 | 5417477.541 | 24228163.4474 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 47599906.0759 | 81334748.9847 | 2371.3737 | 6.5493 | 7267.9813 | 12418.9202 | 148.1676 | 253.1765
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.5099 | 20.1014 | 2.1777 | 4 | 6146.8628 | 10019.6951 | 125.3121 | 204.265 | 232.0348 | 0 | 125.1652 | 3951639.9761 | 353585.8515 | 3672947.1312 | 1535247.7975 | 0 | 227906.0985 | 0 | 3799117.4733 | 9884524.3595 | 6746390.982 | 30171359.6695 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 53543102.298 | 87277945.2068 | 3162.2777 | 8.7106 | 6146.8628 | 10019.6951 | 125.3121 | 204.265
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 30.8789 | 26.6599 | 2.8924 | 4 | 5270.3845 | 8186.1622 | 107.4439 | 166.886 | 233.2942 | 0 | 106.242 | 4828034.5632 | 430861.6654 | 4603847.5767 | 2013136.3802 | 0 | 265628.7381 | 0 | 4735188.4802 | 12319989.1047 | 8408645.7144 | 37605332.2228 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 60977074.8514 | 94711917.7601 | 4216.965 | 11.5698 | 5270.3845 | 8186.1622 | 107.4439 | 166.886
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 40.5279 | 35.2498 | 3.8289 | 4 | 4583.3232 | 6785.9961 | 93.4372 | 138.3417 | 234.2531 | 0 | 130.6614 | 5887457.5529 | 523897.7929 | 5756512.6834 | 2639011.007 | 0 | 310946.6618 | 0 | 5895952.0222 | 15340057.7357 | 10469904.6113 | 46823740.0671 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 70195482.6956 | 103930325.6044 | 5623.4133 | 15.3154 | 4583.3232 | 6785.9961 | 93.4372 | 138.3417
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 53.03 | 46.3665 | 5.0408 | 4 | 4042.7422 | 5715.8429 | 82.4168 | 116.5252 | 234.9366 | 0 | 129.4296 | 7154706.7151 | 634715.783 | 7167981.4104 | 3449726.0271 | 0 | 365095.527 | 0 | 7321167.9304 | 19048177.1769 | 13000772.3241 | 58142342.8941 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 81514085.5226 | 115248928.4313 | 7498.9421 | 20.1631 | 4042.7422 | 5715.8429 | 82.4168 | 116.5252
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 68.9085 | 60.3911 | 6.5685 | 4 | 3620.0173 | 4903.9731 | 73.7989 | 99.9741 | 235.2423 | 0 | 123.557 | 8635969.0939 | 763690.6351 | 8855476.1702 | 4477828.4949 | 0 | 429853.0103 | 0 | 9033498.7878 | 23503310.8203 | 16041492.5796 | 71741119.5922 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 95112862.2208 | 128847705.1295 | 10000 | 26.2741 | 3620.0173 | 4903.9731 | 73.7989 | 99.9741
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 88.4358 | 77.3144 | 8.4071 | 4 | 3296.2031 | 4299.3738 | 67.1976 | 87.6486 | 234.9216 | 0 | 114.571 | 10298847.6608 | 907859.657 | 10790508.7586 | 5736728.7433 | 0 | 508396.4635 | 0 | 11014513.1004 | 28657503.7 | 19559335.128 | 87473693.2115 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 110845435.84 | 144580278.7488 | 13335.2143 | 33.6282 | 3296.2031 | 4299.3738 | 67.1976 | 87.6486
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 111.281 | 96.3953 | 10.4686 | 4 | 3057.2401 | 3862.8563 | 62.326 | 78.7496 | 233.7239 | 0 | 133.1566 | 12054328.1298 | 1059438.2891 | 12872960.3801 | 7197556.1326 | 0 | 603366.6361 | 0 | 13177183.3314 | 34284328.0163 | 23399758.3436 | 104648919.2589 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 128020661.8874 | 161755504.7962 | 17782.7941 | 41.8746 | 3057.2401 | 3862.8563 | 62.326 | 78.7496
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 136.4795 | 116.2678 | 12.596 | 4 | 2888.9973 | 3558.5545 | 58.8961 | 72.5459 | 231.5644 | 0 | 145.4251 | 13780918.3175 | 1207975.7068 | 14955513.5479 | 8789645.5397 | 0 | 716038.714 | 0 | 15385535.8121 | 40030008.1758 | 27321303.1144 | 122186938.9283 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 145558681.5568 | 179293524.4656 | 23713.7371 | 50.3838 | 2888.9973 | 3558.5545 | 58.8961 | 72.5459
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 162.5185 | 135.7272 | 14.6615 | 4 | 2770.7853 | 3346.0131 | 56.4862 | 68.213 | 229.0132 | 0 | 142.7838 | 15392501.3516 | 1346180.7331 | 16926502.8726 | 10417379.3595 | 0 | 835906.9116 | 0 | 17518203.7791 | 45578772.7555 | 31108448.9558 | 139123896.7188 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 162495639.3473 | 196230482.2561 | 31622.7766 | 58.6461 | 2770.7853 | 3346.0131 | 56.4862 | 68.213
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 187.6005 | 153.224 | 16.4972 | 4 | 2692.7981 | 3204.0203 | 54.8963 | 65.3183 | 226.1817 | 0 | 149.1453 | 16786683.0402 | 1465430.2705 | 18650693.9972 | 11965711.5809 | 0 | 956989.5977 | 0 | 19431948.3097 | 50557943.4611 | 34506835.2741 | 154322235.5312 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 177693978.1597 | 211428821.0685 | 42169.6503 | 65.9886 | 2692.7981 | 3204.0203 | 54.8963 | 65.3183
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 201.7749 | 162.4996 | 17.5541 | 4 | 2642.3304 | 3122.7701 | 53.8675 | 63.6619 | 224.4106 | 0 | 167.3663 | 17507511.6471 | 1526979.2637 | 19548594.8831 | 12831111.591 | 0 | 943061.1967 | 0 | 20419330.8468 | 53126910.2827 | 36260207.9168 | 162163707.6277 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 185535450.2562 | 219270293.165 | 56234.1325 | 70.2166 | 2642.3304 | 3122.7701 | 53.8675 | 63.6619
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 208.3908 | 166.6581 | 18.1223 | 4 | 2604.4609 | 3069.8391 | 53.0955 | 62.5828 | 223.5351 | 0 | 173.7188 | 17826907.4784 | 1554229.1288 | 19947793.6132 | 13232329.6179 | 0 | 848403.8912 | 0 | 20829768.8545 | 54194785.7863 | 36989054.8906 | 165423273.2609 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 188795015.8895 | 222529858.7982 | 74989.4209 | 72.4891 | 2604.4609 | 3069.8391 | 53.0955 | 62.5828
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 213.5982 | 169.8581 | 18.5669 | 4 | 2575.534 | 3029.7683 | 52.5057 | 61.7659 | 222.8289 | 0 | 212.0196 | 18071160.3734 | 1575059.0159 | 20253618.3792 | 13546965.3499 | 0 | 764679.176 | 0 | 21142478.0948 | 55008391.0842 | 37544357.2244 | 167906708.6978 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 191278451.3263 | 225013294.2351 | 100000 | 74.2675 | 2575.534 | 3029.7683 | 52.5057 | 61.7659
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 217.5734 | 172.2562 | 18.907 | 4 | 2553.483 | 2999.5468 | 52.0562 | 61.1498 | 222.2793 | 0 | 261.0651 | 18253363.8062 | 1590592.2964 | 20482055.0843 | 13786411.5028 | 0 | 691817.2687 | 0 | 21373653.5838 | 55609862.2858 | 37954873.6785 | 169742629.5066 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 193114372.1351 | 226849215.0438 | 133352.1432 | 75.6278 | 2553.483 | 2999.5468 | 52.0562 | 61.1498
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.589 | 174.0497 | 19.1656 | 4 | 2536.7069 | 2976.7522 | 51.7142 | 60.6851 | 221.8565 | 0 | 316.8753 | 18389163.4929 | 1602166.7757 | 20652480.0725 | 13967743.6855 | 0 | 630240.186 | 0 | 21544299.7429 | 56053848.5874 | 38257903.4523 | 171097845.9952 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 194469588.6237 | 228204431.5324 | 177827.941 | 76.6622 | 2536.7069 | 2976.7522 | 51.7142 | 60.6851
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 222.8345 | 175.3701 | 19.3595 | 4 | 2523.9666 | 2959.6025 | 51.4545 | 60.3355 | 221.5382 | 0 | 344.9572 | 18488894.786 | 1610665.5763 | 20777730.2512 | 14102519.7203 | 0 | 578949.9563 | 0 | 21667916.5132 | 56375474.0665 | 38477419.4505 | 172079570.3203 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 195451312.9489 | 229186155.8576 | 237137.3706 | 77.4382 | 2523.9666 | 2959.6025 | 51.4545 | 60.3355
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 224.5077 | 176.3458 | 19.505 | 4 | 2514.3087 | 2946.6963 | 51.2576 | 60.0724 | 221.299 | 0 | 400.1022 | 18562451.1658 | 1616933.0211 | 20870156.5894 | 14202872.8145 | 0 | 537149.1152 | 0 | 21757929.4553 | 56609669.2777 | 38637262.4944 | 172794423.9333 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 196166166.5618 | 229901009.4706 | 316227.766 | 78.0199 | 2514.3087 | 2946.6963 | 51.2576 | 60.0724
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 225.7381 | 177.0587 | 19.613 | 4 | 2506.9991 | 2937.0043 | 51.1086 | 59.8748 | 221.1221 | 0 | 426.2157 | 18616124.2964 | 1621505.8621 | 20937624.8282 | 14276630.3082 | 0 | 503423.3599 | 0 | 21822570.3754 | 56777851.692 | 38752050.448 | 173307781.17 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 196679523.7986 | 230414366.7073 | 421696.5034 | 78.4522 | 2506.9991 | 2937.0043 | 51.1086 | 59.8748
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.7003 | 177.6137 | 19.6964 | 4 | 2501.4748 | 2929.6599 | 50.9959 | 59.7251 | 220.9832 | 0 | 426.634 | 18657872.6563 | 1625062.4858 | 20990118.4756 | 14334276.2242 | 0 | 477375.5001 | 0 | 21873035.0834 | 56909150.5105 | 38841664.5895 | 173708555.5254 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197080298.154 | 230815141.0627 | 562341.3252 | 78.7856 | 2501.4748 | 2929.6599 | 50.9959 | 59.7251
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.7844 | 178.2386 | 19.7794 | 4 | 2497.1859 | 2923.5742 | 50.9085 | 59.601 | 220.8281 | 0 | 459.4991 | 18704826.1631 | 1629062.284 | 21049172.724 | 14399092.3999 | 0 | 461148.9392 | 0 | 21934887.979 | 57070079.0572 | 38951501.6294 | 174199771.1758 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197571513.8043 | 231306356.7131 | 749894.2093 | 79.1177 | 2497.1859 | 2923.5742 | 50.9085 | 59.601
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.2667 | 178.5138 | 19.8228 | 4 | 2494.1111 | 2919.5662 | 50.8458 | 59.5193 | 220.7575 | 0 | 405.3408 | 18725491.3185 | 1630822.5855 | 21075168.9239 | 14427892.5415 | 0 | 445110.4467 | 0 | 21958749.4683 | 57132161.7576 | 38993874.3481 | 174389271.39 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197761014.0186 | 231495856.9273 | 1000000 | 79.2912 | 2494.1111 | 2919.5662 | 50.8458 | 59.5193
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.4325 | 178.6073 | 19.8456 | 4 | 2491.6419 | 2916.6079 | 50.7955 | 59.459 | 220.7326 | 0 | 385.6099 | 18732511.4152 | 1631420.56 | 21084000.7458 | 14437774.9117 | 0 | 428996.6751 | 0 | 21962734.6801 | 57142530.4612 | 39000951.2014 | 174420920.6506 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197792663.2791 | 231527506.1878 | 1333521.4322 | 79.3825 | 2491.6419 | 2916.6079 | 50.7955 | 59.459
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.8929 | 178.8702 | 19.8794 | 4 | 2490.0552 | 2914.2984 | 50.7631 | 59.4119 | 220.6657 | 0 | 391.142 | 18752238.3562 | 1633100.8751 | 21108820.7422 | 14465276.7452 | 0 | 423319.7759 | 0 | 21989275.0329 | 57211583.0151 | 39048080.9883 | 174631695.5309 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 198003438.1594 | 231738281.0682 | 1778279.41 | 79.5177 | 2490.0552 | 2914.2984 | 50.7631 | 59.4119
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.0749 | 178.9734 | 19.8966 | 4 | 2488.7463 | 2912.6236 | 50.7365 | 59.3778 | 220.6389 | 0 | 503.828 | 18759981.9184 | 1633760.4483 | 21118564.3195 | 14476135.5774 | 0 | 415884.0668 | 0 | 21997687.2688 | 57233469.9274 | 39063019.2557 | 174698502.7822 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 198070245.4108 | 231805088.3195 | 2371373.7057 | 79.5864 | 2488.7463 | 2912.6236 | 50.7365 | 59.3778
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.2166 | 179.0537 | 19.9098 | 4 | 2487.763 | 2911.3601 | 50.7164 | 59.352 | 220.618 | 0 | 480.2574 | 18766009.8758 | 1634273.8863 | 21126149.4961 | 14484591.5338 | 0 | 410323.1041 | 0 | 22004325.6794 | 57250741.7101 | 39074807.6022 | 174751222.8877 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 198122965.5162 | 231857808.4249 | 3162277.6602 | 79.639 | 2487.763 | 2911.3601 | 50.7164 | 59.352
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.5 | 177.4817 | 19.7652 | 4 | 2487.0113 | 2913.7057 | 50.7011 | 59.3998 | 221.0005 | 0 | 930.0025 | 18647947.3068 | 1624216.9459 | 20977637.3221 | 14322034.8541 | 0 | 365975.3193 | 0 | 21815746.5818 | 56760097.5809 | 38739932.9023 | 173253588.8132 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 196625331.4417 | 230360174.3505 | 4216965.0343 | 79.0609 | 2487.0113 | 2913.7057 | 50.7011 | 59.3998
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.399 | 178.0031 | 19.8181 | 4 | 2486.3856 | 2911.9422 | 50.6883 | 59.3639 | 220.8738 | 0 | 482.5461 | 18687139.8252 | 1627555.6818 | 21026926.3528 | 14375836.0727 | 0 | 374072.1678 | 0 | 21875696.7391 | 56916075.5928 | 38846391.1005 | 173729693.5328 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197101436.1613 | 230836279.07 | 5623413.2519 | 79.2723 | 2486.3856 | 2911.9422 | 50.6883 | 59.3639
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.928 | 178.3089 | 19.8495 | 4 | 2485.9372 | 2910.8193 | 50.6792 | 59.341 | 220.799 | 0 | 667.6552 | 18710110.5343 | 1629512.423 | 21055820.012 | 14407482.874 | 0 | 378127.618 | 0 | 21910610.8499 | 57006914.9472 | 38908390.8264 | 174006970.0849 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197378712.7134 | 231113555.6222 | 7498942.0933 | 79.3981 | 2485.9372 | 2910.8193 | 50.6792 | 59.341
1 | 5800 | 707 | 0.04 | 15 | 15 | 7 | 1e-08 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 228.6124 | 178.7038 | 19.8888 | 4 | 2485.5998 | 2909.6427 | 50.6723 | 59.317 | 220.7022 | 0 | 468.2376 | 18739757.883 | 1632037.8103 | 21093117.7493 | 14448422.9589 | 0 | 385192.5249 | 0 | 21956426.2813 | 57126117.3017 | 38989748.8827 | 174370821.3922 | 961560.8286 | 22410181.7999 | 22410181.7999 | 1478867.319 | 9845793.7898 | 0 | 197742564.0208 | 231477406.9295 | 10000000 | 79.5553 | 2485.5998 | 2909.6427 | 50.6723 | 59.317
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.1276 | 0.4035 | 0.036188 | 4 | 177663.0179 | 415999.6981 | 3621.9009 | 8480.7165 | 153.5082 | 0 | 63.3344 | 252478.2947 | 22464.481 | 161275.2662 | 83103.0834 | 0 | 61511.4979 | 0 | 226524.723 | 589370.8627 | 402257.7242 | 1798985.9332 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 25716738.342 | 60215994.9432 | 100 | 0.14475 | 177663.0179 | 415999.6981 | 3621.9009 | 8480.7165
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.4565 | 0.66886 | 0.064837 | 4 | 101894.9457 | 234917.5659 | 2077.2663 | 4789.1123 | 168.8106 | 0 | 64.0317 | 361340.6822 | 32656.6661 | 241380.7536 | 106998.7082 | 0 | 67559.8449 | 0 | 315875.2955 | 821842.7238 | 560924.5462 | 2508579.2205 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 26426331.6293 | 60925588.2305 | 133.3521 | 0.25935 | 101894.9457 | 234917.5659 | 2077.2663 | 4789.1123
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 1.8653 | 1.0109 | 0.10146 | 4 | 67093.2175 | 152097.4583 | 1367.786 | 3100.7124 | 181.8435 | 0 | 272.4099 | 481969.4895 | 43604.6493 | 335892.9362 | 134154.1653 | 0 | 73795.6107 | 0 | 417072.5719 | 1085137.2788 | 740628.4901 | 3312255.1918 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 27230007.6006 | 61729264.2018 | 177.8279 | 0.40585 | 67093.2175 | 152097.4583 | 1367.786 | 3100.7124
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 2.3904 | 1.4604 | 0.14976 | 4 | 47059.3175 | 104648.3364 | 959.3678 | 2133.3979 | 193.0597 | 0 | 358.7712 | 623283.2064 | 56411.775 | 450831.8054 | 168289.6503 | 0 | 80981.8285 | 0 | 538121.3236 | 1400081.3002 | 955584.2562 | 4273585.1456 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 28191337.5544 | 62690594.1556 | 237.1374 | 0.59906 | 47059.3175 | 104648.3364 | 959.3678 | 2133.3979
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.0517 | 2.0374 | 0.21217 | 4 | 34554.9839 | 75206.0049 | 704.4501 | 1533.1761 | 202.3436 | 0 | 463.491 | 786933.0788 | 71217.5364 | 588425.2845 | 211042.2953 | 0 | 88440.689 | 0 | 680962.9647 | 1771725.9496 | 1209239.3659 | 5407987.1642 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 29325739.573 | 63824996.1742 | 316.2278 | 0.84867 | 34554.9839 | 75206.0049 | 704.4501 | 1533.1761
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 3.8996 | 2.7887 | 0.29374 | 4 | 26125.9431 | 55488.3493 | 532.6127 | 1131.2051 | 210.0565 | 0 | 77.9271 | 980762.4662 | 88718.9843 | 756403.8715 | 266046.1929 | 0 | 96727.851 | 0 | 853577.1527 | 2220832.6586 | 1515763.9231 | 6778833.1004 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 30696585.5092 | 65195842.1104 | 421.6965 | 1.1749 | 26125.9431 | 55488.3493 | 532.6127 | 1131.2051
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 4.9863 | 3.7614 | 0.39974 | 4 | 20232.6589 | 41808.6558 | 412.4701 | 852.326 | 216.3639 | 0 | 85.2038 | 1210212.2565 | 109390.9609 | 960978.3449 | 336540.594 | 0 | 105791.4913 | 0 | 1061936.3226 | 2762940.4782 | 1885763.6491 | 8433554.0975 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 32351306.5064 | 66850563.1076 | 562.3413 | 1.599 | 20232.6589 | 41808.6558 | 412.4701 | 852.326
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-13 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 6.4166 | 5.0495 | 0.54018 | 4 | 15922.9546 | 31889.5247 | 324.611 | 650.1111 | 221.5295 | 0 | 77.4033 | 1488855.3256 | 134433.6075 | 1216268.6282 | 429462.7262 | 0 | 116967.7371 | 0 | 1320535.3296 | 3435762.0485 | 2344978.196 | 10487263.5986 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 34405016.0075 | 68904272.6086 | 749.8942 | 2.1607 | 15922.9546 | 31889.5247 | 324.611 | 650.1111
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 8.2654 | 6.7083 | 0.72121 | 4 | 12788.3999 | 24747.2782 | 260.7088 | 504.5067 | 225.3834 | 0 | 70.8447 | 1818793.6907 | 164007.4819 | 1526588.0438 | 549525.2565 | 0 | 130128.2772 | 0 | 1633726.6726 | 4250621.6786 | 2901136.6372 | 12974527.7385 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 36892280.1474 | 71391536.7486 | 1000 | 2.8848 | 12788.3999 | 24747.2782 | 260.7088 | 504.5067
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 10.7474 | 8.9871 | 0.9706 | 4 | 10327.2689 | 19213.3117 | 210.5353 | 391.6893 | 229.1757 | 0 | 90.1386 | 2235684.7569 | 201265.8567 | 1928986.6545 | 711572.4219 | 0 | 145483.2385 | 0 | 2036967.2421 | 5299770.9246 | 3617202.5555 | 16176933.6508 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 40094686.0596 | 74593942.6608 | 1333.5214 | 3.8824 | 10327.2689 | 19213.3117 | 210.5353 | 391.6893
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 13.9922 | 11.9467 | 1.2944 | 4 | 8501.2154 | 15164.2181 | 173.3088 | 309.1431 | 231.8525 | 0 | 87.4608 | 2733862.5222 | 245646.8464 | 2422330.0796 | 923190.2039 | 0 | 164358.4879 | 0 | 2530861.3746 | 6584782.1456 | 4494249.1181 | 20099280.7782 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 44017033.1871 | 78516289.7882 | 1778.2794 | 5.1777 | 8501.2154 | 15164.2181 | 173.3088 | 309.1431
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 18.3043 | 15.8854 | 1.7254 | 4 | 7091.3969 | 12090.1734 | 144.5677 | 246.4745 | 233.9662 | 0 | 84.6971 | 3344622.6085 | 299871.7774 | 3042514.3639 | 1204523.7088 | 0 | 187821.3949 | 0 | 3150948.0029 | 8198120.3551 | 5595385.5969 | 25023807.8084 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 48941560.2172 | 83440816.8184 | 2371.3737 | 6.9015 | 7091.3969 | 12090.1734 | 144.5677 | 246.4745
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 23.9922 | 21.0856 | 2.2946 | 4 | 6001.1271 | 9759.8576 | 122.3411 | 198.9679 | 235.6074 | 0 | 93.8994 | 4087859.652 | 365617.3778 | 3816125.2558 | 1575764.9356 | 0 | 216189.2442 | 0 | 3924007.0215 | 10209461.3454 | 6968167.1517 | 31163191.9839 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 55080944.3928 | 89580200.994 | 3162.2777 | 9.1784 | 6001.1271 | 9759.8576 | 122.3411 | 198.9679
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 31.4831 | 27.9379 | 3.0449 | 4 | 5150.4852 | 7983.0537 | 104.9996 | 162.7453 | 236.8732 | 0 | 127.2293 | 4991209.8904 | 445216.9155 | 4779562.4177 | 2064755.2089 | 0 | 250538.9162 | 0 | 4887200.506 | 12715493.214 | 8678585.3958 | 38812562.4646 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 62730314.8734 | 97229571.4746 | 4216.965 | 12.1795 | 5150.4852 | 7983.0537 | 104.9996 | 162.7453
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 41.3005 | 36.92 | 4.0285 | 4 | 4482.1465 | 6623.091 | 91.3746 | 135.0207 | 237.8378 | 0 | 110.6146 | 6084414.2991 | 541152.9482 | 5973700.1611 | 2705666.3367 | 0 | 292019.0038 | 0 | 6082811.5721 | 15826227.9544 | 10801725.7753 | 48307718.0509 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 72225470.4597 | 106724727.0609 | 5623.4133 | 16.114 | 4482.1465 | 6623.091 | 91.3746 | 135.0207
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-12 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 54.0117 | 48.5338 | 5.3003 | 4 | 3956.1216 | 5583.3398 | 80.6509 | 113.8239 | 238.5186 | 0 | 112.0189 | 7391151.6792 | 655341.4394 | 7434799.3255 | 3535307.0022 | 0 | 341663.0719 | 0 | 7549722.3821 | 19642828.9772 | 13406634.3967 | 59957448.2743 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 83875200.6831 | 118374457.2843 | 7498.9421 | 21.2014 | 3956.1216 | 5583.3398 | 80.6509 | 113.8239
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 70.1406 | 63.1617 | 6.9008 | 4 | 3544.9781 | 4794.8031 | 72.2692 | 97.7485 | 238.7993 | 0 | 127.9618 | 8916437.2974 | 788050.2764 | 9179022.7278 | 4586176.0729 | 0 | 401539.5017 | 0 | 9309778.0917 | 24222132.8965 | 16532103.4169 | 73935240.2813 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 97852992.6901 | 132352249.2913 | 10000 | 27.6033 | 3544.9781 | 4794.8031 | 72.2692 | 97.7485
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 89.8831 | 80.7069 | 8.8152 | 4 | 3231.1746 | 4209.5719 | 65.8719 | 85.8178 | 238.4205 | 0 | 135.9755 | 10619189.925 | 935564.8907 | 11167659.0867 | 5866214.7074 | 0 | 474752.4143 | 0 | 11334718.5994 | 29490612.7251 | 20127949.1564 | 90016661.505 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 113934413.9139 | 148433670.5151 | 13335.2143 | 35.261 | 3231.1746 | 4209.5719 | 65.8719 | 85.8178
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 112.94 | 100.4194 | 10.9536 | 4 | 3000.0057 | 3787.401 | 61.1592 | 77.2113 | 237.1311 | 0 | 130.6664 | 12411485.0961 | 1090206.6286 | 13301105.8926 | 7347966.3655 | 0 | 565704.9822 | 0 | 13539422.8963 | 35226801.0587 | 24043015.561 | 107525708.481 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 131443460.8899 | 165942717.4911 | 17782.7941 | 43.8144 | 3000.0057 | 3787.401 | 61.1592 | 77.2113
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 138.2117 | 120.7774 | 13.1414 | 4 | 2838.1208 | 3494.4307 | 57.8589 | 71.2387 | 234.8642 | 0 | 130.1928 | 14160737 | 1240584.4626 | 15417787.6156 | 8951182.7865 | 0 | 675047.4444 | 0 | 15773682.3306 | 41039885.797 | 28010565.3418 | 125269472.7785 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 149187225.1873 | 183686481.7885 | 23713.7371 | 52.5655 | 2838.1208 | 3494.4307 | 57.8589 | 71.2387
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 164.248 | 140.6634 | 15.2608 | 4 | 2724.0447 | 3289.2062 | 55.5333 | 67.0549 | 232.2452 | 0 | 155.4465 | 15790689.9569 | 1380267.7187 | 17417211.381 | 10585295.4435 | 0 | 791971.4775 | 0 | 17926520.0313 | 46641127.8864 | 31833528.1618 | 142366612.0571 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 166284364.4659 | 200783621.0671 | 31622.7766 | 61.0432 | 2724.0447 | 3289.2062 | 55.5333 | 67.0549
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 189.2058 | 158.4141 | 17.1301 | 4 | 2649.2574 | 3152.7448 | 54.0087 | 64.273 | 229.3361 | 0 | 151.571 | 17191480.2265 | 1500003.1041 | 19154406.9645 | 12130464.4521 | 0 | 910961.7997 | 0 | 19846053.4533 | 51635360.1002 | 35242194.2689 | 157610924.3693 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 181528676.7781 | 216027933.3793 | 42169.6503 | 68.5206 | 2649.2574 | 3152.7448 | 54.0087 | 64.273
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 205.1512 | 169.0131 | 18.3045 | 4 | 2601.7093 | 3072.8952 | 53.0394 | 62.6451 | 227.2774 | 0 | 164.2838 | 18006792.0306 | 1569570.4358 | 20172978.5634 | 13106069.476 | 0 | 925778.1147 | 0 | 20974663.562 | 54571772.0933 | 37246355.7914 | 166573980.0673 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 190491732.4761 | 224990989.0773 | 56234.1325 | 73.2179 | 2601.7093 | 3072.8952 | 53.0394 | 62.6451
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-11 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 211.7035 | 173.1767 | 18.87 | 4 | 2566.6327 | 3023.6966 | 52.3243 | 61.6421 | 226.3767 | 0 | 167.4579 | 18323116.4927 | 1596537.752 | 20569575.1336 | 13504157.3443 | 0 | 833287.4425 | 0 | 21382402.9244 | 55632626.2753 | 37970410.5691 | 169812113.9338 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 193729866.3427 | 228229122.9439 | 74989.4209 | 75.4802 | 2566.6327 | 3023.6966 | 52.3243 | 61.6421
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 216.8702 | 176.3849 | 19.3124 | 4 | 2539.8636 | 2986.4579 | 51.7786 | 60.883 | 225.6491 | 0 | 210.2476 | 18565394.8327 | 1617183.8249 | 20873856.2731 | 13816917.892 | 0 | 752004.4223 | 0 | 21693889.3256 | 56443049.9966 | 38523541.4114 | 172285837.9788 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 196203590.3876 | 230702846.9888 | 100000 | 77.2497 | 2539.8636 | 2986.4579 | 51.7786 | 60.883
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 220.8332 | 178.7994 | 19.6513 | 4 | 2519.4677 | 2958.3595 | 51.3628 | 60.3102 | 225.0807 | 0 | 248.6803 | 18746931.9071 | 1632648.8835 | 21102143.9985 | 14056019.8769 | 0 | 681725.9517 | 0 | 21925593.5409 | 57045896.8357 | 38934996.7663 | 174125957.7604 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 198043710.1692 | 232542966.7704 | 133352.1432 | 78.6054 | 2519.4677 | 2958.3595 | 51.3628 | 60.3102
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 223.8681 | 180.6213 | 19.9103 | 4 | 2503.9553 | 2937.1388 | 51.0465 | 59.8775 | 224.6393 | 0 | 289.3405 | 18883447.5526 | 1644275.8647 | 21273979.5879 | 14238653.1262 | 0 | 622828.0134 | 0 | 22098641.8164 | 57496132.9516 | 39242292.1669 | 175500251.0796 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 199418003.4884 | 233917260.0896 | 177827.941 | 79.6412 | 2503.9553 | 2937.1388 | 51.0465 | 59.8775
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 226.1092 | 181.951 | 20.1033 | 4 | 2492.1802 | 2921.2046 | 50.8065 | 59.5527 | 224.3098 | 0 | 336.2819 | 18982846.9217 | 1652740.2066 | 21399183.7096 | 14373335.907 | 0 | 573548.055 | 0 | 22222845.3719 | 57819285.1254 | 39462850.1656 | 176486635.4627 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 200404387.8716 | 234903644.4727 | 237137.3706 | 80.4133 | 2492.1802 | 2921.2046 | 50.8065 | 59.5527
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 227.7844 | 182.9365 | 20.2482 | 4 | 2483.2569 | 2909.211 | 50.6246 | 59.3082 | 224.0615 | 0 | 415.8325 | 19056383.3136 | 1659001.4008 | 21491857.9664 | 14473939.3998 | 0 | 533509.412 | 0 | 22313729.6821 | 58055747.4575 | 39624240.566 | 177208409.1981 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 201126161.6069 | 235625418.2081 | 316227.766 | 80.9929 | 2483.2569 | 2909.211 | 50.6246 | 59.3082
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.0903 | 183.6996 | 20.3598 | 4 | 2476.5031 | 2900.1221 | 50.4869 | 59.1229 | 223.867 | 0 | 409.131 | 19113250.0808 | 1663842.8154 | 21563551.812 | 14552187.2437 | 0 | 502232.0891 | 0 | 22384074.976 | 58238771.4824 | 39749158.2239 | 177767068.7233 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 201684821.1322 | 236184077.7334 | 421696.5034 | 81.4394 | 2476.5031 | 2900.1221 | 50.4869 | 59.1229
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 230 | 184.2279 | 20.4398 | 4 | 2471.3999 | 2893.3612 | 50.3828 | 58.9851 | 223.7307 | 0 | 458.3737 | 19152579.9572 | 1667190.9743 | 21613150.2947 | 14606612.1129 | 0 | 476630.9648 | 0 | 22431304.0785 | 58361651.9192 | 39833026.6469 | 178142146.9484 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202059899.3573 | 236559155.9585 | 562341.3252 | 81.7593 | 2471.3999 | 2893.3612 | 50.3828 | 58.9851
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-10 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.0776 | 184.8542 | 20.5222 | 4 | 2467.4663 | 2887.7343 | 50.3026 | 58.8704 | 223.5707 | 0 | 463.6373 | 19199163.4272 | 1671156.3865 | 21671910.965 | 14671114.3644 | 0 | 461426.6838 | 0 | 22493161.0125 | 58522590.9727 | 39942870.8579 | 178633394.6699 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202551147.0788 | 237050403.68 | 749894.2093 | 82.0887 | 2467.4663 | 2887.7343 | 50.3026 | 58.8704
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 229.9398 | 184.1847 | 20.4764 | 4 | 2464.5412 | 2885.7492 | 50.243 | 58.8299 | 223.734 | 0 | 445.7182 | 19149365.1306 | 1666917.3027 | 21609095.6831 | 14602878.8527 | 0 | 423199.4983 | 0 | 22406068.0224 | 58295992.8776 | 39788213.0019 | 177941730.3694 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 201859482.7783 | 236358739.3794 | 1000000 | 81.9055 | 2464.5412 | 2885.7492 | 50.243 | 58.8299
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.3335e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 231.9324 | 185.3455 | 20.5982 | 4 | 2462.4937 | 2881.2113 | 50.2013 | 58.7374 | 223.441 | 0 | 470.424 | 19235670.5577 | 1674263.8653 | 21717972.444 | 14722205.86 | 0 | 434513.5039 | 0 | 22536004.2301 | 58634060.2365 | 40018950.9209 | 178973641.6184 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202891394.0273 | 237390650.6284 | 1333521.4322 | 82.3927 | 2462.4937 | 2881.2113 | 50.2013 | 58.7374
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 1.7783e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.2102 | 185.5048 | 20.6228 | 4 | 2460.8877 | 2879.1056 | 50.1685 | 58.6945 | 223.3987 | 0 | 458.9113 | 19247501.4111 | 1675270.8698 | 21732901.6735 | 14738808.8928 | 0 | 425646.6031 | 0 | 22549850.4857 | 58670085.3533 | 40043538.8034 | 179083604.0928 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 203001356.5016 | 237500613.1028 | 1778279.41 | 82.4911 | 2460.8877 | 2879.1056 | 50.1685 | 58.6945
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 2.3714e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.4077 | 185.6177 | 20.6406 | 4 | 2459.6807 | 2877.5366 | 50.1439 | 58.6625 | 223.3687 | 0 | 465.3608 | 19255891.0769 | 1675984.961 | 21743489.1273 | 14750605.1096 | 0 | 418760.4182 | 0 | 22559444.9703 | 58695048.2343 | 40060576.4825 | 179159800.3802 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 203077552.789 | 237576809.3902 | 2371373.7057 | 82.5626 | 2459.6807 | 2877.5366 | 50.1439 | 58.6625
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 3.1623e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 230.805 | 184.6833 | 20.5579 | 4 | 2458.6876 | 2878.2251 | 50.1237 | 58.6765 | 223.6025 | 0 | 691.1113 | 19186452.7411 | 1670074.4174 | 21655876.0429 | 14654592.5371 | 0 | 388570.8149 | 0 | 22446670.9558 | 58401633.3817 | 39860314.8166 | 178264185.7075 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202181938.1164 | 236681194.7176 | 3162277.6602 | 82.2316 | 2458.6876 | 2878.2251 | 50.1237 | 58.6765
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 4.217e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.0595 | 185.4138 | 20.6315 | 4 | 2457.9589 | 2876.0004 | 50.1088 | 58.6312 | 223.4186 | 0 | 481.5212 | 19240742.4679 | 1674695.5722 | 21724372.5082 | 14729725.2082 | 0 | 400210.387 | 0 | 22530200.996 | 58618961.4118 | 40008645.6628 | 178927554.2141 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202845306.6229 | 237344563.2241 | 4216965.0343 | 82.5259 | 2457.9589 | 2876.0004 | 50.1088 | 58.6312
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 5.6234e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.3345 | 185.5729 | 20.6497 | 4 | 2457.4348 | 2875.108 | 50.0981 | 58.613 | 223.3778 | 0 | 479.0785 | 19252564.1428 | 1675701.7881 | 21739290.5954 | 14746186.8694 | 0 | 399777.6844 | 0 | 22547273.2213 | 58663379.8401 | 40038962.1528 | 179063136.2944 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 202980888.7033 | 237480145.3045 | 5623413.2519 | 82.5987 | 2457.4348 | 2875.108 | 50.0981 | 58.613
1 | 5900 | 707 | 0.04 | 15 | 15 | 7 | 7.4989e-09 | 5spot_SharedNeighbor | Water | Porous | Wet | R600a | MinimizeLCOE_Brownfield | IgnoreSilica | 2019 | 232.3929 | 185.6063 | 20.6552 | 4 | 2457.042 | 2874.6043 | 50.0901 | 58.6027 | 223.3689 | 0 | 484.2784 | 19255042.849 | 1675912.764 | 21742418.6709 | 14749672.7655 | 0 | 397403.5188 | 0 | 22549975.7216 | 58670411.1916 | 40043761.1946 | 179084598.676 | 961560.8286 | 22956191.5802 | 22956191.5802 | 1478867.319 | 10064197.702 | 0 | 203002351.0849 | 237501607.6861 | 7498942.0933 | 82.6206 | 2457.042 | 2874.6043 | 50.0901 | 58.6027